## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:December 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-12-01 |  | 2023-11-01 |  | 2022-12-12
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10921 | 2023-12-04 | 12608 | 2023-11-02 | 10346 | 2022-12-01 | 15648 | 2023-04-19
|  |  | 19:00 |  | 18:00 |  | 18:00 |  | 21:00
2 | Minimum Generation (MW) | 5635 | 2023-12-17 | 5719 | 2023-11-18 | 5506 | 2022-12-17 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10921 | 2023-12-04 | 12608 | 2023-11-02 | 10346 | 2022-12-01 | 15648 | 2023-04-19
|  |  | 19:00 |  | 18:00 |  | 18:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 9618 | 2023-12-28 | 11209 | 2023-11-02 | 9246 | 2022-12-01 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10921 | 2023-12-30 | 12650 | 2023-11-30 | 10550 | 2022-12-31 | 16096 | 2023-04-19
|  |  | 19:00 |  | 18:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 9939.1935 |  | 11024.2667 |  | 9584.8065 |  | - | -
7 | Average Generation (MW) at Day Peak | 8800.1935 |  | 9678.8333 |  | 8308.3226 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 928 | 2023-12-02 | 928 | 2023-11-12 | 934 | 2022-12-18 | 956 | 27/3/2019
|  |  | 1:00 |  | 5:00 |  | 10:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 134 | 2023-12-04 | 158 | 2023-11-02 | 122 | 2022-12-01 | 194 | 12/06/19
|  |  | 17:00 |  | 18:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | 44 | 2023-11-01 | 188 | 2022-12-01 | 4395 | 04/10/2022
[5 empty] | 19:00 |  | 18:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | 12524 | 2023-11-01 | 10346 | 44896 | 13200 | 04/10/2022
|  |  |  | - | 19:00 | - | 0.75 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | 0 | 2023-11-05 | 0 | 44897 | - | -
[5 empty] | 19:00 |  | 18:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | 12197 | 2023-11-05 | 8976 | 2022-12-02 | - | -
|  | - | - |  | 19:00 |  | 18:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | 324 | 2023-11-08 | 52 | 44896 | - | -
|  | - | - |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | 9911 | 2023-11-08 | 9246 | 44896 | - | -
|  | - | - |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | 0 | 2023-11-05 | 0 | 44897 | - | -
|  | - | - |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | 10908 | 2023-11-05 | 8089 | 44897 | - | -
|  | - | - |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | - | - | 5 |  | 2 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | - | - | 6 |  | 1 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1616.4983 |  | 1832.996 |  | 1409.473 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 31.8652 |  | 22.2246 |  | 53.265 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1584.6331 |  | 1810.7714 |  | 1356.208 |  | - | -
23 | Net Generation of IPP (MKWH) | 2407.5536 |  | 3456.7822 |  | 3151.7645 |  | - | -
24 | Net Generation of REB (MKWH) | 75.7392 |  | 102.6847 |  | 135.1789 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 78.4238 |  | 101.6965 |  | 277.2375 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4146.3497 |  | 5471.9348 |  | 4920.3889 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 3078.1257 |  | 3323.4316 |  | 3396.0047 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 8.2293 |  | 7.0767 |  | 33.738 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 366.9347 |  | 495.1555 |  | 1031.992 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 62.1719 |  | 87.2163 |  | 32.3793 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 32.3549 |  | 37.3187 |  | 33.1894 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 700.7034 |  | 835.1367 |  | 446.3504 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 585.1283 |  | 641.9939 |  | 653.3183 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 74.6495 |  | 70.0491 |  | 85.1421 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:December 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10921 | 2023-12-04 | 19:00
Generation Period
| Dhaka | MW | 4227.83
| Chattogram | MW | 1167
| Cumilla | MW | 896
| Mymensingh | MW | 793
| Sylhet | MW | 388
a) | Total supply in East zone | MW | 7471.83
| Khulna | MW | 1102.2
| Barisal | MW | 284
| Rajshahi | MW | 924.8
| Rangpur | MW | 697
b) | Total supply in West zone | MW | 3008
c) | Total supply in both zone ( a+b) | MW | 10479.83
Ref: | 27.21.0000.603.16.087.20.756 | Date: 16/01/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:December 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 320 | 2023-12-01 | 18:30
| b) Ishurdi end | MW | 240 | 2023-12-14 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 500 | 2023-12-12 | 15:00
| b) Ishurdi end | MW | 116 | 2023-12-12 | 19:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 2.5195
| b) Ishurdi end | MKWH | 62.4529
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 60.5794
| b) Ishurdi end | MKWH | 2.4461
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 |  |  |  |  | 2.955
| a) Ashuganj end | MW | 330 | 2023-12-01 | 18:00
| b)Serajganj end | MW | 470 | 2023-12-14 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 180 | 2023-12-01 | 1:00
| b)Sirajganj end | MW | 160 | 2023-12-01 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.6616
| b)Sirajganj end | MKWH | 126.01
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 122.9926
| b)Sirajganj end | MKWH | 1.182
30 | Transmission loss of EWI /NO-2 | % | 2.364%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 1696 | 23.12.2023 | 14:30
|  | MW | 1070
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 1678 | 23.12.2023 | 14:30
|  | MW | 1064
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 35119.104 | 23.12.2023 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 34996.402 | 23.12.2023
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 519885.82
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 518726
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.22
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: December 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2023-12-24 00:03 | 2023-12-24 01:58 | 1:55 | T | TAP PRV Trip false tripping. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2023-12-16 16:54 | 2023-12-16 17:11 | 0:17 | T | Unknown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2023-12-23 15:53 | 2023-12-23 16:15 | 0:22 | T | Unknown | 0 | 0 | Power interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2023-12-25 02:05 | 2023-12-25 02:05 | 0:00 | T | Unknown | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-12-19 11:40 | 2023-12-19 12:00 | 0:20 | T | PBS 33 kV Feeders fault | 43 | 14.3333 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-12-29 07:56 | 2023-12-29 08:21 | 0:25 | T | Dhamrai-Kaliakoir ckt-1 & 2 tripped from Kaliakoir end. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-19 11:40 | 2023-12-19 12:00 | 0:20 | T | 33 kV PBS feeders fault | 43 | 14.3333 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-29 09:02 | 2023-12-29 09:22 | 0:20 | T | Dhamrai-Kaliakoir ckt-1&2 tripped from Kaliakoir end. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 HT | 2023-12-03 08:29 | 2023-12-03 16:09 | 7:40 | E/O | works on transformer bushing and Connector. | 50 | 383.3333 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2023-12-22 23:14 | 2023-12-23 00:40 | 1:26 | E/O | 33 kv Bus- Section T-1 and Bus- Section T-3 D/S B-Phase Red hot | 30 | 43 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-12-14 09:44 | 2023-12-14 10:57 | 1:13 | E/O | 33 kV CB fault | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 & GT-4 (50/75 MVA) LT | 2023-12-18 13:45 | 2023-12-18 13:47 | 0:02 | T | Trip due to df/dt(U/F relay) | 20 | 0.66667 | Power interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-12-21 19:11 | 2023-12-22 16:33 | 21:22 | E/O | Transformer T1 Hydraulic Parser Fault. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2023-12-03 15:26 | 2023-12-03 15:53 | 0:27 | T | Over current & Earth fault general trip. | 13 | 5.85 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2023-12-03 15:26 | 2023-12-03 15:56 | 0:30 | T | Over current & Earth fault genaral trip. | 13 | 6.5 | Power interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2023-12-15 16:32 | 2023-12-15 16:42 | 0:10 | T | T-1 Main Bus Isolator foult | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2023-12-15 16:32 | 2023-12-15 16:55 | 0:23 | T | T-1 Main Bus Isolator foult | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-12-18 13:44 | 2023-12-18 13:50 | 0:06 | T | df/dt | 47 | 4.7 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-12-07 10:11 | 2023-12-07 11:40 | 1:29 | E/O | 33kV BUS Section DS burn. Working on PDB's own responsibility for this reason no loadshed. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2023-12-14 07:55 | 2023-12-14 16:08 | 8:13 | T | df/dt | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-3 HT | 2023-12-14 07:55 | 2023-12-14 16:08 | 8:13 | T | df/dt | 0 | 0 | No interruption
|  |  | Total : | 55:13 |  | Unserved Energy: |  | 472.7167
Dhaka (South) Grid Circle :
Mogbazar 132/33kV Grid Sub-Station | GT-2 HT | 2023-12-21 04:02 | 2023-12-21 04:15 | 0:13 | T | Heavy Fault in 33 kv Green Road Dormetory Feeder at short distance . | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-3 HT | 2023-12-21 04:02 | 2023-12-21 05:05 | 1:03 | T | Heavy Fault in 33 kv Green Road Dormetory Feeder at short distance . | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | 132 kV Main Bus-2 | 2023-12-25 12:01 | 2023-12-25 17:00 | 4:59 | E/O | Main bus-2 S/D for Bus Coupler commissioning | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-12-16 15:31 | 2023-12-16 19:55 | 4:24 | E/O | T-3 33kv XLPE Cable R-ph Burst. | 23 | 101.2 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2023-12-06 06:20 | 2023-12-06 06:52 | 0:32 | T | DPDC ends 33kv Bus Problem | 34 | 18.1333 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 HT | 2023-12-06 06:20 | 2023-12-06 07:34 | 1:14 | T | DPDC ends 33kv Bus Problem | 34 | 41.9333 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-12-26 16:10 | 2023-12-26 17:13 | 1:03 | E/O | Due to 33 kv side fault kabilgonj feeder | 0 | 0 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-12-24 12:15 | 2023-12-24 13:10 | 0:55 | E/O | Emergency maintenance work of 33kV Kabilganj feeder Y-ph ( Bus loop cable blast) By PBS. | 35 | 32.0833 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2023-12-02 17:45 | 2023-12-03 19:40 | 25:55 | E/O | Corrective Maintenance of 33 KV CT at B Phase (Transformer-2) for Oil Leakage | 30 | 0.5 | Power interruption 17:45 to 17:46
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2023-12-11 17:04 | 2023-12-11 17:20 | 0:16 | T | Over current trip | 28 | 7.4667 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 LT | 2023-12-29 13:27 | 2023-12-30 18:17 | 28:50 | E/O | Due to Emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 69:24 |  | Unserved Energy: |  | 201.3167
Chattogram Grid Circle :
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2023-12-18 06:48 | 2023-12-18 07:14 | 0:26 | E/O | High Temperature Maintenance. | 15 | 6.5 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2023-12-30 18:48 | 2023-12-30 18:48 | 0:00 | T | 33kv R phase blust. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Power Transformer TR1 (405T) HT | 2023-12-03 06:19 | 2023-12-03 15:10 | 8:51 | E/O | T1(404T) X-former secondary breaker(407B) is off due to R-phase current not show. | 0 | 0 | No interruption
|  |  | Total : | 9:17 |  | Unserved Energy: |  | 6.5
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-12-04 07:29 | 2023-12-04 13:58 | 6:29 | T | Unknown. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-12-28 10:12 | 2023-12-28 10:20 | 0:08 | E/O | SPS protection test | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2023-12-02 10:03 | 2023-12-02 11:55 | 1:52 | E/O | maintenance work by PDB in TR-3 33 kv bus | 10 | 18.6667 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 LT | 2023-12-01 07:54 | 2023-12-01 08:00 | 0:06 | T | Unknown. | 14 | 1.4 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 LT | 2023-12-20 16:34 | 2023-12-20 16:46 | 0:12 | T | 33 KV PBS feeder faulty. | 30 | 6 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2023-12-22 15:20 | 2023-12-22 21:20 | 6:00 | T | 132 kV Transformer side LA Burst | 0 | 0 | No interruption
|  |  | Total : | 14:47 |  | Unserved Energy: |  | 26.0667
Khulna Grid Circle :
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-12-17 11:10 | 2023-12-17 11:21 | 0:11 | E/O | 33KV Bus connector Disconnect | 12 | 2.2 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT & T2 | 2023-12-09 11:15 | 2023-12-09 11:30 | 0:15 | T | LA blast | 20 | 5 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-12-10 09:34 | 2023-12-10 11:23 | 1:49 | E/O | 33 kv underground cable reconnection. | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-16 14:27 | 2023-12-16 14:39 | 0:12 | E/O | Auxiliary fuse cut | 16 | 3.2 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-12-14 17:27 | 2023-12-14 17:36 | 0:09 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-12-20 10:15 | 2023-12-20 13:55 | 3:40 | E/O | Loop maintenance work between transfer DS to CT DS | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2023-12-22 11:00 | 2023-12-22 12:39 | 1:39 | E/O | Red hot maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2023-12-02 15:41 | 2023-12-02 16:50 | 1:09 | E/O | Unexpected sound | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2023-12-22 08:11 | 2023-12-22 10:33 | 2:22 | E/O | Red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 11:26 |  | Unserved Energy: |  | 10.4
HVDC Grid Circle :
BIPTC | 20D09C 20MVA HT | 2023-12-18 17:38 | 2023-12-18 18:06 | 0:28 | E/O | 20D09.C Q0 for tc-1 maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-1 HT | 2023-12-14 15:59 | 2023-12-15 15:13 | 23:14 | T | OV trip | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-12-26 23:45 | 2023-12-27 03:34 | 3:49 | T | nesco control room fired by 33 kv system fault | 23 | 87.7833 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-12-26 23:50 | 2023-12-27 01:02 | 1:12 | E/O | For 33 kv nesco control room fire | 20 | 24 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2023-12-26 23:45 | 2023-12-27 12:08 | 12:23 | T | 33 kv nesco control room fired by 33 kv system fault | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-12-13 14:30 | 2023-12-13 21:16 | 6:46 | T | Cable blast | 10 | 67.6667 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-12-13 21:46 | 2023-12-13 23:54 | 2:08 | E/O | T1A Y phase CT fault | 20 | 42.6667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-12-07 11:28 | 2023-12-07 12:02 | 0:34 | T | Trip 50/51 O/C IDMT-1 | 36 | 20.4 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-12-07 15:48 | 2023-12-07 16:05 | 0:17 | T | poradaha(PBS) 33 kv feeder fault (R & Y phase) | 32 | 9.0667 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-12-01 10:25 | 2023-12-01 17:11 | 6:46 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-12-12 10:01 | 2023-12-12 12:46 | 2:45 | E/O | 33kv CT Oil Leakage Maintenance Work. | 0 | 0 | No interruption
|  |  | Total : | 60:22 |  | Unserved Energy: |  | 251.5833
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2023-12-14 16:37 | 2023-12-14 17:58 | 1:21 | E/O | Request Of R/E NESCO, Fulbari- For Red Hot Maintenance | 20 | 27 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-12-09 17:08 | 2023-12-09 18:43 | 1:35 | E/O | Emergency S/D | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) HT | 2023-12-13 13:33 | 2023-12-13 13:33 | 0:00 | T | 132kV T-02 Y-phase LA Blast. | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) HT | 2023-12-13 15:50 | 2023-12-13 19:19 | 3:29 | E/O | LA change | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-12-11 16:15 | 2023-12-11 18:40 | 2:25 | E/O | Transformer Oil Filling. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-12-07 08:35 | 2023-12-07 12:20 | 3:45 | E/O | Changing Of 33 kv Bus DS | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-12-07 08:35 | 2023-12-07 12:20 | 3:45 | E/O | Changing Of 33 kv Bus DS | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 HT | 2023-12-06 17:46 | 2023-12-06 18:20 | 0:34 | E/O | Mohadevpur 33 kv feeder Bus D/s (R-phase) maintanance. | 25 | 14.1667 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-12-07 07:37 | 2023-12-07 08:05 | 0:28 | T | 33 kv feeder fault. | 32 | 14.9333 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-12-23 16:07 | 2023-12-23 16:37 | 0:30 | T | Y-phase lopp out auxiliary x-former-2. | 35 | 17.5 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2023-12-07 07:37 | 2023-12-07 08:08 | 0:31 | T | 33 kv feeder fault. | 32 | 16.5333 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2023-12-23 16:07 | 2023-12-23 18:15 | 2:08 | T | Y-phase lopp out auxiliary x-former-2. | 35 | 74.6667 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-12-19 12:30 | 2023-12-19 17:06 | 4:36 | E/O | Emergency S/D | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 426T LT | 2023-12-07 15:02 | 2023-12-07 15:09 | 0:07 | T | 33 kV porsa feeder (PBS) O/C & E/F. | 10 | 1.1667 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-02 (416T) HT | 2023-12-08 10:47 | 2023-12-08 11:36 | 0:49 | E/O | Emergency S/D | 6 | 4.9 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 33 kV BUS | 2023-12-08 10:53 | 2023-12-08 11:37 | 0:44 | E/O | Red hot Maintenance | 6 | 4.4 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-12-07 17:03 | 2023-12-07 18:04 | 1:01 | E/O | Sirajgonj PBS-01 has been taken shut down for emergency tamai 33kV feeder maintenance.(tami bus ds red hot) | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) LT | 2023-12-19 16:14 | 2023-12-20 17:10 | 24:56 | E/O | To transfer load t4, T-3 33KV CB open. | 0 | 0 | No interruption
|  |  | Total : | 52:44 |  | Unserved Energy: |  | 175.2667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 273:13 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [9 empty] | 498.6333
Month: December 2023 | [9 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2023-12-26 22:30 | 2023-12-27 17:40 | 19:10 | E/O | Line DS (2001S) finger (Line side) Red hot, Temp 216 degree celcius | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2023-12-15 16:32 | 2023-12-15 16:41 | 0:09 | T | T-1 Main Bus Isolator fault. | 35 | 5.25 | Power interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2023-12-15 16:32 | 2023-12-15 16:42 | 0:10 | T | T-1 Main Bus Isolator foult | 35 | 5.8333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2023-12-14 20:06 | 2023-12-14 20:28 | 0:22 | T | ABC phase, Zone-1 | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2023-12-15 18:18 | 2023-12-15 19:18 | 1:00 | T | 186.1 (Lock out relay) | 70 | 70 | Power interruption
|  |  | Total : | 20:51 |  | Unserved Energy: |  | 81.0833
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | HPL-2 | 2023-12-17 16:35 | 2023-12-18 16:18 | 23:43 | E/O | From other end. | 0 | 0 | No interruption |  | 120.3333 | 251.2167
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-12-14 11:24 | 2023-12-14 16:30 | 5:06 | T | Triped | 12 | 61.2 | Power interruption |  | 14.7833
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-2 | 2023-12-04 06:44 | 2023-12-04 12:58 | 6:14 | E/O | CVT-22(Y-ph),Post insulator crack & flashing | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-2 | 2023-12-07 05:43 | 2023-12-07 13:23 | 7:40 | E/O | Due to Sparking at CVT -22 | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2023-12-21 18:01 | 2023-12-21 20:04 | 2:03 | T | Distance fault location | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Kamrangirchar | 2023-12-29 12:22 | 2023-12-29 20:00 | 7:38 | T | Showing Distance Relay | 78 | 595.4 | Power interruption
Maniknagar 132/33kV Grid Sub-Station | Mero Rail - 1 | 2023-12-25 01:42 | 2023-12-25 02:11 | 0:29 | T | For SCADA Upgradation test at Motijheel end. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2023-12-24 01:52 | 2023-12-24 09:40 | 7:48 | T | Triped | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Rampura 2 | 2023-12-24 13:51 | 2023-12-24 15:36 | 1:45 | E/O | Y-phase CB Lower Part Plate Flash Over | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2023-12-13 08:17 | 2023-12-13 08:51 | 0:34 | T | Unknown | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-12-14 10:56 | 2023-12-14 10:56 | 0:00 | T | Red Ph Loop Disconect eart fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-12-14 11:15 | 2023-12-14 15:15 | 4:00 | E/O | Loop Disconnect | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-12-06 10:42 | 2023-12-06 10:55 | 0:13 | E/O | EGCB Ends X-former Tap change | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-12-09 11:23 | 2023-12-09 14:20 | 2:57 | E/O | for Transformer tap change in plant side done by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-12-14 10:56 | 2023-12-14 11:38 | 0:42 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-12-24 01:52 | 2023-12-24 02:36 | 0:44 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-12-06 11:17 | 2023-12-06 11:37 | 0:20 | E/O | EGCB Ends X-former Tap change | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-12-07 21:30 | 2023-12-07 22:18 | 0:48 | E/O | Transformer Oil leakage maintenance work by EGCB. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-12-09 10:55 | 2023-12-09 11:13 | 0:18 | E/O | Transformer Tap change in plant end by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-12-11 09:32 | 2023-12-11 09:58 | 0:26 | T | Remote trip from 230kv | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2023-12-02 08:43 | 2023-12-02 08:59 | 0:16 | T | General trip,Distance Zone 02,B-phase | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2023-12-30 08:41 | 2023-12-30 16:46 | 8:05 | E/O | Request from NLDC xen | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2023-12-30 08:41 | 2023-12-30 16:47 | 8:06 | E/O | Request from NLDC xen sir | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPML(IEL-1) | 2023-12-01 14:05 | 2023-12-01 14:05 | 0:00 | T | Hydrolic truck crain hit the R phase at asharir chor point | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPML(IEL-1) | 2023-12-01 16:03 | 2023-12-01 19:27 | 3:24 | E/O | Cable armour joint | 0 | 0 | No interruption
|  |  | Total : | 93:19 |  | Unserved Energy: |  | 656.6
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2023-12-11 09:08 | 2023-12-11 14:28 | 5:20 | E/O | Hathazari SS works | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2023-12-13 09:21 | 2023-12-13 10:35 | 1:14 | T | Triped | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-12-18 09:09 | 2023-12-18 18:06 | 8:57 | E/O | kaptai ss demand. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2023-12-18 09:09 | 2023-12-18 18:07 | 8:58 | E/O | kaptai ss demand | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | Madunaghat-T.K. chemical | 2023-12-20 09:25 | 2023-12-20 11:00 | 1:35 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 26:04 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Summit GTG | 2023-12-18 11:57 | 2023-12-18 16:01 | 4:04 | T | Inter trip from power station | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-12-28 06:04 | 2023-12-28 16:14 | 10:10 | E/O | Work for LILO in Feni Side | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-12-17 16:40 | 2023-12-17 17:01 | 0:21 | T | Triped | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-12-21 10:50 | 2023-12-21 11:00 | 0:10 | T | N/A | 0 | 0 | No interruption
|  |  | Total : | 14:45 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-12-19 09:15 | 2023-12-19 10:58 | 1:43 | E/O | Emergency maintenance work of 33No. Tower. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2023-12-09 23:31 | 2023-12-10 06:30 | 6:59 | T | Triped | 0 | 0 | No interruption
|  |  | Total : | 8:42 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara 230/132kV Grid Sub-Station | STG (NW) | 2023-12-11 07:18 | 2023-12-11 14:39 | 7:21 | T | Bukhlaz Relay trip NWPGCL End | 0 | 0 | No interruption
|  |  | Total : | 7:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-12-27 09:58 | 2023-12-28 16:22 | 30:24 | E/O | CVT fail (CB open 11:52 pm 26.12.2023 | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Bus Coupler | 2023-12-22 23:06 | 2023-12-23 04:30 | 5:24 | E/O | Red hot maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Bus Coupler | 2023-12-26 12:56 | 2023-12-26 14:47 | 1:51 | T | No signal | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-1 | 2023-12-22 21:28 | 2023-12-23 08:18 | 10:50 | E/O | Red hot in BCB Bay (CT-Y-Phase). (132 KV Raj (New) Ckt-2 is ON through BCB) | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-2 | 2023-12-22 21:28 | 2023-12-23 08:18 | 10:50 | E/O | Red hot in BCB Bay (CT-Y-Phase). (132 KV Raj (New) Ckt-2 is ON through BCB) | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2023-12-26 12:56 | 2023-12-26 13:04 | 0:08 | T | Unidentified & Unknown | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2023-12-07 17:54 | 2023-12-07 19:57 | 2:03 | E/O | Red hot maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-1 | 2023-12-19 12:53 | 2023-12-19 13:09 | 0:16 | T | Triped | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2023-12-19 17:17 | 2023-12-19 19:28 | 2:11 | E/O | Due to Emergency work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-21 10:47 | 2023-12-21 13:04 | 2:17 | T | Distance relay trip zone-1 | 0 | 0 | No interruption
|  |  | Total : | 66:14 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 237:16 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: December 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) HT | 2023-12-03 08:22 | 2023-12-03 20:09 | 11:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) HT | 2023-12-06 08:25 | 2023-12-06 16:51 | 8:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) LT | 2023-12-02 07:56 | 2023-12-02 16:05 | 8:09 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) HT | 2023-12-11 15:39 | 2023-12-13 18:55 | 51:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 2023-12-09 07:41 | 2023-12-09 16:39 | 8:58 | S/O | Annual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 2023-12-10 10:20 | 2023-12-10 17:12 | 6:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2023-12-17 07:20 | 2023-12-17 19:42 | 12:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) LT | 2023-12-18 07:26 | 2023-12-18 20:36 | 13:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) LT | 2023-12-20 07:32 | 2023-12-20 23:08 | 15:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) LT | 2023-12-24 14:27 | 2023-12-24 22:25 | 7:58 | S/O | PRV maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) HT | 2023-12-30 07:38 | 2023-12-30 21:05 | 13:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) LT | 2023-12-13 13:15 | 2023-12-13 15:41 | 2:26 | S/O | For Oil leakage identify | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) LT | 2023-12-27 07:30 | 2023-12-27 21:13 | 13:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) LT | 2023-12-28 07:39 | 2023-12-29 03:52 | 20:13 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-1 HT | 2023-12-18 06:26 | 2023-12-18 20:34 | 14:08 | S/O | Anual maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-1 LT | 2023-12-17 07:19 | 2023-12-17 19:43 | 12:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-1 LT | 2023-12-20 07:31 | 2023-12-20 23:10 | 15:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 LT | 2023-12-13 13:14 | 2023-12-13 15:44 | 2:30 | S/O | For Oil leakage identify | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 LT | 2023-12-27 07:29 | 2023-12-27 21:14 | 13:45 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 LT | 2023-12-30 07:36 | 2023-12-30 21:10 | 13:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-12-18 13:17 | 2023-12-18 16:00 | 2:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-12-19 10:24 | 2023-12-19 12:28 | 2:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-12-20 09:29 | 2023-12-20 12:28 | 2:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-12-25 12:19 | 2023-12-26 16:35 | 28:16 | S/O | DS change Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-12-30 09:59 | 2023-12-30 09:59 | 0:00 | S/O | Mirpur loop purpose | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-12-22 08:30 | 2023-12-22 10:04 | 1:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-12-25 09:43 | 2023-12-25 12:00 | 2:17 | S/O | DS maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-12-28 07:59 | 2023-12-29 17:32 | 33:33 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-12-30 09:32 | 2023-12-30 09:42 | 0:10 | S/O | T 3 loop change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-12-10 11:56 | 2023-12-10 18:21 | 6:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-12-11 08:35 | 2023-12-11 13:20 | 4:45 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2023-12-09 09:05 | 2023-12-09 13:20 | 4:15 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2023-12-12 09:43 | 2023-12-12 17:30 | 7:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 LT | 2023-12-02 08:38 | 2023-12-02 15:57 | 7:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 LT | 2023-12-17 10:40 | 2023-12-17 12:11 | 1:31 | S/O | DS Red Hot, Emergency S/D | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2023-12-03 09:04 | 2023-12-03 12:39 | 3:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2023-12-30 08:31 | 2023-12-30 17:16 | 8:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 LT | 2023-12-27 09:50 | 2023-12-27 17:09 | 7:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2023-12-05 08:54 | 2023-12-05 13:21 | 4:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2023-12-20 09:09 | 2023-12-20 12:44 | 3:35 | S/O | Red hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer LT | 2023-12-25 09:44 | 2023-12-26 17:00 | 31:16 | S/O | DS Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer LT | 2023-12-28 08:30 | 2023-12-29 17:48 | 33:18 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2023-12-09 07:24 | 2023-12-09 13:37 | 6:13 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2023-12-10 11:46 | 2023-12-10 18:18 | 6:32 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2023-12-11 08:27 | 2023-12-11 13:36 | 5:09 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2023-12-12 08:38 | 2023-12-12 18:17 | 9:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan LT | 2023-12-09 10:04 | 2023-12-09 15:18 | 5:14 | S/O | Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2023-12-09 10:03 | 2023-12-09 15:10 | 5:07 | S/O | Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 LT | 2023-12-24 06:30 | 2023-12-24 09:13 | 2:43 | S/O | HT side Y-phase CT connecting clamp temperature high | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus B | 2023-12-02 12:10 | 2023-12-02 16:40 | 4:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus B | 2023-12-03 10:20 | 2023-12-03 16:17 | 5:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2023-12-02 12:17 | 2023-12-02 16:20 | 4:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-12-03 10:12 | 2023-12-03 16:34 | 6:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-B | 2023-12-10 12:14 | 2023-12-10 16:00 | 3:46 | D/W | T-4 Change work. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-12-28 07:04 | 2023-12-28 07:56 | 0:52 | S/O | GT-2 Transformer 132KV side R-phase CT high temperature maintenance. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Aux. X-former-2 HT | 2023-12-01 07:08 | 2023-12-01 12:45 | 5:37 | S/O | Red hot maintenance and 33kv bus clump change | 130 | 730.1667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Main bus | 2023-12-08 11:41 | 2023-12-08 16:45 | 5:04 | S/O | Annual maintenance work purpose. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Reserve bus | 2023-12-02 10:49 | 2023-12-02 15:10 | 4:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2023-12-01 07:06 | 2023-12-01 12:32 | 5:26 | S/O | Red hot maintenance and 33KV bus clump change | 130 | 706.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2023-12-09 07:52 | 2023-12-09 18:43 | 10:51 | S/O | Annual maintenance and 33 KV bushing to bus loop changing | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-12-01 07:06 | 2023-12-01 12:34 | 5:28 | S/O | Red hot maintenance and 33KV bus clump change | 130 | 710.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-12-05 07:12 | 2023-12-05 16:51 | 9:39 | S/O | Annual maintenance and LA changing work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-12-06 08:33 | 2023-12-06 08:33 | 0:00 | S/O | Shutdown taken for annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2023-12-10 10:14 | 2023-12-10 13:40 | 3:26 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 HT | 2023-12-06 15:28 | 2023-12-06 16:48 | 1:20 | S/O | Relay Test | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 HT | 2023-12-07 09:56 | 2023-12-07 12:06 | 2:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 HT | 2023-12-06 08:49 | 2023-12-06 15:10 | 6:21 | S/O | RTS and SPMD | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-12-19 08:30 | 2023-12-30 16:58 | 272:28 | S/O | Oil centrifuging work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | BUS-B | 2023-12-23 10:33 | 2023-12-23 11:21 | 0:48 | S/O | 132 kV B-Bus Y-phase DS clamp maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2023-12-23 12:00 | 2023-12-23 12:57 | 0:57 | S/O | 132 kv Ashu-2 Ckt A-Bus D/S miantance work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-12-23 10:19 | 2023-12-23 11:31 | 1:12 | S/O | 132 kV B-Bus Y-phase DS clamp maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-12-10 08:57 | 2023-12-10 17:20 | 8:23 | S/O | Maintenance work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-12-09 09:03 | 2023-12-09 16:23 | 7:20 | S/O | Maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-12-11 09:20 | 2023-12-11 17:31 | 8:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-12-12 09:05 | 2023-12-12 14:27 | 5:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2023-12-13 09:10 | 2023-12-13 15:06 | 5:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2023-12-30 08:17 | 2023-12-30 13:19 | 5:02 | S/O | None | 50 | 251.6667 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2023-12-17 09:26 | 2023-12-17 15:22 | 5:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2023-12-18 09:18 | 2023-12-18 16:09 | 6:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2023-12-30 08:19 | 2023-12-30 13:20 | 5:01 | S/O | None | 50 | 250.8333 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2023-12-30 08:21 | 2023-12-30 15:36 | 7:15 | S/O | None | 50 | 362.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-12-03 07:15 | 2023-12-03 16:58 | 9:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-12-04 06:58 | 2023-12-04 17:37 | 10:39 | S/O | Maintenance work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-12-05 07:39 | 2023-12-05 16:18 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-12-06 08:53 | 2023-12-06 17:30 | 8:37 | S/O | à¦¬à¦¾à§Žà¦¸à¦°à¦¿à¦• à¦¸à¦‚à¦°à¦•à§à¦·à¦£ | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-12-03 07:14 | 2023-12-03 07:14 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-12-09 08:29 | 2023-12-09 15:03 | 6:34 | S/O | Pbs side Maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-12-10 14:17 | 2023-12-11 19:02 | 28:45 | D/W | Project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-12-02 09:34 | 2023-12-02 16:07 | 6:33 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-12-04 09:37 | 2023-12-04 19:14 | 9:37 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-12-06 09:25 | 2023-12-06 17:55 | 8:30 | S/O | Transformer-1, A/M work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-12-05 08:49 | 2023-12-05 19:56 | 11:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 HT | 2023-12-09 10:59 | 2023-12-09 16:48 | 5:49 | S/O | T-2 Transformer Annual Maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 HT | 2023-12-11 09:40 | 2023-12-11 15:48 | 6:08 | S/O | Annual Maintenance Work . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 LT | 2023-12-10 10:34 | 2023-12-10 17:04 | 6:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 HT | 2023-12-18 09:35 | 2023-12-18 14:07 | 4:32 | S/O | Annual maintenance Work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | T-2 Bus | 2023-12-01 07:40 | 2023-12-01 10:12 | 2:32 | S/O | A/M | 45 | 114 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-12-18 09:46 | 2023-12-18 17:50 | 8:04 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-12-19 09:25 | 2023-12-19 16:15 | 6:50 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-12-17 09:35 | 2023-12-17 16:56 | 7:21 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-12-23 10:57 | 2023-12-23 16:25 | 5:28 | S/O | Annual maintenance works. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-12-24 09:58 | 2023-12-24 16:40 | 6:42 | S/O | Annual maintenance works | 0 | 0 | No interruption
Netrakona 132/33kV Grid Sub-Station | Transformer-1 (415T) HT | 2023-12-02 09:21 | 2023-12-02 11:50 | 2:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2023-12-12 10:15 | 2023-12-12 13:11 | 2:56 | S/O | Maintenance work of L-31 & L-32 feeder of DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2023-12-14 12:30 | 2023-12-14 13:33 | 1:03 | S/O | Maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2023-12-27 10:15 | 2023-12-27 15:12 | 4:57 | S/O | Maintenance of L-31 BUS feeder by DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2023-12-28 10:33 | 2023-12-28 16:29 | 5:56 | S/O | annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2023-12-30 10:03 | 2023-12-30 16:15 | 6:12 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2023-12-21 11:12 | 2023-12-21 13:47 | 2:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2023-12-02 09:59 | 2023-12-02 16:57 | 6:58 | S/O | annual maintenance of T-1 Transformer | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2023-12-15 08:53 | 2023-12-15 16:54 | 8:01 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2023-12-30 10:08 | 2023-12-30 13:55 | 3:47 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 LT | 2023-12-03 11:04 | 2023-12-03 18:22 | 7:18 | S/O | Maintenance work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2023-12-13 10:01 | 2023-12-13 16:58 | 6:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2023-12-14 09:31 | 2023-12-14 16:32 | 7:01 | S/O | Annual maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-12-26 12:26 | 2023-12-26 16:51 | 4:25 | S/O | Metering rectification work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 HT | 2023-12-04 10:17 | 2023-12-04 16:29 | 6:12 | S/O | Due to Busbar protection testing of ATR-01 | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2023-12-06 10:58 | 2023-12-06 17:07 | 6:09 | D/W | Busbar testing | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 1 HT | 2023-12-04 10:17 | 2023-12-04 17:33 | 7:16 | S/O | Due to busbar protection testing of ATR-01 | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 230 kV Bus-1 | 2023-12-02 10:10 | 2023-12-02 16:40 | 6:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2023-12-01 05:37 | 2023-12-01 07:04 | 1:27 | S/O | Emergency maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2023-12-03 09:35 | 2023-12-03 16:27 | 6:52 | S/O | Annual maintenance work. | 10 | 68.6667 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2023-12-04 09:10 | 2023-12-04 16:20 | 7:10 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2023-12-22 09:25 | 2023-12-22 09:25 | 0:00 | D/W | DFDR work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 LT | 2023-12-22 09:24 | 2023-12-22 09:24 | 0:00 | D/W | DFDR work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2023-12-15 09:40 | 2023-12-15 21:23 | 11:43 | D/W | DFDR COMMISSIONING WORK | 0 | 0 | No interruption
|  |  | Total : | 1223:22 |  | Unserved Energy: |  | 3194.8333
Dhaka (South) Grid Circle : | [11 empty] | 39.3333
Bhulta 400/230kV Grid Sub-Station | 230kV Bus-01 | 2023-12-18 09:32 | 2023-12-18 16:09 | 6:37 | S/O | Annual Maintannce Work of 230 kV Main Bus -01 (A&B Section) | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 230kV Bus-02 | 2023-12-20 09:35 | 2023-12-20 16:40 | 7:05 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 400kV Bus-1 | 2023-12-28 09:42 | 2023-12-28 16:00 | 6:18 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | 400kV Bus-2 | 2023-12-30 09:48 | 2023-12-30 15:48 | 6:00 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-01 HT | 2023-12-24 10:15 | 2023-12-24 16:54 | 6:39 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-01 HT | 2023-12-26 08:52 | 2023-12-26 17:13 | 8:21 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-01 LT | 2023-12-23 11:11 | 2023-12-23 16:15 | 5:04 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Aux. Transformer HT | 2023-12-03 08:36 | 2023-12-03 15:55 | 7:19 | S/O | annual maintenance | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | MT-2 LT | 2023-12-03 08:35 | 2023-12-03 16:05 | 7:30 | S/O | MT-2 annual maintenance | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2023-12-09 14:10 | 2023-12-09 16:32 | 2:22 | S/O | Red hot | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 33kv Reserve Bus | 2023-12-09 14:20 | 2023-12-09 16:34 | 2:14 | S/O | Red hot | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-12-03 07:20 | 2023-12-03 17:12 | 9:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-12-04 07:33 | 2023-12-04 18:18 | 10:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-12-05 07:12 | 2023-12-05 19:55 | 12:43 | S/O | annual maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2023-12-06 10:36 | 2023-12-06 10:36 | 0:00 | S/O | Oil centrifuge of Y phase. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 LT | 2023-12-06 10:36 | 2023-12-06 10:36 | 0:00 | S/O | Oil centrifuge of Y phase. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-1 | 2023-12-20 07:41 | 2023-12-20 11:48 | 4:07 | S/O | Annual maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 HT | 2023-12-03 07:17 | 2023-12-03 15:17 | 8:00 | S/O | Annual maientence work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Earthing Trafo-2 LT | 2023-12-03 07:15 | 2023-12-03 15:28 | 8:13 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2023-12-22 07:29 | 2023-12-22 12:11 | 4:42 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2023-12-29 08:26 | 2023-12-29 10:44 | 2:18 | S/O | Annual maintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2023-12-15 07:35 | 2023-12-15 09:52 | 2:17 | S/O | Annual Maintenance . | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2023-12-23 08:16 | 2023-12-23 12:23 | 4:07 | S/O | Yearly Maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2023-12-29 11:11 | 2023-12-29 13:26 | 2:15 | S/O | maintenance work purpose for PBS | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Main Bus | 2023-12-23 10:00 | 2023-12-23 15:36 | 5:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Reserve Bus | 2023-12-26 10:58 | 2023-12-26 16:40 | 5:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-1 HT | 2023-12-22 10:24 | 2023-12-22 18:28 | 8:04 | S/O | Annual Maintenance schedule by DPDC | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-1 HT | 2023-12-30 11:20 | 2023-12-30 18:02 | 6:42 | S/O | GT-1 Protection relay Test. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-2 HT | 2023-12-29 10:04 | 2023-12-29 16:11 | 6:07 | S/O | Annual maintenance schedule by DPDC. | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132/33 kV GT-2 HT | 2023-12-01 09:35 | 2023-12-01 18:03 | 8:28 | S/O | Scheduled winter maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-1 LT | 2023-12-18 09:23 | 2023-12-18 15:12 | 5:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-2 LT | 2023-12-20 09:09 | 2023-12-20 20:51 | 11:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-3 LT | 2023-12-21 09:33 | 2023-12-21 18:50 | 9:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Main Bus | 2023-12-18 10:38 | 2023-12-18 11:16 | 0:38 | S/O | Annual Maintenance( GT-01 Main bus isolator maintenance) | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Main Bus | 2023-12-20 09:17 | 2023-12-20 10:30 | 1:13 | S/O | GT-2 Main Bus Isolator Maintenance (Annual Maintenance) | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Main Bus | 2023-12-21 09:42 | 2023-12-21 11:27 | 1:45 | S/O | GT-03 Main Bus Isolator Maintenance (Annual Maintenance) | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Main Bus | 2023-12-26 09:25 | 2023-12-26 11:34 | 2:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Reserve Bus | 2023-12-18 09:53 | 2023-12-18 10:30 | 0:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Reserve Bus | 2023-12-20 10:38 | 2023-12-20 12:31 | 1:53 | S/O | GT-2 Reserve Bus Isolator Maintenance (Annual Maintenance) | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Reserve Bus | 2023-12-21 11:39 | 2023-12-21 18:16 | 6:37 | S/O | GT-03 Reserve Bus Isolator Maintenance(Annual Maintenance) | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-12-08 07:34 | 2023-12-08 12:06 | 4:32 | S/O | PBS Annual Maintenance | 46 | 208.5333 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-12-08 07:34 | 2023-12-08 12:10 | 4:36 | S/O | PBS Annual Maintenance | 46 | 211.6 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | 132 kV Main Bus-1 | 2023-12-21 07:35 | 2023-12-21 10:57 | 3:22 | S/O | Tr-2 Bus Ds -1 Maintenance Work. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 LT | 2023-12-21 07:25 | 2023-12-21 09:48 | 2:23 | S/O | Tr-2 Bus Ds -1 Maintenance Work. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-12-20 09:41 | 2023-12-20 16:15 | 6:34 | S/O | Purpose of Tr-3 Annual Maintenance . | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-12-10 07:33 | 2023-12-10 10:23 | 2:50 | S/O | S/D due to 33Kv bus sec-02 maintenance taken by PBS | 10 | 28.3333 | Power interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2023-12-19 14:30 | 2023-12-19 17:14 | 2:44 | D/W | Project work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2023-12-08 14:05 | 2023-12-08 19:23 | 5:18 | D/W | Shoutdown for testing existing Auto tx-02(Before Relesed) | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2023-12-15 06:16 | 2023-12-15 20:32 | 14:16 | S/O | Removing old 1-ph auto TX by Project. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Aux Transformer-03 HT | 2023-12-02 07:27 | 2023-12-02 22:11 | 14:44 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo HT | 2023-12-02 07:04 | 2023-12-03 08:52 | 25:48 | S/O | Annual maintenance. | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132/33 kV GT-1 HT | 2023-12-22 10:10 | 2023-12-22 18:21 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2023-12-01 06:51 | 2023-12-01 12:29 | 5:38 | S/O | TAN DELTA TEST & MAINTENANCE WORK | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 230kV BUS A | 2023-12-17 09:26 | 2023-12-17 09:26 | 0:00 | S/O | Annual maintence | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 230kV BUS B | 2023-12-19 09:27 | 2023-12-19 14:02 | 4:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 HT | 2023-12-11 09:32 | 2023-12-11 15:07 | 5:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2023-12-13 09:45 | 2023-12-13 15:08 | 5:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS A | 2023-12-24 08:50 | 2023-12-24 11:15 | 2:25 | S/O | Tasnim chemical Bay extension work and pre-commissioning work going on. For this purpose Bus-A shutdown needed. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2023-12-24 11:30 | 2023-12-24 17:16 | 5:46 | S/O | Tasnim chemical Bay extension work and pre-commissioning work going on. For this purpose Bus-B shutdown needed. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 LT | 2023-12-06 08:43 | 2023-12-06 13:55 | 5:12 | S/O | 33 kV bus-1 annual maintenance by PBS. | 18 | 93.6 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 LT | 2023-12-09 08:11 | 2023-12-09 14:01 | 5:50 | S/O | Annual Maintenance by Munshigonj pbs. | 9 | 52.5 | Power interruption
Ullon 132/33kV Grid Sub-Station | GT-1 HT | 2023-12-27 09:11 | 2023-12-27 09:11 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Uttara 132/33kV Grid Sub-Station | GT-01 LT | 2023-12-10 09:20 | 2023-12-10 09:20 | 0:00 | S/O | GT-2 Shutdown due to Annual maintenance | 0 | 0 | No interruption
Uttara 132/33kV Grid Sub-Station | GT-02 HT | 2023-12-10 09:21 | 2023-12-10 09:21 | 0:00 | S/O | Annual maintenance | 0 | 0 | No interruption
UttaraNew 132/33kV Grid Sub-Station | GT-01 HT | 2023-12-07 09:44 | 2023-12-07 09:44 | 0:00 | S/O | Annual maintenance | 0 | 0 | No interruption
UttaraNew 132/33kV Grid Sub-Station | GT-02 HT | 2023-12-17 09:19 | 2023-12-17 14:31 | 5:12 | S/O | Due to Annual maintenance of GT-2 X/Former | 0 | 0 | No interruption
|  |  | Total : | 358:01 |  | Unserved Energy: |  | 594.5667
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | 230/33 kV Transformer-1 (125/140 MVA) HT | 2023-12-25 09:59 | 2023-12-25 09:59 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption | 14:20
BSRM 230/33kV Grid Sub-Station | 230/33 kV Transformer-1 (125/140 MVA) LT | 2023-12-25 09:57 | 2023-12-25 09:57 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | T-3 (422T) HT | 2023-12-02 08:09 | 2023-12-02 15:04 | 6:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-12-03 08:56 | 2023-12-03 14:05 | 5:09 | S/O | Implant oil in transformer conservator. | 15 | 77.25 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2023-12-02 09:39 | 2023-12-02 16:51 | 7:12 | S/O | Annual maintenance work | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Main BUS | 2023-12-01 04:50 | 2023-12-01 09:31 | 4:41 | D/W | Project work. | 30 | 140.5 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Main BUS | 2023-12-28 05:50 | 2023-12-28 09:28 | 3:38 | D/W | G2G T-01 Tx lbus oop connection | 29 | 105.3667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2023-12-01 04:48 | 2023-12-30 14:40 | 705:52 | D/W | Project work. | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2023-12-14 09:47 | 2023-12-15 14:29 | 28:42 | S/O | maintenance work | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | Transformer-01(D05) HT | 2023-12-15 14:58 | 2023-12-16 14:25 | 23:27 | S/O | maintenance | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 132 kV Single Bus | 2023-12-15 06:55 | 2023-12-15 12:03 | 5:08 | S/O | annual Maintenanace | 40 | 205.3333 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | 230KV MAIN BUS-01 | 2023-12-30 09:36 | 2023-12-30 15:00 | 5:24 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | 230KV MAIN BUS-02 | 2023-12-28 10:22 | 2023-12-28 15:59 | 5:37 | S/O |  | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-01 HT | 2023-12-24 09:05 | 2023-12-24 16:50 | 7:45 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 LT | 2023-12-23 09:12 | 2023-12-23 16:32 | 7:20 | S/O |  | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-03 LT | 2023-12-27 09:22 | 2023-12-27 16:48 | 7:26 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-04 HT | 2023-12-26 09:55 | 2023-12-26 17:52 | 7:57 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-12-03 09:14 | 2023-12-03 16:45 | 7:31 | S/O | Annual maintenance | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2023-12-17 12:12 | 2023-12-17 15:53 | 3:41 | D/W | For Oil leakage removed. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) LT | 2023-12-09 07:45 | 2023-12-09 13:10 | 5:25 | S/O | annual maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) LT | 2023-12-03 07:05 | 2023-12-03 11:38 | 4:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Main Bus | 2023-12-02 06:32 | 2023-12-02 07:28 | 0:56 | S/O | Red hot maintenance work in 132 kV Rampur Ckt-2's R-phase in between 132kV main Bus to Bus isolator. | 30 | 28 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2023-12-21 09:02 | 2023-12-21 14:21 | 5:19 | S/O | For annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2023-12-14 09:30 | 2023-12-14 14:58 | 5:28 | S/O | For Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-01 | 2023-12-14 12:16 | 2023-12-19 15:05 | 122:49 | D/W | TR-1 GIS bay integration with 132kv Bus-1. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-02 | 2023-12-11 08:58 | 2023-12-14 11:59 | 75:01 | D/W | To connect new Bay of TR-1. Where TR-1 energies with ATR-1 (Sec) Bay. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2023-12-05 09:14 | 2023-12-05 20:15 | 11:01 | S/O |  | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2023-12-06 09:17 | 2023-12-06 16:22 | 7:05 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2023-12-05 09:13 | 2023-12-05 20:24 | 11:11 | S/O |  | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2023-12-06 09:15 | 2023-12-06 16:18 | 7:03 | D/W | project work | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Main Bus 02 | 2023-12-01 10:59 | 2023-12-01 14:16 | 3:17 | S/O | isolator checking | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Power Transformer TR1 (405T) HT | 2023-12-01 10:03 | 2023-12-01 15:04 | 5:01 | S/O | Maintenance (Oil refill) | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Power Transformer TR1 (405T) HT | 2023-12-09 10:05 | 2023-12-09 13:56 | 3:51 | S/O | 33kV Side Line DS(408S) fixing alignment | 0 | 0 | No interruption
|  |  | Total : | 1111:25 |  |  |  | 556.45
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | ICT-01 HT | 2023-12-10 09:13 | 2023-12-10 17:26 | 8:13 | S/O | Relay testing | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | ICT-02 HT | 2023-12-11 09:11 | 2023-12-11 18:16 | 9:05 | S/O | Relay testing | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2023-12-27 12:50 | 2023-12-27 17:59 | 5:09 | S/O | S/D taken by SPMD | 0 | 0 | No interruption | Check
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2023-12-17 12:35 | 2023-12-17 20:15 | 7:40 | S/O | Relay testing by SPMD,Cumilla. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2023-12-18 08:20 | 2023-12-18 17:55 | 9:35 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2023-12-23 07:20 | 2023-12-23 15:40 | 8:20 | S/O | 33kv bus section Tr-1& Tr-2 annual maintenance work by BPDB | 14 | 116.6667 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2023-12-09 07:40 | 2023-12-09 11:05 | 3:25 | S/O | Annual maintenance of 33 KV T3 BUS section by BPDB & Pbs | 9 | 30.75 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2023-12-17 09:37 | 2023-12-17 12:27 | 2:50 | S/O | Relay Testing by SPMD, Cumilla. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2023-12-20 08:23 | 2023-12-20 17:50 | 9:27 | S/O | Annual Maintainance | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 HT | 2023-12-21 08:48 | 2023-12-21 16:43 | 7:55 | S/O | Yearly Maintenance. | 20 | 158.3333 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2023-12-23 10:15 | 2023-12-23 14:55 | 4:40 | S/O | 33Kv Bus Maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2023-12-23 08:47 | 2023-12-23 18:02 | 9:15 | S/O | 33 Kv Bus Maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-3 HT | 2023-12-23 08:49 | 2023-12-23 18:01 | 9:12 | S/O | 33Kv Bus Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Main Bus | 2023-12-22 08:45 | 2023-12-22 17:12 | 8:27 | S/O | 132 kv bus shutdown for annual maintenance. | 88 | 743.6 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1 | 2023-12-14 07:55 | 2023-12-14 15:55 | 8:00 | S/O | For yearly maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1 | 2023-12-22 08:24 | 2023-12-22 14:51 | 6:27 | S/O | 132 kv bus shutdown for annual maintenance. | 32 | 206.4 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2023-12-17 08:02 | 2023-12-17 14:43 | 6:41 | S/O | Due to yearly maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2023-12-22 08:25 | 2023-12-22 11:30 | 3:05 | S/O | 132 kv bus shutdown for annual maintenance. | 32 | 98.6667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2023-12-22 14:53 | 2023-12-22 17:17 | 2:24 | S/O | 132 kv bus shutdown for annual maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2023-12-22 08:42 | 2023-12-22 17:18 | 8:36 | S/O | 132 kv bus shutdown for annual maintenance. | 24 | 206.4 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3-435T HT | 2023-12-19 08:12 | 2023-12-19 16:06 | 7:54 | S/O | Yearly Schedule Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2023-12-23 08:26 | 2023-12-23 14:52 | 6:26 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2023-12-04 12:53 | 2023-12-04 14:20 | 1:27 | S/O | PDB Corrective maintenance at 33KV Kaliajuri Bus DS Red hot | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2023-12-24 09:05 | 2023-12-24 14:22 | 5:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 LT | 2023-12-26 09:45 | 2023-12-26 13:28 | 3:43 | S/O |  | 0 | 0 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 HT | 2023-12-05 09:56 | 2023-12-05 16:47 | 6:51 | S/O | Yearly maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2023-12-09 09:35 | 2023-12-09 17:02 | 7:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 HT | 2023-12-11 10:06 | 2023-12-11 15:54 | 5:48 | S/O | For Annual maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 HT | 2023-12-21 10:45 | 2023-12-21 13:04 | 2:19 | S/O | PDB work on T04 33KV Bus | 0 | 0 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 LT | 2023-12-13 09:58 | 2023-12-13 16:22 | 6:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Main | 2023-12-30 08:58 | 2023-12-30 17:49 | 8:51 | S/O | Annual Maintenance work | 60 | 531 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-12-10 08:29 | 2023-12-10 16:23 | 7:54 | S/O | for annual maintenance | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-12-12 08:16 | 2023-12-12 17:02 | 8:46 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-12-14 08:16 | 2023-12-14 14:58 | 6:42 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2023-12-26 10:30 | 2023-12-26 16:52 | 6:22 | S/O | Annual maintenace | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 230 KV Bus-2 | 2023-12-21 09:18 | 2023-12-21 16:34 | 7:16 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 HT | 2023-12-27 10:02 | 2023-12-27 18:45 | 8:43 | S/O | Special Protection Scheme implementation By SPMD, Cumilla. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2023-12-28 09:33 | 2023-12-28 12:08 | 2:35 | S/O | SPS work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2023-12-26 09:53 | 2023-12-26 17:11 | 7:18 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 LT | 2023-12-28 12:10 | 2023-12-28 13:22 | 1:12 | S/O | SPS work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Bus-2 | 2023-12-29 07:17 | 2023-12-29 17:02 | 9:45 | S/O | For 132KV Bus-02 Annual Maintenance. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-12-07 06:35 | 2023-12-07 20:38 | 14:03 | S/O | 33kV VCB Replace Work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-12-10 07:30 | 2023-12-10 19:16 | 11:46 | S/O | AMS-2023-24 | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-12-12 07:40 | 2023-12-12 20:16 | 12:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Main Bus-1 | 2023-12-05 06:13 | 2023-12-05 16:39 | 10:26 | D/W |  | 9 | 93.9 | Power interruption
Kachua 132/33kV Grid Sub-Station | Main Bus-1 | 2023-12-06 06:26 | 2023-12-06 16:14 | 9:48 | D/W |  | 9 | 88.2 | Power interruption
Kachua 132/33kV Grid Sub-Station | Main Bus-2 | 2023-12-05 06:13 | 2023-12-05 16:39 | 10:26 | D/W |  | 9 | 93.9 | Power interruption
Kachua 132/33kV Grid Sub-Station | Main Bus-2 | 2023-12-06 06:27 | 2023-12-06 16:14 | 9:47 | D/W |  | 9 | 88.05 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 HT | 2023-12-05 06:28 | 2023-12-05 16:46 | 10:18 | D/W |  | 9 | 92.7 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 HT | 2023-12-06 06:34 | 2023-12-06 16:15 | 9:41 | D/W | None | 9 | 87.15 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 LT | 2023-12-07 06:06 | 2023-12-07 13:56 | 7:50 | D/W |  | 9 | 70.5 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 LT | 2023-12-13 08:17 | 2023-12-13 17:34 | 9:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | TR-2 HT | 2023-12-05 06:29 | 2023-12-05 17:01 | 10:32 | D/W |  | 9 | 94.8 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-2 HT | 2023-12-06 06:27 | 2023-12-06 16:17 | 9:50 | D/W | None | 9 | 88.5 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-2 LT | 2023-12-07 06:07 | 2023-12-07 14:20 | 8:13 | D/W |  | 9 | 73.95 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-2 LT | 2023-12-17 08:23 | 2023-12-17 19:36 | 11:13 | S/O | Annual maintenance | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 LT | 2023-12-11 08:20 | 2023-12-11 15:18 | 6:58 | S/O | Annual maintenance work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 HT | 2023-12-09 08:17 | 2023-12-09 16:16 | 7:59 | S/O | Annual Maintenance | 17 | 135.7167 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-12-29 08:19 | 2023-12-29 08:19 | 0:00 | S/O | TR-04 33KV Side CT Change work, Load flow by TR-02 & TR-06 by Parallel. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-12-19 11:36 | 2023-12-19 15:17 | 3:41 | S/O | 33 Kv CT Mesurment & Change Work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-12-29 08:16 | 2023-12-29 08:16 | 0:00 | S/O | TR-04 33KV side CT Change work. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-2 LT | 2023-12-23 07:54 | 2023-12-23 17:34 | 9:40 | S/O | PBS works. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-12-23 07:54 | 2023-12-23 17:34 | 9:40 | S/O | PBS works. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2023-12-15 07:38 | 2023-12-15 10:32 | 2:54 | S/O | work of PDB | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 LT | 2023-12-15 09:32 | 2023-12-15 10:55 | 1:23 | D/W | 33 kV bus Section Maintenance | 5 | 6.9167 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-12-15 11:13 | 2023-12-15 12:37 | 1:24 | D/W | 33 kV Bus Section Maintenance | 20 | 28 | Power interruption
|  |  | Total : | 466:51 |  | Unserved Energy: |  | 3134.1
Khulna Grid Circle : | [10 empty] | 251.2167
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-12-09 13:46 | 2023-12-09 16:59 | 3:13 | S/O | 33 kv bus annual maintenance work | 20 | 64.3333 | Power interruption |  | 113.55
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-12-09 09:08 | 2023-12-09 13:31 | 4:23 | S/O | For annual maintenance of 33 kv bus of WZPDCL | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-12-02 07:39 | 2023-12-02 09:21 | 1:42 | S/O | 33 kV source DS maintenance for Nobogram feeder by Jhalokathi PBS | 22 | 37.4 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-12-04 08:01 | 2023-12-04 15:54 | 7:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-12-05 08:26 | 2023-12-05 16:31 | 8:05 | S/O | Yearly Maintenance. | 0 | 0 | No interruption |  | 364.7667
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-12-07 08:11 | 2023-12-07 15:51 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-06 08:14 | 2023-12-06 17:01 | 8:47 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-30 08:27 | 2023-12-30 09:33 | 1:06 | S/O | High temperature maintenance | 13 | 14.3 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-12-28 09:16 | 2023-12-28 11:49 | 2:33 | D/W | 230kV SAS signal testing by SPMD, Khulna. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-28 11:55 | 2023-12-28 12:19 | 0:24 | D/W | 230kV SAS signal testing by SPMD, Khulna. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-12-28 07:45 | 2023-12-28 16:58 | 9:13 | D/W | SAS Signal Testing SPMD, Khulna | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Bus 2 | 2023-12-02 08:35 | 2023-12-02 15:27 | 6:52 | S/O | annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-12-14 10:50 | 2023-12-14 13:37 | 2:47 | S/O | Tan- delta test | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 HT | 2023-12-23 08:18 | 2023-12-23 15:48 | 7:30 | S/O | 33 kv incoming DS maintenance. | 7 | 52.5 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-12-12 08:38 | 2023-12-12 14:34 | 5:56 | S/O | Change to breaker pole transformer -2 (Blue phase) | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-12-14 13:45 | 2023-12-14 16:46 | 3:01 | S/O | Tan delta test | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-01 | 2023-12-05 09:00 | 2023-12-05 16:00 | 7:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 HT | 2023-12-27 10:47 | 2023-12-27 19:55 | 9:08 | D/W | SAS DFDR Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2023-12-26 09:27 | 2023-12-26 20:43 | 11:16 | D/W | SAS COMMISSION | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-12-21 09:53 | 2023-12-21 23:44 | 13:51 | D/W |  | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2023-12-12 07:25 | 2023-12-12 08:50 | 1:25 | S/O | 33kv Shibchar feeder B-phase source ds red hot | 12 | 17 | Power interruption
Narail 132/33kV Grid Sub-Station | 132 kV Busbar | 2023-12-15 08:29 | 2023-12-15 11:50 | 3:21 | S/O | 132 kV Bus section D.S Maintenance (R-Phase) | 14 | 46.9 | Power interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) HT | 2023-12-15 08:17 | 2023-12-15 12:05 | 3:48 | S/O | 132 kV Bus section D.S Maintenance (R-Phase) | 14 | 53.2 | Power interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-12-02 08:08 | 2023-12-02 17:10 | 9:02 | S/O | Annual maintenance work of Tr-01 and associated equipments. | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-12-03 08:12 | 2023-12-03 17:21 | 9:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-12-04 07:40 | 2023-12-04 15:18 | 7:38 | S/O | Annual Maintenance | 0 | 0 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) HT | 2023-12-15 08:21 | 2023-12-15 12:09 | 3:48 | S/O | 132 kV Bus section D.S Maintenance (R-Phase) | 14 | 53.2 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2023-12-05 08:11 | 2023-12-05 16:17 | 8:06 | S/O | Annual maintenance works of Tr-02 | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2023-12-06 07:42 | 2023-12-06 16:49 | 9:07 | S/O | Annual Maintenance. | 0 | 0 | Power interruption
Noapara 132/33kV Grid Sub-Station | BUS A | 2023-12-19 08:09 | 2023-12-19 16:07 | 7:58 | S/O | Jack Bus Conductor Replacement | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | BUS A | 2023-12-20 08:33 | 2023-12-20 15:14 | 6:41 | S/O | Jack Bus Conductor Replacement | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | BUS A | 2023-12-28 08:32 | 2023-12-28 16:42 | 8:10 | S/O | Replace jackbus of jashore Ckt-1 | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | BUS A | 2023-12-29 08:25 | 2023-12-29 16:56 | 8:31 | S/O | Replace Jack BUA of Jashore Ckt -2 | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | Bus Section-1 | 2023-12-29 08:36 | 2023-12-29 10:40 | 2:04 | D/W |  | 17 | 35.1333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2023-12-01 10:22 | 2023-12-01 15:42 | 5:20 | S/O | 33kV DS Upgradation Work. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-4 HT | 2023-12-29 08:37 | 2023-12-29 08:37 | 0:00 | D/W | G to G Upgradation project work. (17 MW Interruption for two hours) | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-12-25 07:13 | 2023-12-25 09:17 | 2:04 | S/O | 33 kv bus side(REB-3 ) Red Hot Point Maintenance. | 17 | 35.1333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-12-29 08:36 | 2023-12-29 08:36 | 0:00 | D/W | G to G Upgradation project work. (17 MW Interruption for two hours) | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2023-12-03 08:01 | 2023-12-03 16:22 | 8:21 | S/O | Annual Maintenance-2023 | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2023-12-02 07:58 | 2023-12-02 15:47 | 7:49 | S/O | Annual maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2023-12-04 08:01 | 2023-12-04 15:04 | 7:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-12-04 08:57 | 2023-12-04 11:23 | 2:26 | D/W | Project work. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-2 HT | 2023-12-21 05:34 | 2023-12-21 17:28 | 11:54 | D/W | Relay Maintenance | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2023-12-26 09:31 | 2023-12-26 16:09 | 6:38 | S/O | Annual maintenance work | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2023-12-30 09:02 | 2023-12-30 15:18 | 6:16 | S/O |  | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-12-30 09:02 | 2023-12-30 15:20 | 6:18 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 275:17 |  | Unserved Energy : |  | 409.1
HVDC Grid Circle
BIPTC | 20D09C 20MVA LT | 2023-12-18 10:19 | 2023-12-18 16:22 | 6:03 | S/O | For Annual maintenance | 0 | 0 | No interruption
BIPTC | 20D10A 20MVA HT | 2023-12-19 10:30 | 2023-12-19 17:06 | 6:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | 22T01 HT | 2023-12-02 08:25 | 2023-12-06 16:12 | 103:47 | S/O | For maintenance purpose | 0 | 0 | No interruption
BIPTC | 230kV Bus-2 | 2023-12-05 11:30 | 2023-12-05 19:07 | 7:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | 400kV Bus-2 | 2023-12-04 | 2023-12-04 17:41 | 17:41 | S/O |  | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Bus-1 | 2023-12-30 12:21 | 2023-12-30 16:13 | 3:52 | D/W | Project Work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-1 LT | 2023-12-06 09:30 | 2023-12-06 18:41 | 9:11 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-2 Bank LT | 2023-12-27 08:59 | 2023-12-27 19:11 | 10:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-2 Bank LT | 2023-12-28 08:40 | 2023-12-28 17:28 | 8:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) HT | 2023-12-04 09:06 | 2023-12-04 15:16 | 6:10 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | Tr-2(413T) LT | 2023-12-21 08:45 | 2023-12-21 14:31 | 5:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T1(416T) LT | 2023-12-04 14:21 | 2023-12-04 16:54 | 2:33 | D/W | SCADA Integration with NLDC. | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) LT | 2023-12-05 10:50 | 2023-12-05 14:18 | 3:28 | D/W | SCADA Integration with NLDC. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-12-23 07:33 | 2023-12-23 17:22 | 9:49 | S/O | A/M | 18 | 176.7 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-12-24 09:17 | 2023-12-24 16:44 | 7:27 | S/O | A/M | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-12-02 07:21 | 2023-12-02 14:26 | 7:05 | S/O | 33kv wzpdcl bus maintenance | 35 | 247.9167 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2023-12-02 07:21 | 2023-12-02 14:27 | 7:06 | S/O | 33kv wzpdcl bus maintenance | 35 | 248.5 | Power interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-12-12 07:10 | 2023-12-12 11:10 | 4:00 | S/O | Maintenance purpose(Oil leakage of 33 kV Auxiliary transformer-2) | 10 | 40 | Power interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) HT | 2023-12-21 09:55 | 2023-12-21 18:56 | 9:01 | D/W | Energypac test. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2023-12-07 08:47 | 2023-12-07 09:12 | 0:25 | S/O | Power shifting from main bus to transfer bus using bus coupler BKR (903B) | 20 | 8.3333 | Power interruption
Ruppur 132/11kV Grid Sub-Station | 132kv BUS-2 | 2023-12-19 09:14 | 2023-12-19 09:14 | 0:00 | S/O | Annual maintenance of 132kv Bus-2 | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2023-12-11 07:33 | 2023-12-11 16:47 | 9:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-12-05 07:42 | 2023-12-07 14:29 | 54:47 | S/O | Annual maintenance and oil centrifuge | 0 | 0 | No interruption
|  |  | Total : | 300:38 |  | Unserved Energy : |  | 721.45
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Bus-2 | 2023-12-03 09:00 | 2023-12-03 14:13 | 5:13 | S/O | Annual maintenance. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) LT | 2023-12-12 10:05 | 2023-12-12 11:35 | 1:30 | S/O | Oil sample collection | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) LT | 2023-12-17 12:28 | 2023-12-18 15:45 | 27:17 | S/O | 132 KV CT change. Clearance from NLDC. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) LT | 2023-12-12 11:37 | 2023-12-12 12:21 | 0:44 | S/O | Oil sample collection | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus A | 2023-12-11 09:25 | 2023-12-11 16:03 | 6:38 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2023-12-13 08:52 | 2023-12-13 15:58 | 7:06 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2023-12-19 10:44 | 2023-12-19 15:37 | 4:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2023-12-21 09:26 | 2023-12-21 15:48 | 6:22 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2023-12-27 10:49 | 2023-12-27 16:20 | 5:31 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T LT | 2023-12-19 09:32 | 2023-12-19 16:10 | 6:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T LT | 2023-12-20 08:46 | 2023-12-20 16:10 | 7:24 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2023-12-21 08:45 | 2023-12-21 16:16 | 7:31 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 2023-12-11 09:17 | 2023-12-11 15:58 | 6:41 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 2023-12-12 08:51 | 2023-12-12 16:39 | 7:48 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T HT | 2023-12-14 08:46 | 2023-12-14 15:49 | 7:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T LT | 2023-12-13 08:47 | 2023-12-13 16:05 | 7:18 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T LT | 2023-12-27 10:45 | 2023-12-27 16:04 | 5:19 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T LT | 2023-12-28 10:20 | 2023-12-28 15:26 | 5:06 | S/O | Anual maintainance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-12-21 09:45 | 2023-12-21 16:02 | 6:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-12-23 09:38 | 2023-12-23 18:02 | 8:24 | S/O |  | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-12-24 08:37 | 2023-12-24 15:36 | 6:59 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-12-27 09:50 | 2023-12-27 15:14 | 5:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-12-17 08:30 | 2023-12-17 14:29 | 5:59 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-12-18 09:30 | 2023-12-18 14:29 | 4:59 | S/O | Annual Maintenance . | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-12-20 09:20 | 2023-12-20 17:27 | 8:07 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-12-21 08:40 | 2023-12-21 14:24 | 5:44 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-12-19 09:03 | 2023-12-19 11:58 | 2:55 | S/O | tan delta test | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-12-29 08:34 | 2023-12-29 12:01 | 3:27 | S/O | Bus cuplar maintanance | 35 | 120.75 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-12-24 08:19 | 2023-12-24 09:38 | 1:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-12-18 15:24 | 2023-12-18 17:24 | 2:00 | S/O | Tan Delta Test | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-12-29 08:34 | 2023-12-29 12:22 | 3:48 | S/O | Bus cuplar maintanance | 35 | 133 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-12-30 08:20 | 2023-12-30 14:52 | 6:32 | S/O | annual maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 1 | 2023-12-10 13:22 | 2023-12-10 16:50 | 3:28 | S/O | Annual Maintenance ( T#01 LT Bus DS Loop Change) | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 1 | 2023-12-12 14:51 | 2023-12-12 17:24 | 2:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-12-10 08:30 | 2023-12-10 16:54 | 8:24 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-12-11 08:22 | 2023-12-11 15:58 | 7:36 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-12-18 07:38 | 2023-12-18 12:13 | 4:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2023-12-12 08:13 | 2023-12-12 17:25 | 9:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2023-12-13 08:44 | 2023-12-13 13:43 | 4:59 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2023-12-17 12:27 | 2023-12-17 16:20 | 3:53 | S/O | Annual maintenance(Tan dalta test) | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-03 HT | 2023-12-14 08:24 | 2023-12-14 16:15 | 7:51 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-03 HT | 2023-12-15 08:30 | 2023-12-15 10:48 | 2:18 | S/O |  | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-03 HT | 2023-12-17 08:29 | 2023-12-17 12:20 | 3:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Main Bus | 2023-12-01 07:20 | 2023-12-01 12:49 | 5:29 | S/O | Annual maintenance. | 35 | 191.9167 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-12-06 07:59 | 2023-12-06 16:10 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-12-07 09:18 | 2023-12-07 16:16 | 6:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-12-09 08:16 | 2023-12-09 15:28 | 7:12 | S/O | For Annual maintenence | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-12-10 08:15 | 2023-12-10 17:40 | 9:25 | S/O | Shedule shut down | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-12-11 08:08 | 2023-12-11 16:50 | 8:42 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-12-12 08:14 | 2023-12-12 14:51 | 6:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-12-13 08:16 | 2023-12-13 09:28 | 1:12 | S/O |  | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2023-12-13 08:16 | 2023-12-13 16:15 | 7:59 | S/O | annual maintenence | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2023-12-14 08:26 | 2023-12-14 18:37 | 10:11 | S/O | Annual maintenance. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-1 (407 T) HT | 2023-12-18 08:07 | 2023-12-18 16:14 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-1 (407 T) LT | 2023-12-25 07:40 | 2023-12-25 11:04 | 3:24 | S/O | Tan delta test. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-2 (417 T) HT | 2023-12-21 08:17 | 2023-12-21 16:29 | 8:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-2 (417 T) LT | 2023-12-23 09:45 | 2023-12-23 13:10 | 3:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-2 (417 T) LT | 2023-12-25 11:11 | 2023-12-25 14:24 | 3:13 | S/O | ten delta test | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-3 (427 T) LT | 2023-12-24 08:40 | 2023-12-24 16:24 | 7:44 | S/O | Annual Maintenance for T-3 Transformer (427T) | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-3 (427 T) LT | 2023-12-25 08:51 | 2023-12-25 12:24 | 3:33 | S/O | tan delta test | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) LT | 2023-12-25 12:30 | 2023-12-25 16:53 | 4:23 | S/O | ten delta test | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) LT | 2023-12-27 09:45 | 2023-12-27 16:47 | 7:02 | S/O | annual meaintence | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) HT | 2023-12-04 09:24 | 2023-12-04 16:36 | 7:12 | S/O | annual maintenance | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) HT | 2023-12-05 08:52 | 2023-12-05 15:16 | 6:24 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) HT | 2023-12-09 09:18 | 2023-12-09 15:40 | 6:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) LT | 2023-12-10 09:27 | 2023-12-10 14:12 | 4:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-12-02 08:14 | 2023-12-02 17:16 | 9:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-12-06 11:43 | 2023-12-06 17:12 | 5:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-12-24 11:41 | 2023-12-24 14:37 | 2:56 | S/O | Tan-Delta Test | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 HT | 2023-12-05 08:17 | 2023-12-05 16:06 | 7:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2023-12-24 14:38 | 2023-12-24 17:23 | 2:45 | S/O | Tan-Delta Test | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Main Bus | 2023-12-02 07:15 | 2023-12-02 08:56 | 1:41 | S/O | 132 Kv Bogura -2 D/S change (main Bus side). | 45 | 75.75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-12-08 07:30 | 2023-12-08 12:25 | 4:55 | S/O | T-1,T-2,T-3 33 Kv Main Bus S/D (Annual Maintanance work held By Nesco). | 50 | 245.8333 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 HT | 2023-12-02 07:06 | 2023-12-03 17:15 | 34:09 | S/O | Annual maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-12-08 07:30 | 2023-12-08 11:50 | 4:20 | S/O | T-1,T-2,T-3 33 Kv Main Bus S/D (Annual Maintanance work held By Nesco). | 50 | 216.6667 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2023-12-05 09:24 | 2023-12-05 15:08 | 5:44 | S/O | annual maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-12-04 08:15 | 2023-12-04 17:24 | 9:09 | S/O | annual maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-12-08 07:30 | 2023-12-08 11:24 | 3:54 | S/O | T-1,T-2,T-3 33 Kv Main Bus S/D (Annual Maintanance work held By Nesco). | 50 | 195 | Power interruption
Natore 132/33kV Grid Sub-Station | 132 KV MAIN BUS | 2023-12-08 06:20 | 2023-12-08 10:20 | 4:00 | S/O | annual maintenance | 51 | 204 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 2023-12-17 07:40 | 2023-12-17 15:40 | 8:00 | S/O | Yearly maintanance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 2023-12-18 08:40 | 2023-12-18 15:20 | 6:40 | S/O | annual maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-12-08 06:16 | 2023-12-08 11:18 | 5:02 | S/O | bus maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) HT | 2023-12-19 08:29 | 2023-12-19 16:45 | 8:16 | S/O | Yearly maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2023-12-08 06:16 | 2023-12-08 11:22 | 5:06 | S/O | bus maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2023-12-20 08:20 | 2023-12-20 16:47 | 8:27 | S/O | annual maintenacr | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2023-12-08 06:17 | 2023-12-08 10:34 | 4:17 | S/O | bus maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) HT | 2023-12-23 10:37 | 2023-12-23 17:31 | 6:54 | S/O | annual maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) LT | 2023-12-08 06:17 | 2023-12-08 10:32 | 4:15 | S/O | bus maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) LT | 2023-12-21 08:18 | 2023-12-21 16:06 | 7:48 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-1(407T) HT | 2023-12-27 10:20 | 2023-12-27 13:20 | 3:00 | S/O | SCADA Integration Work. | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-2(417T) LT | 2023-12-28 10:13 | 2023-12-28 13:27 | 3:14 | D/W | SCADA Intrigation work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Single Bus | 2023-12-23 06:42 | 2023-12-23 12:29 | 5:47 | S/O | Annual maintenance of 132 kV bus | 150 | 867.5 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-12-23 06:31 | 2023-12-23 12:30 | 5:59 | S/O | Annual maintenance of 132 kV bus | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) HT | 2023-12-23 06:31 | 2023-12-23 13:34 | 7:03 | S/O | Annual maintenance of 132 kV bus | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer HT | 2023-12-23 06:32 | 2023-12-23 12:50 | 6:18 | S/O | Annual maintenance of 132 kV bus | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 33 kV T-1 Bus | 2023-12-30 07:02 | 2023-12-30 09:22 | 2:20 | S/O | general cleaning | 10 | 23.3333 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | 33 kV T-2 Bus | 2023-12-30 07:03 | 2023-12-30 10:09 | 3:06 | S/O | general cleaning | 27 | 83.7 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | 33 kV T-3 Bus | 2023-12-30 07:04 | 2023-12-30 09:47 | 2:43 | S/O | general cleaning | 23 | 62.4833 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2023-12-07 12:49 | 2023-12-07 14:44 | 1:55 | S/O | Maintenance Work of T-1 33KV Bus. | 9 | 17.25 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2023-12-30 07:02 | 2023-12-30 09:23 | 2:21 | S/O | general cleaning | 10 | 23.5 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2023-12-07 10:13 | 2023-12-07 12:34 | 2:21 | S/O | Maintenance Work of T-33KV Bus. | 4 | 9.4 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2023-12-30 07:03 | 2023-12-30 10:09 | 3:06 | S/O | general cleaning | 27 | 83.7 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-12-07 07:29 | 2023-12-07 10:02 | 2:33 | S/O | Maintenance work of T3 33 kv BUS. | 25 | 63.75 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-12-30 07:04 | 2023-12-30 09:47 | 2:43 | S/O | general cleaning | 23 | 62.4833 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-02 (416T) HT | 2023-12-02 08:18 | 2023-12-02 17:26 | 9:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-02 (416T) HT | 2023-12-03 08:15 | 2023-12-03 15:55 | 7:40 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) HT | 2023-12-06 08:29 | 2023-12-06 17:19 | 8:50 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) HT | 2023-12-06 08:30 | 2023-12-06 17:20 | 8:50 | S/O | A/M | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Main Bus | 2023-12-13 06:17 | 2023-12-13 08:58 | 2:41 | D/W | PGNSP (G2G) has taken shutdown for T4 installation, | 60 | 161 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-12-17 08:28 | 2023-12-17 16:31 | 8:03 | S/O | Annual maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-12-18 08:30 | 2023-12-18 17:48 | 9:18 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-12-23 10:41 | 2023-12-23 13:10 | 2:29 | S/O | Tan delta test of transformer-1 | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) HT | 2023-12-23 13:14 | 2023-12-23 15:39 | 2:25 | S/O | Tan Delta test of transformer-2 | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-12-20 08:52 | 2023-12-20 17:03 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-12-21 08:29 | 2023-12-21 20:10 | 11:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) LT | 2023-12-24 08:34 | 2023-12-24 15:54 | 7:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Bus-2 | 2023-12-20 07:52 | 2023-12-20 16:03 | 8:11 | S/O | Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 712:12 |  | Unserved Energy : |  | 2841.0167
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 4447:46 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: December 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kallyanpur-02 | 2023-12-17 08:48 | 2023-12-17 16:56 | 8:08 | S/O | Annual maintenace | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-01 | 2023-12-17 11:16 | 2023-12-17 13:22 | 2:06 | S/O | Teleprotection Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-02 | 2023-12-17 13:23 | 2023-12-17 14:36 | 1:13 | S/O | Teleprotection Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2023-12-19 09:40 | 2023-12-19 12:56 | 3:16 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2023-12-20 10:51 | 2023-12-20 18:07 | 7:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2023-12-23 09:16 | 2023-12-23 12:43 | 3:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2023-12-25 08:25 | 2023-12-25 21:05 | 12:40 | S/O | SAS Integration | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2023-12-22 10:12 | 2023-12-24 15:59 | 53:47 | S/O | Ds loop cobnection | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2023-12-25 09:20 | 2023-12-25 14:28 | 5:08 | S/O | DS Change work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2023-12-26 12:13 | 2023-12-26 16:11 | 3:58 | S/O | DS change work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-02 | 2023-12-08 07:39 | 2023-12-08 14:55 | 7:16 | S/O | PT change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-02 | 2023-12-15 08:28 | 2023-12-17 15:58 | 55:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-02 | 2023-12-22 07:25 | 2023-12-22 09:54 | 2:29 | S/O | Annula maintenance | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-12-04 09:25 | 2023-12-04 16:27 | 7:02 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-12-05 09:24 | 2023-12-05 15:10 | 5:46 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 01 | 2023-12-02 12:12 | 2023-12-02 15:55 | 3:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-12-03 10:04 | 2023-12-03 16:49 | 6:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2023-12-05 11:55 | 2023-12-05 11:57 | 0:02 | S/O | Work on kaliakoir end. | 100 | 3.3333 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2023-12-05 13:45 | 2023-12-05 15:52 | 2:07 | D/W | Work at Kaliakoir end. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2023-12-05 11:55 | 2023-12-05 11:57 | 0:02 | D/W | Work at Kaliakoir end. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2023-12-05 12:03 | 2023-12-05 13:44 | 1:41 | D/W | Work at Kaliakoir end. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-02 | 2023-12-02 09:32 | 2023-12-02 16:34 | 7:02 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-02 | 2023-12-03 09:33 | 2023-12-03 15:49 | 6:16 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | 132KV UMPL Ckt-02 | 2023-12-04 09:20 | 2023-12-04 15:56 | 6:36 | S/O | Annual maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-12-10 11:44 | 2023-12-10 14:45 | 3:01 | D/W | T-4 Chang work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2023-12-13 14:20 | 2023-12-13 16:55 | 2:35 | S/O | SF6 Gass leakage maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2023-12-06 06:58 | 2023-12-06 17:31 | 10:33 | S/O | OPGW change work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2023-12-08 10:52 | 2023-12-08 18:25 | 7:33 | S/O | Shutdown taken by TRTUD due to OPGW changing work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-2 | 2023-12-06 06:58 | 2023-12-08 18:26 | 59:28 | S/O | OPGW change work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-12-03 07:45 | 2023-12-03 14:08 | 6:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-12-08 11:13 | 2023-12-08 17:34 | 6:21 | S/O | Dead line checking. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-2 | 2023-12-05 07:24 | 2023-12-05 16:02 | 8:38 | S/O | Due to maint.work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2023-12-05 09:53 | 2023-12-05 11:49 | 1:56 | S/O | relay test by SPMD | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2023-12-10 07:45 | 2023-12-10 16:54 | 9:09 | S/O | Annual Maintenance and Dead Line Checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2023-12-11 08:37 | 2023-12-11 17:28 | 8:51 | S/O | Annual Maintenance CB open at 08:37 ES Close at 09:17 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2023-12-12 07:44 | 2023-12-12 17:13 | 9:29 | S/O | Annual maintenance and Dead line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2023-12-13 08:10 | 2023-12-13 17:09 | 8:59 | S/O | Annual Maintenance and Dead line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2023-12-24 08:18 | 2023-12-24 17:00 | 8:42 | S/O | annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2023-12-26 08:29 | 2023-12-26 16:26 | 7:57 | S/O | annual maintenance & Dead Line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2023-12-17 08:24 | 2023-12-17 17:34 | 9:10 | S/O | Annual Maintenance and Dead Line Checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2023-12-18 08:48 | 2023-12-18 16:59 | 8:11 | S/O | Annual Maintenance & Dead line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2023-12-19 07:30 | 2023-12-19 17:14 | 9:44 | S/O | annual maintenance and dead line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2023-12-21 08:36 | 2023-12-21 15:58 | 7:22 | S/O | Annual Maintainance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Kabirpur-2 | 2023-12-05 13:13 | 2023-12-05 16:26 | 3:13 | S/O | Relay Test by SPMD. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Summit/Kodda PS | 2023-12-10 09:17 | 2023-12-10 16:54 | 7:37 | S/O | Annual Maintenance and dead line checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Summit/Kodda PS | 2023-12-11 08:42 | 2023-12-11 17:28 | 8:46 | S/O | Annual Maintenance CB open at 08:42 ES Close at 09:19 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Summit/Kodda PS | 2023-12-12 08:47 | 2023-12-12 18:26 | 9:39 | S/O | Annual maintenance and Dead line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-2 | 2023-12-30 08:58 | 2023-12-30 15:55 | 6:57 | S/O | Annual Maintenance and dead line check. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tongi-2 | 2023-12-04 11:11 | 2023-12-04 12:17 | 1:06 | S/O | Relay Testing By SPMD | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2023-12-13 09:16 | 2023-12-13 17:30 | 8:14 | S/O | Due to Aminbazar grid Annual Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2023-12-14 10:45 | 2023-12-14 16:13 | 5:28 | S/O | Due to Annual Maintenance of Aminbazar Grid. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2023-12-18 08:29 | 2023-12-18 17:05 | 8:36 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-12-23 12:14 | 2023-12-23 13:16 | 1:02 | S/O | 132 kv Ashu-2 Ckt A-Bus D/S miantance work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | RPCL 100 MW PS | 2023-12-30 09:45 | 2023-12-30 13:29 | 3:44 | S/O | Due to maint.work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-12-02 09:35 | 2023-12-02 16:02 | 6:27 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-12-29 07:48 | 2023-12-29 16:12 | 8:24 | D/W | Rup pur project work. | 20 | 168 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-12-03 07:15 | 2023-12-04 17:37 | 34:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-12-06 08:53 | 2023-12-06 16:48 | 7:55 | S/O | à¦¬à¦¾à§Žà¦¸à¦°à¦¿à¦• à¦¸à¦‚à¦°à¦•à§à¦·à¦£ | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-12-09 09:03 | 2023-12-09 15:00 | 5:57 | S/O | Pbs side Maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-12-29 07:24 | 2023-12-29 15:52 | 8:28 | D/W | Rup pur project work. | 20 | 169.3333 | Power interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2023-12-21 09:23 | 2023-12-21 18:20 | 8:57 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-12-28 10:13 | 2023-12-28 17:32 | 7:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-12-30 09:26 | 2023-12-30 17:47 | 8:21 | S/O | Annual Maintenance Dead Line Caking Work . | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakair-ckt-2A(E08) | 2023-12-30 08:59 | 2023-12-30 15:56 | 6:57 | S/O | Annual Maintenance By Tangail Grid, Direction or S/D taken by NLDC. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakoir ckt-2B(E-09) | 2023-12-30 08:59 | 2023-12-30 15:56 | 6:57 | S/O | Annual maintenance By Tangail Grid, direction or S/D taken by NLDC. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2A(E04) | 2023-12-29 08:41 | 2023-12-29 15:49 | 7:08 | S/O | Anual Maintenance | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2B(E03) | 2023-12-29 08:41 | 2023-12-29 15:49 | 7:08 | S/O | Anual Maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2023-12-24 10:45 | 2023-12-24 12:55 | 2:10 | S/O | Maintenance works at Bha end | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-2 | 2023-12-02 09:22 | 2023-12-02 16:26 | 7:04 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-2 | 2023-12-03 09:20 | 2023-12-03 14:41 | 5:21 | S/O | A/M | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2023-12-17 11:52 | 2023-12-17 16:45 | 4:53 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2023-12-18 12:22 | 2023-12-18 15:14 | 2:52 | S/O | annual Maintenance Work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2023-12-19 11:40 | 2023-12-19 16:44 | 5:04 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2023-12-20 10:15 | 2023-12-20 12:45 | 2:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 2023-12-04 08:36 | 2023-12-04 17:15 | 8:39 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 2023-12-05 07:46 | 2023-12-05 15:58 | 8:12 | S/O | Due to NLDC instructions | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 2023-12-06 09:10 | 2023-12-06 16:29 | 7:19 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2023-12-01 09:08 | 2023-12-01 16:32 | 7:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2023-12-02 09:00 | 2023-12-02 17:05 | 8:05 | S/O | Line annual maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2023-12-03 08:26 | 2023-12-03 17:23 | 8:57 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2023-12-20 08:30 | 2023-12-20 17:27 | 8:57 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2023-12-28 09:19 | 2023-12-28 16:31 | 7:12 | S/O | Dead Line Checking | 50 | 360 | Power interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-12-29 08:40 | 2023-12-29 15:48 | 7:08 | S/O | Dead Line Checking | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-12-04 09:02 | 2023-12-04 15:39 | 6:37 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-12-05 08:59 | 2023-12-05 16:32 | 7:33 | S/O | Due to Dead line checking | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-12-06 08:55 | 2023-12-06 17:00 | 8:05 | S/O | Dead line checking | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-12-07 09:02 | 2023-12-07 15:49 | 6:47 | S/O | Dead Line Checking | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-12-09 09:01 | 2023-12-09 16:12 | 7:11 | S/O | Annual maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-12-10 09:22 | 2023-12-10 16:56 | 7:34 | S/O | Annual maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-12-11 09:12 | 2023-12-11 16:45 | 7:33 | S/O | Dead line checking | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-12-20 09:40 | 2023-12-20 17:24 | 7:44 | S/O | Instruction by NLDC | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-12-05 07:20 | 2023-12-08 13:12 | 77:52 | D/W | Shutdown for 400/230/132Kv GNDP project working (1-Month). | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-12-19 09:38 | 2023-12-19 12:18 | 2:40 | S/O | Due to maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-12-05 07:45 | 2023-12-08 13:35 | 77:50 | D/W | Shutdown for 400/240/132kv GNDP project working (1-Month) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-12-11 09:18 | 2023-12-11 11:54 | 2:36 | S/O | Shutdown taken by Basundhara End via NLDC. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2023-12-05 07:45 | 2023-12-05 07:45 | 0:00 | D/W | Shutdown for 400/230/132Kv GNDP Project Working.(1-Month). | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-12-03 11:15 | 2023-12-03 13:15 | 2:00 | S/O | DS(636s) maintenance work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2023-12-05 07:45 | 2023-12-05 07:45 | 0:00 | D/W | Shutdown for GNDP project working (1-Month) | 0 | 0 | No interruption
|  |  | Total : | 919:49 |  | Unserved Energy: |  | 700.6667
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2023-12-30 09:15 | 2023-12-30 18:31 | 9:16 | S/O | winter maintenance work | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-1 | 2023-12-02 07:47 | 2023-12-02 22:08 | 14:21 | S/O | annual maintenance | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | HPL-1 | 2023-12-11 12:21 | 2023-12-14 11:16 | 70:55 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | HPL-2 | 2023-12-11 12:22 | 2023-12-14 11:17 | 70:55 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | HPL-2 | 2023-12-17 10:11 | 2023-12-17 15:32 | 5:21 | S/O | S/D taken by HPL. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | HPL-2 | 2023-12-24 11:33 | 2023-12-24 11:33 | 0:00 | S/O | CB-842 Replacement work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2023-12-02 10:09 | 2023-12-02 14:51 | 4:42 | S/O | For Annual maintanance Work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-12-24 13:27 | 2023-12-24 17:27 | 4:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Sonargaon 1 | 2023-12-24 11:02 | 2023-12-24 17:44 | 6:42 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Sonargaon 2 | 2023-12-24 11:03 | 2023-12-24 17:44 | 6:41 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-12-24 11:30 | 2023-12-24 15:37 | 4:07 | S/O | Bay maitenance siddhirganj. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2023-12-30 09:12 | 2023-12-30 18:38 | 9:26 | S/O | Annual maintenace | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2023-12-17 07:18 | 2023-12-17 18:03 | 10:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2023-12-13 07:32 | 2023-12-13 17:27 | 9:55 | S/O | Annual maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2023-12-18 07:35 | 2023-12-18 15:36 | 8:01 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-2 | 2023-12-14 07:25 | 2023-12-14 15:57 | 8:32 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Srinagar-1 | 2023-12-27 09:07 | 2023-12-28 20:14 | 35:07 | S/O | yearly maintenance. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2023-12-26 10:40 | 2023-12-26 23:20 | 12:40 | S/O | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2023-12-27 09:52 | 2023-12-27 21:10 | 11:18 | S/O | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2023-12-28 09:06 | 2023-12-28 18:49 | 9:43 | S/O | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2023-12-02 10:07 | 2023-12-02 14:51 | 4:44 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 102 MW 132 kv Ckt | 2023-12-09 09:34 | 2023-12-09 17:07 | 7:33 | S/O | Du eto maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2023-12-06 09:23 | 2023-12-06 17:16 | 7:53 | S/O | Du eto maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2023-12-03 09:36 | 2023-12-03 15:21 | 5:45 | S/O | Annaul Maintenance work. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-1 | 2023-12-01 08:25 | 2023-12-01 14:44 | 6:19 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Rampura 1 | 2023-12-24 09:31 | 2023-12-24 13:49 | 4:18 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | Rampura 2 | 2023-12-26 09:11 | 2023-12-26 09:11 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Haripur | 2023-12-24 11:31 | 2023-12-24 17:27 | 5:56 | S/O | Haropur End Scheduled Shutdown. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | Keraniganj-1 | 2023-12-24 08:35 | 2023-12-24 15:58 | 7:23 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | Keraniganj-2 | 2023-12-26 08:47 | 2023-12-26 15:27 | 6:40 | S/O | For Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2023-12-04 09:55 | 2023-12-04 12:26 | 2:31 | S/O | Annual maintenance work at basundhara Grid. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Madertek-01 | 2023-12-13 10:31 | 2023-12-13 18:13 | 7:42 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Madertek-02 | 2023-12-17 08:38 | 2023-12-17 17:06 | 8:28 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2023-12-26 09:38 | 2023-12-26 17:43 | 8:05 | S/O | Annuai Maintenance at Mogbazar S/S | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2023-12-17 07:18 | 2023-12-17 18:00 | 10:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-12-12 11:32 | 2023-12-12 14:33 | 3:01 | S/O | OTI & WTI meter checking in unit transformer by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 1 | 2023-12-11 09:27 | 2023-12-11 15:10 | 5:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-12-13 09:43 | 2023-12-13 15:12 | 5:29 | S/O | Annuan maintenance in 230kv End | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2023-12-28 09:43 | 2023-12-28 12:43 | 3:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2023-12-30 09:22 | 2023-12-30 13:35 | 4:13 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2023-12-21 09:16 | 2023-12-21 13:58 | 4:42 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2023-12-14 09:24 | 2023-12-14 14:17 | 4:53 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2023-12-02 10:37 | 2023-12-02 14:49 | 4:12 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2023-12-13 09:04 | 2023-12-13 19:12 | 10:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-2 | 2023-12-20 09:19 | 2023-12-20 15:51 | 6:32 | S/O | Bay annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-2 | 2023-12-21 08:30 | 2023-12-21 17:05 | 8:35 | S/O | Relay change | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPML(IEL-1) | 2023-12-27 08:58 | 2023-12-27 16:09 | 7:11 | S/O | Annual maintenance purpose, Bay maintenance | 0 | 0 | No interruption
UttaraNew 132/33kV Grid Sub-Station | Mirpur | 2023-12-10 10:40 | 2023-12-10 10:40 | 0:00 | S/O | due to annual maintenance of mirpur grid | 0 | 0 | No interruption
|  |  | Total : | 474:05 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2023-12-19 07:22 | 2023-12-19 18:42 | 11:20 | D/W | ESPNER Project Work. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2023-12-20 07:07 | 2023-12-20 17:20 | 10:13 | D/W | Comilla 1no ckt phase replace to ERS for ESPNER project work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2023-12-18 06:43 | 2023-12-18 18:21 | 11:38 | D/W | T-Connection With 400kV Korerhat SS. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2023-12-26 08:50 | 2023-12-26 14:57 | 6:07 | S/O | For Annual Maintenance. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2023-12-27 08:24 | 2023-12-27 15:25 | 7:01 | S/O | For Annual Maintenance . | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2023-12-28 08:47 | 2023-12-28 15:37 | 6:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-01 | 2023-12-14 08:29 | 2023-12-14 14:42 | 6:13 | S/O | Due to maint.work | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-02 | 2023-12-18 08:29 | 2023-12-18 13:57 | 5:28 | S/O | Annual Maintanence. Dead Line Checking . | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2023-12-10 08:50 | 2023-12-10 17:04 | 8:14 | S/O | Annual Bay maintenane work | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2023-12-17 08:19 | 2023-12-17 15:28 | 7:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-12-11 06:57 | 2023-12-11 17:22 | 10:25 | D/W | Due to project work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | PHP | 2023-12-11 06:57 | 2023-12-11 17:56 | 10:59 | D/W | Due to project work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-01 | 2023-12-30 08:39 | 2023-12-30 17:25 | 8:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2023-12-02 10:30 | 2023-12-03 17:25 | 30:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-06 09:30 | 2023-12-06 17:25 | 7:55 | S/O | Annual maintenance( Dohazari side) | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-07 08:23 | 2023-12-07 17:25 | 9:02 | S/O | Annual maintenance ( Dohazari side) | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-09 09:07 | 2023-12-09 17:34 | 8:27 | S/O | Annual maintenance ( Dohazari side) | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-10 09:08 | 2023-12-10 17:17 | 8:09 | S/O | Annual maintenance( Dohazari side) | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-23 08:21 | 2023-12-23 17:07 | 8:46 | S/O | Annual maintentance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-24 08:20 | 2023-12-24 18:28 | 10:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-26 08:50 | 2023-12-26 17:31 | 8:41 | S/O | Annual maintenance. (Cox side) | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-12-27 08:59 | 2023-12-27 16:30 | 7:31 | S/O | annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 2023-12-17 09:11 | 2023-12-17 17:33 | 8:22 | S/O | Annual Maintenance(Line) | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2023-12-05 08:22 | 2023-12-05 16:05 | 7:43 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2023-12-06 08:40 | 2023-12-06 16:35 | 7:55 | S/O | For annual maintenance work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2023-12-13 08:23 | 2023-12-13 16:37 | 8:14 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-12-19 09:50 | 2023-12-19 16:06 | 6:16 | S/O | Line checking & tree trimming. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-01 | 2023-12-12 09:22 | 2023-12-12 16:34 | 7:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-01 | 2023-12-13 09:18 | 2023-12-13 16:30 | 7:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-02 | 2023-12-15 07:29 | 2023-12-15 15:25 | 7:56 | S/O | Dead line checking | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-02 | 2023-12-16 08:58 | 2023-12-16 16:54 | 7:56 | D/W | Project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2023-12-15 06:24 | 2023-12-15 12:04 | 5:40 | S/O | Halishahar End Bus S/D. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2023-12-19 08:46 | 2023-12-19 14:34 | 5:48 | S/O | Annual maintenance and dead line checking. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2023-12-20 08:26 | 2023-12-20 14:50 | 6:24 | S/O | Annual Maintenance Work . | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2023-12-21 08:24 | 2023-12-21 14:22 | 5:58 | S/O | annual maintenance and dead line checking. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2023-12-07 08:48 | 2023-12-07 14:47 | 5:59 | S/O | Annual Maintenance . | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2023-12-11 08:37 | 2023-12-11 16:00 | 7:23 | S/O | Annual maintenance and dead line checking. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2023-12-12 07:50 | 2023-12-12 13:29 | 5:39 | S/O | Annual Maintenance (Dead line Checking) and bay Maintenance work with loop change in between CB to CT at R-phase.. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-2(Rampur) | 2023-12-04 08:14 | 2023-12-04 15:42 | 7:28 | S/O | Annual Maintenance . | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2023-12-05 08:23 | 2023-12-05 16:08 | 7:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2023-12-06 08:41 | 2023-12-06 16:34 | 7:53 | S/O | Annual m/t and dead line checking | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-1 | 2023-12-06 08:29 | 2023-12-06 12:58 | 4:29 | D/W | For DCMPS project work | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2023-12-06 08:29 | 2023-12-06 12:58 | 4:29 | D/W | For DCMPS project work | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-12-19 08:32 | 2023-12-27 12:23 | 195:51 | D/W | For Cable change | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-12-23 07:40 | 2023-12-23 20:48 | 13:08 | S/O | Reconductoring of Modunaghat-Shikalbaha 132kV line in Karnafuly river. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-12-25 08:23 | 2023-12-25 22:40 | 14:17 | S/O | For reconducting of Madunaghat-Shikalbaha circuit | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2023-12-15 06:27 | 2023-12-15 12:06 | 5:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2023-12-15 06:27 | 2023-12-15 12:06 | 5:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2023-12-04 08:13 | 2023-12-04 15:43 | 7:30 | S/O | Khulshi-2 Line Maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2023-12-01 04:17 | 2023-12-01 04:39 | 0:22 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2023-12-01 09:50 | 2023-12-01 10:02 | 0:12 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2023-12-01 04:51 | 2023-12-01 09:30 | 4:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2023-12-12 09:23 | 2023-12-12 16:33 | 7:10 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2023-12-13 09:18 | 2023-12-13 16:28 | 7:10 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2023-12-15 07:27 | 2023-12-15 15:26 | 7:59 | D/W | Due to project work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2023-12-16 08:59 | 2023-12-29 07:03 | 310:04 | D/W | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 933:18 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Fen Ckt-I | 2023-12-12 09:28 | 2023-12-12 17:20 | 7:52 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Fen Ckt-II | 2023-12-13 14:15 | 2023-12-13 17:15 | 3:00 | S/O | Relay Testing | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Fen Ckt-II | 2023-12-24 09:07 | 2023-12-24 17:39 | 8:32 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2023-12-17 08:27 | 2023-12-18 17:00 | 32:33 | S/O | For dead line checking. | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2023-12-19 08:20 | 2023-12-19 17:16 | 8:56 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2023-12-21 08:56 | 2023-12-21 16:06 | 7:10 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-II | 2023-12-23 08:47 | 2023-12-23 17:20 | 8:33 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2023-12-13 09:10 | 2023-12-13 13:49 | 4:39 | S/O | Relay Testing | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-II | 2023-12-14 09:15 | 2023-12-14 13:53 | 4:38 | S/O | Relay test | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2023-12-06 09:23 | 2023-12-06 12:42 | 3:19 | S/O | Relay testing | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2023-12-13 08:38 | 2023-12-13 14:37 | 5:59 | S/O | Relay testing | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2023-12-27 09:47 | 2023-12-27 16:02 | 6:15 | D/W | S/D taken by NLDC | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-12-06 12:48 | 2023-12-06 15:02 | 2:14 | S/O | Relay testing | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-12-17 09:06 | 2023-12-17 14:42 | 5:36 | D/W | LA replacement work by AIS-GIS project at Ashugonj end. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-12-26 10:01 | 2023-12-26 18:28 | 8:27 | D/W | S/D taken by NLDC | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2023-12-17 09:02 | 2023-12-17 16:35 | 7:33 | S/O | As per NLDC's requirement. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2023-12-07 08:47 | 2023-12-07 12:11 | 3:24 | S/O | Relay testing by SPMD | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2023-12-30 09:05 | 2023-12-30 19:20 | 10:15 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-12-07 12:30 | 2023-12-07 14:04 | 1:34 | S/O | Relay test by SPMD, Cumilla. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-12-23 11:20 | 2023-12-23 12:32 | 1:12 | S/O | Removing polythene paper from Tower no 250 at Shahbazpur. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 100MW(GT) Power Plant Incomer (T4) | 2023-12-02 16:02 | 2023-12-02 16:14 | 0:12 | S/O | Black Start operation | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2023-12-21 08:53 | 2023-12-21 15:42 | 6:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2023-12-02 16:02 | 2023-12-02 16:14 | 0:12 | S/O | Black start operation | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 02 | 2023-12-04 09:06 | 2023-12-04 17:34 | 8:28 | S/O | annual maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-12-22 08:29 | 2023-12-22 15:46 | 7:17 | S/O | 132 kv bus shutdown for annual maintenance. | 44 | 320.4667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2023-12-26 06:20 | 2023-12-27 17:38 | 35:18 | D/W | ESPNER project work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-12-22 08:30 | 2023-12-22 11:21 | 2:51 | S/O | 132 kv bus shutdown for annual maintenance. | 44 | 125.4 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | HFPL line | 2023-12-22 08:26 | 2023-12-22 17:20 | 8:54 | S/O | 132 kv bus shutdown for annual maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2023-12-22 08:31 | 2023-12-22 15:32 | 7:01 | S/O | 132 kv bus shutdown for annual maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2023-12-22 08:45 | 2023-12-22 15:30 | 6:45 | S/O | 132 kv bus shutdown for annual maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2023-12-02 08:27 | 2023-12-03 15:17 | 30:50 | S/O | Annual maintenance works( Dead Line Cheek) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2023-12-05 09:49 | 2023-12-05 14:51 | 5:02 | S/O | Relay test (SPMD) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2023-12-05 15:14 | 2023-12-05 17:22 | 2:08 | S/O | Relay testing | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2023-12-13 09:04 | 2023-12-13 13:48 | 4:44 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Chowddagram-2 | 2023-12-27 08:38 | 2023-12-27 16:06 | 7:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua | 2023-12-05 06:14 | 2023-12-05 16:35 | 10:21 | D/W | Due to project work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua | 2023-12-06 06:21 | 2023-12-06 16:30 | 10:09 | S/O | Annual maintenance. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-12-05 08:40 | 2023-12-05 16:14 | 7:34 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-12-06 08:48 | 2023-12-06 15:25 | 6:37 | S/O | Annual maintenance work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-12-10 10:06 | 2023-12-10 16:44 | 6:38 | S/O | Maintenance work at sonargoan ss end. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2023-12-15 08:36 | 2023-12-15 16:59 | 8:23 | S/O | Annual maintenance at sonargaon substation | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2023-12-19 07:48 | 2023-12-19 15:31 | 7:43 | S/O | Annual Maintenance work at Sonargaon-2 ckt. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2023-12-20 08:13 | 2023-12-20 17:08 | 8:55 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2023-12-28 09:49 | 2023-12-28 12:25 | 2:36 | S/O | SPS WORK | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-2 | 2023-12-28 12:29 | 2023-12-28 13:12 | 0:43 | S/O | SPS Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2023-12-10 07:32 | 2023-12-28 15:42 | 440:10 | S/O | with instruction of NLDC | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Barayerhat Ckt | 2023-12-29 06:56 | 2023-12-29 17:48 | 10:52 | S/O | For 132KV Bus-02 Annual Maintenance. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-1 | 2023-12-29 06:44 | 2023-12-29 17:28 | 10:44 | S/O | For 132KV Bus-02 Annual Maintenance. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-2 | 2023-12-29 06:43 | 2023-12-29 17:30 | 10:47 | S/O | For 132KV Bus-02 Annual Maintenance. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2023-12-29 06:56 | 2023-12-29 17:49 | 10:53 | S/O | For 132KV Bus-02 Annual Maintenance. | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-1 | 2023-12-05 06:11 | 2023-12-05 17:05 | 10:54 | D/W | Due to project work | 9 | 98.1 | Power interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-1 | 2023-12-06 06:29 | 2023-12-06 16:14 | 9:45 | D/W | None | 9 | 87.75 | Power interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-1 | 2023-12-07 06:04 | 2023-12-07 14:46 | 8:42 | D/W | Due to project work | 9 | 78.3 | Power interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-1 | 2023-12-30 07:46 | 2023-12-30 15:58 | 8:12 | S/O | Due to project work | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-2 | 2023-12-05 06:12 | 2023-12-05 17:05 | 10:53 | D/W | Due to project work | 9 | 97.95 | Power interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-2 | 2023-12-06 06:33 | 2023-12-06 16:15 | 9:42 | D/W | None | 9 | 87.3 | Power interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-2 | 2023-12-07 06:05 | 2023-12-07 14:46 | 8:41 | D/W | Due to project work | 9 | 78.15 | Power interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2023-12-05 06:13 | 2023-12-05 17:42 | 11:29 | D/W | Due to project work | 9 | 103.35 | Power interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2023-12-06 06:18 | 2023-12-06 16:20 | 10:02 | D/W | None | 9 | 90.3 | Power interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2023-12-07 06:08 | 2023-12-07 13:47 | 7:39 | D/W | Due to project work | 9 | 68.85 | Power interruption
Kachua 132/33kV Grid Sub-Station | Cumilla South CKT | 2023-12-05 06:12 | 2023-12-05 16:40 | 10:28 | D/W | Due to project work | 9 | 94.2 | Power interruption
Kachua 132/33kV Grid Sub-Station | Cumilla South CKT | 2023-12-06 06:18 | 2023-12-06 16:29 | 10:11 | D/W | None | 9 | 91.65 | Power interruption
Kachua 132/33kV Grid Sub-Station | Cumilla South CKT | 2023-12-07 06:09 | 2023-12-07 14:17 | 8:08 | D/W | Due to project work | 9 | 73.2 | Power interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2023-12-02 08:45 | 2023-12-02 15:58 | 7:13 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2023-12-03 08:38 | 2023-12-03 15:53 | 7:15 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj- Desh Energy Ckt-01 | 2023-12-23 08:32 | 2023-12-23 17:06 | 8:34 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj- Desh Energy Ckt-01 | 2023-12-24 08:29 | 2023-12-24 14:41 | 6:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-01 | 2023-12-04 08:42 | 2023-12-04 16:09 | 7:27 | S/O | Annual Maintenence | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-01 | 2023-12-05 09:06 | 2023-12-05 16:31 | 7:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-01 | 2023-12-06 09:04 | 2023-12-06 16:24 | 7:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-01 | 2023-12-26 08:52 | 2023-12-26 16:14 | 7:22 | S/O | Shutdown taken by Sreemingol grid. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-12-10 09:03 | 2023-12-10 16:32 | 7:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-12-11 08:31 | 2023-12-11 16:55 | 8:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-12-12 08:23 | 2023-12-12 16:26 | 8:03 | S/O | S/D Taken y Sreemongal Grid for A/M | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-12-09 08:42 | 2023-12-09 16:02 | 7:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-12-02 08:53 | 2023-12-02 16:22 | 7:29 | S/O | Annual maintance works | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-12-03 09:56 | 2023-12-03 16:09 | 6:13 | S/O | Annual Maintanance Works | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-12-13 10:17 | 2023-12-13 16:46 | 6:29 | S/O | Due to the maintenance work at Fenchuganj end. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | sreemangal-Shahjibazar circuit-2 | 2023-12-09 08:32 | 2023-12-09 16:44 | 8:12 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-12-23 09:06 | 2023-12-23 13:39 | 4:33 | S/O | Chatok-Sunamgonj line-1 bay annual Maintenance works | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2023-12-08 10:30 | 2023-12-08 10:30 | 0:00 | S/O | work of 20MW PS | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2023-12-02 07:24 | 2023-12-02 14:24 | 7:00 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2023-12-03 08:20 | 2023-12-03 12:12 | 3:52 | S/O | Yearly maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2023-12-05 09:17 | 2023-12-05 13:32 | 4:15 | S/O | work of chhatak end | 0 | 0 | No interruption
|  |  | Total : | 1091:38 |  | Unserved Energy: |  | 1494.9667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-12-09 08:02 | 2023-12-09 16:57 | 8:55 | S/O | Yearly maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-12-10 08:25 | 2023-12-10 16:50 | 8:25 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-12-11 08:16 | 2023-12-11 16:21 | 8:05 | S/O | 132kV Bagerhat-Bhandaria Line S/D for Yearly maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2023-12-23 07:38 | 2023-12-23 16:38 | 9:00 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv GTPS | 2023-12-12 07:34 | 2023-12-12 16:21 | 8:47 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv GTPS | 2023-12-13 07:15 | 2023-12-13 16:48 | 9:33 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv Summit power | 2023-12-12 07:26 | 2023-12-12 16:20 | 8:54 | S/O | Due to Annual maintenance work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv Summit power | 2023-12-14 07:17 | 2023-12-14 15:36 | 8:19 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv Summit power | 2023-12-23 09:02 | 2023-12-23 16:44 | 7:42 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-01 | 2023-12-17 08:37 | 2023-12-17 16:32 | 7:55 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-01 | 2023-12-22 07:35 | 2023-12-22 15:55 | 8:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-12-09 09:19 | 2023-12-09 14:50 | 5:31 | S/O | annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-12-10 11:19 | 2023-12-10 14:44 | 3:25 | S/O | A/M | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-12-28 14:59 | 2023-12-28 16:32 | 1:33 | D/W | A/M | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-12-03 08:18 | 2023-12-03 15:37 | 7:19 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-12-04 08:14 | 2023-12-04 16:44 | 8:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-12-28 12:37 | 2023-12-28 13:05 | 0:28 | D/W | 230kV SAS signal testing by SPMD, Khulna. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2023-12-28 13:06 | 2023-12-28 13:22 | 0:16 | D/W | 230kV SAS signal testing by SPMD, Khulna. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2023-12-04 11:42 | 2023-12-04 12:42 | 1:00 | S/O | S/D from Rajbari s/s | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2023-12-28 13:26 | 2023-12-28 14:23 | 0:57 | D/W | 230kV SAS signal testing by SPMD, Khulna. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2023-12-04 14:53 | 2023-12-04 16:09 | 1:16 | S/O | A/M | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2023-12-28 14:26 | 2023-12-28 14:51 | 0:25 | D/W | 230kV SAS signal testing by SPMD, Khulna. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-1 | 2023-12-13 08:25 | 2023-12-13 15:07 | 6:42 | S/O | Annual Maintenance works. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-1 | 2023-12-30 10:28 | 2023-12-30 12:13 | 1:45 | S/O | CB open by the instruction of ALDC, Khulna | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-2 | 2023-12-30 12:16 | 2023-12-30 13:25 | 1:09 | S/O | By the instruction of ALDC Khulna | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-NWPGCL | 2023-12-23 08:58 | 2023-12-23 15:50 | 6:52 | S/O | By the instruction of ALDC, Khulna | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2023-12-20 09:15 | 2023-12-20 16:07 | 6:52 | S/O | Annual Maintanance works of Goalpara - Orion Line. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2023-12-21 08:50 | 2023-12-21 15:59 | 7:09 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-1 | 2023-12-02 08:38 | 2023-12-02 15:28 | 6:50 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-12-12 08:09 | 2023-12-12 16:53 | 8:44 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-12-13 08:27 | 2023-12-13 16:37 | 8:10 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-12-14 08:45 | 2023-12-14 17:44 | 8:59 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2023-12-18 09:38 | 2023-12-18 22:21 | 12:43 | D/W | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2023-12-19 09:07 | 2023-12-19 20:57 | 11:50 | D/W | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2023-12-20 09:25 | 2023-12-20 21:55 | 12:30 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2023-12-21 09:39 | 2023-12-22 00:43 | 15:04 | D/W | Annual Maintananace Works. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2023-12-24 08:40 | 2023-12-24 19:45 | 11:05 | D/W | SAS COMMISSIONING | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2023-12-25 08:53 | 2023-12-25 22:48 | 13:55 | D/W | SAS & DFDR Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2023-12-26 08:54 | 2023-12-26 20:33 | 11:39 | D/W | SAS COMMISSION | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2023-12-27 10:33 | 2023-12-27 17:26 | 6:53 | D/W | SAS & DFDR Commissioning | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- Noapara-2 | 2023-12-19 07:48 | 2023-12-19 16:07 | 8:19 | S/O | Due to annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- South -1 | 2023-12-10 08:45 | 2023-12-10 15:51 | 7:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- South -2 | 2023-12-11 08:21 | 2023-12-11 15:32 | 7:11 | S/O | Due to annual maintenance work. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Goalpara-2 | 2023-12-14 08:21 | 2023-12-14 14:21 | 6:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Noapara-1 | 2023-12-20 08:13 | 2023-12-20 15:26 | 7:13 | S/O | Due to Noapara END Instruction by ALDC | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2023-12-24 07:45 | 2023-12-24 15:45 | 8:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North-WestCkt-1 | 2023-12-30 08:18 | 2023-12-30 16:01 | 7:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-1 | 2023-12-09 08:03 | 2023-12-09 15:58 | 7:55 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-2 | 2023-12-12 08:04 | 2023-12-12 16:09 | 8:05 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2023-12-28 11:09 | 2023-12-28 11:09 | 0:00 | D/W | Annual Maintananace Works. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-1 | 2023-12-12 08:35 | 2023-12-12 16:08 | 7:33 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2023-12-19 09:21 | 2023-12-19 16:19 | 6:58 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Barishal CKT-02 | 2023-12-23 08:42 | 2023-12-23 16:12 | 7:30 | S/O | Annual maintenance. | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Magura 1 | 2023-12-03 14:46 | 2023-12-03 15:35 | 0:49 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 2 | 2023-12-17 07:43 | 2023-12-18 17:24 | 33:41 | S/O | Khulna Central (S) for Annual Maintenance Work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2023-12-03 09:29 | 2023-12-03 13:08 | 3:39 | D/W | Annual Maintananace Works. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2023-12-03 13:17 | 2023-12-03 16:11 | 2:54 | D/W | Annual Maintananace Works. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2023-12-04 14:53 | 2023-12-04 16:07 | 1:14 | D/W | Project work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur -1 | 2023-12-04 11:42 | 2023-12-04 12:43 | 1:01 | D/W | Project work. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-1 (L-1) | 2023-12-13 08:49 | 2023-12-13 15:55 | 7:06 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-1 (L-1) | 2023-12-14 08:35 | 2023-12-14 16:09 | 7:34 | S/O | Annual Maintananace Works. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-2 (L-2) | 2023-12-17 09:18 | 2023-12-17 16:30 | 7:12 | S/O | Yearly maintenance | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-2 (L-2) | 2023-12-18 10:14 | 2023-12-18 15:56 | 5:42 | S/O | Yearly Maintenance Work. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | Madaripur-Shariatpur CKT-01 | 2023-12-28 08:16 | 2023-12-28 16:59 | 8:43 | S/O | Annual Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 452:34 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2023-12-15 11:17 | 2023-12-16 13:51 | 26:34 | S/O | Shutdown is taken from baharampur end | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2023-12-19 10:51 | 2023-12-19 20:09 | 9:18 | S/O | Taken from India side | 0 | 0 | No interruption
BIPTC | Ishurdi-3 | 2023-12-03 08:34 | 2023-12-03 19:34 | 11:00 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | Ishurdi-4 | 2023-12-05 09:10 | 2023-12-05 19:02 | 9:52 | S/O | Annual Maintenance Shutdown is taken for iswordi side. | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2023-12-06 08:29 | 2023-12-06 17:22 | 8:53 | S/O | Annual Maintenance. | 0 | 0 | Power interruption
BIPTC | Rajshahi-1 | 2023-12-24 08:31 | 2023-12-24 08:31 | 0:00 | S/O | For annual maintenance at Rajshahi end | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2023-12-24 10:31 | 2023-12-24 16:58 | 6:27 | S/O | For relay testing (Main-2 ABB) | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2023-12-25 08:39 | 2023-12-25 16:40 | 8:01 | S/O | For annual maintenance at Rajshahi end | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2023-12-26 08:48 | 2023-12-26 16:12 | 7:24 | D/W | Shutdown is taken from Ruppur project team. | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2023-12-06 08:29 | 2023-12-06 17:22 | 8:53 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2023-12-26 08:49 | 2023-12-26 16:12 | 7:23 | D/W | Shutdown is taken from Ruppur project team. | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2023-12-27 09:01 | 2023-12-28 15:21 | 30:20 | D/W | shutdown is taken from Rajshahi end | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-12-19 10:25 | 2023-12-19 13:22 | 2:57 | S/O | shutdown is taken from Rajshahi end | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-12-26 09:20 | 2023-12-26 15:22 | 6:02 | D/W | Order from NLDC Xen | 4 | 24.1333 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2023-12-26 09:20 | 2023-12-26 15:23 | 6:03 | D/W | Order from NLDC Xen | 4 | 24.2 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Kushtia 1 | 2023-12-18 08:24 | 2023-12-18 14:23 | 5:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Kushtia 2 | 2023-12-20 08:11 | 2023-12-20 13:23 | 5:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 2 | 2023-12-03 13:17 | 2023-12-03 16:10 | 2:53 | D/W | Maintenance | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-1 | 2023-12-30 08:26 | 2023-12-30 14:57 | 6:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | Jhenaidah-Chuadanga Ckt-1 | 2023-12-09 12:27 | 2023-12-09 15:03 | 2:36 | D/W | SCADA Integration with NLDC. | 36 | 93.6 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2023-12-28 09:10 | 2023-12-28 16:17 | 7:07 | S/O | requested by aldc bogura | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 3 | 2023-12-02 09:30 | 2023-12-02 18:54 | 9:24 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 4 | 2023-12-04 08:42 | 2023-12-04 19:00 | 10:18 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2023-12-05 10:06 | 2023-12-05 16:27 | 6:21 | S/O | Requested By Jhenaidah 230/132KV S/S | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-12-26 07:56 | 2023-12-26 16:36 | 8:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-12-27 07:34 | 2023-12-27 16:35 | 9:01 | S/O | For Annual miantenance from Noapara end | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-12-28 07:49 | 2023-12-28 16:41 | 8:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2023-12-29 07:54 | 2023-12-29 16:58 | 9:04 | S/O | Annual Maintenance from Noapara end | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Kushtia 132kV Circuit-1(L1) | 2023-12-09 08:03 | 2023-12-09 15:19 | 7:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Magura 132kV Circuit-2(L6) | 2023-12-05 08:08 | 2023-12-05 16:09 | 8:01 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Magura 132kV Circuit-2(L6) | 2023-12-06 08:12 | 2023-12-06 15:46 | 7:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-2 | 2023-12-05 10:07 | 2023-12-05 16:26 | 6:19 | D/W | Circuit breaker punch point problem clear | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia -Bheramara-1 | 2023-12-17 08:34 | 2023-12-17 14:54 | 6:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Bheramara-2 | 2023-12-21 08:33 | 2023-12-21 13:49 | 5:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Jhenaidah-1 | 2023-12-10 08:16 | 2023-12-11 12:52 | 28:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Jhenaidah-2 | 2023-12-12 08:09 | 2023-12-12 14:35 | 6:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Jhenaidah-2 | 2023-12-13 08:11 | 2023-12-13 14:19 | 6:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. - 2 | 2023-12-11 06:52 | 2023-12-11 19:22 | 12:30 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. -1 | 2023-12-02 09:50 | 2023-12-02 15:36 | 5:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. -1 | 2023-12-03 07:47 | 2023-12-03 15:53 | 8:06 | S/O | Annual Maintenance of Jhe. Mag. Ckt.-1 | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. -1 | 2023-12-04 07:54 | 2023-12-04 14:50 | 6:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Sirajgonj | 2023-12-22 07:27 | 2023-12-25 17:31 | 82:04 | D/W | Project work | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Sirajgonj | 2023-12-28 07:18 | 2023-12-28 16:24 | 9:06 | D/W | Project work | 0 | 0 | No interruption
|  |  | Total : | 447:29 |  | Unserved Energy: |  | 141.9333
Bogura Grid Circle :
Amnura 132/33kV Grid Sub-Station | Amnura - Chapai Nawabganj | 2023-12-24 08:17 | 2023-12-24 16:21 | 8:04 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - Chapai Nawabganj | 2023-12-26 08:18 | 2023-12-26 14:43 | 6:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2023-12-02 09:51 | 2023-12-02 16:48 | 6:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2023-12-03 08:36 | 2023-12-03 16:16 | 7:40 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2023-12-04 08:28 | 2023-12-04 16:26 | 7:58 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2023-12-05 08:39 | 2023-12-05 16:30 | 7:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2023-12-06 08:43 | 2023-12-06 17:07 | 8:24 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2023-12-07 09:11 | 2023-12-07 14:35 | 5:24 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | PS 230 KV Ckt1 | 2023-12-09 09:24 | 2023-12-09 16:16 | 6:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | PS 230 KV Ckt2 | 2023-12-10 08:54 | 2023-12-10 18:18 | 9:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | PS 230 KV Ckt2 | 2023-12-30 10:18 | 2023-12-30 15:35 | 5:17 | S/O | Jumper replacement of conductor | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-12-29 06:10 | 2023-12-29 06:10 | 0:00 | D/W | For project work at Bogura side. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-2 | 2023-12-29 06:24 | 2023-12-29 06:24 | 0:00 | D/W | For project work at Bogura side. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-12-13 06:11 | 2023-12-13 09:39 | 3:28 | D/W | For project work at Bogura side. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-12-13 06:11 | 2023-12-13 09:40 | 3:29 | D/W | For project work at Bogura side. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-1 | 2023-12-09 08:39 | 2023-12-09 13:40 | 5:01 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-1 | 2023-12-10 08:52 | 2023-12-10 16:42 | 7:50 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-1 | 2023-12-11 07:38 | 2023-12-11 16:18 | 8:40 | S/O | Annual Maintenance work. CB- Open. Line DS - Open. Earth Switch - Close. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-1 | 2023-12-29 07:01 | 2023-12-29 07:01 | 0:00 | D/W | S/d | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-2 | 2023-12-12 07:45 | 2023-12-12 15:05 | 7:20 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-2 | 2023-12-13 08:10 | 2023-12-13 15:36 | 7:26 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-2 | 2023-12-14 09:21 | 2023-12-14 13:27 | 4:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-2 | 2023-12-29 07:04 | 2023-12-29 07:04 | 0:00 | D/W | S/d | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-12-15 06:35 | 2023-12-19 20:36 | 110:01 | S/O | S/d | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-12-15 06:50 | 2023-12-19 20:36 | 109:46 | S/O | S/d | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Confidance UN-1 | 2023-12-29 06:23 | 2023-12-29 06:23 | 0:00 | D/W | 230kV Naogaon Line Conductor Stringing. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Confidance UN-2 | 2023-12-29 06:26 | 2023-12-29 06:26 | 0:00 | D/W | 230kV Naogaon Line Conductor Stringing. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2023-12-29 06:13 | 2023-12-29 06:13 | 0:00 | D/W | 230kV Naogaon Line Conductor Stringing. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2023-12-29 06:31 | 2023-12-29 06:31 | 0:00 | D/W | 230kV Naogaon Line Conductor Stringing. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2023-12-01 07:10 | 2023-12-01 13:45 | 6:35 | S/O | Main bus S/D | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2023-12-01 07:10 | 2023-12-01 13:45 | 6:35 | S/O | Main bus S/D | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Amnura | 2023-12-01 07:12 | 2023-12-01 12:55 | 5:43 | S/O | Main bus S/D | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2023-12-01 07:20 | 2023-12-01 12:49 | 5:29 | S/O | Main bus S/D | 35 | 191.9167 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-01 | 2023-12-28 08:40 | 2023-12-28 17:25 | 8:45 | S/O | Annual Maintenance of 132KV Line and Bay Equipment. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-01 | 2023-12-30 08:30 | 2023-12-30 17:25 | 8:55 | S/O | Due to annual Maintenance (death line checking) | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Rangpur-Kurigram Ckt-01 | 2023-12-15 08:02 | 2023-12-15 17:37 | 9:35 | S/O | OPGW maintenancce | 35 | 335.4167 | Power interruption
Lalmonirhat 132/33kV Grid Sub-Station | Rangpur-Lalmonirhat | 2023-12-15 07:50 | 2023-12-15 16:28 | 8:38 | D/W | 132KV Rangpur-Lalmonirhat transmission Line OPGW maintenance. | 26 | 224.4667 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Polashbari 1 | 2023-12-20 08:37 | 2023-12-20 16:20 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Polashbari 1 | 2023-12-23 08:31 | 2023-12-23 14:51 | 6:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Polashbari 2 | 2023-12-24 08:49 | 2023-12-24 16:42 | 7:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Polashbari 2 | 2023-12-28 09:22 | 2023-12-28 15:32 | 6:10 | S/O | Annual Maintenance & B phase LA Change | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2023-12-09 08:26 | 2023-12-09 17:00 | 8:34 | S/O | annual maintenance | 35 | 299.8333 | Power interruption
Natore 132/33kV Grid Sub-Station | Bogura-1 | 2023-12-08 06:15 | 2023-12-08 16:37 | 10:22 | S/O | bus maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Bogura-1 | 2023-12-29 07:04 | 2023-12-29 07:04 | 0:00 | D/W | Due to project work | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Bogura-2 | 2023-12-08 06:15 | 2023-12-08 16:39 | 10:24 | S/O | bus maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Bogura-2 | 2023-12-29 07:04 | 2023-12-29 07:04 | 0:00 | D/W | Due to project work | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-12-02 07:43 | 2023-12-02 16:05 | 8:22 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-12-03 08:25 | 2023-12-03 15:49 | 7:24 | S/O | Annual maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-12-04 08:12 | 2023-12-04 12:51 | 4:39 | S/O | Yearly maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-12-08 06:20 | 2023-12-08 10:20 | 4:00 | S/O | bus maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-12-05 08:17 | 2023-12-05 16:11 | 7:54 | S/O | Annual maintanance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-12-08 06:13 | 2023-12-08 10:38 | 4:25 | S/O | bus maintenance. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajlanka | 2023-12-08 06:15 | 2023-12-08 10:40 | 4:25 | S/O | bus maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-1 | 2023-12-08 06:14 | 2023-12-08 10:35 | 4:21 | S/O | bus maintenance | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-2 | 2023-12-08 06:14 | 2023-12-08 10:39 | 4:25 | S/O | bus maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-01 | 2023-12-21 08:50 | 2023-12-21 15:56 | 7:06 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-02 | 2023-12-27 09:01 | 2023-12-27 16:16 | 7:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | Thakurgaon-1 | 2023-12-23 06:44 | 2023-12-23 13:18 | 6:34 | S/O | Purbosadipur BUS Sutdown | 30 | 197 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2023-12-10 08:48 | 2023-12-10 16:47 | 7:59 | S/O | annual maintanance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2023-12-11 08:44 | 2023-12-11 15:24 | 6:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2023-12-23 06:42 | 2023-12-23 12:29 | 5:47 | S/O | Annual maintenance of 132 kV bus | 75 | 433.75 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2023-12-13 10:42 | 2023-12-13 19:20 | 8:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2023-12-14 09:31 | 2023-12-14 16:36 | 7:05 | S/O | annual maintanance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2023-12-17 08:32 | 2023-12-17 15:06 | 6:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2023-12-23 06:42 | 2023-12-23 12:29 | 5:47 | S/O | Annual maintenance of 132 kV bus | 75 | 433.75 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2023-12-20 07:59 | 2023-12-20 16:33 | 8:34 | S/O | annual maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2023-12-22 08:57 | 2023-12-22 15:48 | 6:51 | S/O | annual maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2023-12-23 06:40 | 2023-12-23 12:32 | 5:52 | S/O | Annual maintenance of 132 kV bus | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2023-12-23 06:41 | 2023-12-23 13:04 | 6:23 | S/O | Annual maintenance of 132 kV bus | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2023-12-27 09:22 | 2023-12-27 15:31 | 6:09 | S/O | Annual Maintenance (Schedule Changed 26.12.23 to 27.12.23 for Prime Minister program) | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Bogura 400 KV Line Ckt-01 | 2023-12-10 08:40 | 2023-12-10 17:17 | 8:37 | S/O | Bay & Line checking | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Bogura 400 KV Line Ckt-01 | 2023-12-11 08:42 | 2023-12-11 20:19 | 11:37 | S/O | Bay & Line Checking | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Bogura 400 KV Line Ckt-02 | 2023-12-12 07:48 | 2023-12-12 16:50 | 9:02 | S/O | Annual maintenance | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Bogura 400 KV Line Ckt-02 | 2023-12-13 07:51 | 2023-12-13 16:59 | 9:08 | S/O | Dead line checking. | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Bogura 400 KV Line Ckt-02 | 2023-12-14 07:20 | 2023-12-14 15:35 | 8:15 | S/O | Annual Maintance S/D | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Amnura | 2023-12-17 08:27 | 2023-12-17 10:55 | 2:28 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Amnura | 2023-12-22 08:25 | 2023-12-22 15:53 | 7:28 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Chapainawabganj | 2023-12-20 08:24 | 2023-12-20 16:08 | 7:44 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Chapainawabganj | 2023-12-21 08:18 | 2023-12-21 15:07 | 6:49 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-01 | 2023-12-06 08:29 | 2023-12-06 17:21 | 8:52 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-01 | 2023-12-23 08:35 | 2023-12-23 15:35 | 7:00 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-01 | 2023-12-24 08:18 | 2023-12-24 16:58 | 8:40 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-01 | 2023-12-25 08:29 | 2023-12-25 16:39 | 8:10 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-01 | 2023-12-26 08:25 | 2023-12-26 16:11 | 7:46 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-12-06 08:29 | 2023-12-06 17:21 | 8:52 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-12-26 08:37 | 2023-12-26 16:11 | 7:34 | D/W | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-12-27 08:33 | 2023-12-27 15:29 | 6:56 | S/O | A/M | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-12-28 08:17 | 2023-12-28 15:20 | 7:03 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230 Kv BIPTC Ckt-02 | 2023-12-29 08:31 | 2023-12-29 14:51 | 6:20 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-02 | 2023-12-02 08:32 | 2023-12-02 16:09 | 7:37 | S/O | As the instructions of ALDC, Bogura and QF-GMD-39 | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Purbosadipur CKT-01 | 2023-12-12 08:20 | 2023-12-12 16:12 | 7:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-04 07:12 | 2023-12-04 17:05 | 9:53 | D/W | Solar project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-05 07:23 | 2023-12-06 17:18 | 33:55 | D/W | BCRECL has taken shutdown. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-15 07:47 | 2023-12-15 16:50 | 9:03 | D/W | Due to project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-16 07:39 | 2023-12-16 17:11 | 9:32 | D/W | BCRECL has taken Shutdown for project work. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-17 07:22 | 2023-12-17 16:29 | 9:07 | D/W | BCRECL project work s/d | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-18 06:54 | 2023-12-18 16:40 | 9:46 | D/W | Due to project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-20 07:16 | 2023-12-20 16:49 | 9:33 | D/W | Due to project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-22 07:26 | 2023-12-22 14:24 | 6:58 | D/W | Rooppur project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-24 07:08 | 2023-12-24 20:20 | 13:12 | D/W | BCRECL has taken shutdown | 0 | 0 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-25 07:21 | 2023-12-25 17:32 | 10:11 | D/W | 68 MW Solar project | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2023-12-28 07:16 | 2023-12-28 16:59 | 9:43 | D/W | EEGBPSP project PGCB , has taken shutdown for LILO & Ullahpara 132/33kV substation commissioning. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-01 07:23 | 2023-12-01 16:57 | 9:34 | D/W | BCRECL has taken shutdown | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-02 07:12 | 2023-12-02 16:08 | 8:56 | D/W | 68 MW solar park project. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-08 08:19 | 2023-12-09 16:42 | 32:23 | D/W | Due to project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-19 07:12 | 2023-12-19 17:00 | 9:48 | D/W | 68 Mw solar | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-22 07:27 | 2023-12-23 18:13 | 34:46 | D/W | Rooppur Project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2023-12-26 07:03 | 2023-12-28 17:19 | 58:16 | D/W | jumpering for LILO of Sirajgonj-baghabari 132 kv ckt to ullapara 132/33 kv ss. | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-01 | 2023-12-04 08:35 | 2023-12-04 17:15 | 8:40 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-01 | 2023-12-05 07:40 | 2023-12-05 15:54 | 8:14 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-01 | 2023-12-06 08:45 | 2023-12-06 16:28 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2023-12-01 08:16 | 2023-12-01 16:32 | 8:16 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2023-12-02 08:58 | 2023-12-02 17:03 | 8:05 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2023-12-03 08:29 | 2023-12-03 17:20 | 8:51 | S/O | annual maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2023-12-20 08:33 | 2023-12-20 17:26 | 8:53 | S/O | Sreepur ckt-2 Bus DS maintenance work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-1 | 2023-12-21 09:15 | 2023-12-21 16:17 | 7:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-2 | 2023-12-24 08:55 | 2023-12-24 16:51 | 7:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1140:19 |  | Unserved Energy: |  | 2116.1333
Others :
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-12-04 09:25 | 2023-12-04 16:27 | 7:02 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-12-05 09:24 | 2023-12-05 15:10 | 5:46 | S/O | Annual maintenance work | 0 | 0 | No interruption
|  |  | Total : | 12:48 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 5472:00 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:December 2023
| Area | Previous Month (November' 2023) |  |  |  | Current Month (December '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 9 | 13 | 225 | 247 | 21 | 6 | 224 | 251
2 | Dhaka (South) Grid Circle. | 32 | 23 | 106 | 161 | 17 | 19 | 114 | 150
3 | Chattogram Grid Circle. | 14 | 11 | 97 | 122 | 2 | 6 | 89 | 97
4 | Cumilla Grid Circle. | 16 | 11 | 123 | 150 | 7 | 3 | 150 | 160
5 | Khulna Grid Circle. | 25 | 11 | 121 | 157 | 4 | 11 | 110 | 125
6 | HVDC Grid Circle | 3 | 14 | 55 | 72 | 7 | 5 | 66 | 78
7 | Bogura Grid Circle. | 9 | 20 | 174 | 203 | 8 | 15 | 234 | 257
8 | Others | 1 | 0 | 0 | 1 |  |  | 2 | 2
9 | Total | 109 | 103 | 901 | 1113 | 66 | 65 | 989 | 1120
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:December 2023
| Area | Previous Month (November' 2023) |  |  |  | Current Month (December '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 70 | 436.28 | 283.27 | 789.55 | 127.46 | 426.33 | 3895.5 | 4449.29
2 | Dhaka (South) Grid Circle. | 138.75 | 100.2 | 175.7 | 414.65 | 724.14 | 133.78 | 594.57 | 1452.49
3 | Chattogram Grid Circle. | 21.4 | 49.33 | 260.73 | 331.46 |  | 6.5 | 556.45 | 562.95
4 | Cumilla Grid Circle. | 31.53 | 158.22 | 223.9 | 413.65 | 7.4 | 18.67 | 4629.07 | 4655.14
5 | Khulna Grid Circle. | 997.85 | 46.75 | 291.08 | 1335.68 | 5 | 5.4 | 409.1 | 419.5
6 | HVDC Grid Circle | 0 | 149.32 | 520.68 | 670 | 184.92 | 66.67 | 863.38 | 1114.97
7 | Bogura Grid Circle. | 136.83 | 202.02 | 559.87 | 898.72 | 138.97 | 36.3 | 4957.15 | 5132.42
8 | Others | 0 | 0 | 0 | 0 |  |  |  | 0
9 | Total | 1396.36 | 1142.12 | 2315.23 | 4853.71 | 1187.89 | 693.65 | 15905.22 | 17786.76
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:December 2023
A) Power Interruption | [10 empty] | 2 | 1
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 8 | 8 | 16 | 6 | - | 10 | 3667.53
2 | Dhaka (South) | 5031.6 | 6 | 5 | 11 | 2 | 2 | 7 | 795.89
3 | Chattogram | 2042 | 1 | 5 | 6 | 1 | 1 | 4 | 562.95
4 | Khulna | 2434 | 3 | 10 | 13 | 3 |  | 10 | 419.5
5 | HVDC | 5954.3 | 6 | 5 | 11 | 2 | 1 | 8 | 973.03
6 | Bogura | 3145.6 | 9 | 20 | 29 | 3 | 4 | 22 | 3016.29
7 | Cumilla | 2981 | 3 | 20 | 23 | 2 |  | 21 | 3160.17
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 12595.36
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.97%
4 | Khulna | 99.95%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.98% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:December 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | 4 | 7 | 3 | 1 | 3 | 781.75
2 | Dhaka (South) | 990.29 | - | 2 |  | 2 | - | - | 2 | 656.6
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | 3 |  | 3 | - | - | 3 | 141.93
6 | Bogura | 1803.3 | - | - | 7 | 7 | - | - | 7 | 2116.13
7 | Cumilla | 1648.16 | - |  | 14 | 14 | - | - | 14 | 1494.97
8 | Others | - | - | 2 | 2 | 4 | - | - | 1 | -
| Total | 10176.6215 | [7 empty] | 5191.38
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.97%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:December 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-12-01 | 30 | - | 5 | 11hr15 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:December 2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Dhamrai 132/33kV Grid Sub-Station | 2 | 0:40 | 28.7
Kaliakoir 400/230/132kV Grid Sub-Station | 1 | 7:40 | 383.3333
Kishoreganj 132/33kV Grid Sub-Station | 1 | 1:26 | 43
Manikganj 132/33kV Grid Sub-Station | 1 | 0:02 | 0.66667
Mirzapur 132/33kV GIS Grid Sub-Station | 2 | 0:57 | 12.35
Sreepur 230/132/33kV Grid Sub-Station | 1 | 0:06 | 4.7
Savar 132/33kV Grid Sub-Station | 2 | 0:19 | 11.08
Tongi 230/132/33kV Grid Sub-Station | 1 | 1:00 | 70
Kabirpur 132/33kV Grid Sub-Station | 3 | 16:31 | 2147.17
Kodda 132/33kV Grid Sub-Station | 3 | 17:18 | 865
Mymensingh 132/33kV Grid Sub-Station | 1 | 2:32 | 114
Tongi 230/132/33kV Grid Sub-Station | 1 | 6:52 | 68.6667
Dhamrai 132/33kV Grid Sub-Station | 1 | 0:02 | 3.3333
Manikganj 132/33kV Grid Sub-Station | 2 | 16:52 | 337.33
Tangail 132/33kV Grid Sub-Station | 1 | 7:12 | 360
Narshingdi 132/33kV Grid Sub-Station | 1 | 4:24 | 101.2
Siddhirganj 132/33kV Grid Sub-Station | 2 | 1:46 | 60.07
Sonargaon 132/33kV Grid Sub-Station | 3 | 27:06 | 40.05
Haripur 230/132kV Grid Sub-Station | 1 | 5:06 | 61.2
Keranigonj 230/132/33kV Grid Sub-Station | 1 | 7:38 | 595.4
Munshiganj 132/33kV Grid Sub-Station | 2 | 9:08 | 420.13
Nawabganj 132/33kV Grid Sub-Station | 1 | 2:50 | 28.3333
Srinagar 132/33kV Grid Sub-Station | 2 | 11:02 | 146.1
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:26 | 6.5
Baroaulia 132/33kV Grid Sub-Station | 1 | 5:09 | 77.25
Dohazari 132/33kV Grid Sub-Station | 2 | 8:19 | 245.87
Halishahar 132/33kV Grid Sub-Station | 1 | 5:08 | 205.3333
Khulshi 132/33kV Grid Sub-Station | 1 | 0:56 | 28
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 1:52 | 18.6667
Chauddagram 132/33kV Grid Sub-Station | 1 | 0:06 | 1.4
Chauddagram 132/33kV Grid Sub-Station | 1 | 0:12 | 6
Chandpur 132/33kV Grid Sub-Station | 2 | 11:45 | 147.42
Chauddagram 132/33kV Grid Sub-Station | 1 | 7:55 | 158.3333
Chowmuhani 132/33kV Grid Sub-Station | 4 | 26:35 | 1255.07
Daudkandi 132/33kV Grid Sub-Station | 1 | 8:51 | 531
Kachua 132/33kV Grid Sub-Station | 10 | 107:37 | 871.65
Ramganj 132/33kV Grid Sub-Station | 1 | 7:59 | 135.7167
Sylhet 132/33kV Grid Sub-Station | 2 | 2:47 | 34.92
Chowmuhani 132/33kV Grid Sub-Station | 3 | 21:02 | 543.97
Kachua 132/33kV Grid Sub-Station | 11 | 105:40 | 951
Benapole 132/33kV Grid Sub-Station | 1 | 0:11 | 2.2
Bhandaria 132/33kV Grid Sub-Station | 2 | 0:27 | 8.2
Barishal 132/33kV Grid Sub-Station | 2 | 4:55 | 101.73
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:06 | 14.3
Gopalganj 132/33kV Grid Sub-Station | 1 | 7:30 | 52.5
Madaripur 132/33kV Grid Sub-Station | 1 | 1:25 | 17
Narail 132/33kV Grid Sub-Station | 4 | 13:01 | 188.43
Noapara 132/33kV Grid Sub-Station | 1 | 2:04 | 35.1333
Ishurdi 132/33kV Grid Sub-Station | 2 | 5:01 | 111.78
Jhenaidah 132/33kV Grid Sub-Station | 2 | 8:54 | 110.33
Kushtia 132/33kV Grid Sub-Station | 2 | 0:51 | 29.47
Ishurdi 132/33kV Grid Sub-Station | 2 | 9:49 | 176.7
Jhenaidah 132/33kV Grid Sub-Station | 2 | 14:11 | 496.42
Magura 132/33kV Grid Sub-Station | 1 | 4:00 | 40
Pabna 132/33kV Grid Sub-Station | 1 | 0:25 | 8.3333
Bheramara 230/132kV Grid Sub-Station | 2 | 12:05 | 48.33
Chuadanga 132/33kV Grid Sub-Station | 1 | 2:36 | 93.6
Barapukuria 230/132/33kV Grid Sub-Station | 1 | 1:21 | 27
Naogaon 132/33kV Grid Sub-Station | 1 | 0:34 | 14.1667
Natore 132/33kV Grid Sub-Station | 4 | 3:37 | 123.63
Niamatpur 132/33kV Grid Sub-Station | 1 | 0:07 | 1.1667
Rajshahi 230/132/33kV Grid Sub-Station | 2 | 1:33 | 9.3
Bogura 132/33kV Grid Sub-Station | 2 | 7:15 | 253.75
Chapai 132/33kV Grid Sub-Station | 1 | 5:29 | 191.9167
Naogaon 132/33kV Grid Sub-Station | 4 | 14:50 | 733.25
Natore 132/33kV Grid Sub-Station | 1 | 4:00 | 204
Purbasadipur 132/33kV Grid Sub-Station | 1 | 5:47 | 867.5
Rajshahi 132/33kV Grid Sub-Station | 9 | 23:08 | 429.6
Sirajganj 132/33kV Grid Sub-Station | 1 | 2:41 | 161
Chapai 132/33kV Grid Sub-Station | 1 | 5:29 | 191.9167
Kurigram 132/33kV Grid Sub-Station | 1 | 9:35 | 335.4167
Lalmonirhat 132/33kV Grid Sub-Station | 1 | 8:38 | 224.4667
Naogaon 132/33kV Grid Sub-Station | 1 | 8:34 | 299.8333
Panchagarh 132/33kV Grid Sub-Station | 1 | 6:34 | 197
Purbasadipur 132/33kV Grid Sub-Station | 2 | 11:34 | 867.5
Total Unserved energy : | 152 | 680:05 | 17786.7833
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:December 2023
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-12-03 13:00 | 30
2 | Agargaon 230/132kV Grid Sub-Station | 2023-12-06 13:00 | 77
3 | Banani 132/33kV Grid Sub-Station | 2023-12-31 01:00 | 52
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-12-03 10:00 | 15
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-12-30 13:00 | 134
6 | BashundharaCement 132/33kV Sub-Station | 2023-12-31 06:00 | 17
7 | Bhulta 132/33kV Grid Sub-Station | 2023-12-26 12:00 | 235
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-12-07 11:00 | 134
9 | Charsaidpur 132/33kV Sub-Station | 2023-12-26 16:00 | 34
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-12-06 13:00 | 26
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-12-03 18:00 | 122
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-12-03 13:00 | 118.3
13 | Fatullah 132/33kV Grid Sub-Station | 2023-12-04 12:00 | 59
14 | Ghorashal 230/132/33kV Sub-Station | 2023-12-27 20:00 | 62
15 | Gulshan 132/33kV Grid Sub-Station | 2023-12-04 13:00 | 90
16 | HaripurSBU 132/33kV Sub-Station | 2023-12-05 10:00 | 167
17 | Hasnabad 132/33kV Grid Substation | 2023-12-29 12:00 | 78
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-12-04 12:00 | 148
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-12-05 18:00 | 259
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-12-19 11:00 | 96
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-12-20 12:00 | 62.4
22 | Kazla 132/33kV Grid Sub-Station | 2023-12-06 13:00 | 86
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-12-14 13:00 | 72
24 | Kodda 132/33kV Grid Sub-Station | 2023-12-18 11:00 | 287
25 | Lalbag 132/33kV Grid Sub-Station | 2023-12-07 13:00 | 86
26 | Madanganj 132/33kV Grid Sub-Station | 2023-12-31 18:00 | 37
27 | Madartek 132/33kV Grid Sub-Station | 2023-12-06 18:30 | 90.22
28 | Manikganj 132/33kV Grid Sub-Station | 2023-12-19 18:00 | 101
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-12-24 13:00 | 66
30 | Matuail 132/33kV Grid Sub-Station | 2023-12-21 12:00 | 63.6
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-12-28 12:00 | 102
32 | Mirpur 132/33kV Grid Sub-Station | 2023-12-05 13:00 | 111
33 | Mirzapur 132/33kV GIS Grid Sub-Station | 2023-12-28 18:30 | 44
34 | MI_Cement 132/33kV Grid Sub-Station | 2023-12-13 17:00 | 20
35 | Mogbazar 132/33kV Grid Sub-Station | 2023-12-27 14:00 | 86.3
36 | Motijheel 132/33kV Grid Sub-Station | 2023-12-03 13:00 | 35
37 | Munshiganj 132/33kV Grid Sub-Station | 2023-12-08 13:00 | 80
38 | Narinda 132/33kV Grid Sub-Station | 2023-12-06 13:00 | 57
39 | Narshingdi 132/33kV Grid Sub-Station | 2023-12-04 18:30 | 152
40 | Nawabganj 132/33kV Grid Sub-Station | 2023-12-06 21:00 | 34.8
41 | New Tongi 132/33kV Grid Sub-Station | 2023-12-06 12:00 | 66
42 | Postogola 132/33kV Grid Sub-Station | 2023-12-02 12:00 | 45
43 | Purbachal 132/33kV Grid Sub-Station | 2023-12-01 12:00 | 15
44 | Rahim Steel 132/33kV Sub-Station | 2023-12-24 11:00 | 129
45 | Rajendrapur 132/33kV Grid Sub-Station | 2023-12-30 13:00 | 88
46 | Satmasjid 132/33kV Grid Sub-Station | 2023-12-27 13:00 | 91
47 | Savar 132/33kV Grid Sub-Station | 2023-12-09 12:00 | 146
48 | SevenRings 132/11kV Sub-Station | 2023-12-30 15:00 | 22.41
49 | ShahCement 132/33kV Grid Sub-Station | 2023-12-01 01:00 | 37
50 | Shitalakhya 132/33kV Grid Sub-Station | 2023-12-06 15:00 | 91
51 | Shyampur 132/33kV Grid Sub-Station | 2023-12-06 12:00 | 168
52 | Siddhirganj 132/33kV Grid Sub-Station | 2023-12-02 12:00 | 100
53 | Sonargaon 132/33kV Grid Sub-Station | 2023-12-31 11:00 | 94
54 | Sreepur 230/132/33kV Grid Sub-Station | 2023-12-04 17:00 | 63
55 | Srinagar 132/33kV Grid Sub-Station | 2023-12-22 13:00 | 33
56 | Tongi 230/132/33kV Grid Sub-Station | 2023-12-20 11:00 | 123
57 | Ullon 132/33kV Grid Sub-Station | 2023-12-06 13:00 | 46
58 | Uttara 132/33kV Grid Sub-Station | 2023-12-07 18:00 | 57
59 | UttaraNew 132/33kV Grid Sub-Station | 2023-12-24 17:00 | 52
60 | Zigatola 132/33kV Grid Sub-Station | 2023-12-03 13:00 | 83
61 | Agrabad 132/33kV Grid Sub-Station | 2023-12-03 14:00 | 56
62 | AKS 132/33kV Grid Sub-Station | 2023-12-30 15:00 | 21
63 | AKSML 230/33kV Grid Sub-Station | 2023-12-01 03:00 | 103.4
64 | Bakulia 132/33kV Grid Sub-Station | 2023-12-03 11:00 | 85
65 | Baroaulia 132/33kV Grid Sub-Station | 2023-12-28 14:00 | 69
66 | Baroirhat 132/33kV Grid Sub-Station | 2023-12-25 13:00 | 45
67 | BSRM 230/33kV Grid Sub-Station | 2023-12-01 02:00 | 142
68 | Chandraghona 132/33kV Grid Sub-Station | 2023-12-02 17:00 | 26
69 | Coxsbazar 132/33kV Grid Sub-Station | 2023-12-03 18:00 | 112
70 | Dohazari 132/33kV Grid Sub-Station | 2023-12-04 03:00 | 80
71 | GPH 230/33kV Grid Sub-Station | 2023-12-02 19:00 | 96
72 | Halishahar 132/33kV Grid Sub-Station | 2023-12-03 15:00 | 100.5
73 | Hathazari 230/132/33kV Grid Sub-Station | 2023-12-03 17:00 | 59
74 | Juldah 132/33kV Grid Sub-Station | 2023-12-28 18:00 | 33
75 | Kalurghat 132/33kV Grid Sub-Station | 2023-12-02 12:00 | 46
76 | Khagrachori 132/33kV Grid Sub-Station | 2023-12-19 18:00 | 24
77 | Khulshi 132/33kV Grid Sub-Station | 2023-12-05 17:00 | 159
78 | KSRM 132/33kV Grid Sub-Station | 2023-12-13 10:00 | 62
79 | Madunaghat 132/33kV Grid Sub-Station | 2023-12-24 19:30 | 40
80 | Matarbari 132/33kV Sub-Station | 2023-12-03 | 40
81 | Mirsorai 230/33kV Grid Sub-Station | 2023-12-13 11:00 | 8
82 | Modern Steel 132/11kV Grid Sub-Station | 2023-12-01 | 0
83 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-12-02 11:00 | 32
84 | Rangamati 132/33kV Grid Sub-Station | 2023-12-03 18:00 | 14
85 | Shahmirpur 132/33kV Grid Sub-Station | 2023-12-03 18:00 | 53
86 | Shikalbaha 132/33kV Sub-Station | 2023-12-05 11:00 | 26
87 | Sholosohor 132/33kV Grid Sub-Station | 2023-12-03 12:00 | 39
88 | SSM 132/33kV Grid Sub-Station | 2023-12-31 01:00 | 16
89 | TK chemical 132kV Grid Sub-Station | 2023-12-03 18:00 | 22.3
90 | Ashuganj 230/132/33kV Sub-Station | 2023-12-08 01:00 | 60
91 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-12-02 18:00 | 112
92 | Chandpur 132/33kV Grid Sub-Station | 2023-12-05 19:30 | 54
93 | Chauddagram 132/33kV Grid Sub-Station | 2023-12-29 13:00 | 45
94 | Chowmuhani 132/33kV Grid Sub-Station | 2023-12-04 18:30 | 144
95 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-12-06 18:00 | 120
96 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-12-04 18:00 | 132
97 | Daudkandi 132/33kV Grid Sub-Station | 2023-12-05 18:00 | 128
98 | Feni 132/33kV Grid Sub-Station | 2023-12-02 18:00 | 89
99 | Kachua 132/33kV Grid Sub-Station | 2023-12-09 19:00 | 51
100 | PHP 132/33kV Sub-Station | 2023-12-13 17:00 | 10
101 | Ramganj 132/33kV Grid Sub-Station | 2023-12-22 13:00 | 90
102 | Bhaluka 132/33kV Grid Sub-Station | 2023-12-27 18:30 | 117
103 | Jamalpur 132/33kV Grid Sub-Station | 2023-12-09 18:00 | 116
104 | Kishoreganj 132/33kV Grid Sub-Station | 2023-12-23 18:30 | 106
105 | Mymensingh 132/33kV Grid Sub-Station | 2023-12-29 13:00 | 166
106 | Netrakona 132/33kV Grid Sub-Station | 2023-12-27 18:00 | 102
107 | Sherpur 132/33kV Grid Sub-Station | 2023-12-23 18:00 | 106
108 | Tangail 132/33kV Grid Sub-Station | 2023-12-02 18:00 | 144
109 | Beanibazar 132/33kV Grid Sub-Station | 2023-12-06 18:00 | 44
110 | Chhatak 132/33kV Grid Sub-Station | 2023-12-30 18:30 | 26
111 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-12-23 18:00 | 26
112 | Kulaura 132/33kV Grid Sub-Station | 2023-12-21 18:00 | 32
113 | Shahjibazar 132/33kV Grid Sub-Station | 2023-12-30 21:00 | 95
114 | Sreemongol 132/33kV Grid Sub-Station | 2023-12-09 19:00 | 50
115 | Sunamganj 132/33kV Grid Sub-Station | 2023-12-17 18:00 | 40
116 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2023-12-27 10:00 | 18
117 | Sylhet 132/33kV Grid Sub-Station | 2023-12-02 18:30 | 99
118 | Bagerhat 132/33kV Grid Sub-Station | 2023-12-22 20:00 | 68
119 | Benapole 132/33kV Grid Sub-Station | 2023-12-23 18:00 | 58
120 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-12-19 18:00 | 40
121 | Chuadanga 132/33kV Grid Sub-Station | 2023-12-23 13:00 | 73
122 | Faridpur 132/33kV Grid Sub-Station | 2023-12-06 19:00 | 108
123 | Goalpara 132/33kV Grid Sub-Station | 2023-12-24 13:00 | 30
124 | Gollamari 132/33kV Grid Sub-Station | 2023-12-02 12:00 | 49
125 | Gopalganj 132/33kV Grid Sub-Station | 2023-12-31 18:30 | 73
126 | Jashore 132/33kV Grid Sub-Station | 2023-12-15 13:00 | 97
127 | Jhenaidah 132/33kV Grid Sub-Station | 2023-12-02 18:00 | 102
128 | Khulna (C) 132/33kV Grid Sub-Station | 2023-12-07 18:30 | 78
129 | Kushtia 132/33kV Grid Sub-Station | 2023-12-02 18:00 | 105
130 | Madaripur 132/33kV Grid Sub-Station | 2023-12-04 20:00 | 64
131 | Magura 132/33kV Grid Sub-Station | 2023-12-14 18:00 | 46
132 | Mongla 132/33kV Grid Sub-Station | 2023-12-13 09:00 | 34
133 | Narail 132/33kV Grid Sub-Station | 2023-12-19 18:30 | 39
134 | Noapara 132/33kV Grid Sub-Station | 2023-12-30 13:00 | 38
135 | Rajbari 132/33kV Grid Sub-Station | 2023-12-19 18:00 | 48
136 | Satkhira 132/33kV Grid Sub-Station | 2023-12-31 18:00 | 85
137 | Shariatpur 132/33kV Grid Sub-Station | 2023-12-02 20:00 | 56
138 | Barguna 132/33kV Grid Sub-Station | 2023-12-03 21:00 | 14
139 | Barishal 132/33kV Grid Sub-Station | 2023-12-28 13:00 | 84
140 | Barishal 230/132kV Grid Sub-Station | 2023-12-29 21:00 | 66
141 | Bhandaria 132/33kV Grid Sub-Station | 2023-12-06 20:00 | 35
142 | Borhanuddin 230/33kV Grid Sub-Station | 2023-12-25 20:00 | 48
143 | Patuakhali 132/33kV Grid Sub-Station | 2023-12-24 21:00 | 67
144 | Payra 400/132/33kV Grid Sub-Station | 2023-12-06 20:00 | 22
145 | Amnura 132/33kV Grid Sub-Station | 2023-12-30 13:00 | 35
146 | Bhangura 132/33kV Grid Sub-Station | 2023-12-03 18:00 | 21
147 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-12-06 19:30 | 52
148 | Bogura 132/33kV Grid Sub-Station | 2023-12-10 07:00 | 120
149 | Chapai 132/33kV Grid Sub-Station | 2023-12-27 12:00 | 53
150 | Ishurdi 132/33kV Grid Sub-Station | 2023-12-04 18:30 | 59
151 | Joypurhat 132/33kV Grid Sub-Station | 2023-12-20 18:00 | 44
152 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-12-02 18:00 | 56
153 | Naogaon 132/33kV Grid Sub-Station | 2023-12-25 18:00 | 98
154 | Natore 132/33kV Grid Sub-Station | 2023-12-27 18:00 | 96
155 | Niamatpur 132/33kV Grid Sub-Station | 2023-12-09 18:00 | 54
156 | Pabna 132/33kV Grid Sub-Station | 2023-12-27 18:30 | 85
157 | Rajshahi 132/33kV Grid Sub-Station | 2023-12-23 13:00 | 104
158 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-12-01 12:00 | 29
159 | Ruppur 132/11kV Grid Sub-Station | 2023-12-03 11:00 | 5
160 | Shahjadpur 132/33kV Grid Sub-Station | 2023-12-20 18:00 | 73
161 | Sirajganj 132/33kV Grid Sub-Station | 2023-12-05 18:30 | 97
162 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-12-05 18:00 | 52
163 | Jaldhaka 132/33kV Grid Sub-Station | 2023-12-10 18:00 | 56
164 | Kurigram 132/33kV Grid Sub-Station | 2023-12-15 18:30 | 63
165 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-12-12 18:00 | 40
166 | Mithapukur 132/33kV Grid Sub-Station | 2023-12-17 18:00 | 46
167 | Palashbari 132/33kV Grid Sub-Station | 2023-12-04 18:00 | 82
168 | Panchagarh 132/33kV Grid Sub-Station | 2023-12-20 18:00 | 49
169 | Purbasadipur 132/33kV Grid Sub-Station | 2023-12-23 18:00 | 106
170 | Rangpur 132/33kV Grid Sub-Station | 2023-12-06 18:00 | 110
171 | Saidpur 132/33kV Grid Sub-Station | 2023-12-27 18:00 | 92
172 | Thakurgaon 132/33kV Grid Sub-Station | 2023-12-23 18:00 | 81
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:December 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 4227.83 | 2023-12-04 | 18:00
Chattogram | 1198 | 2023-12-06 | 18:00
Cumilla | 908 | 2023-12-03 | 20:00
Mymensingh | 799 | 2023-12-02 | 18:00
Sylhet | 388 | 2023-12-04 | 18:00
Khulna | 1173.4 | 2023-12-02 | 18:00
Barishal | 305.6 | 2023-12-06 | 21:00
Rajshahi | 989.4 | 2023-12-03 | 18:00
Rangpur | 718 | 2023-12-20 | 18:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:December 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 410 | 2023-12-17 03:00 | 369 | 2023-12-14 01:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 421 | 2023-12-11 18:30 | 388 | 2023-12-20 12:00
3 | Bibiana 400/230kV Sub-Station | 400 | 428 | 2023-12-15 18:00 | 396 | 2023-12-23 16:00
4 | BIPTC | 400 | 414 | 2023-12-08 04:00 | 390 | 2023-12-15 13:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 416 | 2023-12-27 05:00 | 368 | 2023-12-05 11:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 421 | 2023-12-17 02:00 | 360 | 2023-12-26 12:00
7 | Payra 400kV Sub-Station | 400 | 421 | 2023-12-30 03:00 | 404 | 2023-12-26 12:00
8 | Rahanpur 400/132kV Grid Sub-Station | 400 | 422 | 2023-12-15 14:00 | 394 | 2023-12-02 05:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 418 | 2023-12-27 04:00 | 390 | 2023-12-26 11:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 243 | 2023-12-17 04:00 | 216 | 2023-12-26 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 237 | 2023-12-23 19:30 | 215 | 2023-12-03 11:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 239 | 2023-12-15 05:00 | 220 | 2023-12-01 12:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 228 | 2023-12-11 03:00 | 213 | 2023-12-28 08:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 245 | 2023-12-01 06:00 | 235 | 2023-12-20 13:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 238 | 2023-12-09 04:00 | 221 | 2023-12-12 12:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 236 | 2023-12-01 06:00 | 218 | 2023-12-28 12:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 241 | 2023-12-23 21:00 | 219 | 2023-12-21 11:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 242 | 2023-12-15 18:00 | 220 | 2023-12-02 17:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 249 | 2023-12-15 18:00 | 231 | 2023-12-02 15:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 247 | 2023-12-12 14:00 | 230 | 2023-12-01 01:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 237 | 2023-12-23 20:00 | 215 | 2023-12-21 11:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 243 | 2023-12-12 19:30 | 218 | 2023-12-26 12:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 243 | 2023-12-17 01:00 | 218 | 2023-12-26 12:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-12-23 21:00 | 216 | 2023-12-21 12:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 256 | 2023-12-30 01:00 | 223 | 2023-12-02 16:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 239 | 2023-12-09 04:00 | 220 | 2023-12-03 17:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 242 | 2023-12-17 03:00 | 216 | 2023-12-26 12:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 246 | 2023-12-29 03:00 | 224 | 2023-12-22 09:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 244 | 2023-12-16 17:00 | 219 | 2023-12-26 12:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 248 | 2023-12-11 21:00 | 226 | 2023-12-26 13:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 242 | 2023-12-23 19:00 | 218 | 2023-12-21 12:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 238 | 2023-12-15 05:00 | 217 | 2023-12-26 09:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 244 | 2023-12-17 04:00 | 220 | 2023-12-20 12:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 233 | 2023-12-27 18:30 | 215 | 2023-12-15 13:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 244 | 2023-12-17 03:00 | 218 | 2023-12-26 12:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 247 | 2023-12-17 05:00 | 221 | 2023-12-26 12:00
28 | Sirajgonj 230 kV Switching Station | 230 | 242 | 2023-12-15 04:00 | 224 | 2023-12-20 12:00
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-12-17 05:00 | 222 | 2023-12-20 12:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 242 | 2023-12-15 18:00 | 211 | 2023-12-21 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-17 04:00 | 123 | 2023-12-21 12:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-23 19:00 | 125 | 2023-12-20 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-23 19:30 | 124 | 2023-12-21 12:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-01 19:00 | 125 | 2023-12-26 09:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 143 | 2023-12-14 18:00 | 133 | 2023-12-04 12:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-08 15:00 | 120 | 2023-12-02 18:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-23 20:00 | 127 | 2023-12-02 16:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 144 | 2023-12-30 04:00 | 121 | 2023-12-21 12:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-06 04:00 | 120 | 2023-12-26 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-14 18:00 | 132 | 2023-12-02 18:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-11 19:00 | 129 | 2023-12-02 18:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-12 18:00 | 126 | 2023-12-20 12:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-11 18:30 | 123 | 2023-12-20 12:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-08 14:00 | 122 | 2023-12-20 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 142 | 2023-12-27 21:00 | 117 | 2023-12-03 11:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-15 02:00 | 126 | 2023-12-03 12:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-01 03:00 | 124 | 2023-12-02 18:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-15 17:00 | 124 | 2023-12-21 12:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-23 21:00 | 128 | 2023-12-02 19:30
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 143 | 2023-12-09 05:00 | 130 | 2023-12-27 12:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-01 05:00 | 125 | 2023-12-26 09:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 131 | 2023-12-16 17:00 | 115 | 2023-12-21 12:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-01 06:00 | 122 | 2023-12-28 12:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-08 05:00 | 125 | 2023-12-28 12:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-14 22:00 | 122 | 2023-12-24 12:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 143 | 2023-12-17 02:00 | 125 | 2023-12-26 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 144 | 2023-12-05 12:00 | 116 | 2023-12-22 12:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-23 19:00 | 126 | 2023-12-21 12:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-01 19:00 | 129 | 2023-12-25 12:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 140 | 2023-12-08 10:00 | 125 | 2023-12-20 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-24 18:00 | 123 | 2023-12-05
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-14 22:00 | 126 | 2023-12-03 11:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-15 18:00 | 115 | 2023-12-22 12:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-07 03:00 | 125 | 2023-12-04 13:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 133 | 2023-12-17 09:00 | 115 | 2023-12-02 18:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-15 18:00 | 116 | 2023-12-07 17:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-12 19:00 | 124 | 2023-12-02 16:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-17 03:00 | 124 | 2023-12-26 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 144 | 2023-12-29 03:00 | 121 | 2023-12-11 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 140.7 | 2023-12-30 04:00 | 125 | 2023-12-21 13:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-23 19:00 | 125 | 2023-12-21 11:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-16 06:00 | 125 | 2023-12-26 12:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-27 04:00 | 126 | 2023-12-20 12:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-23 20:00 | 124 | 2023-12-20 12:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-09 04:00 | 124 | 2023-12-04 11:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-09 03:00 | 125 | 2023-12-20 12:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-09 03:00 | 124 | 2023-12-26 12:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-16 17:00 | 125 | 2023-12-03 12:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-23 19:00 | 125 | 2023-12-20 12:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 140 | 2023-12-16 17:00 | 123 | 2023-12-05 21:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 141 | 2023-12-15 18:00 | 126 | 2023-12-20 12:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-30 04:00 | 131 | 2023-12-14 08:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-05 17:00 | 114 | 2023-12-11 09:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-01 18:30 | 116 | 2023-12-01 08:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-01 04:00 | 124 | 2023-12-26 13:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-20 06:00 | 128 | 2023-12-26 09:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 144 | 2023-12-12 17:00 | 130 | 2023-12-04 12:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-10 05:00 | 119 | 2023-12-28 08:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-23 20:00 | 127 | 2023-12-02 16:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-15 18:00 | 119 | 2023-12-09 15:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-15 18:00 | 119 | 2023-12-22 12:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-29 17:00 | 124 | 2023-12-20 12:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-23 23:00 | 126 | 2023-12-03 11:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-28 06:00 | 121 | 2023-12-20 12:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-02 05:00 | 120 | 2023-12-21 13:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-23 20:00 | 125 | 2023-12-20 12:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-11 04:00 | 124 | 2023-12-18 12:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-23 20:00 | 124 | 2023-12-21 11:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-14 21:00 | 127 | 2023-12-04 12:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 143 | 2023-12-17 02:00 | 118 | 2023-12-21 09:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-23 19:00 | 125 | 2023-12-20 12:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-14 22:00 | 128 | 2023-12-27 11:00
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-03 19:30 | 115 | 2023-12-11 09:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-01 06:00 | 126 | 2023-12-26 11:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 143 | 2023-12-30 04:00 | 121 | 2023-12-26 12:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 134 | 2023-12-06 20:00 | 117 | 2023-12-11 09:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-11 18:30 | 124 | 2023-12-21 11:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-11 04:00 | 126 | 2023-12-26 10:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-24 02:00 | 122 | 2023-12-26 12:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-23 20:00 | 126 | 2023-12-20 12:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-08 14:00 | 127 | 2023-12-04 12:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-01 05:00 | 124 | 2023-12-28 08:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-15 18:00 | 121 | 2023-12-17 11:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-08 14:00 | 121 | 2023-12-21 13:00
85 | Matarbari 132/33kV Sub-Station | 132 | 136 | 2023-12-26 15:00 | 115 | 2023-12-07 16:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-08 14:00 | 126 | 2023-12-21 12:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-08 17:00 | 121 | 2023-12-21 11:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-09 02:00 | 122 | 2023-12-20 12:00
89 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 141 | 2023-12-09 04:00 | 120 | 2023-12-21 09:00
90 | Mithapukur 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-04 18:30 | 120 | 2023-12-28 12:00
91 | MI_Cement 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-12 18:30 | 125 | 2023-12-21 12:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 141 | 2023-12-23 19:30 | 126 | 2023-12-20 12:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-17 03:00 | 124 | 2023-12-21 14:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-08 18:00 | 121 | 2023-12-02 18:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-06 04:00 | 120 | 2023-12-26 12:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-05 18:30 | 126 | 2023-12-21 12:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-09 03:00 | 121 | 2023-12-04 07:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-08 04:00 | 120 | 2023-12-28 12:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-16 03:00 | 126 | 2023-12-03 13:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-16 18:30 | 115 | 2023-12-24 18:30
101 | Natore 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-09 04:00 | 127 | 2023-12-27 08:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-28 03:00 | 122 | 2023-12-26 12:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-09 04:00 | 120 | 2023-12-07 08:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-08 14:00 | 122 | 2023-12-21 11:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-01 04:00 | 118 | 2023-12-27 08:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-09 04:00 | 124 | 2023-12-17 12:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-17 03:00 | 128 | 2023-12-27 13:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-25 19:00 | 119 | 2023-12-28 12:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-10 19:30 | 113 | 2023-12-13 09:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-14 18:00 | 131 | 2023-12-02 21:00
111 | PHP 132/33kV Sub-Station | 132 | 140 | 2023-12-23 20:00 | 122 | 2023-12-21 12:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-17 02:00 | 122 | 2023-12-27 17:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 143 | 2023-12-17 02:00 | 121 | 2023-12-21 12:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-05 17:00 | 115 | 2023-12-05 08:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 140 | 2023-12-16 17:00 | 124 | 2023-12-22 19:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-06 08:00 | 123 | 2023-12-18 12:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-12 18:30 | 118 | 2023-12-21 13:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-01 06:00 | 126 | 2023-12-26 11:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-12 19:30 | 116 | 2023-12-29 13:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-23 19:00 | 126 | 2023-12-21 11:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-10 19:30 | 118 | 2023-12-13 09:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 141 | 2023-12-04 06:00 | 128 | 2023-12-18 01:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-04 19:00 | 116 | 2023-12-29 07:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 136 | 2023-12-09 04:00 | 122 | 2023-12-13 13:00
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 143 | 2023-12-17 03:00 | 125 | 2023-12-26 12:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-09 09:00 | 120 | 2023-12-21 12:00
127 | SevenRings 132/11kV Sub-Station | 132 | 146 | 2023-12-17 03:00 | 133 | 2023-12-21 12:00
128 | ShahCement 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-08 10:00 | 125 | 2023-12-20 12:00
129 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 144 | 2023-12-01 03:00 | 133 | 2023-12-27 12:00
130 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-15 | 126 | 2023-12-03 12:00
131 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-12-23 19:30 | 126 | 2023-12-02 16:00
132 | Shariatpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-08 01:00 | 126 | 2023-12-21 13:00
133 | Sherpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-02 18:00 | 114 | 2023-12-01 08:00
134 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-12 18:30 | 125 | 2023-12-21 12:00
135 | Sholosohor 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-23 19:30 | 125 | 2023-12-20 12:00
136 | Shyampur 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-08 18:00 | 126 | 2023-12-21 11:00
137 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-08 14:00 | 126 | 2023-12-20 12:00
138 | Sirajganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-01 06:00 | 118 | 2023-12-28 12:00
139 | Sonargaon 132/33kV Grid Sub-Station | 132 | 140 | 2023-12-11 18:00 | 122 | 2023-12-21 12:00
140 | Sreemongol 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-15 | 127 | 2023-12-03 11:00
141 | Srinagar 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-30 03:00 | 121 | 2023-12-26 12:00
142 | SSM 132/33kV Grid Sub-Station | 132 | 145 | 2023-12-24 20:00 | 130 | 2023-12-03 12:00
143 | Sunamganj 132/33kV Grid Sub-Station | 132 | 135 | 2023-12-15 | 125 | 2023-12-03 11:00
144 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 137 | 2023-12-16 06:00 | 127 | 2023-12-03 12:00
145 | Sylhet 132/33kV Grid Sub-Station | 132 | 137 | 2023-12-14 22:00 | 128 | 2023-12-03 11:00
146 | Tangail 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-09 04:00 | 123 | 2023-12-20 12:00
147 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 139 | 2023-12-05 18:30 | 113 | 2023-12-05 08:00
148 | TK chemical 132kV Grid Sub-Station | 132 | 142 | 2023-12-23 19:00 | 127 | 2023-12-03 11:00
149 | Ullon 132/33kV Grid Sub-Station | 132 | 138 | 2023-12-22 12:00 | 124 | 2023-12-04 12:00
150 | Uttara 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-09 08:00 | 123 | 2023-12-20 12:00
151 | UttaraNew 132/33kV Grid Sub-Station | 132 | 143 | 2023-12-17 04:00 | 120 | 2023-12-21 12:00
152 | Zigatola 132/33kV Grid Sub-Station | 132 | 142 | 2023-12-28 05:00 | 122 | 2023-12-21 13:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:December 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 266 | 475.3862 | 2023-12-06 10:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 428 | 435.2298 | 2023-12-26 12:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -292 | 383.1031 | 2023-12-23 13:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -408 | 476.9413 | 2023-12-26 15:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -268 | 268.1194 | 2023-12-11 18:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -269 | 271.1402 | 2023-12-10 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 268 | 279.4011 | 2023-12-06 11:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 43 | 396.3395 | 2023-12-28 08:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -332.36 | 332.913 | 2023-12-21 08:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -453.54 | 453.7315 | 2023-12-20 07:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 249 | 250.6831 | 2023-12-20 11:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -120 | 120.9339 | 2023-12-02 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -120 | 120.9339 | 2023-12-02 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -120 | 120.9339 | 2023-12-02 19:30
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 266 | 376.1808 | 2023-12-27 06:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 319 | 322.2996 | 2023-12-30 18:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -55 | 55.4437 | 2023-12-03 21:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -55 | 55.4437 | 2023-12-03 21:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 127 | 127.0039 | 2023-12-17 22:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 65 | 188.5577 | 2023-12-08 19:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 240 | 250 | 2023-12-27 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 226 | 234.3502 | 2023-12-24 18:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 153 | 157.4103 | 2023-12-05 09:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 151 | 158.1455 | 2023-12-02 11:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 153 | 157.4103 | 2023-12-03 10:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 40 | 139.8428 | 2023-12-06 07:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 164 | 203.2142 | 2023-12-21 07:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 119 | 127.2242 | 2023-12-01 18:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 105 | 120.9339 | 2023-12-06 10:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 189 | 189.9526 | 2023-12-17 15:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 134 | 172.1046 | 2023-12-16 01:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 207 | 208.5042 | 2023-12-08 03:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 160 | 226.2742 | 2023-12-25 08:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 167 | 167.6723 | 2023-12-07 09:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -84 | 104.4031 | 2023-12-06 18:30
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -76 | 107.4802 | 2023-12-09 20:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 218 | 219.4288 | 2023-12-31 09:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 218 | 219.4288 | 2023-12-31 09:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 158 | 301.6836 | 2023-12-23 07:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 197 | 203.0025 | 2023-12-22 21:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 145 | 260.1557 | 2023-12-24 21:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 162 | 165.7377 | 2023-12-04 17:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 105 | 105 | 2023-12-02 08:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 105 | 105 | 2023-12-02 08:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 144 | 151.4761 | 2023-12-23 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 0 | 0 | 2023-12-01
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 144 | 151.4761 | 2023-12-23 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 88 | 96.2549 | 2023-12-23 13:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 72 | 80.4984 | 2023-12-13 15:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 73 | 101.8332 | 2023-12-31 14:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 109 | 109.4578 | 2023-12-02 18:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 109 | 109.4578 | 2023-12-02 18:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 109 | 109.4578 | 2023-12-02 18:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 109 | 109.4578 | 2023-12-02 18:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 82 | 111.8034 | 2023-12-27 08:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 80 | 106.9626 | 2023-12-19 18:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 82 | 111.8034 | 2023-12-27 08:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -157 | 162.7821 | 2023-12-20 13:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -157 | 162.7821 | 2023-12-20 13:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 114 | 121.4907 | 2023-12-05 10:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 139 | 145.2067 | 2023-12-06 19:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2023-12-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 139 | 145.2067 | 2023-12-06 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -103 | 103.0437 | 2023-12-02 18:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -103 | 103.0437 | 2023-12-02 18:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -132 | 132.0341 | 2023-12-02 18:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 134 | 139.56 | 2023-12-24 09:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 186 | 195.438 | 2023-12-02 11:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -114 | 115.9181 | 2023-12-01 20:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -115 | 116.7262 | 2023-12-01 20:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2023-12-01 12:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1.4142 | 2023-12-09 03:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 209 | 209.4684 | 2023-12-08 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 295 | 305.1377 | 2023-12-03 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 209 | 209.4684 | 2023-12-08 12:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 226 | 251.7876 | 2023-12-02 18:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 226 | 251.7876 | 2023-12-02 18:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 128 | 204.9 | 2023-12-28 09:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 138 | 155.6535 | 2023-12-30 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 85 | 269.7425 | 2023-12-20 18:30
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 161 | 165.1969 | 2023-12-23 11:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 222.5 | 225.236 | 2023-12-06 17:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 213 | 217.297 | 2023-12-04 14:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 210 | 210.0595 | 2023-12-15 11:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 198 | 213.5509 | 2023-12-05 12:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 220 | 220.0205 | 2023-12-22 10:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: December 2023 |  |  |  |  | (For Evening Peak) | [9 empty] | Month: December 2023 |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  | Areawise load shed (MW) | [8 empty] | Remarks | Date | Generation | Demand (Gen End) |  | Areawise load shed (MW) | [9 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-12-01 | 9203 | 9203 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-01 | 8306 | 8306 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-02 | 10636 | 10636 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-02 | 8833 | 8833 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-03 | 10876 | 10876 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-03 | 9413 | 9413 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-04 | 10921 | 10921 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-04 | 9415 | 9415 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-05 | 10838 | 10838 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-05 | 9039 | 9039 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-06 | 10827 | 10827 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-06 | 9153 | 9153 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-07 | 9839 | 9839 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-07 | 9214 | 9214 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-08 | 8619 | 8619 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-08 | 8019 | 8019 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-09 | 9849 | 9849 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-09 | 8067 | 8067 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-10 | 9773 | 9773 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-10 | 8640 | 8640 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-11 | 9966 | 9966 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-11 | 8635 | 8635 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-12 | 10074 | 10074 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-12 | 8827 | 8827 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-13 | 10083 | 10083 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-13 | 9003 | 9003 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-14 | 9911 | 9911 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-14 | 8870 | 8870 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-15 | 8466 | 8466 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-15 | 7625 | 7625 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-16 | 8192 | 8192 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-16 | 7199 | 7199 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-17 | 9648 | 9648 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-17 | 8567 | 8567 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-18 | 10111 | 10111 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-18 | 8756 | 8756 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-19 | 10180 | 10180 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-19 | 8790 | 8790 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-20 | 10093 | 10093 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-20 | 9048 | 9048 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-21 | 10145 | 10145 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-21 | 9235 | 9235 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-22 | 8694 | 8694 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-22 | 8173 | 8173 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-23 | 9910 | 9910 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-23 | 8475 | 8475 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-24 | 10203 | 10203 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-24 | 9141 | 9141 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-25 | 9985 | 9985 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-25 | 9015 | 9015 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-26 | 10225 | 10225 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-26 | 9194 | 9194 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-27 | 10396 | 10396 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-27 | 9540 | 9540 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-28 | 10487 | 10487 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-12-28 | 9618 | 9618 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-12-29 | 8978 | 8978 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-12-29 | 8465 | 8465 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-12-30 | 10262 | 10262 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-12-30 | 8923 | 8923 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-12-31 | 10725 | 10725 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-12-31 | 9608 | 9608 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1638
0

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:December 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10921 | 2023-12-04 | 19:00
2 | Maximum Day Peak Genaration | MW | 9618 | 2023-12-28 | 12:00
3 | Maximum Evening Peak Demand | MW | 10921 | 2023-12-30 | 19:00
4 | Minimum Generation | MW | 5635 | 2023-12-17 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9939.1935 | - | -
6 | Average of the daily day peak Genaration | MW | 8800.1935 | - | -
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0 | - | -
11 | Total Generation | MkWh | 4990.7399 | - | -
12 | Total Generation by BPDB | MkWh | 1616.4983 | % of total Gen. | 32.39%
13 | Total Generation by IPP | MkWh | 1164.2162 | '' | 23.33%
14 | A) Total Generation by Generation Companies | MkWh | 1243.3374 | '' | 24.91%
| B) Total Generation by REB | MkWh | 75.7392 | " | 1.518%
| C) Total Generation by RENTAL | MkWh | 78.4238 | " | 1.571%
| D) Total Imported from India (BIPTC) | MkWh | 413.3871 | " | 8.283%
| E) Total Imported from Tripura, India (A.C) | MkWh | 399.1379 | " | 7.998%
15 | Fuel wise Generation.
| A) Gas | MkWh | 2491.2152 | % of total Gen. | 49.92%
| B) Oil | MkWh | 297.23 | '' | 5.956%
| C) Hydro | MkWh | 49.8754 | '' | 0.9994%
| D) Solar | MkWh | 45.5568 | '' | 0.9128%
| E) Coal | MkWh | 1638.1916 | '' | 32.82%
| F) BIPTC (Import from India) | MkWh | 413.3871 | '' | 8.283%
| G) A.C (Import from Tripura, India) | MkWh | 52.8346 | '' | 1.059%
| H) Wind | MkWh | 2.4408 | '' | 0.04891%
16 | Maximun of the daily total Generation . | MkWh | 298.3798 | 2023-12-11
17 | Monthly Load factor | % | 74.6495 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 22291.6663 | - | -
| A) Gas | M.Taka | 3176.4171 | - | -
| B) Liquid fuel | M.Taka | 4830.6911 | - | -
| C) Coal | M.Taka | 11499.8844 | - | -
| D) BIPTC (Import from India) | M.Taka | 2351.5122 | - | -
| E) Tripura(Import from India) | M.Taka | 433.1615 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 963.4589 | 2023-12-14
| A) Gas | M.Taka | 127.7966 | 2023-12-17
| B) Liquid fuel | M.Taka | 431.8468 | 2023-12-14
| C) Coal | M.Taka | 519.2072 | 2023-12-24
| D) BIPTC (Import from India) | M.Taka | 90.0202 | 2023-12-03
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.4666
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 4.556
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 103.1 | 31/12/2023 | 06:00
b) | Actual | FT (MSL) | 93.5 | 31/12/2023 | 6:00
22 | Peak Genaration of December 2022 | MW | 10346 | 2022-12-01 | 18:00
23 | Peak Demand of December 2022 | MW | 10550 | 2022-12-31 | 19:00
24 | Maximum peak Generation recorded upto 31/12/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/12/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 31/12/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:December 2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [11 empty] | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ |  |  |  | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 |  |  |  |  | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | [21 empty] | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | [5 empty] | √ | √ | √ | √ | √ | √ | [12 empty] | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | [6 empty] | √ | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [5 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable |  |  |  | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | [10 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [10 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  |  |  | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable |  |  |  |  | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable |  |  | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD