## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2024-02-08 | Thursday
|  | Date (day): | 2024-02-08 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11055.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12615 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-07 | 2024-02-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 190 | 200 | 200 |  |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 40 | 0 | 280 | 400 | 12 |  |  |  | 2024-02-12
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 100 | 43 | 85 | 100 | 0 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 80 | 80 | 80 | 80 | 22 |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 25 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 4 | 0 | 0 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 99 | 62 | 100 | 100 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 67 | 8 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  | 335 | Under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 41 | 91 | 40 | 91 |  | 11 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 149 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 41 | 41 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 22 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 75 | 82 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 17 | 50 | 99 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 51 | 17 | 53 | 51 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 17 | 35 | 127 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 340 | 300 | 370 | 370 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1716 | 1874 | 2038 | 2651 | 1550 | 1345
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 205 | 204 | 205 | 205 | 20
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 16 | 8 | 16 | 82 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 68 | 51 | 68 | 34 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 17 | 18 | 18 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 20 | 15 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 105 | 50 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 0 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 145 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 0 | 0 | 0 | 0 | 1224 |  | under maint.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 3 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 0 | 566 | 156 | 570 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 552 | 1327 | 716 | 1335 | 2673 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 144 | 152 | 150 | 150 |  | 71 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 280 | 360 | 360 |  |  | FGMO
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 290 | 360 | 360 | 0 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 13 | 15 | 6 | 25 | 125 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 33 | 40 | 40 |  | 12 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 16 | 16 |  | 6 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 9 | 9
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 130 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 16 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 30 | 57 | 9 | 57 | 56 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 37 | 0 | 37 | 78 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1247 | 1252 | 1338 | 1455 | 1073 | 307
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 32 | 36 | 35 | 75 | 127 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 67 | 56 | 66 | 134 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 9 | 9 | 106 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 2 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 155 | 118 | 153.6 | 156 | 127 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 51 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 50 | 50
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 0 | 30 | 30
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 145 | 145 | 150 | 150 |  | 81 | ST under maint
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 25 | 24 | 24
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 320 | 320 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 135 | 150 | 315 | 315 |  | 400 | ST under maint.
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 390 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1324 | 1281 | 1606 | 1616 | 0 | 988
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 799 | 924 | 924
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 8 | 53 | 15 | 53
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 56 | 50 | 60 | 84 |  | 25 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 75 | 17 | 75 |  | 30 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 61 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 357 | 359 | 360 | 360 |  | 330 | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1405 | 1336 | 1476 | 1504 | 1244 | 385
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 4 | 6 | 10 | 10 |  | 30 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 125 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1200 | 1000 | 1200 | 1240 |  | 4
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 110 | 115 | 115 |  |  | GT-2 Under maint
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 54 | 17 | 54 | 96 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 200 | 200 | 200 | 107 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1716 | 1516 | 1672 | 1765 | 297 | 98
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 25 | 25 | 27 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 15 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 14 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 25 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 49 | 48 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 173 | 220 | 220
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 0 | 0
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 4 | 32 | 25 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 8 | 8
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 45 | 91 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 0 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 752 | 1020 | 1260 | 1260
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1463 | 1907 | 1712 | 1854 | 1040 | 78
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 35 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 70 | 0 | 74 | 41 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 172 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 386 | 275 | 344 | 279 | 244 | 189
| Total |  |  |  |  | 26504 | 25481 | 9964 | 10886 | 11055.6 | 12615 | 8248 | 3720
A. |  | 2024-02-07 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10886 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7294 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10980 | MW
3 | Day peak Generation : |  |  | 9964 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10488.37 | MW
4 | Evening peak Generation : |  |  | 10886 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 90 | MW
5 | Total Energy Generation : |  | 222.4463 | MKWHr | By Solar | 2.3489 | MKWHr
| By Gas : | 103.9836 | MKWHr |  | By Oil: | 22.2067 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 70.341 | MKWHr |  | By Hydro: | 1.1128 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0384 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8248 | MW | Dhaka | 3851.37 | 3843.37 |  | 8 |  | 18:00 |  | 85.95
|  |  | For Plants S/D or M/C prob = |  |  | 3720 | MW | Chittagong | 1045 | 1045 |  | 0 |  | 19:00 |  | 89.77
|  |  | Total = |  |  | 11968 | MW | Khulna | 1219 | 1219 |  | 0 |  | 19:30 |  | 86.905
7 | Total Gas Supplied : |  |  | 849.76 | MMCFD |  |  | Rajshahi | 1099 | 1099 |  | 0 |  | 20:00 |  | 79.265
8 | Fuel Cost : | i) Gas : | Taka | 299483043.604 | ii) Oil : | Taka | 408911718.92 | Comilla | 897 | 897 |  | 0 |  | 21:00 |  | 89.77
|  | iii) Coal : | Taka | 469174515.05 | Total | Taka | 1177569277.574 | Mymensingh | 945 | 863 |  | 82 |  | 22:00 |  | 120.33
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 364 | 364 |  | 0 |  | 23:00 |  | 108.87
| ii) During Peak Demand : |  |  | 1170 | MW (W to E) at | 19:00 | hrs | Barisal | 278 | 278 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 950 | MW at | 5:00 | hrs | Rangpur | 790 | 790 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 26.3°C |  |  | Total | 10488.37 | 10398.37 |  | 90
B. |  | 2024-02-08 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 30.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12615 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
4 | Reserve(Generation end) |  |  |  | 1415 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 228.8627 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7297 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.2276 | MKWHr. | ii) HVDC Flow at Peak Time |  | 799 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1872 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.66 |  | (b) Today: | 86.55 |  | (c) Rule Curve: |  | 96.02
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-02-07 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 291 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 0 | 0 | 0 | 280 | 300 | 134 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 0 | 13 | 9 | 33 | 12 | 94 | 74 | 0 | 0 | 0 | 43 | 40 | 40 | 0 | 120 | 0 | 60 | 0 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 568 | 0 | 96 |  | 717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 762 | 0 | 0 |  | 4440 | 3829 | 8269 | 2603 | 717 | 1547 | 0 | 29 | 3233 | 46 | 0 | 0 | 94 | 0 | 0 | 0 | 86.71
2:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 271 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 0 | 0 | 0 | 280 | 300 | 151 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 13 | 9 | 33 | 12 | 100 | 86 | 0 | 0 | 0 | 43 | 40 | 11 | 0 | 120 | 0 | 60 | 0 | 0 | 145 | 0 | 0 | 10 | 290 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 569 | 0 | 96 |  | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 150 | 764 | 0 | 0 |  | 4255 | 3626 | 7881 | 2600 | 528 | 1398 | 0 | 0 | 3209 | 46 | 0 | 0 | 100 | 0 | 0 | 0 | 86.7
3:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 248 | 0 |  | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 280 | 300 | 155 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 13 | 9 | 33 | 12 | 96 | 86 | 0 | 0 | 0 | 43 | 40 | 10 | 0 | 120 | 0 | 60 | 0 | 0 | 145 | 0 | 0 | 10 | 280 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 1 | 569 | 0 | 96 |  | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 674 | 0 | 0 |  | 4208 | 3329 | 7537 | 2533 | 528 | 1342 | 0 | 0 | 2991 | 46 | 0 | 0 | 96 | 0 | 1 | 0 | 86.69
4:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 212 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 320 | 305 | 150 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 13 | 9 | 8 | 12 | 90 | 96 | 0 | 0 | 0 | 43 | 40 | 10 | 0 | 120 | 0 | 60 | 0 | 0 | 145 | 0 | 0 | 10 | 300 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 3 | 396 | 0 | 97 |  | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 638 | 0 | 0 |  | 4096 | 3225 | 7321 | 2597 | 528 | 1343 | 0 | 0 | 2714 | 46 | 0 | 0 | 90 | 0 | 3 | 0 | 86.68
5:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 202 | 0 |  | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 285 | 300 | 152 | 0 | 0 | 5 | 0 | 0 | 10 | 0 | 0 | 0 | 13 | 9 | 8 | 12 | 96 | 98 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 120 | 0 | 60 | 0 | 0 | 145 | 0 | 0 | 10 | 310 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 404 | 0 | 98 |  | 529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 150 | 631 | 0 | 0 |  | 4081 | 3213 | 7294 | 2570 | 529 | 1342 | 0 | 0 | 2711 | 46 | 0 | 0 | 96 | 0 | 0 | 0 | 86.67
6:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 228 | 0 |  | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37 | 0 | 0 | 0 | 310 | 360 | 152 | 0 | 0 | 5 | 0 | 0 | 23 | 0 | 0 | 0 | 13 | 9 | 8 | 12 | 96 | 98 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 120 | 0 | 60 | 0 | 0 | 145 | 0 | 0 | 10 | 310 | 23 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 403 | 0 | 98 |  | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 150 | 745 | 0 | 0 |  | 4234 | 3415 | 7649 | 2706 | 528 | 1521 | 0 | 5 | 2747 | 46 | 0 | 0 | 96 | 0 | 0 | 0 | 86.66
7:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 298 | 0 |  | 0 | 450 | 0 | 1 | 25 | 0 | 0 | 0 | 103 | 8 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 1 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 15 | 19 | 0 | 0 | 0 | 300 | 290 | 153 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 0 | 13 | 9 | 33 | 12 | 100 | 72 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 59 | 0 | 0 | 145 | 0 | 0 | 10 | 310 | 23 | 0 | 0 | 25 | 0 | 0 | 56 | 0 | 9 | 1 | 0 | 10 | 2 | 135 | 9 | 17 | 0 | 0 | 16 | 0 | 6 | 52 | 0 | 0 | 320 | 7 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 274 | 0 | 320 |  | 811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 414 | 6 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 850 | 91 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 358 | 0 | 150 | 759 | 3 | 0 |  | 4598 | 3932 | 8530 | 2848 | 811 | 1837 | 0 | 288 | 2561 | 46 | 0 | 33 | 100 | 6 | 0 | 57 | 86.65
8:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 280 | 0 |  | 0 | 450 | 0 | 36 | 80 | 0 | 0 | 0 | 102 | 50 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 31 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 | 6 | 15 | 7 | 0 | 0 | 0 | 325 | 315 | 138 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 8 | 13 | 9 | 33 | 12 | 114 | 68 | 0 | 0 | 1 | 43 | 40 | 0 | 0 | 163 | 0 | 59 | 0 | 0 | 145 | 0 | 0 | 10 | 320 | 23 | 0 | 0 | 45 | 0 | 0 | 56 | 0 | 17 | 4 | 0 | 17 | 5 | 134 | 9 | 17 | 0 | 1 | 16 | 0 | 17 | 98 | 9 | 0 | 320 | 17 | 12 | 0 | 17 | 0 | 0 | 6 | 0 | 0 | 0 | 17 | 0 | 0 | 1 | 158 | 0 | 385 |  | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 414 | 17 | 0 | 1 | 0 | 6 | 0 | 0 | 0 | 1050 | 90 | 0 | 17 | 1 | 14 | 0 | 0 | 0 | 359 | 2 | 150 | 761 | 39 | 0 |  | 4887 | 4381 | 9268 | 2874 | 900 | 1898 | 0 | 668 | 2648 | 46 | 0 | 39 | 114 | 80 | 1 | 106.96 | 86.64
9:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 230 | 0 |  | 0 | 450 | 0 | 85 | 80 | 0 | 0 | 0 | 101 | 68 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 25 | 28 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 5 | 15 | 6 | 0 | 0 | 0 | 280 | 270 | 143 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 6 | 8 | 13 | 9 | 33 | 12 | 118 | 68 | 0 | 0 | 1 | 42 | 40 | 0 | 0 | 130 | 0 | 59 | 0 | 0 | 145 | 0 | 0 | 10 | 300 | 23 | 0 | 0 | 62 | 0 | 0 | 56 | 0 | 17 | 9 | 0 | 17 | 6 | 135 | 9 | 17 | 0 | 1 | 49 | 4 | 17 | 98 | 9 | 0 | 320 | 17 | 28 | 0 | 17 | 0 | 7 | 15 | 0 | 0 | 0 | 17 | 0 | 0 | 1 | 6 | 0 | 370 |  | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 360 | 17 | 0 | 26 | 0 | 6 | 0 | 0 | 0 | 1230 | 110 | 0 | 17 | 2 | 32 | 0 | 0 | 0 | 356 | 16 | 150 | 758 | 56 | 0 |  | 4741 | 4522 | 9263 | 2736 | 798 | 1795 | 0 | 849 | 2670 | 46 | 0 | 90 | 118 | 160 | 1 | 512.835 | 86.63
10:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 47 | 0 |  | 0 | 450 | 0 | 93 | 80 | 0 | 0 | 0 | 62 | 68 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 28 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 6 | 18 | 6 | 0 | 0 | 0 | 315 | 270 | 155 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 41 | 8 | 13 | 9 | 25 | 12 | 118 | 32 | 0 | 0 | 2 | 43 | 40 | 0 | 0 | 130 | 0 | 59 | 0 | 0 | 145 | 0 | 0 | 10 | 290 | 23 | 0 | 0 | 72 | 0 | 0 | 57 | 0 | 17 | 14 | 0 | 17 | 6 | 135 | 9 | 17 | 17 | 3 | 49 | 17 | 17 | 98 | 9 | 0 | 400 | 17 | 42 | 0 | 17 | 0 | 17 | 23 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 370 |  | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 42 | 0 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 1 | 0 | 1244 | 110 | 0 | 17 | 4 | 47 | 0 | 0 | 0 | 358 | 11 | 150 | 759 | 130 | 0 |  | 4736 | 4669 | 9405 | 2603 | 798 | 1839 | 0 | 918 | 2681 | 46 | 0 | 125 | 118 | 277 | 0 | 377.225 | 86.63
11:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 27 | 0 |  | 0 | 450 | 0 | 99 | 80 | 3 | 0 | 0 | 100 | 67 | 41 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 26 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 6 | 18 | 4 | 0 | 0 | 0 | 310 | 270 | 142 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 33 | 8 | 13 | 9 | 25 | 12 | 128 | 32 | 0 | 0 | 1 | 43 | 40 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 145 | 0 | 0 | 10 | 315 | 23 | 0 | 0 | 65 | 0 | 0 | 58 | 0 | 17 | 17 | 25 | 17 | 10 | 135 | 9 | 17 | 17 | 2 | 50 | 17 | 17 | 98 | 9 | 12 | 400 | 17 | 51 | 0 | 17 | 0 | 17 | 29 | 0 | 0 | 0 | 17 | 0 | 0 | 1 | 0 | 0 | 360 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 17 | 0 | 37 | 0 | 6 | 0 | 1 | 0 | 1210 | 110 | 0 | 17 | 5 | 70 | 0 | 0 | 0 | 357 | 29 | 150 | 757 | 124 | 0 |  | 4826 | 4750 | 9576 | 2569 | 907 | 1885 | 0 | 914 | 2644 | 46 | 0 | 153 | 128 | 329 | 1 | 405 | 86.62
12:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 40 | 0 |  | 0 | 450 | 0 | 100 | 80 | 15 | 0 | 0 | 99 | 67 | 41 | 32 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 26 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 8 | 51 | 0 | 0 | 6 | 18 | 4 | 0 | 0 | 0 | 350 | 290 | 144 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 41 | 8 | 13 | 9 | 25 | 16 | 128 | 32 | 0 | 0 | 2 | 43 | 40 | 0 | 0 | 163 | 0 | 56 | 0 | 0 | 145 | 0 | 0 | 10 | 310 | 22 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 17 | 17 | 25 | 17 | 13 | 135 | 9 | 17 | 17 | 4 | 50 | 17 | 17 | 98 | 30 | 25 | 400 | 17 | 54 | 17 | 17 | 0 | 17 | 20 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 340 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 28 | 0 | 0 | 0 | 4 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1200 | 220 | 0 | 17 | 5 | 61 | 0 | 0 | 0 | 357 | 36 | 150 | 752 | 172 | 0 |  | 4994 | 4970 | 9964 | 2652 | 906 | 1970 | 0 | 998 | 2629 | 46 | 0 | 262 | 128 | 373 | 0 | 416.38 | 86.62
13:00 | 0 | 0 | 134 | 0 | 0 | 12 | 0 | 61 | 0 |  | 0 | 450 | 0 | 63 | 80 | 15 | 0 | 0 | 101 | 61 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 26 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 8 | 51 | 0 | 0 | 6 | 18 | 3 | 0 | 0 | 0 | 280 | 290 | 147 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 42 | 8 | 13 | 9 | 33 | 10 | 124 | 27 | 0 | 0 | 2 | 43 | 40 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 142 | 0 | 0 | 10 | 305 | 22 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 17 | 16 | 25 | 17 | 11 | 135 | 9 | 17 | 17 | 3 | 57 | 17 | 17 | 98 | 38 | 25 | 400 | 17 | 51 | 35 | 17 | 0 | 17 | 30 | 13 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 320 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 65 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 30 | 0 | 48 | 28 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1200 | 110 | 0 | 17 | 3 | 61 | 0 | 0 | 0 | 357 | 37 | 150 | 741 | 179 | 0 |  | 4877 | 4894 | 9771 | 2568 | 906 | 1834 | 0 | 995 | 2618 | 46 | 0 | 296 | 124 | 384 | 0 | 648.445 | 86.62
14:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 185 | 0 |  | 0 | 450 | 0 | 59 | 80 | 15 | 0 | 0 | 59 | 59 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 26 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 206 | 0 | 0 | 0 |  | 0 | 8 | 51 | 0 | 0 | 6 | 18 | 2 | 0 | 0 | 0 | 280 | 290 | 149 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 42 | 8 | 13 | 9 | 33 | 10 | 128 | 27 | 0 | 0 | 2 | 43 | 40 | 0 | 0 | 120 | 0 | 58 | 0 | 0 | 142 | 0 | 0 | 10 | 300 | 22 | 0 | 0 | 52 | 0 | 0 | 58 | 0 | 17 | 10 | 25 | 17 | 13 | 135 | 9 | 17 | 17 | 2 | 49 | 17 | 17 | 114 | 39 | 25 | 385 | 17 | 45 | 17 | 17 | 0 | 17 | 27 | 18 | 0 | 0 | 17 | 0 | 0 | 3 | 0 | 0 | 320 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 30 | 0 | 47 | 28 | 42 | 22 | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 350 | 17 | 0 | 35 | 0 | 6 | 0 | 4 | 0 | 1160 | 110 | 0 | 17 | 5 | 65 | 0 | 0 | 0 | 360 | 32 | 150 | 819 | 151 | 0 |  | 4859 | 4899 | 9758 | 2639 | 906 | 1721 | 0 | 1001 | 2659 | 46 | 0 | 312 | 128 | 343 | 3 | 136 | 86.62
15:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 383 | 0 |  | 0 | 450 | 0 | 59 | 80 | 15 | 0 | 0 | 59 | 59 | 45 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 26 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 206 | 0 | 0 | 0 |  | 0 | 8 | 49 | 0 | 0 | 6 | 18 | 0 | 0 | 0 | 0 | 280 | 290 | 146 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 41 | 8 | 13 | 9 | 33 | 16 | 128 | 29 | 0 | 0 | 1 | 43 | 40 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 143 | 0 | 0 | 10 | 285 | 25 | 0 | 0 | 47 | 0 | 0 | 58 | 0 | 17 | 10 | 25 | 17 | 13 | 300 | 9 | 17 | 17 | 2 | 49 | 17 | 17 | 98 | 42 | 25 | 350 | 17 | 36 | 17 | 17 | 0 | 17 | 21 | 18 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 320 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 55 | 0 | 90 | 4 | 0 | 0 | 0 | 0 | 30 | 0 | 47 | 14 | 16 | 24 | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 300 | 17 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1090 | 110 | 0 | 17 | 4 | 46 | 0 | 0 | 0 | 359 | 21 | 150 | 832 | 110 | 0 |  | 5105 | 4636 | 9741 | 2901 | 905 | 1654 | 0 | 947 | 2601 | 46 | 0 | 306 | 128 | 253 | 0 | 85 | 0
16:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 360 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 0 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 202 | 0 | 0 | 0 |  | 0 | 8 | 51 | 0 | 0 | 6 | 18 | 0 | 0 | 0 | 0 | 280 | 290 | 147 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 8 | 13 | 9 | 25 | 16 | 122 | 30 | 0 | 0 | 1 | 43 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 10 | 290 | 25 | 0 | 0 | 30 | 0 | 0 | 58 | 0 | 22 | 5 | 25 | 17 | 13 | 300 | 9 | 17 | 17 | 1 | 50 | 0 | 17 | 34 | 48 | 25 | 350 | 0 | 19 | 17 | 17 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 320 |  | 804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 30 | 0 | 90 | 3 | 0 | 0 | 0 | 0 | 30 | 0 | 48 | 14 | 8 | 24 | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 250 | 17 | 0 | 0 | 0 | 20 | 0 | 2 | 35 | 920 | 110 | 0 | 17 | 2 | 25 | 17 | 0 | 0 | 362 | 12 | 150 | 845 | 57 | 0 |  | 4152 | 4253 | 8405 | 2376 | 804 | 1561 | 0 | 660 | 2457 | 46 | 0 | 255 | 122 | 124 | 0 | 62.075 | 0
17:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 420 | 0 | 0 | 2 | 0 | 0 | 0 | 38 | 6 | 50 | 32 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 22 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 1 | 10 | 63 | 0 | 0 | 6 | 0 | 8 | 0 | 0 | 0 | 280 | 290 | 149 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 8 | 13 | 9 | 33 | 16 | 110 | 32 | 0 | 0 | 0 | 35 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 10 | 305 | 25 | 0 | 0 | 30 | 0 | 0 | 67 | 0 | 35 | 1 | 25 | 17 | 13 | 275 | 9 | 17 | 17 | 0 | 50 | 0 | 17 | 34 | 48 | 25 | 370 | 0 | 5 | 17 | 17 | 0 | 0 | 4 | 25 | 0 | 0 | 17 | 0 | 0 | 0 | 198 | 0 | 320 |  | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 30 | 0 | 90 | 3 | 16 | 0 | 0 | 0 | 30 | 4 | 48 | 14 | 8 | 24 | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 280 | 40 | 0 | 0 | 0 | 34 | 0 | 1 | 35 | 840 | 110 | 0 | 17 | 0 | 9 | 35 | 0 | 0 | 358 | 3 | 150 | 814 | 17 | 0 |  | 4453 | 4297 | 8750 | 2419 | 905 | 1631 | 0 | 756 | 2530 | 46 | 0 | 313 | 110 | 40 | 0 | 47.75 | 0
18:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 3 | 38 | 12 | 0 | 0 | 63 | 15 | 75 | 120 | 10 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 14 | 33 | 22 | 17 | 0 | 46 | 0 | 0 | 0 | 15 | 205 | 0 | 0 | 0 |  | 6 | 24 | 68 | 0 | 0 | 12 | 16 | 13 | 0 | 0 | 0 | 280 | 290 | 153 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 9 | 8 | 13 | 9 | 33 | 16 | 120 | 34 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 10 | 280 | 25 | 0 | 0 | 30 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 16 | 225 | 9 | 105 | 17 | 0 | 102 | 0 | 17 | 74 | 56 | 25 | 400 | 38 | 0 | 17 | 17 | 0 | 0 | 0 | 37 | 31 | 0 | 128 | 0 | 0 | 4 | 567 | 0 | 320 |  | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 36 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 30 | 10 | 83 | 14 | 25 | 30 | 0 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 291 | 71 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 850 | 110 | 0 | 54 | 0 | 0 | 50 | 0 | 0 | 355 | 0 | 184 | 910 | 0 | 0 |  | 5597 | 4603 | 10200 | 2533 | 849 | 1698 | 0 | 1297 | 3036 | 46 | 0 | 617 | 120 | 0 | 4 | 85.95 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 43 | 80 | 25 | 0 | 0 | 62 | 8 | 91 | 149 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 22 | 33 | 22 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 16 | 68 | 0 | 0 | 19 | 17 | 20 | 0 | 0 | 0 | 280 | 290 | 152 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 33 | 8 | 13 | 9 | 33 | 16 | 130 | 36 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 10 | 305 | 25 | 0 | 0 | 75 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 15 | 150 | 9 | 105 | 17 | 0 | 105 | 0 | 17 | 114 | 57 | 25 | 400 | 51 | 0 | 17 | 17 | 0 | 0 | 0 | 37 | 17 | 0 | 145 | 0 | 0 | 3 | 566 | 0 | 300 |  | 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 50 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 26 | 15 | 91 | 14 | 25 | 49 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 75 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1000 | 110 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 359 | 0 | 200 | 1020 | 0 | 0 |  | 5852 | 5034 | 10886 | 2514 | 799 | 1833 | 0 | 1519 | 3315 | 46 | 0 | 727 | 130 | 0 | 3 | 89.77 | 0
19:30 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 66 | 80 | 15 | 0 | 0 | 38 | 8 | 91 | 149 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 22 | 33 | 22 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 16 | 68 | 0 | 0 | 19 | 17 | 20 | 0 | 0 | 0 | 280 | 290 | 155 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 33 | 8 | 13 | 9 | 33 | 16 | 122 | 37 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 10 | 275 | 25 | 0 | 0 | 95 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 20 | 150 | 9 | 105 | 17 | 0 | 105 | 0 | 17 | 114 | 57 | 25 | 400 | 51 | 0 | 17 | 17 | 0 | 0 | 0 | 36 | 17 | 0 | 145 | 0 | 0 | 3 | 517 | 0 | 320 |  | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 32 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 26 | 15 | 91 | 14 | 8 | 49 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 380 | 75 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1020 | 110 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 359 | 0 | 200 | 1019 | 0 | 0 |  | 5759 | 4970 | 10729 | 2492 | 798 | 1746 | 0 | 1539 | 3285 | 46 | 0 | 698 | 122 | 0 | 3 | 86.905 | 0
20:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 68 | 80 | 15 | 0 | 0 | 39 | 8 | 91 | 149 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 19 | 22 | 33 | 22 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 16 | 68 | 0 | 0 | 19 | 18 | 24 | 0 | 0 | 0 | 280 | 290 | 154 | 0 | 0 | 12 | 0 | 0 | 43 | 0 | 33 | 8 | 13 | 9 | 33 | 16 | 122 | 51 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 10 | 270 | 25 | 0 | 0 | 95 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 18 | 150 | 9 | 105 | 17 | 0 | 105 | 0 | 17 | 114 | 58 | 25 | 400 | 53 | 0 | 17 | 17 | 0 | 0 | 0 | 36 | 17 | 0 | 145 | 0 | 0 | 1 | 335 | 0 | 330 |  | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 40 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 26 | 15 | 91 | 14 | 8 | 50 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 380 | 75 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1020 | 110 | 0 | 54 | 0 | 0 | 72 | 0 | 0 | 359 | 0 | 200 | 1016 | 0 | 0 |  | 5497 | 4970 | 10467 | 2418 | 798 | 1755 | 0 | 1527 | 3100 | 46 | 0 | 700 | 122 | 0 | 1 | 79.265 | 0
21:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 68 | 80 | 15 | 0 | 0 | 37 | 8 | 91 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 22 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 16 | 68 | 0 | 0 | 19 | 18 | 27 | 0 | 0 | 0 | 280 | 290 | 157 | 0 | 0 | 20 | 0 | 0 | 43 | 0 | 25 | 8 | 13 | 9 | 33 | 16 | 124 | 62 | 0 | 0 | 0 | 43 | 40 | 51 | 25 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 25 | 0 | 0 | 95 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 16 | 150 | 9 | 105 | 17 | 0 | 106 | 0 | 17 | 114 | 58 | 25 | 380 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 36 | 0 | 0 | 17 | 0 | 0 | 4 | 275 | 0 | 330 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 48 | 0 | 130 | 7 | 16 | 0 | 0 | 0 | 26 | 15 | 91 | 14 | 8 | 50 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 380 | 75 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1080 | 110 | 0 | 17 | 0 | 0 | 72 | 0 | 0 | 360 | 0 | 200 | 1113 | 0 | 0 |  | 5222 | 5184 | 10406 | 2356 | 906 | 1908 | 0 | 1421 | 3198 | 46 | 0 | 443 | 124 | 0 | 4 | 89.77 | 0
22:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 54 | 0 |  | 0 | 450 | 0 | 15 | 51 | 15 | 0 | 0 | 39 | 8 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 26 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 16 | 17 | 0 | 0 | 19 | 18 | 34 | 0 | 0 | 0 | 280 | 290 | 157 | 0 | 0 | 20 | 0 | 0 | 43 | 0 | 25 | 8 | 13 | 9 | 32 | 16 | 120 | 62 | 0 | 0 | 0 | 43 | 40 | 53 | 25 | 130 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 10 | 265 | 25 | 0 | 0 | 95 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 17 | 20 | 150 | 9 | 105 | 17 | 0 | 65 | 0 | 17 | 114 | 58 | 25 | 350 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 0 | 0 | 17 | 0 | 0 | 4 | 156 | 0 | 330 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 4 | 75 | 0 | 0 | 48 | 8 | 24 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 300 | 75 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1070 | 110 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 200 | 1115 | 0 | 0 |  | 4772 | 4882 | 9654 | 2386 | 906 | 1769 | 0 | 1093 | 3071 | 46 | 0 | 259 | 120 | 0 | 4 | 120.33 | 86.58
23:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 84 | 0 |  | 0 | 450 | 0 | 0 | 20 | 15 | 0 | 0 | 38 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 26 | 17 | 0 | 46 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 6 | 16 | 17 | 0 | 0 | 19 | 18 | 32 | 0 | 0 | 0 | 280 | 290 | 158 | 0 | 0 | 20 | 0 | 0 | 43 | 0 | 0 | 8 | 13 | 9 | 25 | 16 | 112 | 61 | 0 | 0 | 0 | 43 | 40 | 53 | 25 | 130 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 10 | 290 | 25 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 17 | 20 | 150 | 9 | 52 | 17 | 0 | 0 | 0 | 17 | 34 | 48 | 25 | 350 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 4 | 155 | 0 | 330 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 8 | 24 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 300 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 1111 | 0 | 0 |  | 4378 | 4638 | 9016 | 2421 | 906 | 1792 | 0 | 579 | 3016 | 46 | 0 | 140 | 112 | 0 | 4 | 108.87 | 86.58
24:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 232 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 26 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 18 | 40 | 0 | 0 | 0 | 280 | 290 | 158 | 0 | 0 | 20 | 0 | 0 | 43 | 0 | 0 | 0 | 17 | 9 | 25 | 11 | 110 | 68 | 0 | 0 | 0 | 43 | 40 | 53 | 25 | 163 | 0 | 30 | 0 | 0 | 0 | 20 | 0 | 10 | 290 | 23 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 0 | 20 | 315 | 9 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 155 | 0 | 330 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 976 | 0 | 0 |  | 4442 | 4255 | 8697 | 2780 | 907 | 1761 | 0 | 214 | 2811 | 46 | 0 | 58 | 110 | 0 | 10 | 0 | 86.57
KWH | 0 | 0 | 3902000 | 0 | 0 | 326181 | 0 | 3816000 | 0 |  | 0 | 9583000 | 0 | 842880 | 993528 | 200920 | 0 | 0 | 1602000 | 592858 | 842112 | 741120 | 12169 | 0 | 0 | 0 | 38520 | 40734 | 39001 | 0 | 408000 | 439560 | 722300 | 632700 | 198240 | 0 | 1112842 | 0 | 0 | 0 | 182019 | 4838495 | 0 | 0 | 0 |  | 44880 | 146688 | 747534 | 0 | 0 | 185760 | 378384 | 470400 | 0 | 0 | 0 | 7418000 | 7207000 | 3610000 | 0 | 0 | 196056 | 0 | 0 | 909402 | 0 | 393182 | 139099 | 316116 | 209880 | 663500 | 342990 | 3187200 | 1304640 | 0 | 0 | 13050 | 995000 | 946560 | 262200 | 100944 | 3532173 | 0 | 921408 | 0 | 0 | 2889190 | 17000 | 0 | 250560 | 7258500 | 572256 | 0 | 0 | 1056327 | 0 | 0 | 928800 | 0 | 487296 | 104085 | 331200 | 306240 | 235854 | 3605000 | 182400 | 825600 | 258436 | 18117 | 973527 | 123941 | 308620 | 1445520 | 622440 | 324480 | 8593800 | 483840 | 340440 | 194400 | 308618 | 0 | 124560 | 189978 | 274560 | 72360 | 0 | 618909 | 0 | 1696363 | 38400 | 6123636 | 0 | 6416364 |  | 19227636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247680 | 479616 | 0 | 2749000 | 132125 | 99360 | 0 | 0 | 0 | 277553 | 64127 | 765440 | 263390 | 359370 | 319810 | 71957 | 192637 | 0 | 0 | 79812 | 0 | 0 | 4139200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4247545 | 0 | 8634618 | 674880 | 0 | 269856 | 0 | 271286 | 0 | 16238 | 262944 | 25856400 | 2482934 | 0 | 378000 | 33420 | 443520 | 339648 | 0 | 0 | 8640000 | 189317 | 3883600 | 20001818 | 1000750 | 0 |  | 115350842 | 107095487 | 222446329 | 63624192 | 19227636 | 40359401 | 0 | 17212430 | 70341017 | 1112842 | 0 | 4994296 | 3187200 | 2348915 | 38400 | 0
Fuel Cost | 0 | 0 | 16739580 | 0 | 0 | 1246011.42 | 0 | 10990080 | 0 |  | 0 | 30473940 | 0 | 16309728 | 20724994.08 | 3453814.8 | 0 | 0 | 8570700 | 11424373.66 | 15663283.2 | 13651430.4 | 220867.35 | 0 | 0 | 0 | 703375.2 | 651336.66 | 713328.29 | 0 | 306000 | 0 | 0 | 0 | 3550478.4 | 0 | 0 | 0 | 0 | 0 | 3447439.86 | 15434799.05 | 0 | 0 | 0 |  | 788092.8 | 2583175.68 | 13388333.94 | 0 | 0 | 3057609.6 | 1407588.48 | 0 | 0 | 0 | 0 | 20696220 | 22053420 | 11985200 | 0 | 0 | 660708.72 | 0 | 0 | 3646702.02 | 0 | 7041889.62 | 2503782 | 1175951.52 | 157410 | 2468220 | 257242.5 | 20908032 | 4057430.4 | 0 | 0 | 0 | 3880500 | 3530668.8 | 1193010 | 459295.2 | 12080031.66 | 0 | 5113814.4 | 0 | 0 | 8060840.1 | 111860 | 0 | 1002240 | 22428765 | 429192 | 0 | 0 | 21813152.55 | 0 | 0 | 17740080 | 0 | 8693360.64 | 0 | 5719824 | 5389824 | 3971781.36 | 9553250 | 2701344 | 14860800 | 4483864.6 | 0 | 18049190.58 | 2419328.32 | 4919402.8 | 26510836.8 | 11533813.2 | 5778988.8 | 22859508 | 8089804.8 | 0 | 3555576 | 5246506 | 0 | 2178554.4 | 0 | 4543968 | 1238803.2 | 0 | 11072282.01 | 0 | 11823650.11 | 0 | 36129452.4 | 0 | 0 |  | 56529249.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4658860.8 | 9021576.96 | 0 | 8686840 | 626272.5 | 1712966.4 | 0 | 0 | 0 | 4970974.23 | 1176730.45 | 12867046.4 | 5604939.2 | 6849592.2 | 5727797.1 | 1272919.33 | 3450128.67 | 0 | 0 | 60417.684 | 0 | 0 | 34934848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14144324.85 | 0 | 25213084.56 | 12228825.6 | 0 | 5380928.64 | 0 | 5450135.74 | 0 | 0 | 5085336.96 | 155396964 | 7721924.74 | 0 | 7314300 | 0 | 0 | 5750240.64 | 0 | 0 | 61344000 | 0 | 28932820 | 140612780.54 | 0 | 0 |  | 622279733.38 | 632726826.034 | 1255006559.414 | 193391766.504 | 56529249.84 | 106091277.1 | 0 | 319301492.66 | 469174515.05 | 0 | 0 | 89610226.26 | 20908032 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 40 | 0 |  | 0 | 450 | 0 | 100 | 80 | 15 | 0 | 0 | 99 | 67 | 41 | 32 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 26 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 8 | 51 | 0 | 0 | 6 | 18 | 4 | 0 | 0 | 0 | 350 | 290 | 144 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 41 | 8 | 13 | 9 | 25 | 16 | 128 | 32 | 0 | 0 | 2 | 43 | 40 | 0 | 0 | 163 | 0 | 56 | 0 | 0 | 145 | 0 | 0 | 10 | 310 | 22 | 0 | 0 | 80 | 0 | 0 | 58 | 0 | 17 | 17 | 25 | 17 | 13 | 135 | 9 | 17 | 17 | 4 | 50 | 17 | 17 | 98 | 30 | 25 | 400 | 17 | 54 | 17 | 17 | 0 | 17 | 20 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 340 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 0 | 125 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 28 | 0 | 0 | 0 | 4 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1200 | 220 | 0 | 17 | 5 | 61 | 0 | 0 | 0 | 357 | 36 | 150 | 752 | 172 | 0 |  | 9964 | DayPeak
Yesterday Evening Peak | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 450 | 0 | 43 | 80 | 25 | 0 | 0 | 62 | 8 | 91 | 149 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 22 | 33 | 22 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 | 0 | 6 | 16 | 68 | 0 | 0 | 19 | 17 | 20 | 0 | 0 | 0 | 280 | 290 | 152 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 33 | 8 | 13 | 9 | 33 | 16 | 130 | 36 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 10 | 305 | 25 | 0 | 0 | 75 | 0 | 0 | 67 | 0 | 35 | 0 | 25 | 17 | 15 | 150 | 9 | 105 | 17 | 0 | 105 | 0 | 17 | 114 | 57 | 25 | 400 | 51 | 0 | 17 | 17 | 0 | 0 | 0 | 37 | 17 | 0 | 145 | 0 | 0 | 3 | 566 | 0 | 300 |  | 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 50 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 26 | 15 | 91 | 14 | 25 | 49 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 414 | 75 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1000 | 110 | 0 | 54 | 0 | 0 | 70 | 0 | 0 | 359 | 0 | 200 | 1020 | 0 | 0 |  | 10886 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 0 | 12 | 0 | 400 | 0 |  | 0 | 450 | 0 | 100 | 80 | 30 | 0 | 0 | 100 | 90 | 91 | 132 | 13 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 19 | 22 | 33 | 33 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 205 | 0 | 0 | 0 |  | 6 | 16 | 68 | 0 | 0 | 19 | 18 | 20 | 0 | 0 | 0 | 360 | 360 | 150 | 8 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 8 | 16 | 9 | 33 | 15 | 141 | 75 | 0 | 0 | 0 | 43 | 40 | 51 | 50 | 163 | 0 | 30 | 0 | 0 | 150 | 20 | 0 | 10 | 320 | 24 | 0 | 0 | 130 | 0 | 0 | 66 | 0 | 50 | 0 | 25 | 17 | 25 | 315 | 9 | 105 | 17 | 0 | 100 | 0 | 17 | 114 | 57 | 25 | 400 | 53 | 0 | 35 | 17 | 0 | 17 | 0 | 37 | 17 | 0 | 145 | 0 | 0 | 10 | 570 | 0 | 370 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 84 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 25 | 15 | 90 | 28 | 42 | 50 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 75 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 1240 | 115 | 0 | 54 | 0 | 0 | 74 | 0 | 0 | 360 | 0 | 200 | 1260 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 200 | 0 | 0 | 12 | 0 | 280 | 0 | 0 | 0 | 450 | 0 | 85 | 80 | 15 | 0 | 0 | 100 | 90 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 205 |  | 0 | 0 | 0 | 2 | 8 | 51 | 0 | 0 | 6 | 18 | 15 | 0 | 0 | 0 | 360 | 360 | 150 | 8 | 0 | 5 | 0 | 0 | 43 | 0 | 40 | 8 | 16 | 9 | 33 | 15 | 128 | 35 | 0 | 0 | 1.6 | 43 | 40 | 51 | 50 | 163 | 0 | 30 | 0 | 0 | 150 | 20 | 0 | 10 | 320 | 24 | 0 | 0 | 82 | 0 | 0 | 56 | 0 | 17 | 20 | 25 | 17 | 6 | 315 | 9 | 17 | 17 | 5 | 50 | 0 | 17 | 114 | 9 | 25 | 390 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 0 | 17 | 0 | 0 | 10 | 156 | 0 | 370 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 28 | 34 | 48 | 8 | 25 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 17 | 0 | 0 | 0 | 6 | 0 | 8 | 0 | 1200 | 115 |  | 17 | 6 | 100 | 0 | 0 |  | 360 | 30 | 200 | 1260 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 0 | 12 | 0 | 276 | 0 | 0 | 0 | 450 | 0 | 48 | 15 | 0 | 0 | 0 | 104 | 30 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 25 | 24 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 6 | 18 | 15 | 0 | 0 | 0 | 360 | 325 | 126 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 8 | 18 | 9 | 17 | 11 | 110 | 65 | 0 | 0 | 1 | 43 | 40 | 53 | 25 | 163 | 0 | 30 | 0 | 0 | 0 | 20 | 0 | 10 | 315 | 23 | 0 | 0 | 40 | 0 | 0 | 56 | 0 | 17 | 7 | 25 | 17 | 6 | 315 | 9 | 17 | 17 | 1 | 16 | 0 | 17 | 95 | 7 | 25 | 390 | 17 | 13 | 0 | 17 | 0 | 0 | 9 | 0 | 0 | 0 | 17 | 0 | 0 | 9 | 156 | 0 | 330 | 0 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 200 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1030 | 110 | 0 | 17 | 1 | 20 | 0 | 0 | 0 | 360 | 6 | 174 | 1263 | 57 | 0 | 0 |  |  |  | 103983593 | 19227636 | 0 | 70341017 | 22206726 | 3187200 | 2348915 | 38400 | 1112842
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  |  |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [27 empty] | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 103.9836 | 19.2276 | 0 | 70.341 | 22.2067 | 3.1872 | 2.3489 | 0.0384 | 1.1128
| Minimum Generation |  | 7294 | 5:00
| Highest Generation |  | 10886 | 19:00 | [129 empty] | 0 | [70 empty] | 222.4463
| Day Peak Generation |  | 9964 | 12:00
| Evening Peak Generation |  | 10886 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 907 | 11:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 799 | 19:00
| Load factor L.F |  | 85.14% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-02-08
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9964 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7297
Evening Peak Generation : |  |  | 10886 | MW Hour : | 19:00 | Available Max Generation : |  | 12615
E.P. Demand (at gen end) : |  |  | 10980 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11200
Maximum Generation : |  |  | 10886 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1415
Total Gen. (MKWH) : |  |  | 222.4463 | System Load Factor : | 85.14% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 950 | MW at | 5:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-08
Actual : |  | 86.55 | Ft.(MSL) , | Rule curve : | 96.02 | Ft.( MSL )
Gas Consumed : |  | Total = | 849.76 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 299483043.604
: |  |  | Coal : | 469174515.05 | Oil : | 408911718.92 | Total : | 1177569277.574
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 8 | 192:00 | 3693.7597 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1009.6328 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1412.702 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1226.4236 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1009.8797 |  |  | 0 | 0%
Mymensingh Area |  | 82 | 1968:00 | 750.3172 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 421.4087 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 350.4332 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 685.4034 |  |  | 0 | 0%
Total |  | 90 |  | 10559.9605 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj East
8) Bibiyana South
9) Haripur-412 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:05 | 15:26 | Magura 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to Annual Maintenance.
08:13 | 19:36 | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Payra 400/132/33kV end Due to Anual maintenance.
08:22 | 19:32 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D Due to Annual Maintenance
08:50 |  | Bakulia-Khulshi 132 kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual maintenance.
08:51 | 16:54 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Kachua end Due to yearly maintenance Due to Shutdown for Dead line checking
08:56 | 16:48 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Forced S/D from Bogura end Due to মহাস্থানগড়-বগুড়া সার্কিট-2 এর BUS DS এর
Junction Temperature এর পয়েন্ট মেরামত।
| 08:57 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
08:58 | 17:29 | Bheramara P/S-Ishurdi 132 kV Ckt-1 Project Work S/D from Bheramara 230/132kV end Due to Conductor change.
08:59 | 15:21 | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to Annual Maintenance
09:00 | 18:26 | Ashuganj-Sreepur 230 kV Ckt-2 Project Work S/D from Sirajgonj 230 end Due to Project work
09:02 |  | Matarbari 2*600 MW (CPGCL) Shutdown
09:21 | 17:21 | Chandraghona-Madunaghat 132 kV Ckt-1 S/D from Madunaghat end Due to For disk changing work .
| 09:24 | Juldah-Sikalbaha 132kV Ckt-1 is restored.
| 09:27 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT is restored.
09:35 | 23:31 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 S/D from Cumilla(N) end Due to Busbar protection panel replacement work done by SPMD. |  |  |  |  | 50 MW power interrupt.
09:36 |  | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to Maintenance work
| 09:40 | Juldah-Shahmirpur 132kV Ckt-2 is restored.
09:49 | 14:31 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensing end Due to Annual Maintanance Work.
09:50 |  | Hathazari 230/132/33kV S/S Raojan-02 Scheduled S/D Due to annual dead line checking
| 09:57 | Juldah 132/33kV S/S Julda power plant unit-2 & 3 is restored.
10:14 | 13:20 | Madanganj-Munsiganj 132 kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end Due to Dead End line checking
11:35 | 16:22 | Sreepur 230/132/33kV S/S 230 kV Bus-1 Project Work S/D Due to All Bus-1 DS Maintenance
| 11:45 | Daudkandi 132/33kV S/S Transformer-3 HT is restored.
12:40 |  | Haripur 412 MW CCPP Syncronized with remarks:- ST
13:21 | 16:50 | Madanganj-Munsiganj 132 kV Ckt-2 Scheduled S/D from Munshiganj end Due to Dead Line Checking.
| 13:33 | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT is restored.
| 15:19 | Rampur 230/132/33 S/S 132kV BUS-02 is restored.
| 15:34 | Haripur 230/132kV S/S 132kV Main Bus Sec-1 is restored.
| 15:34 | Haripur 230/132kV S/S 132kV Main Bus Sec-2 is restored.
15:44 | 16:57 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to 33 kV Bus-DS red hot maintenance by PBS |  |  |  |  | 27 MW power interrupt.
15:50 |  | Matarbari 2*600 MW (CPGCL) Syncronized
15:52 | 16:37 | Haripur 230/132kV S/S 132kV Main Bus Sec-2 Tripped showing MCGG relays Due to Reserve Bus Y Phase PT Burst
15:52 | 16:36 | Haripur 230/132kV S/S Auto TR-1 LT Tripped showing MCGG relays Due to Reserve Bus Y Phase PT Burst
15:52 | 16:53 | Haripur 230/132kV S/S Auto TR-3 LT Tripped showing SIEMENS relays Due to Reserve Bus Y Phase PT Burst
15:52 | 20:00 | Haripur-Siddirganj 230kV Ckt-2 Tripped from Siddhirganj end showing Distance relays Due to ZONE 2 TRIP (PT brust Haripur side)
15:54 | 16:58 | Sonargaon 132/33kV S/S Bashundhara Line Tripped showing P-127 relays Due to Over voltage trip
15:54 | 16:46 | Haripur-Sonargaon 132kV Ckt-1 Tripped from Sonargaon end showing General tirp , zone -1&2 trip, R,Y,B phase fault, carrier
send. relays Due to Trip
15:53 |  | Haripur 412 MW CCPP Tripped with remarks:- GT
15:54 | 16:58 | Sonargaon 132/33kV S/S Bashundhara Line Tripped showing P-127 relays Due to Over voltage trip. |  |  |  |  | 50 MW power interrupt.
15:54 | 16:49 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing P-127 relays Due to Sonargaon grid power failure. |  |  |  |  | 41 MW power interrupt.
15:56 | 16:48 | Haripur-Madanganj 132kV Ckt-1 Tripped from Madanganj end showing Main protection Trip relays.
15:56 | 16:59 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Tripped showing Line DIST.PROT OPTD, DIR O/C &E/F PROT.
OPTD, ZONE-2 relays Due to None
17:13 | 17:13 | Gulsan-Rampura 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Dis. Relay: 1). R,Y,B- Ph pick up. 2) Dis. Trip
Zone-1, Zone 3/4. 3). SOTF 4) Over current.Rel 316*4: 1). Diff. Trip-R 2) DEF signal received 3). DEF signal send Master Trip: 86T1,
86T2, 86T3, 86T4 relays Due to unknown
| 17:15 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75MVA) HT is restored.
| 17:15 | Kabirpur - Manikganj 132kV Ckt-1 is restored.
| 17:15 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT is restored.
| 17:21 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT is restored.
17:47 |  | Chandpur 132/33kV S/S 100MW(GT) Power Plant Incomer (T4) Scheduled S/D
| 19:23 | Ishurdi 132/33kV S/S 132 kV Baghabari Line is restored.
19:32 |  | BIPTC S/S 20DF24 Tripped showing impedence 21R relays Due to impedence 21R
| 19:46 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
20:07 |  | Sylhet 225 MW CCPP Shutdown with remarks:- GT
20:07 |  | Sylhet CCPP 225 MW was forced shutdown
21:01 |  | Haripur 412 MW CCPP Syncronized with remarks:- GT
21:01 |  | Haripur EGCB 412MW CCPP GT was sync.
21:05 |  | Bogura west 400 KV bus-1 syn.
01:06 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- ST
01:18 |  | Sirajgonj 400 MW CCPP Unit-4 Shutdown with remarks:- GT
07:00 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
07:14 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Project Work S/D Due to Project Work
07:30 |  | Kabirpur - Manikganj 132kV Ckt-2 Project Work S/D from Manikganj 132/33kV end Due to Project Work
07:32 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Project Work S/D Due to Project Work
07:33 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Project Work S/D Due to Project Work
07:43 |  | Bheramara P/S-Ishurdi 132 kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end.
07:50 |  | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Scheduled S/D
07:50 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Scheduled S/D Due to Due to Annual Maintenance of Gopalganj Line-1
07:51 |  | Gopalganj(N)-Rampal Ckt-1 Scheduled S/D from Rampal 400/230kV end Due to Due to Annual Maintenance
07:57 |  | Kabirpur - Manikganj 132kV Ckt-1 Project Work S/D from
07:13 |  | BIPTC S/S 20DF42 Tripped showing relay 286 & 186 operated relays Due to summary trip(backup protection opt.)
07:14 |  | Rampur 230/132/33 S/S Khulshi-2 Scheduled S/D Due to Bus shutdown at khulshi Grid
07:14 |  | Rampur 230/132/33 S/S Khulshi-1 Scheduled S/D Due to Bus shutdown at khulshi Grid
07:22 |  | Khulshi 132/33kV S/S Main Bus Scheduled S/D Due to Annual maintenance.... |  |  |  |  | 30.0MW
load
07:26 |  | AKSML-Khulshi 132kV Ckt-1 Project Work S/D from AKS 132/33kV end Due to Comand to Nldc
07:33 |  | BSRM-Cumilla(N) 230 kV Ckt-1 Project Work S/D from BSRM 230/33kV end Due to Shutdown taken by ESPNER project.
07:36 |  | Baghabari-Sirajganj 230 kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to IDRNPP,400kV Rooppur Dhaka
Phase-2 Stringing Work
07:39 |  | Baghabari-Sirajganj 230 kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to IDRNPP,400kV Rooppur Dhaka
Phase-2 Stringing Work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 190 | 3902000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 326181 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 3816000 | Under maint.
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9583000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 43 | 842880 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 993528 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 25 | 200920 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 12169 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 62 | 1602000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 592858 | Line overload
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 842112 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 38520 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 741120
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 40734 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 39001 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 847560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 722300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 22 | 632700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 198240 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 75 | 1056327 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 487296 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 825600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 51 | 483840 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 189978
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 72360 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 300 | 6416364 | On test.
| Dhaka area Total |  |  |  | 5062 | 1874 | 35699988
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 182019 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 104085
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 185760 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1112842 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 204 | 4838495
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 258436 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 146688 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 747534 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 331200 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 378384 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 470400
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18117
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 105 | 973527 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 123941 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 308620 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 324480 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 308618 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 618909 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 0 | 1696363 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 3 | 38400 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 566 | 6123636 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1327 | 19290454
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 152 | 3610000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7418000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7207000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 196056 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 909402 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 15 | 235854 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 393182 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 306240 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 316116 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 209880 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 130 | 3187200
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 663500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 139099 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 16 | 342990 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1445520
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 622440 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 124560 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 37 | 274560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1252 | 27601599
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 36 | 1304640 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13050
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 67 | 928800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 182400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 340440
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 44880 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 118 | 2814210
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 995000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 946560 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3532173
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 262200 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 100944 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 921408 | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 2889190 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 17000 | Engine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 25 | 572256
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7258500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 150 | 3605000 | On test.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250560
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8593800
| Sylhet Area Total |  |  |  | 2427 | 1281 | 29944591
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 799 | 19227636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 53 | 247680
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 479616 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 75 | 674880 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 443520
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 359 | 8640000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1336 | 29713332
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 99360 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 6 | 132125 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2749000 | ST Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1000 | 25856400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2482934 | GT-2 under maint
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 378000 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 3883600 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1516 | 35581419
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 277553 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 64127 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 14 | 263390 | Low demand
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 359370 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 49 | 319810
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 173 | 4247545 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8634618
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 192637 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 79812 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 71957 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 765440 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 269856 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 262944 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33420
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1020 | 20001818
| Rajshahi Area Total |  |  |  | 3631 | 1907 | 35844297
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4139200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 271286 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 16238
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 70 | 339648 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 189317
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1000750
| Rangpur Area Total |  |  |  | 950 | 275 | 5956439
| Total |  |  |  | 25481 | 10886 | 222446329
| Eastern Grid Total |  |  |  | 15398 | 5852 | 115350842
| Western Grid Total |  |  |  | 10083 | 5034 | 107095487
| National Grid Total |  |  |  | 25481 | 10886 | 222446329
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-07
| (a) ENTIRE EASTERN GRID : |  | 7012.37 | MW | (b) ENTIRE WESTERN GRID : |  | 3386 | MW
| i) Dhaka area |  | 3843.37 | MW | i) Khulna area |  | 1219 | MW
| ii) Chittagong area |  | 1045 | MW | ii) Rajshahi area |  | 1099 | MW
| iii) Comilla area |  | 897 | MW | iii) Barisal area |  | 278 | MW
| iv) Mymensingh area |  | 863 | MW | iv) Rangpur area |  | 790 | MW
| v) Sylhet area |  | 364 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10398.37 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 21 | 14:00 | Kamrangirchar | 46.2 | 12:00 | Narinda | 49 | 13:00 | Sherpur | 108 | 21:00
2 | AKSML | 9 | 19:00 | Chowmuhani | 142 | 20:00 | Kaptai | N/A | N/A | Narshingdi | 147 | 19:00 | Shikalbaha | 18 | 22:00
3 | Aftabnagar | 24 | 12:00 | Chuadanga | 75 | 18:30 | Kazla | 94 | 13:00 | Natore | 100 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 59 | 13:00 | Coxsbazar | 99 | 18:00 | Keranigonj | 60 | 13:00 | Nawabganj | 28 | 21:00 | Shitalakhya | 79.5 | 12:00
5 | Agrabad | 46 | 18:00 | Cumilla(N) | 96 | 18:00 | Khagrachori | 26 | 18:30 | Netrakona | 101 | 19:30 | Sholosohor | 34 | 10:00
6 | Amnura | 56 | 08:00 | Cumilla(S) | 129 | 12:00 | Khulna | 72 | 12:00 | New | 18.2 | 12:00 | Shyampur | 160 | 11:00
7 | Ashuganj | 46 | 12:00 | Daudkandi | 110 | 21:00 | Khulshi | 151 | 13:00 | Niamatpur | 73 | 14:00 | Siddhirganj | 98 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 16 | 12:00 | Kishoreganj | 112 | 19:00 | Noapara | 37 | 18:30 | Sirajganj | 96 | 19:00
9 | BSRM | 81 | 04:00 | Dhamrai | 124 | 12:00 | Kodda | 258 | 18:30 | PHP | 7 | 19:30 | Sonargaon | 94 | 07:00
10 | Bagerhat | 69 | 19:00 | Dhanmondi | 103 | 13:00 | Kulaura | 24 | 18:00 | Pabna | 82 | 19:00 | Sreemongol | 45 | 19:30
11 | Bakulia | 62 | 18:30 | Dohazari | 62 | 19:00 | Kurigram | 66 | 18:30 | Palashbari | 92 | 08:00 | Sreepur | 62 | 18:30
12 | Banani | 22.6 | 14:00 | Faridpur | 114 | 19:00 | Kushtia | 94 | 18:30 | Panchagarh | 46 | 18:30 | Srinagar | 29.4 | 21:00
13 | Bangabhaban | 8 | 10:00 | Fatullah | 48 | 12:00 | Lalbag | 70 | 13:00 | Patuakhali | 53.5 | 21:00 | Sunamganj | 36 | 18:00
14 | Barapukuria | 58 | 08:00 | Fenchuganj | 23 | 18:00 | Lalmonirhat | 44 | 08:00 | Payra | 12 | 11:00 | Sylhet | 10 | 13:00
15 | Barguna | 14 | 21:00 | Feni | 72 | 18:00 | MI_Cement | 12.8 | 15:00 | Postogola | 43 | 13:00 | Sylhet-132 | 90 | 19:00
16 | Barishal | 80 | 13:00 | GPH | 97 | 18:30 | Madanganj | 42 | 21:00 | Purbachal | 13 | 12:00 | TK | 14 | 21:00
17 | Barishal-230 | 64 | 18:30 | Ghorashal | 67 | 18:30 | Madaripur | 64 | 19:00 | Purbasadipur | 116 | 18:30 | Tangail | 156 | 07:00
18 | Baroaulia | 57 | 14:00 | Goalpara | 22 | 00:00 | Madartek | 48.47 | 19:00 | Rahim | 47 | 13:00 | Thakurgaon | 78 | 18:30
19 | Baroirhat | 40 | 20:00 | Gollamari | 38 | 18:30 | Madunaghat | 35 | 18:00 | Rajbari | 50 | 18:30 | Tongi | 134 | 11:00
20 | Bashundhara | 121 | 12:00 | Gopalganj | 74 | 19:00 | Magura | 46 | 18:30 | Rajendrapur | 74 | 18:30 | Ullahpara | 16 | 15:00
21 | BashundharaCement | 7 | 11:00 | Gulshan | 72 | 13:00 | Mahasthangarh | 60 | 08:00 | Rajshahi | 110 | 20:00 | Ullon | 32 | 13:00
22 | Beanibazar | 42 | 18:00 | Halishahar | 65 | 15:00 | Manikganj | 85 | 18:30 | Rajshahi-230 | 25 | 21:00 | Uttara | 42 | 13:00
23 | Benapole | 60 | 08:00 | HaripurSBU | 166 | 13:00 | Maniknagar | 52 | 12:00 | Ramganj | 68 | 19:30 | UttaraNew | 29 | 14:00
24 | Bhaluka | 112 | 19:30 | Hasnabad | 63 | 12:00 | Matarbari | 32 | 18:00 | Rampur | 27 | 19:00 | Zigatola | 54 | 13:00
25 | Bhandaria | 32 | 21:00 | Hathazari | 47 | 18:30 | Matuail | 58 | 12:00 | Rangamati | 12 | 18:30
26 | Bhangura | 23 | 18:30 | Ishurdi | 46 | 19:00 | Millgate | 75 | 12:00 | Rangpur | 105 | 19:00
27 | Bheramara(GK) | 41 | 18:30 | Jaldhaka | 64 | 08:00 | Mirpur | 89.5 | 14:00 | Ruppur | 4.4 | 11:00
28 | Bhulta | 222 | 01:00 | Jamalpur | 128 | 07:00 | Mirsorai | 5 | 09:00 | SSM | 15 | 06:00
29 | Bog-Sherpur | 56 | 08:00 | Jashore | 95 | 18:30 | Mirzapur | 46.4 | 14:00 | Saidpur | 96 | 14:00
30 | Bogura | 120 | 14:00 | Jhenaidah | 93 | 18:30 | Mithapukur | 54 | 18:30 | Satkhira | 97 | 19:00
31 | Borhanuddin | 49 | 20:00 | Joydebpur | 125 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 81 | 13:00
32 | Brahmanbaria | 112 | 19:30 | Joypurhat | 49 | 19:30 | Mogbazar | 68.5 | 12:00 | Savar | 164 | 10:00
33 | Cantonment | 96 | 13:00 | Juldah | 18 | 12:00 | Mongla | 25 | 04:00 | SevenRings | 14.64 | 17:00
34 | Chandpur | 41 | 18:30 | KSRM | 38 | 00:00 | Motijheel | 28 | 13:00 | ShahCement | 22 | 01:00
35 | Chandraghona | 23 | 18:00 | Kabirpur | 227 | 15:00 | Munshiganj | 60 | 21:00 | Shahjadpur | 56 | 19:00
36 | Chapai | 57 | 08:00 | Kachua | 52 | 18:00 | Mymensingh | 192 | 08:00 | Shahjibazar | 84 | 18:30
37 | Charsaidpur | 39 | 15:00 | Kallyanpur | 72 | 12:00 | Naogaon | 107 | 13:00 | Shahmirpur | 48 | 18:00
38 | Chauddagram | 42 | 18:00 | Kalurghat | 28 | 10:00 | Narail | 40 | 18:30 | Shariatpur | 50 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 411 | 05:00 | 395 | 12:00 | Gopalganj | 415 | 06:00 | 400 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 405 | 04:00 | 390 | 11:00
| Bhulta | 407 | 04:00 | 392 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 420 | 21:00 | 410 | 10:00 | Payra | 420 | 03:00 | 413 | 08:00
| BIPTC | 409 | 02:00 | 392 | 11:00 | Rahanpur | 416 | 03:00 | 400 | 07:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 415 | 05:00 | 400 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 237 | 05:00 | 224 | 12:00 | Hasnabad | 236 | 04:00 | 227 | 12:00
| AKSML | 238 | 20:00 | 227 | 00:00 | Hathazari | 238 | 19:30 | 228 | 00:00
| Aminbazar | 238 | 05:00 | 229 | 11:00 | Ishurdi | 240 | 03:00 | 225 | 08:00
| Ashuganj | 243 | 04:00 | 235 | 12:00 | Jhenaidah | 238 | 03:00 | 222 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 05:00 | 225 | 11:00
| Baghabari | 238 | 02:00 | 228 | 11:00 | Keranigonj | 239 | 01:00 | 225 | 12:00
| Barapukuria | 225 | 04:00 | 209 | 08:00 | Khulna(S) | 242 | 05:00 | 230 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 245 | 04:00 | 240 | 00:00 | Maniknagar | 239 | 04:00 | 230 | 12:00
| Bheramara | 238 | 03:00 | 223 | 08:00 | Meghnaghat | 246 | 20:00 | 238 | 12:00
| Bhulta | 242 | 04:00 | 232 | 12:00 | Mirsorai | 242 | 20:00 | 230 | 00:00
| Bibiana | 241 | 19:00 | 235 | 11:00 | Rajshahi | 241 | 04:00 | 228 | 12:00
| BIPTC | 240 | 05:00 | 224 | 08:00 | Rampal | 240 | 05:00 | 227 | 12:00
| Bogura | 232 | 05:00 | 224 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 01:00 | 243 | 08:00 | Rampura | 240 | 05:00 | 232 | 11:00
| BSRM | 241 | 20:00 | 227 | 00:00 | Shikalbaha | 235 | 19:30 | 225 | 01:00
| Cumilla(N) | 240 | 19:00 | 233 | 00:00 | Shyampur | 238 | 05:00 | 227 | 12:00
| Fenchuganj | 245 | 22:00 | 239 | 15:00 | Siddhirganj | 238 | 01:00 | 233 | 11:00
| Ghorashal | 242 | 01:00 | 239 | 11:00 | Sirajgonj | 243 | 05:00 | 226 | 12:00
| Ghorashal-230 | 238 | 09:00 | 231 | 10:00 | Sreepur | 239 | 06:00 | 227 | 12:00
| GPH | 238 | 20:00 | 225 | 00:00 | Tongi | 235 | 19:30 | 219 | 11:00
| Haripur | 239 | 07:00 | 229 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 05:00 | 130 | 12:00 | Lalbag | 135 | 03:00 | 127 | 12:00
| Agargaon | 140 | 05:00 | 131 | 12:00 | Lalmonirhat | 131 | 02:00 | 117 | 08:00
| Agrabad | 138 | 21:00 | 131 | 00:00 | Madanganj | 137 | 18:30 | 130 | 12:00
| AKS | 136 | 20:00 | 129 | 00:00 | Madaripur | 138 | 06:00 | 134 | 11:00
| Aminbazar | 136 | 03:00 | 129 | 10:00 | Madartek | 136 | 05:00 | 129 | 12:00
| Amnura | 138 | 18:00 | 125 | 08:00 | Madunaghat | 139 | 21:00 | 130 | 00:00
| Ashuganj | 141 | 06:00 | 139 | 12:00 | Magura | 140 | 03:00 | 128 | 08:00
| Bagerhat | 135 | 23:00 | 127 | 08:00 | Mahasthangarh | 135 | 03:00 | 124 | 08:00
| Bakulia | 138 | 19:00 | 130 | 00:00 | Manikganj | 134 | 18:30 | 128 | 05:00
| Banani | 137 | 02:00 | 125 | 12:00 | Maniknagar | 134 | 04:00 | 127 | 12:00
| Bangabhaban | 134 | 04:00 | 126 | 12:00 | Matarbari | 136 | 00:00 | 124 | 01:00
| Barapukuria | 135 | 03:00 | 121 | 08:00 | Matuail | 136 | 20:00 | 131 | 11:00
| Barguna | 139 | 18:00 | 136 | 07:00 | Millgate | 138 | 02:00 | 126 | 12:00
| Barishal | 140 | 19:30 | 137 | 11:00 | Mirpur | 135 | 18:30 | 127 | 12:00
| Barishal-230 | 140 | 02:00 | 136 | 13:00 | Mirzapur | 133 | 02:00 | 124 | 07:00
| Baroaulia | 141 | 22:00 | 131 | 00:00 | Mithapukur | 133 | 02:00 | 118 | 08:00
| Baroirhat | 140 | 14:00 | 130 | 00:00 | MI_Cement | 138 | 19:30 | 132 | 12:00
| Bashundhara | 138 | 02:00 | 125 | 12:00 | Modern | 138 | 19:30 | 130 | 00:00
| BashundharaCement | 139 | 14:00 | 125 | 07:00 | Mogbazar | 137 | 02:00 | 128 | 08:00
| Beanibazar | 136 | 01:00 | 132 | 14:00 | Mongla | 135 | 05:00 | 127 | 12:00
| Benapole | 138 | 04:00 | 124 | 08:00 | Motijheel | 134 | 04:00 | 126 | 12:00
| Bhaluka | 133 | 09:00 | 126 | 12:00 | Munshiganj | 135 | 09:00 | 130 | 12:00
| Bhandaria | 140 | 17:00 | 135 | 00:00 | Mymensingh | 133 | 13:00 | 120 | 17:00
| Bhangura | 141 | 03:00 | 131 | 08:00 | Naogaon | 133 | 04:00 | 117 | 08:00
| Bheramara | 139 | 05:00 | 129 | 08:00 | Narail | 139 | 03:00 | 128 | 12:00
| Bheramara(GK) | 139 | 04:00 | 129 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 128 | 18:00 | 120 | 00:00 | Narshingdi | 136 | 04:00 | 123 | 12:00
| Bog-Sherpur | 137 | 03:00 | 128 | 08:00 | Natore | 136 | 02:00 | 126 | 08:00
| Bogura | 137 | 03:00 | 124 | 08:00 | Nawabganj | 136 | 05:00 | 129 | 11:00
| Bogura-230 | 136 | 05:00 | 130 | 13:00 | Netrakona | 133 | 13:00 | 120 | 04:00
| Brahmanbaria | 137 | 01:00 | 133 | 16:00 | New | 137 | 02:00 | 127 | 12:00
| Cantonment | 139 | 03:00 | 131 | 12:00 | Niamatpur | 133 | 00:00 | 111 | 07:00
| Chandpur | 140 | 19:00 | 127 | 00:00 | Noapara | 135 | 05:00 | 128 | 08:00
| Chandraghona | 139 | 19:00 | 132 | 01:00 | Pabna | 140 | 03:00 | 130 | 08:00
| Chapai | 134 | 00:00 | 129 | 07:00 | Palashbari | 132 | 03:00 | 115 | 08:00
| Charsaidpur | 137 | 19:30 | 131 | 12:00 | Panchagarh | 134 | 03:00 | 109 | 08:00
| Chauddagram | 141 | 09:00 | 130 | 00:00 | Patuakhali | 137 | 04:00 | 134 | 07:00
| Chhatak | 136 | 02:00 | 131 | 20:00 | Payra | 137 | 01:00 | 135 | 10:00
| Chowmuhani | 138 | 19:00 | 126 | 00:00 | PHP | 140 | 13:00 | 130 | 00:00
| Chuadanga | 138 | 02:00 | 124 | 08:00 | Postogola | 139 | 19:00 | 132 | 12:00
| Coxsbazar | 127 | 09:00 | 123 | 00:00 | Purbachal | 138 | 02:00 | 124 | 12:00
| Cumilla(N) | 142 | 08:00 | 136 | 00:00 | Purbasadipur | 131 | 03:00 | 110 | 08:00
| Cumilla(S) | 142 | 14:00 | 127 | 09:00 | Rahanpur | 136 | 01:00 | 132 | 07:00
| Daudkandi | 133 | 09:00 | 126 | 00:00 | Rahim | 135 | 04:00 | 131 | 12:00
| Dhaka | 136 | 03:00 | 130 | 12:00 | Rajbari | 139 | 05:00 | 130 | 04:00
| Dhamrai | 134 | 03:00 | 122 | 12:00 | Rajendrapur | 138 | 19:30 | 125 | 11:00
| Dhanmondi | 136 | 04:00 | 130.5 | 12:00 | Rajshahi | 134 | 09:00 | 126 | 08:00
| Dohazari | 134 | 13:00 | 127 | 00:00 | Rajshahi-230 | 135 | 03:00 | 126 | 08:00
| Faridpur | 139 | 03:00 | 132 | 12:00 | Ramganj | 138 | 14:00 | 127 | 00:00
| Fatullah | 138 | 19:30 | 131 | 12:00 | Rampur | 138 | 20:00 | 132 | 00:00
| Fenchuganj | 139 | 00:00 | 136 | 15:00 | Rampura | 136 | 04:00 | 131 | 12:00
| Feni | 139 | 09:00 | 129 | 00:00 | Rangamati | 138 | 20:00 | 132 | 00:00
| Ghorashal | 143 | 21:00 | 139 | 17:00 | Rangpur | 128 | 00:00 | 115 | 07:00
| Goalpara | 137 | 03:00 | 130 | 08:00 | Ruppur | 140 | 23:00 | 132 | 07:00
| Gollamari | 136 | 03:00 | 129 | 08:00 | Saidpur | 131 | 04:00 | 113 | 08:00
| Gopalganj | 137 | 03:00 | 131 | 08:00 | Satkhira | 134 | 03:00 | 125 | 08:00
| Gopalganj-400 | 139 | 05:00 | 132 | 12:00 | Satmasjid | 139 | 03:00 | 131 | 12:00
| Gulshan | 136 | 05:00 | 130 | 12:00 | Savar | 134 | 19:30 | 125 | 10:00
| Halishahar | 138 | 20:00 | 129 | 00:00 | SevenRings | 144 | 05:00 | 139 | 11:00
| Haripur | 136 | 19:30 | 131 | 12:00 | ShahCement | 137 | 19:30 | 131 | 12:00
| HaripurSBU | 135 | 04:00 | 131 | 12:00 | Shahjadpur | 143 | 03:00 | 135 | 12:00
| Hasnabad | 139 | 19:00 | 133 | 12:00 | Shahjibazar | 136 | 04:00 | 133 | 15:00
| Hathazari | 140 | 19:30 | 135 | 00:00 | Shahmirpur | 137 | 21:00 | 129 | 00:00
| Ishurdi | 141 | 03:00 | 132 | 08:00 | Shariatpur | 138 | 03:00 | 132 | 12:00
| Jaldhaka | 130 | 02:00 | 112 | 08:00 | Sherpur | 125 | 13:00 | 113 | 06:00
| Jamalpur | 130 | 20:00 | 115 | 06:00 | Shikalbaha | 127 | 19:30 | 120 | 00:00
| Jashore | 135 | 02:00 | 125 | 08:00 | Shikalbaha-230 | 138 | 19:30 | 131 | 06:00
| Jhenaidah | 139 | 02:00 | 130 | 08:00 | Shitalakhya | 138 | 19:30 | 132 | 12:00
| Jhenaidah-230 | 141 | 03:00 | 130 | 08:00 | Sholosohor | 138 | 20:00 | 130 | 00:00
| Joydebpur | 145 | 22:00 | 139 | 12:00 | Shyampur | 137 | 09:00 | 129 | 13:00
| Joypurhat | 135 | 01:00 | 116 | 08:00 | Shyampur-230 | 138 | 20:00 | 131 | 12:00
| Juldah | 137 | 19:00 | 130 | 00:00 | Siddhirganj | 136 | 09:00 | 131 | 12:00
| Kabirpur | 137 | 18:30 | 127 | 11:00 | Sirajganj | 136 | 02:00 | 125 | 08:00
| Kachua | 141 | 19:00 | 128 | 00:00 | Sonargaon | 136 | 19:00 | 127 | 00:00
| Kaliakoir | 136 | 02:00 | 128 | 10:00 | Sreemongol | 136 | 01:00 | 133 | 15:00
| Kallyanpur | 137 | 02:00 | 130 | 12:00 | Sreepur | 137 | 05:00 | 128 | 12:00
| Kalurghat | 139 | 20:00 | 132 | 00:00 | Srinagar | 136 | 06:00 | 128 | 12:00
| Kamrangirchar | 135 | 07:00 | 129 | 11:00 | SSM | 140 | 08:00 | 134 | 02:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 03:00 | 132 | 14:00
| Kazla | 134 | 03:00 | 127 | 12:00 | Sylhet | 136 | 23:00 | 134 | 08:00
| Keranigonj | 135 | 03:00 | 128 | 12:00 | Sylhet-132 | 136 | 01:00 | 134 | 11:00
| Khagrachori | 137 | 14:00 | 132 | 01:00 | Tangail | 130 | 13:00 | 122 | 12:00
| Khulna | 136 | 04:00 | 128 | 08:00 | Thakurgaon | 133 | 21:00 | 107 | 08:00
| Khulna(S) | 137 | 05:00 | 129 | 08:00 | TK | 138 | 18:30 | 133 | 02:00
| Khulshi | 137 | 18:30 | 130 | 00:00 | Tongi | 137 | 04:00 | 128 | 11:00
| Kishoreganj | 136 | 03:00 | 131 | 08:00 | Ullahpara | 139 | 03:00 | 131 | 12:00
| Kodda | 141 | 19:00 | 126 | 10:00 | Ullon | 135 | 01:00 | 131 | 12:00
| KSRM | 139 | 21:00 | 131 | 00:00 | Uttara | 137 | 03:00 | 125 | 12:00
| Kulaura | 139 | 04:00 | 136 | 10:00 | UttaraNew | 137 | 02:00 | 125 | 12:00
| Kurigram | 132 | 04:00 | 113 | 08:00 | Zigatola | 137 | 04:00 | 130 | 11:00
| Kushtia | 139 | 03:00 | 130 | 08:00

## L-Curve
Date | 2024-02-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1382 | 4442 | 4255 | 8697 |  |  |  | QF-LDC-11
0:30 | 1206 | 4441 | 4042 | 8483 | Date: | 2024-02-07
1:00 | 1030 | 4440 | 3829 | 8269
1:30 | 1020 | 4347.5 | 3727.5 | 8075
2:00 | 1010 | 4255 | 3626 | 7881
2:30 | 995 | 4231.5 | 3477.5 | 7709 | [5 empty] | Gen. at Eve. Peak | 10886 | 10886 MW (19:00 )
3:00 | 980 | 4208 | 3329 | 7537 | [6 empty] | 19:00
3:30 | 970 | 4152 | 3277 | 7429 | [5 empty] | Gen. at Day Peak | 9964 | 9964 MW (12:00 )
4:00 | 960 | 4096 | 3225 | 7321 | [6 empty] | 12:00
4:30 | 955 | 4088.5 | 3219 | 7307.5 | [5 empty] | Highest Generation | 10886
5:00 | 950 | 4081 | 3213 | 7294 | [6 empty] | 19:00
5:30 | 965 | 4157.5 | 3314 | 7471.5
6:00 | 980 | 4234 | 3415 | 7649
6:30 | 965 | 4416 | 3673.5 | 8089.5
7:00 | 950 | 4598 | 3932 | 8530
7:30 | 981 | 4742.5 | 4156.5 | 8899
8:00 | 1012 | 4887 | 4381 | 9268
8:30 | 1047.5 | 4814 | 4451.5 | 9265.5
9:00 | 1083 | 4741 | 4522 | 9263
9:30 | 1211.5 | 4738.5 | 4595.5 | 9334
10:00 | 1340 | 4736 | 4669 | 9405
10:30 | 1345.5 | 4781 | 4709.5 | 9490.5
11:00 | 1351 | 4826 | 4750 | 9576
11:30 | 1343 | 4910 | 4860 | 9770
12:00 | 1335 | 4994 | 4970 | 9964
12:30 | 1278.5 | 4935.5 | 4932 | 9867.5
13:00 | 1222 | 4877 | 4894 | 9771
13:30 | 1224.5 | 4868 | 4896.5 | 9764.5
14:00 | 1227 | 4859 | 4899 | 9758
14:30 | 1307 | 4982 | 4767.5 | 9749.5
15:00 | 1387 | 5105 | 4636 | 9741
15:30 | 1307 | 4628.5 | 4444.5 | 9073
16:00 | 1227 | 4152 | 4253 | 8405
16:30 | 1261.5 | 4302.5 | 4275 | 8577.5
17:00 | 1296 | 4453 | 4297 | 8750
17:30 | 1193 | 5025 | 4450 | 9475
18:00 | 1090 | 5597 | 4603 | 10200
18:30 | 1130 | 5724.5 | 4818.5 | 10543
19:00 | 1170 | 5852 | 5034 | 10886
19:30 | 1200 | 5759 | 4970 | 10729
20:00 | 1250 | 5497 | 4970 | 10467 |  |  |  | Executive Engineer
20:30 | 1385 | 5359.5 | 5077 | 10436.5 |  |  |  | Network Operation Division
21:00 | 1520 | 5222 | 5184 | 10406
21:30 | 1490 | 4997 | 5033 | 10030
22:00 | 1460 | 4772 | 4882 | 9654 |  |  |  |  | Page 6 of 7
22:30 | 1430 | 4575 | 4760 | 9335
23:00 | 1400 | 4378 | 4638 | 9016
23:30 | 1391 | 4410 | 4446.5 | 8856.5
24:00 | 1382 | 4442 | 4255 | 8697
10886 MW (19:00 )
9964 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-07 |  | Energy |  | 222446329
[15 empty] | 43867 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 2780 | 907 | 1761 | 0 | 214 | 2811 | 46 | 0 | 58 | 110 | 0 | 10 | 0
0:30 | 2691.5 | 812 | 1654 | 0 | 121.5 | 3022 | 46 | 0 | 29 | 102 | 0 | 5 | 0 |  |  | Date: | 43867
1:00 | 2603 | 717 | 1547 | 0 | 29 | 3233 | 46 | 0 | 0 | 94 | 0 | 0 | 0
1:30 | 2601.5 | 622.5 | 1472.5 | 0 | 14.5 | 3221 | 46 | 0 | 0 | 97 | 0 | 0 | 0 | [9 empty] | Total Energy | 222.4463 | 222.4463 | Total Energy Gen 222.446 MKWHr Energy Not Served 2.800 MKWHr Energy Requirement 225.246 MKWHr
2:00 | 2600 | 528 | 1398 | 0 | 0 | 3209 | 46 | 0 | 0 | 100 | 0 | 0 | 0 | [9 empty] | Energy not Served | 2.7995 | 2.7995
2:30 | 2566.5 | 528 | 1370 | 0 | 0 | 3100 | 46 | 0 | 0 | 98 | 0 | 0.5 | 0 | [9 empty] | Energy Requirement | 225.2459 | 225.2459
3:00 | 2533 | 528 | 1342 | 0 | 0 | 2991 | 46 | 0 | 0 | 96 | 0 | 1 | 0
3:30 | 2565 | 528 | 1342.5 | 0 | 0 | 2852.5 | 46 | 0 | 0 | 93 | 0 | 2 | 0 | [8 empty] | Shortage
4:00 | 2597 | 528 | 1343 | 0 | 0 | 2714 | 46 | 0 | 0 | 90 | 0 | 3 | 0
4:30 | 2583.5 | 528.5 | 1342.5 | 0 | 0 | 2712.5 | 46 | 0 | 0 | 93 | 0 | 1.5 | 0
5:00 | 2570 | 529 | 1342 | 0 | 0 | 2711 | 46 | 0 | 0 | 96 | 0 | 0 | 0
5:30 | 2638 | 528.5 | 1431.5 | 0 | 2.5 | 2729 | 46 | 0 | 0 | 96 | 0 | 0 | 0
6:00 | 2706 | 528 | 1521 | 0 | 5 | 2747 | 46 | 0 | 0 | 96 | 0 | 0 | 0
6:30 | 2777 | 669.5 | 1679 | 0 | 146.5 | 2654 | 46 | 0 | 16.5 | 98 | 3 | 0 | 28.5 | [7 empty] | Coal
7:00 | 2848 | 811 | 1837 | 0 | 288 | 2561 | 46 | 0 | 33 | 100 | 6 | 0 | 57
7:30 | 2861 | 855.5 | 1867.5 | 0 | 478 | 2604.5 | 46 | 0 | 36 | 107 | 43 | 0.5 | 81.98 | [6 empty] | Oil
8:00 | 2874 | 900 | 1898 | 0 | 668 | 2648 | 46 | 0 | 39 | 114 | 80 | 1 | 106.96
8:30 | 2805 | 849 | 1846.5 | 0 | 758.5 | 2659 | 46 | 0 | 64.5 | 116 | 120 | 1 | 309.8975
9:00 | 2736 | 798 | 1795 | 0 | 849 | 2670 | 46 | 0 | 90 | 118 | 160 | 1 | 512.835
9:30 | 2669.5 | 798 | 1817 | 0 | 883.5 | 2675.5 | 46 | 0 | 107.5 | 118 | 218.5 | 0.5 | 445.03
10:00 | 2603 | 798 | 1839 | 0 | 918 | 2681 | 46 | 0 | 125 | 118 | 277 | 0 | 377.225
10:30 | 2586 | 852.5 | 1862 | 0 | 916 | 2662.5 | 46 | 0 | 139 | 123 | 303 | 0.5 | 391.1125
11:00 | 2569 | 907 | 1885 | 0 | 914 | 2644 | 46 | 0 | 153 | 128 | 329 | 1 | 405
11:30 | 2610.5 | 906.5 | 1927.5 | 0 | 956 | 2636.5 | 46 | 0 | 207.5 | 128 | 351 | 0.5 | 410.69
12:00 | 2652 | 906 | 1970 | 0 | 998 | 2629 | 46 | 0 | 262 | 128 | 373 | 0 | 416.38
12:30 | 2610 | 906 | 1902 | 0 | 996.5 | 2623.5 | 46 | 0 | 279 | 126 | 378.5 | 0 | 276.19
13:00 | 2568 | 906 | 1834 | 0 | 995 | 2618 | 46 | 0 | 296 | 124 | 384 | 0 | 136
13:30 | 2568 | 906 | 1834 | 0 | 995 | 2618 | 46 | 0 | 296 | 124 | 384 | 0 | 136
14:00 | 2568 | 906 | 1834 | 0 | 995 | 2618 | 46 | 0 | 296 | 124 | 384 | 0 | 136
14:30 | 2734.5 | 905.5 | 1744 | 0 | 971 | 2609.5 | 46 | 0 | 301 | 126 | 318.5 | 0 | 110.5
15:00 | 2901 | 905 | 1654 | 0 | 947 | 2601 | 46 | 0 | 306 | 128 | 253 | 0 | 85
15:30 | 2638.5 | 854.5 | 1607.5 | 0 | 803.5 | 2529 | 46 | 0 | 280.5 | 125 | 188.5 | 0 | 73.5375
16:00 | 2376 | 804 | 1561 | 0 | 660 | 2457 | 46 | 0 | 255 | 122 | 124 | 0 | 62.075
16:30 | 2397.5 | 854.5 | 1596 | 0 | 708 | 2493.5 | 46 | 0 | 284 | 116 | 82 | 0 | 54.9125
17:00 | 2419 | 905 | 1631 | 0 | 756 | 2530 | 46 | 0 | 313 | 110 | 40 | 0 | 47.75
17:30 | 2476 | 877 | 1664.5 | 0 | 1026.5 | 2783 | 46 | 0 | 465 | 115 | 20 | 2 | 66.85
18:00 | 2533 | 849 | 1698 | 0 | 1297 | 3036 | 46 | 0 | 617 | 120 | 0 | 4 | 85.95
18:30 | 2523.5 | 824 | 1765.5 | 0 | 1408 | 3175.5 | 46 | 0 | 672 | 125 | 0 | 3.5 | 87.86
19:00 | 2514 | 799 | 1833 | 0 | 1519 | 3315 | 46 | 0 | 727 | 130 | 0 | 3 | 89.77
19:30 | 2492 | 798 | 1746 | 0 | 1539 | 3285 | 46 | 0 | 698 | 122 | 0 | 3 | 84.5175
20:00 | 2418 | 798 | 1755 | 0 | 1527 | 3100 | 46 | 0 | 700 | 122 | 0 | 1 | 79.265
20:30 | 2387 | 852 | 1831.5 | 0 | 1474 | 3149 | 46 | 0 | 571.5 | 123 | 0 | 2.5 | 84.5175
21:00 | 2356 | 906 | 1908 | 0 | 1421 | 3198 | 46 | 0 | 443 | 124 | 0 | 4 | 89.77
21:30 | 2371 | 906 | 1838.5 | 0 | 1257 | 3134.5 | 46 | 0 | 351 | 122 | 0 | 4 | 105.05
22:00 | 2386 | 906 | 1769 | 0 | 1093 | 3071 | 46 | 0 | 259 | 120 | 0 | 4 | 120.33
22:30 | 2403.5 | 906 | 1780.5 | 0 | 836 | 3043.5 | 46 | 0 | 199.5 | 116 | 0 | 4 | 114.6
23:00 | 2421 | 906 | 1792 | 0 | 579 | 3016 | 46 | 0 | 140 | 112 | 0 | 4 | 108.87
23:30 | 2600.5 | 906.5 | 1776.5 | 0 | 396.5 | 2913.5 | 46 | 0 | 99 | 111 | 0 | 7 | 54.435 |  |  | Max Temp. in Dhaka |  | 26.3°C
24:00 | 2780 | 907 | 1761 | 0 | 214 | 2811 | 46 | 0 | 58 | 110 | 0 | 10 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 222.446 MKWHr Energy Not Served 2.800 MKWHr Energy Requirement 225.246 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-02-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1112842
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 182019
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 9 | 14 | 17 | 17 | 16 | 10 | 10 | 5 | 1 | [9 empty] | 104085
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 205 | 205 | 205 | 205 | 205 | 206 | 206 | 202 | 205 | 205 |  | 204 | 204 | 204 | 204 | 204 | 204 | 205 | 4838495
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [7 empty] | 6 | 51 | 51 | 51 | 51 | 51 | 51 | 49 | 51 | 63 | 68 |  | 68 | 68 | 68 | 68 | 17 | 17 | 0 | 747534
12 | Hathazari 100 MW peaking PP | [11 empty] | 8 | 8 | 8 | 8 | 8 | 10 | 24 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 146688
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 258436
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [8 empty] | 6 | 41 | 33 | 41 | 42 | 42 | 41 |  |  | 9 |  | 33 | 33 | 33 | 25 | 25 | 0 | 0 | 393182
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 41 | 40 | 42 | 42 | 42 | 65 | 103 | 102 | 101 | 62 | 100 | 99 | 101 | 59 | 59 |  | 38 | 63 |  | 62 | 38 | 39 | 37 | 39 | 38 | 41 | 1602000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 25 | 45 | 62 | 72 | 65 | 80 | 80 | 52 | 47 | 30 | 30 | 30 |  | 75 | 95 | 95 | 95 | 95 | 0 | 0 | 1056327
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 180 | 180 | 180 | 180 | 140 | 160 | 134 | 140 | 140 | 140 | 140 | 140 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 3902000
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 295 | 297 | 280 | 280 | 280 | 180 | [19 empty] | 0 | 1696363
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 12 | 20 | 20 | 20 | 20 | 196056
33 | Ashuganj 225 MW CCPP | 134 | 151 | 155 | 150 | 152 | 152 | 153 | 138 | 143 | 155 | 142 | 144 | 147 | 149 | 146 | 147 | 149 | 153 |  | 152 | 155 | 154 | 157 | 157 | 158 | 158 | 3610000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 305 | 300 | 360 | 290 | 315 | 270 | 270 | 270 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 7207000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 320 | 285 | 310 | 300 | 325 | 280 | 315 | 310 | 350 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7418000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | [26 empty] | 0
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 291 | 271 | 248 | 212 | 202 | 228 | 298 | 280 | 230 | 47 | 27 | 40 | 61 | 185 | 383 | [8 empty] | 54 | 84 | 232 | 3816000
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 96 | 96 | 96 | 97 | 98 | 98 | 320 | 385 | 370 | 370 | 360 | 340 | 320 | 320 | 320 | 320 | 320 | 320 |  | 300 | 320 | 330 | 330 | 330 | 330 | 330 | 6416364
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 340 | 340 | 300 | 300 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 360 | 420 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9583000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 74 | 86 | 86 | 96 | 98 | 98 | 72 | 68 | 68 | 32 | 32 | 32 | 27 | 27 | 29 | 30 | 32 | 34 |  | 36 | 37 | 51 | 62 | 62 | 61 | 68 | 1304640
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 12 | 28 | 42 | 51 | 54 | 51 | 45 | 36 | 19 | 5 | 0 | [8 empty] | 340440
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 995000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 946560
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 58 | 56 | 58 | 58 | 20 | [8 empty] | 5 | 20 | 30 | 921408
48 | Shahjibazar 86 MW PP (Shahjibazar) | [25 empty] | 0 | 0
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 142 | 142 | 143 | 141 | 143 | 145 |  | 145 | 145 | 50 |  |  |  | 0 | 2889190
51 | Sylhet 20 MW GTPP | [25 empty] | 20 | 17000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250560
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 40 | 11 | 10 | 10 | [18 empty] | 51 | 53 | 53 | 53 | 262200
56 | Shahjahanulla 25 MW PP | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 23 | 572256
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 280 | 300 | 310 | 310 | 310 | 320 | 300 | 290 | 315 | 310 | 305 | 300 | 285 | 290 | 305 | 280 |  | 305 | 275 | 270 | 300 | 265 | 290 | 290 | 7258500
| Bibiyana South 400 MW | 350 | 340 | 340 | 320 | 320 | 320 | 320 | 320 | 320 | 400 | 400 | 400 | 400 | 385 | 350 | 350 | 370 | 400 |  | 400 | 400 | 400 | 380 | 350 | 350 | 350 | 8593800
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 |  |  |  |  | 0 | 39001
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 44880
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 16 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 378384
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 94 | 100 | 96 | 90 | 96 | 96 | 100 | 114 | 118 | 118 | 128 | 128 | 124 | 128 | 128 | 122 | 110 | 120 |  | 130 | 122 | 122 | 124 | 120 | 112 | 110 | 3187200
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 37 | 37 | 37 | 37 | 19 | 7 | 6 | 6 | 4 | 4 | 3 | 2 | 0 | 0 | 8 | 13 |  | 20 | 20 | 24 | 27 | 34 | 32 | 40 | 470400
65 | Feni 22 MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 17 | 316116
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 209880
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 8 | 8 | 8 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 32 | 25 | 25 | 663500
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 16 | 10 | 10 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 11 | 342990
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 18 | 17 | 17 | 408000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  | 14 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 439560
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 722300
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 31 | 28 | 28 | 26 | 26 | 26 | 26 | 26 |  | 22 | 22 |  | 22 | 22 | 22 | 22 | 26 | 26 | 26 | 632700
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 326181
| Feni Lanka Power | [6 empty] | 52 | 98 | 98 | 98 | 98 | 98 | 98 | 114 | 98 | 34 | 34 | 74 |  | 114 | 114 | 114 | 114 | 114 | 34 | 0 | 1445520
| Chowmuhani 113 MW | [7 empty] | 9 | 9 | 9 | 9 | 30 | 38 | 39 | 42 | 48 | 48 | 56 |  | 57 | 57 | 58 | 58 | 58 | 48 | 0 | 622440
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 8 | 50 | 68 | 68 | 67 | 67 | 61 | 59 | 59 |  | 6 | 15 |  | 8 | 8 | 8 | 8 | 8 | 0 |  | 592858
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 198240
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 32 | 32 | 16 | 16 | 16 | 16 | 32 | 120 |  | 149 | 149 | 149 | 32 | 16 | 16 | 16 | 741120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 139099
| Gazipur 100 MW PP | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | 105 | 105 | 105 | 105 | 52 | 0 | 825600
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 3 | 2 | 4 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 18117
| Jodiac Power | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | [10 empty] | 0 | 123941
| Karnaphuli Power Ltd. | [6 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 308620
82 | Madanganj 102 PP(Summit) | [6 empty] | 25 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 44 | 2 | 38 |  | 80 | 80 | 80 | 80 | 51 | 20 | 0 | 993528
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 4 |  |  |  |  | 5 | 10 | [7 empty] | 0 | 12169
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 1 | 36 | 85 | 93 | 99 | 100 | 63 | 59 | 59 |  |  | 3 |  | 43 | 66 | 68 | 68 | 15 | 0 | 0 | 842880
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 38 |  | 51 | 51 | 53 | 53 | 53 | 53 | 53 | 483840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima) | [22 empty] | 25 | 25 | 25 | 25 | 100944
93 | Ashuganj 51 MW PP (Midland) | 43 | 10 | 10 | 10 | 10 | 23 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 909402
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 45 | 24 | 50 | 75 |  | 91 | 91 | 91 | 91 | 50 | 33 | 0 | 842112
95 | Patenga 50MW PP (Baraka) | [6 empty] | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 185760
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 3 | 15 | 15 | 15 | 15 |  |  | 12 |  | 25 | 15 | 15 | 15 | 15 | 15 | 0 | 200920
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 40734
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 120 | 120 | 163 | 120 | 163 |  | 163 | 120 | 120 | 163 | 130 | 130 | 163 | 3532173
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13050
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 38520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [5 empty] | 3 | 56 | 56 | 56 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 67 | 67 |  | 67 | 67 | 67 | 67 | 9 | 9 | 9 | 928800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 20 | [5 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 487296
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 331200
116 | Chandpur 200 MW (Desh energy) | [6 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 306240
117 | Ashuganj 150 MW PP (Midland) | [6 empty] | 2 | 5 | 6 | 6 | 10 | 13 | 11 | 13 | 13 | 13 | 13 | 16 |  | 15 | 20 | 18 | 16 | 20 | 20 | 20 | 235854
118 | Bibiyana-III 400 MW CCPP |  |  |  | 115 | 134 | 135 | 135 | 134 | 135 | 135 | 135 | 135 | 135 | 135 | 300 | 300 | 275 | 225 |  | 150 | 150 | 150 | 150 | 150 | 150 | 315 | 3605000
| Jamalpur 115 MW PP (United) | 9 |  |  |  |  | 2 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 182400
| Anwara 300 MW PP (United) | [6 empty] | 16 | 16 | 49 | 49 | 50 | 50 | 57 | 49 | 49 | 50 | 50 | 102 |  | 105 | 105 | 105 | 106 | 65 | 0 | 0 | 973527
| Juldah unit-2 (Acorn) | [10 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 324480
| Anlima Energy Ltd. | [6 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 308618
| Bhairob 54.5 MW | [8 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | [10 empty] | 0 | 124560
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 6 | 15 | 23 | 29 | 20 | 30 | 27 | 21 | 0 | 4 | [9 empty] | 189978
| Chandpur 115(Doreen) | [12 empty] | 13 | 18 | 18 | 18 | 25 | 37 |  | 37 | 36 | 36 | 36 | 20 | 0 | 0 | 274560
| Kanchan Purbachal Power Generation Ltd. | [17 empty] | 31 |  | 17 | 17 | 17 |  |  |  | 0 | 72360
| Mirsharai 150 MW (Oil) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 128 |  | 145 | 145 | 145 | 17 | 17 | 17 | 0 | 618909
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 4 |  | 3 | 3 | 1 | 4 | 4 | 4 | 10 | 38400
| Matarbari 2*600 MW (CPGCL) | 568 | 569 | 569 | 396 | 404 | 403 | 274 | 158 | 6 | [6 empty] | 10 | 198 | 567 |  | 566 | 517 | 335 | 275 | 156 | 155 | 155 | 6123636
120 | Eastern Zone Total | 4440 | 4255 | 4208 | 4096 | 4081 | 4234 | 4598 | 4887 | 4741 | 4736 | 4826 | 4994 | 4877 | 4859 | 5105 | 4152 | 4453 | 5597 |  | 5852 | 5759 | 5497 | 5222 | 4772 | 4378 | 4442 | 115350842
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [11 empty] | 8 | 11 | 11 | 11 | 23 | 47 | 47 |  | 53 | 42 | 35 | 23 |  |  |  | 247680
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 71 |  | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 674880
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 14 | 32 | 47 | 70 | 61 | 61 | 65 | 46 | 25 | 9 | [9 empty] | 443520
131 | Rampal 1320 MW (BIFPCL) | 358 | 359 | 358 | 360 | 356 | 359 | 358 | 359 | 356 | 358 | 357 | 357 | 357 | 360 | 359 | 362 | 358 | 355 |  | 359 | 359 | 359 | 360 | 360 | 360 | 360 | 8640000
132 | United Payra Power Ltd. | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 |  | 54 | 54 | 54 | 17 | 17 | 0 | 0 | 378000
133 | Bhola Nutan Biddut BD LTD (GAS) | 98 | 110 | 101 | 94 | 92 | 92 | 91 | 90 | 110 | 110 | 110 | 220 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 108 | 2482934
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 99360
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 184 |  | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 3883600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 80 | 80 | 80 | 80 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 90 | 90 | 90 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2749000
140 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 6 |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 132125
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [10 empty] | 20 | 56 | 65 | 60 | 55 | 30 | 30 | 36 |  | 50 | 32 | 40 | 48 | 17 | 0 |  | 479616
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 717 | 528 | 528 | 528 | 529 | 528 | 811 | 900 | 798 | 798 | 907 | 906 | 906 | 906 | 905 | 804 | 905 | 849 |  | 799 | 798 | 798 | 906 | 906 | 906 | 907 | 19227636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 930 | 900 | 790 | 720 | 720 | 740 | 850 | 1050 | 1230 | 1244 | 1210 | 1200 | 1200 | 1160 | 1090 | 920 | 840 | 850 |  | 1000 | 1020 | 1020 | 1080 | 1070 | 1070 | 1000 | 25856400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4139200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  | 26 | 26 | 26 | 26 |  |  |  | 277553
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 3 | 5 | 4 | 2 | 0 | [9 empty] | 33420
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 150 | 150 | 130 | 130 | 130 | 167 | 206 | 206 | 189 | 190 | 178 | 168 | 163 | 161 | 158 | 155 | 175 |  | 173 | 171 | 170 | 158 | 158 | 165 | 173 | 4247545
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 355 | 357 | 320 | 348 | 348 | 414 | 414 | 414 | 360 | 414 | 414 | 414 | 414 | 350 | 300 | 250 | 280 | 291 |  | 414 | 380 | 380 | 380 | 300 | 300 | 230 | 8634618
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 10 |  | 15 | 15 | 15 | 15 | 4 | 0 |  | 64127
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 |  | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 79812
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 |  |  | 0 | 263390
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 42 | 42 | 42 |  |  |  | 42 | 16 | 8 | 8 | 25 |  | 25 | 8 | 8 | 8 |  |  | 0 | 359370
167 | Katakhali 50 MW Peaking PP | [13 empty] | 22 | 24 | 24 | 24 | 30 |  | 49 | 49 | 50 | 50 | 48 | 0 |  | 319810
168 | Santahar 50 MW Peaking PP | [11 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 32 |  | 32 | 32 | 32 | 32 | 24 | 24 |  | 192637
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 8 | 8 | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 71957
170 | Chapainawabganj 100 MW Peaking PP | [11 empty] | 45 | 48 | 47 | 47 | 48 | 48 | 83 |  | 91 | 91 | 91 | 91 | 75 | 50 | 42 | 765440
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 1 | 26 | 35 | 37 | 35 | 35 | 35 | 35 | [10 empty] | 0 | 269856
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 262944
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 20 | 34 | 35 |  | 35 | 35 | 35 | 35 | 35 | 0 | 0 | 271286
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 4 | 2 | 2 | 1 | [9 empty] | 16238
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 17 | 35 | 50 |  | 70 | 70 | 72 | 72 |  |  | 0 | 339648
| Intraco Solar 30 MW | [6 empty] | 0 | 2 | 16 | 11 | 29 | 36 | 37 | 32 | 21 | 12 | 3 | 0 | [8 empty] | 189317
| Adani Power Jharkhanda Ltd | 762 | 764 | 674 | 638 | 631 | 745 | 759 | 761 | 758 | 759 | 757 | 752 | 741 | 819 | 832 | 845 | 814 | 910 |  | 1020 | 1019 | 1016 | 1113 | 1115 | 1111 | 976 | 20001818
178 | Teesta Solar Limited | [6 empty] | 3 | 39 | 56 | 130 | 124 | 172 | 179 | 151 | 110 | 57 | 17 | [9 empty] | 1000750