## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-02-13 | Tuesday
|  | Date (day): | 2024-02-13 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11393.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12276 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-12 | 2024-02-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 180 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 390 | 104 | 412 | 412 |  |  |  |  | 2024-02-12
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  |  | Line S/D
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 54 | 90 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 50 | 65 | 85 | 85 | 17 |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 25 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 62 | 105 | 105 | 105 |  | GT-2 S/D Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 30 | 84 | 60 | 60 |  | 40 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 42 | 83 | 40 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 16 | 98 | 51 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 34 | 41 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 62 | 82 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 24 | 142 | 17 | 51 | 98
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 0 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 17 | 35 | 127 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 100 | 38 | 340 | 340 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1438 | 1686 | 2000 | 2389 | 1518 | 1039
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 46 | 46 | 184 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 211 | 210 | 210 | 15
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 | 98 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 51 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 18 | 18 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 20 | 2 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 128 | 60 | 150 | 150 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 17 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 145 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 498 | 540 | 550 | 550 | 674
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 6 | 10 | 20 | 20 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 0 | 0 | 0 | 0 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1023 | 1314 | 1156 | 1372 | 2076 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 151 | 151 | 150 | 150 |  | 71 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 285 | 280 | 280 | 80 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 280 | 280 | 80 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 35 | 25 | 35
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 43 | 43 |  | 8 | Engine problem
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 13 | 18 | 13 | 28 | 122 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 24 | 32 | 40 | 40 |  | 12 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 30 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 17 | 16 | 16 |  | 6 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 108 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 60 | 114 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 78 | 48 | 65 | 48 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 40 | 0 | 36 | 79 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1094 | 1257 | 1237 | 1328 | 1231 | 307
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 29 | 46 | 30 | 50 | 152 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9 | 9 | 191 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 57 | 69 | 46 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 147 | 130 | 147.6 | 134 | 152 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 20 | 20 | 20 | 20
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 59 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 121 | 207 | 210 | 210 |  | 21 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 20 | 16 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 24 | 24
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 320 | 320 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 250 | 309 | 300 | 310 |  | 90 | ST under maint
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 340 | 390 | 400 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1318 | 1388 | 1488 | 1508 | 0 | 781
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 624 | 926 | 926
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 0 | 54 |  | Fuel shortage
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 0 | 55 |  | 54 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 35 | 94 | 74 | 31 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 76 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 359 | 0 | 0 | 0 |  | 330 | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1377 | 709 | 1120 | 1055 | 1337 | 384
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 5 | 7 | 10 | 10 |  | 30 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 70 | 70 |  | 124 | ST, GT-1 Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1040 | 1210 | 1200 | 1240 |  | 4
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 180 | 200 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 150 | 35 | 150 |  |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 307 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1460 | 1870 | 1822 | 2013 | 94 | 158
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 25 | 25 | 27 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 8 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 25 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 48 | 48 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 164 | 160 | 180 | 40 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 380 | 350 | 380 | 34 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 8 | 8
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 0 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 82 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 35 | 35 | 0 | 113 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 54 | 35 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1211 | 1305 | 1300 | 1300
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1807 | 2168 | 2079 | 2199 | 1149 | 78
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 34 | 6 | 34 | 79 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 0 | 74 | 41 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 170 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 387 | 276 | 344 | 278 | 245 | 189
| Total |  |  |  |  | 26504 | 25481 | 10051 | 10798 | 11393.6 | 12276 | 7802 | 3266
A. |  | 2024-02-12 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10798 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7115 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10900 | MW
3 | Day peak Generation : |  |  | 10051 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10416.76 | MW
4 | Evening peak Generation : |  |  | 10798 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 97 | MW
5 | Total Energy Generation : |  | 222.2461 | MKWHr | By Solar | 2.5432 | MKWHr
| By Gas : | 99.819 | MKWHr |  | By Oil: | 20.1797 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 77.537 | MKWHr |  | By Hydro: | 1.0796 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.1992 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7802 | MW | Dhaka | 3839.86 | 3839.86 |  | 0 |  | 18:00 |  | 89
|  |  | For Plants S/D or M/C prob = |  |  | 3266 | MW | Chittagong | 989 | 989 |  | 0 |  | 19:00 |  | 97.41
|  |  | Total = |  |  | 11068 | MW | Khulna | 1208.5 | 1208.5 |  | 0 |  | 19:30 |  | 69.715
7 | Total Gas Supplied : |  |  | 787.09 | MMCFD |  |  | Rajshahi | 1100.6 | 1100.6 |  | 0 |  | 20:00 |  | 66.85
8 | Fuel Cost : | i) Gas : | Taka | 297477895.61 | ii) Oil : | Taka | 365428457.94 | Comilla | 890 | 890 |  | 0 |  | 21:00 |  | 59
|  | iii) Coal : | Taka | 527256768.53 | Total | Taka | 1190163122.08 | Mymensingh | 954 | 857 |  | 97 |  | 22:00 |  | 81
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 373 | 373 |  | 0 |  | 23:00 |  | 63
| ii) During Peak Demand : |  |  | 1180 | MW (W to E) at | 19:00 | hrs | Barisal | 284.8 | 284.8 |  | 0 |  | 24:00 |  | 39
| iii) Maximum : |  |  | 1000 | MW at | 7:00 | hrs | Rangpur | 777 | 777 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.3°C |  |  | Total | 10416.76 | 10319.76 |  | 97
B. |  | 2024-02-13 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 29.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12276 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10300 | MW
4 | Reserve(Generation end) |  |  |  | 976 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 232.5783 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7288 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.4058 | MKWHr. | ii) HVDC Flow at Peak Time |  | 624 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4826 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.99 |  | (b) Today: | 85.84 |  | (c) Rule Curve: |  | 95.32
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-02-12 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 402 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 280 | 270 | 155 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 17 | 9 | 33 | 9 | 94 | 71 | 0 | 0 | 0 | 42 | 40 | 53 | 42 | 0 | 0 | 60 | 0 | 0 | 21 | 0 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 25 | 0 | 0 | 0 | 0 | 300 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 443 | 0 | 0 | 0 | 60 |  | 801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 1072 | 0 | 0 |  | 4053 | 4120 | 8173 | 3040 | 801 | 1067 | 0 | 43 | 3066 | 46 | 0 | 16 | 94 | 0 | 0 | 0 | 86.01
2:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 403 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 280 | 270 | 155 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 33 | 9 | 90 | 71 | 0 | 0 | 0 | 42 | 40 | 53 | 42 | 0 | 0 | 61 | 0 | 0 | 52 | 0 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 0 | 0 | 0 | 110 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 972 | 0 | 0 |  | 4071 | 3678 | 7749 | 3080 | 624 | 1116 | 0 | 0 | 2793 | 46 | 0 | 0 | 90 | 0 | 0 | 0 | 86.01
3:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 404 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 27 | 0 | 0 | 0 | 280 | 270 | 157 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 25 | 9 | 86 | 71 | 0 | 0 | 0 | 42 | 40 | 53 | 42 | 0 | 0 | 61 | 0 | 0 | 55 | 0 | 0 | 10 | 295 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 3 | 0 | 0 | 110 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 913 | 0 | 0 |  | 3921 | 3524 | 7445 | 3082 | 624 | 1119 | 0 | 0 | 2485 | 46 | 0 | 0 | 86 | 0 | 3 | 0 | 86
4:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 389 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 31 | 0 | 0 | 0 | 290 | 275 | 154 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 25 | 9 | 90 | 87 | 0 | 0 | 0 | 42 | 40 | 53 | 42 | 0 | 0 | 40 | 0 | 0 | 65 | 0 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 9 | 0 | 0 | 110 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 819 | 0 | 0 |  | 3908 | 3303 | 7211 | 3041 | 624 | 1108 | 0 | 0 | 2293 | 46 | 0 | 0 | 90 | 0 | 9 | 0 | 86
5:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 352 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 32 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 31 | 0 | 0 | 0 | 295 | 285 | 155 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 0 | 9 | 80 | 86 | 0 | 0 | 0 | 42 | 40 | 53 | 42 | 0 | 0 | 40 | 0 | 0 | 65 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293 | 10 | 0 | 0 | 120 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 150 | 825 | 0 | 0 |  | 3867 | 3248 | 7115 | 2969 | 624 | 1087 | 0 | 0 | 2299 | 46 | 0 | 0 | 80 | 0 | 10 | 0 | 85.99
6:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 352 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 0 | 0 | 290 | 280 | 150 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 0 | 9 | 90 | 81 | 0 | 0 | 0 | 42 | 40 | 53 | 42 | 0 | 0 | 40 | 0 | 0 | 65 | 0 | 0 | 10 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 13 | 0 | 0 | 120 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 150 | 951 | 0 | 0 |  | 3916 | 3518 | 7434 | 2968 | 624 | 1124 | 0 | 33 | 2536 | 46 | 0 | 0 | 90 | 0 | 13 | 0 | 85.99
7:00 | 0 | 0 | 150 | 0 | 0 | 12 | 0 | 366 | 0 |  | 0 | 0 | 0 | 6 | 8 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 24 | 0 | 0 | 0 | 315 | 305 | 129 | 0 | 0 | 30 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 0 | 7 | 92 | 67 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 65 | 0 | 0 | 10 | 310 | 17 | 0 | 0 | 1 | 0 | 0 | 9 | 0 | 2 | 1 | 0 | 1 | 1 | 300 | 57 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 395 | 17 | 2 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 330 | 13 | 0 | 0 | 120 |  | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 200 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 362 | 1 | 150 | 1103 | 6 | 0 |  | 4194 | 4063 | 8257 | 3100 | 730 | 1146 | 0 | 129 | 2955 | 46 | 0 | 33 | 92 | 13 | 13 | 70 | 85.98
8:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 431 | 0 |  | 0 | 0 | 0 | 50 | 45 | 0 | 335 | 0 | 0 | 24 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 3 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 14 | 2 | 0 | 0 | 0 | 280 | 270 | 149 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 0 | 1 | 18 | 9 | 0 | 9 | 102 | 68 | 0 | 0 | 1 | 42 | 40 | 53 | 20 | 0 | 0 | 61 | 0 | 0 | 65 | 0 | 0 | 10 | 305 | 17 | 0 | 0 | 35 | 0 | 0 | 9 | 0 | 17 | 6 | 4 | 15 | 6 | 300 | 57 | 17 | 17 | 1 | 15 | 0 | 14 | 80 | 0 | 5 | 340 | 17 | 12 | 0 | 17 | 0 | 0 | 6 | 0 | 0 | 0 | 17 | 0 | 430 | 12 | 0 | 0 | 120 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 300 | 35 | 0 | 6 | 0 | 6 | 0 | 1 | 0 | 1120 | 220 | 0 | 17 | 0 | 21 | 0 | 0 | 0 | 361 | 7 | 150 | 1319 | 45 | 0 |  | 4671 | 4594 | 9265 | 3110 | 624 | 1088 | 0 | 600 | 3550 | 46 | 0 | 33 | 102 | 100 | 12 | 81.175 | 85.98
9:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 423 | 0 |  | 0 | 0 | 0 | 84 | 78 | 0 | 335 | 0 | 0 | 56 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 6 | 14 | 2 | 0 | 0 | 0 | 280 | 260 | 157 | 0 | 0 | 25 | 0 | 0 | 43 | 0 | 14 | 8 | 18 | 9 | 25 | 9 | 106 | 32 | 0 | 0 | 1 | 42 | 40 | 53 | 20 | 0 | 0 | 61 | 0 | 0 | 65 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 47 | 0 | 0 | 9 | 0 | 17 | 11 | 25 | 18 | 5 | 300 | 56 | 17 | 17 | 2 | 49 | 1 | 17 | 98 | 0 | 25 | 340 | 17 | 28 | 0 | 17 | 0 | 0 | 11 | 0 | 0 | 0 | 17 | 0 | 443 | 4 | 0 | 0 | 111 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 56 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1120 | 220 | 0 | 17 | 1 | 42 | 0 | 0 | 0 | 364 | 18 | 150 | 1311 | 92 | 0 |  | 4944 | 4730 | 9674 | 3081 | 624 | 1074 | 0 | 892 | 3558 | 46 | 0 | 81 | 106 | 208 | 4 | 82.13 | 85.67
10:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 390 | 0 |  | 0 | 0 | 0 | 84 | 80 | 2 | 290 | 0 | 0 | 60 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 6 | 14 | 10 | 0 | 0 | 0 | 280 | 260 | 149 | 0 | 0 | 28 | 0 | 0 | 43 | 0 | 33 | 8 | 18 | 9 | 25 | 13 | 110 | 30 | 0 | 0 | 2 | 42 | 40 | 53 | 20 | 0 | 0 | 60 | 0 | 0 | 66 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 77 | 0 | 0 | 9 | 0 | 17 | 16 | 25 | 17 | 6 | 249 | 59 | 17 | 17 | 4 | 65 | 17 | 17 | 98 | 3 | 25 | 340 | 17 | 26 | 0 | 17 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 0 | 440 | 0 | 0 | 0 | 120 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 55 | 0 | 35 | 0 | 6 | 0 | 4 | 0 | 1030 | 180 | 0 | 17 | 3 | 61 | 0 | 0 | 0 | 362 | 27 | 150 | 1266 | 130 | 0 |  | 4942 | 4629 | 9571 | 2969 | 624 | 1031 | 0 | 975 | 3418 | 46 | 0 | 100 | 110 | 298 | 0 | 80 | 85.97
11:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 382 | 0 |  | 0 | 0 | 0 | 61 | 55 | 15 | 290 | 0 | 0 | 37 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 6 | 14 | 5 | 0 | 0 | 0 | 280 | 240 | 149 | 0 | 0 | 28 | 0 | 0 | 43 | 0 | 32 | 8 | 18 | 9 | 33 | 13 | 116 | 30 | 0 | 0 | 2 | 43 | 40 | 53 | 20 | 0 | 0 | 60 | 0 | 0 | 73 | 20 | 0 | 10 | 290 | 12 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 23 | 17 | 25 | 17 | 12 | 250 | 59 | 17 | 17 | 4 | 30 | 17 | 17 | 52 | 18 | 25 | 340 | 17 | 45 | 0 | 17 | 0 | 0 | 28 | 0 | 0 | 0 | 17 | 0 | 440 | 0 | 0 | 0 | 118 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 35 | 0 | 35 | 0 | 8 | 0 | 6 | 0 | 1040 | 180 | 0 | 17 | 4 | 75 | 0 | 0 | 0 | 360 | 32 | 150 | 1214 | 161 | 0 |  | 4777 | 4956 | 9733 | 2917 | 909 | 1035 | 0 | 813 | 3374 | 46 | 0 | 149 | 116 | 374 | 0 | 90 | 85.96
12:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 390 | 0 |  | 0 | 0 | 0 | 54 | 50 | 15 | 335 | 0 | 0 | 30 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 6 | 14 | 12 | 0 | 0 | 0 | 280 | 240 | 151 | 0 | 0 | 28 | 0 | 0 | 43 | 0 | 24 | 8 | 18 | 9 | 33 | 13 | 126 | 29 | 0 | 0 | 2 | 43 | 40 | 53 | 20 | 0 | 0 | 59 | 0 | 0 | 121 | 20 | 0 | 10 | 290 | 12 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 24 | 19 | 25 | 30 | 13 | 250 | 59 | 17 | 17 | 4 | 30 | 17 | 17 | 60 | 18 | 25 | 400 | 17 | 48 | 17 | 17 | 0 | 0 | 29 | 0 | 0 | 0 | 17 | 0 | 498 | 6 | 0 | 0 | 100 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 35 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1040 | 180 | 0 | 35 | 5 | 76 | 0 | 0 | 0 | 359 | 35 | 200 | 1211 | 170 | 0 |  | 5020 | 5031 | 10051 | 3078 | 907 | 1025 | 0 | 850 | 3478 | 46 | 0 | 141 | 126 | 394 | 6 | 95 | 85.96
13:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 408 | 0 |  | 0 | 0 | 0 | 82 | 50 | 15 | 335 | 0 | 0 | 30 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 6 | 14 | 9 | 0 | 0 | 0 | 280 | 240 | 152 | 0 | 0 | 28 | 0 | 0 | 43 | 0 | 32 | 8 | 17 | 9 | 33 | 13 | 124 | 27 | 0 | 0 | 2 | 43 | 40 | 53 | 20 | 0 | 0 | 59 | 0 | 0 | 118 | 16 | 0 | 10 | 280 | 12 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 25 | 18 | 25 | 17 | 13 | 306 | 59 | 17 | 17 | 4 | 72 | 17 | 17 | 114 | 58 | 25 | 340 | 17 | 45 | 35 | 17 | 0 | 0 | 29 | 10 | 0 | 0 | 17 | 0 | 522 | 7 | 0 | 0 | 70 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 350 | 17 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 1060 | 220 | 0 | 0 | 4 | 47 | 0 | 0 | 0 | 360 | 35 | 220 | 1213 | 174 | 0 |  | 5206 | 5003 | 10209 | 3090 | 908 | 1071 | 0 | 889 | 3545 | 46 | 0 | 165 | 124 | 364 | 7 | 87 | 85.95
14:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 385 | 0 |  | 0 | 0 | 0 | 57 | 14 | 15 | 300 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 51 | 0 | 0 | 6 | 14 | 5 | 0 | 0 | 0 | 280 | 240 | 147 | 0 | 0 | 28 | 0 | 0 | 43 | 0 | 32 | 8 | 16 | 9 | 33 | 13 | 126 | 28 | 0 | 0 | 2 | 43 | 40 | 53 | 20 | 0 | 0 | 58 | 0 | 0 | 119 | 16 | 0 | 10 | 285 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 26 | 16 | 25 | 17 | 12 | 230 | 59 | 17 | 17 | 3 | 30 | 0 | 17 | 34 | 67 | 25 | 340 | 17 | 43 | 35 | 17 | 0 | 0 | 26 | 18 | 0 | 0 | 17 | 0 | 500 | 8 | 0 | 0 | 62 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 1090 | 220 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 360 | 30 | 220 | 1184 | 159 | 0 |  | 4767 | 4990 | 9757 | 2966 | 908 | 1064 | 0 | 598 | 3524 | 46 | 0 | 165 | 126 | 352 | 8 | 113 | 85.96
15:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 381 | 0 |  | 0 | 0 | 0 | 43 | 0 | 15 | 300 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 50 | 0 | 0 | 6 | 14 | 1 | 0 | 0 | 0 | 280 | 240 | 149 | 0 | 0 | 35 | 0 | 0 | 43 | 0 | 32 | 8 | 16 | 9 | 33 | 13 | 120 | 30 | 0 | 0 | 1 | 43 | 40 | 53 | 20 | 0 | 0 | 56 | 0 | 0 | 118 | 16 | 0 | 10 | 300 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 30 | 12 | 25 | 17 | 13 | 230 | 59 | 17 | 17 | 2 | 30 | 0 | 17 | 34 | 68 | 25 | 340 | 0 | 30 | 17 | 17 | 0 | 0 | 18 | 18 | 0 | 0 | 17 | 0 | 500 | 7 | 0 | 0 | 62 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 1080 | 220 | 0 | 0 | 1 | 42 | 0 | 0 | 0 | 358 | 24 | 180 | 1144 | 116 | 0 |  | 4690 | 4817 | 9507 | 2965 | 907 | 1074 | 0 | 541 | 3432 | 46 | 0 | 164 | 120 | 251 | 7 | 89 | 0
16:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 42 | 0 | 15 | 334 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 50 | 0 | 0 | 6 | 14 | 0 | 0 | 0 | 0 | 325 | 240 | 145 | 0 | 0 | 35 | 0 | 0 | 43 | 0 | 32 | 8 | 16 | 9 | 33 | 13 | 114 | 32 | 0 | 0 | 1 | 43 | 40 | 52 | 20 | 0 | 0 | 56 | 0 | 0 | 120 | 16 | 0 | 10 | 295 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 4 | 25 | 17 | 13 | 270 | 59 | 17 | 17 | 1 | 30 | 0 | 17 | 34 | 68 | 25 | 372 | 0 | 19 | 35 | 17 | 0 | 0 | 11 | 18 | 0 | 0 | 17 | 0 | 500 | 6 | 0 | 0 | 62 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 350 | 0 | 0 | 0 | 0 | 23 | 0 | 3 | 0 | 1000 | 220 | 0 | 0 | 1 | 22 | 7 | 0 | 0 | 358 | 13 | 150 | 1119 | 69 | 0 |  | 4441 | 4638 | 9079 | 2746 | 908 | 1067 | 0 | 587 | 3297 | 46 | 0 | 164 | 114 | 144 | 6 | 116 | 85.94
17:00 | 0 | 0 | 141 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 62 | 20 | 15 | 300 | 0 | 0 | 40 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 32 | 8 | 0 | 46 | 0 | 0 | 0 | 6 | 212 | 0 | 0 | 0 |  | 1 | 0 | 50 | 0 | 0 | 6 | 14 | 10 | 0 | 0 | 0 | 280 | 240 | 147 | 0 | 0 | 35 | 0 | 0 | 43 | 0 | 32 | 8 | 17 | 9 | 33 | 13 | 112 | 34 | 0 | 0 | 0 | 43 | 40 | 51 | 20 | 0 | 0 | 58 | 0 | 0 | 160 | 16 | 0 | 10 | 285 | 12 | 0 | 0 | 5 | 0 | 0 | 19 | 0 | 65 | 1 | 25 | 17 | 13 | 260 | 59 | 17 | 17 | 0 | 60 | 0 | 17 | 70 | 68 | 25 | 340 | 0 | 4 | 17 | 17 | 0 | 0 | 4 | 28 | 9 | 0 | 17 | 0 | 508 | 4 | 0 | 0 | 59 |  | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 300 | 0 | 0 | 0 | 0 | 33 | 0 | 1 | 0 | 990 | 190 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 359 | 4 | 150 | 1171 | 19 | 0 |  | 4534 | 4581 | 9115 | 2665 | 917 | 985 | 0 | 831 | 3348 | 46 | 0 | 174 | 112 | 33 | 4 | 91 | 85.93
18:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 93 | 34 | 22 | 335 | 0 | 0 | 82 | 42 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 10 | 33 | 32 | 17 | 0 | 46 | 0 | 0 | 0 | 11 | 212 | 0 | 0 | 0 |  | 6 | 0 | 51 | 20 | 0 | 0 | 14 | 19 | 0 | 0 | 0 | 290 | 240 | 148 | 0 | 0 | 35 | 0 | 0 | 43 | 0 | 32 | 8 | 17 | 9 | 33 | 13 | 114 | 35 | 0 | 0 | 0 | 43 | 40 | 51 | 20 | 0 | 0 | 58 | 0 | 0 | 200 | 16 | 0 | 10 | 280 | 12 | 0 | 0 | 30 | 0 | 0 | 19 | 0 | 126 | 0 | 25 | 17 | 13 | 307 | 68 | 70 | 17 | 0 | 101 | 0 | 17 | 70 | 68 | 25 | 345 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 41 | 35 | 0 | 145 | 0 | 529 | 10 | 0 | 0 | 61 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 25 | 4 | 77 | 0 | 8 | 8 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 350 | 9 | 0 | 3 | 0 | 35 | 0 | 0 | 30 | 1000 | 190 | 0 | 18 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 198 | 1205 | 0 | 0 |  | 5319 | 4518 | 9837 | 2800 | 908 | 1043 | 0 | 1331 | 3102 | 46 | 0 | 483 | 114 | 0 | 10 | 89 | 85.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 65 | 25 | 335 | 0 | 62 | 84 | 83 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 15 | 33 | 32 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 25 | 0 | 6 | 14 | 20 | 0 | 0 | 0 | 285 | 240 | 151 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 16 | 17 | 9 | 33 | 13 | 108 | 46 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 59 | 0 | 0 | 207 | 16 | 0 | 10 | 280 | 12 | 0 | 0 | 62 | 0 | 0 | 9 | 0 | 142 | 0 | 25 | 17 | 18 | 309 | 69 | 105 | 17 | 0 | 128 | 0 | 17 | 114 | 78 | 25 | 340 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 40 | 17 | 0 | 145 | 0 | 540 | 10 | 0 | 0 | 38 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 34 | 8 | 82 | 0 | 25 | 48 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 380 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 54 | 1210 | 180 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1305 | 0 | 0 |  | 5775 | 5023 | 10798 | 3028 | 624 | 1051 | 0 | 1823 | 3532 | 46 | 0 | 576 | 108 | 0 | 10 | 97.41 | 85.91
19:30 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 217 | 0 |  | 0 | 0 | 0 | 59 | 77 | 15 | 300 | 0 | 37 | 84 | 83 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 15 | 33 | 25 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 25 | 0 | 6 | 14 | 22 | 0 | 0 | 0 | 280 | 240 | 151 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 16 | 17 | 9 | 33 | 15 | 106 | 70 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 207 | 16 | 0 | 10 | 260 | 12 | 0 | 0 | 65 | 0 | 0 | 9 | 0 | 149 | 0 | 25 | 17 | 26 | 310 | 69 | 105 | 17 | 0 | 160 | 0 | 17 | 114 | 68 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 36 | 0 | 0 | 145 | 0 | 570 | 12 | 0 | 0 | 30 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 6 | 16 | 0 | 0 | 0 | 34 | 12 | 82 | 0 | 25 | 50 | 0 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 56 | 0 | 35 | 0 | 34 | 0 | 0 | 54 | 1120 | 180 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 260 | 1329 | 0 | 0 |  | 5801 | 4886 | 10687 | 3053 | 624 | 994 | 0 | 1817 | 3449 | 46 | 0 | 586 | 106 | 0 | 12 | 69.715 | 0
20:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 375 | 0 |  | 0 | 0 | 0 | 48 | 58 | 15 | 300 | 0 | 42 | 62 | 83 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 15 | 33 | 25 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 0 | 0 | 6 | 14 | 27 | 0 | 0 | 0 | 280 | 240 | 151 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 16 | 17 | 9 | 33 | 15 | 108 | 71 | 0 | 0 | 0 | 43 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 270 | 12 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 142 | 0 | 25 | 17 | 26 | 306 | 69 | 105 | 17 | 0 | 100 | 0 | 17 | 70 | 70 | 25 | 340 | 13 | 0 | 17 | 17 | 0 | 0 | 0 | 36 | 0 | 0 | 90 | 0 | 584 | 16 | 0 | 0 | 60 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 20 | 7 | 16 | 0 | 0 | 0 | 34 | 20 | 82 | 0 | 0 | 50 | 0 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 60 | 0 | 35 | 0 | 35 | 0 | 0 | 55 | 1120 | 180 | 0 | 54 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 260 | 1264 | 0 | 0 |  | 5748 | 4702 | 10450 | 3235 | 623 | 1010 | 0 | 1477 | 3398 | 46 | 0 | 537 | 108 | 0 | 16 | 66.85 | 85.92
21:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 373 | 0 |  | 0 | 0 | 0 | 9 | 17 | 15 | 300 | 0 | 42 | 9 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 0 | 0 | 6 | 14 | 34 | 0 | 0 | 0 | 280 | 240 | 151 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 33 | 8 | 17 | 9 | 33 | 15 | 108 | 71 | 0 | 0 | 0 | 43 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 310 | 12 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 149 | 0 | 25 | 17 | 26 | 309 | 69 | 105 | 17 | 0 | 100 | 0 | 17 | 70 | 68 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 33 | 0 | 0 | 17 | 0 | 565 | 16 | 0 | 0 | 60 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 70 | 4 | 16 | 0 | 0 | 0 | 25 | 20 | 82 | 0 | 0 | 50 | 0 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 75 | 0 | 35 | 0 | 34 | 0 | 0 | 55 | 1120 | 180 | 0 | 54 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 260 | 1257 | 0 | 0 |  | 5462 | 4736 | 10198 | 3294 | 624 | 1054 | 0 | 1322 | 3372 | 46 | 0 | 362 | 108 | 0 | 16 | 59 | 85.91
22:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 371 | 0 |  | 0 | 0 | 0 | 8 | 8 | 15 | 300 | 0 | 38 | 0 | 83 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 0 | 0 | 6 | 14 | 35 | 0 | 0 | 0 | 285 | 240 | 151 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 33 | 8 | 17 | 9 | 33 | 15 | 98 | 71 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 275 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 149 | 0 | 25 | 17 | 26 | 132 | 9 | 70 | 17 | 0 | 84 | 0 | 17 | 70 | 68 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 565 | 17 | 0 | 0 | 50 |  | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 16 | 0 | 0 | 0 | 25 | 20 | 82 | 0 | 0 | 50 | 8 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 75 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1080 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 1258 | 0 | 0 |  | 5032 | 4633 | 9665 | 3115 | 820 | 1010 | 0 | 922 | 3333 | 40 | 0 | 310 | 98 | 0 | 17 | 81 | 85.91
23:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 370 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 300 | 0 | 40 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 6 | 14 | 36 | 0 | 0 | 0 | 285 | 240 | 153 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 33 | 8 | 17 | 9 | 33 | 15 | 100 | 74 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 280 | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 149 | 0 | 25 | 17 | 21 | 80 | 9 | 70 | 17 | 0 | 16 | 0 | 17 | 9 | 27 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 530 | 19 | 0 | 0 | 60 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 75 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 1214 | 0 | 0 |  | 4662 | 4347 | 9009 | 3066 | 907 | 1026 | 0 | 619 | 3067 | 40 | 0 | 165 | 100 | 0 | 19 | 63 | 85.9
24:00 | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 371 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 33 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 14 | 34 | 0 | 0 | 0 | 285 | 275 | 154 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 0 | 8 | 17 | 9 | 33 | 13 | 96 | 74 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 40 | 0 | 0 | 210 | 16 | 0 | 10 | 295 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 137 | 0 | 25 | 17 | 8 | 80 | 9 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 0 | 25 | 340 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 520 | 20 | 0 | 0 | 60 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1211 | 0 | 0 |  | 4453 | 4266 | 8719 | 3092 | 907 | 1043 | 0 | 355 | 3051 | 40 | 0 | 115 | 96 | 0 | 20 | 39 | 85.9
KWH | 0 | 0 | 3809000 | 0 | 0 | 287500 | 0 | 7999200 | 0 |  | 0 | 0 | 0 | 873600 | 535743 | 241036 | 7401612 | 0 | 325000 | 503040 | 800208 | 561120 | 0 | 0 | 0 | 0 | 38880 | 40123 | 39075 | 0 | 450000 | 346680 | 814640 | 774400 | 202080 | 0 | 1079640 | 0 | 0 | 0 | 134422 | 5004426 | 0 | 0 | 0 |  | 45120 | 0 | 654561 | 42960 | 0 | 106080 | 340992 | 465600 | 0 | 0 | 0 | 7284500 | 6334000 | 3648000 | 0 | 0 | 739800 | 0 | 0 | 1082704 | 0 | 478975 | 160526 | 413460 | 210420 | 603000 | 281460 | 2482560 | 1272000 | 0 | 0 | 13350 | 1005000 | 959280 | 1276200 | 663624 | 0 | 0 | 1251264 | 0 | 0 | 2723100 | 243000 | 0 | 249480 | 7146000 | 257424 | 0 | 0 | 582109 | 0 | 0 | 194400 | 0 | 1342800 | 123660 | 405120 | 312000 | 252581 | 6436000 | 973200 | 720960 | 299418 | 24000 | 991091 | 77811 | 297745 | 1125180 | 819840 | 397440 | 8265100 | 206400 | 303840 | 194400 | 298582 | 0 | 0 | 177218 | 275520 | 68760 | 0 | 600509 | 0 | 10794544 | 199200 | 0 | 0 | 2025000 |  | 18405818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138624 | 0 | 284000 | 125414 | 128544 | 0 | 0 | 0 | 138334 | 57214 | 887232 | 112810 | 155579 | 180464 | 73661 | 143872 | 0 | 0 | 93240 | 0 | 0 | 4125600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4006673 | 0 | 7927054 | 657120 | 0 | 310464 | 0 | 273465 | 0 | 40962 | 200640 | 24795700 | 4993718 | 0 | 484800 | 28200 | 470880 | 343488 | 0 | 0 | 6458182 | 230519 | 4385500 | 26977455 | 1130560 | 0 |  | 113480293 | 108765786 | 222246079 | 73576671 | 18405818 | 26242294 | 0 | 16338821 | 77536981 | 1079640 | 0 | 3840905 | 2482560 | 2543189 | 199200 | 0
Fuel Cost | 0 | 0 | 16340610 | 0 | 0 | 1098250 | 0 | 23037696 | 0 |  | 0 | 0 | 0 | 16904160 | 11175598.98 | 4143408.84 | 22574916.6 | 0 | 1738750 | 9693580.8 | 14883868.8 | 10335830.4 | 0 | 0 | 0 | 0 | 709948.8 | 641566.77 | 714681.75 | 0 | 337500 | 0 | 0 | 0 | 3619252.8 | 0 | 0 | 0 | 0 | 0 | 2545952.68 | 15964118.94 | 0 | 0 | 0 |  | 792307.2 | 0 | 11723187.51 | 796048.8 | 0 | 1746076.8 | 1268490.24 | 0 | 0 | 0 | 0 | 20323755 | 19382040 | 12111360 | 0 | 0 | 2493126 | 0 | 0 | 4341643.04 | 0 | 8578442.25 | 2889468 | 1538071.2 | 157815 | 2243160 | 211095 | 16285593.6 | 3955920 | 0 | 0 | 0 | 3919500 | 3578114.4 | 5806710 | 3019489.2 | 0 | 0 | 6944515.2 | 0 | 0 | 7597449 | 1598940 | 0 | 997920 | 22081140 | 193068 | 0 | 0 | 12020550.85 | 0 | 0 | 3713040 | 0 | 23955552 | 0 | 6996422.4 | 5491200 | 4253464.04 | 17055400 | 14413092 | 12977280 | 5194902.3 | 0 | 18374827.14 | 1518870.72 | 4746055.3 | 20635801.2 | 15191635.2 | 7078406.4 | 21985166 | 3451008 | 0 | 3555576 | 5075894 | 0 | 0 | 0 | 4559856 | 1177171.2 | 0 | 10743106.01 | 0 | 75237971.68 | 0 | 0 | 0 | 0 |  | 54113104.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2607517.44 | 0 | 897440 | 594462.36 | 2216098.56 | 0 | 0 | 0 | 2477561.94 | 1049876.9 | 14914369.92 | 2400596.8 | 2965335.74 | 3232110.24 | 1303063.09 | 2576747.52 | 0 | 0 | 70582.68 | 0 | 0 | 34820064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13342221.09 | 0 | 23146997.68 | 11907014.4 | 0 | 6190652.16 | 0 | 5493911.85 | 0 | 0 | 3880377.6 | 149022157 | 15530462.98 | 0 | 9380880 | 0 | 0 | 5815251.84 | 0 | 0 | 45853092.2 | 0 | 32671975 | 189651508.65 | 0 | 0 |  | 622436386.04 | 638125434.56 | 1260561820.6 | 220860820.35 | 54113104.92 | 76617075.26 | 0 | 297189707.81 | 527256768.53 | 0 | 0 | 68238750.13 | 16285593.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 390 | 0 |  | 0 | 0 | 0 | 54 | 50 | 15 | 335 | 0 | 0 | 30 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 30 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 6 | 14 | 12 | 0 | 0 | 0 | 280 | 240 | 151 | 0 | 0 | 28 | 0 | 0 | 43 | 0 | 24 | 8 | 18 | 9 | 33 | 13 | 126 | 29 | 0 | 0 | 2 | 43 | 40 | 53 | 20 | 0 | 0 | 59 | 0 | 0 | 121 | 20 | 0 | 10 | 290 | 12 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 24 | 19 | 25 | 30 | 13 | 250 | 59 | 17 | 17 | 4 | 30 | 17 | 17 | 60 | 18 | 25 | 400 | 17 | 48 | 17 | 17 | 0 | 0 | 29 | 0 | 0 | 0 | 17 | 0 | 498 | 6 | 0 | 0 | 100 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 25 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 35 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1040 | 180 | 0 | 35 | 5 | 76 | 0 | 0 | 0 | 359 | 35 | 200 | 1211 | 170 | 0 |  | 10051 | DayPeak
Yesterday Evening Peak | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 104 | 0 |  | 0 | 0 | 0 | 90 | 65 | 25 | 335 | 0 | 62 | 84 | 83 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 15 | 33 | 32 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 | 0 | 6 | 0 | 51 | 25 | 0 | 6 | 14 | 20 | 0 | 0 | 0 | 285 | 240 | 151 | 0 | 0 | 35 | 0 | 0 | 51 | 0 | 32 | 16 | 17 | 9 | 33 | 13 | 108 | 46 | 0 | 0 | 0 | 42 | 40 | 53 | 20 | 0 | 0 | 59 | 0 | 0 | 207 | 16 | 0 | 10 | 280 | 12 | 0 | 0 | 62 | 0 | 0 | 9 | 0 | 142 | 0 | 25 | 17 | 18 | 309 | 69 | 105 | 17 | 0 | 128 | 0 | 17 | 114 | 78 | 25 | 340 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 40 | 17 | 0 | 145 | 0 | 540 | 10 | 0 | 0 | 38 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 7 | 16 | 0 | 0 | 0 | 34 | 8 | 82 | 0 | 25 | 48 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 380 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 54 | 1210 | 180 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1305 | 0 | 0 |  | 10798 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 412 | 0 |  | 0 | 0 | 0 | 100 | 85 | 15 | 335 | 0 | 105 | 60 | 92 | 98 | 25 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 22 | 33 | 33 | 17 | 0 | 46 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 0 | 51 | 25 | 0 | 19 | 18 | 20 | 0 | 0 | 0 | 280 | 280 | 150 | 0 | 0 | 35 | 0 | 0 | 43 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 141 | 50 | 0 | 0 | 0 | 43 | 40 | 51 | 20 | 0 | 0 | 60 | 0 | 0 | 210 | 20 | 0 | 10 | 320 | 24 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 51 | 0 | 25 | 17 | 28 | 310 | 69 | 105 | 17 | 0 | 150 | 0 | 17 | 114 | 65 | 25 | 400 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 0 | 145 | 0 | 550 | 20 | 0 | 0 | 340 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 70 | 10 | 16 | 0 | 0 | 0 | 25 | 15 | 90 | 28 | 42 | 50 | 8 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 380 | 74 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1240 | 220 | 0 | 150 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 307 | 1300 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 12 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 100 | 85 | 15 | 335 | 0 | 105 | 60 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 33 | 8 | 0 | 46 | 0 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 0 | 0 | 51 | 25 | 0 | 6 | 18 | 2 | 0 | 0 | 0 | 280 | 280 | 150 | 0 | 0 | 25 | 0 | 0 | 43 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 128 | 30 | 0 | 0 | 1.6 | 43 | 40 | 51 | 20 | 0 | 0 | 60 | 0 | 0 | 210 | 20 | 0 | 10 | 320 | 24 | 0 | 0 | 82 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 13 | 300 | 57 | 17 | 17 | 5 | 60 | 17 | 17 | 114 | 48 | 25 | 390 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 0 | 17 | 0 | 550 | 20 | 0 | 0 | 340 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 28 | 34 | 48 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 94 | 0 | 35 | 0 | 6 | 0 | 8 | 35 | 1200 | 200 |  | 35 | 6 | 100 | 0 | 0 |  | 0 | 30 | 307 | 1300 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 441 | 0 | 0 | 0 | 0 | 0 | 12 | 5 | 0 | 335 | 0 | 40 | 12 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 0 | 33 | 8 | 0 | 40 | 0 | 0 | 0 | 6 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 6 | 14 | 2 | 0 | 0 | 0 | 285 | 280 | 153 | 0 | 0 | 10 | 0 | 0 | 51 | 0 | 0 | 3 | 15 | 0 | 33 | 9 | 102 | 70 | 0 | 0 | 1 | 39 | 40 | 8 | 5 | 0 | 0 | 61 | 0 | 0 | 210 | 16 | 0 | 10 | 305 | 12 | 0 | 0 | 5 | 0 | 0 | 9 | 0 | 17 | 5 | 25 | 17 | 6 | 320 | 56 | 17 | 17 | 2 | 60 | 0 | 17 | 106 | 0 | 25 | 230 | 17 | 14 | 0 | 17 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 0 | 542 | 28 | 0 | 0 | 100 | 0 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 25 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 414 | 24 | 0 | 5 | 0 | 6 | 0 | 1 | 0 | 1100 | 220 | 0 | 17 | 1 | 17 | 0 | 0 | 0 | 0 | 7 | 190 | 1257 | 51 | 0 | 0 |  |  |  | 99818965 | 18405818 | 0 | 77536981 | 20179726 | 2482560 | 2543189 | 199200 | 1079640
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 99.819 | 18.4058 | 0 | 77.537 | 20.1797 | 2.4826 | 2.5432 | 0.1992 | 1.0796
| Minimum Generation |  | 7115 | 5:00
| Highest Generation |  | 10798 | 19:00 | [129 empty] | 0 | [70 empty] | 222.2461
| Day Peak Generation |  | 10051 | 12:00
| Evening Peak Generation |  | 10798 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 917 | 17:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 624 | 19:00
| Load factor L.F |  | 85.76% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-02-13
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10051 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7288
Evening Peak Generation : |  |  | 10798 | MW Hour : | 19:00 | Available Max Generation : |  | 12276
E.P. Demand (at gen end) : |  |  | 10900 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11300
Maximum Generation : |  |  | 10798 | MW Hour : | 19:00 | Reserve(Generation end) |  | 976
Total Gen. (MKWH) : |  |  | 222.2461 | System Load Factor : | 85.76% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1000 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-13
Actual : |  | 85.84 | Ft.(MSL) , | Rule curve : | 95.32 | Ft.( MSL )
Gas Consumed : |  | Total = | 787.09 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 297477895.61
: |  |  | Coal : | 527256768.53 | Oil : | 365428457.94 | Total : | 1190163122.08
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3823.072 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1045.9496 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1463.8103 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1271.063 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1046.4992 |  |  | 0 | 0%
Mymensingh Area |  | 97 | 2328:00 | 777.6683 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 436.6164 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 363.2198 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 710.409 |  |  | 0 | 0%
Total |  | 97 |  | 10938.3077 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj East
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:58 | 18:16 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Deadline checking. and from
Haripur 230/132kV end Due to Dead line checking.
9:07 | 17:42 | Keranigonj 230/132/33kV S/S Hasnabad Scheduled S/D Due to Deadline checking in Hasnabad end. Hasnabad line 1&2
both are shutdown.
9:07 | 17:43 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead line checking from sreenagar end.
9:16 | - | Hasnabad 132/33kV S/S Keraniganj-1 (Pre- Lalbag) Scheduled S/D Due to Dead line purpose.
9:18 | 12:54 | Shyampur-Shyampur(New) 132kV Ckt-2 Forced S/D from Shyampur 230/132kV end Due to Maintenance of Shyampur Old end.
9:21 | - | Hasnabad 132/33kV S/S Keraniganj-2 (Pre- Aourahati) Scheduled S/D Due to Dead line Checking purpose.
9:25 | 13:43 | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to Oil Leakage.
9:25 | 13:42 | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to Oil Leakage.
9:27 | - | Rampura 230/132kV S/S Auto Transformer - 03 HT Scheduled S/D Due to TX-3 replacement work.
9:27 | 14:48 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Annual maintenance(Bay).
9:27 | - | Rampura 230/132kV S/S Aux Transformer-03 LT Scheduled S/D Due to TX-3 replacement work.
9:30 | 17:47 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar 132/33kV end Due to Keraniganj-2
Deadline Checking and from Keranigonj 230/132/33kV end Due to Deadline checking in Srinagar end.
9:54 | 19:31 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to Dead line check and from
Kishoreganj 132/33kVend.
10:17 | 17:42 | Sreepur 230/132/33kV S/S Auxiliary Transformer - 2 LT Project Work S/D Due to SAS Integration by Siemens.
10:17 | 16:52 | Sreepur 230/132/33kV S/S 230/132 kV T-2 HT Project Work S/D Due to SAS Integration by Siemens.
10:17 | 16:52 | Sreepur 230/132/33kV S/S 230/132 kV T-2 LT Project Work S/D Due to SAS Integration by Siemens.
10:17 | 17:42 | Sreepur 230/132/33kV S/S Auxiliary Transformer - 2 HT Project Work S/D Due to SAS Integration by Siemens.
10:57 | 11:59 | Bogura 400/230kV S/S ATR-02 LT Project Work S/D Due to SAS commissioning work.
11:40 | 13:39 | Kushtia 132/33kV S/S T-1 LT Forced S/D.
11:41 | 13:38 | Kushtia 132/33kV S/S T-1 HT Forced S/D.
12:00 | - | Day peak generation:10051MW
12:08 | 13:05 | Bogura 400/230kV S/S ATR-03 LT Project Work S/D Due to SAS commissioning work.
12:20 | 14:37 | Haripur 230/132kV S/S 132kV Main Bus Sec-1 Scheduled S/D Due to 132 Sonargaon-1 Main Bus Isolator Y-phase to Main
Busbar loop changing work.
12:39 | 17:00 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D Due to 132KV Busbar modification.
12:39 | 17:00 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D Due to 132KV Busbar modification.
13:32 | 14:04 | Sholosohor 132/33kV S/S TRAFO-02 LT Forced S/D Due to Bird nest removing by BPDB.
- | 13:33 | Ishurdi-Pabna 132kV ckt is restored.
- | 13:38 | Juldah 132/33kV S/S Julda power plant unit-1 is restored.
14:43 | 14:55 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing line Distance Relay 21L relays Due to Trip. |  |  |  |  | 16.0MW load interrup.
- | 15:10 | Bogura 230/132kV S/S 230KV Main 2 is restored.
15:44 | - | Haripur 412 MW CCPP Tripped with remarks:- ST
15:47 | - | Haripur 412 MW CCPP Tripped with remarks:- GT
15:47 | 18:32 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing line Distance Relay 21L relays Due to Trip.
16:07 | - | Mirsorai 230/33kV S/S Bus-1 Project Work S/D Due to Project work.
16:18 | 19:06 | Mongla 132/33kV S/S 100MW ERBL Solar PS Scheduled S/D Due to Annual maintenance Work. |  |  |  |  | 20.0MW load interrup.
16:26 | 17:15 | Bogura 132/33kV S/S Transformer-1 HT Forced S/D Due to Oil Leakage of OLTC.
16:26 | 17:16 | Bogura 132/33kV S/S Transformer-1 LT Forced S/D Due to Oil Leakage of OLTC.
- | 16:33 | Aminbazar-Meghnaghat 230kV Ckt-1 is restored.
16:34 | 21:25 | Joydebpur 132/33kV S/S GT-2 HT Forced S/D Due to Oil fallen from PRD.
- | 16:49 | Juldah 132/33kV S/S 133/33 KV T-2 416T HT is restored.
- | 16:51 | Naogaon 132/33kV S/S T-3 HT is restored.
- | 16:55 | Juldah 132/33kV S/S 133/33 KV T-2 416T LT is restored.
- | 17:09 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 is restored.
17:56 | - | Rampal 1320 MW (BIFPCL) Tripped with remarks:- unit-1.
17:56 | - | Rampal 1320 MW (BIFPCL) Tripped with remarks:- unit-2.
18:00 | - | Haripur 412 MW CCPP Syncronized with remarks:- GT.
19:00 | - | Evening peak generation:10798 MW.
- | 19:04 | Ishurdi 132/33kV S/S 132 kV Baghabari Line is restored.
19:14 | - | Haripur 412 MW CCPP Syncronized with remarks:- ST.
19:54 | - | Bhola 225 MW CCPP Syncronized with remarks:- GT1.
2:14 | - | Meghnaghat CCPP(Summit)-2 Syncronized with remarks:- ST.
3:02 | - | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST.
3:02 | - | Meghnaghat CCPP(Summit)-2 Syncronized with remarks:- GT Running.
5:00 | - | Minimum Generation: 7288 MW.
7:02 | - | Thakurgaon 132/33kV S/S T-1(422T) HT Scheduled S/D. |  |  |  |  | 12.0MW load interrup.
7:02 | - | Thakurgaon 132/33kV S/S T-1(422T) LT Scheduled S/D. |  |  |  |  | 12.0MW load interrup.
7:03 | - | Thakurgaon 132/33kV S/S RPC Scheduled S/D.
7:12 | - | Madaripur 132/33kV S/S T2-415T HT Scheduled S/D Due to Incoming CB -Replacement work.
7:13 | - | Madaripur 132/33kV S/S T2-415T LT Scheduled S/D Due to Incoming CB -Replacement work.
7:15 | - | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Feni 132/33kV end Due to reconducting work.
7:45 | - | Mirpur 132/33kV S/S T3 LT Scheduled S/D Due to T-3, Annual maintenance work .
7:45 | - | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to T-3 33kv ds to 33kv bus conductor change. |  |  |  |  | 30.0MW load interrup.
06:00 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T LT Project Work S/D |  |  |  |  | 20.0MW
|  | Due to project work |  |  |  |  | load
interrup.
06:15 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT Project Work S/D |  |  |  |  | 20.0MW
|  | Due to project work |  |  |  |  | load
interrup.
06:16 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 LT Scheduled S/D Due |  |  |  |  | 20.0MW
|  | to project work |  |  |  |  | load
interrup.
06:18 |  | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha
230/132kV end.
06:58 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Project Work S/D |  |  |  |  | 20.0MW
|  | Due to project work |  |  |  |  | load
interrup.
07:05 |  | Bogura 230/132kV S/S 230KV Main 2 Project Work S/D Due to
X-Former T-04 Jack Bus (Upper Bus) Conductor Stringing.
07:46 |  | Aminbazar-Meghnaghat 230kV Ckt-1 Scheduled S/D from
Aminbazar 400/230/132kV end Due to OPGW maintenace
07:52 |  | Ishurdi 132/33kV S/S 132 kV Baghabari Line Project Work S/D
Due to project work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 180 | 3809000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 287500 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 104 | 7999200 | Synchronized at 18:00
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Line shutdown
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 90 | 873600 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 65 | 535743 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 25 | 241036 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 62 | 325000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 84 | 503040 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7401612
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 83 | 800208 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 38880 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 561120 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 40123 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 39075 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 796680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 814640
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 774400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 202080 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 62 | 582109 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 142 | 1342800
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 720960
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 206400 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 177218
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 68760 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 38 | 2025000 | On test.
| Dhaka area Total |  |  |  | 5062 | 1686 | 31360584
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 134422 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 123660
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 106080 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1079640 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 211 | 5004426
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 299418 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 654561 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 42960 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 405120 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 340992 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 465600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 128 | 991091 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 77811 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 297745 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 397440 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 298582 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 600509
| SS Power I |  | SS Power | 2*612 | 1224 | 540 | 10794544
| Cox's Bazar Wind |  | IPP | 66 | 0 | 10 | 199200 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 0 | 0 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1314 | 22337801
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 151 | 3648000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7284500 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6334000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 739800 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1082704
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 18 | 252581 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 478975 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 312000 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 413460 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 210420 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2482560
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 603000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 160526 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 13 | 281460 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1125180
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 819840 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 0 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 40 | 275520 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1257 | 26504526
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 46 | 1272000 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13350
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 194400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 973200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 303840
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 45120 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 130 | 2801910
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1005000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 959280 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1276200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 20 | 663624 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1251264
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 2723100
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 243000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 257424 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7146000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 309 | 6436000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 249480
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8265100 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1388 | 30475472
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 624 | 18405818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 138624 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 657120 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 470880
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 6458182 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 709 | 26130624
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 128544 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 7 | 125414 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 284000 | Under maint.
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1210 | 24795700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 4993718
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 484800 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4385500
| Barisal Area Total |  |  |  | 2265 | 1870 | 35197676
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 138334 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 8 | 57214 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 112810 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 155579 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 48 | 180464
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 164 | 4006673 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 380 | 7927054 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 143872 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 93240 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 73661 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 887232 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 310464 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 54 | 200640 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28200
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1305 | 26977455
| Rajshahi Area Total |  |  |  | 3631 | 2168 | 41292892
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4125600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 273465 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40962
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 343488 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230519
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1130560
| Rangpur Area Total |  |  |  | 950 | 276 | 6144594
| Total |  |  |  | 25481 | 10798 | 222246079
| Eastern Grid Total |  |  |  | 15398 | 5775 | 113480293
| Western Grid Total |  |  |  | 10083 | 5023 | 108765786
| National Grid Total |  |  |  | 25481 | 10798 | 222246079
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-12
| (a) ENTIRE EASTERN GRID : |  | 6948.86 | MW | (b) ENTIRE WESTERN GRID : |  | 3370.9 | MW
| i) Dhaka area |  | 3839.86 | MW | i) Khulna area |  | 1208.5 | MW
| ii) Chittagong area |  | 989 | MW | ii) Rajshahi area |  | 1100.6 | MW
| iii) Comilla area |  | 890 | MW | iii) Barisal area |  | 284.8 | MW
| iv) Mymensingh area |  | 857 | MW | iv) Rangpur area |  | 777 | MW
| v) Sylhet area |  | 373 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10319.76 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 23 | 21:00 | Kamrangirchar | 47.7 | 19:30 | Narinda | 48 | 12:00 | Sherpur | 108 | 01:00
2 | AKSML | 10 | 15:00 | Chowmuhani | 141 | 19:30 | Kaptai | N/A | N/A | Narshingdi | 148 | 19:30 | Shikalbaha | 18 | 19:00
3 | Aftabnagar | 26 | 13:00 | Chuadanga | 74 | 18:30 | Kazla | 70 | 15:00 | Natore | 107 | 18:30 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 59 | 13:00 | Coxsbazar | 86 | 07:00 | Keranigonj | 60 | 13:00 | Nawabganj | 28.2 | 13:00 | Shitalakhya | 74.2 | 12:00
5 | Agrabad | 44 | 18:00 | Cumilla(N) | 108 | 18:00 | Khagrachori | 26 | 18:30 | Netrakona | 109 | 15:00 | Sholosohor | 34 | 09:00
6 | Amnura | 63 | 09:00 | Cumilla(S) | 126 | 12:00 | Khulna | 71 | 13:00 | New | 17.2 | 12:00 | Shyampur | 120 | 00:00
7 | Ashuganj | 48 | 12:00 | Daudkandi | 109 | 18:30 | Khulshi | 148 | 13:00 | Niamatpur | 82 | 13:00 | Siddhirganj | 96 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 16 | 12:00 | Kishoreganj | 117 | 19:00 | Noapara | 38.5 | 19:00 | Sirajganj | 90 | 19:00
9 | BSRM | 87 | 17:00 | Dhamrai | 134 | 08:00 | Kodda | 255 | 18:00 | PHP | 10 | 17:00 | Sonargaon | 99 | 11:00
10 | Bagerhat | 69 | 19:00 | Dhanmondi | 100.6 | 13:00 | Kulaura | 28 | 12:00 | Pabna | 79 | 19:00 | Sreemongol | 43 | 18:30
11 | Bakulia | 63 | 18:00 | Dohazari | 61 | 20:00 | Kurigram | 65 | 08:00 | Palashbari | 96 | 08:00 | Sreepur | 58 | 15:00
12 | Banani | 20.6 | 14:00 | Faridpur | 112 | 18:30 | Kushtia | 102 | 19:00 | Panchagarh | 45 | 18:30 | Srinagar | 28.9 | 21:00
13 | Bangabhaban | 8 | 15:00 | Fatullah | 50 | 12:00 | Lalbag | 70 | 13:00 | Patuakhali | 51.8 | 19:00 | Sunamganj | 36 | 18:30
14 | Barapukuria | 57 | 09:00 | Fenchuganj | 23 | 20:00 | Lalmonirhat | 41 | 18:30 | Payra | 14 | 18:30 | Sylhet | 14 | 11:00
15 | Barguna | 12 | 00:00 | Feni | 78 | 18:00 | MI_Cement | 12.2 | 09:00 | Postogola | 39 | 13:00 | Sylhet-132 | 88 | 18:00
16 | Barishal | 76 | 07:00 | GPH | 85 | 09:00 | Madanganj | 32 | 00:00 | Purbachal | 14 | 18:00 | TK | 14 | 18:30
17 | Barishal-230 | 72 | 18:30 | Ghorashal | 66 | 23:00 | Madaripur | 65 | 19:30 | Purbasadipur | 116 | 13:00 | Tangail | 156 | 18:00
18 | Baroaulia | 56 | 10:00 | Goalpara | 26 | 12:00 | Madartek | 57.8 | 18:30 | Rahim | 34 | 10:00 | Thakurgaon | 79 | 18:30
19 | Baroirhat | 34 | 14:00 | Gollamari | 39 | 13:00 | Madunaghat | 36 | 18:30 | Rajbari | 50 | 18:30 | Tongi | 140 | 12:00
20 | Bashundhara | 118 | 12:00 | Gopalganj | 71 | 19:00 | Magura | 46 | 18:30 | Rajendrapur | 90 | 18:30 | Ullahpara | 81 | 17:00
21 | BashundharaCement | 5 | 11:00 | Gulshan | 70 | 13:00 | Mahasthangarh | 60 | 08:00 | Rajshahi | 104 | 19:00 | Ullon | 32 | 14:00
22 | Beanibazar | 42 | 19:30 | Halishahar | 76 | 10:00 | Manikganj | 82 | 18:30 | Rajshahi-230 | 25 | 19:30 | Uttara | 43 | 13:00
23 | Benapole | 53 | 08:00 | HaripurSBU | 147 | 13:00 | Maniknagar | 54 | 13:00 | Ramganj | 68 | 21:00 | UttaraNew | 30 | 13:00
24 | Bhaluka | 118 | 18:30 | Hasnabad | 62 | 13:00 | Matarbari | 34 | 12:00 | Rampur | 23 | 11:00 | Zigatola | 58 | 18:30
25 | Bhandaria | 32 | 18:30 | Hathazari | 55 | 13:00 | Matuail | 57 | 16:00 | Rangamati | 12 | 18:30
26 | Bhangura | 26 | 18:30 | Ishurdi | 49 | 18:30 | Millgate | 83 | 12:00 | Rangpur | 105 | 18:30
27 | Bheramara(GK) | 40 | 18:00 | Jaldhaka | 65 | 18:30 | Mirpur | 90 | 18:00 | Ruppur | 4.6 | 15:00
28 | Bhulta | 244 | 11:00 | Jamalpur | 121 | 07:00 | Mirsorai | 4 | 18:00 | SSM | 16 | 19:00
29 | Bog-Sherpur | 54 | 08:00 | Jashore | 117 | 13:00 | Mirzapur | 48 | 08:00 | Saidpur | 102 | 08:00
30 | Bogura | 123 | 19:00 | Jhenaidah | 94 | 18:30 | Mithapukur | 54 | 08:00 | Satkhira | 90 | 18:30
31 | Borhanuddin | 50 | 21:00 | Joydebpur | 136 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 86 | 13:00
32 | Brahmanbaria | 111 | 19:00 | Joypurhat | 56 | 08:00 | Mogbazar | 71 | 14:00 | Savar | 164 | 12:00
33 | Cantonment | 94 | 13:00 | Juldah | 16 | 23:00 | Mongla | 24 | 00:00 | SevenRings | 8.05 | 00:00
34 | Chandpur | 42 | 19:30 | KSRM | 41 | 08:00 | Motijheel | 28 | 12:00 | ShahCement | 17 | 01:00
35 | Chandraghona | 24 | 18:30 | Kabirpur | 231 | 18:30 | Munshiganj | 63 | 19:00 | Shahjadpur | 55 | 19:30
36 | Chapai | 58 | 09:00 | Kachua | 49 | 18:00 | Mymensingh | 184 | 18:30 | Shahjibazar | 93 | 18:30
37 | Charsaidpur | 36 | 15:00 | Kallyanpur | 69 | 12:00 | Naogaon | 98 | 13:00 | Shahmirpur | 45 | 06:00
38 | Chauddagram | 43 | 13:00 | Kalurghat | 26 | 10:00 | Narail | 41 | 19:00 | Shariatpur | 51 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 413 | 03:00 | 391 | 16:00 | Gopalganj | 415 | 03:00 | 397 | 14:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 401 | 04:00 | 377 | 16:00
| Bhulta | 408 | 03:00 | 383 | 16:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 420 | 19:30 | 404 | 11:00 | Payra | 421 | 03:00 | 412 | 14:00
| BIPTC | 407 | 02:00 | 389 | 13:00 | Rahanpur | 418 | 02:00 | 394 | 08:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 412 | 03:00 | 398 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 240 | 03:00 | 223 | 16:00 | Hasnabad | 239 | 00:00 | 224 | 16:00
| AKSML | 239 | 18:00 | 230 | 17:00 | Hathazari | 237 | 19:00 | 228 | 00:00
| Aminbazar | 240 | 05:00 | 227 | 11:00 | Ishurdi | 240 | 01:00 | 224 | 12:00
| Ashuganj | 242 | 03:00 | 230 | 12:00 | Jhenaidah | 237 | 01:00 | 222 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 239 | 04:00 | 222 | 14:00
| Baghabari | 236 | 01:00 | 224 | 10:00 | Keranigonj | 240 | 05:00 | 222 | 16:00
| Barapukuria | 226 | 04:00 | 206 | 08:00 | Khulna(S) | 242 | 04:00 | 229 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 244 | 03:00 | 237 | 14:00 | Maniknagar | 241 | 04:00 | 226 | 12:00
| Bheramara | 238 | 01:00 | 222 | 11:00 | Meghnaghat | 242 | 00:00 | 229 | 15:00
| Bhulta | 244 | 04:00 | 226 | 16:00 | Mirsorai | 242 | 19:30 | 232 | 00:00
| Bibiana | 240 | 19:30 | 230 | 12:00 | Rajshahi | 240 | 04:00 | 227 | 11:00
| BIPTC | 239 | 01:00 | 222 | 11:00 | Rampal | 238 | 03:00 | 227 | 12:00
| Bogura | 235 | 04:00 | 216 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 00:00 | 241 | 13:00 | Rampura | 242 | 03:00 | 226 | 16:00
| BSRM | 242 | 19:00 | 230 | 12:00 | Shikalbaha | 236 | 19:30 | 227 | 00:00
| Cumilla(N) | 241 | 19:00 | 230 | 12:00 | Shyampur | 241 | 03:00 | 224 | 16:00
| Fenchuganj | 242 | 05:00 | 236 | 13:00 | Siddhirganj | 241 | 05:00 | 230 | 14:00
| Ghorashal | 240 | 01:00 | 235 | 00:00 | Sirajgonj | 241 | 02:00 | 230 | 11:00
| Ghorashal-230 | 239 | 19:30 | 225 | 16:00 | Sreepur | 238 | 05:00 | 224 | 12:00
| GPH | 237 | 22:00 | 228 | 06:00 | Tongi | 239 | 19:30 | 217 | 15:00
| Haripur | 239 | 03:00 | 225 | 16:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 02:00 | 127 | 16:00 | Lalbag | 137 | 03:00 | 125 | 16:00
| Agargaon | 141 | 03:00 | 131 | 12:00 | Lalmonirhat | 130 | 03:00 | 114 | 08:00
| Agrabad | 137 | 08:00 | 133 | 00:00 | Madanganj | 137 | 19:00 | 128 | 15:00
| AKS | 136 | 18:00 | 132 | 00:00 | Madaripur | 137 | 01:00 | 132 | 13:00
| Aminbazar | 136 | 01:00 | 127 | 12:00 | Madartek | 137 | 03:00 | 126 | 16:00
| Amnura | 137 | 19:00 | 125 | 08:00 | Madunaghat | 139 | 18:30 | 133 | 00:00
| Ashuganj | 140 | 00:00 | 135 | 12:00 | Magura | 140 | 04:00 | 128 | 12:00
| Bagerhat | 134 | 01:00 | 126 | 14:00 | Mahasthangarh | 136 | 04:00 | 121 | 08:00
| Bakulia | 139 | 19:00 | 132 | 00:00 | Manikganj | 135 | 01:00 | 128 | 06:00
| Banani | 140 | 03:00 | 125 | 14:00 | Maniknagar | 136 | 04:00 | 120 | 16:00
| Bangabhaban | 134 | 01:00 | 120 | 16:00 | Matarbari | 129 | 08:00 | 124 | 00:00
| Barapukuria | 138 | 03:00 | 122 | 08:00 | Matuail | 136 | 03:00 | 125.5 | 16:00
| Barguna | 139 | 19:30 | 134 | 13:00 | Millgate | 140 | 03:00 | 126 | 15:00
| Barishal | 140 | 04:00 | 130 | 22:00 | Mirpur | 134 | 03:00 | 125 | 16:00
| Barishal-230 | 140 | 03:00 | 135 | 14:00 | Mirzapur | 133 | 19:00 | 121 | 13:00
| Baroaulia | 140 | 18:00 | 133 | 00:00 | Mithapukur | 134 | 03:00 | 117 | 08:00
| Baroirhat | 140 | 17:00 | 132 | 00:00 | MI_Cement | 138.3 | 19:00 | 127.2 | 16:00
| Bashundhara | 140 | 02:00 | 126 | 15:00 | Modern | 139 | 18:30 | 132 | 12:00
| BashundharaCement | 137 | 19:00 | 126 | 16:00 | Mogbazar | 139 | 05:00 | 129 | 16:00
| Beanibazar | 136 | 04:00 | 132 | 12:00 | Mongla | 134 | 22:00 | 126 | 14:00
| Benapole | 135 | 03:00 | 124 | 12:00 | Motijheel | 134 | 01:00 | 120 | 16:00
| Bhaluka | 133 | 03:00 | 121 | 12:00 | Munshiganj | 137 | 19:00 | 127 | 16:00
| Bhandaria | 138 | 05:00 | 132 | 22:00 | Mymensingh | 131 | 02:00 | 117 | 12:00
| Bhangura | 140 | 03:00 | 129 | 13:00 | Naogaon | 133 | 01:00 | 115 | 08:00
| Bheramara | 138 | 01:00 | 129 | 11:00 | Narail | 139 | 03:00 | 127 | 13:00
| Bheramara(GK) | 139 | 05:00 | 129 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 125 | 05:00 | 115 | 16:00 | Narshingdi | 130 | 05:00 | 120 | 15:00
| Bog-Sherpur | 136 | 01:00 | 123 | 08:00 | Natore | 136 | 01:00 | 127 | 08:00
| Bogura | 137 | 04:00 | 126 | 08:00 | Nawabganj | 138 | 03:00 | 125 | 16:00
| Bogura-230 | 137 | 04:00 | 124 | 08:00 | Netrakona | 130 | 17:00 | 117 | 15:00
| Brahmanbaria | 137 | 22:00 | 130 | 12:00 | New | 141 | 05:00 | 127 | 12:00
| Cantonment | 141 | 03:00 | 130 | 16:00 | Niamatpur | 133 | 01:00 | 114 | 13:00
| Chandpur | 141 | 17:00 | 129 | 00:00 | Noapara | 137 | 03:00 | 126 | 14:00
| Chandraghona | 140 | 19:00 | 134 | 00:00 | Pabna | 138 | 03:00 | 123 | 12:00
| Chapai | 134 | 03:00 | 125 | 08:00 | Palashbari | 132 | 03:00 | 115 | 08:00
| Charsaidpur | 137 | 06:00 | 126 | 16:00 | Panchagarh | 135 | 21:00 | 108 | 08:00
| Chauddagram | 143 | 18:30 | 133 | 00:00 | Patuakhali | 140 | 18:30 | 133 | 13:00
| Chhatak | 136 | 02:00 | 132 | 12:00 | Payra | 137 | 01:00 | 134 | 16:00
| Chowmuhani | 140 | 17:00 | 128 | 00:00 | PHP | 141 | 19:00 | 132 | 02:00
| Chuadanga | 139 | 04:00 | 124 | 12:00 | Postogola | 138 | 18:30 | 130 | 16:00
| Coxsbazar | 128 | 09:00 | 124 | 07:00 | Purbachal | 141 | 02:00 | 126 | 14:00
| Cumilla(N) | 143 | 22:00 | 136 | 14:00 | Purbasadipur | 132 | 21:00 | 108 | 08:00
| Cumilla(S) | 143 | 20:00 | 128 | 09:00 | Rahanpur | 137 | 04:00 | 131 | 12:00
| Daudkandi | 132 | 19:00 | 123 | 16:00 | Rahim | 135 | 03:00 | 126 | 16:00
| Dhaka | 137 | 02:00 | 127 | 16:00 | Rajbari | 138 | 01:00 | 130 | 12:00
| Dhamrai | 135 | 03:00 | 122 | 16:00 | Rajendrapur | 138 | 19:30 | 122 | 13:00
| Dhanmondi | 137 | 03:00 | 126 | 16:00 | Rajshahi | 134 | 19:00 | 126 | 13:00
| Dohazari | 136 | 18:30 | 12 | 12:00 | Rajshahi-230 | 135 | 04:00 | 124 | 08:00
| Faridpur | 138 | 03:00 | 131 | 12:00 | Ramganj | 139 | 17:00 | 128 | 00:00
| Fatullah | 138 | 03:00 | 129 | 16:00 | Rampur | 137 | 18:00 | 132 | 00:00
| Fenchuganj | 138 | 00:00 | 135 | 15:00 | Rampura | 137 | 04:00 | 127 | 16:00
| Feni | 140 | 18:30 | 130 | 00:00 | Rangamati | 139 | 19:30 | 133 | 12:00
| Ghorashal | 144 | 22:00 | 135 | 14:00 | Rangpur | 131 | 02:00 | 117 | 08:00
| Goalpara | 137 | 03:00 | 128 | 12:00 | Ruppur | 140 | 00:00 | 132 | 11:00
| Gollamari | 136 | 03:00 | 128 | 13:00 | Saidpur | 133 | 03:00 | 112 | 08:00
| Gopalganj | 137 | 03:00 | 129 | 14:00 | Satkhira | 134 | 02:00 | 125 | 13:00
| Gopalganj-400 | 138 | 01:00 | 132 | 12:00 | Satmasjid | 140 | 01:00 | 130 | 16:00
| Gulshan | 137 | 03:00 | 127 | 16:00 | Savar | 134 | 01:00 | 125 | 12:00
| Halishahar | 139 | 19:30 | 131 | 07:00 | SevenRings | 144 | 04:00 | 134 | 12:00
| Haripur | 135 | 03:00 | 126 | 16:00 | ShahCement | 138 | 19:00 | 126 | 16:00
| HaripurSBU | 135 | 03:00 | 126 | 16:00 | Shahjadpur | 142 | 01:00 | 132 | 08:00
| Hasnabad | 137 | 05:00 | 129 | 16:00 | Shahjibazar | 136 | 04:00 | 130 | 12:00
| Hathazari | 141 | 19:00 | 135 | 00:00 | Shahmirpur | 138 | 19:00 | 132 | 00:00
| Ishurdi | 141 | 01:00 | 132 | 11:00 | Shariatpur | 139 | 04:00 | 131 | 14:00
| Jaldhaka | 132 | 03:00 | 114 | 08:00 | Sherpur | 126 | 17:00 | 110 | 02:00
| Jamalpur | 128 | 17:00 | 114 | 01:00 | Shikalbaha | 126 | 19:00 | 120 | 00:00
| Jashore | 135 | 00:00 | 125 | 12:00 | Shikalbaha-230 | 165 | 19:00 | 133 | 00:00
| Jhenaidah | 139 | 03:00 | 129 | 12:00 | Shitalakhya | 138.3 | 19:00 | 127.4 | 16:00
| Jhenaidah-230 | 140 | 01:00 | 129 | 12:00 | Sholosohor | 139 | 19:00 | 133 | 07:00
| Joydebpur | 144 | 03:00 | 130 | 13:00 | Shyampur | 137 | 02:00 | 129 | 16:00
| Joypurhat | 131 | 01:00 | 112 | 08:00 | Shyampur-230 | 138 | 03:00 | 128 | 16:00
| Juldah | 138 | 18:00 | 132 | 00:00 | Siddhirganj | 137 | 04:00 | 125 | 16:00
| Kabirpur | 138 | 19:00 | 124 | 12:00 | Sirajganj | 136 | 01:00 | 124 | 12:00
| Kachua | 141 | 19:30 | 130 | 00:00 | Sonargaon | 135 | 18:30 | 123 | 16:00
| Kaliakoir | 135 | 04:00 | 125 | 14:00 | Sreemongol | 136 | 03:00 | 131 | 12:00
| Kallyanpur | 136 | 02:00 | 130 | 16:00 | Sreepur | 135 | 03:00 | 124 | 12:00
| Kalurghat | 139 | 19:30 | 133 | 12:00 | Srinagar | 136 | 03:00 | 125 | 16:00
| Kamrangirchar | 136 | 02:00 | 126 | 16:00 | SSM | 142 | 19:30 | 138 | 14:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 05:00 | 131 | 11:00
| Kazla | 135 | 04:00 | 121 | 15:00 | Sylhet | 136 | 03:00 | 133 | 12:00
| Keranigonj | 137 | 03:00 | 125 | 16:00 | Sylhet-132 | 136 | 01:00 | 134 | 12:00
| Khagrachori | 138 | 19:00 | 133 | 12:00 | Tangail | 128 | 19:00 | 117 | 12:00
| Khulna | 136 | 03:00 | 127 | 14:00 | Thakurgaon | 134 | 21:00 | 106 | 08:00
| Khulna(S) | 137 | 02:00 | 128 | 13:00 | TK | 139 | 19:00 | 133 | 00:00
| Khulshi | 137 | 19:00 | 131 | 12:00 | Tongi | 139 | 06:00 | 127 | 15:00
| Kishoreganj | 136 | 23:00 | 127 | 12:00 | Ullahpara | 140 | 03:00 | 128 | 11:00
| Kodda | 142 | 21:00 | 122 | 16:00 | Ullon | 136 | 01:00 | 127 | 16:00
| KSRM | 139 | 19:30 | 134 | 00:00 | Uttara | 136 | 04:00 | 126 | 16:00
| Kulaura | 137 | 00:00 | 134 | 12:00 | UttaraNew | 141 | 03:00 | 125 | 14:00
| Kurigram | 131 | 05:00 | 112 | 08:00 | Zigatola | 157 | 07:00 | 126 | 15:00
| Kushtia | 139 | 05:00 | 129 | 12:00

## L-Curve
Date | 2024-02-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1468 | 4453 | 4266 | 8719 |  |  |  | QF-LDC-11
0:30 | 1384 | 4253 | 4193 | 8446 | Date: | 2024-02-12
1:00 | 1300 | 4053 | 4120 | 8173
1:30 | 1290 | 4062 | 3899 | 7961
2:00 | 1280 | 4071 | 3678 | 7749
2:30 | 1238 | 3996 | 3601 | 7597 | [5 empty] | Gen. at Eve. Peak | 10798 | 10798 MW (19:00 )
3:00 | 1196 | 3921 | 3524 | 7445 | [6 empty] | 19:00
3:30 | 1143 | 3914.5 | 3413.5 | 7328 | [5 empty] | Gen. at Day Peak | 10051 | 10051 MW (12:00 )
4:00 | 1090 | 3908 | 3303 | 7211 | [6 empty] | 12:00
4:30 | 1090 | 3887.5 | 3275.5 | 7163 | [5 empty] | Highest Generation | 10798
5:00 | 1090 | 3867 | 3248 | 7115 | [6 empty] | 19:00
5:30 | 1095 | 3891.5 | 3383 | 7274.5
6:00 | 1100 | 3916 | 3518 | 7434
6:30 | 1050 | 4055 | 3790.5 | 7845.5
7:00 | 1000 | 4194 | 4063 | 8257
7:30 | 1040 | 4432.5 | 4328.5 | 8761
8:00 | 1080 | 4671 | 4594 | 9265
8:30 | 1139 | 4807.5 | 4662 | 9469.5
9:00 | 1198 | 4944 | 4730 | 9674
9:30 | 1229 | 4943 | 4679.5 | 9622.5
10:00 | 1260 | 4942 | 4629 | 9571
10:30 | 1352 | 4859.5 | 4792.5 | 9652
11:00 | 1444 | 4777 | 4956 | 9733
11:30 | 1479 | 4898.5 | 4993.5 | 9892
12:00 | 1514 | 5020 | 5031 | 10051
12:30 | 1480 | 5113 | 5017 | 10130
13:00 | 1446 | 5206 | 5003 | 10209
13:30 | 1484 | 4986.5 | 4996.5 | 9983
14:00 | 1522 | 4767 | 4990 | 9757
14:30 | 1539 | 4728.5 | 4903.5 | 9632
15:00 | 1556 | 4690 | 4817 | 9507
15:30 | 1613 | 4565.5 | 4727.5 | 9293
16:00 | 1670 | 4441 | 4638 | 9079
16:30 | 1580 | 4487.5 | 4609.5 | 9097
17:00 | 1490 | 4534 | 4581 | 9115
17:30 | 1465 | 4926.5 | 4549.5 | 9476
18:00 | 1440 | 5319 | 4518 | 9837
18:30 | 1310 | 5547 | 4770.5 | 10317.5
19:00 | 1180 | 5775 | 5023 | 10798
19:30 | 1140 | 5801 | 4886 | 10687
20:00 | 1120 | 5748 | 4702 | 10450 |  |  |  | Executive Engineer
20:30 | 1163 | 5605 | 4719 | 10324 |  |  |  | Network Operation Division
21:00 | 1206 | 5462 | 4736 | 10198
21:30 | 1320 | 5247 | 4684.5 | 9931.5
22:00 | 1434 | 5032 | 4633 | 9665 |  |  |  |  | Page 6 of 7
22:30 | 1425 | 4847 | 4490 | 9337
23:00 | 1416 | 4662 | 4347 | 9009
23:30 | 1442 | 4557.5 | 4306.5 | 8864
24:00 | 1468 | 4453 | 4266 | 8719
10798 MW (19:00 )
10051 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-12 |  | Energy |  | 222246079
[14 empty] | Date: | 2024-02-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3092 | 907 | 1043 | 0 | 355 | 3051 | 40 | 0 | 115 | 96 | 0 | 20 | 39
0:30 | 3066 | 854 | 1055 | 0 | 199 | 3058.5 | 43 | 0 | 65.5 | 95 | 0 | 10 | 19.5 |  |  | Date: | 43872
1:00 | 3040 | 801 | 1067 | 0 | 43 | 3066 | 46 | 0 | 16 | 94 | 0 | 0 | 0
1:30 | 3060 | 712.5 | 1091.5 | 0 | 21.5 | 2929.5 | 46 | 0 | 8 | 92 | 0 | 0 | 0 | [9 empty] | Total Energy | 222.2461 | 222.2461 | Total Energy Gen 222.246 MKWHr Energy Not Served 1.474 MKWHr Energy Requirement 223.720 MKWHr
2:00 | 3080 | 624 | 1116 | 0 | 0 | 2793 | 46 | 0 | 0 | 90 | 0 | 0 | 0 | [9 empty] | Energy not Served | 1.4737 | 1.4737
2:30 | 3081 | 624 | 1117.5 | 0 | 0 | 2639 | 46 | 0 | 0 | 88 | 0 | 1.5 | 0 | [9 empty] | Energy Requirement | 223.7197 | 223.7197
3:00 | 3082 | 624 | 1119 | 0 | 0 | 2485 | 46 | 0 | 0 | 86 | 0 | 3 | 0
3:30 | 3061.5 | 624 | 1113.5 | 0 | 0 | 2389 | 46 | 0 | 0 | 88 | 0 | 6 | 0 | [8 empty] | Shortage
4:00 | 3041 | 624 | 1108 | 0 | 0 | 2293 | 46 | 0 | 0 | 90 | 0 | 9 | 0
4:30 | 3005 | 624 | 1097.5 | 0 | 0 | 2296 | 46 | 0 | 0 | 85 | 0 | 9.5 | 0
5:00 | 2969 | 624 | 1087 | 0 | 0 | 2299 | 46 | 0 | 0 | 80 | 0 | 10 | 0
5:30 | 2968.5 | 624 | 1105.5 | 0 | 16.5 | 2417.5 | 46 | 0 | 0 | 85 | 0 | 11.5 | 0
6:00 | 2968 | 624 | 1124 | 0 | 33 | 2536 | 46 | 0 | 0 | 90 | 0 | 13 | 0
6:30 | 3034 | 677 | 1135 | 0 | 81 | 2745.5 | 46 | 0 | 16.5 | 91 | 6.5 | 13 | 35 | [7 empty] | Coal
7:00 | 3100 | 730 | 1146 | 0 | 129 | 2955 | 46 | 0 | 33 | 92 | 13 | 13 | 70
7:30 | 3105 | 677 | 1117 | 0 | 364.5 | 3252.5 | 46 | 0 | 33 | 97 | 56.5 | 12.5 | 75.5875 | [6 empty] | Oil
8:00 | 3110 | 624 | 1088 | 0 | 600 | 3550 | 46 | 0 | 33 | 102 | 100 | 12 | 81.175
8:30 | 3095.5 | 624 | 1081 | 0 | 746 | 3554 | 46 | 0 | 57 | 104 | 154 | 8 | 81.6525
9:00 | 3081 | 624 | 1074 | 0 | 892 | 3558 | 46 | 0 | 81 | 106 | 208 | 4 | 82.13
9:30 | 3025 | 624 | 1052.5 | 0 | 933.5 | 3488 | 46 | 0 | 90.5 | 108 | 253 | 2 | 81.065
10:00 | 2969 | 624 | 1031 | 0 | 975 | 3418 | 46 | 0 | 100 | 110 | 298 | 0 | 80
10:30 | 2943 | 766.5 | 1033 | 0 | 894 | 3396 | 46 | 0 | 124.5 | 113 | 336 | 0 | 85
11:00 | 2917 | 909 | 1035 | 0 | 813 | 3374 | 46 | 0 | 149 | 116 | 374 | 0 | 90
11:30 | 2997.5 | 908 | 1030 | 0 | 831.5 | 3426 | 46 | 0 | 145 | 121 | 384 | 3 | 92.5
12:00 | 3078 | 907 | 1025 | 0 | 850 | 3478 | 46 | 0 | 141 | 126 | 394 | 6 | 95
12:30 | 3084 | 907.5 | 1048 | 0 | 869.5 | 3511.5 | 46 | 0 | 153 | 125 | 379 | 6.5 | 104
13:00 | 3090 | 908 | 1071 | 0 | 889 | 3545 | 46 | 0 | 165 | 124 | 364 | 7 | 113
13:30 | 3090 | 908 | 1071 | 0 | 889 | 3545 | 46 | 0 | 165 | 124 | 364 | 7 | 113
14:00 | 3090 | 908 | 1071 | 0 | 889 | 3545 | 46 | 0 | 165 | 124 | 364 | 7 | 113
14:30 | 3027.5 | 907.5 | 1072.5 | 0 | 715 | 3488.5 | 46 | 0 | 164.5 | 122 | 307.5 | 7 | 101
15:00 | 2965 | 907 | 1074 | 0 | 541 | 3432 | 46 | 0 | 164 | 120 | 251 | 7 | 89
15:30 | 2855.5 | 907.5 | 1070.5 | 0 | 564 | 3364.5 | 46 | 0 | 164 | 117 | 197.5 | 6.5 | 102.5
16:00 | 2746 | 908 | 1067 | 0 | 587 | 3297 | 46 | 0 | 164 | 114 | 144 | 6 | 116
16:30 | 2705.5 | 912.5 | 1026 | 0 | 709 | 3322.5 | 46 | 0 | 169 | 113 | 88.5 | 5 | 103.5
17:00 | 2665 | 917 | 985 | 0 | 831 | 3348 | 46 | 0 | 174 | 112 | 33 | 4 | 91
17:30 | 2732.5 | 912.5 | 1014 | 0 | 1081 | 3225 | 46 | 0 | 328.5 | 113 | 16.5 | 7 | 90
18:00 | 2800 | 908 | 1043 | 0 | 1331 | 3102 | 46 | 0 | 483 | 114 | 0 | 10 | 89
18:30 | 2914 | 766 | 1047 | 0 | 1577 | 3317 | 46 | 0 | 529.5 | 111 | 0 | 10 | 93.205
19:00 | 3028 | 624 | 1051 | 0 | 1823 | 3532 | 46 | 0 | 576 | 108 | 0 | 10 | 97.41
19:30 | 3053 | 624 | 994 | 0 | 1817 | 3449 | 46 | 0 | 586 | 106 | 0 | 12 | 82.13
20:00 | 3235 | 623 | 1010 | 0 | 1477 | 3398 | 46 | 0 | 537 | 108 | 0 | 16 | 66.85
20:30 | 3264.5 | 623.5 | 1032 | 0 | 1399.5 | 3385 | 46 | 0 | 449.5 | 108 | 0 | 16 | 62.925
21:00 | 3294 | 624 | 1054 | 0 | 1322 | 3372 | 46 | 0 | 362 | 108 | 0 | 16 | 59
21:30 | 3204.5 | 722 | 1032 | 0 | 1122 | 3352.5 | 43 | 0 | 336 | 103 | 0 | 16.5 | 70
22:00 | 3115 | 820 | 1010 | 0 | 922 | 3333 | 40 | 0 | 310 | 98 | 0 | 17 | 81
22:30 | 3090.5 | 863.5 | 1018 | 0 | 770.5 | 3200 | 40 | 0 | 237.5 | 99 | 0 | 18 | 72
23:00 | 3066 | 907 | 1026 | 0 | 619 | 3067 | 40 | 0 | 165 | 100 | 0 | 19 | 63
23:30 | 3079 | 907 | 1034.5 | 0 | 487 | 3059 | 40 | 0 | 140 | 98 | 0 | 19.5 | 51 |  |  | Max Temp. in Dhaka |  | 29.3°C
24:00 | 3092 | 907 | 1043 | 0 | 355 | 3051 | 40 | 0 | 115 | 96 | 0 | 20 | 39
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 222.246 MKWHr Energy Not Served 1.474 MKWHr Energy Requirement 223.720 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-02-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 40 | 40 | 40 | 1079640
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 0 |  | 0 | 6 | 11 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 134422
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 11 | 16 | 17 | 19 | 18 | 16 | 12 | 4 | 1 | 0 | [8 empty] | 123660
6 | Sikalbaha 225MW CCPP (Gas) | 211 | 211 | 210 | 211 | 211 | 212 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 212 | 212 |  | 211 | 211 | 211 | 211 | 211 | 211 | 212 | 5004426
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 34 | 34 | 34 | 34 | 51 | 51 | 50 | 50 | 50 | 51 |  | 51 | 51 | 51 | 51 | 51 | 17 | 0 | 654561
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 299418
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [8 empty] | 14 | 33 | 32 | 24 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 33 | 33 | 33 | 0 | 478975
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [19 empty] | 62 | 37 | 42 | 42 | 38 | 40 | 40 | 325000
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 280 | 280 | 335 | 335 | 335 | 290 | 290 | 335 | 335 | 300 | 300 | 334 | 300 | 335 |  | 335 | 300 | 300 | 300 | 300 | 300 | 300 | 7401612
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 1 | 35 | 47 | 77 | 45 | 45 | 45 |  |  |  | 5 | 30 |  | 62 | 65 | 30 | 30 | 0 |  | 0 | 582109
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 190 | 190 | 190 | 140 | 140 | 140 | 140 | 140 | 140 | 141 | 140 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3809000
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 443 | 440 | 291 | 293 | 293 | 290 | 330 | 430 | 443 | 440 | 440 | 498 | 522 | 500 | 500 | 500 | 508 | 529 |  | 540 | 570 | 584 | 565 | 565 | 530 | 520 | 10794544
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 5 | 25 | 28 | 28 | 28 | 28 | 28 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 739800
33 | Ashuganj 225 MW CCPP | 155 | 155 | 157 | 154 | 155 | 150 | 129 | 149 | 157 | 149 | 149 | 151 | 152 | 147 | 149 | 145 | 147 | 148 |  | 151 | 151 | 151 | 151 | 151 | 153 | 154 | 3648000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 275 | 285 | 280 | 305 | 270 | 260 | 260 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 275 | 6334000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 290 | 295 | 290 | 315 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 325 | 280 | 290 |  | 285 | 280 | 280 | 280 | 285 | 285 | 285 | 7284500
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 403 | 404 | 389 | 352 | 352 | 366 | 431 | 423 | 390 | 382 | 390 | 408 | 385 | 381 |  | 0 |  |  | 104 | 217 | 375 | 373 | 371 | 370 | 371 | 7999200
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 60 | 110 | 110 | 110 | 120 | 120 | 120 | 120 | 111 | 120 | 118 | 100 | 70 | 62 | 62 | 62 | 59 | 61 |  | 38 | 30 | 60 | 60 | 50 | 60 | 60 | 2025000
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 71 | 71 | 71 | 87 | 86 | 81 | 67 | 68 | 32 | 30 | 30 | 29 | 27 | 28 | 30 | 32 | 34 | 35 |  | 46 | 70 | 71 | 71 | 71 | 74 | 74 | 1272000
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 12 | 28 | 26 | 45 | 48 | 45 | 43 | 30 | 19 | 4 | 0 | [8 empty] | 303840
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 42 | 42 | 43 | 43 | 42 | 42 | 42 | 1005000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 959280
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 61 | 61 | 40 | 40 | 40 | 40 | 61 | 61 | 60 | 60 | 59 | 59 | 58 | 56 | 56 | 58 | 58 |  | 59 | 40 | 40 | 40 | 40 | 40 | 40 | 1251264
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 21 | 52 | 55 | 65 | 65 | 65 | 65 | 65 | 65 | 66 | 73 | 121 | 118 | 119 | 118 | 120 | 160 | 200 |  | 207 | 207 | 208 | 208 | 208 | 208 | 210 | 2723100
51 | Sylhet 20 MW GTPP | [9 empty] | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 243000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 249480
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 51 | 51 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1276200
56 | Shahjahanulla 25 MW PP | 17 | 17 | 17 |  |  | 17 | 17 | 17 |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 257424
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 295 | 280 | 300 | 310 | 310 | 305 | 300 | 280 | 290 | 290 | 280 | 285 | 300 | 295 | 285 | 280 |  | 280 | 260 | 270 | 310 | 275 | 280 | 295 | 7146000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 345 | 345 | 395 | 340 | 340 | 340 | 340 | 400 | 340 | 340 | 340 | 372 | 340 | 345 |  | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 8265100
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | [5 empty] | 0 | 39075
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 45120
60 | Barabkunda 22 MW PP (Regent) | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 340992
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 94 | 90 | 86 | 90 | 80 | 90 | 92 | 102 | 106 | 110 | 116 | 126 | 124 | 126 | 120 | 114 | 112 | 114 |  | 108 | 106 | 108 | 108 | 98 | 100 | 96 | 2482560
64 | Malancha, Ctg. EPZ (United) | 34 | 34 | 27 | 31 | 31 | 28 | 24 | 2 | 2 | 10 | 5 | 12 | 9 | 5 | 1 | 0 | 10 | 19 |  | 20 | 22 | 27 | 34 | 35 | 36 | 34 | 465600
65 | Feni 22 MW PP (Doreen) | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 16 | 16 | 16 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 413460
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 210420
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 25 | 25 |  |  |  |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 603000
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 15 | 15 | 15 | 15 | 15 | 13 | 281460
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 10 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 346680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 814640
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 32 |  | 32 | 25 | 25 | 33 | 33 | 33 | 33 | 774400
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287500
| Feni Lanka Power | [7 empty] | 80 | 98 | 98 | 52 | 60 | 114 | 34 | 34 | 34 | 70 | 70 |  | 114 | 114 | 70 | 70 | 70 | 9 | 0 | 1125180
| Chowmuhani 113 MW | [9 empty] | 3 | 18 | 18 | 58 | 67 | 68 | 68 | 68 | 68 |  | 78 | 68 | 70 | 68 | 68 | 27 | 0 | 819840
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 35 | 35 | 17 | 35 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 24 | 56 | 60 | 37 | 30 | 30 |  |  |  | 40 | 82 |  | 84 | 84 | 62 | 9 | 0 |  | 0 | 503040
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 202080
79 | Kodda 150 MW PP | 16 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 98 |  | 98 | 98 | 98 | 16 | 16 | 16 | 16 | 561120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 160526
| Gazipur 100 MW PP | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 70 |  | 105 | 105 | 105 | 105 | 70 | 70 | 0 | 720960
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 24000
| Jodiac Power | [8 empty] | 1 | 17 | 17 | 17 | 17 | [12 empty] | 0 | 77811
| Karnaphuli Power Ltd. | [7 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 297745
82 | Madanganj 102 PP(Summit) | [6 empty] | 8 | 45 | 78 | 80 | 55 | 50 | 50 | 14 |  |  | 20 | 34 |  | 65 | 77 | 58 | 17 | 8 | 0 | 0 | 535743
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 6 | 50 | 84 | 84 | 61 | 54 | 82 | 57 | 43 | 42 | 62 | 93 |  | 90 | 59 | 48 | 9 | 8 | 0 | 0 | 873600
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 17 | 13 | 17 | 17 | 17 | 0 | 206400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 20 |  | 25 | 25 |  |  |  |  | 0 | 42960
92 | Fenchuganj 44 MW (Energyprima) | 42 | 42 | 42 | 42 | 42 | 42 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 663624
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1082704
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 33 | 42 |  | 83 | 83 | 83 | 83 | 83 | 8 | 0 | 800208
95 | Patenga 50MW PP (Baraka) | [7 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 106080
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 22 |  | 25 | 15 | 15 | 15 | 15 | 15 | 0 | 241036
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 40123
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13350
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | [5 empty] | 0 | 38880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 |  |  |  |  | 5 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 19 | 19 |  | 9 | 9 | 9 | 9 | 9 | 18 | 9 | 194400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 25 | [5 empty] | 2 | 17 | 17 | 17 | 23 | 24 | 25 | 26 | 30 | 35 | 65 | 126 |  | 142 | 149 | 142 | 149 | 149 | 149 | 137 | 1342800
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 4 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 405120
116 | Chandpur 200 MW (Desh energy) | [6 empty] | 1 | 15 | 18 | 17 | 17 | 30 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 312000
117 | Ashuganj 150 MW PP (Midland) | [6 empty] | 1 | 6 | 5 | 6 | 12 | 13 | 13 | 12 | 13 | 13 | 13 | 13 |  | 18 | 26 | 26 | 26 | 26 | 21 | 8 | 252581
118 | Bibiyana-III 400 MW CCPP | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 249 | 250 | 250 | 306 | 230 | 230 | 270 | 260 | 307 |  | 309 | 310 | 306 | 309 | 132 | 80 | 80 | 6436000
| Jamalpur 115 MW PP (United) | 9 |  |  |  |  | 28 | 57 | 57 | 56 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 68 |  | 69 | 69 | 69 | 69 | 9 | 9 | 9 | 973200
| Anwara 300 MW PP (United) | [7 empty] | 15 | 49 | 65 | 30 | 30 | 72 | 30 | 30 | 30 | 60 | 101 |  | 128 | 160 | 100 | 100 | 84 | 16 | 16 | 991091
| Juldah unit-2 (Acorn) | [7 empty] | 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 397440
| Anlima Energy Ltd. | [6 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 298582
| Bhairob 54.5 MW | [25 empty] | 0 | 0
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 6 | 11 | 25 | 28 | 29 | 29 | 26 | 18 | 11 | 4 | 0 | [8 empty] | 177218
| Chandpur 115(Doreen) | [12 empty] | 10 | 18 | 18 | 18 | 28 | 41 |  | 40 | 36 | 36 | 33 | 18 | 0 | 0 | 275520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 9 | 35 |  | 17 | [5 empty] | 0 | 68760
| Mirsharai 150 MW (Oil) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 145 |  | 145 | 145 | 90 | 17 | 17 | 17 | 17 | 600509
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 3 | 9 | 10 | 13 | 13 | 12 | 4 | 0 | 0 | 6 | 7 | 8 | 7 | 6 | 4 | 10 |  | 10 | 12 | 16 | 16 | 17 | 19 | 20 | 199200
| Matarbari 2*600 MW (CPGCL) | [25 empty] | 0 | 0
120 | Eastern Zone Total | 4053 | 4071 | 3921 | 3908 | 3867 | 3916 | 4194 | 4671 | 4944 | 4942 | 4777 | 5020 | 5206 | 4767 | 4690 | 4441 | 4534 | 5319 |  | 5775 | 5801 | 5748 | 5462 | 5032 | 4662 | 4453 | 113480293
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 35 | 56 | 55 | 35 | 35 | 17 |  |  |  |  | 9 |  | 35 | 56 | 60 | 75 | 75 | 75 | 0 | 657120
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 2 | 21 | 42 | 61 | 75 | 76 | 47 | 64 | 42 | 22 | [10 empty] | 470880
131 | Rampal 1320 MW (BIFPCL) | 361 | 361 | 361 | 361 | 361 | 365 | 362 | 361 | 364 | 362 | 360 | 359 | 360 | 360 | 358 | 358 | 359 | 0 | [8 empty] | 6458182
132 | United Payra Power Ltd. | [7 empty] | 17 | 17 | 17 | 17 | 35 | [5 empty] | 18 |  | 150 | 150 | 54 | 54 | 0 |  | 0 | 484800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 200 | 200 | 200 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 190 | 190 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4993718
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 128544
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 220 | 220 | 180 | 150 | 150 | 198 |  | 307 | 260 | 260 | 260 | 260 | 153 | 150 | 4385500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [21 empty] | 20 | 70 | 70 | 70 | 66 | 284000
140 | Bhola 33 MW PP (Venture) | 8 | 7 | 7 | 7 | 6 | 6 | 4 | 3 | 3 | 3 | 4 | 5 | 4 | 4 | 3 | 3 | 5 | 7 |  | 7 | 6 | 7 | 4 | 4 | 4 | 8 | 125414
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 15 |  | 50 | 50 | 48 | 36 | 0 |  |  | 138624
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 801 | 624 | 624 | 624 | 624 | 624 | 730 | 624 | 624 | 624 | 909 | 907 | 908 | 908 | 907 | 908 | 917 | 908 |  | 624 | 624 | 623 | 624 | 820 | 907 | 907 | 18405818
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 870 | 700 | 600 | 500 | 500 | 610 | 840 | 1120 | 1120 | 1030 | 1040 | 1040 | 1060 | 1090 | 1080 | 1000 | 990 | 1000 |  | 1210 | 1120 | 1120 | 1120 | 1080 | 1000 | 1000 | 24795700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4125600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 34 | 34 | 34 | 25 | 25 | 0 | 0 | 138334
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 3 | 4 | 5 | 4 | 4 | 1 | 1 | 0 | [9 empty] | 28200
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 172 | 177 | 150 | 140 | 140 | 140 | 151 | 140 | 140 | 140 | 140 | 150 | 165 | 160 | 171 | 160 | 159 |  | 164 | 140 | 140 | 140 | 140 | 140 | 140 | 4006673
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 300 | 300 | 300 | 300 | 270 | 300 | 350 | 300 | 300 | 300 | 300 | 300 | 350 | 350 | 350 | 350 | 300 | 350 |  | 380 | 350 | 320 | 320 | 320 | 320 | 320 | 7927054
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 |  | 8 | 12 | 20 | 20 | 20 | 0 |  | 57214
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 5 |  | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 93240
165 | Amnura 50 MW PP(Sinha) | [8 empty] | 21 | 28 | 28 | 28 | [13 empty] | 0 | 112810
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 25 | 25 | 25 | 25 | 25 | [5 empty] | 8 |  | 25 | 25 | [5 empty] | 155579
167 | Katakhali 50 MW Peaking PP | [17 empty] | 8 |  | 48 | 50 | 50 | 50 | 50 | 0 |  | 180464
168 | Santahar 50 MW Peaking PP | [16 empty] | 10 | 28 |  | 28 | 32 | 32 | 32 | 16 | 0 |  | 143872
169 | Natore 52 MW PP (Rajlanka) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | [10 empty] | 8 | 8 | 8 | 73661
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 50 | 50 | 49 | 49 | 49 | 49 | 49 | 77 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 887232
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 6 | 35 | 35 | 35 | 35 | [5 empty] | 3 |  | 35 | 35 | 35 | 35 | 0 |  | 0 | 310464
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 30 |  | 54 | 54 | 55 | 55 | 0 |  | 0 | 200640
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 6 | 6 | 6 | 8 | 6 | 6 | 6 | 6 | 23 | 33 | 35 |  | 34 | 34 | 35 | 34 | 34 | 6 | 6 | 273465
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 6 | 6 | 6 | 5 | 5 | 3 | 1 | 0 | [8 empty] | 40962
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 7 | 35 | 50 |  | 72 | 72 | 72 | 72 | 0 |  | 0 | 343488
| Intraco Solar 30 MW | [6 empty] | 1 | 7 | 18 | 27 | 32 | 35 | 35 | 30 | 24 | 13 | 4 | 0 | [8 empty] | 230519
| Adani Power Jharkhanda Ltd | 1072 | 972 | 913 | 819 | 825 | 951 | 1103 | 1319 | 1311 | 1266 | 1214 | 1211 | 1213 | 1184 | 1144 | 1119 | 1171 | 1205 |  | 1305 | 1329 | 1264 | 1257 | 1258 | 1214 | 1211 | 26977455
178 | Teesta Solar Limited | [6 empty] | 6 | 45 | 92 | 130 | 161 | 170 | 174 | 159 | 116 | 69 | 19 | 0 | [8 empty] | 1130560