## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-02-15 | Thursday
|  | Date (day): | 2024-02-15 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11372.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12054 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-14 | 2024-02-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 190 | 140 | 140 | 190
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 405 | 412 | 412 |  |  |  |  | 2024-02-12
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  |  | Line S/D
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 84 | 8 | 50 | 50 |  |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 65 | 34 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 40 | 103 | 100 | 100 | 110 |  | GT-2 S/D Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 59 | 67 | 60 | 68 |  | 32 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 42 | 91 | 91 | 91 |  | 11 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 98 | 16 | 98 | 51 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 26 | 34 | 34 | 34 |  | 46 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 21 | 24 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 82 | 130 | 82 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 36 | 17 | 35 | 114
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 17 | 17 | 145 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 345 | 395 | 400 | 400 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1428 | 2182 | 2004 | 2380 | 1525 | 1061
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 18 | 32 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 212 | 210 | 210 | 15
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 | 98 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 49 | 51 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 12 | 5 | 15
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 35 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 72 | 103 | 65 | 155 | 145 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 20 | 0 | 17 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 145 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 550 | 480 | 550 | 580 | 644
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 14 | 14 | 20 | 20 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 0 | 0 | 0 | 0 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1150 | 1265 | 1152 | 1389 | 2048 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 150 | 151 | 150 | 150 |  | 71 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 0 | 0 | 0 | 360 |  | under maint.
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 280 | 290 | 290 | 70 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 300 | 320 | 80 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 30 | 35 | 35 | 10 |  | Gas shortage
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 120 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 16 | 13 | 25 | 125 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 25 | 39 | 40 | 41 |  | 11 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 17 | 16 | 16 |  | 6 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 120 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 8 | 8 | 16 | 36 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 15 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 98 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 68 | 48 | 68 | 45 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 42 | 0 | 42 | 73 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1170 | 1114 | 1293 | 1409 | 1224 | 298
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 29 | 32 | 50 | 50 | 152 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9 | 9 | 191 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 57 | 69 | 46 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 28 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 127 | 116 | 167.6 | 134 | 152 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 51 | 53 | 51 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 61 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 210 | 208 | 210 | 210 |  | 21 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 16 | 16 | 4 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 17 | 17 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 410 | 350 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 340 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1408 | 1493 | 1451 | 1501 | 57 | 692
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 623 | 922 | 633
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 52 | 0 | 52 | 2
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 50 |  | 59 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 54 | 54 | 54 | 51 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 69 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 330 | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1011 | 729 | 1076 | 789 | 1305 | 389
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 4 | 6 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 40 | 70 | 70 | 70 |  | 124 | ST, GT-1 Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1050 | 1200 | 1240
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 180 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 150 | 150 | 150 | 150
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 307 | 250 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1868 | 1819 | 1857 | 2010 | 94 | 157
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 25 | 26 | 26 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 8 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 40 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 142 | 155 | 155 | 65 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 330 | 309 | 350 | 350 | 64 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 15 | 30 | 0 | 35 | 15 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 49 | 74 | 50 | 82 |  | 22 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 35 | 0 | 113 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1268 | 1275 | 1300 | 1350
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1930 | 1985 | 2028 | 2165 | 1206 | 108
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 35 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 0 | 72 | 43 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 129 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 336 | 277 | 344 | 277 | 246 | 189
| Total |  |  |  |  | 26504 | 25481 | 10428 | 10980 | 11372.6 | 12054 | 7857 | 3224
A. |  | 2024-02-14 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10980 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7431 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11043 | MW
3 | Day peak Generation : |  |  | 10428 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10560.85 | MW
4 | Evening peak Generation : |  |  | 10980 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 60 | MW
5 | Total Energy Generation : |  | 227.0045 | MKWHr | By Solar | 1.7426 | MKWHr
| By Gas : | 108.453 | MKWHr |  | By Oil: | 21.0687 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 73.8775 | MKWHr |  | By Hydro: | 0.96454 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.36096 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7857 | MW | Dhaka | 3984.55 | 3984.55 |  | 0 |  | 18:00 |  | 143.25
|  |  | For Plants S/D or M/C prob = |  |  | 3224 | MW | Chittagong | 1032 | 1032 |  | 0 |  | 19:00 |  | 60.165
|  |  | Total = |  |  | 11081 | MW | Khulna | 1183.6 | 1183.6 |  | 0 |  | 19:30 |  | 64.94
7 | Total Gas Supplied : |  |  | 841.33 | MMCFD |  |  | Rajshahi | 1068.2 | 1068.2 |  | 0 |  | 20:00 |  | 75.445
8 | Fuel Cost : | i) Gas : | Taka | 313818045.666 | ii) Oil : | Taka | 383132315.47 | Comilla | 897 | 897 |  | 0 |  | 21:00 |  | 95
|  | iii) Coal : | Taka | 499908286.98 | Total | Taka | 1196858648.116 | Mymensingh | 969 | 909 |  | 60 |  | 22:00 |  | 93
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 378 | 378 |  | 0 |  | 23:00 |  | 84
| ii) During Peak Demand : |  |  | 1020 | MW (W to E) at | 19:00 | hrs | Barisal | 291.5 | 291.5 |  | 0 |  | 24:00 |  | 21
| iii) Maximum : |  |  | 960 | MW at | 6:00 | hrs | Rangpur | 757 | 757 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.6°C |  |  | Total | 10560.85 | 10500.85 |  | 60
B. |  | 2024-02-15 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12054 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
4 | Reserve(Generation end) |  |  |  | 1054 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 227.418 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7492 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.0029 | MKWHr. | ii) HVDC Flow at Peak Time |  | 623 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5344 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 18:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.72 |  | (b) Today: | 85.59 |  | (c) Rule Curve: |  | 95.04
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-02-14 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 380 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 290 | 280 | 151 | 8 | 0 | 15 | 0 | 0 | 51 | 0 | 0 | 0 | 17 | 9 | 33 | 11 | 82 | 75 | 0 | 0 | 0 | 42 | 40 | 53 | 5 | 0 | 0 | 60 | 0 | 0 | 208 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 436 | 17 | 0 | 0 | 170 |  | 813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1164 | 0 | 0 |  | 4156 | 4148 | 8304 | 3160 | 813 | 1262 | 0 | 30 | 2900 | 40 | 0 | 0 | 82 | 0 | 17 | 0 | 85.74
2:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 404 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 30 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 290 | 280 | 151 | 8 | 0 | 15 | 0 | 0 | 51 | 0 | 0 | 0 | 17 | 9 | 33 | 11 | 80 | 75 | 0 | 0 | 0 | 42 | 40 | 53 | 5 | 0 | 0 | 60 | 0 | 0 | 208 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 22 | 0 | 0 | 185 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1007 | 0 | 0 |  | 4143 | 3750 | 7893 | 3171 | 624 | 1285 | 0 | 17 | 2654 | 40 | 0 | 0 | 80 | 0 | 22 | 0 | 85.74
3:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 432 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 30 | 0 | 0 | 0 | 290 | 280 | 151 | 8 | 0 | 15 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 33 | 11 | 76 | 75 | 0 | 0 | 0 | 42 | 40 | 53 | 0 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 24 | 0 | 0 | 227 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 878 | 0 | 0 |  | 4115 | 3529 | 7644 | 3177 | 624 | 1303 | 0 | 0 | 2400 | 40 | 0 | 0 | 76 | 0 | 24 | 0 | 85.74
4:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 416 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 31 | 0 | 0 | 0 | 290 | 280 | 151 | 8 | 0 | 15 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 33 | 11 | 74 | 75 | 0 | 0 | 0 | 42 | 40 | 53 | 0 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 14 | 0 | 0 | 228 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 818 | 0 | 0 |  | 4121 | 3310 | 7431 | 3167 | 624 | 1261 | 0 | 0 | 2251 | 40 | 0 | 0 | 74 | 0 | 14 | 0 | 85.73
5:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 408 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 35 | 0 | 0 | 0 | 280 | 280 | 144 | 8 | 0 | 15 | 0 | 0 | 43 | 0 | 0 | 0 | 18 | 9 | 33 | 11 | 74 | 75 | 0 | 0 | 0 | 42 | 40 | 51 | 0 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 21 | 0 | 0 | 266 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 815 | 0 | 0 |  | 4223 | 3237 | 7460 | 3237 | 624 | 1236 | 0 | 0 | 2228 | 40 | 0 | 0 | 74 | 0 | 21 | 0 | 85.72
6:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 372 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 65 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 25 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 36 | 0 | 0 | 0 | 280 | 280 | 153 | 8 | 0 | 15 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 11 | 78 | 75 | 0 | 0 | 0 | 42 | 40 | 51 | 0 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1 | 0 | 0 | 0 | 0 | 315 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 22 | 0 | 0 | 306 |  | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 881 | 0 | 0 |  | 4389 | 3344 | 7733 | 3303 | 625 | 1300 | 0 | 15 | 2334 | 40 | 0 | 16 | 78 | 0 | 22 | 0 | 85.72
7:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 379 | 0 |  | 0 | 0 | 0 | 1 | 0 | 0 | 335 | 0 | 65 | 1 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 25 | 2 | 0 | 40 | 0 | 0 | 0 | 1 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 12 | 25 | 0 | 0 | 0 | 375 | 320 | 122 | 8 | 0 | 15 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 11 | 80 | 66 | 0 | 0 | 0 | 42 | 40 | 51 | 0 | 0 | 0 | 40 | 0 | 0 | 208 | 16 | 0 | 10 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 15 | 1 | 25 | 8 | 3 | 315 | 56 | 17 | 7 | 0 | 15 | 0 | 11 | 17 | 0 | 24 | 330 | 6 | 1 | 0 | 11 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 377 | 17 | 0 | 0 | 367 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 840 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 150 | 992 | 6 | 0 |  | 4840 | 3652 | 8492 | 3444 | 624 | 1474 | 0 | 238 | 2529 | 40 | 0 | 33 | 80 | 13 | 17 | 79 | 85.71
8:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 430 | 0 |  | 0 | 0 | 0 | 15 | 12 | 0 | 335 | 0 | 99 | 18 | 32 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 25 | 23 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 12 | 7 | 0 | 0 | 0 | 315 | 300 | 137 | 8 | 0 | 15 | 0 | 0 | 51 | 0 | 0 | 6 | 18 | 9 | 33 | 11 | 96 | 66 | 0 | 0 | 0 | 42 | 40 | 51 | 5 | 0 | 0 | 40 | 0 | 0 | 209 | 16 | 0 | 10 | 310 | 17 | 0 | 0 | 10 | 0 | 0 | 9 | 0 | 17 | 7 | 25 | 17 | 6 | 315 | 59 | 17 | 17 | 1 | 49 | 0 | 17 | 70 | 1 | 24 | 340 | 17 | 9 | 0 | 17 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 0 | 460 | 16 | 0 | 0 | 347 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 29 | 0 | 4 | 0 | 6 | 0 | 1 | 0 | 1060 | 220 | 0 | 10 | 0 | 18 | 0 | 0 | 0 | 0 | 5 | 150 | 1121 | 21 | 0 |  | 5251 | 4142 | 9393 | 3533 | 624 | 1439 | 0 | 585 | 2961 | 40 | 0 | 33 | 96 | 66 | 16 | 102.185 | 85.71
9:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 50 | 40 | 0 | 335 | 0 | 77 | 50 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 33 | 23 | 8 | 0 | 0 | 40 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 51 | 25 | 0 | 6 | 12 | 6 | 0 | 0 | 0 | 280 | 300 | 131 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 8 | 18 | 9 | 33 | 15 | 108 | 34 | 0 | 0 | 0 | 42 | 40 | 30 | 5 | 0 | 0 | 60 | 0 | 0 | 209 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 17 | 13 | 25 | 17 | 6 | 316 | 59 | 17 | 17 | 3 | 66 | 0 | 17 | 78 | 9 | 24 | 340 | 17 | 16 | 0 | 17 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 0 | 541 | 19 | 0 | 0 | 345 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 414 | 35 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1170 | 220 | 0 | 54 | 0 | 43 | 0 | 0 | 0 | 0 | 4 | 150 | 1255 | 31 | 0 |  | 5030 | 4499 | 9529 | 3012 | 624 | 1397 | 0 | 840 | 3286 | 40 | 0 | 84 | 108 | 119 | 19 | 354.305 | 85.7
10:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 67 | 72 | 0 | 335 | 0 | 37 | 59 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 33 | 23 | 8 | 0 | 0 | 40 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 51 | 25 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 280 | 250 | 150 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 13 | 8 | 18 | 9 | 33 | 15 | 114 | 29 | 0 | 0 | 1 | 42 | 40 | 48 | 5 | 0 | 0 | 58 | 0 | 0 | 209 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 75 | 0 | 0 | 9 | 0 | 17 | 16 | 25 | 17 | 6 | 316 | 59 | 17 | 17 | 3 | 66 | 17 | 17 | 98 | 9 | 24 | 340 | 17 | 19 | 0 | 17 | 0 | 2 | 8 | 0 | 0 | 0 | 17 | 0 | 550 | 7 | 0 | 0 | 0 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 330 | 35 | 0 | 35 | 0 | 6 | 0 | 3 | 0 | 1180 | 180 | 0 | 115 | 2 | 35 | 0 | 0 | 0 | 0 | 19 | 229 | 1264 | 76 | 0 |  | 4765 | 4590 | 9355 | 2907 | 624 | 935 | 0 | 1056 | 3393 | 40 | 0 | 97 | 114 | 182 | 7 | 568.225 | 85.7
11:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 79 | 70 | 15 | 280 | 0 | 40 | 59 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 7 | 33 | 21 | 8 | 0 | 30 | 40 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 0 | 51 | 25 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 280 | 250 | 153 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 38 | 18 | 9 | 33 | 15 | 118 | 29 | 0 | 0 | 1 | 43 | 40 | 51 | 5 | 0 | 0 | 57 | 0 | 0 | 210 | 16 | 0 | 10 | 280 | 17 | 0 | 0 | 80 | 0 | 0 | 9 | 0 | 17 | 19 | 25 | 17 | 6 | 316 | 59 | 17 | 17 | 4 | 62 | 17 | 17 | 98 | 32 | 24 | 340 | 17 | 41 | 0 | 17 | 0 | 17 | 23 | 0 | 0 | 0 | 17 | 0 | 552 | 8 | 0 | 0 | 0 |  | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 330 | 35 | 0 | 35 | 0 | 6 | 0 | 3 | 0 | 1190 | 180 | 0 | 150 | 4 | 65 | 0 | 0 | 0 | 0 | 23 | 250 | 1271 | 116 | 0 |  | 4910 | 4980 | 9890 | 2856 | 819 | 928 | 0 | 1194 | 3433 | 70 | 0 | 165 | 118 | 299 | 8 | 152.8 | 85.69
12:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 84 | 65 | 15 | 280 | 0 | 40 | 59 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 7 | 33 | 21 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 0 | 49 | 25 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 250 | 150 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 52 | 18 | 9 | 33 | 15 | 126 | 29 | 0 | 0 | 2 | 43 | 40 | 51 | 5 | 0 | 0 | 56 | 0 | 0 | 210 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 82 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 5 | 320 | 59 | 17 | 17 | 3 | 72 | 20 | 17 | 98 | 36 | 24 | 350 | 17 | 28 | 17 | 17 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 0 | 550 | 14 | 0 | 0 | 345 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 15 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 330 | 35 | 0 | 35 | 0 | 6 | 0 | 3 | 0 | 1244 | 180 | 0 | 150 | 4 | 69 | 0 | 0 | 0 | 0 | 28 | 250 | 1268 | 129 | 0 |  | 5283 | 5145 | 10428 | 2862 | 907 | 1280 | 0 | 1235 | 3482 | 40 | 0 | 171 | 126 | 311 | 14 | 136 | 85.69
13:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 23 | 0 |  | 0 | 0 | 0 | 86 | 77 | 15 | 335 | 0 | 37 | 59 | 42 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 21 | 8 | 0 | 43 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 49 | 25 | 0 | 6 | 12 | 1 | 0 | 0 | 0 | 280 | 280 | 151 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 28 | 52 | 18 | 9 | 33 | 15 | 132 | 28 | 0 | 0 | 1 | 43 | 40 | 53 | 5 | 0 | 0 | 54 | 0 | 0 | 207 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 82 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 6 | 329 | 59 | 17 | 17 | 3 | 62 | 17 | 17 | 98 | 39 | 24 | 340 | 0 | 38 | 17 | 17 | 0 | 0 | 20 | 18 | 0 | 0 | 17 | 0 | 550 | 9 | 0 | 0 | 345 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 370 | 51 | 0 | 35 | 0 | 6 | 0 | 3 | 0 | 1244 | 220 | 0 | 150 | 4 | 73 | 0 | 0 | 0 | 0 | 14 | 250 | 1268 | 100 | 0 |  | 5411 | 5229 | 10640 | 3008 | 908 | 1371 | 0 | 1240 | 3482 | 43 | 0 | 191 | 132 | 256 | 9 | 124 | 85.68
14:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 176 | 0 |  | 0 | 0 | 0 | 91 | 80 | 15 | 290 | 0 | 36 | 59 | 42 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 25 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 0 | 50 | 25 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 250 | 149 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 32 | 52 | 18 | 9 | 33 | 15 | 134 | 28 | 0 | 0 | 2 | 43 | 40 | 51 | 5 | 0 | 0 | 40 | 0 | 0 | 206 | 16 | 0 | 10 | 280 | 17 | 0 | 0 | 52 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 6 | 345 | 59 | 17 | 17 | 3 | 67 | 17 | 17 | 98 | 38 | 24 | 340 | 7 | 20 | 17 | 17 | 0 | 0 | 16 | 18 | 0 | 0 | 17 | 0 | 500 | 7 | 0 | 0 | 345 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 308 | 54 | 0 | 35 | 0 | 6 | 0 | 2 | 35 | 1040 | 180 | 0 | 85 | 1 | 67 | 0 | 0 | 0 | 0 | 9 | 200 | 1270 | 108 | 0 |  | 5325 | 4819 | 10144 | 2991 | 908 | 1246 | 0 | 1202 | 3180 | 40 | 0 | 208 | 134 | 228 | 7 | 139.43 | 85.69
15:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 402 | 0 |  | 0 | 0 | 0 | 92 | 45 | 15 | 280 | 0 | 37 | 59 | 42 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 33 | 25 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 0 | 47 | 25 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 115 | 250 | 150 | 26 | 0 | 30 | 0 | 0 | 51 | 0 | 34 | 8 | 17 | 9 | 33 | 15 | 126 | 29 | 0 | 0 | 1 | 43 | 40 | 50 | 5 | 0 | 0 | 40 | 0 | 0 | 206 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 40 | 0 | 0 | 9 | 0 | 17 | 10 | 25 | 17 | 6 | 315 | 59 | 17 | 17 | 2 | 65 | 8 | 17 | 98 | 40 | 24 | 340 | 17 | 29 | 17 | 17 | 0 | 0 | 15 | 17 | 0 | 0 | 17 | 0 | 461 | 8 | 0 | 0 | 395 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 16 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 300 | 54 | 0 | 35 | 0 | 6 | 0 | 2 | 35 | 960 | 180 | 0 | 54 | 2 | 33 | 0 | 0 | 0 | 0 | 6 | 200 | 1263 | 43 | 0 |  | 5331 | 4613 | 9944 | 3028 | 908 | 1323 | 0 | 1081 | 3054 | 40 | 0 | 233 | 126 | 143 | 8 | 148.98 | 85.67
16:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 411 | 0 |  | 0 | 0 | 0 | 31 | 34 | 15 | 335 | 0 | 99 | 59 | 42 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 25 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 0 | 47 | 25 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 280 | 150 | 26 | 0 | 30 | 0 | 0 | 51 | 0 | 39 | 8 | 17 | 9 | 33 | 15 | 124 | 29 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 56 | 0 | 0 | 206 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 45 | 0 | 0 | 18 | 0 | 17 | 8 | 25 | 17 | 5 | 362 | 59 | 17 | 17 | 1 | 58 | 0 | 17 | 98 | 66 | 24 | 340 | 17 | 9 | 35 | 17 | 0 | 0 | 5 | 18 | 0 | 0 | 17 | 0 | 404 | 11 | 0 | 0 | 395 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 16 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 295 | 54 | 0 | 0 | 0 | 23 | 0 | 1 | 35 | 800 | 180 | 0 | 17 | 0 | 22 | 6 | 0 | 0 | 0 | 2 | 150 | 1263 | 11 | 0 |  | 5339 | 4290 | 9629 | 3126 | 908 | 1331 | 0 | 1003 | 2787 | 40 | 0 | 240 | 124 | 59 | 11 | 153.755 | 85.67
17:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 410 | 0 |  | 0 | 0 | 0 | 9 | 34 | 15 | 335 | 0 | 45 | 59 | 42 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 1 | 0 | 39 | 25 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 0 | 280 | 149 | 26 | 0 | 30 | 0 | 0 | 51 | 0 | 38 | 8 | 17 | 9 | 33 | 15 | 116 | 30 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 56 | 0 | 0 | 207 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 19 | 1 | 25 | 17 | 6 | 363 | 59 | 17 | 17 | 0 | 30 | 0 | 17 | 17 | 18 | 24 | 343 | 17 | 2 | 35 | 17 | 0 | 0 | 2 | 18 | 8 | 0 | 17 | 0 | 399 | 18 | 0 | 0 | 395 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 40 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 25 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 296 | 54 | 0 | 0 | 0 | 33 | 0 | 1 | 0 | 780 | 180 | 0 | 17 | 0 | 8 | 35 | 0 | 0 | 0 | 4 | 186 | 1271 | 9 | 0 |  | 5084 | 4334 | 9418 | 3075 | 908 | 1337 | 0 | 847 | 2806 | 40 | 0 | 244 | 116 | 27 | 18 | 135.61 | 85.66
18:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 380 | 0 |  | 0 | 0 | 0 | 9 | 34 | 20 | 280 | 0 | 39 | 67 | 74 | 75 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 19 | 15 | 33 | 24 | 10 | 0 | 40 | 0 | 0 | 0 | 10 | 212 | 0 | 0 | 0 |  | 6 | 0 | 51 | 25 | 0 | 19 | 12 | 12 | 0 | 0 | 0 | 0 | 280 | 148 | 26 | 0 | 30 | 0 | 0 | 51 | 0 | 38 | 8 | 17 | 9 | 33 | 15 | 122 | 32 | 0 | 0 | 0 | 43 | 40 | 11 | 5 | 0 | 0 | 40 | 0 | 0 | 206 | 16 | 0 | 10 | 285 | 17 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 6 | 313 | 69 | 105 | 17 | 0 | 97 | 0 | 17 | 98 | 55 | 24 | 353 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 29 | 35 | 0 | 145 | 0 | 421 | 19 | 0 | 0 | 395 |  | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 40 | 6 | 16 | 0 | 0 | 0 | 26 | 5 | 74 | 28 | 34 | 31 | 0 | 23 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 230 | 54 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 880 | 180 | 0 | 150 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 248 | 1257 | 0 | 0 |  | 5513 | 4637 | 10150 | 2928 | 909 | 1223 | 0 | 1435 | 2976 | 40 | 0 | 498 | 122 | 0 | 19 | 143.25 | 85.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 405 | 0 |  | 0 | 0 | 0 | 8 | 34 | 30 | 335 | 0 | 103 | 67 | 91 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 19 | 15 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 6 | 0 | 51 | 25 | 35 | 19 | 12 | 12 | 0 | 0 | 0 | 0 | 280 | 151 | 120 | 0 | 30 | 0 | 0 | 51 | 0 | 39 | 8 | 17 | 9 | 33 | 15 | 120 | 32 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 61 | 0 | 0 | 208 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 16 | 410 | 69 | 105 | 17 | 0 | 103 | 0 | 17 | 98 | 68 | 24 | 340 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 42 | 17 | 0 | 145 | 0 | 480 | 14 | 0 | 0 | 395 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 70 | 6 | 16 | 0 | 0 | 0 | 26 | 5 | 74 | 28 | 8 | 40 | 8 | 30 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 309 | 54 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1050 | 220 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1275 | 0 | 0 |  | 6170 | 4810 | 10980 | 3217 | 623 | 1483 | 0 | 1641 | 3282 | 40 | 0 | 560 | 120 | 0 | 14 | 60.165 | 85.64
19:30 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 413 | 0 |  | 0 | 0 | 0 | 0 | 20 | 30 | 335 | 0 | 100 | 0 | 91 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 19 | 15 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 6 | 0 | 51 | 0 | 50 | 19 | 12 | 17 | 0 | 0 | 0 | 0 | 285 | 149 | 120 | 0 | 35 | 0 | 0 | 51 | 0 | 33 | 8 | 17 | 9 | 33 | 15 | 120 | 32 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 60 | 0 | 0 | 208 | 16 | 0 | 10 | 315 | 17 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 26 | 412 | 69 | 105 | 17 | 0 | 51 | 0 | 17 | 98 | 69 | 24 | 340 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 42 | 0 | 0 | 145 | 0 | 501 | 16 | 0 | 0 | 395 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 70 | 6 | 16 | 0 | 0 | 0 | 26 | 7 | 80 | 28 | 0 | 40 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 308 | 54 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1100 | 220 | 0 | 100 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1270 | 0 | 0 |  | 6004 | 4764 | 10768 | 3232 | 624 | 1512 | 0 | 1356 | 3348 | 40 | 0 | 520 | 120 | 0 | 16 | 64.94 | 0
20:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 412 | 0 |  | 0 | 0 | 0 | 0 | 4 | 15 | 335 | 0 | 102 | 0 | 91 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 19 | 15 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 0 | 56 | 19 | 12 | 19 | 0 | 0 | 0 | 0 | 280 | 151 | 167 | 0 | 41 | 0 | 0 | 51 | 0 | 40 | 8 | 17 | 9 | 33 | 15 | 122 | 38 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 60 | 0 | 0 | 208 | 16 | 0 | 10 | 295 | 17 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 26 | 398 | 69 | 105 | 17 | 0 | 45 | 0 | 17 | 98 | 68 | 24 | 340 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 42 | 0 | 0 | 145 | 0 | 495 | 17 | 0 | 0 | 395 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 16 | 0 | 0 | 0 | 26 | 10 | 82 | 28 | 0 | 42 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 320 | 54 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1100 | 220 | 0 | 54 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1258 | 0 | 0 |  | 6000 | 4718 | 10718 | 3227 | 624 | 1554 | 0 | 1278 | 3330 | 40 | 0 | 526 | 122 | 0 | 17 | 75.445 | 85.65
21:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 413 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 102 | 0 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 0 | 51 | 0 | 104 | 19 | 12 | 25 | 0 | 0 | 0 | 0 | 280 | 151 | 167 | 0 | 47 | 0 | 0 | 51 | 0 | 40 | 8 | 18 | 9 | 33 | 15 | 120 | 70 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 60 | 0 | 0 | 208 | 16 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 26 | 398 | 69 | 105 | 17 | 0 | 45 | 0 | 17 | 70 | 68 | 24 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 36 | 0 | 0 | 17 | 0 | 493 | 15 | 0 | 0 | 402 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 26 | 10 | 82 | 28 | 0 | 39 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 325 | 54 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1100 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1271 | 0 | 0 |  | 5726 | 4663 | 10389 | 3267 | 624 | 1562 | 0 | 1107 | 3341 | 40 | 0 | 313 | 120 | 0 | 15 | 95 | 85.64
22:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 414 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 101 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 108 | 19 | 12 | 28 | 0 | 0 | 0 | 0 | 280 | 151 | 167 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 15 | 114 | 72 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 60 | 0 | 0 | 209 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 26 | 398 | 9 | 50 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 499 | 13 | 0 | 0 | 402 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 348 | 35 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 1266 | 0 | 0 |  | 5233 | 4565 | 9798 | 3272 | 907 | 1603 | 0 | 539 | 3277 | 40 | 0 | 33 | 114 | 0 | 13 | 93 | 85.64
23:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 384 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 102 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 108 | 19 | 12 | 30 | 0 | 0 | 0 | 0 | 270 | 151 | 167 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 15 | 108 | 75 | 0 | 0 | 0 | 42 | 40 | 53 | 5 | 0 | 0 | 30 | 0 | 0 | 209 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 0 | 0 | 26 | 398 | 9 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 10 | 0 | 0 | 400 |  | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1216 | 0 | 0 |  | 4883 | 4319 | 9202 | 3086 | 908 | 1584 | 0 | 309 | 3141 | 40 | 0 | 16 | 108 | 0 | 10 | 84 | 85.63
24:00 | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 370 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 102 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 26 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 0 | 275 | 151 | 167 | 0 | 47 | 0 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 15 | 102 | 75 | 0 | 0 | 0 | 42 | 40 | 53 | 5 | 0 | 0 | 30 | 0 | 0 | 209 | 16 | 0 | 10 | 295 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 36 | 0 | 0 | 0 | 0 | 398 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 12 | 0 | 0 | 405 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1139 | 0 | 0 |  | 4662 | 4231 | 8893 | 3090 | 907 | 1579 | 0 | 88 | 3059 | 40 | 0 | 16 | 102 | 0 | 12 | 21 | 85.63
KWH | 0 | 0 | 3766875 | 0 | 0 | 309454 | 0 | 7758000 | 0 |  | 0 | 0 | 0 | 620160 | 552581 | 232585 | 7667785 | 0 | 1868000 | 672000 | 711936 | 605760 | 705 | 0 | 0 | 0 | 38880 | 39545 | 32376 | 0 | 456000 | 284040 | 751200 | 58600 | 194400 | 0 | 876540 | 88000 | 0 | 0 | 160540 | 4999702 | 0 | 0 | 0 |  | 44880 | 0 | 645178 | 255000 | 446736 | 184320 | 278880 | 416640 | 0 | 0 | 0 | 4580500 | 6824000 | 3625000 | 1053818 | 0 | 554040 | 0 | 0 | 1197711 | 0 | 383520 | 300110 | 419724 | 221400 | 814700 | 333940 | 2534400 | 1212480 | 0 | 0 | 7950 | 1005000 | 957720 | 1191600 | 120312 | 0 | 0 | 1202976 | 0 | 0 | 5233460 | 383000 | 0 | 249300 | 7242000 | 294672 | 0 | 0 | 878182 | 0 | 0 | 175200 | 0 | 507024 | 85050 | 402240 | 300960 | 220800 | 7071000 | 980400 | 662400 | 286036 | 25082 | 890727 | 128482 | 320327 | 1214100 | 619920 | 394560 | 8048800 | 282240 | 224380 | 194400 | 309873 | 0 | 24120 | 129813 | 275520 | 65160 | 0 | 623927 | 0 | 10925453 | 360960 | 0 | 0 | 7205455 |  | 18002909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142560 | 0 | 0 | 1383000 | 131617 | 89088 | 0 | 0 | 0 | 87582 | 23401 | 649960 | 387530 | 354232 | 183030 | 42931 | 191930 | 0 | 0 | 113418 | 0 | 0 | 4153400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3895718 | 0 | 8323490 | 732000 | 0 | 271968 | 0 | 262137 | 0 | 21202 | 248928 | 26153200 | 4947927 | 0 | 1177200 | 19500 | 440640 | 346368 | 0 | 0 | 0 | 115649 | 4821800 | 27823619 | 673340 | 0 |  | 120793222 | 106211274 | 227004496 | 76063630 | 18002909 | 32389324 | 0 | 17531807 | 73877472 | 964540 | 0 | 3536848 | 2534400 | 1742606 | 360960 | 0
Fuel Cost | 0 | 0 | 16159893.75 | 0 | 0 | 1182114.28 | 0 | 22343040 | 0 |  | 0 | 0 | 0 | 12000096 | 11526839.66 | 3998136.15 | 23386744.25 | 0 | 9993800 | 12949440 | 13242009.6 | 11158099.2 | 12795.75 | 0 | 0 | 0 | 709948.8 | 632324.55 | 592157.04 | 0 | 342000 | 0 | 0 | 0 | 3481704 | 0 | 0 | 0 | 0 | 0 | 3040627.6 | 15949049.38 | 0 | 0 | 0 |  | 788092.8 | 0 | 11555137.98 | 4725150 | 6785919.84 | 3033907.2 | 1037433.6 | 0 | 0 | 0 | 0 | 12779595 | 20881440 | 12035000 | 3530290.3 | 0 | 1867114.8 | 0 | 0 | 4802821.11 | 0 | 6868843.2 | 5401980 | 1561373.28 | 166050 | 3030684 | 250455 | 16625664 | 3770812.8 | 0 | 0 | 0 | 3919500 | 3572295.6 | 5421780 | 547419.6 | 0 | 0 | 6676516.8 | 0 | 0 | 14601353.4 | 2520140 | 0 | 997200 | 22377780 | 221004 | 0 | 0 | 18134458.3 | 0 | 0 | 3346320 | 0 | 9045308.16 | 0 | 6946684.8 | 5296896 | 3718272 | 18738150 | 14519724 | 11923200 | 4962724.6 | 0 | 16514078.58 | 2507968.64 | 5106012.38 | 22266594 | 11487117.6 | 7027113.6 | 21409808 | 4719052.8 | 0 | 3555576 | 5267841 | 0 | 421858.8 | 0 | 4559856 | 1115539.2 | 0 | 11162054.03 | 0 | 76150407.41 | 0 | 0 | 0 | 0 |  | 52928552.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2681553.6 | 0 | 0 | 4370280 | 623864.58 | 1535877.12 | 0 | 0 | 0 | 1568593.62 | 429408.35 | 10925827.6 | 8246638.4 | 6751661.92 | 3278067.3 | 759449.39 | 3437466.3 | 0 | 0 | 85857.426 | 0 | 0 | 35054696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12972740.94 | 0 | 24304590.8 | 13263840 | 0 | 5423041.92 | 0 | 5266332.33 | 0 | 0 | 4814267.52 | 157180732 | 15388052.97 | 0 | 22778820 | 0 | 0 | 5864010.24 | 0 | 0 | 0 | 0 | 35922410 | 195600041.57 | 0 | 0 |  | 634956190.22 | 631456674.356 | 1266412864.576 | 234642132.026 | 52928552.46 | 79175913.64 | 0 | 320067264.29 | 499908286.98 | 0 | 0 | 63065051.18 | 16625664 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 84 | 65 | 15 | 280 | 0 | 40 | 59 | 42 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 7 | 33 | 21 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 0 | 49 | 25 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 250 | 150 | 0 | 0 | 5 | 0 | 0 | 51 | 0 | 25 | 52 | 18 | 9 | 33 | 15 | 126 | 29 | 0 | 0 | 2 | 43 | 40 | 51 | 5 | 0 | 0 | 56 | 0 | 0 | 210 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 82 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 5 | 320 | 59 | 17 | 17 | 3 | 72 | 20 | 17 | 98 | 36 | 24 | 350 | 17 | 28 | 17 | 17 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 0 | 550 | 14 | 0 | 0 | 345 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 15 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 330 | 35 | 0 | 35 | 0 | 6 | 0 | 3 | 0 | 1244 | 180 | 0 | 150 | 4 | 69 | 0 | 0 | 0 | 0 | 28 | 250 | 1268 | 129 | 0 |  | 10428 | DayPeak
Yesterday Evening Peak | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 405 | 0 |  | 0 | 0 | 0 | 8 | 34 | 30 | 335 | 0 | 103 | 67 | 91 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 19 | 15 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 | 0 | 6 | 0 | 51 | 25 | 35 | 19 | 12 | 12 | 0 | 0 | 0 | 0 | 280 | 151 | 120 | 0 | 30 | 0 | 0 | 51 | 0 | 39 | 8 | 17 | 9 | 33 | 15 | 120 | 32 | 0 | 0 | 0 | 43 | 40 | 53 | 5 | 0 | 0 | 61 | 0 | 0 | 208 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 17 | 16 | 410 | 69 | 105 | 17 | 0 | 103 | 0 | 17 | 98 | 68 | 24 | 340 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 42 | 17 | 0 | 145 | 0 | 480 | 14 | 0 | 0 | 395 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 70 | 6 | 16 | 0 | 0 | 0 | 26 | 5 | 74 | 28 | 8 | 40 | 8 | 30 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 309 | 54 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1050 | 220 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1275 | 0 | 0 |  | 10980 | EvPeak
Forecast for Evening | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 412 | 0 |  | 0 | 0 | 0 | 50 | 80 | 30 | 335 | 0 | 100 | 68 | 91 | 98 | 25 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 19 | 15 | 33 | 33 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 0 | 51 | 25 | 0 | 18 | 12 | 15 | 0 | 0 | 0 | 0 | 290 | 150 | 8 | 0 | 35 | 0 | 0 | 51 | 0 | 41 | 16 | 16 | 10 | 33 | 15 | 141 | 50 | 0 | 0 | 0 | 42 | 40 | 51 | 5 | 0 | 0 | 60 | 0 | 0 | 210 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 17 | 25 | 400 | 69 | 105 | 17 | 0 | 155 | 0 | 17 | 114 | 68 | 25 | 350 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 17 | 320 | 145 | 0 | 580 | 20 | 0 | 0 | 400 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 50 | 0 | 70 | 7 | 16 | 0 | 0 | 0 | 26 | 15 | 82 | 28 | 34 | 42 | 8 | 35 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 350 | 54 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1240 | 220 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 307 | 1350 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 140 | 0 | 0 | 12 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 15 | 335 | 0 | 100 | 60 | 91 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 15 | 33 | 33 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 0 | 0 | 51 | 25 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 0 | 290 | 150 | 8 | 0 | 35 | 0 | 0 | 51 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 128 | 50 | 0 | 0 | 1.6 | 42 | 40 | 51 | 5 | 0 | 0 | 60 | 0 | 0 | 210 | 16 | 0 | 10 | 300 | 17 | 0 | 0 | 82 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 13 | 350 | 57 | 17 | 17 | 5 | 65 | 17 | 17 | 114 | 48 | 25 | 350 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 300 | 17 | 0 | 550 | 20 | 0 | 0 | 400 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 28 | 34 | 40 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 350 | 54 | 0 | 35 | 0 | 6 | 0 | 8 | 0 | 1200 | 180 |  | 150 | 6 | 100 | 0 | 0 |  | 0 | 30 | 250 | 1300 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  |  | 108452954 | 18002909 | 0 | 73877472 | 21068655 | 2534400 | 1742606 | 360960 | 964540
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 108.453 | 18.0029 | 0 | 73.8775 | 21.0687 | 2.5344 | 1.7426 | 0.36096 | 0.96454
| Minimum Generation |  | 7431 | 4:00
| Highest Generation |  | 10980 | 19:00 | [129 empty] | 0 | [70 empty] | 227.0045
| Day Peak Generation |  | 10428 | 12:00
| Evening Peak Generation |  | 10980 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 909 | 18:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 623 | 19:00
| Load factor L.F |  | 86.14% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
|  |  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  |  | DAILY REPORT |  |  |  |  | Page -1
[7 empty] | Reporting Date : | 2024-02-15
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10428 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7492 | MW
Evening Peak Generation : |  |  | 10980 | MW Hour : | 19:00 | Available Max Generation : |  | 12054 | MW
E.P. Demand (at gen end) : |  |  | 11043 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  |  | 10980 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1054 | MW
Total Gen. (MKWH) : |  |  | 227.0045 | System Load Factor : | 86.14% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 960 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-15
Actual : |  | 85.59 | Ft.(MSL) , | Rule curve : | 95.04 | Ft.( MSL )
Gas Consumed : |  | Total = | 841.33 | MMCFD. | Oil Consumed (PDB) :
[7 empty] | HSD : |  | Liter
[7 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 313818045.666
: |  |  | Coal : | 499908286.98 | Oil : | 383132315.47 | Total : | 1196858648.116
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3823.072 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1045.9496 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1463.8103 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1271.063 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1046.4992 |  |  | 0 | 0%
Mymensingh Area |  | 60 | 1440:00 | 777.6683 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 436.6164 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 363.2198 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 710.409 |  |  | 0 | 0%
Total |  | 60 |  | 10938.3077 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj East
8) Megnaghat-450 MW.
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:18 | 19:11 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to Annual Maintenance.
08:18 | 10:04 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Forced S/D Due to To perform high temperature mitigate works of 33kV |  |  |  |  | 15.0MW load interrup.
Bha-1 feeder (B-Phase, Bus DS, Bus loop).
08:18 | 10:04 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Forced S/D Due to To perform high temperature mitigate works of 33kV |  |  |  |  | 15.0MW load interrup.
Bha-1 feeder (B-Phase, Bus DS, Bus loop).
08:21 | 19:12 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Annual Maintenance.
08:25 | 15:30 | Juldah-Shahmirpur 132kV Ckt-2 Scheduled S/D from Shahmirpur 132/33kV end Due to Annual Bay Maintenance and
from Juldah 132/33kV end Due to Annual Bay equipment maintenance work.
08:30 |  | Haripur 412MW CCPP tripped due to problem with RMS of TITAS.
08:31 |  | Haripur 412 MW CCPP Tripped
08:41 | 15:14 | Munshiganj 132/33kV S/S Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP Scheduled S/D Due to Annual Maintenance.
08:50 | 17:29 | Bibiyana-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
08:52 | 17:29 | Cumilla(N)-Shahjibazar 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end.
08:52 | 15:40 | Daudkandi-Sonargaon 132 kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Deadline checking. Shutdown
taken by Incharge Siddirganj.
09:06 | 16:43 | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Khagrachori 132/33kV end Due to Dead Line Checking
09:14 |  | Summit Meghnaghat-2 589 MW CCPP tripped due to problem with GBC.
09:14 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
09:16 | 13:03 | Cumilla(N)-Kachua 132 kV Ckt-2 Forced S/D from Kachua 132/33kV end.
09:17 | 13:04 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end.
09:21 | 18:23 | Keraniganj-Nawabganj 132kV Ckt-1 Scheduled S/D from Nawabganj 132/33kV end Due to Deadline checking(annual
maintenance) and from Keranigonj 230/132/33kV end Due to Dead line check from Nawabganj end.
| 10:08 | Thakurgaon 132/33kV S/S T-1(422T) HT is restored.
| 10:08 | Thakurgaon 132/33kV S/S Auxiliary Transformer-1 LT is restored.
Thakurgaon 132/33kV S/S T-1(422T) LT is restored.
10:08
10:58 | 00:52 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to Bus low voltage ( 389KV)
11:10 | 13:26 | Bogura 400/230kV S/S ATR-01 LT Project Work S/D Due to SAS commissioning of A2-B2 Bus section of 230kV Bus(Also S/D
of A2 and B2 BUS section of 230kV due to SAS Commissioning )
11:19 |  | Summit Meghnaghat-2 589 MW GT was sync.
11:19 |  | Meghnaghat CCPP(Summit)-2 Syncronized with remarks:- GT
11:27 | 16:17 | Niamatpur 132/33kV S/S 407T LT Project Work S/D Due to Bus Stability Test ( Relay Test )
11:28 | 16:14 | Niamatpur 132/33kV S/S 407T HT Project Work S/D Due to Bus Stability Test ( Relay Test )
12:00 |  | Day Peak Gen. 10428 MW
12:08 | 14:39 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Asper Rajuk requirement.
12:08 | 14:39 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Asper Rajuk requirement.
12:17 | 12:33 | Sonargaon 132/33kV S/S OPSL(IEL-2) Tripped showing General trip relays Due to Line distance |  |  |  |  | 16.0MW load interrup.
12:24 |  | Haripur 412MW CCPP GT was sync.
12:24 |  | Haripur 412 MW CCPP Syncronized with remarks:- GT
| 12:30 | Thakurgaon 132/33kV S/S RPC is restored.
13:24 |  | Haripur 412MW CCPP ST was sync.
13:24 |  | Haripur 412 MW CCPP Syncronized with remarks:- ST
13:51 | 14:52 | Kalurghat 132/33kV S/S 33 KV BUS-1 Forced S/D Due to 33 KV Bus maintenance by S&D Kalurghat BPDB |  |  |  |  | 3.0 MW load interrup.
13:54 | 14:53 | Kalurghat 132/33kV S/S 33 KV BUS-2 Forced S/D Due to 33 KV Bus maintenance by S&D Kalurghat BPDB. |  |  |  |  | 3.0 MW load interrup.
14:15 | 15:22 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Project Work S/D from Cumilla(S) 132/33kV end Due to Work at Cumilla(N) S/S end
14:16 | 15:21 | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Cumilla(N) 230/132/33kV end.
15:14 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
19:00 |  | Evening Peak Generation: 10980 MW.
| 21:36 | Chauddagram-Feni 132 kV Ckt-1 is restored.
| 21:36 | Chauddagram-Feni 132 kV Ckt-1 is restored.
01:04 |  | Ashuganj 420 MW CCPP(East) Syncronized with remarks:- GT
03:08 | 07:25 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Tripped showing Gas pressure low. relays Due to Gas pressure low in |  |  |  |  | 10.0 MW load interrup.
33 KV CB of TR -3.
04:28 |  | Bhola Nutan Biddut BD LTD Tripped with remarks:- st
04:29 |  | Bhola Nutan Biddut BD LTD Syncronized with remarks:- GT
05:00 |  | minimum generation :7492 MW
05:33 |  | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Tripped showing Distance Zone-1, 6.43Km. relays Due to Trip
05:33 |  | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Forced S/D Due to LA Blast of Y-Phase at 50MW Power Station
end (LA Replaced Now)
06:24 | 07:25 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Forced S/D Due to Gas pressure low
06:24 | 07:23 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Forced S/D Due to Gas pressure low.
07:10 |  | Kamrangirchar 132/33kV S/S Bus-1 Scheduled S/D Due to To do maintenance & renovation work at 132KV bus coupler
isolator.
07:10 |  | Kamrangirchar-Keraniganj 132kV Ckt Scheduled S/D from Kamrangirchar 132/33kV end Due to To do maintenance &
renovation work at 132KV bus coupler isolator.
07:18 |  | Kamrangirchar 132/33kV S/S GT-3 LT Scheduled S/D Due to To do maintenance & renovation work at 132KV bus coupler
isolator.
07:18 |  | Kamrangirchar 132/33kV S/S GT-3 HT Scheduled S/D Due to To do maintenance & renovation work at 132KV bus coupler
isolator.
07:21 |  | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Chauddagram 132/33kV end Due to Bus upgradation at Feni
grid.
07:35 |  | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) LT Scheduled S/D Due to Annual Maintenance
07:36 |  | Ashuganj 420 MW CCPP(East) Syncronized with remarks:- ST
07:36 |  | Agargaon 230/132kV S/S 132kV Transformer-1 (405T1) HT Scheduled S/D Due to Annual Maintenance
07:57 |  | Gollamari 132/33kV S/S Tr-1 LT Project Work S/D Due to 33kV Bus Development Work
07:58 |  | Gollamari 132/33kV S/S Tr-1 HT Project Work S/D Due to 33 kV Bus Development
06:00 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T LT Project Work S/D |  |  |  |  | 20.0MW
|  | Due to project work |  |  |  |  | load
interrup.
06:15 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 HT Project Work S/D |  |  |  |  | 20.0MW
|  | Due to project work |  |  |  |  | load
interrup.
06:16 |  | Juldah 132/33kV S/S 132/33 KV 406T T-1 LT Scheduled S/D Due |  |  |  |  | 20.0MW
|  | to project work |  |  |  |  | load
interrup.
06:18 |  | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha
230/132kV end.
06:58 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Project Work S/D |  |  |  |  | 20.0MW
|  | Due to project work |  |  |  |  | load
interrup.
07:05 |  | Bogura 230/132kV S/S 230KV Main 2 Project Work S/D Due to
X-Former T-04 Jack Bus (Upper Bus) Conductor Stringing.
07:46 |  | Aminbazar-Meghnaghat 230kV Ckt-1 Scheduled S/D from
Aminbazar 400/230/132kV end Due to OPGW maintenace
07:52 |  | Ishurdi 132/33kV S/S 132 kV Baghabari Line Project Work S/D
Due to project work
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 3766875 | Machine problem
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 309454 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 405 | 7758000
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 620160 | low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 552581 | low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 232585 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 705 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 103 | 1868000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 67 | 672000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7667785
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 91 | 711936 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 38880 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 605760 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 39545 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 32376 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 740040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 751200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 58600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 194400 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 130 | 878182 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 36 | 507024 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 662400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 282240 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 129813
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 65160 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 395 | 7205455 | On test.
| Dhaka area Total |  |  |  | 5062 | 2182 | 36545556
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 160540 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 85050
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 184320 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964540 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 212 | 4999702
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 286036 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under maint.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 645178 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 255000 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 402240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 278880 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 416640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 35 | 446736 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25082
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 103 | 890727 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 128482 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 320327 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 394560 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 309873 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 623927
| SS Power I |  | SS Power | 2*612 | 1224 | 480 | 10925453
| Cox's Bazar Wind |  | IPP | 66 | 0 | 14 | 360960 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 0 | 0 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1265 | 23104253
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 151 | 3625000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 4580500 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6824000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 554040 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 120 | 1053818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1197711
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 16 | 220800 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 383520 | Fuel shortage
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 300960 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 419724 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 221400 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2534400
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 814700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 300110 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 333940 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1214100 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 68 | 619920 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 24120 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 42 | 275520 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1114 | 25498283
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 32 | 1212480 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7950
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 175200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 980400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 224380
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 44880 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 116 | 2645290
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1005000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 957720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1191600
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 120312 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1202976
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 5233460
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 383000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 294672 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7242000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 410 | 7071000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 249300
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8048800 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1493 | 32999840
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 623 | 18002909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 52 | 142560
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 54 | 732000 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 440640
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 729 | 19318109
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 89088 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 6 | 131617 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 70 | 1383000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 26153200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4947927
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1177200 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4821800
| Barisal Area Total |  |  |  | 2265 | 1819 | 38703832
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 87582 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 23401 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 387530 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 354232 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 183030
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 142 | 3895718 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 309 | 8323490 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 191930 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 113418 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 42931 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 74 | 649960 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 271968 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 248928 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19500
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1275 | 27823619
| Rajshahi Area Total |  |  |  | 3631 | 1985 | 42617237
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4153400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 262137 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 21202
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 346368 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 115649
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 673340
| Rangpur Area Total |  |  |  | 950 | 277 | 5572096
| Total |  |  |  | 25481 | 10980 | 227004496
| Eastern Grid Total |  |  |  | 15398 | 6170 | 120793222
| Western Grid Total |  |  |  | 10083 | 4810 | 106211274
| National Grid Total |  |  |  | 25481 | 10980 | 227004496
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-14
| (a) ENTIRE EASTERN GRID : |  | 7200.55 | MW | (b) ENTIRE WESTERN GRID : |  | 3300.3 | MW
| i) Dhaka area |  | 3984.55 | MW | i) Khulna area |  | 1183.6 | MW
| ii) Chittagong area |  | 1032 | MW | ii) Rajshahi area |  | 1068.2 | MW
| iii) Comilla area |  | 897 | MW | iii) Barisal area |  | 291.5 | MW
| iv) Mymensingh area |  | 909 | MW | iv) Rangpur area |  | 757 | MW
| v) Sylhet area |  | 378 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10500.85 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 23 | 18:00 | Kamrangirchar | 48.9 | 13:00 | Narinda | 42 | 13:00 | Sherpur | 110 | 07:00
2 | AKSML | 11 | 16:00 | Chowmuhani | 144 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 144 | 20:00 | Shikalbaha | 16 | 11:00
3 | Aftabnagar | 24 | 12:00 | Chuadanga | 74 | 18:30 | Kazla | 79 | 13:00 | Natore | 108 | 18:30 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 57 | 13:00 | Coxsbazar | 95 | 18:00 | Keranigonj | 64 | 13:00 | Nawabganj | 29.4 | 13:00 | Shitalakhya | 80.4 | 12:00
5 | Agrabad | 52 | 18:30 | Cumilla(N) | 98 | 19:30 | Khagrachori | 26 | 19:00 | Netrakona | 130 | 19:30 | Sholosohor | 33 | 12:00
6 | Amnura | 57 | 12:00 | Cumilla(S) | 134 | 14:00 | Khulna | 76 | 13:00 | New | 18 | 11:00 | Shyampur | 164 | 13:00
7 | Ashuganj | 91 | 12:00 | Daudkandi | 110 | 20:00 | Khulshi | 139 | 14:00 | Niamatpur | 77 | 08:00 | Siddhirganj | 96 | 09:00
8 | BIPTC | N/A | N/A | Dhaka | 16 | 12:00 | Kishoreganj | 112 | 18:30 | Noapara | 47 | 18:30 | Sirajganj | 92 | 19:00
9 | BSRM | 86 | 00:00 | Dhamrai | 108 | 20:00 | Kodda | 258 | 19:00 | PHP | 10 | 15:00 | Sonargaon | 99 | 06:00
10 | Bagerhat | 69 | 18:30 | Dhanmondi | 101 | 13:00 | Kulaura | 26 | 18:00 | Pabna | 80 | 18:30 | Sreemongol | 44 | 18:30
11 | Bakulia | 75 | 14:00 | Dohazari | 62 | 19:30 | Kurigram | 62 | 18:30 | Palashbari | 100 | 08:00 | Sreepur | 63 | 18:30
12 | Banani | 21.2 | 13:00 | Faridpur | 110 | 18:30 | Kushtia | 90 | 18:00 | Panchagarh | 43 | 18:30 | Srinagar | 29.2 | 20:00
13 | Bangabhaban | 10 | 13:00 | Fatullah | 49 | 10:00 | Lalbag | 81 | 13:00 | Patuakhali | 52 | 20:00 | Sunamganj | 37 | 18:30
14 | Barapukuria | 56 | 08:00 | Fenchuganj | 23 | 19:00 | Lalmonirhat | 41 | 08:00 | Payra | 14 | 12:00 | Sylhet | 14 | 18:00
15 | Barguna | 12 | 00:00 | Feni | 74 | 18:00 | MI_Cement | 12.4 | 16:00 | Postogola | 41 | 13:00 | Sylhet-132 | 87 | 18:00
16 | Barishal | 79 | 21:00 | GPH | 98 | 14:00 | Madanganj | 26 | 12:00 | Purbachal | 15 | 18:00 | TK | 14 | 18:00
17 | Barishal-230 | 62 | 19:30 | Ghorashal | 72 | 17:00 | Madaripur | 68 | 21:00 | Purbasadipur | 116 | 13:00 | Tangail | 160 | 20:00
18 | Baroaulia | 63 | 11:00 | Goalpara | 28 | 13:00 | Madartek | 59.1 | 13:00 | Rahim | 44 | 09:00 | Thakurgaon | 79 | 18:30
19 | Baroirhat | 41 | 19:00 | Gollamari | 36 | 12:00 | Madunaghat | 35 | 19:00 | Rajbari | 47 | 18:30 | Tongi | 129 | 17:00
20 | Bashundhara | 128 | 13:00 | Gopalganj | 70.6 | 19:00 | Magura | 45 | 18:30 | Rajendrapur | 74 | 18:00 | Ullahpara | 20 | 18:30
21 | BashundharaCement | 12 | 01:00 | Gulshan | 74 | 13:00 | Mahasthangarh | 54 | 08:00 | Rajshahi | 103 | 13:00 | Ullon | 36 | 14:00
22 | Beanibazar | 40 | 18:00 | Halishahar | 74 | 15:00 | Manikganj | 82 | 18:30 | Rajshahi-230 | 27 | 13:00 | Uttara | 43 | 13:00
23 | Benapole | 50 | 08:00 | HaripurSBU | 157 | 15:00 | Maniknagar | 52 | 12:00 | Ramganj | 68 | 19:30 | UttaraNew | 30 | 13:00
24 | Bhaluka | 116 | 18:30 | Hasnabad | 68 | 13:00 | Matarbari | 34 | 18:30 | Rampur | 19 | 18:30 | Zigatola | 52 | 13:00
25 | Bhandaria | 32 | 19:30 | Hathazari | 50 | 18:00 | Matuail | 59 | 12:00 | Rangamati | 12 | 19:00
26 | Bhangura | 25 | 18:00 | Ishurdi | 52 | 18:30 | Millgate | 85 | 12:00 | Rangpur | 108 | 18:30
27 | Bheramara(GK) | 40 | 18:30 | Jaldhaka | 61 | 08:00 | Mirpur | 94 | 18:30 | Ruppur | 4.6 | 11:00
28 | Bhulta | 227 | 19:30 | Jamalpur | 114 | 06:00 | Mirsorai | 4 | 19:30 | SSM | 12 | 21:00
29 | Bog-Sherpur | 56 | 07:00 | Jashore | 103 | 13:00 | Mirzapur | 52 | 20:00 | Saidpur | 101 | 11:00
30 | Bogura | 118 | 13:00 | Jhenaidah | 90 | 18:30 | Mithapukur | 50 | 08:00 | Satkhira | 89 | 19:00
31 | Borhanuddin | 50 | 20:00 | Joydebpur | 141 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 82 | 13:00
32 | Brahmanbaria | 111 | 19:30 | Joypurhat | 56 | 09:00 | Mogbazar | 82.1 | 14:00 | Savar | 162 | 12:00
33 | Cantonment | 102 | 13:00 | Juldah | 20 | 23:00 | Mongla | 27 | 11:00 | SevenRings | 15.59 | 15:00
34 | Chandpur | 44 | 20:00 | KSRM | 29 | 17:00 | Motijheel | 30 | 13:00 | ShahCement | 32 | 15:00
35 | Chandraghona | 22 | 18:00 | Kabirpur | 215 | 19:00 | Munshiganj | 66 | 13:00 | Shahjadpur | 56 | 09:00
36 | Chapai | 63 | 12:00 | Kachua | 49 | 18:00 | Mymensingh | 188 | 13:00 | Shahjibazar | 86 | 18:30
37 | Charsaidpur | 42 | 11:00 | Kallyanpur | 78 | 13:00 | Naogaon | 105 | 13:00 | Shahmirpur | 44.5 | 00:00
38 | Chauddagram | 44 | 13:00 | Kalurghat | 29 | 12:00 | Narail | 40 | 19:00 | Shariatpur | 50 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 415 | 05:00 | 386 | 12:00 | Gopalganj | 419 | 05:00 | 393 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 400 | 03:00 | 381 | 12:00
| Bhulta | 409 | 05:00 | 383 | 12:00 | Madunaghat_I | 419 | 20:00 | 411 | 13:00
| Bibiana | 416 | 01:00 | 406 | 11:00 | Payra | 422 | 05:00 | 409 | 12:00
| BIPTC | 407 | 03:00 | 391 | 12:00 | Rahanpur | 418 | 05:00 | 396 | 13:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 419 | 03:00 | 389 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 240 | 05:00 | 216 | 12:00 | Hasnabad | 237 | 00:00 | 226 | 11:00
| AKSML | 238 | 20:00 | 230 | 01:00 | Hathazari | 238 | 19:30 | 230 | 12:00
| Aminbazar | 240 | 03:00 | 228 | 13:00 | Ishurdi | 241 | 05:00 | 227 | 12:00
| Ashuganj | 243 | 05:00 | 231 | 12:00 | Jhenaidah | 239 | 05:00 | 223 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 239 | 05:00 | 224 | 12:00
| Baghabari | 239 | 05:00 | 226 | 12:00 | Keranigonj | 240 | 05:00 | 223 | 12:00
| Barapukuria | 226 | 04:00 | 207 | 08:00 | Khulna(S) | 244 | 03:00 | 228 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 238 | 20:00 | 213 | 03:00
| Barishal | 245 | 05:00 | 239 | 11:00 | Maniknagar | 241 | 04:00 | 226 | 13:00
| Bheramara | 239 | 05:00 | 223 | 12:00 | Meghnaghat | 246 | 04:00 | 234 | 18:00
| Bhulta | 244 | 04:00 | 228 | 12:00 | Mirsorai | 242 | 19:00 | 231 | 12:00
| Bibiana | 238 | 01:00 | 232 | 12:00 | Rajshahi | 242 | 05:00 | 228 | 08:00
| BIPTC | 240 | 05:00 | 225 | 12:00 | Rampal | 242 | 05:00 | 224 | 12:00
| Bogura | 233 | 05:00 | 217 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 02:00 | 241 | 12:00 | Rampura | 240 | 02:00 | 227 | 12:00
| BSRM | 242 | 20:00 | 231 | 23:00 | Shikalbaha | 234 | 10:00 | 228 | 01:00
| Cumilla(N) | 240 | 02:00 | 227 | 12:00 | Shyampur | 241 | 05:00 | 225 | 13:00
| Fenchuganj | 241 | 05:00 | 236 | 12:00 | Siddhirganj | 242 | 06:00 | 227 | 12:00
| Ghorashal | 244 | 04:00 | 232 | 13:00 | Sirajgonj | 243 | 04:00 | 232 | 12:00
| Ghorashal-230 | 240 | 04:00 | 227 | 13:00 | Sreepur | 239 | 02:00 | 227 | 11:00
| GPH | 238 | 20:00 | 230 | 01:00 | Tongi | 238 | 05:00 | 220 | 11:00
| Haripur | 240 | 03:00 | 228 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 03:00 | 128 | 12:00 | Lalbag | 137 | 05:00 | 126 | 12:00
| Agargaon | 141 | 03:00 | 130 | 12:00 | Lalmonirhat | 130 | 02:00 | 116 | 08:00
| Agrabad | 139 | 09:00 | 132 | 12:00 | Madanganj | 135 | 03:00 | 128 | 12:00
| AKS | 137 | 20:00 | 131 | 16:00 | Madaripur | 138 | 03:00 | 133 | 07:00
| Aminbazar | 136 | 03:00 | 125 | 12:00 | Madartek | 138 | 05:00 | 127 | 13:00
| Amnura | 140 | 14:00 | 126 | 08:00 | Madunaghat | 139 | 21:00 | 134 | 01:00
| Ashuganj | 142 | 05:00 | 135 | 12:00 | Magura | 138 | 01:00 | 128 | 12:00
| Bagerhat | 137 | 05:00 | 127 | 12:00 | Mahasthangarh | 136 | 03:00 | 123 | 08:00
| Bakulia | 137 | 09:00 | 132 | 17:00 | Manikganj | 133 | 15:00 | 124 | 12:00
| Banani | 140 | 04:00 | 126 | 11:00 | Maniknagar | 135 | 20:00 | 121 | 12:00
| Bangabhaban | 136 | 21:00 | 121 | 12:00 | Matarbari | 130 | 10:00 | 126 | 12:00
| Barapukuria | 138 | 04:00 | 122 | 08:00 | Matuail | 135.3 | 06:00 | 127.5 | 13:00
| Barguna | 139 | 10:00 | 133 | 22:00 | Millgate | 141 | 04:00 | 128 | 12:00
| Barishal | 140 | 00:00 | 129 | 22:00 | Mirpur | 136 | 03:00 | 125 | 12:00
| Barishal-230 | 141 | 02:00 | 136 | 11:00 | Mirzapur | 129 | 04:00 | 122 | 12:00
| Baroaulia | 139 | 20:00 | 134 | 12:00 | Mithapukur | 134 | 05:00 | 117 | 08:00
| Baroirhat | 140 | 19:00 | 131 | 23:00 | MI_Cement | 137.5 | 05:00 | 129 | 13:00
| Bashundhara | 140 | 03:00 | 126 | 13:00 | Modern | 138 | 19:30 | 133 | 12:00
| BashundharaCement | 135 | 03:00 | 128 | 12:00 | Mogbazar | 140 | 05:00 | 130 | 11:00
| Beanibazar | 136 | 01:00 | 130 | 13:00 | Mongla | 135 | 16:00 | 126 | 12:00
| Benapole | 138 | 04:00 | 125 | 11:00 | Motijheel | 136 | 21:00 | 121 | 12:00
| Bhaluka | 135 | 04:00 | 125 | 13:00 | Munshiganj | 135 | 06:00 | 128 | 12:00
| Bhandaria | 137 | 03:00 | 131 | 22:00 | Mymensingh | 132 | 04:00 | 116 | 05:00
| Bhangura | 140 | 03:00 | 131 | 11:00 | Naogaon | 133 | 04:00 | 119 | 13:00
| Bheramara | 139 | 05:00 | 129 | 12:00 | Narail | 141 | 03:00 | 129 | 12:00
| Bheramara(GK) | 138 | 03:00 | 129 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 124 | 02:00 | 119 | 11:00 | Narshingdi | 129 | 00:00 | 118 | 12:00
| Bog-Sherpur | 137 | 02:00 | 126 | 12:00 | Natore | 137 | 05:00 | 128 | 08:00
| Bogura | 138 | 03:00 | 126 | 12:00 | Nawabganj | 138 | 05:00 | 126 | 12:00
| Bogura-230 | 136 | 03:00 | 127 | 08:00 | Netrakona | 130 | 21:00 | 114 | 19:30
| Brahmanbaria | 139 | 05:00 | 130 | 12:00 | New | 141 | 03:00 | 130 | 12:00
| Cantonment | 141 | 04:00 | 130 | 12:00 | Niamatpur | 133 | 03:00 | 116 | 13:00
| Chandpur | 140 | 18:00 | 125 | 23:00 | Noapara | 136 | 05:00 | 126 | 12:00
| Chandraghona | 139 | 09:00 | 134 | 01:00 | Pabna | 139 | 01:00 | 130 | 12:00
| Chapai | 136 | 06:00 | 127 | 12:00 | Palashbari | 132 | 04:00 | 117 | 08:00
| Charsaidpur | 137 | 03:00 | 129 | 12:00 | Panchagarh | 134 | 21:00 | 107 | 13:00
| Chauddagram | 142 | 19:00 | 130 | 23:00 | Patuakhali | 139 | 13:00 | 134 | 00:00
| Chhatak | 137 | 04:00 | 131 | 12:00 | Payra | 138 | 14:00 | 135 | 08:00
| Chowmuhani | 139 | 19:00 | 125 | 23:00 | PHP | 140 | 19:00 | 129 | 23:00
| Chuadanga | 139 | 04:00 | 125 | 12:00 | Postogola | 139 | 04:00 | 130 | 11:00
| Coxsbazar | 130 | 09:00 | 123 | 18:00 | Purbachal | 140 | 02:00 | 126 | 13:00
| Cumilla(N) | 143 | 20:00 | 129 | 09:00 | Purbasadipur | 131 | 20:00 | 109 | 12:00
| Cumilla(S) | 141 | 05:00 | 126 | 09:00 | Rahanpur | 139 | 05:00 | 131 | 12:00
| Daudkandi | 130 | 05:00 | 119 | 13:00 | Rahim | 135 | 02:00 | 127 | 12:00
| Dhaka | 137 | 03:00 | 128 | 11:00 | Rajbari | 139 | 03:00 | 130 | 12:00
| Dhamrai | 136 | 05:00 | 125 | 12:00 | Rajendrapur | 133 | 18:30 | 123 | 13:00
| Dhanmondi | 137 | 04:00 | 128 | 12:00 | Rajshahi | 135 | 04:00 | 128 | 07:00
| Dohazari | 134 | 10:00 | 130 | 01:00 | Rajshahi-230 | 136 | 05:00 | 124 | 12:00
| Faridpur | 140 | 03:00 | 131 | 12:00 | Ramganj | 139 | 19:30 | 124 | 23:00
| Fatullah | 138 | 04:00 | 129 | 12:00 | Rampur | 139 | 19:30 | 133 | 01:00
| Fenchuganj | 138 | 06:00 | 133 | 12:00 | Rampura | 138 | 05:00 | 127 | 12:00
| Feni | 140 | 19:00 | 128 | 23:00 | Rangamati | 139 | 20:00 | 134 | 23:00
| Ghorashal | 145 | 05:00 | 135 | 13:00 | Rangpur | 131 | 21:00 | 116 | 08:00
| Goalpara | 139 | 05:00 | 128 | 12:00 | Ruppur | 139 | 02:00 | 132 | 11:00
| Gollamari | 138 | 05:00 | 129 | 12:00 | Saidpur | 132 | 21:00 | 113 | 08:00
| Gopalganj | 138 | 02:00 | 129 | 12:00 | Satkhira | 137 | 03:00 | 126 | 12:00
| Gopalganj-400 | 139 | 03:00 | 131 | 12:00 | Satmasjid | 141 | 05:00 | 130 | 12:00
| Gulshan | 137 | 04:00 | 127 | 13:00 | Savar | 133 | 02:00 | 123 | 12:00
| Halishahar | 139 | 20:00 | 132 | 03:00 | SevenRings | 145 | 05:00 | 133 | 13:00
| Haripur | 135 | 02:00 | 127 | 12:00 | ShahCement | 137 | 03:00 | 129 | 12:00
| HaripurSBU | 135 | 02:00 | 127 | 12:00 | Shahjadpur | 140 | 00:00 | 133 | 10:00
| Hasnabad | 138 | 05:00 | 131 | 13:00 | Shahjibazar | 137 | 05:00 | 129 | 12:00
| Hathazari | 140 | 19:00 | 135 | 12:00 | Shahmirpur | 138 | 09:00 | 133 | 11:00
| Ishurdi | 142 | 05:00 | 133 | 12:00 | Shariatpur | 139 | 03:00 | 130 | 12:00
| Jaldhaka | 132 | 21:00 | 111 | 08:00 | Sherpur | 124 | 10:00 | 110 | 02:00
| Jamalpur | 127 | 10:00 | 113 | 02:00 | Shikalbaha | 127 | 20:00 | 121 | 13:00
| Jashore | 136 | 03:00 | 125 | 12:00 | Shikalbaha-230 | 139 | 23:00 | 133 | 13:00
| Jhenaidah | 139 | 04:00 | 130 | 12:00 | Shitalakhya | 137.5 | 05:00 | 129 | 13:00
| Jhenaidah-230 | 142 | 05:00 | 130 | 12:00 | Sholosohor | 138 | 20:00 | 133 | 01:00
| Joydebpur | 142 | 04:00 | 131 | 16:00 | Shyampur | 138 | 03:00 | 128 | 13:00
| Joypurhat | 133 | 03:00 | 117 | 13:00 | Shyampur-230 | 138 | 04:00 | 128 | 13:00
| Juldah | 139 | 20:00 | 133 | 01:00 | Siddhirganj | 136 | 04:00 | 127 | 12:00
| Kabirpur | 135 | 00:00 | 124 | 12:00 | Sirajganj | 137 | 03:00 | 126 | 12:00
| Kachua | 141 | 20:00 | 127 | 22:00 | Sonargaon | 133 | 00:00 | 125 | 10:00
| Kaliakoir | 138 | 04:00 | 127 | 12:00 | Sreemongol | 136 | 01:00 | 130 | 13:00
| Kallyanpur | 137 | 02:00 | 129 | 12:00 | Sreepur | 136 | 01:00 | 128 | 13:00
| Kalurghat | 139 | 19:00 | 134 | 13:00 | Srinagar | 136 | 02:00 | 126 | 12:00
| Kamrangirchar | 136 | 04:00 | 126 | 12:00 | SSM | 142 | 20:00 | 139 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 03:00 | 131 | 11:00
| Kazla | 135 | 00:00 | 121 | 12:00 | Sylhet | 136 | 05:00 | 132 | 18:00
| Keranigonj | 137 | 03:00 | 126 | 12:00 | Sylhet-132 | 136 | 05:00 | 133 | 11:00
| Khagrachori | 137 | 08:00 | 131 | 13:00 | Tangail | 127 | 21:00 | 120 | 12:00
| Khulna | 136 | 02:00 | 128 | 12:00 | Thakurgaon | 133 | 21:00 | 105 | 13:00
| Khulna(S) | 139 | 05:00 | 128 | 12:00 | TK | 138 | 19:00 | 133 | 05:00
| Khulshi | 137 | 20:00 | 132 | 02:00 | Tongi | 139 | 03:00 | 128 | 11:00
| Kishoreganj | 136 | 04:00 | 127 | 12:00 | Ullahpara | 138 | 03:00 | 128 | 11:00
| Kodda | 140 | 03:00 | 124 | 09:00 | Ullon | 135 | 00:00 | 127 | 13:00
| KSRM | 141 | 20:00 | 134 | 01:00 | Uttara | 135 | 03:00 | 126 | 12:00
| Kulaura | 137 | 00:00 | 133 | 12:00 | UttaraNew | 140 | 05:00 | 126 | 12:00
| Kurigram | 130 | 21:00 | 112 | 08:00 | Zigatola | 138 | 05:00 | 125 | 13:00
| Kushtia | 140 | 05:00 | 130 | 11:00

## L-Curve
Date | 2024-02-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1410 | 4662 | 4231 | 8893 |  |  |  | QF-LDC-11 |  |  |  |  | Forecast Last Row | 188
0:30 | 1445 | 4409 | 4189.5 | 8598.5 | Date: | 2024-02-14 | [6 empty] | Forecast Last Column | 18
1:00 | 1480 | 4156 | 4148 | 8304
1:30 | 1385 | 4149.5 | 3949 | 8098.5
2:00 | 1290 | 4143 | 3750 | 7893
2:30 | 1195 | 4129 | 3639.5 | 7768.5 | [5 empty] | Gen. at Eve. Peak | #REF! | 10980 MW (19:00 )
3:00 | 1100 | 4115 | 3529 | 7644 | [6 empty] | #REF!
3:30 | 1076 | 4118 | 3419.5 | 7537.5 | [5 empty] | Gen. at Day Peak | #REF! | 10428 MW (12:00 )
4:00 | 1052 | 4121 | 3310 | 7431 | [6 empty] | #REF!
4:30 | 1011 | 4172 | 3273.5 | 7445.5 | [5 empty] | Highest Generation | #REF!
5:00 | 970 | 4223 | 3237 | 7460 | [6 empty] | #REF!
5:30 | 965 | 4306 | 3290.5 | 7596.5
6:00 | 960 | 4389 | 3344 | 7733
6:30 | 975 | 4614.5 | 3498 | 8112.5
7:00 | 990 | 4840 | 3652 | 8492
7:30 | 1020 | 5045.5 | 3897 | 8942.5
8:00 | 1050 | 5251 | 4142 | 9393
8:30 | 1100 | 5140.5 | 4320.5 | 9461
9:00 | 1150 | 5030 | 4499 | 9529
9:30 | 1300 | 4897.5 | 4544.5 | 9442
10:00 | 1450 | 4765 | 4590 | 9355
10:30 | 1520 | 4837.5 | 4785 | 9622.5
11:00 | 1590 | 4910 | 4980 | 9890
11:30 | 1605 | 5096.5 | 5062.5 | 10159
12:00 | 1620 | 5283 | 5145 | 10428
12:30 | 1520 | 5347 | 5187 | 10534
13:00 | 1420 | 5411 | 5229 | 10640
13:30 | 1405 | 5368 | 5024 | 10392
14:00 | 1390 | 5325 | 4819 | 10144
14:30 | 1460 | 5328 | 4716 | 10044
15:00 | 1530 | 5331 | 4613 | 9944
15:30 | 1550 | 5335 | 4451.5 | 9786.5
16:00 | 1570 | 5339 | 4290 | 9629
16:30 | 1585 | 5211.5 | 4312 | 9523.5
17:00 | 1600 | 5084 | 4334 | 9418
17:30 | 1520 | 5298.5 | 4485.5 | 9784
18:00 | 1440 | 5513 | 4637 | 10150
18:30 | 1230 | 5841.5 | 4723.5 | 10565
19:00 | 1020 | 6170 | 4810 | 10980
19:30 | 1090 | 6004 | 4764 | 10768
20:00 | 1050 | 6000 | 4718 | 10718 |  |  |  | Executive Engineer
20:30 | 1075 | 5863 | 4690.5 | 10553.5 |  |  |  | Network Operation Division
21:00 | 1100 | 5726 | 4663 | 10389
21:30 | 1195 | 5479.5 | 4614 | 10093.5
22:00 | 1290 | 5233 | 4565 | 9798 |  |  |  |  | Page 6 of 7
22:30 | 1345 | 5058 | 4442 | 9500
23:00 | 1400 | 4883 | 4319 | 9202
23:30 | 1405 | 4772.5 | 4275 | 9047.5
24:00 | 1410 | 4662 | 4231 | 8893
10980 MW (19:00 )
10428 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-14 |  | Energy |  | 227004496
[14 empty] | 2024-02-14 |  |  |  |  | QF-LDC-12 | [6 empty] | Forecast Last Row | 188
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE | [12 empty] | Forecast Last Column | 18
0:00 | 3090 | 907 | 1579 | 0 | 88 | 3059 | 40 | 0 | 16 | 102 | 0 | 12 | 21
0:30 | 3125 | 860 | 1420.5 | 0 | 59 | 2979.5 | 40 | 0 | 8 | 92 | 0 | 14.5 | 10.5 |  | Date: | 2024-02-14
1:00 | 3160 | 813 | 1262 | 0 | 30 | 2900 | 40 | 0 | 0 | 82 | 0 | 17 | 0
1:30 | 3165.5 | 718.5 | 1273.5 | 0 | 23.5 | 2777 | 40 | 0 | 0 | 81 | 0 | 19.5 | 0 | [8 empty] | Total Energy | 227.0045 | 227.0045 | Total Energy Gen 227.004 MKWHr Energy Not Served 2.584 MKWHr Energy Requirement 229.589 MKWHr
2:00 | 3171 | 624 | 1285 | 0 | 17 | 2654 | 40 | 0 | 0 | 80 | 0 | 22 | 0 | [8 empty] | Energy not Served | 2.5844 | 2.5844
2:30 | 3174 | 624 | 1294 | 0 | 8.5 | 2527 | 40 | 0 | 0 | 78 | 0 | 23 | 0 | [8 empty] | Energy Requirement | 229.5889 | 229.5889
3:00 | 3177 | 624 | 1303 | 0 | 0 | 2400 | 40 | 0 | 0 | 76 | 0 | 24 | 0
3:30 | 3172 | 624 | 1282 | 0 | 0 | 2325.5 | 40 | 0 | 0 | 75 | 0 | 19 | 0 | [7 empty] | Shortage
4:00 | 3167 | 624 | 1261 | 0 | 0 | 2251 | 40 | 0 | 0 | 74 | 0 | 14 | 0
4:30 | 3202 | 624 | 1248.5 | 0 | 0 | 2239.5 | 40 | 0 | 0 | 74 | 0 | 17.5 | 0
5:00 | 3237 | 624 | 1236 | 0 | 0 | 2228 | 40 | 0 | 0 | 74 | 0 | 21 | 0
5:30 | 3270 | 624.5 | 1268 | 0 | 7.5 | 2281 | 40 | 0 | 8 | 76 | 0 | 21.5 | 0
6:00 | 3303 | 625 | 1300 | 0 | 15 | 2334 | 40 | 0 | 16 | 78 | 0 | 22 | 0
6:30 | 3373.5 | 624.5 | 1387 | 0 | 126.5 | 2431.5 | 40 | 0 | 24.5 | 79 | 6.5 | 19.5 | 39.5 | [5 empty] | Coal
7:00 | 3444 | 624 | 1474 | 0 | 238 | 2529 | 40 | 0 | 33 | 80 | 13 | 17 | 79
7:30 | 3488.5 | 624 | 1456.5 | 0 | 411.5 | 2745 | 40 | 0 | 33 | 88 | 39.5 | 16.5 | 90.5925 |  |  |  |  | Oil
8:00 | 3533 | 624 | 1439 | 0 | 585 | 2961 | 40 | 0 | 33 | 96 | 66 | 16 | 102.185
8:30 | 3272.5 | 624 | 1418 | 0 | 712.5 | 3123.5 | 40 | 0 | 58.5 | 102 | 92.5 | 17.5 | 228.245
9:00 | 3012 | 624 | 1397 | 0 | 840 | 3286 | 40 | 0 | 84 | 108 | 119 | 19 | 354.305
9:30 | 2959.5 | 624 | 1166 | 0 | 948 | 3339.5 | 40 | 0 | 90.5 | 111 | 150.5 | 13 | 461.265
10:00 | 2907 | 624 | 935 | 0 | 1056 | 3393 | 40 | 0 | 97 | 114 | 182 | 7 | 568.225
10:30 | 2881.5 | 721.5 | 931.5 | 0 | 1125 | 3413 | 55 | 0 | 131 | 116 | 240.5 | 7.5 | 360.5125
11:00 | 2856 | 819 | 928 | 0 | 1194 | 3433 | 70 | 0 | 165 | 118 | 299 | 8 | 152.8
11:30 | 2859 | 863 | 1104 | 0 | 1214.5 | 3457.5 | 55 | 0 | 168 | 122 | 305 | 11 | 144.4
12:00 | 2862 | 907 | 1280 | 0 | 1235 | 3482 | 40 | 0 | 171 | 126 | 311 | 14 | 136
12:30 | 2935 | 907.5 | 1325.5 | 0 | 1237.5 | 3482 | 41.5 | 0 | 181 | 129 | 283.5 | 11.5 | 137.715
13:00 | 3008 | 908 | 1371 | 0 | 1240 | 3482 | 43 | 0 | 191 | 132 | 256 | 9 | 139.43
13:30 | 3008 | 908 | 1371 | 0 | 1240 | 3482 | 43 | 0 | 191 | 132 | 256 | 9 | 139.43
14:00 | 3008 | 908 | 1371 | 0 | 1240 | 3482 | 43 | 0 | 191 | 132 | 256 | 9 | 139.43
14:30 | 3018 | 908 | 1347 | 0 | 1160.5 | 3268 | 41.5 | 0 | 212 | 129 | 199.5 | 8.5 | 144.205
15:00 | 3028 | 908 | 1323 | 0 | 1081 | 3054 | 40 | 0 | 233 | 126 | 143 | 8 | 148.98
15:30 | 3077 | 908 | 1327 | 0 | 1042 | 2920.5 | 40 | 0 | 236.5 | 125 | 101 | 9.5 | 151.3675
16:00 | 3126 | 908 | 1331 | 0 | 1003 | 2787 | 40 | 0 | 240 | 124 | 59 | 11 | 153.755
16:30 | 3100.5 | 908 | 1334 | 0 | 925 | 2796.5 | 40 | 0 | 242 | 120 | 43 | 14.5 | 144.6825
17:00 | 3075 | 908 | 1337 | 0 | 847 | 2806 | 40 | 0 | 244 | 116 | 27 | 18 | 135.61
17:30 | 3001.5 | 908.5 | 1280 | 0 | 1141 | 2891 | 40 | 0 | 371 | 119 | 13.5 | 18.5 | 139.43
18:00 | 2928 | 909 | 1223 | 0 | 1435 | 2976 | 40 | 0 | 498 | 122 | 0 | 19 | 143.25
18:30 | 3072.5 | 766 | 1353 | 0 | 1538 | 3129 | 40 | 0 | 529 | 121 | 0 | 16.5 | 101.7075
19:00 | 3217 | 623 | 1483 | 0 | 1641 | 3282 | 40 | 0 | 560 | 120 | 0 | 14 | 60.165
19:30 | 3232 | 624 | 1512 | 0 | 1356 | 3348 | 40 | 0 | 520 | 120 | 0 | 16 | 67.805
20:00 | 3227 | 624 | 1554 | 0 | 1278 | 3330 | 40 | 0 | 526 | 122 | 0 | 17 | 75.445
20:30 | 3247 | 624 | 1558 | 0 | 1192.5 | 3335.5 | 40 | 0 | 419.5 | 121 | 0 | 16 | 85.2225
21:00 | 3267 | 624 | 1562 | 0 | 1107 | 3341 | 40 | 0 | 313 | 120 | 0 | 15 | 95
21:30 | 3269.5 | 765.5 | 1582.5 | 0 | 823 | 3309 | 40 | 0 | 173 | 117 | 0 | 14 | 94
22:00 | 3272 | 907 | 1603 | 0 | 539 | 3277 | 40 | 0 | 33 | 114 | 0 | 13 | 93
22:30 | 3179 | 907.5 | 1593.5 | 0 | 424 | 3209 | 40 | 0 | 24.5 | 111 | 0 | 11.5 | 88.5
23:00 | 3086 | 908 | 1584 | 0 | 309 | 3141 | 40 | 0 | 16 | 108 | 0 | 10 | 84
23:30 | 3088 | 907.5 | 1581.5 | 0 | 198.5 | 3100 | 40 | 0 | 16 | 105 | 0 | 11 | 52.5 |  | Max Temp. in Dhaka |  | 29.6°C
24:00 | 3090 | 907 | 1579 | 0 | 88 | 3059 | 40 | 0 | 16 | 102 | 0 | 12 | 21
Executive Engineer
[5 empty] | 10718 | [13 empty] | Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 227.004 MKWHr Energy Not Served 2.584 MKWHr Energy Requirement 229.589 MKWHr
Shortage

## Generation
2024-02-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 969780
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 17 | 17 | 17 | 17 | 17 | 11 | 0 | 176713
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 5 | 10 | 17 | 20 | 20 | 20 | 16 | 15 | 6 | 2 | [9 empty] | 126225
6 | Sikalbaha 225MW CCPP (Gas) | 210 | 213 | 213 | 211 | 211 | 211 | 211 | 210 | 211 | 211 | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 211 |  | 211 | 211 | 211 | 211 | 211 | 211 | 212 | 5018422
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 51 | 51 | 50 | 41 | 50 | 49 | 50 | 50 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 0 | 763601
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 308618
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [8 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 32 |  | 41 | 32 | 32 | 31 | 33 | 33 | 0 | 489056
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 41 | 40 | 42 | 41 | 41 | 42 | 107 | 40 | 38 | 40 | 62 | 99 | 99 | 99 | 98 | 99 | 99 | 62 |  | 39 | 104 | 103 | 99 | 97 | 63 | 100 | 1809000
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 300 | 300 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 330 | 335 | 290 |  | 335 | 335 | 335 | 335 | 330 | 335 | 300 | 7836312
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 5 | 47 | 67 | 75 | 92 | 97 | 50 | 47 | 47 | 52 | 117 |  | 127 | 95 | 95 | 95 | 95 | 45 | 0 | 1219418
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 8 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 180 | 190 | 190 | 190 | 190 | 190 | 160 | 190 | 190 | 131 | 130 | 130 | 130 |  | 190 | 190 | 190 | 190 | 160 | 160 | 160 | 4015031
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 509 | 503 | 502 | 476 | 430 | 407 | 440 | 542 | 540 | 540 | 540 | 540 | 540 | 540 | 556 | 589 | 580 | 582 |  | 581 | 525 | 529 | 522 | 509 | 450 | 443 | 12403635
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 35 | 35 | 35 | 15 | 15 | 15 | 15 | 598896
33 | Ashuganj 225 MW CCPP | 154 | 155 | 155 | 155 | 154 | 154 | 113 | 153 | 156 | 151 | 152 | 147 | 138 | 147 | 147 | 148 | 147 | 148 |  | 152 | 148 | 152 | 136 | 145 | 150 | 149 | 3619000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 275 | 305 | 275 | 375 | 280 | 275 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 280 |  | 270 | 280 | 270 | 300 | 300 | 280 | 280 | 6740000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 315 | 285 | 305 | 285 | 285 | 315 | 285 | 310 | 285 | 285 | 285 | 285 | 285 | 295 |  | 305 | 305 | 305 | 315 | 280 | 290 | 290 | 7494700
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 370 | 370 | 370 | 370 | 370 | 371 | 383 | 441 | 434 | 389 | 385 | 401 | 416 | 418 | 414 | 417 | 418 | 405 |  | 402 | 425 | 423 | 423 | 427 | 429 | 416 | 9792000
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 60 | 60 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 130 | 120 | 110 | 100 | 100 | 100 | 100 | 100 |  | 120 | 120 | 120 | 145 | 145 | 147 | 167 | 2629091
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 75 | 74 | 85 | 85 | 85 | 85 | 69 | 70 | 30 | 31 | 34 | 34 | 33 | 31 | 32 | 33 | 33 | 33 |  | 34 | 40 | 56 | 73 | 74 | 74 | 75 | 1316160
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 14 | 25 | 40 | 46 | 49 | 48 | 42 | 33 | 17 | 2 | 0 | [8 empty] | 314720
44 | Fenchugonj CCPP Phase-1 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 39 | 39 | 40 | 43 | 43 | 43 | 43 | 43 | 43 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 967000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 966960
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 61 | 40 | 40 | 59 | 58 | 58 | 58 | 59 | 59 | 59 | 60 |  | 61 | 60 | 61 | 60 | 61 | 40 | 61 | 1234368
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 209 | 210 | 211 | 211 | 211 | 211 | 210 | 210 | 210 | 213 | 206 | 206 | 206 | 208 | 206 | 206 | 208 |  | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 5221980
51 | Sylhet 20 MW GTPP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 | 14 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 377000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248940
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 51 | 53 | 53 | 53 | 53 | 53 | 749400
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 16 | 8 | 8 |  | 8 | 10 | 16 | 16 | 16 | 16 | 17 | 277584
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 300 | 280 | 300 | 300 | 315 | 320 | 305 | 295 | 290 | 310 | 300 | 330 | 305 | 315 | 300 | 290 | 280 |  | 290 | 305 | 285 | 310 | 290 | 295 | 300 | 7359000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 280 | 230 | 210 | 230 | 330 | 360 | 400 | 370 | 340 | 340 | 340 | 340 | 340 | 347 |  | 290 | 300 | 300 | 360 | 340 | 320 | 324 | 7833100
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 17 |  |  |  | 17 | [9 empty] | 0 | 39120
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 45360
60 | Barabkunda 22 MW PP (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 9 | 9 | 11 | 9 | 9 | 9 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 275136
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 90 | 82 | 86 | 78 | 74 | 78 | 82 | 102 | 98 | 108 | 106 | 130 | 128 | 132 | 112 | 110 | 98 | 114 |  | 104 | 104 | 102 | 100 | 98 | 96 | 88 | 2383680
64 | Malancha, Ctg. EPZ (United) | 35 | 34 | 34 | 34 | 36 | 36 | 36 | 2 | 5 | 6 | 4 | 4 | 2 | 2 | 0 | 0 | 2 | 2 |  | 14 | 14 | 17 | 21 | 27 | 30 | 30 | 403200
65 | Feni 22 MW PP (Doreen) | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 382068
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 0 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 187380
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 749700
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 13 | 10 | 10 | 10 | 10 | 11 | 10 | 10 | 14 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 276820
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 337680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 704060
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 31 | 30 |  | 30 | 30 | 30 | 31 | 30 | 31 | 33 | 766900
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 294818
| Feni Lanka Power | [7 empty] | 106 | 114 | 70 | 70 | 93 | 114 | 114 | 114 | 114 | 114 | 97 |  | 98 | 98 | 98 | 98 | 98 | 70 | 0 | 1589160
| Chowmuhani 113 MW | [8 empty] | 6 | 9 | 9 | 16 | 37 | 37 | 47 | 67 | 68 | 68 |  | 68 | 69 | 68 | 68 | 64 | 50 | 27 | 753480
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 12 | 60 | 60 | 60 | 60 | 60 | 62 | 60 | 60 | 68 | 72 |  | 68 | 68 | 68 | 48 | 10 | 9 | 0 | 792816
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 198240
79 | Kodda 150 MW PP | 16 | 0 |  |  | 0 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 98 |  | 98 | 98 | 98 | 16 | 16 | 16 | 16 | 558720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 |  | 16 | 16 | 16 | 8 | 8 | 8 |  | 163997
| Gazipur 100 MW PP | [6 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 92 |  | 105 | 105 | 105 | 105 | 105 | 105 | 0 | 805440
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 3 | 3 | 3 | 1 | 0 | [9 empty] | 27359
| Jodiac Power | [8 empty] | 1 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 0 | 100367
| Karnaphuli Power Ltd. | [5 empty] | 0 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 333709
82 | Madanganj 102 PP(Summit) | [7 empty] | 5 | 68 | 58 | 34 | 34 | 55 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 25 | 1017337
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 13 | [8 empty] | 0 | 11189
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 12 | 54 | 59 | 57 | 57 | 79 | 97 | 100 | 100 | 100 | 100 |  | 29 | 9 | 9 | 9 | 8 | 11 | 0 | 876480
| Meghnaghat 104 MW PP (OPCL) |  |  |  |  | 0 | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 22 | 17 | 17 | 17 | 0 | 3 | 17 | 290880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [7 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 32 | 32 | 34 |  | 35 | 36 | 36 | 36 | 36 | 36 | 0 | 431160
92 | Fenchuganj 44 MW (Energyprima) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 8 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 275832
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1213330
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 91 |  | 91 | 91 | 91 | 91 | 91 | 8 | 0 | 854208
95 | Patenga 50MW PP (Baraka) | 3 | 0 |  |  |  |  | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  |  | 18 | 19 | 19 | 19 | 19 | 19 | 6 | 174240
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 6 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 207751
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 39958
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13050
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 38880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 196800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 62 | 4 |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 538560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 0 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 445440
116 | Chandpur 200 MW (Desh energy) | [6 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 318720
117 | Ashuganj 150 MW PP (Midland) | 6 | 0 |  |  |  | 1 | 5 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 5 | 6 |  | 15 | 26 | 25 | 26 | 25 | 26 | 26 | 225818
118 | Bibiyana-III 400 MW CCPP | 80 | 80 | 80 | 80 | 80 | 220 | 290 | 320 | 317 | 309 | 309 | 301 | 302 | 81 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 3525000
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 |  | 0 | 53 | 56 | 56 | 56 | 56 | 59 | 59 | 59 | 59 | 59 | 59 | 69 | 69 |  | 69 | 69 | 69 | 68 | 9 | 9 | 9 | 1004400
| Anwara 300 MW PP (United) | 0 | [6 empty] | 60 | 61 | 63 | 68 | 68 | 68 | 65 | 65 | 65 | 93 | 102 |  | 104 | 70 | 69 | 69 | 16 | 16 | 0 | 1018691
| Juldah unit-2 (Acorn) | [6 empty] | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 436800
| Anlima Energy Ltd. | [6 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 326182
| Bhairob 54.5 MW | [14 empty] | 1 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 167040
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 16 | 16 | 20 | 28 | 27 | 19 | 13 | 7 | 2 | [9 empty] | 165801
| Chandpur 115(Doreen) | [12 empty] | 14 | 18 | 18 | 18 | 25 | 37 |  | 37 | 36 | 36 | 34 | 18 | 0 | 0 | 274560
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 7 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 63000
| Mirsharai 150 MW (Oil) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 145 |  | 145 | 90 | 90 | 17 | 17 | 17 | 17 | 597164
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 23 | 30 | 30 | 29 | 35 | 29 | 27 | 28 | 9 | 3 | 0 | 4 | 9 | 11 | 16 | 9 | 8 | 14 |  | 18 | 19 | 25 | 36 | 26 | 20 | 17 | 459840
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 4148 | 4073 | 4070 | 4052 | 4009 | 4139 | 4556 | 4863 | 5228 | 5277 | 5377 | 5461 | 5559 | 5283 | 5196 | 5231 | 5248 | 5663 |  | 5771 | 5747 | 5751 | 5630 | 5326 | 4996 | 4525 | 120897431
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 5 | 20 |  | 45 | 42 | 42 | 42 | 0 |  |  | 148800
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 4 | 24 | 49 | 35 | 17 | 17 | 53 | 55 | 55 | 35 | 50 | 55 |  | 55 | 55 | 55 | 55 | 0 |  | 0 | 665760
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 17 | 38 | 65 | 67 | 69 | 62 | 52 | 47 | 7 | 4 | [9 empty] | 442080
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 80 |  | 136 | 90 | 62 | 35 | 0 |  | 0 | 484800
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 |  | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 4940400
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 0 |  | 0 | 79776
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 170 | 190 | 190 | 190 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 198 |  | 290 | 270 | 250 | 250 | 150 | 150 | 150 | 4200000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 40 | 40 | 40 |  | 66 | 66 | 40 | 40 | 40 | 70 | 70 | 1479000
140 | Bhola 33 MW PP (Venture) | 8 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 132000
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 30 |  | 35 | [6 empty] | 43392
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 812 | 624 | 624 | 624 | 624 | 624 | 625 | 624 | 624 | 624 | 846 | 907 | 907 | 908 | 908 | 908 | 908 | 907 |  | 624 | 624 | 624 | 624 | 907 | 909 | 908 | 18605090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 980 | 980 | 900 | 800 | 800 | 840 | 940 | 1100 | 1040 | 1020 | 1000 | 960 | 1030 | 940 | 880 | 800 | 760 | 800 |  | 1130 | 1180 | 1130 | 1100 | 1080 | 1000 | 970 | 25262300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4142000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 17 |  | 26 | 26 | 26 | 26 | 26 | 0 |  | 117215
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 3 | 3 | 1 | 1 | 0 | [9 empty] | 27480
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 151 | 199 | 206 | 198 | 191 | 190 | 182 | 175 | 167 | 162 | 150 | 140 |  | 161 | 164 | 164 | 150 | 161 | 140 | 150 | 4169127
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 320 | 320 | 320 | 320 | 320 | 360 | 414 | 414 | 350 | 350 | 350 | 414 | 414 | 414 | 414 | 330 | 330 | 300 |  | 381 | 376 | 385 | 376 | 330 | 300 | 414 | 8691490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 4 |  | 5 | 10 | 20 | 20 | 4 | 0 |  | 45636
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 110736
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 7 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 14 | 14 | 28 |  | 28 | [5 empty] | 0 | 273230
166 | Katakhali 50 MW PP (Northern) | [7 empty] | 25 | 25 | 8 | 8 | 16 | 34 | 34 | 34 | 8 | 8 | 34 |  | 34 | [6 empty] | 226248
167 | Katakhali 50 MW Peaking PP | [13 empty] | 28 | 32 | 32 | 32 | 35 |  | 41 | 41 | 42 | 38 | 38 | 0 |  | 285292
168 | Santahar 50 MW Peaking PP | [15 empty] | 16 | 16 | 22 |  | 30 | 30 | 32 | 32 | 32 | 0 |  | 156530
169 | Natore 52 MW PP (Rajlanka) | [8 empty] | 8 | 8 | 8 |  |  |  | 8 | 8 | [7 empty] | 8 | 8 | 0 | 61800
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 16 | 49 | 49 | 49 | 49 | 49 | 49 | 55 | 82 |  | 82 | 82 | 82 | 82 | 82 | 43 | 0 | 843088
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 5 | 35 | 35 | 35 | 35 | 35 | 35 | [11 empty] | 0 | 244704
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [8 empty] | 0 | 266304
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 23 | 33 | 35 |  | 34 | 34 | 35 | 34 | 6 | 6 | 0 | 273312
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 5 | 5 | 6 | 5 | 4 | 3 | 2 | 2 | [9 empty] | 39214
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 5 | 35 | 50 |  | 72 | 72 | 72 | 72 | 0 |  | 0 | 350208
| Intraco Solar 30 MW | [6 empty] | 1 | 7 | 19 | 27 | 32 | 32 | 37 | 14 | 14 | 13 | 4 | 0 | [8 empty] | 200285
| Adani Power Jharkhanda Ltd | 1118 | 1048 | 873 | 818 | 818 | 941 | 1107 | 1257 | 1260 | 1255 | 1256 | 1253 | 1258 | 1261 | 1249 | 1211 | 1157 | 1244 |  | 1372 | 1367 | 1365 | 1364 | 1339 | 1275 | 1244 | 28324364
178 | Teesta Solar Limited | [6 empty] | 5 | 51 | 100 | 132 | 148 | 176 | 167 | 157 | 59 | 82 | 16 | [9 empty] | 1064160