## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-02-19 | Monday
|  | Date (day): | 2024-02-19 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10718.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11750 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-18 | 2024-02-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 190 | 130 | 190 | 190
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 0 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 347 | 0 | 0 | 0 |  | 412 | Under maint.
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  |  | Line S/D
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 34 | 31 | 50 | 75 | 25 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 78 | 80 | 80 | 80 |  | 22 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 34 | 36 | 14 | 36 | 39 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 80 | 105 | 105 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 26 | 34 | 60 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 42 | 82 | 80 | 82 |  | 20 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 0 | 0 | 0 | 54 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 149 | 64 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 40 | 41 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 30 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 15 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 190 | 97 | 195 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 62 | 17 | 100 | 17 | 132 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 17 | 35 | 127 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 390 | 390 | 390 | 390 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 2013 | 1707 | 1862 | 2007 | 1555 | 1443
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 211 | 210 | 210
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 49 | 19 | 50 | 48 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 48 | 68 | 51 | 68 | 34 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 8 | 8 | 8 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 13 | 5 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 240 | 15 | 120 | 180 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 17 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 145 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 301 | 355 | 300 | 355 | 869 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 3 | 9 | 20 | 29 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 157 | 156 | 150 | 150 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1035 | 1456 | 1017 | 1357 | 2225 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 144 | 149 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 205 | 300 | 320 | 40 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 320 | 330 | 350 | 360 | 40 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 41 | 45 | 47 | 45
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 27 | 40 | 40 | 40 | 15 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 23 | 13 | 25 | 125 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 40 | 40 | 40 |  | 12 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 32 | 17 | 18 | 18 | 182 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 16 | 16 |  | 6 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 108 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 11 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 88 | 88 | 98 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 66 | 38 | 68 | 45 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 42 | 0 | 42 | 73 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1220 | 1282 | 1222 | 1363 | 759 | 809
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 27 | 55 | 35 | 65 | 137 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9 | 9 | 191 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 57 | 69 | 46 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 2 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 138 | 135 | 152.6 | 149 | 137 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 35 | 35 | 34 | 35 |  | 35 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 120 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 28 | 28 | 28 |  | 33 | GT-9 Under maint.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 210 | 209 | 210 | 210 |  | 21 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 10 | 15 | 15 | 5 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 17 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 300 | 315 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 253 | 295 | 400 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 300 | 322 | 320 | 370 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1288 | 1410 | 1542 | 1608 | 109 | 569
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 472 | 619 | 483 | 483
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 53 | 0 | 53 | 1
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 43 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 38 | 17 | 50 | 55 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 330 | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 571 | 753 | 600 | 656 | 1308 | 369
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 3 | 6 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 50 | 60 | 60 | 60 |  | 134 | ST, GT-1 Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1200 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 190 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 17 | 150 | 150
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 282 | 307 | 250 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1804 | 1826 | 1887 | 2004 | 94 | 167
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 24 | 24 | 28 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 50 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 209 | 179 | 160 | 180 | 40
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 400 | 414 | 410 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 16 | 32 | 0 | 35 | 15 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 90 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 35 | 0 | 113 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 55 | 0 | 36 | 77 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1318 | 1412 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 2099 | 2336 | 2092 | 2319 | 1118 | 92
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 42 | 6 | 42 | 71 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 0 | 75 | 40 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 177 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 393 | 287 | 344 | 287 | 236 | 189
| Total |  |  |  |  | 26504 | 25481 | 10561 | 11192 | 10718.6 | 11750 | 7541 | 3968
A. |  | 2024-02-18 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11192 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7628 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11350 | MW
3 | Day peak Generation : |  |  | 10561 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10861.74 | MW
4 | Evening peak Generation : |  |  | 11192 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 151 | MW
5 | Total Energy Generation : |  | 232.2828 | MKWHr | By Solar | 2.5171 | MKWHr
| By Gas : | 112.2312 | MKWHr |  | By Oil: | 24.3385 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 77.3179 | MKWHr |  | By Hydro: | 0.94902 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.12288 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7541 | MW | Dhaka | 4116.04 | 4088.04 |  | 28 |  | 18:00 |  | 85.95
|  |  | For Plants S/D or M/C prob = |  |  | 3968 | MW | Chittagong | 1058 | 1058 |  | 0 |  | 19:00 |  | 150.89
|  |  | Total = |  |  | 11509 | MW | Khulna | 1224.7 | 1224.7 |  | 0 |  | 19:30 |  | 91.68
7 | Total Gas Supplied : |  |  | 817.99 | MMCFD |  |  | Rajshahi | 1126 | 1126 |  | 0 |  | 20:00 |  | 68.76
8 | Fuel Cost : | i) Gas : | Taka | 312766122.19 | ii) Oil : | Taka | 444098182.54 | Comilla | 879 | 879 |  | 0 |  | 21:00 |  | 50
|  | iii) Coal : | Taka | 518082854.98 | Total | Taka | 1274947159.71 | Mymensingh | 1012 | 889 |  | 123 |  | 22:00 |  | 61.12
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 365 | 365 |  | 0 |  | 23:00 |  | 57.3
| ii) During Peak Demand : |  |  | 1220 | MW (W to E) at | 19:00 | hrs | Barisal | 288 | 288 |  | 0 |  | 24:00 |  | 42.02
| iii) Maximum : |  |  | 776 | MW at | 7:00 | hrs | Rangpur | 793 | 793 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.2°C |  |  | Total | 10861.74 | 10710.74 |  | 151
B. |  | 2024-02-19 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 30.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11750 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | 250 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 238.6752 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7644 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 12.5425 | MKWHr. | ii) HVDC Flow at Peak Time |  | 619 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2637 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 22:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.21 |  | (b) Today: | 85.11 |  | (c) Rule Curve: |  | 94.48
.

## YesterdayGen
2024-02-18 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 359 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 64 | 0 | 0 | 0 | 6 | 8 | 40 | 0 | 0 | 0 | 0 | 220 | 127 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 33 | 10 | 86 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 0 | 0 | 0 | 210 | 18 | 0 | 9 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 8 | 367 | 9 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 0 | 159 | 0 | 400 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1137 | 0 | 0 |  | 4799 | 3702 | 8501 | 3129 | 473 | 1582 | 0 | 175 | 2936 | 40 | 0 | 80 | 86 | 0 | 0 | 42.02 | 85.24
2:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 357 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 220 | 123 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 33 | 10 | 78 | 75 | 0 | 0 | 0 | 34 | 40 | 0 | 5 | 163 | 0 | 0 | 0 | 0 | 210 | 18 | 0 | 9 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 0 | 6 | 365 | 9 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 310 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 320 | 2 | 157 | 0 | 400 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1090 | 0 | 0 |  | 4535 | 3584 | 8119 | 3060 | 473 | 1516 | 0 | 67 | 2867 | 40 | 0 | 16 | 78 | 0 | 2 | 29.605 | 85.23
3:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 357 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 220 | 123 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 33 | 10 | 78 | 75 | 0 | 0 | 0 | 34 | 40 | 0 | 5 | 163 | 0 | 0 | 0 | 0 | 210 | 18 | 0 | 9 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 0 | 0 | 362 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 0 | 158 | 0 | 400 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1006 | 0 | 0 |  | 4496 | 3420 | 7916 | 3047 | 473 | 1526 | 0 | 52 | 2684 | 40 | 0 | 16 | 78 | 0 | 0 | 22.92 | 85.23
4:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 357 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 220 | 123 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 33 | 10 | 74 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 0 | 0 | 0 | 210 | 18 | 0 | 9 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 0 | 0 | 364 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 4 | 157 | 0 | 400 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 912 | 0 | 0 |  | 4472 | 3226 | 7698 | 3041 | 473 | 1526 | 0 | 35 | 2489 | 40 | 0 | 16 | 74 | 0 | 4 | 21.01 | 85.22
5:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 335 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 220 | 123 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 33 | 10 | 76 | 75 | 0 | 0 | 0 | 34 | 40 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 211 | 18 | 0 | 9 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 0 | 0 | 364 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 5 | 158 | 0 | 400 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 920 | 0 | 0 |  | 4405 | 3223 | 7628 | 3018 | 473 | 1477 | 0 | 35 | 2488 | 40 | 0 | 16 | 76 | 0 | 5 | 30.56 | 85.22
6:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 345 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 38 | 0 | 0 | 0 | 0 | 220 | 135 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 33 | 10 | 82 | 75 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 211 | 18 | 0 | 9 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 335 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 5 | 159 | 0 | 400 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 918 | 0 | 0 |  | 4452 | 3301 | 7753 | 3081 | 473 | 1520 | 0 | 19 | 2517 | 40 | 0 | 16 | 82 | 0 | 5 | 45 | 85.21
7:00 | 0 | 0 | 160 | 0 | 0 | 12 | 0 | 415 | 0 |  | 0 | 0 | 0 | 1 | 2 | 0 | 335 | 0 | 0 | 2 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 3 | 0 | 40 | 0 | 0 | 0 | 1 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 8 | 37 | 0 | 0 | 0 | 0 | 250 | 136 | 0 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 3 | 0 | 10 | 33 | 10 | 80 | 74 | 0 | 0 | 0 | 34 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 185 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 6 | 1 | 15 | 18 | 5 | 390 | 56 | 17 | 1 | 0 | 15 | 0 | 11 | 59 | 0 | 24 | 292 | 0 | 2 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 360 | 17 | 0 | 300 | 3 | 157 | 0 | 390 |  | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 414 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 920 | 190 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 150 | 1060 | 6 | 0 |  | 4887 | 3590 | 8477 | 3348 | 405 | 1459 | 0 | 338 | 2757 | 40 | 0 | 33 | 80 | 14 | 3 | 79 | 85.21
8:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 419 | 0 |  | 0 | 0 | 0 | 8 | 44 | 0 | 335 | 0 | 0 | 17 | 33 | 48 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 8 | 8 | 0 | 0 | 0 | 0 | 280 | 134 | 0 | 0 | 47 | 36 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 33 | 10 | 92 | 71 | 0 | 0 | 1 | 34 | 40 | 0 | 5 | 163 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 9 | 320 | 0 | 0 | 0 | 15 | 0 | 0 | 9 | 0 | 17 | 7 | 25 | 17 | 6 | 374 | 56 | 17 | 17 | 1 | 16 | 0 | 17 | 98 | 5 | 24 | 355 | 17 | 12 | 0 | 17 | 0 | 0 | 7 | 0 | 0 | 350 | 17 | 0 | 304 | 1 | 159 | 0 | 390 |  | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 414 | 17 | 0 | 4 | 0 | 6 | 0 | 0 | 0 | 1130 | 190 | 0 | 12 | 1 | 21 | 0 | 0 | 0 | 0 | 7 | 250 | 1234 | 40 | 0 |  | 5427 | 3989 | 9416 | 3443 | 191 | 1602 | 0 | 638 | 3247 | 40 | 0 | 65 | 92 | 97 | 1 | 175.72 | 85.2
9:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 420 | 0 |  | 0 | 0 | 0 | 9 | 65 | 0 | 335 | 0 | 0 | 17 | 33 | 64 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 22 | 8 | 0 | 40 | 0 | 0 | 0 | 4 | 212 | 0 | 0 | 0 |  | 0 | 33 | 51 | 25 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 0 | 270 | 117 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 33 | 10 | 94 | 35 | 0 | 0 | 1 | 34 | 40 | 0 | 5 | 163 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 9 | 310 | 0 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 17 | 13 | 25 | 17 | 6 | 362 | 59 | 17 | 17 | 3 | 16 | 4 | 17 | 98 | 9 | 25 | 340 | 17 | 24 | 0 | 17 | 0 | 0 | 14 | 0 | 0 | 320 | 17 | 0 | 302 | 3 | 156 | 0 | 390 |  | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 2 | 0 | 1202 | 190 | 0 | 17 | 2 | 44 | 0 | 0 | 0 | 0 | 15 | 289 | 1273 | 87 | 0 |  | 5467 | 4307 | 9774 | 3365 | 192 | 1573 | 0 | 745 | 3392 | 40 | 0 | 165 | 94 | 205 | 3 | 359.08 | 85.2
10:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 386 | 0 |  | 0 | 0 | 0 | 11 | 65 | 0 | 270 | 0 | 0 | 21 | 33 | 64 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 22 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 32 | 51 | 25 | 0 | 6 | 8 | 3 | 0 | 0 | 0 | 0 | 270 | 116 | 0 | 0 | 42 | 20 | 0 | 43 | 0 | 0 | 8 | 0 | 10 | 33 | 10 | 100 | 34 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 9 | 270 | 16 | 0 | 0 | 160 | 0 | 0 | 9 | 0 | 20 | 17 | 25 | 17 | 6 | 253 | 59 | 17 | 17 | 4 | 16 | 17 | 17 | 98 | 9 | 25 | 300 | 17 | 33 | 0 | 17 | 0 | 0 | 22 | 0 | 0 | 320 | 17 | 0 | 301 | 0 | 158 | 0 | 390 |  | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 28 | 34 | 0 | 8 | 16 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 320 | 17 | 0 | 35 | 0 | 6 | 0 | 3 | 0 | 1210 | 190 | 0 | 35 | 3 | 65 | 0 | 0 | 0 | 0 | 24 | 307 | 1314 | 127 | 0 |  | 5323 | 4415 | 9738 | 3132 | 191 | 1386 | 0 | 919 | 3460 | 40 | 0 | 210 | 100 | 300 | 0 | 250.21 | 85.19
11:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 341 | 0 |  | 0 | 0 | 0 | 30 | 65 | 5 | 270 | 0 | 0 | 26 | 33 | 64 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 39 | 51 | 25 | 0 | 6 | 8 | 3 | 0 | 0 | 0 | 0 | 300 | 130 | 0 | 0 | 44 | 20 | 0 | 43 | 0 | 21 | 8 | 0 | 9 | 33 | 11 | 100 | 28 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 9 | 285 | 16 | 0 | 0 | 200 | 0 | 0 | 9 | 0 | 65 | 19 | 25 | 17 | 5 | 253 | 59 | 17 | 17 | 4 | 16 | 17 | 17 | 98 | 22 | 25 | 300 | 17 | 40 | 0 | 17 | 0 | 0 | 27 | 0 | 0 | 320 | 17 | 0 | 300 | 2 | 158 | 0 | 390 |  | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 32 | 8 | 16 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 320 | 17 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 1210 | 190 | 0 | 17 | 4 | 77 | 0 | 0 | 0 | 0 | 25 | 307 | 1315 | 156 | 0 |  | 5494 | 4632 | 10126 | 3115 | 332 | 1401 | 0 | 1027 | 3460 | 40 | 0 | 290 | 100 | 359 | 2 | 261.67 | 85.19
12:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 347 | 0 |  | 0 | 0 | 0 | 34 | 78 | 15 | 335 | 0 | 0 | 26 | 42 | 64 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 32 | 48 | 25 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 300 | 144 | 0 | 0 | 41 | 27 | 0 | 51 | 0 | 23 | 0 | 0 | 9 | 33 | 11 | 108 | 27 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 9 | 300 | 16 | 0 | 0 | 190 | 0 | 0 | 9 | 0 | 62 | 20 | 25 | 32 | 6 | 253 | 59 | 17 | 17 | 4 | 16 | 17 | 17 | 88 | 27 | 25 | 300 | 17 | 41 | 17 | 17 | 0 | 0 | 29 | 0 | 0 | 320 | 35 | 0 | 301 | 3 | 157 | 0 | 390 |  | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 0 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 400 | 17 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1244 | 190 | 0 | 35 | 4 | 82 | 0 | 0 | 0 | 0 | 34 | 282 | 1318 | 177 | 0 |  | 5694 | 4867 | 10561 | 3184 | 472 | 1509 | 0 | 1106 | 3472 | 40 | 0 | 268 | 108 | 399 | 3 | 233.02 | 85.18
13:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 412 | 0 |  | 0 | 0 | 0 | 33 | 82 | 15 | 335 | 0 | 0 | 26 | 42 | 64 | 36 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 22 | 33 | 8 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 40 | 48 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 270 | 147 | 0 | 0 | 44 | 30 | 0 | 51 | 0 | 28 | 3 | 0 | 9 | 33 | 11 | 108 | 27 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 9 | 315 | 17 | 0 | 0 | 180 | 0 | 0 | 9 | 0 | 63 | 19 | 25 | 28 | 6 | 253 | 59 | 17 | 32 | 4 | 16 | 17 | 17 | 88 | 29 | 25 | 300 | 17 | 27 | 17 | 17 | 0 | 0 | 28 | 12 | 5 | 320 | 35 | 0 | 296 | 6 | 157 | 0 | 390 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 31 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 1244 | 190 | 0 | 17 | 0 | 74 | 0 | 0 | 0 | 0 | 30 | 250 | 1257 | 169 | 0 |  | 5764 | 4767 | 10531 | 3202 | 473 | 1541 | 0 | 1117 | 3374 | 40 | 0 | 312 | 108 | 358 | 6 | 280.77 | 85.18
14:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 415 | 0 |  | 0 | 0 | 0 | 34 | 80 | 15 | 280 | 0 | 0 | 26 | 42 | 64 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 40 | 47 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 260 | 147 | 0 | 0 | 44 | 30 | 0 | 51 | 0 | 39 | 8 | 0 | 0 | 33 | 11 | 112 | 27 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 206 | 0 | 0 | 8 | 290 | 17 | 0 | 0 | 82 | 0 | 0 | 9 | 0 | 19 | 0 | 25 | 19 | 6 | 253 | 59 | 17 | 17 | 4 | 16 | 17 | 17 | 88 | 30 | 25 | 300 | 17 | 32 | 35 | 17 | 0 | 0 | 24 | 17 | 17 | 280 | 17 | 0 | 297 | 20 | 158 | 0 | 390 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 28 | 34 | 32 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 320 | 17 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 1244 | 190 | 0 | 17 | 4 | 50 | 0 | 0 | 0 | 0 | 29 | 200 | 1252 | 155 | 0 |  | 5515 | 4579 | 10094 | 3116 | 473 | 1421 | 0 | 974 | 3321 | 40 | 0 | 312 | 112 | 305 | 20 | 292.23 | 85.19
15:00 | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 413 | 0 |  | 0 | 0 | 0 | 34 | 80 | 15 | 280 | 0 | 0 | 26 | 42 | 64 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 0 | 44 | 47 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 260 | 144 | 0 | 0 | 44 | 30 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 112 | 27 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 206 | 0 | 0 | 8 | 300 | 17 | 0 | 0 | 47 | 0 | 0 | 9 | 0 | 17 | 13 | 25 | 35 | 6 | 253 | 59 | 17 | 17 | 2 | 16 | 17 | 17 | 88 | 28 | 25 | 300 | 17 | 26 | 17 | 17 | 0 | 6 | 12 | 18 | 17 | 280 | 17 | 0 | 300 | 20 | 158 | 0 | 390 |  | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 28 | 25 | 32 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 320 | 17 | 0 | 0 | 0 | 6 | 0 | 4 | 0 | 1244 | 190 | 0 | 17 | 3 | 51 | 0 | 0 | 0 | 0 | 23 | 200 | 1272 | 121 | 0 |  | 5498 | 4500 | 9998 | 3118 | 473 | 1430 | 0 | 896 | 3344 | 40 | 0 | 308 | 112 | 257 | 20 | 145.16 | 85.17
16:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 409 | 0 |  | 0 | 0 | 0 | 23 | 54 | 15 | 335 | 0 | 0 | 17 | 42 | 64 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 48 | 47 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 260 | 144 | 0 | 0 | 45 | 36 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 106 | 33 | 0 | 0 | 1 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 206 | 0 | 0 | 8 | 290 | 17 | 0 | 0 | 47 | 0 | 0 | 9 | 0 | 17 | 9 | 25 | 22 | 5 | 253 | 58 | 17 | 17 | 1 | 171 | 0 | 17 | 88 | 38 | 25 | 340 | 17 | 15 | 17 | 17 | 0 | 17 | 8 | 18 | 17 | 280 | 17 | 0 | 325 | 14 | 158 | 0 | 380 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 14 | 8 | 32 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 320 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 1120 | 190 | 0 | 0 | 1 | 29 | 17 | 0 | 0 | 0 | 14 | 150 | 1155 | 72 | 0 |  | 5606 | 4202 | 9808 | 3123 | 618 | 1416 | 0 | 938 | 3078 | 40 | 0 | 323 | 106 | 152 | 14 | 63.985 | 85.16
17:00 | 0 | 0 | 130 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 17 | 15 | 335 | 0 | 0 | 9 | 42 | 82 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 1 | 48 | 51 | 25 | 0 | 12 | 8 | 5 | 0 | 0 | 0 | 0 | 260 | 147 | 0 | 0 | 45 | 38 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 100 | 33 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 207 | 0 | 0 | 8 | 300 | 17 | 0 | 0 | 77 | 0 | 0 | 18 | 0 | 17 | 3 | 25 | 17 | 6 | 252 | 59 | 17 | 17 | 0 | 268 | 0 | 17 | 88 | 38 | 25 | 300 | 17 | 5 | 17 | 17 | 0 | 11 | 3 | 24 | 0 | 280 | 17 | 0 | 315 | 6 | 157 | 0 | 390 |  | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 40 | 4 | 16 | 0 | 0 | 0 | 24 | 0 | 48 | 14 | 25 | 8 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 320 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 2 | 1120 | 190 | 0 | 0 | 0 | 10 | 36 | 0 | 0 | 0 | 6 | 150 | 1159 | 29 | 0 |  | 5223 | 4269 | 9492 | 2676 | 667 | 1443 | 0 | 1079 | 3071 | 40 | 0 | 353 | 100 | 57 | 6 | 103.14 | 85.16
18:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 26 | 32 | 15 | 300 | 0 | 0 | 27 | 42 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 48 | 66 | 25 | 0 | 14 | 8 | 9 | 0 | 0 | 0 | 0 | 260 | 147 | 0 | 0 | 45 | 40 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 112 | 33 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 209 | 0 | 0 | 9 | 290 | 17 | 0 | 0 | 97 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 11 | 252 | 69 | 105 | 17 | 0 | 279 | 0 | 17 | 88 | 53 | 25 | 305 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 0 | 340 | 145 | 0 | 360 | 6 | 157 | 0 | 390 |  | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 5 | 0 | 40 | 5 | 16 | 0 | 0 | 0 | 24 | 0 | 88 | 28 | 34 | 40 | 0 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 414 | 25 | 0 | 0 | 0 | 40 | 0 | 0 | 55 | 1100 | 220 | 0 | 12 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 161 | 1225 | 0 | 0 |  | 5760 | 4750 | 10510 | 2715 | 726 | 1553 | 0 | 1503 | 3173 | 40 | 0 | 682 | 112 | 0 | 6 | 85.95 | 85.16
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 31 | 80 | 30 | 335 | 0 | 0 | 34 | 82 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 2 | 49 | 68 | 25 | 0 | 19 | 8 | 13 | 0 | 0 | 0 | 0 | 205 | 149 | 0 | 0 | 45 | 40 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 108 | 55 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 209 | 10 | 0 | 9 | 315 | 17 | 5 | 0 | 97 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 23 | 295 | 69 | 105 | 17 | 0 | 240 | 0 | 17 | 88 | 66 | 25 | 322 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 42 | 0 | 330 | 145 | 0 | 355 | 9 | 156 | 0 | 390 |  | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 43 | 0 | 60 | 6 | 16 | 0 | 0 | 0 | 24 | 5 | 90 | 28 | 34 | 50 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 38 | 0 | 0 | 0 | 42 | 0 | 0 | 55 | 1200 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 307 | 1412 | 0 | 0 |  | 5990 | 5202 | 11192 | 2814 | 619 | 1583 | 0 | 1671 | 3600 | 40 | 0 | 748 | 108 | 0 | 9 | 150.89 | 85.14
19:30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 34 | 80 | 30 | 280 | 0 | 0 | 34 | 82 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 3 | 56 | 68 | 25 | 0 | 19 | 8 | 14 | 0 | 0 | 0 | 0 | 210 | 151 | 0 | 0 | 45 | 40 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 100 | 55 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 209 | 20 | 0 | 9 | 285 | 17 | 5 | 0 | 97 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 26 | 322 | 69 | 105 | 17 | 0 | 226 | 0 | 17 | 88 | 66 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 0 | 280 | 145 | 0 | 360 | 9 | 158 | 0 | 390 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 59 | 0 | 60 | 6 | 16 | 0 | 0 | 0 | 24 | 13 | 90 | 28 | 34 | 50 | 8 | 34 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 360 | 36 | 0 | 0 | 0 | 42 | 0 | 0 | 55 | 1200 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 280 | 1413 | 0 | 0 |  | 5899 | 5145 | 11044 | 2772 | 624 | 1500 | 0 | 1644 | 3581 | 40 | 0 | 774 | 100 | 0 | 9 | 91.68 | 0
20:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 34 | 80 | 30 | 280 | 0 | 62 | 34 | 82 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 5 | 64 | 68 | 25 | 0 | 19 | 8 | 15 | 0 | 0 | 0 | 0 | 240 | 150 | 0 | 0 | 46 | 37 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 102 | 73 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 212 | 16 | 0 | 9 | 275 | 17 | 5 | 0 | 97 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 26 | 326 | 69 | 105 | 17 | 0 | 226 | 0 | 17 | 88 | 69 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 41 | 0 | 230 | 145 | 0 | 355 | 12 | 156 | 0 | 390 |  | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 52 | 0 | 60 | 6 | 16 | 0 | 0 | 0 | 24 | 22 | 90 | 28 | 34 | 50 | 8 | 34 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 360 | 42 | 0 | 0 | 0 | 42 | 0 | 0 | 55 | 1160 | 190 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 250 | 1368 | 0 | 0 |  | 5947 | 5006 | 10953 | 2836 | 624 | 1478 | 0 | 1620 | 3459 | 40 | 0 | 782 | 102 | 0 | 12 | 68.76 | 85.15
21:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 14 | 80 | 15 | 335 | 0 | 63 | 0 | 8 | 149 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 64 | 68 | 25 | 0 | 19 | 8 | 35 | 0 | 0 | 0 | 0 | 300 | 150 | 0 | 0 | 46 | 20 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 108 | 73 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 15 | 0 | 9 | 300 | 17 | 5 | 0 | 97 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 26 | 364 | 69 | 105 | 17 | 0 | 16 | 0 | 17 | 88 | 69 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 270 | 17 | 0 | 340 | 6 | 157 | 0 | 390 |  | 623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 55 | 0 | 60 | 7 | 16 | 0 | 0 | 0 | 24 | 20 | 90 | 28 | 34 | 50 | 8 | 34 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 55 | 0 | 0 | 0 | 35 | 0 | 0 | 55 | 1160 | 190 | 0 | 17 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 248 | 1370 | 0 | 0 |  | 5687 | 5054 | 10741 | 3057 | 623 | 1584 | 0 | 1235 | 3445 | 40 | 0 | 643 | 108 | 0 | 6 | 50 | 85.14
22:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 80 | 15 | 335 | 0 | 63 | 0 | 8 | 48 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 64 | 68 | 25 | 0 | 19 | 8 | 37 | 0 | 0 | 0 | 0 | 290 | 148 | 0 | 0 | 46 | 20 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 96 | 74 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 15 | 0 | 9 | 285 | 8 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 26 | 410 | 9 | 105 | 17 | 0 | 0 | 0 | 17 | 105 | 68 | 25 | 380 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 19 | 0 | 330 | 17 | 0 | 340 | 1 | 157 | 0 | 300 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1325 | 0 | 0 |  | 5416 | 4520 | 9936 | 3183 | 907 | 1481 | 0 | 749 | 3242 | 40 | 0 | 237 | 96 | 0 | 1 | 61.12 | 85.14
23:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 65 | 15 | 335 | 0 | 41 | 0 | 8 | 48 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 17 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 64 | 68 | 0 | 0 | 19 | 8 | 39 | 0 | 0 | 0 | 0 | 280 | 149 | 0 | 0 | 47 | 20 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 100 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 15 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 26 | 346 | 9 | 70 | 17 | 0 | 0 | 0 | 17 | 60 | 68 | 25 | 335 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 300 | 17 | 0 | 340 | 0 | 158 | 0 | 300 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1302 | 0 | 0 |  | 5126 | 4434 | 9560 | 3028 | 907 | 1488 | 0 | 580 | 3180 | 40 | 0 | 237 | 100 | 0 | 0 | 57.3 | 85.14
24:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 65 | 0 | 335 | 0 | 39 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 28 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 64 | 68 | 0 | 0 | 6 | 8 | 33 | 0 | 0 | 0 | 0 | 260 | 154 | 0 | 0 | 47 | 20 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 88 | 72 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 209 | 15 | 0 | 9 | 295 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 18 | 0 | 25 | 17 | 26 | 364 | 9 | 17 | 17 | 0 | 0 | 0 | 17 | 52 | 47 | 25 | 330 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 300 | 17 | 0 | 340 | 0 | 158 | 0 | 40 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1274 | 0 | 0 |  | 4679 | 4407 | 9086 | 3011 | 907 | 1257 | 0 | 414 | 3132 | 40 | 0 | 237 | 88 | 0 | 0 | 42.02 | 85.14
KWH | 0 | 0 | 3971000 | 0 | 0 | 184000 | 0 | 6490800 | 0 |  | 0 | 0 | 0 | 336000 | 1043056 | 230326 | 7501767 | 0 | 281000 | 300480 | 592560 | 1538880 | 495104 | 0 | 0 | 0 | 38880 | 39929 | 39536 | 0 | 456000 | 524160 | 730100 | 452400 | 196320 | 0 | 949020 | 0 | 0 | 0 | 136346 | 5008992 | 0 | 0 | 0 |  | 40080 | 809856 | 889060 | 353880 | 0 | 200160 | 182112 | 485760 | 0 | 0 | 0 | 0 | 6278000 | 3400000 | 0 | 0 | 1103040 | 862560 | 0 | 1230959 | 0 | 459856 | 146842 | 0 | 212400 | 817700 | 266110 | 2263680 | 1258560 | 0 | 0 | 13300 | 825000 | 968400 | 0 | 143568 | 3616854 | 0 | 668352 | 0 | 0 | 5251530 | 186000 | 0 | 192420 | 7137000 | 361488 | 34512 | 0 | 1520509 | 0 | 0 | 204000 | 0 | 559296 | 136215 | 473280 | 393120 | 252581 | 7661000 | 991200 | 786240 | 332872 | 27723 | 1324800 | 128996 | 352108 | 1544700 | 688800 | 469440 | 7676800 | 286080 | 266910 | 194400 | 337473 | 0 | 167760 | 178741 | 274560 | 61200 | 7021000 | 685818 | 0 | 7614544 | 122880 | 3832727 | 0 | 9090455 |  | 12542545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186720 | 141312 | 0 | 1227000 | 132242 | 98208 | 0 | 0 | 0 | 125474 | 48808 | 797480 | 347560 | 409405 | 303807 | 50813 | 245500 | 0 | 0 | 134010 | 0 | 0 | 4120600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4642455 | 0 | 8805236 | 355680 | 0 | 262464 | 0 | 249484 | 0 | 35982 | 218880 | 27959100 | 4758491 | 0 | 248400 | 26640 | 516960 | 332160 | 0 | 0 | 0 | 203356 | 4843600 | 28947300 | 1111250 | 0 |  | 127853923 | 104428922 | 232282845 | 75591688 | 12542545 | 36639545 | 0 | 18105968 | 77317871 | 949020 | 0 | 6232571 | 2263680 | 2517077 | 122880 | 0
Fuel Cost | 0 | 0 | 17035590 | 0 | 0 | 702880 | 0 | 18693504 | 0 |  | 0 | 0 | 0 | 6501600 | 21758148.16 | 3959303.94 | 22880389.35 | 0 | 1503350 | 5790249.6 | 11021616 | 28346169.6 | 8986137.6 | 0 | 0 | 0 | 709948.8 | 638464.71 | 723113.44 | 0 | 342000 | 0 | 0 | 0 | 3516091.2 | 0 | 0 | 0 | 0 | 0 | 2582393.24 | 15978684.48 | 0 | 0 | 0 |  | 703804.8 | 14261564.16 | 15923064.6 | 6557396.4 | 0 | 3294633.6 | 677456.64 | 0 | 0 | 0 | 0 | 0 | 19210680 | 11288000 | 0 | 0 | 3717244.8 | 3778012.8 | 0 | 4936145.59 | 0 | 8236020.96 | 2643156 | 0 | 159300 | 3041844 | 199582.5 | 14849740.8 | 3914121.6 | 0 | 0 | 0 | 3217500 | 3612132 | 0 | 653234.4 | 12369640.68 | 0 | 3709353.6 | 0 | 0 | 14651768.7 | 1223880 | 0 | 769680 | 22053330 | 271116 | 26229.12 | 0 | 31398510.85 | 0 | 0 | 3896400 | 0 | 9977840.64 | 0 | 8173545.6 | 6918912 | 4253464.04 | 20301650 | 14679672 | 14152320 | 5775329.2 | 0 | 24561792 | 2518001.92 | 5612601.52 | 28329798 | 12763464 | 8360726.4 | 20420288 | 4783257.6 | 0 | 3555576 | 5737041 | 0 | 2934122.4 | 0 | 4543968 | 1047744 | 20852370 | 12269284.02 | 0 | 53073371.68 | 0 | 22613089.3 | 0 | 0 |  | 36875082.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3512203.2 | 2658078.72 | 0 | 3877320 | 626827.08 | 1693105.92 | 0 | 0 | 0 | 2247239.34 | 895626.8 | 13405638.8 | 7396076.8 | 7803259.3 | 5441183.37 | 898881.97 | 4396905 | 0 | 0 | 101445.57 | 0 | 0 | 34777864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15459375.15 | 0 | 25711289.12 | 6444921.6 | 0 | 5233532.16 | 0 | 5012133.56 | 0 | 0 | 4233139.2 | 168034191 | 14798907.01 | 0 | 4806540 | 0 | 0 | 5623468.8 | 0 | 0 | 0 | 0 | 36084820 | 203499519 | 0 | 0 |  | 705123408.04 | 621548574.77 | 1326671982.81 | 226366175.51 | 36875082.3 | 86399946.68 | 0 | 332505203.97 | 518082854.98 | 0 | 0 | 111592978.57 | 14849740.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 347 | 0 |  | 0 | 0 | 0 | 34 | 78 | 15 | 335 | 0 | 0 | 26 | 42 | 64 | 34 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 22 | 33 | 16 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 32 | 48 | 25 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 300 | 144 | 0 | 0 | 41 | 27 | 0 | 51 | 0 | 23 | 0 | 0 | 9 | 33 | 11 | 108 | 27 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 120 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 9 | 300 | 16 | 0 | 0 | 190 | 0 | 0 | 9 | 0 | 62 | 20 | 25 | 32 | 6 | 253 | 59 | 17 | 17 | 4 | 16 | 17 | 17 | 88 | 27 | 25 | 300 | 17 | 41 | 17 | 17 | 0 | 0 | 29 | 0 | 0 | 320 | 35 | 0 | 301 | 3 | 157 | 0 | 390 |  | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 28 | 34 | 0 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 400 | 17 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1244 | 190 | 0 | 35 | 4 | 82 | 0 | 0 | 0 | 0 | 34 | 282 | 1318 | 177 | 0 |  | 10561 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 31 | 80 | 30 | 335 | 0 | 0 | 34 | 82 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 22 | 33 | 15 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 | 0 | 2 | 49 | 68 | 25 | 0 | 19 | 8 | 13 | 0 | 0 | 0 | 0 | 205 | 149 | 0 | 0 | 45 | 40 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 108 | 55 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 209 | 10 | 0 | 9 | 315 | 17 | 5 | 0 | 97 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 23 | 295 | 69 | 105 | 17 | 0 | 240 | 0 | 17 | 88 | 66 | 25 | 322 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 42 | 0 | 330 | 145 | 0 | 355 | 9 | 156 | 0 | 390 |  | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 43 | 0 | 60 | 6 | 16 | 0 | 0 | 0 | 24 | 5 | 90 | 28 | 34 | 50 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 414 | 38 | 0 | 0 | 0 | 42 | 0 | 0 | 55 | 1200 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 307 | 1412 | 0 | 0 |  | 11192 | EvPeak
Forecast for Evening | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 |  | 0 | 0 | 0 | 75 | 80 | 15 | 335 | 0 | 105 | 60 | 82 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 19 | 22 | 33 | 32 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 50 | 68 | 25 | 0 | 19 | 8 | 20 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 45 | 40 | 0 | 51 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 141 | 65 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 210 | 15 | 0 | 10 | 315 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 18 | 25 | 400 | 69 | 105 | 17 | 0 | 120 | 0 | 17 | 114 | 68 | 25 | 370 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 42 | 17 | 360 | 145 | 0 | 355 | 29 | 150 | 0 | 390 |  | 483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 70 | 0 | 60 | 7 | 16 | 0 | 0 | 0 | 24 | 15 | 90 | 28 | 34 | 50 | 8 | 35 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 50 | 0 | 0 | 0 | 42 | 0 | 0 | 36 | 1244 | 220 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 307 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 15 | 335 | 0 | 80 | 60 | 80 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 30 | 32 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 0 | 19 | 51 | 25 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 47 | 40 | 0 | 51 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 128 | 35 | 0 | 0 | 1.6 | 34 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 210 | 15 | 0 | 10 | 300 | 17 | 0 | 0 | 195 | 0 | 0 | 9 | 0 | 100 | 20 | 25 | 18 | 13 | 400 | 57 | 17 | 17 | 5 | 15 | 17 | 17 | 98 | 38 | 25 | 320 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 350 | 17 | 0 | 300 | 20 | 150 | 0 | 390 |  | 483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 50 | 28 | 34 | 40 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 410 | 17 | 0 | 35 | 0 | 6 | 0 | 8 | 0 | 1200 | 220 |  | 150 | 6 | 100 | 0 | 0 |  | 0 | 30 | 250 | 1300 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 60 | 0 | 335 | 0 | 63 | 8 | 8 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 30 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 25 | 0 | 6 | 8 | 12 | 0 | 0 | 0 | 0 | 285 | 0 | 102 | 0 | 44 | 53 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 33 | 11 | 60 | 67 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 16 | 0 | 9 | 325 | 17 | 8 | 0 | 47 | 0 | 0 | 9 | 0 | 17 | 7 | 25 | 17 | 6 | 408 | 56 | 17 | 17 | 1 | 16 | 0 | 17 | 105 | 0 | 25 | 340 | 2 | 12 | 0 | 17 | 0 | 0 | 7 | 0 | 0 | 395 | 17 | 0 | 340 | 13 | 159 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 17 | 0 | 1 | 0 | 6 | 0 | 1 | 0 | 1244 | 220 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 0 | 7 | 307 | 1323 | 40 | 0 | 0 |  |  |  | 112231233 | 12542545 | 0 | 77317871 | 24338539 | 2263680 | 2517077 | 122880 | 949020
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 112.2312 | 12.5425 | 0 | 77.3179 | 24.3385 | 2.2637 | 2.5171 | 0.12288 | 0.94902
| Minimum Generation |  | 7628 | 5:00
| Highest Generation |  | 11192 | 19:00 | [129 empty] | 0 | [70 empty] | 232.2828
| Day Peak Generation |  | 10561 | 12:00
| Evening Peak Generation |  | 11192 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 907 | 22:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 619 | 19:00
| Load factor L.F |  | 86.48% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-02-19
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10561 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7644
Evening Peak Generation : |  |  | 11192 | MW Hour : | 19:00 | Available Max Generation : |  | 11750
E.P. Demand (at gen end) : |  |  | 11350 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11500
Maximum Generation : |  |  | 11192 | MW Hour : | 19:00 | Reserve(Generation end) |  | 250
Total Gen. (MKWH) : |  |  | 232.2828 | System Load Factor : | 86.48% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 776 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-19
Actual : |  | 85.11 | Ft.(MSL) , | Rule curve : | 94.48 | Ft.( MSL )
Gas Consumed : |  | Total = | 817.99 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 312766122.19
: |  |  | Coal : | 518082854.98 | Oil : | 444098182.54 | Total : | 1274947159.71
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 28 | 672:00 | 3823.072 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1045.9496 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1463.8103 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1271.063 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1046.4992 |  |  | 0 | 0%
Mymensingh Area |  | 123 | 2952:00 | 777.6683 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 436.6164 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 363.2198 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 710.409 |  |  | 0 | 0%
Total |  | 151 |  | 10938.3077 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Megnaghat-450 MW.
8) Haripur-412 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:31 | 16:33 | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Khagrachori 132/33kV end Due to Annual Deadline Checking.
and from Rangamati 132/33kV end Due to Annual deadline checking Rangamati-Kharachari Ckt-01.
08:58 | 19:21 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Scheduled S/D Due to For 132 KV Bus Modification Work
08:58 | 19:21 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D Due to For 132 KV Bus Modification Work.All 33 KV Feeder
Shift T-3 &T-4.
09:00 | 17:10 | Kallyanpur 132/33kV S/S GT-1 (132kV) HT Scheduled S/D Due to Annual Maintenance of main bus Isolator.
09:08 | 12:56 | Khulshi-Madunaghat 132kV Ckt-1 Scheduled S/D from Khulshi 132/33kV end Due to Annual Maintenance Bay
09:27 | 18:49 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to Realy test
09:27 | 18:48 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Emergency Line Maintenance
10:03 | 15:58 | Keraniganj-Nawabganj 132kV Ckt-2 Scheduled S/D from Nawabganj 132/33kV end Due to Deadline checking(annual
maintenance) and from Keranigonj 230/132/33kV end Due to Dead line checking at Nawabganj end.
10:27 |  | Ruppur 132/11kV S/S TR-02 HT Project Work S/D Due to 11kv Tr-02 Bus section maintenance by NSECO
10:31 |  | BIPTC S/S 20DF44 Forced S/D Due to Shutdown for corrective maintenance due to trip
11:36 |  | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to bus voltage low 389.32 kv .BR taken shut down.
12:24 | 15:18 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Kulaura 132/33kV end Due to fenchuganj s/s take this shutdown and
from Fenchuganj 230/132/33kV end Due to Kulaura 01 132KV Line Spare Post insulator removal work
12:34 | 16:36 | Gulshan 132/33kV S/S MT-1 LT Scheduled S/D Due to relay test by spmd
12:36 | 16:32 | Gulshan 132/33kV S/S MT-1 HT Scheduled S/D Due to relay test by spmd
13:44 | 14:40 | Gulsan-Rampura 132kV Ckt-1 Scheduled S/D from Gulshan 132/33kV end Due to relay test by spmd and from Rampura
230/132kV end Due to None
13:45 | 14:16 | Chowmuhani-Ramganj 132 kV Ckt-2 Tripped from Ramganj 132/33kV end showing Distance relay, start B C, zone 2,
37.58 Km relays Due to Distance trip and from Chowmuhani 132/33kV end showing Distance relay relays.
15:27 | 16:20 | Fenchuganj-Kulaura 132 kV Ckt-2 Scheduled S/D from Kulaura 132/33kV end Due to By NLDC instructions and from
Fenchuganj 230/132/33kV end Due to Kulaura 02 132KV Line Spare Post insulator removal work
15:45 | 17:42 | Madunaghat 132/33kV S/S TR-1(507T) LT Scheduled S/D Due to For redhot and bus isolator maintenance work of BPDB 33kv
mohora ckt-2 feeder.
16:46 |  | Haripur EGCB 412 MW CCPP tripped due to a stator ground fault.
16:46 |  | Haripur 412 MW CCPP Tripped with remarks:- GT
| 17:05 | Chauddagram-Feni 132 kV Ckt-2 is restored.
| 17:41 | Rampur 230/132/33 S/S 132kV BUS-01 is restored.
| 17:43 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT is restored.
| 17:43 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT is restored.
| 18:11 | Bhulta-Ghorasal 230 kV Ckt-1 is restored.
19:00 |  | Evening peak generation :11192 MW
| 21:44 | Barishal 230/132kV S/S ATR-2 LT is restored.
| 21:47 | Barishal 230/132kV S/S ATR-2 HT is restored.
0:02 |  | Meghnaghat CCPP(Summit)-2 Shutdown
05:00 |  | Minimum Generation: 7644 MW
5:13 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
07:39 |  | Cumilla(S) 132/33kV S/S TR-2 LT Scheduled S/D Due to Red hot maintenance 33 KV Tr-05 feeder by PDB. |  |  |  |  | 20.0MW load interruption.
07:39 |  | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3971000 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 184000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 6490800 | Tripped at 16:46
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 31 | 336000 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 1043056 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 230326 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 36 | 495104 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 281000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 34 | 300480 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7501767
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 592560 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 38880 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1538880
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 39929 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 39536 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 980160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 730100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 15 | 452400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 196320 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 97 | 1520509 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 559296 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 786240
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 286080 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178741
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 61200 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 390 | 9090455 | On test.
| Dhaka area Total |  |  |  | 5062 | 1707 | 38119219
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 136346 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136215
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 200160 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 949020 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 211 | 5008992
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 332872 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 49 | 809856 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 889060 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 353880 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 473280 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 182112 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 485760
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27723
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 240 | 1324800 | FGMO Test
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 128996 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 352108 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 469440 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 337473 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 685818
| SS Power I |  | SS Power | 2*612 | 1224 | 355 | 7614544
| Cox's Bazar Wind |  | IPP | 66 | 0 | 9 | 122880 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 156 | 3832727 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1456 | 24854062
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 149 | 3400000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 205 | 6278000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 330 | 7021000
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 45 | 1103040
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 40 | 862560
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1230959
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 23 | 252581 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 459856 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 393120 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 212400
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2263680
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 146842 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 11 | 266110 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1544700 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 66 | 688800 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 167760 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 42 | 274560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1282 | 27383668
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 55 | 1258560 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 204000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 991200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 266910
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 2 | 40080 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 135 | 2774050
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 35 | 825000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 968400 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3616854 | Frequency Control
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 143568 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 34512 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 668352 | GT-9 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5251530
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 186000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 361488 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7137000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 295 | 7661000 | Line Overload
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 192420
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 322 | 7676800 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1410 | 34722924
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 619 | 12542545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 53 | 186720
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 43 | 141312 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 38 | 355680 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 516960
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 753 | 13743217
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 98208 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 6 | 132242 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1227000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 27959100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4758491
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 248400 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4843600
| Barisal Area Total |  |  |  | 2265 | 1826 | 39267041
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 125474 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 48808 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 347560 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 409405 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 50 | 303807
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 179 | 4642455 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8805236
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 245500 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 134010 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 50813 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 797480 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 262464 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 218880 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26640
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1412 | 28947300
| Rajshahi Area Total |  |  |  | 3631 | 2336 | 45365832
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4120600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 42 | 249484 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35982
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 332160 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 203356
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1111250
| Rangpur Area Total |  |  |  | 950 | 287 | 6052832
| Total |  |  |  | 25481 | 11192 | 232282845
| Eastern Grid Total |  |  |  | 15398 | 5990 | 127853923
| Western Grid Total |  |  |  | 10083 | 5202 | 104428922
| National Grid Total |  |  |  | 25481 | 11192 | 232282845
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-18
| (a) ENTIRE EASTERN GRID : |  | 7279.04 | MW | (b) ENTIRE WESTERN GRID : |  | 3431.7 | MW
| i) Dhaka area |  | 4088.04 | MW | i) Khulna area |  | 1224.7 | MW
| ii) Chittagong area |  | 1058 | MW | ii) Rajshahi area |  | 1126 | MW
| iii) Comilla area |  | 879 | MW | iii) Barisal area |  | 288 | MW
| iv) Mymensingh area |  | 889 | MW | iv) Rangpur area |  | 793 | MW
| v) Sylhet area |  | 365 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10710.74 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 13:00 | Kamrangirchar | 47.7 | 12:00 | Narinda | 42 | 13:00 | Sherpur | 118 | 21:00
2 | AKSML | 104 | 00:00 | Chowmuhani | 143 | 18:30 | Kaptai | N/A | N/A | Narshingdi | 149 | 20:00 | Shikalbaha | 22 | 15:00
3 | Aftabnagar | 26 | 13:00 | Chuadanga | 72 | 18:30 | Kazla | 60 | 00:00 | Natore | 102 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 68 | 13:00 | Coxsbazar | 95 | 18:30 | Keranigonj | 64 | 13:00 | Nawabganj | 28.4 | 21:00 | Shitalakhya | 81.6 | 12:00
5 | Agrabad | 52 | 18:00 | Cumilla(N) | 120 | 19:30 | Khagrachori | 26 | 18:30 | Netrakona | 101 | 16:00 | Sholosohor | 34 | 13:00
6 | Amnura | 56 | 08:00 | Cumilla(S) | 112 | 14:00 | Khulna | 74 | 19:00 | New | 19.5 | 12:00 | Shyampur | 158 | 09:00
7 | Ashuganj | 50 | 12:00 | Daudkandi | 103 | 20:00 | Khulshi | 113 | 19:00 | Niamatpur | 82 | 09:00 | Siddhirganj | 104 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 18 | 11:00 | Kishoreganj | 110 | 20:00 | Noapara | 36 | 18:30 | Sirajganj | 92 | 08:00
9 | BSRM | 138 | 15:00 | Dhamrai | 118 | 10:00 | Kodda | 267 | 11:00 | PHP | 8 | 00:00 | Sonargaon | 98 | 09:00
10 | Bagerhat | 72 | 18:30 | Dhanmondi | 106 | 13:00 | Kulaura | 24 | 18:00 | Pabna | 81 | 19:00 | Sreemongol | 44 | 18:30
11 | Bakulia | 67 | 18:00 | Dohazari | 58 | 19:30 | Kurigram | 63 | 18:30 | Palashbari | 96 | 08:00 | Sreepur | 63 | 18:00
12 | Banani | 17.6 | 10:00 | Faridpur | 108 | 19:00 | Kushtia | 106 | 18:30 | Panchagarh | 47 | 18:30 | Srinagar | 29.51 | 21:00
13 | Bangabhaban | 10 | 10:00 | Fatullah | 50 | 12:00 | Lalbag | 80 | 13:00 | Patuakhali | 52.1 | 21:00 | Sunamganj | 36 | 18:30
14 | Barapukuria | 58 | 08:00 | Fenchuganj | 24 | 19:00 | Lalmonirhat | 39 | 19:00 | Payra | 14 | 11:00 | Sylhet | 12 | 00:00
15 | Barguna | 14 | 21:00 | Feni | 75 | 18:30 | MI_Cement | 12.1 | 08:00 | Postogola | 40 | 13:00 | Sylhet-132 | 96 | 13:00
16 | Barishal | 78 | 21:00 | GPH | 95 | 00:00 | Madanganj | 38 | 12:00 | Purbachal | 14 | 18:30 | TK | 14 | 18:30
17 | Barishal-230 | 60 | 18:30 | Ghorashal | 67 | 11:00 | Madaripur | 64 | 19:30 | Purbasadipur | 111 | 08:00 | Tangail | 164 | 08:00
18 | Baroaulia | 53 | 18:30 | Goalpara | 24 | 19:00 | Madartek | 56.52 | 13:00 | Rahim | 50 | 16:00 | Thakurgaon | 78 | 19:00
19 | Baroirhat | 43 | 13:00 | Gollamari | 36 | 13:00 | Madunaghat | 30 | 12:00 | Rajbari | 48 | 18:30 | Tongi | 135 | 12:00
20 | Bashundhara | 134 | 14:00 | Gopalganj | 74.7 | 19:00 | Magura | 45 | 18:30 | Rajendrapur | 76 | 18:30 | Ullahpara | 23 | 19:00
21 | BashundharaCement | 12 | 11:00 | Gulshan | 78 | 13:00 | Mahasthangarh | 54 | 08:00 | Rajshahi | 109 | 19:30 | Ullon | 34 | 13:00
22 | Beanibazar | 41 | 19:30 | Halishahar | 72 | 15:00 | Manikganj | 84 | 19:00 | Rajshahi-230 | 26 | 19:00 | Uttara | 46 | 13:00
23 | Benapole | 64 | 07:00 | HaripurSBU | 146 | 15:00 | Maniknagar | 58 | 13:00 | Ramganj | 68 | 19:30 | UttaraNew | 30 | 14:00
24 | Bhaluka | 112 | 09:00 | Hasnabad | 65 | 19:00 | Matarbari | 35 | 18:30 | Rampur | 20 | 18:30 | Zigatola | 44 | 12:00
25 | Bhandaria | 32 | 18:00 | Hathazari | 57 | 19:30 | Matuail | 61 | 12:00 | Rangamati | 13 | 18:30
26 | Bhangura | 30 | 19:00 | Ishurdi | 52 | 19:00 | Millgate | 82 | 11:00 | Rangpur | 111 | 19:00
27 | Bheramara(GK) | 39 | 18:30 | Jaldhaka | 64 | 08:00 | Mirpur | 93 | 19:00 | Ruppur | 4.8 | 15:00
28 | Bhulta | 243 | 15:00 | Jamalpur | 148 | 21:00 | Mirsorai | 4 | 19:30 | SSM | 12 | 00:00
29 | Bog-Sherpur | 56 | 08:00 | Jashore | 108 | 13:00 | Mirzapur | 53 | 07:00 | Saidpur | 95 | 18:30
30 | Bogura | 123 | 18:30 | Jhenaidah | 90 | 18:30 | Mithapukur | 50 | 07:00 | Satkhira | 94 | 19:00
31 | Borhanuddin | 50 | 21:00 | Joydebpur | 150 | 18:00 | Modern | 0 | 00:00 | Satmasjid | 83 | 14:00
32 | Brahmanbaria | 112 | 19:00 | Joypurhat | 49 | 19:00 | Mogbazar | 92.2 | 13:00 | Savar | 150 | 12:00
33 | Cantonment | 104 | 13:00 | Juldah | 19 | 07:00 | Mongla | 37 | 12:00 | SevenRings | 6.64 | 07:00
34 | Chandpur | 42 | 20:00 | KSRM | 35 | 18:00 | Motijheel | 31 | 13:00 | ShahCement | 24 | 03:00
35 | Chandraghona | 24 | 18:30 | Kabirpur | 258 | 12:00 | Munshiganj | 65 | 13:00 | Shahjadpur | 58 | 08:00
36 | Chapai | 53 | 12:00 | Kachua | 48 | 18:30 | Mymensingh | 184 | 08:00 | Shahjibazar | 85 | 20:00
37 | Charsaidpur | 41 | 01:00 | Kallyanpur | 68 | 13:00 | Naogaon | 108 | 13:00 | Shahmirpur | 43 | 03:00
38 | Chauddagram | 43 | 14:00 | Kalurghat | 28 | 10:00 | Narail | 40 | 19:00 | Shariatpur | 51 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 413 | 05:00 | 390 | 18:30 | Gopalganj | 416 | 05:00 | 294 | 18:30
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 399 | 04:00 | 364 | 16:00
| Bhulta | 400 | 05:00 | 378 | 16:00 | Madunaghat_I | 412 | 20:00 | 404 | 12:00
| Bibiana | 415 | 05:00 | 408 | 15:00 | Payra | 421 | 05:00 | 408 | 12:00
| BIPTC | 408 | 04:00 | 398 | 12:00 | Rahanpur | 419 | 05:00 | 398 | 12:00
| Bogura | 411 | 05:00 | 386 | 18:30 | Rampal | 415 | 04:00 | 391 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 04:00 | 218 | 16:00 | Haripur | 231 | 00:00 | 219 | 17:00
| AKSML | 233 | 19:00 | 225 | 02:00 | Hasnabad | 230 | 01:00 | 218 | 16:00
| Aminbazar | 233 | 04:00 | 220 | 16:00 | Hathazari | 237 | 19:30 | 226 | 03:00
| Ashuganj | 240 | 03:00 | 230 | 12:00 | Ishurdi | 242 | 05:00 | 225 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 239 | 05:00 | 220 | 12:00
| Baghabari | 236 | 01:00 | 223 | 11:00 | Kaliakoir | 233 | 04:00 | 131 | 02:00
| Barapukuria | 223 | 04:00 | 212 | 08:00 | Keranigonj | 234 | 05:00 | 219 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 242 | 05:00 | 224 | 11:00
| Barishal | 245 | 04:00 | 239 | 10:00 | Madunaghat_I | 236 | 20:00 | 227 | 12:00
| Bheramara | 241 | 05:00 | 223 | 18:30 | Maniknagar | 232 | 04:00 | 220 | 16:00
| Bhulta | 236 | 04:00 | 222 | 16:00 | Meghnaghat | 234 | 00:00 | 224 | 15:00
| Bibiana | 238 | 18:00 | 232 | 16:00 | Mirsorai | 240 | 19:30 | 226 | 06:00
| BIPTC | 241 | 04:00 | 222 | 12:00 | Rajshahi | 243 | 04:00 | 227 | 12:00
| Bogura | 235 | 05:00 | 220 | 12:00 | Rampal | 240 | 04:00 | 224 | 12:00
| Bogura-400 | 237 | 04:00 | 222 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 02:00 | 242 | 11:00 | Rampura | 232 | 03:00 | 220 | 17:00
| BSRM | 238 | 19:30 | 226 | 15:00 | Shikalbaha | 235 | 20:00 | 225 | 02:00
| Cumilla(N) | 235 | 20:00 | 225 | 12:00 | Shyampur | 234 | 05:00 | 219 | 16:00
| Fenchuganj | 242 | 19:30 | 237 | 18:30 | Siddhirganj | 233 | 06:00 | 221 | 17:00
| Ghorashal | 240 | 00:00 | 230 | 12:00 | Sirajgonj | 243 | 03:00 | 232 | 18:30
| Ghorashal-230 | 236 | 06:00 | 224 | 11:00 | Sreepur | 238 | 05:00 | 225 | 12:00
| GPH | 236 | 19:30 | 225 | 02:00 | Tongi | 230 | 09:00 | 210 | 15:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 133 | 03:00 | 123 | 14:00 | Lalbag | 134 | 05:00 | 123 | 16:00
| Agargaon | 138 | 05:00 | 125 | 16:00 | Lalmonirhat | 130 | 03:00 | 120 | 08:00
| Agrabad | 137 | 18:30 | 130 | 12:00 | Madanganj | 130 | 00:00 | 123 | 17:00
| AKS | 135 | 19:30 | 128 | 05:00 | Madaripur | 137 | 04:00 | 130 | 12:00
| Aminbazar | 132 | 04:00 | 124 | 16:00 | Madartek | 133 | 05:00 | 123 | 16:00
| Amnura | 139 | 19:30 | 125 | 08:00 | Madunaghat | 138 | 19:00 | 132 | 02:00
| Ashuganj | 141 | 04:00 | 135 | 12:00 | Magura | 140 | 04:00 | 126 | 11:00
| Bagerhat | 133 | 21:00 | 123 | 11:00 | Mahasthangarh | 136 | 03:00 | 125 | 12:00
| Bakulia | 137 | 19:30 | 131 | 11:00 | Manikganj | 135 | 19:30 | 124 | 16:00
| Banani | 135 | 04:00 | 124 | 17:00 | Maniknagar | 135 | 07:00 | 125 | 17:00
| Bangabhaban | 134 | 03:00 | 125 | 17:00 | Matarbari | 130 | 07:00 | 123 | 03:00
| Barapukuria | 136 | 04:00 | 126 | 08:00 | Matuail | 132 | 04:00 | 124 | 16:00
| Barguna | 131 | 18:00 | 127 | 11:00 | Millgate | 135 | 02:00 | 121 | 16:00
| Barishal | 140 | 02:00 | 126 | 11:00 | Mirpur | 130 | 00:00 | 123 | 12:00
| Barishal-230 | 140 | 04:00 | 134 | 11:00 | Mirzapur | 135 | 19:00 | 123 | 18:30
| Baroaulia | 137 | 20:00 | 131 | 12:00 | Mithapukur | 134 | 04:00 | 121 | 07:00
| Baroirhat | 137 | 18:00 | 129 | 02:00 | MI_Cement | 133 | 03:00 | 125 | 16:00
| Bashundhara | 135 | 03:00 | 121 | 16:00 | Modern | 138 | 19:30 | 130 | 12:00
| BashundharaCement | 130 | 00:00 | 123 | 17:00 | Mogbazar | 133 | 01:00 | 123 | 17:00
| Beanibazar | 135 | 01:00 | 132 | 12:00 | Mongla | 133 | 21:00 | 123 | 11:00
| Benapole | 136 | 03:00 | 122 | 12:00 | Motijheel | 134 | 03:00 | 125 | 17:00
| Bhaluka | 134 | 04:00 | 124 | 12:00 | Munshiganj | 131 | 03:00 | 123 | 16:00
| Bhandaria | 130 | 05:00 | 123 | 08:00 | Mymensingh | 132 | 03:00 | 116 | 18:30
| Bhangura | 141 | 04:00 | 130 | 12:00 | Naogaon | 133 | 04:00 | 122 | 07:00
| Bheramara | 139 | 04:00 | 129 | 12:00 | Narail | 139 | 04:00 | 129 | 11:00
| Bheramara(GK) | 138 | 03:00 | 128 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 120 | 00:00 | 110 | 16:00 | Narshingdi | 134 | 00:00 | 116 | 16:00
| Bog-Sherpur | 138 | 02:00 | 127 | 12:00 | Natore | 137 | 04:00 | 126 | 12:00
| Bogura | 136 | 06:00 | 128 | 08:00 | Nawabganj | 134 | 04:00 | 124 | 16:00
| Bogura-230 | 138 | 05:00 | 127 | 12:00 | Netrakona | 131 | 06:00 | 120 | 11:00
| Brahmanbaria | 135 | 00:00 | 130 | 12:00 | New | 134 | 07:00 | 123 | 15:00
| Cantonment | 138 | 05:00 | 125 | 15:00 | Niamatpur | 136 | 02:00 | 128 | 12:00
| Chandpur | 137 | 19:00 | 130 | 12:00 | Noapara | 134 | 21:00 | 124 | 11:00
| Chandraghona | 139 | 19:00 | 133 | 01:00 | Pabna | 140 | 04:00 | 128 | 12:00
| Chapai | 135 | 06:00 | 128 | 11:00 | Palashbari | 132 | 04:00 | 121 | 12:00
| Charsaidpur | 132 | 04:00 | 122 | 17:00 | Panchagarh | 135 | 05:00 | 115 | 08:00
| Chauddagram | 138 | 20:00 | 132 | 01:00 | Patuakhali | 131 | 19:30 | 126 | 16:00
| Chhatak | 136 | 00:00 | 132 | 13:00 | Payra | 132 | 19:30 | 127 | 11:00
| Chowmuhani | 137 | 20:00 | 127 | 04:00 | PHP | 137 | 19:30 | 128 | 06:00
| Chuadanga | 138 | 04:00 | 123 | 12:00 | Postogola | 134 | 03:00 | 126 | 16:00
| Coxsbazar | 127 | 09:00 | 122 | 12:00 | Purbachal | 137 | 04:00 | 124 | 16:00
| Cumilla(N) | 139 | 19:00 | 133 | 12:00 | Purbasadipur | 131 | 03:00 | 115 | 08:00
| Cumilla(S) | 139 | 18:30 | 129 | 09:00 | Rahanpur | 138 | 05:00 | 132 | 08:00
| Daudkandi | 126 | 19:00 | 119 | 17:00 | Rahim | 131 | 00:00 | 122 | 17:00
| Dhaka | 132 | 01:00 | 124 | 12:00 | Rajbari | 139 | 04:00 | 129 | 12:00
| Dhamrai | 133 | 07:00 | 120 | 16:00 | Rajendrapur | 138 | 07:00 | 124 | 16:00
| Dhanmondi | 132 | 04:00 | 122 | 17:00 | Rajshahi | 134 | 19:30 | 127 | 11:00
| Dohazari | 133 | 17:00 | 127 | 06:00 | Rajshahi-230 | 136 | 05:00 | 125 | 12:00
| Faridpur | 137 | 03:00 | 130 | 12:00 | Ramganj | 135 | 19:30 | 128 | 12:00
| Fatullah | 134 | 05:00 | 125 | 16:00 | Rampur | 137 | 19:30 | 131 | 00:00
| Fenchuganj | 137 | 00:00 | 135 | 12:00 | Rampura | 134 | 05:00 | 125 | 15:00
| Feni | 136 | 19:30 | 128 | 06:00 | Rangamati | 137 | 19:30 | 131 | 12:00
| Ghorashal | 140 | 00:00 | 133 | 12:00 | Rangpur | 132 | 21:00 | 120 | 08:00
| Goalpara | 138 | 04:00 | 127 | 10:00 | Ruppur | 140 | 02:00 | 130 | 11:00
| Gollamari | 136 | 04:00 | 126 | 11:00 | Saidpur | 133 | 03:00 | 120 | 08:00
| Gopalganj | 137 | 04:00 | 128 | 11:00 | Satkhira | 133 | 02:00 | 123 | 18:30
| Gopalganj-400 | 139 | 05:00 | 130 | 11:00 | Satmasjid | 137 | 05:00 | 125 | 12:00
| Gulshan | 133 | 05:00 | 124 | 17:00 | Savar | 131 | 05:00 | 121 | 16:00
| Halishahar | 138 | 19:30 | 130 | 05:00 | SevenRings | 142 | 03:00 | 133 | 12:00
| Haripur | 131 | 00:00 | 122 | 17:00 | ShahCement | 132 | 04:00 | 122 | 17:00
| HaripurSBU | 131 | 00:00 | 122 | 17:00 | Shahjadpur | 140 | 00:00 | 133 | 12:00
| Hasnabad | 134 | 00:00 | 126 | 16:00 | Shahjibazar | 134 | 00:00 | 130 | 12:00
| Hathazari | 140 | 19:30 | 132 | 05:00 | Shahmirpur | 137 | 17:00 | 130 | 10:00
| Ishurdi | 142 | 05:00 | 131 | 12:00 | Shariatpur | 145 | 21:00 | 130 | 11:00
| Jaldhaka | 132 | 04:00 | 117 | 08:00 | Sherpur | 128 | 07:00 | 108 | 18:00
| Jamalpur | 131 | 07:00 | 114 | 18:30 | Shikalbaha | 126 | 22:00 | 120 | 03:00
| Jashore | 137 | 05:00 | 123 | 12:00 | Shikalbaha-230 | 138 | 20:00 | 131 | 03:00
| Jhenaidah | 139 | 02:00 | 128 | 12:00 | Shitalakhya | 133 | 03:00 | 128 | 11:00
| Jhenaidah-230 | 142 | 05:00 | 129 | 12:00 | Sholosohor | 137 | 20:00 | 131 | 02:00
| Joydebpur | 141 | 20:00 | 128 | 12:00 | Shyampur | 134 | 03:00 | 125 | 12:00
| Joypurhat | 131 | 00:00 | 120 | 12:00 | Shyampur-230 | 134 | 04:00 | 125 | 16:00
| Juldah | 138 | 19:00 | 131 | 12:00 | Siddhirganj | 131 | 03:00 | 122 | 17:00
| Kabirpur | 139 | 19:00 | 118 | 12:00 | Sirajganj | 136 | 01:00 | 126 | 12:00
| Kachua | 138 | 19:00 | 130 | 02:00 | Sonargaon | 128 | 00:00 | 120 | 17:00
| Kaliakoir | 139 | 02:00 | 125 | 11:00 | Sreemongol | 135 | 01:00 | 131 | 12:00
| Kallyanpur | 137 | 00:00 | 128 | 12:00 | Sreepur | 136 | 04:00 | 127 | 12:00
| Kalurghat | 138 | 19:00 | 132 | 01:00 | Srinagar | 131 | 00:00 | 125 | 11:00
| Kamrangirchar | 134 | 07:00 | 125 | 15:00 | SSM | 140 | 07:00 | 137 | 04:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 01:00 | 131 | 12:00
| Kazla | 136 | 05:00 | 126 | 13:00 | Sylhet | 135 | 00:00 | 133 | 13:00
| Keranigonj | 134 | 05:00 | 124 | 17:00 | Sylhet-132 | 135 | 00:00 | 133 | 15:00
| Khagrachori | 136 | 19:30 | 130 | 12:00 | Tangail | 132 | 19:00 | 119 | 18:30
| Khulna | 133 | 02:00 | 126 | 11:00 | Thakurgaon | 134 | 05:00 | 113 | 08:00
| Khulna(S) | 137 | 05:00 | 126 | 11:00 | TK | 138 | 19:00 | 128 | 06:00
| Khulshi | 136 | 20:00 | 129 | 05:00 | Tongi | 134 | 01:00 | 123 | 15:00
| Kishoreganj | 135 | 00:00 | 127 | 12:00 | Ullahpara | 138 | 01:00 | 129 | 12:00
| Kodda | 138 | 07:00 | 125 | 16:00 | Ullon | 133 | 03:00 | 122 | 16:00
| KSRM | 139 | 19:00 | 131 | 02:00 | Uttara | 136 | 05:00 | 120 | 16:00
| Kulaura | 137 | 03:00 | 134 | 13:00 | UttaraNew | 133 | 00:00 | 123 | 12:00
| Kurigram | 131 | 04:00 | 120 | 07:00 | Zigatola | 134 | 04:00 | 125 | 12:00
| Kushtia | 140 | 05:00 | 127 | 12:00

## L-Curve
Date | 2024-02-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1510 | 4679 | 4407 | 9086 |  |  |  | QF-LDC-11
0:30 | 1390 | 4739 | 4054.5 | 8793.5 | Date: | 2024-02-18
1:00 | 1270 | 4799 | 3702 | 8501
1:30 | 1241 | 4667 | 3643 | 8310
2:00 | 1212 | 4535 | 3584 | 8119
2:30 | 1176 | 4515.5 | 3502 | 8017.5 | [5 empty] | Gen. at Eve. Peak | 11192 | 11192 MW (19:00 )
3:00 | 1140 | 4496 | 3420 | 7916 | [6 empty] | 19:00
3:30 | 1125 | 4484 | 3323 | 7807 | [5 empty] | Gen. at Day Peak | 10561 | 10561 MW (12:00 )
4:00 | 1110 | 4472 | 3226 | 7698 | [6 empty] | 12:00
4:30 | 1075 | 4438.5 | 3224.5 | 7663 | [5 empty] | Highest Generation | 11192
5:00 | 1040 | 4405 | 3223 | 7628 | [6 empty] | 19:00
5:30 | 955 | 4428.5 | 3262 | 7690.5
6:00 | 870 | 4452 | 3301 | 7753
6:30 | 823 | 4669.5 | 3445.5 | 8115
7:00 | 776 | 4887 | 3590 | 8477
7:30 | 861 | 5157 | 3789.5 | 8946.5
8:00 | 946 | 5427 | 3989 | 9416
8:30 | 1027 | 5447 | 4148 | 9595
9:00 | 1108 | 5467 | 4307 | 9774
9:30 | 1289 | 5395 | 4361 | 9756
10:00 | 1470 | 5323 | 4415 | 9738
10:30 | 1405 | 5408.5 | 4523.5 | 9932
11:00 | 1340 | 5494 | 4632 | 10126
11:30 | 1425 | 5594 | 4749.5 | 10343.5
12:00 | 1510 | 5694 | 4867 | 10561
12:30 | 1491 | 5729 | 4817 | 10546
13:00 | 1472 | 5764 | 4767 | 10531
13:30 | 1436 | 5639.5 | 4673 | 10312.5
14:00 | 1400 | 5515 | 4579 | 10094
14:30 | 1413 | 5506.5 | 4539.5 | 10046
15:00 | 1426 | 5498 | 4500 | 9998
15:30 | 1403 | 5552 | 4351 | 9903
16:00 | 1380 | 5606 | 4202 | 9808
16:30 | 1370 | 5414.5 | 4235.5 | 9650
17:00 | 1360 | 5223 | 4269 | 9492
17:30 | 1365 | 5491.5 | 4509.5 | 10001
18:00 | 1370 | 5760 | 4750 | 10510
18:30 | 1295 | 5875 | 4976 | 10851
19:00 | 1220 | 5990 | 5202 | 11192
19:30 | 1312 | 5899 | 5145 | 11044
20:00 | 1310 | 5947 | 5006 | 10953 |  |  |  | Executive Engineer
20:30 | 1390 | 5817 | 5030 | 10847 |  |  |  | Network Operation Division
21:00 | 1470 | 5687 | 5054 | 10741
21:30 | 1450 | 5551.5 | 4787 | 10338.5
22:00 | 1430 | 5416 | 4520 | 9936 |  |  |  |  | Page 6 of 7
22:30 | 1440 | 5271 | 4477 | 9748
23:00 | 1450 | 5126 | 4434 | 9560
23:30 | 1480 | 4902.5 | 4420.5 | 9323
24:00 | 1510 | 4679 | 4407 | 9086
11192 MW (19:00 )
10561 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-18 |  | Energy |  | 232282845
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3011 | 907 | 1257 | 0 | 414 | 3132 | 40 | 0 | 237 | 88 | 0 | 0 | 42.02
0:30 | 3070 | 690 | 1419.5 | 0 | 294.5 | 3034 | 40 | 0 | 158.5 | 87 | 0 | 0 | 42.02 |  | Date: | 43878
1:00 | 3129 | 473 | 1582 | 0 | 175 | 2936 | 40 | 0 | 80 | 86 | 0 | 0 | 42.02
1:30 | 3094.5 | 473 | 1549 | 0 | 121 | 2901.5 | 40 | 0 | 48 | 82 | 0 | 1 | 35.8125 | [8 empty] | Total Energy | 232.2828 | 232.2828 | Total Energy Gen 232.283 MKWHr Energy Not Served 2.864 MKWHr Energy Requirement 235.147 MKWHr
2:00 | 3060 | 473 | 1516 | 0 | 67 | 2867 | 40 | 0 | 16 | 78 | 0 | 2 | 29.605 | [8 empty] | Energy not Served | 2.8643 | 2.8643
2:30 | 3053.5 | 473 | 1521 | 0 | 59.5 | 2775.5 | 40 | 0 | 16 | 78 | 0 | 1 | 26.2625 | [8 empty] | Energy Requirement | 235.1471 | 235.1471
3:00 | 3047 | 473 | 1526 | 0 | 52 | 2684 | 40 | 0 | 16 | 78 | 0 | 0 | 22.92
3:30 | 3044 | 473 | 1526 | 0 | 43.5 | 2586.5 | 40 | 0 | 16 | 76 | 0 | 2 | 21.965 | [7 empty] | Shortage
4:00 | 3041 | 473 | 1526 | 0 | 35 | 2489 | 40 | 0 | 16 | 74 | 0 | 4 | 21.01
4:30 | 3029.5 | 473 | 1501.5 | 0 | 35 | 2488.5 | 40 | 0 | 16 | 75 | 0 | 4.5 | 25.785
5:00 | 3018 | 473 | 1477 | 0 | 35 | 2488 | 40 | 0 | 16 | 76 | 0 | 5 | 30.56
5:30 | 3049.5 | 473 | 1498.5 | 0 | 27 | 2502.5 | 40 | 0 | 16 | 79 | 0 | 5 | 37.78
6:00 | 3081 | 473 | 1520 | 0 | 19 | 2517 | 40 | 0 | 16 | 82 | 0 | 5 | 45
6:30 | 3214.5 | 439 | 1489.5 | 0 | 178.5 | 2637 | 40 | 0 | 24.5 | 81 | 7 | 4 | 62 | [6 empty] | Coal
7:00 | 3348 | 405 | 1459 | 0 | 338 | 2757 | 40 | 0 | 33 | 80 | 14 | 3 | 79
7:30 | 3395.5 | 298 | 1530.5 | 0 | 488 | 3002 | 40 | 0 | 49 | 86 | 55.5 | 2 | 127.36 | [5 empty] | Oil
8:00 | 3443 | 191 | 1602 | 0 | 638 | 3247 | 40 | 0 | 65 | 92 | 97 | 1 | 175.72
8:30 | 3404 | 191.5 | 1587.5 | 0 | 691.5 | 3319.5 | 40 | 0 | 115 | 93 | 151 | 2 | 267.4
9:00 | 3365 | 192 | 1573 | 0 | 745 | 3392 | 40 | 0 | 165 | 94 | 205 | 3 | 359.08
9:30 | 3248.5 | 191.5 | 1479.5 | 0 | 832 | 3426 | 40 | 0 | 187.5 | 97 | 252.5 | 1.5 | 304.645
10:00 | 3132 | 191 | 1386 | 0 | 919 | 3460 | 40 | 0 | 210 | 100 | 300 | 0 | 250.21
10:30 | 3123.5 | 261.5 | 1393.5 | 0 | 973 | 3460 | 40 | 0 | 250 | 100 | 329.5 | 1 | 255.94
11:00 | 3115 | 332 | 1401 | 0 | 1027 | 3460 | 40 | 0 | 290 | 100 | 359 | 2 | 261.67
11:30 | 3149.5 | 402 | 1455 | 0 | 1066.5 | 3466 | 40 | 0 | 279 | 104 | 379 | 2.5 | 247.345
12:00 | 3184 | 472 | 1509 | 0 | 1106 | 3472 | 40 | 0 | 268 | 108 | 399 | 3 | 233.02
12:30 | 3193 | 472.5 | 1525 | 0 | 1111.5 | 3423 | 40 | 0 | 290 | 108 | 378.5 | 4.5 | 262.625
13:00 | 3202 | 473 | 1541 | 0 | 1117 | 3374 | 40 | 0 | 312 | 108 | 358 | 6 | 292.23
13:30 | 3202 | 473 | 1541 | 0 | 1117 | 3374 | 40 | 0 | 312 | 108 | 358 | 6 | 292.23
14:00 | 3202 | 473 | 1541 | 0 | 1117 | 3374 | 40 | 0 | 312 | 108 | 358 | 6 | 292.23
14:30 | 3160 | 473 | 1485.5 | 0 | 1006.5 | 3359 | 40 | 0 | 310 | 110 | 307.5 | 13 | 218.695
15:00 | 3118 | 473 | 1430 | 0 | 896 | 3344 | 40 | 0 | 308 | 112 | 257 | 20 | 145.16
15:30 | 3120.5 | 545.5 | 1423 | 0 | 917 | 3211 | 40 | 0 | 315.5 | 109 | 204.5 | 17 | 104.5725
16:00 | 3123 | 618 | 1416 | 0 | 938 | 3078 | 40 | 0 | 323 | 106 | 152 | 14 | 63.985
16:30 | 2899.5 | 642.5 | 1429.5 | 0 | 1008.5 | 3074.5 | 40 | 0 | 338 | 103 | 104.5 | 10 | 83.5625
17:00 | 2676 | 667 | 1443 | 0 | 1079 | 3071 | 40 | 0 | 353 | 100 | 57 | 6 | 103.14
17:30 | 2695.5 | 696.5 | 1498 | 0 | 1291 | 3122 | 40 | 0 | 517.5 | 106 | 28.5 | 6 | 94.545
18:00 | 2715 | 726 | 1553 | 0 | 1503 | 3173 | 40 | 0 | 682 | 112 | 0 | 6 | 85.95
18:30 | 2764.5 | 672.5 | 1568 | 0 | 1587 | 3386.5 | 40 | 0 | 715 | 110 | 0 | 7.5 | 118.42
19:00 | 2814 | 619 | 1583 | 0 | 1671 | 3600 | 40 | 0 | 748 | 108 | 0 | 9 | 150.89
19:30 | 2772 | 624 | 1500 | 0 | 1644 | 3581 | 40 | 0 | 774 | 100 | 0 | 9 | 109.825
20:00 | 2836 | 624 | 1478 | 0 | 1620 | 3459 | 40 | 0 | 782 | 102 | 0 | 12 | 68.76
20:30 | 2946.5 | 623.5 | 1531 | 0 | 1427.5 | 3452 | 40 | 0 | 712.5 | 105 | 0 | 9 | 59.38
21:00 | 3057 | 623 | 1584 | 0 | 1235 | 3445 | 40 | 0 | 643 | 108 | 0 | 6 | 50
21:30 | 3120 | 765 | 1532.5 | 0 | 992 | 3343.5 | 40 | 0 | 440 | 102 | 0 | 3.5 | 55.56
22:00 | 3183 | 907 | 1481 | 0 | 749 | 3242 | 40 | 0 | 237 | 96 | 0 | 1 | 61.12
22:30 | 3105.5 | 907 | 1484.5 | 0 | 664.5 | 3211 | 40 | 0 | 237 | 98 | 0 | 0.5 | 59.21
23:00 | 3028 | 907 | 1488 | 0 | 580 | 3180 | 40 | 0 | 237 | 100 | 0 | 0 | 57.3
23:30 | 3019.5 | 907 | 1372.5 | 0 | 497 | 3156 | 40 | 0 | 237 | 94 | 0 | 0 | 49.66 |  | Max Temp. in Dhaka |  | 29.2°C
24:00 | 3011 | 907 | 1257 | 0 | 414 | 3132 | 40 | 0 | 237 | 88 | 0 | 0 | 42.02
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 232.283 MKWHr Energy Not Served 2.864 MKWHr Energy Requirement 235.147 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-02-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 949020
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 1 | 8 | 4 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 136346
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 7 | 13 | 17 | 19 | 20 | 19 | 0 | 13 | 9 | 3 | [9 empty] | 136215
6 | Sikalbaha 225MW CCPP (Gas) | 211 | 211 | 211 | 212 | 211 | 214 | 213 | 211 | 212 | 213 | 212 | 212 | 213 | 213 | 215 | 213 | 212 | 212 |  | 211 | 211 | 212 | 210 | 211 | 212 | 211 | 5008992
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 51 | 51 | 51 | 48 | 48 | 47 | 47 | 47 | 51 | 66 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 889060
12 | Hathazari 100 MW peaking PP | 64 | 0 | [6 empty] | 33 | 32 | 39 | 32 | 40 | 40 | 44 | 48 | 48 | 48 |  | 49 | 56 | 64 | 64 | 64 | 64 | 64 | 809856
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 0 |  |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 32 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 332872
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [10 empty] | 21 | 23 | 28 | 39 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 459856
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [21 empty] | 62 | 63 | 63 | 41 | 39 | 281000
17 | Siddhirganj 335 MW CCPP | 300 | 270 | 270 | 270 | 270 | 335 | 335 | 335 | 335 | 270 | 270 | 335 | 335 | 280 | 280 | 335 | 335 | 300 |  | 335 | 280 | 280 | 335 | 335 | 335 | 335 | 7501767
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 15 | 30 | 160 | 200 | 190 | 180 | 82 | 47 | 47 | 77 | 97 |  | 97 | 97 | 97 | 97 | 0 |  | 0 | 1520509
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 190 | 160 | 160 | 160 | 160 | 160 | 160 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 130 | 130 | 130 |  | 130 | 130 | 130 | 160 | 160 | 160 | 160 | 3971000
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 320 | 320 | 300 | 300 | 300 | 300 | 300 | 304 | 302 | 301 | 300 | 301 | 296 | 297 | 300 | 325 | 315 | 360 |  | 355 | 360 | 355 | 340 | 340 | 340 | 340 | 7614544
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 42 | 44 | 41 | 44 | 44 | 44 | 45 | 45 | 45 |  | 45 | 45 | 46 | 46 | 46 | 47 | 47 | 1103040
33 | Ashuganj 225 MW CCPP | 127 | 123 | 123 | 123 | 123 | 135 | 136 | 134 | 117 | 116 | 130 | 144 | 147 | 147 | 144 | 144 | 147 | 147 |  | 149 | 151 | 150 | 150 | 148 | 149 | 154 | 3400000
34 | Ashuganj 450 MW CCPP(South) | 220 | 220 | 220 | 220 | 220 | 220 | 250 | 280 | 270 | 270 | 300 | 300 | 270 | 260 | 260 | 260 | 260 | 260 |  | 205 | 210 | 240 | 300 | 290 | 280 | 260 | 6278000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 360 | 350 | 320 | 320 | 320 | 320 | 320 | 280 | 280 | 280 | 280 | 340 |  | 330 | 280 | 230 | 270 | 330 | 300 | 300 | 7021000
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 36 | 20 | 20 | 20 | 27 | 30 | 30 | 30 | 36 | 38 | 40 |  | 40 | 40 | 37 | 20 | 20 | 20 | 20 | 862560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 359 | 357 | 357 | 357 | 335 | 345 | 415 | 419 | 420 | 386 | 341 | 347 | 412 | 415 | 413 | 409 | 0 | [8 empty] | 0 | 6490800
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 400 | 400 | 400 | 400 | 400 | 400 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 380 | 390 | 390 |  | 390 | 390 | 390 | 390 | 300 | 300 | 40 | 9090455
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 71 | 35 | 34 | 28 | 27 | 27 | 27 | 27 | 33 | 33 | 33 |  | 55 | 55 | 73 | 73 | 74 | 75 | 72 | 1258560
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 12 | 24 | 33 | 40 | 41 | 27 | 32 | 26 | 15 | 5 | 0 | [8 empty] | 266910
44 | Fenchugonj CCPP Phase-1 | 35 | 34 | 34 | 35 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 825000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 968400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | [13 empty] | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 668352
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 210 | 210 | 210 | 211 | 211 | 212 | 211 | 212 | 213 | 212 | 210 | 206 | 206 | 206 | 206 | 207 | 209 |  | 209 | 209 | 212 | 212 | 212 | 212 | 209 | 5251530
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | [13 empty] | 10 | 20 | 16 | 15 | 15 | 15 | 15 | 186000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 192420
54 | Hobiganj 11 MW PP Cofidence-E | [19 empty] | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 34512
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 8 | 16 | 16 | 361488
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 285 | 295 | 295 | 290 | 290 | 185 | 320 | 310 | 270 | 285 | 300 | 315 | 290 | 300 | 290 | 300 | 290 |  | 315 | 285 | 275 | 300 | 285 | 300 | 295 | 7137000
| Bibiyana South 400 MW | 310 | 310 | 300 | 290 | 290 | 292 | 292 | 355 | 340 | 300 | 300 | 300 | 300 | 300 | 300 | 340 | 300 | 305 |  | 322 | 340 | 340 | 340 | 380 | 335 | 330 | 7676800
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 | 0 |  |  |  | 0 | 39536
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 2 | 3 | 5 | 6 | 6 | 6 | 6 | 40080
60 | Barabkunda 22 MW PP (Regent) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 182112
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 86 | 78 | 78 | 74 | 76 | 82 | 80 | 92 | 94 | 100 | 100 | 108 | 108 | 112 | 112 | 106 | 100 | 112 |  | 108 | 100 | 102 | 108 | 96 | 100 | 88 | 2263680
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 38 | 37 | 8 | 5 | 3 | 3 | 2 | 0 | 0 | 0 | 0 | 5 | 9 |  | 13 | 14 | 15 | 35 | 37 | 39 | 33 | 485760
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 212400
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817700
68 | Cumilla 25 MW PP (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 266110
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 456000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524160
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 730100
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 15 |  | 15 | 15 | 15 | 15 | 15 | 16 | 28 | 452400
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | [7 empty] | 0 | 184000
| Feni Lanka Power | [6 empty] | 59 | 98 | 98 | 98 | 98 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 105 | 60 | 52 | 1544700
| Chowmuhani 113 MW | [7 empty] | 5 | 9 | 9 | 22 | 27 | 29 | 30 | 28 | 38 | 38 | 53 |  | 66 | 66 | 69 | 69 | 68 | 68 | 47 | 688800
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 17 | 35 | 17 | 17 | 17 | 17 |  | 35 | 17 | 0 |  |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 2 | 17 | 17 | 21 | 26 | 26 | 26 | 26 | 26 | 17 | 9 | 27 |  | 34 | 34 | 34 | 0 |  |  | 0 | 300480
78 | Gazipur 52 MW PP | [6 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 196320
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 82 | 149 |  | 149 | 149 | 149 | 149 | 48 | 48 | 48 | 1538880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 0 |  |  |  |  | 3 | 8 | 8 | 8 | 8 | 0 | 3 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 146842
| Gazipur 100 MW PP | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | 105 | 105 | 105 | 105 | 70 | 17 | 786240
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 27723
| Jodiac Power | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [9 empty] | 0 | 128996
| Karnaphuli Power Ltd. | 17 | 17 | 0 |  |  |  | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 352108
82 | Madanganj 102 PP(Summit) | [6 empty] | 2 | 44 | 65 | 65 | 65 | 78 | 82 | 80 | 80 | 54 | 17 | 32 |  | 80 | 80 | 80 | 80 | 80 | 65 | 65 | 1043056
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [7 empty] | 14 | 25 | 25 | 25 | 34 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 37 | 30 | 0 | 495104
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 1 | 8 | 9 | 11 | 30 | 34 | 33 | 34 | 34 | 23 | 8 | 26 |  | 31 | 34 | 34 | 14 | 8 |  | 0 | 336000
| Meghnaghat 104 MW PP (OPCL) | 0 | 9 | 17 | 0 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 286080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [6 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  | 0 | 353880
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 0 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 143568
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1230959
94 | Gagnagar 102 MW PP (Digital Power) | [6 empty] | 8 | 33 | 33 | 33 | 33 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 82 | 82 | 82 | 8 | 8 | 8 | 8 | 592560
95 | Patenga 50MW PP (Baraka) | 6 | 0 |  |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 14 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 200160
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 30 | 30 | 30 | 15 | 15 | 15 | 0 | 230326
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 | 0 |  |  | 0 | 39929
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 140 | 163 | 163 | 163 | 163 | 3616854
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 13300
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 17 | 17 | [12 empty] | 0 | 38880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 18 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 204000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 6 | 17 | 17 | 20 | 65 | 62 | 63 | 19 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 559296
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 0 |  |  |  |  | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 473280
116 | Chandpur 200 MW (Desh energy) | 17 | 0 |  |  |  |  | 18 | 17 | 17 | 17 | 17 | 32 | 28 | 19 | 35 | 22 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 393120
117 | Ashuganj 150 MW PP (Midland) | 8 | 6 | 0 |  |  |  | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 11 |  | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 252581
118 | Bibiyana-III 400 MW CCPP | 367 | 365 | 362 | 364 | 364 | 335 | 390 | 374 | 362 | 253 | 253 | 253 | 253 | 253 | 253 | 253 | 252 | 252 |  | 295 | 322 | 326 | 364 | 410 | 346 | 364 | 7661000
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 2 | 56 | 56 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 59 | 69 |  | 69 | 69 | 69 | 69 | 9 | 9 | 9 | 991200
| Anwara 300 MW PP (United) | [6 empty] | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 171 | 268 | 279 |  | 240 | 226 | 226 | 16 | 0 |  | 0 | 1324800
| Juldah unit-2 (Acorn) | 25 | 0 |  |  |  |  | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 469440
| Anlima Energy Ltd. | 17 | 0 |  |  |  |  | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 337473
| Bhairob 54.5 MW | [14 empty] | 6 | 17 | 11 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 167760
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 7 | 14 | 22 | 27 | 29 | 28 | 24 | 12 | 8 | 3 | [9 empty] | 178741
| Chandpur 115(Doreen) | [12 empty] | 12 | 17 | 18 | 18 | 24 | 42 |  | 42 | 42 | 41 | 20 | 19 | 18 | 0 | 274560
| Kanchan Purbachal Power Generation Ltd. | [12 empty] | 5 | 17 | 17 | 17 | [9 empty] | 0 | 61200
| Mirsharai 150 MW (Oil) | [6 empty] | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 17 | 17 | 17 | 17 | 145 |  | 145 | 145 | 145 | 17 | 17 | 17 | 17 | 685818
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 2 | 0 | 4 | 5 | 5 | 3 | 1 | 3 | 0 | 2 | 3 | 6 | 20 | 20 | 14 | 6 | 6 |  | 9 | 9 | 12 | 6 | 1 | 0 | 0 | 122880
| Matarbari 2*600 MW (CPGCL) | 159 | 157 | 158 | 157 | 158 | 159 | 157 | 159 | 156 | 158 | 158 | 157 | 157 | 158 | 158 | 158 | 157 | 157 |  | 156 | 158 | 156 | 157 | 157 | 158 | 158 | 3832727
120 | Eastern Zone Total | 4799 | 4535 | 4496 | 4472 | 4405 | 4452 | 4887 | 5427 | 5467 | 5323 | 5494 | 5694 | 5764 | 5515 | 5498 | 5606 | 5223 | 5760 |  | 5990 | 5899 | 5947 | 5687 | 5416 | 5126 | 4679 | 127853923
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 11 | 19 | 45 |  | 53 | 46 | 44 | 32 | 0 |  |  | 186720
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  | 25 |  | 38 | 36 | 42 | 55 | 0 |  | 0 | 355680
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 21 | 44 | 65 | 77 | 82 | 74 | 50 | 51 | 29 | 10 | 0 | [8 empty] | 516960
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [7 empty] | 12 | 17 | 35 | 17 | 35 | 17 | 17 | 17 | 0 |  | 12 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 248400
133 | Bhola Nutan Biddut BD LTD (GAS) | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 220 |  | 220 | 220 | 190 | 190 | 190 | 180 | 220 | 4758491
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 98208
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 250 | 289 | 307 | 307 | 282 | 250 | 200 | 200 | 150 | 150 | 161 |  | 307 | 280 | 250 | 248 | 150 | 150 | 150 | 4843600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 |  | 60 | 60 | 60 | 60 | 60 | 70 | 70 | 1227000
140 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 3 | 5 | 5 | 4 | 4 | 4 | 5 |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 132242
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 5 |  | 43 | 59 | 52 | 55 | 0 |  |  | 141312
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 473 | 473 | 473 | 473 | 473 | 473 | 405 | 191 | 192 | 191 | 332 | 472 | 473 | 473 | 473 | 618 | 667 | 726 |  | 619 | 624 | 624 | 623 | 907 | 907 | 907 | 12542545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1000 | 980 | 900 | 800 | 790 | 820 | 920 | 1130 | 1202 | 1210 | 1210 | 1244 | 1244 | 1244 | 1244 | 1120 | 1120 | 1100 |  | 1200 | 1200 | 1160 | 1160 | 1100 | 1060 | 1040 | 27959100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4120600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [16 empty] | 24 | 24 |  | 24 | 24 | 24 | 24 | 0 |  |  | 125474
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 0 | 4 | 3 | 1 | 0 | [9 empty] | 26640
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 188 | 220 | 220 | 216 | 209 | 197 | 185 | 181 | 160 | 160 | 168 |  | 179 | 180 | 180 | 180 | 176 | 169 | 150 | 4642455
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 300 | 300 | 300 | 300 | 350 | 414 | 414 | 414 | 320 | 320 | 400 | 414 | 320 | 320 | 320 | 320 | 414 |  | 414 | 360 | 360 | 414 | 414 | 414 | 414 | 8805236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 13 | 22 | 20 | 0 |  |  | 48808
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 134010
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 21 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 14 | 14 | 28 |  | 28 | 28 | 28 | 28 | 0 |  | 0 | 347560
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 8 | 25 | 34 |  | 34 | 34 | 34 | 34 | 0 |  |  | 409405
167 | Katakhali 50 MW Peaking PP | [10 empty] | 32 |  | 31 | 32 | 32 | 32 | 8 | 40 |  | 50 | 50 | 50 | 50 | 0 |  |  | 303807
168 | Santahar 50 MW Peaking PP | [9 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 |  | 32 | 34 | 34 | 34 | 0 |  |  | 245500
169 | Natore 52 MW PP (Rajlanka) | [8 empty] | 8 | 8 | 8 | [8 empty] | 8 | 8 | 8 | 8 | 0 |  | 0 | 50813
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 30 | 50 | 50 | 50 | 57 | 48 | 48 | 48 | 88 |  | 90 | 90 | 90 | 90 | 0 |  | 0 | 797480
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 4 | 35 | 35 | 35 | 35 | 35 | 35 | [11 empty] | 0 | 262464
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 2 | 55 |  | 55 | 55 | 55 | 55 | 0 |  | 0 | 218880
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 30 | 40 |  | 42 | 42 | 42 | 35 | 0 |  | 0 | 249484
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 2 | 3 | 5 | 6 | 5 | 5 | 4 | 2 | 1 | [9 empty] | 35982
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 17 | 36 | 72 |  | 75 | 75 | 75 | 74 | 0 |  | 0 | 332160
| Intraco Solar 30 MW | [6 empty] | 1 | 7 | 15 | 24 | 25 | 34 | 30 | 29 | 23 | 14 | 6 | 0 | [8 empty] | 203356
| Adani Power Jharkhanda Ltd | 1137 | 1090 | 1006 | 912 | 920 | 918 | 1060 | 1234 | 1273 | 1314 | 1315 | 1318 | 1257 | 1252 | 1272 | 1155 | 1159 | 1225 |  | 1412 | 1413 | 1368 | 1370 | 1325 | 1302 | 1274 | 28947300
178 | Teesta Solar Limited | [6 empty] | 6 | 40 | 87 | 127 | 156 | 177 | 169 | 155 | 121 | 72 | 29 | [9 empty] | 1111250