## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-02-20 | Tuesday
|  | Date (day): | 2024-02-20 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11789.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12297 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-19 | 2024-02-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 190 | 190 | 190
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 300 | 300 |  |  | ST synchronized process
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  |  | Line S/D
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 9 | 50 | 75 | 25 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 76 | 80 | 80 | 80 |  | 22 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 25 | 14 | 36 | 39 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 100 | 102 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 25 | 17 | 60 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 280 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 58 | 80 | 82 |  | 20 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 0 | 0 | 0 | 54 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 149 | 64 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 39 | 39 | 39 |  | 41 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 24 | 24 | 24
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 132 | 195 | 95 | 205 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 36 | 100 | 17 | 132 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 17 | 35 | 127 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 250 | 65 | 230 | 230 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 187 | 388 | 390 | 390 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1563 | 1867 | 2305 | 2387 | 1695 | 1033
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 15 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 211 | 210 | 210
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 42 | 56 | 19 | 50 | 48 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 68 | 51 | 68 | 34 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 8 | 8 | 8 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 14 | 10 | 15
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 66 | 96 | 15 | 120 | 180 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 17 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 145 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 341 | 315 | 350 | 355 | 869 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 16 | 8 | 20 | 29 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 156 | 157 | 150 | 150 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1150 | 1278 | 1072 | 1352 | 2225 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 290 | 300 | 320 | 40 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 395 | 393 | 350 | 360 | 40 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 44 | 44 | 47 | 45
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 53 | 52 | 40 | 40 | 15 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 102 | 167 | 167 | 28 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 26 | 13 | 25 | 125 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 40 | 40 | 40 |  | 12 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 34 | 34 | 34 | 166 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 16 | 16 |  | 6 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 9 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 104 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 34 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 9 | 15 | 15 |  | 10 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 88 | 88 | 98 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 34 | 69 | 38 | 68 | 45 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 1 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 37 | 0 | 42 | 73 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1272 | 1398 | 1405 | 1546 | 576 | 809
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 32 | 44 | 65 | 137 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9 | 9 | 191 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 57 | 69 | 46 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 142 | 116 | 161.6 | 149 | 137 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 35 | 35 | 35 | 35 |  | 35 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 5 | 5 | 5 | 45 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 28 | 28 | 28 |  | 33 | GT-9 Under maint.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 209 | 208 | 210 | 210 |  | 21 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 15 | 15 | 5 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 17 | 17 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 310 | 315 | 315 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 315 | 410 | 400 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 380 | 400 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1532 | 1649 | 1618 | 1638 | 109 | 569
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 902 | 667 | 921 | 632
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 0 | 53 | 1
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 73 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 36 | 17 | 50 | 55 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 61 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 330 | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 980 | 803 | 1038 | 805 | 1308 | 369
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 0 | 16 | 94 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 5 | 6 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 40 | 70 | 60 | 60 |  | 134 | ST, GT-1 Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1160 | 1190 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 200 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 17
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 244 | 247 | 250 | 250
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1666 | 1782 | 1754 | 1814 | 94 | 167
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 24 | 24 | 28 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 15 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 152 | 146 | 160 | 180 | 40 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 380 | 414 | 410 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 35 | 15 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 49 | 90 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 35 | 0 | 113 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 36 | 77 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1363 | 1398 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 2053 | 2268 | 2092 | 2319 | 1118 | 92
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 42 | 6 | 42 | 71 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 53 | 0 | 75 | 40 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 162 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 375 | 265 | 344 | 287 | 236 | 189
| Total |  |  |  |  | 26504 | 25481 | 10733 | 11426 | 11789.6 | 12297 | 7498 | 3558
A. |  | 2024-02-19 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11426 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7644 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11600 | MW
3 | Day peak Generation : |  |  | 10733 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11075.09 | MW
4 | Evening peak Generation : |  |  | 11426 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 166 | MW
5 | Total Energy Generation : |  | 235.4199 | MKWHr | By Solar | 2.3588 | MKWHr
| By Gas : | 107.0615 | MKWHr |  | By Oil: | 24.4821 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 79.3253 | MKWHr |  | By Hydro: | 0.95616 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.14064 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7498 | MW | Dhaka | 4208.89 | 4198.89 |  | 10 |  | 18:00 |  | 156.62
|  |  | For Plants S/D or M/C prob = |  |  | 3558 | MW | Chittagong | 1130 | 1130 |  | 0 |  | 19:00 |  | 166.17
|  |  | Total = |  |  | 11056 | MW | Khulna | 1251 | 1251 |  | 0 |  | 19:30 |  | 164.26
7 | Total Gas Supplied : |  |  | 826.86 | MMCFD |  |  | Rajshahi | 1135.2 | 1135.2 |  | 0 |  | 20:00 |  | 160
8 | Fuel Cost : | i) Gas : | Taka | 312708541.51 | ii) Oil : | Taka | 446158428.8 | Comilla | 887 | 887 |  | 0 |  | 21:00 |  | 145
|  | iii) Coal : | Taka | 531596579.94 | Total | Taka | 1290463550.25 | Mymensingh | 1025 | 869 |  | 156 |  | 22:00 |  | 172.855
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 380 | 380 |  | 0 |  | 23:00 |  | 121
| ii) During Peak Demand : |  |  | 1220 | MW (W to E) at | 19:00 | hrs | Barisal | 295 | 295 |  | 0 |  | 24:00 |  | 74
| iii) Maximum : |  |  | 776 | MW at | 7:00 | hrs | Rangpur | 763 | 763 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.2°C |  |  | Total | 11075.09 | 10909.09 |  | 166
B. |  | 2024-02-20 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 30.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12297 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | 597 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 241.0654 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7763 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.8393 | MKWHr. | ii) HVDC Flow at Peak Time |  | 667 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.256 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.11 |  | (b) Today: | 84.99 |  | (c) Rule Curve: |  | 94.34
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-02-19 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 65 | 0 | 335 | 0 | 39 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 28 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 48 | 0 | 0 | 0 | 6 | 8 | 39 | 0 | 0 | 0 | 0 | 260 | 154 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 40 | 0 | 0 | 9 | 33 | 11 | 86 | 74 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 211 | 15 | 0 | 9 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 10 | 365 | 9 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 330 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 260 | 8 | 0 | 340 | 2 | 157 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1213 | 0 | 0 |  | 4281 | 4389 | 8670 | 2947 | 907 | 1208 | 0 | 242 | 3110 | 40 | 0 | 128 | 86 | 0 | 2 | 28.65 | 85.13
2:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 65 | 0 | 335 | 0 | 41 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 30 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 39 | 0 | 0 | 0 | 0 | 280 | 154 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 40 | 0 | 0 | 9 | 33 | 11 | 84 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 211 | 15 | 0 | 9 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 6 | 365 | 9 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 320 | 8 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 340 | 6 | 157 | 0 | 0 |  | 705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1115 | 0 | 0 |  | 4183 | 4082 | 8265 | 2964 | 705 | 1203 | 0 | 221 | 3002 | 40 | 0 | 40 | 84 | 0 | 6 | 0 | 85.13
3:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 55 | 0 | 335 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 30 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | 0 | 0 | 0 | 0 | 300 | 153 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 33 | 11 | 80 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 211 | 15 | 0 | 9 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 340 | 7 | 157 | 0 | 0 |  | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1109 | 0 | 0 |  | 4040 | 3948 | 7988 | 2982 | 672 | 1163 | 0 | 98 | 2946 | 40 | 0 | 0 | 80 | 0 | 7 | 0 | 85.12
4:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 335 | 0 | 42 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 30 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | 0 | 0 | 0 | 0 | 300 | 153 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 33 | 11 | 78 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 130 | 0 | 28 | 0 | 0 | 211 | 15 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 341 | 6 | 158 | 0 | 0 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1020 | 0 | 0 |  | 3929 | 3791 | 7720 | 2943 | 671 | 1110 | 0 | 43 | 2829 | 40 | 0 | 0 | 78 | 0 | 6 | 0 | 85.12
5:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 335 | 0 | 40 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 25 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 33 | 11 | 80 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 130 | 0 | 28 | 0 | 0 | 212 | 15 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 340 | 8 | 157 | 0 | 0 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1017 | 0 | 0 |  | 3853 | 3791 | 7644 | 2867 | 671 | 1111 | 0 | 43 | 2824 | 40 | 0 | 0 | 80 | 0 | 8 | 0 | 85.11
6:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 335 | 0 | 41 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 32 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 37 | 0 | 0 | 0 | 0 | 275 | 0 | 8 | 0 | 41 | 30 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 30 | 11 | 78 | 75 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 15 | 0 | 9 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 2 | 0 | 0 | 347 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 340 | 7 | 156 | 0 | 0 |  | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1018 | 0 | 0 |  | 3977 | 3967 | 7944 | 2915 | 760 | 1218 | 0 | 46 | 2864 | 40 | 0 | 16 | 78 | 0 | 7 | 24.83 | 85.11
7:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 18 | 0 | 335 | 0 | 41 | 13 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 30 | 3 | 0 | 40 | 0 | 0 | 0 | 5 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 8 | 35 | 0 | 0 | 0 | 0 | 335 | 0 | 63 | 0 | 41 | 50 | 0 | 51 | 0 | 0 | 3 | 0 | 9 | 33 | 11 | 86 | 67 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 15 | 0 | 9 | 310 | 16 | 8 | 0 | 7 | 0 | 0 | 9 | 0 | 3 | 2 | 25 | 12 | 1 | 408 | 56 | 17 | 13 | 0 | 16 | 0 | 9 | 70 | 0 | 25 | 400 | 0 | 2 | 0 | 12 | 0 | 0 | 2 | 0 | 0 | 393 | 17 | 0 | 340 | 12 | 159 | 0 | 0 |  | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 3 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1110 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 194 | 1091 | 6 | 0 |  | 4659 | 4230 | 8889 | 3171 | 726 | 1326 | 0 | 415 | 3064 | 40 | 0 | 33 | 86 | 16 | 12 | 58 | 85.1
8:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 17 | 60 | 0 | 335 | 0 | 63 | 8 | 8 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 30 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 3 | 0 | 25 | 0 | 6 | 8 | 12 | 0 | 0 | 0 | 0 | 285 | 0 | 102 | 0 | 44 | 53 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 33 | 11 | 60 | 67 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 16 | 0 | 9 | 325 | 17 | 8 | 0 | 47 | 0 | 0 | 9 | 0 | 17 | 7 | 25 | 17 | 6 | 408 | 56 | 17 | 17 | 1 | 16 | 0 | 17 | 105 | 0 | 25 | 340 | 2 | 12 | 0 | 17 | 0 | 0 | 7 | 0 | 0 | 395 | 17 | 0 | 340 | 13 | 159 | 0 | 0 |  | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 414 | 17 | 0 | 1 | 0 | 6 | 0 | 1 | 0 | 1244 | 220 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 0 | 7 | 307 | 1323 | 40 | 0 |  | 4811 | 4716 | 9527 | 3094 | 630 | 1358 | 0 | 635 | 3543 | 40 | 0 | 59 | 60 | 95 | 13 | 213 | 85.1
9:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 18 | 82 | 0 | 335 | 0 | 105 | 8 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 28 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 66 | 51 | 12 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 0 | 310 | 0 | 148 | 0 | 44 | 55 | 0 | 43 | 0 | 0 | 8 | 0 | 9 | 33 | 11 | 90 | 32 | 0 | 0 | 1 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 212 | 16 | 0 | 9 | 300 | 17 | 8 | 0 | 49 | 0 | 0 | 9 | 0 | 17 | 13 | 25 | 17 | 6 | 372 | 59 | 24 | 17 | 3 | 49 | 4 | 17 | 105 | 0 | 25 | 340 | 14 | 23 | 0 | 17 | 0 | 0 | 8 | 0 | 0 | 395 | 35 | 0 | 341 | 0 | 159 | 0 | 0 |  | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 380 | 17 | 0 | 30 | 0 | 6 | 0 | 2 | 0 | 1244 | 200 | 0 | 17 | 2 | 41 | 0 | 0 | 0 | 0 | 16 | 307 | 1357 | 87 | 0 |  | 5086 | 4782 | 9868 | 3063 | 630 | 1311 | 0 | 760 | 3578 | 40 | 0 | 200 | 90 | 196 | 0 | 269 | 85.09
10:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 17 | 78 | 1 | 335 | 0 | 100 | 22 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 66 | 51 | 25 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 0 | 315 | 0 | 148 | 0 | 44 | 53 | 0 | 43 | 0 | 31 | 8 | 0 | 9 | 25 | 6 | 98 | 32 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 163 | 0 | 30 | 0 | 0 | 211 | 16 | 0 | 9 | 290 | 17 | 8 | 0 | 59 | 0 | 0 | 9 | 0 | 17 | 17 | 25 | 17 | 6 | 375 | 59 | 35 | 17 | 4 | 49 | 17 | 17 | 100 | 9 | 25 | 365 | 17 | 34 | 0 | 17 | 0 | 0 | 22 | 0 | 0 | 395 | 35 | 0 | 340 | 0 | 157 | 0 | 0 |  | 630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 4 | 0 | 1210 | 200 | 0 | 17 | 3 | 60 | 0 | 0 | 0 | 0 | 23 | 250 | 1356 | 128 | 0 |  | 5221 | 4818 | 10039 | 3076 | 630 | 1334 | 0 | 829 | 3483 | 40 | 0 | 252 | 98 | 297 | 0 | 154 | 85.09
11:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 18 | 68 | 15 | 335 | 0 | 102 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 17 | 22 | 33 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 42 | 51 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 102 | 0 | 44 | 52 | 0 | 43 | 0 | 31 | 8 | 0 | 7 | 25 | 6 | 100 | 28 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 163 | 0 | 30 | 0 | 0 | 211 | 16 | 0 | 9 | 305 | 17 | 8 | 0 | 77 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 5 | 375 | 59 | 35 | 17 | 4 | 67 | 17 | 17 | 88 | 18 | 25 | 340 | 17 | 39 | 0 | 17 | 0 | 0 | 26 | 0 | 0 | 395 | 35 | 0 | 341 | 2 | 155 | 120 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 380 | 17 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1200 | 200 | 0 | 17 | 4 | 75 | 0 | 0 | 0 | 0 | 29 | 250 | 1364 | 153 | 0 |  | 5216 | 5121 | 10337 | 2943 | 903 | 1383 | 0 | 879 | 3480 | 40 | 0 | 249 | 100 | 358 | 2 | 156 | 85.08
12:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 17 | 76 | 15 | 335 | 0 | 100 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 22 | 33 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 42 | 51 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 102 | 0 | 44 | 53 | 0 | 43 | 0 | 40 | 16 | 0 | 7 | 34 | 6 | 106 | 28 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 163 | 0 | 30 | 0 | 0 | 209 | 16 | 0 | 9 | 285 | 17 | 8 | 0 | 80 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 6 | 315 | 59 | 35 | 17 | 4 | 66 | 17 | 17 | 88 | 34 | 25 | 400 | 17 | 44 | 17 | 17 | 0 | 1 | 29 | 0 | 0 | 395 | 35 | 0 | 341 | 16 | 156 | 250 | 187 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 380 | 17 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1160 | 200 | 0 | 17 | 4 | 61 | 0 | 0 | 0 | 0 | 31 | 244 | 1363 | 162 | 0 |  | 5659 | 5074 | 10733 | 2969 | 902 | 1682 | 0 | 956 | 3434 | 40 | 0 | 265 | 106 | 363 | 16 | 159 | 85.08
13:00 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 82 | 15 | 335 | 0 | 101 | 25 | 24 | 48 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 0 | 44 | 50 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 44 | 55 | 0 | 43 | 0 | 40 | 16 | 0 | 7 | 33 | 9 | 106 | 28 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 163 | 0 | 30 | 0 | 0 | 206 | 16 | 0 | 9 | 300 | 17 | 8 | 0 | 82 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 23 | 6 | 388 | 59 | 35 | 17 | 4 | 66 | 17 | 17 | 88 | 38 | 25 | 400 | 17 | 42 | 17 | 17 | 0 | 17 | 29 | 15 | 0 | 395 | 35 | 0 | 341 | 11 | 160 | 250 | 187 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1110 | 200 | 0 | 17 | 2 | 62 | 0 | 0 | 0 | 0 | 30 | 200 | 1348 | 152 | 0 |  | 5728 | 4981 | 10709 | 3029 | 903 | 1704 | 0 | 972 | 3329 | 40 | 0 | 266 | 106 | 349 | 11 | 202 | 85.07
14:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 80 | 15 | 332 | 0 | 100 | 15 | 24 | 48 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 40 | 50 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 41 | 54 | 0 | 35 | 0 | 40 | 8 | 0 | 7 | 33 | 9 | 110 | 28 | 0 | 0 | 1 | 35 | 40 | 0 | 5 | 163 | 0 | 30 | 0 | 0 | 206 | 12 | 0 | 8 | 280 | 17 | 8 | 0 | 51 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 17 | 6 | 414 | 59 | 35 | 17 | 4 | 66 | 17 | 17 | 88 | 38 | 25 | 340 | 17 | 38 | 17 | 17 | 0 | 17 | 23 | 18 | 0 | 395 | 17 | 0 | 341 | 17 | 160 | 200 | 187 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 300 | 17 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 1170 | 200 | 0 | 17 | 4 | 66 | 0 | 0 | 0 | 0 | 26 | 200 | 1359 | 128 | 0 |  | 5523 | 4914 | 10437 | 2985 | 902 | 1509 | 0 | 932 | 3400 | 40 | 0 | 247 | 110 | 295 | 17 | 251.165 | 85.08
15:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 80 | 15 | 330 | 0 | 97 | 10 | 24 | 48 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 40 | 48 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 44 | 54 | 0 | 35 | 0 | 40 | 8 | 0 | 7 | 33 | 9 | 106 | 29 | 0 | 0 | 1 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 206 | 12 | 0 | 8 | 285 | 0 | 8 | 0 | 50 | 0 | 0 | 9 | 0 | 17 | 14 | 25 | 17 | 6 | 352 | 59 | 35 | 17 | 3 | 66 | 17 | 17 | 88 | 39 | 25 | 340 | 17 | 26 | 17 | 17 | 0 | 17 | 15 | 18 | 0 | 360 | 17 | 0 | 341 | 0 | 158 | 100 | 288 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 300 | 17 | 0 | 35 | 0 | 6 | 0 | 4 | 0 | 1160 | 180 | 0 | 17 | 3 | 37 | 0 | 0 | 0 | 0 | 19 | 200 | 1276 | 95 | 0 |  | 5307 | 4737 | 10044 | 2849 | 902 | 1452 | 0 | 921 | 3305 | 40 | 0 | 252 | 106 | 217 | 0 | 282.68 | 85.06
16:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 80 | 15 | 330 | 0 | 100 | 10 | 24 | 48 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 1 | 213 | 0 | 0 | 0 |  | 0 | 40 | 50 | 25 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 43 | 54 | 0 | 35 | 0 | 40 | 8 | 0 | 7 | 33 | 9 | 104 | 30 | 0 | 0 | 1 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 206 | 12 | 0 | 8 | 300 | 0 | 8 | 0 | 57 | 0 | 0 | 9 | 0 | 17 | 8 | 25 | 17 | 6 | 315 | 59 | 35 | 17 | 1 | 66 | 0 | 17 | 73 | 39 | 25 | 340 | 17 | 14 | 17 | 17 | 0 | 17 | 6 | 18 | 0 | 393 | 17 | 0 | 340 | 0 | 160 | 70 | 290 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 49 | 28 | 34 | 0 | 0 | 21 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 300 | 28 | 0 | 0 | 0 | 6 | 0 | 3 | 35 | 1160 | 180 | 0 | 17 | 1 | 24 | 10 | 0 | 0 | 0 | 10 | 200 | 1270 | 53 | 0 |  | 5250 | 4716 | 9966 | 2848 | 902 | 1439 | 0 | 928 | 3300 | 40 | 0 | 284 | 104 | 121 | 0 | 175.72 | 85.06
17:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 70 | 15 | 280 | 0 | 39 | 17 | 24 | 82 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 1 | 40 | 51 | 25 | 0 | 13 | 8 | 4 | 0 | 0 | 0 | 0 | 280 | 0 | 73 | 0 | 44 | 53 | 0 | 35 | 0 | 40 | 0 | 0 | 7 | 33 | 9 | 104 | 31 | 0 | 0 | 1 | 35 | 40 | 0 | 5 | 120 | 0 | 27 | 0 | 0 | 206 | 12 | 0 | 8 | 295 | 17 | 8 | 0 | 50 | 0 | 0 | 9 | 0 | 20 | 2 | 25 | 24 | 6 | 315 | 59 | 35 | 17 | 0 | 66 | 0 | 17 | 88 | 39 | 25 | 340 | 17 | 4 | 17 | 17 | 0 | 17 | 2 | 19 | 5 | 393 | 17 | 0 | 340 | 0 | 155 | 65 | 288 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 40 | 3 | 32 | 0 | 0 | 0 | 0 | 4 | 49 | 28 | 34 | 0 | 0 | 22 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 350 | 35 | 0 | 0 | 0 | 33 | 0 | 1 | 35 | 1080 | 180 | 0 | 17 | 0 | 10 | 36 | 0 | 0 | 0 | 3 | 150 | 1262 | 16 | 0 |  | 5184 | 4695 | 9879 | 2754 | 903 | 1479 | 0 | 1048 | 3157 | 40 | 0 | 355 | 104 | 39 | 0 | 115.555 | 85.05
18:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 8 | 80 | 15 | 280 | 0 | 40 | 17 | 24 | 133 | 31 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 1 | 211 | 0 | 0 | 0 |  | 6 | 56 | 65 | 25 | 0 | 19 | 8 | 10 | 0 | 0 | 0 | 0 | 300 | 0 | 73 | 0 | 44 | 54 | 0 | 35 | 0 | 40 | 1 | 0 | 9 | 33 | 9 | 110 | 32 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 205 | 12 | 0 | 9 | 280 | 17 | 8 | 0 | 100 | 0 | 0 | 9 | 0 | 34 | 0 | 25 | 34 | 11 | 335 | 69 | 105 | 17 | 0 | 90 | 0 | 17 | 88 | 57 | 25 | 385 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 340 | 145 | 0 | 315 | 0 | 158 | 68 | 288 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 57 | 0 | 40 | 6 | 32 | 0 | 0 | 0 | 24 | 14 | 84 | 28 | 34 | 8 | 8 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 350 | 36 | 0 | 0 | 0 | 40 | 0 | 0 | 35 | 1060 | 180 | 0 | 17 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 150 | 1269 | 0 | 0 |  | 5681 | 4805 | 10486 | 2789 | 903 | 1478 | 0 | 1363 | 3122 | 40 | 0 | 681 | 110 | 0 | 0 | 156.62 | 85.05
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 80 | 15 | 280 | 0 | 102 | 17 | 58 | 149 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 15 | 211 | 0 | 0 | 0 |  | 6 | 56 | 68 | 25 | 0 | 19 | 8 | 14 | 0 | 0 | 0 | 0 | 290 | 0 | 102 | 0 | 44 | 52 | 0 | 43 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 104 | 32 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 208 | 16 | 0 | 9 | 310 | 17 | 8 | 0 | 132 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 34 | 26 | 410 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 88 | 69 | 25 | 400 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 37 | 17 | 393 | 145 | 0 | 315 | 8 | 157 | 65 | 388 |  | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 73 | 0 | 70 | 6 | 32 | 0 | 0 | 0 | 25 | 15 | 90 | 28 | 34 | 33 | 8 | 37 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 36 | 0 | 0 | 0 | 42 | 0 | 0 | 35 | 1190 | 220 | 0 | 17 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 247 | 1398 | 0 | 0 |  | 6308 | 5118 | 11426 | 3080 | 667 | 1791 | 0 | 1501 | 3477 | 40 | 0 | 758 | 104 | 0 | 8 | 166.17 | 85.03
19:30 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 80 | 15 | 260 | 0 | 60 | 17 | 58 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 56 | 68 | 25 | 0 | 19 | 8 | 14 | 0 | 0 | 0 | 0 | 275 | 0 | 102 | 0 | 44 | 52 | 0 | 43 | 0 | 42 | 8 | 0 | 9 | 33 | 9 | 108 | 34 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 208 | 20 | 0 | 10 | 260 | 17 | 8 | 0 | 132 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 34 | 26 | 408 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 88 | 69 | 25 | 400 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 393 | 145 | 0 | 360 | 6 | 156 | 65 | 400 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 67 | 0 | 40 | 6 | 32 | 0 | 0 | 0 | 25 | 15 | 90 | 28 | 34 | 43 | 8 | 37 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 37 | 0 | 0 | 0 | 42 | 0 | 0 | 35 | 1244 | 220 | 0 | 17 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 250 | 1367 | 0 | 0 |  | 6211 | 5067 | 11278 | 2947 | 618 | 1754 | 0 | 1499 | 3547 | 40 | 0 | 759 | 108 | 0 | 6 | 164.26 | 0
20:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 124 | 0 |  | 0 | 0 | 0 | 0 | 80 | 15 | 260 | 0 | 39 | 14 | 58 | 149 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 56 | 68 | 0 | 0 | 19 | 8 | 18 | 0 | 0 | 0 | 0 | 265 | 0 | 102 | 0 | 44 | 54 | 0 | 51 | 0 | 49 | 8 | 0 | 9 | 33 | 9 | 104 | 43 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 130 | 0 | 28 | 0 | 0 | 208 | 18 | 0 | 10 | 270 | 17 | 5 | 0 | 130 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 34 | 26 | 409 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 88 | 68 | 25 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 393 | 125 | 0 | 340 | 5 | 155 | 65 | 390 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 70 | 0 | 40 | 7 | 32 | 0 | 0 | 0 | 25 | 15 | 90 | 0 | 34 | 50 | 8 | 37 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 360 | 37 | 0 | 0 | 0 | 42 | 0 | 0 | 35 | 1160 | 220 | 0 | 17 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 250 | 1370 | 0 | 0 |  | 6157 | 4915 | 11072 | 3045 | 618 | 1682 | 0 | 1377 | 3445 | 40 | 0 | 756 | 104 | 0 | 5 | 160 | 85.04
21:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 188 | 0 |  | 0 | 0 | 0 | 0 | 80 | 15 | 335 | 0 | 40 | 0 | 58 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 64 | 68 | 0 | 0 | 19 | 8 | 31 | 0 | 0 | 0 | 0 | 255 | 0 | 55 | 0 | 44 | 55 | 0 | 51 | 0 | 49 | 8 | 0 | 9 | 33 | 9 | 106 | 43 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 208 | 18 | 0 | 10 | 295 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 26 | 410 | 59 | 105 | 17 | 0 | 83 | 0 | 17 | 88 | 69 | 25 | 400 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 393 | 17 | 0 | 335 | 3 | 157 | 99 | 200 |  | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 59 | 0 | 40 | 7 | 32 | 0 | 0 | 0 | 25 | 9 | 90 | 0 | 34 | 50 | 8 | 37 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 360 | 37 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1110 | 221 | 0 | 17 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 250 | 1330 | 0 | 0 |  | 5961 | 4803 | 10764 | 3171 | 619 | 1552 | 0 | 1282 | 3352 | 40 | 0 | 639 | 106 | 0 | 3 | 145 | 85.03
22:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 78 | 15 | 335 | 0 | 39 | 0 | 58 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 22 | 17 | 0 | 35 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 56 | 68 | 0 | 0 | 19 | 8 | 31 | 0 | 0 | 0 | 0 | 260 | 0 | 55 | 0 | 47 | 55 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 100 | 43 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 208 | 18 | 0 | 10 | 280 | 17 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 26 | 410 | 9 | 105 | 17 | 0 | 16 | 0 | 17 | 98 | 69 | 25 | 400 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 20 | 0 | 350 | 17 | 0 | 282 | 4 | 157 | 128 | 150 |  | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 43 | 0 | 40 | 7 | 32 | 0 | 0 | 0 | 25 | 5 | 90 | 0 | 8 | 50 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 300 | 37 | 0 | 0 | 0 | 6 | 0 | 0 | 35 | 1000 | 220 | 0 | 17 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 223 | 1249 | 0 | 0 |  | 5579 | 4640 | 10219 | 3150 | 824 | 1455 | 0 | 1009 | 3081 | 35 | 0 | 561 | 100 | 0 | 4 | 172.855 | 85.03
23:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 10 | 15 | 335 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 23 | 17 | 0 | 35 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 6 | 64 | 68 | 0 | 0 | 19 | 8 | 39 | 0 | 0 | 0 | 0 | 335 | 0 | 55 | 0 | 47 | 55 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 96 | 37 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 212 | 18 | 0 | 10 | 300 | 17 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 26 | 0 | 25 | 34 | 26 | 406 | 9 | 105 | 17 | 0 | 16 | 0 | 17 | 98 | 65 | 25 | 380 | 16 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 340 | 17 | 0 | 274 | 4 | 158 | 130 | 150 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 220 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 150 | 1214 | 0 | 0 |  | 5345 | 4298 | 9643 | 3113 | 903 | 1492 | 0 | 722 | 2926 | 35 | 0 | 352 | 96 | 0 | 4 | 121 | 85.03
24:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 33 | 23 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 211 | 0 | 0 | 0 |  | 6 | 64 | 68 | 0 | 0 | 6 | 8 | 39 | 0 | 0 | 0 | 0 | 300 | 0 | 55 | 0 | 47 | 55 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 90 | 74 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 210 | 18 | 0 | 10 | 305 | 17 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 18 | 0 | 25 | 34 | 26 | 358 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 98 | 41 | 25 | 340 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 17 | 0 | 278 | 0 | 155 | 130 | 150 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1211 | 0 | 0 |  | 5074 | 4178 | 9252 | 3011 | 903 | 1604 | 0 | 458 | 2914 | 35 | 0 | 237 | 90 | 0 | 0 | 74 | 85.02
KWH | 0 | 0 | 3656562 | 0 | 0 | 0 | 0 | 846000 | 0 |  | 0 | 0 | 0 | 158400 | 1319788 | 220738 | 7828158 | 0 | 1581000 | 204480 | 595008 | 1356480 | 191002 | 0 | 0 | 0 | 52560 | 40199 | 38823 | 0 | 456000 | 518760 | 746300 | 622800 | 200640 | 0 | 956160 | 0 | 0 | 0 | 162460 | 4945284 | 0 | 0 | 0 |  | 44880 | 848736 | 928465 | 281880 | 0 | 210240 | 171696 | 500160 | 0 | 0 | 0 | 0 | 7089000 | 772000 | 1472000 | 0 | 1038456 | 1090560 | 0 | 1092315 | 0 | 672400 | 164966 | 0 | 216720 | 801500 | 224160 | 2256000 | 1119360 | 0 | 0 | 11500 | 822000 | 954600 | 0 | 158400 | 3829500 | 0 | 680160 | 0 | 0 | 5256960 | 370000 | 0 | 206100 | 7249000 | 369552 | 160320 | 0 | 1344873 | 0 | 0 | 213600 | 0 | 446688 | 112320 | 490560 | 498240 | 260945 | 8894000 | 1004400 | 976320 | 350436 | 29039 | 968509 | 129824 | 357125 | 1618800 | 708120 | 485760 | 8633500 | 288000 | 277810 | 194400 | 355036 | 0 | 191880 | 172448 | 275520 | 67320 | 8592500 | 762763 | 0 | 7936363 | 140640 | 3832727 | 1622727 | 2963709 |  | 18839272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124320 | 315648 | 0 | 1139000 | 131852 | 206784 | 0 | 0 | 0 | 153461 | 62118 | 892776 | 329820 | 491038 | 158940 | 49114 | 212892 | 0 | 0 | 146070 | 0 | 0 | 4172600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3930236 | 0 | 9193309 | 414720 | 0 | 263520 | 0 | 259526 | 0 | 36529 | 252768 | 28599100 | 4969255 | 0 | 254400 | 28860 | 473040 | 359040 | 0 | 0 | 0 | 193614 | 4843600 | 29940951 | 1023630 | 0 |  | 122958090 | 112461803 | 235419893 | 72582654 | 18839272 | 34478887 | 0 | 17993150 | 79325341 | 956160 | 0 | 6488999 | 2256000 | 2358790 | 140640 | 0
Fuel Cost | 0 | 0 | 15686650.98 | 0 | 0 | 0 | 0 | 2436480 | 0 |  | 0 | 0 | 0 | 3065040 | 27530777.68 | 3794486.22 | 23875881.9 | 0 | 8458350 | 3940329.6 | 11067148.8 | 24986361.6 | 3466686.3 | 0 | 0 | 0 | 959745.6 | 642782.01 | 710072.67 | 0 | 342000 | 0 | 0 | 0 | 3593462.4 | 0 | 0 | 0 | 0 | 0 | 3076992.4 | 15775455.96 | 0 | 0 | 0 |  | 788092.8 | 14946240.96 | 16628808.15 | 5223236.4 | 0 | 3460550.4 | 638709.12 | 0 | 0 | 0 | 0 | 0 | 21692340 | 2563040 | 4931200 | 0 | 3499596.72 | 4776652.8 | 0 | 4380183.15 | 0 | 12042684 | 2969388 | 0 | 162540 | 2981580 | 168120 | 14799360 | 3481209.6 | 0 | 0 | 0 | 3205800 | 3560658 | 0 | 720720 | 13096890 | 0 | 3774888 | 0 | 0 | 14666918.4 | 2434600 | 0 | 824400 | 22399410 | 277164 | 121843.2 | 0 | 27771627.45 | 0 | 0 | 4079760 | 0 | 7968913.92 | 0 | 8471971.2 | 8769024 | 4394313.8 | 23569100 | 14875164 | 17573760 | 6080064.6 | 0 | 17956156.86 | 2534164.48 | 5692572.5 | 29688792 | 13121463.6 | 8651385.6 | 22965110 | 4815360 | 0 | 3555576 | 6035612 | 0 | 3355981.2 | 0 | 4559856 | 1152518.4 | 25519725 | 13645830.07 | 0 | 55316450.11 | 0 | 22613089.3 | 0 | 0 |  | 55387459.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2338459.2 | 5937338.88 | 0 | 3599240 | 624978.48 | 3564956.16 | 0 | 0 | 0 | 2748486.51 | 1139865.3 | 15007564.56 | 7018569.6 | 9359184.28 | 2846615.4 | 868826.66 | 3812895.72 | 0 | 0 | 110574.99 | 0 | 0 | 35216744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13087685.88 | 0 | 26844462.28 | 7514726.4 | 0 | 5254588.8 | 0 | 5213877.34 | 0 | 0 | 4888533.12 | 171880591 | 15454383.05 | 0 | 4922640 | 0 | 0 | 6078547.2 | 0 | 0 | 0 | 0 | 36084820 | 210484885.53 | 0 | 0 |  | 703358869.91 | 657291500.02 | 1360650369.93 | 218655261.75 | 55387459.68 | 94053279.76 | 0 | 330077278.45 | 531596579.94 | 0 | 0 | 116081150.35 | 14799360 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 17 | 76 | 15 | 335 | 0 | 100 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 22 | 33 | 26 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 42 | 51 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 102 | 0 | 44 | 53 | 0 | 43 | 0 | 40 | 16 | 0 | 7 | 34 | 6 | 106 | 28 | 0 | 0 | 2 | 35 | 40 | 0 | 5 | 163 | 0 | 30 | 0 | 0 | 209 | 16 | 0 | 9 | 285 | 17 | 8 | 0 | 80 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 17 | 6 | 315 | 59 | 35 | 17 | 4 | 66 | 17 | 17 | 88 | 34 | 25 | 400 | 17 | 44 | 17 | 17 | 0 | 1 | 29 | 0 | 0 | 395 | 35 | 0 | 341 | 16 | 156 | 250 | 187 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 380 | 17 | 0 | 35 | 0 | 6 | 0 | 6 | 0 | 1160 | 200 | 0 | 17 | 4 | 61 | 0 | 0 | 0 | 0 | 31 | 244 | 1363 | 162 | 0 |  | 10733 | DayPeak
Yesterday Evening Peak | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 9 | 80 | 15 | 280 | 0 | 102 | 17 | 58 | 149 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 15 | 211 | 0 | 0 | 0 | 0 | 6 | 56 | 68 | 25 | 0 | 19 | 8 | 14 | 0 | 0 | 0 | 0 | 290 | 0 | 102 | 0 | 44 | 52 | 0 | 43 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 104 | 32 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 208 | 16 | 0 | 9 | 310 | 17 | 8 | 0 | 132 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 34 | 26 | 410 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 88 | 69 | 25 | 400 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 37 | 17 | 393 | 145 | 0 | 315 | 8 | 157 | 65 | 388 |  | 667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 73 | 0 | 70 | 6 | 32 | 0 | 0 | 0 | 25 | 15 | 90 | 28 | 34 | 33 | 8 | 37 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 414 | 36 | 0 | 0 | 0 | 42 | 0 | 0 | 35 | 1190 | 220 | 0 | 17 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 247 | 1398 | 0 | 0 |  | 11426 | EvPeak
Forecast for Evening | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 300 | 0 |  | 0 | 0 | 0 | 75 | 80 | 15 | 335 | 0 | 0 | 60 | 82 | 149 | 36 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 17 | 22 | 33 | 24 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 50 | 68 | 25 | 0 | 19 | 8 | 15 | 0 | 0 | 0 | 0 | 320 | 0 | 167 | 0 | 45 | 40 | 0 | 51 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 141 | 65 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 210 | 15 | 0 | 10 | 315 | 17 | 0 | 0 | 95 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 25 | 400 | 69 | 105 | 17 | 0 | 120 | 0 | 17 | 114 | 68 | 25 | 400 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 42 | 17 | 360 | 145 | 0 | 355 | 29 | 150 | 230 | 390 |  | 632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 70 | 0 | 60 | 7 | 16 | 0 | 0 | 0 | 24 | 15 | 90 | 28 | 34 | 50 | 8 | 35 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 50 | 0 | 0 | 0 | 42 | 0 | 0 | 36 | 1244 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 250 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 190 | 0 | 0 | 12 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 15 | 335 | 0 | 0 | 60 | 80 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 0 | 19 | 51 | 25 | 0 | 6 | 8 | 10 | 0 | 0 | 0 | 0 | 300 | 0 | 167 | 0 | 47 | 40 | 0 | 51 | 0 | 40 | 8 | 16 | 10 | 33 | 15 | 128 | 44 | 0 | 0 | 1.6 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 210 | 15 | 0 | 10 | 315 | 17 | 0 | 0 | 195 | 0 | 0 | 9 | 0 | 100 | 20 | 25 | 34 | 13 | 400 | 57 | 17 | 17 | 5 | 15 | 17 | 17 | 98 | 38 | 25 | 380 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 350 | 17 | 0 | 350 | 20 | 150 | 230 | 390 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 50 | 28 | 34 | 40 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 410 | 17 | 0 | 35 | 0 | 6 | 0 | 8 | 0 | 1200 | 220 |  | 17 | 6 | 100 | 0 | 0 |  | 0 | 30 | 250 | 1300 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 6 | 51 | 0 | 335 | 0 | 0 | 9 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 22 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 6 | 8 | 12 | 0 | 0 | 0 | 0 | 300 | 0 | 167 | 0 | 41 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 25 | 9 | 94 | 44 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 215 | 18 | 0 | 10 | 315 | 17 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 17 | 6 | 25 | 34 | 6 | 398 | 57 | 17 | 0 | 1 | 16 | 0 | 17 | 86 | 9 | 25 | 384 | 16 | 4 | 0 | 17 | 0 | 0 | 2 | 0 | 0 | 385 | 17 | 0 | 353 | 0 | 160 | 232 | 150 | 0 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 10 | 0 | 3 | 0 | 6 | 0 | 1 | 0 | 1180 | 220 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 0 | 5 | 150 | 1306 | 20 | 0 | 0 |  |  |  | 107061541 | 18839272 | 0 | 79325341 | 24482149 | 2256000 | 2358790 | 140640 | 956160
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 107.0615 | 18.8393 | 0 | 79.3253 | 24.4821 | 2.256 | 2.3588 | 0.14064 | 0.95616
| Minimum Generation |  | 7644 | 5:00
| Highest Generation |  | 11426 | 19:00 | [129 empty] | 0 | [70 empty] | 235.4199
| Day Peak Generation |  | 10733 | 12:00
| Evening Peak Generation |  | 11426 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 907 | 1:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 667 | 19:00
| Load factor L.F |  | 85.85% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-02-20
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10733 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 7763
Evening Peak Generation : |  |  | 11426 | MW Hour : | 19:00 | Available Max Generation : |  | 12297
E.P. Demand (at gen end) : |  |  | 11600 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11700
Maximum Generation : |  |  | 11426 | MW Hour : | 19:00 | Reserve(Generation end) |  | 597
Total Gen. (MKWH) : |  |  | 235.4199 | System Load Factor : | 85.85% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 776 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-20
Actual : |  | 84.99 | Ft.(MSL) , | Rule curve : | 94.34 | Ft.( MSL )
Gas Consumed : |  | Total = | 826.86 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 312708541.51
: |  |  | Coal : | 531596579.94 | Oil : | 446158428.8 | Total : | 1290463550.25
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 10 | 240:00 | 3823.072 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1045.9496 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1463.8103 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1271.063 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1046.4992 |  |  | 0 | 0%
Mymensingh Area |  | 156 | 3744:00 | 777.6683 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 436.6164 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 363.2198 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 710.409 |  |  | 0 | 0%
Total |  | 166 |  | 10938.3077 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Megnaghat-450 MW.
8) Haripur-412 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:15 | 17:32 | Keranigonj 230/132/33kV S/S Hasnabad Scheduled S/D Due to Deadline checking from Hasnabad end
08:16 | 17:33 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Deadline checking from
Hasnabad end.
08:30 |  | Hasnabad 132/33kV S/S Keraniganj-1 (Pre- Lalbag) Scheduled S/D Due to Dead line checking
08:32 |  | Hasnabad 132/33kV S/S Keraniganj-2 (Pre- Aourahati) Scheduled S/D Due to Dead line checking
| 08:36 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
| 08:36 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
08:37 | 16:37 | Bibiyana-Kaliakoir 400 kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to emergency Maintenance.
and from Bibiana 400/230kV end Due to Emergency maintenance
08:38 | 16:49 | Khagrachari-Rangamati 132kV Ckt-1 Scheduled S/D from Khagrachori 132/33kV end Due to Deadline Checking. and from
Rangamati 132/33kV end Due to annual deadline checking at Khagrachari Grid S/S.
08:48 | 17:26 | Keraniganj-Sreenagar 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to Deadline checking for
Hasnabad-keraniganj 132kv line 1&2 from Hasnabad end.
09:00 |  | Fenchuganj 230/132/33kV S/S TR-01 LT Scheduled S/D Due to 132kV bus-1 shutdown for bus conductor & Bus PI placement.
09:01 | 14:24 | Jhenaidah 230/132kV S/S 230 kV Bus Scheduled S/D Due to Annual Maintenance
09:05 |  | Fenchuganj 230/132/33kV S/S TR-01 HT Scheduled S/D Due to 132kV bus-1 shutdown for bus conductor & Bus PI placement
09:06 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to 132kV bus-1
shutdown for bus conductor & Bus PI placement
09:07 |  | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Annual maintenance&oil leakage repair
09:08 |  | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Annual maintenance & oli leakage repair
09:14 |  | Fenchuganj 230/132/33kV S/S 132 KV Bus-1 Scheduled S/D Due to 132kV bus-1 shutdown for bus conductor & Bus PI
placement
09:38 | 17:37 | Rajbari 132/33kV S/S Transformer-2 LT Project Work S/D Due to 132kV faulty anergy meter change.
09:39 | 17:35 | Rajbari 132/33kV S/S Transformer-2 HT Project Work S/D Due to 132kV faulty anergy meter change.
10:08 | 01:08 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to Low Voltage.
10:48 | 01:07 | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Forced S/D Due to Due to Low Voltage.
10:57 |  | Unique Meghnaghat Power 584 MW CCPP GT was sync.
10:58 |  | Unique Meghnaghat Power Limited (UMPL) Syncronized with remarks:- GT
11:28 |  | Summit Meghnaghat-2 589 MW PP (Gas) GT was sync.
11:28 |  | Meghnaghat CCPP(Summit)-2 Syncronized
12:00 |  | Day peak Generation: 10,733 MW
12:25 | 12:37 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing 1) DEF START Alarm. 2) Master Trip
86T2, 86T4 3) High Impedance Diff. A (Tee point) 87TEE=2(FDR) relays Due to Unknown
13:14 |  | Mirersorai EZ - Sonagazi Solar PP 230 kv line was switched on.
14:02 | 16:40 | Madunaghat 132/33kV S/S TR-1(507T) LT Tripped showing REF-615 relays Due to CT Blust of Mohora-02,33kV feeder of |  |  |  |  | 12.0MW load interrup.
BPDB.
14:11 | 15:13 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to CT Blust of 33kV Mohora-02 feeder of BPDB. |  |  |  |  | 10.0MW load interrup.
14:14 | 15:24 | Madunaghat-TKCL 132kV Ckt-1 Forced S/D from Madunaghat 132/33kV end Due to Fire in 33kV Switchyard near this
feeder.
14:16 | 15:25 | Madunaghat-Sikalbaha 132kV Ckt-2 Forced S/D from Madunaghat 132/33kV end Due to Fire in 33 kV switchyard near this
feeder.
| 14:41 | Cumilla(N)-Daudkandi 132 kV Ckt-2 is restored.
| 15:01 | Saidpur 132/33kV S/S TR-3 (424T) HT is restored.
15:32 | 17:07 | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to SCADA Integration Testing
15:37 | 17:02 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to SCADA Integration Testing
16:03 | 16:28 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to kite removing from 132kV T-3 PT |  |  |  |  | 50.0MW load interrup.
16:03 | 16:28 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to kite removing from 132kV T-3 PT |  |  |  |  | 50.0MW load interrup.
16:09 | 19:32 | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Kachua 132/33kV end Due to For comilla north grid
| 16:18 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT is restored.
16:22 |  | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Project Work S/D Due to Transformer is tripped by Differential protection.
Now it is under maintenance
16:22 | 16:22 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Tripped showing Differential relays Due to Differential protection Trip
19:00 |  | Evening Peak Generation = 11,426MW
19:39 |  | Haripur 412 MW CCPP Syncronized with remarks:- GT
20:22 |  | Unique Meghnaghat Power Limited (UMPL) Syncronized with remarks:- ST
22:11 |  | Bhola 225 MW CCPP Shutdown with remarks:- GT1 shutdown due to controller update work
00:45 |  | Meghnaghat- Madunaghat 400 kV Line-2 was switched on.
| 01:11 | Rampal 400/230kV S/S Bus Reactor is restored.
06:33 | 07:02 | Meghnaghat-Shyampur 230kV Ckt-1 Tripped from Meghnaghat 230/132kV end showing Distance relay relays.
07:04 | 07:20 | Aminbazar-Keraniganj 230kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing 86.1 relays Due to Distance zone 1
trip R Phase (8.10km).
07:32 |  | Daudkandi-Sonargaon 132 kV Ckt-2 Scheduled S/D from Daudkandi 132/33kV end Due to Deadline check by third party
5:48 | 6:44 | Bibiyana-Kaliakoir 400 kV Ckt-1 Tripped from Bibiana
400/230kV end showing SOTF, Zcom tripped. relays Due to
SOTF, Zcom tripped.
5:49 | 6:39 | Bibiyana-Kaliakoir 400 kV Ckt-2 Tripped from Kaliakoir
400/230/132kV end showing REL 670 relays Due to General
Trip 67N Trip
7:32 |  | Agargaon 230/132kV S/S Auxiliary Tr-2 LT Scheduled S/D Due
to Annual Maintenance.
7:33 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT
Scheduled S/D Due to Annual Maintenance.
7:34 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT
Scheduled S/D Due to Annual Maintenance.
Temperature Transducer Maintenance
11:23 |  | From NLDC: Matarbari 2*600 MW (CPGCL) Unit 1 was sync.
11:23 |  | Matarbari 2*600 MW (CPGCL) Syncronized with remarks:- u-1
sync
| 11:45 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT is restored.
| 11:47 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT is restored.
11:48 |  | Bhola Natun Biddut BD LTD (GAS) GT1 was sync.
12:00 |  | Day peak Generation: 9959 MW
12:08 | 18:11 | Chauddagram-Feni 132 kV Ckt-2 Forced S/D from Feni 132/33kV
end Due to 132 kV Red Phase CT Top Side Oil Leakage, and
from Chauddagram 132/33kV end Due to Emergency maintenance
work in Feni Grid S/S.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 190 | 3656562
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 846000 | Under maint.
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 158400 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 1319788 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 220738 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 191002 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 102 | 1581000 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 17 | 204480 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 7828158 | Loop oil temperature High
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 595008 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 52560 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1356480
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 40199 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 38823 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 974760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 746300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 622800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 200640 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 132 | 1344873 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 36 | 446688 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 976320
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 288000 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 172448
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 67320 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 65 | 1622727 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 388 | 2963709 | On test.
| Dhaka area Total |  |  |  | 5062 | 1867 | 28710183
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 15 | 162460 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 112320
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 210240 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 956160 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 211 | 4945284
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 350436 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 848736 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 928465 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 281880 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 490560 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 171696 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 500160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29039
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 96 | 968509 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 129824 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 357125 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 485760 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 355036 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 762763
| SS Power I |  | SS Power | 2*612 | 1224 | 315 | 7936363
| Cox's Bazar Wind |  | IPP | 66 | 0 | 8 | 140640 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 157 | 3832727 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1278 | 24956183
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 772000 | ST under shutdown
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 7089000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 8592500
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 44 | 1038456
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 52 | 1090560
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 102 | 1472000 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1092315
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 26 | 260945 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 672400 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 498240 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 216720
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2256000
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 801500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 164966 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 9 | 224160 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1618800 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 69 | 708120 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 191880 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 37 | 275520 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1398 | 29036082
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 32 | 1119360 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11500
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 213600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 1004400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 277810
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 44880 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 116 | 2671550
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 35 | 822000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 954600 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3829500
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 158400 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 160320 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 680160 | GT-9 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 5256960
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 370000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 369552 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7249000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 410 | 8894000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 206100
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8633500 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1649 | 37584092
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 667 | 18839272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 124320 | Fuel shortage
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 73 | 315648 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 414720 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 473040
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 803 | 20167000
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 206784 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 6 | 131852 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 70 | 1139000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1190 | 28599100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4969255
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 254400 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 247 | 4843600 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1782 | 40143991
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 153461 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 15 | 62118 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 329820 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 491038 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 158940 | Fuel shortage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 146 | 3930236 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9193309
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 212892 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 146070 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 49114 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 892776 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 263520 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 252768 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28860
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1398 | 29940951
| Rajshahi Area Total |  |  |  | 3631 | 2268 | 46105873
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4172600 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 42 | 259526 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36529
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 53 | 359040 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 193614
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1023630
| Rangpur Area Total |  |  |  | 950 | 265 | 6044939
| Total |  |  |  | 25481 | 11426 | 235419893
| Eastern Grid Total |  |  |  | 15398 | 6308 | 122958090
| Western Grid Total |  |  |  | 10083 | 5118 | 112461803
| National Grid Total |  |  |  | 25481 | 11426 | 235419893
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-19
| (a) ENTIRE EASTERN GRID : |  | 7464.89 | MW | (b) ENTIRE WESTERN GRID : |  | 3444.2 | MW
| i) Dhaka area |  | 4198.89 | MW | i) Khulna area |  | 1251 | MW
| ii) Chittagong area |  | 1130 | MW | ii) Rajshahi area |  | 1135.2 | MW
| iii) Comilla area |  | 887 | MW | iii) Barisal area |  | 295 | MW
| iv) Mymensingh area |  | 869 | MW | iv) Rangpur area |  | 763 | MW
| v) Sylhet area |  | 380 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10909.09 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 16 | 08:00 | Kamrangirchar | 49.5 | 13:00 | Narinda | 44 | 13:00 | Sherpur | 126 | 18:30
2 | AKSML | 105 | 12:00 | Chowmuhani | 148 | 20:00 | Kaptai | N/A | N/A | Narshingdi | 152 | 20:00 | Shikalbaha | 19 | 18:00
3 | Aftabnagar | 26 | 12:00 | Chuadanga | 75 | 18:30 | Kazla | 80 | 13:00 | Natore | 108 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 71 | 13:00 | Coxsbazar | 105 | 18:00 | Keranigonj | 64 | 18:30 | Nawabganj | 29.4 | 21:00 | Shitalakhya | 78.9 | 15:00
5 | Agrabad | 52 | 15:00 | Cumilla(N) | 116 | 19:00 | Khagrachori | 24 | 18:00 | Netrakona | 127 | 07:00 | Sholosohor | 32 | 15:00
6 | Amnura | 59 | 08:00 | Cumilla(S) | 110 | 14:00 | Khulna | 84 | 13:00 | New | 18.8 | 12:00 | Shyampur | 134 | 01:00
7 | Ashuganj | 58 | 01:00 | Daudkandi | 109 | 18:30 | Khulshi | 144 | 19:00 | Niamatpur | 84 | 08:00 | Siddhirganj | 108 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 20 | 13:00 | Kishoreganj | 108 | 19:30 | Noapara | 37 | 19:30 | Sirajganj | 92 | 19:00
9 | BSRM | 135 | 15:00 | Dhamrai | 106 | 19:30 | Kodda | 285 | 18:30 | PHP | 4 | 10:00 | Sonargaon | 94 | 18:30
10 | Bagerhat | 71 | 18:30 | Dhanmondi | 109 | 13:00 | Kulaura | 26 | 18:00 | Pabna | 83 | 18:30 | Sreemongol | 48 | 18:00
11 | Bakulia | 67 | 19:00 | Dohazari | 62 | 20:00 | Kurigram | 64 | 18:30 | Palashbari | 94 | 13:00 | Sreepur | 62 | 08:00
12 | Banani | 18 | 14:00 | Faridpur | 110 | 18:30 | Kushtia | 102 | 19:00 | Panchagarh | 47 | 19:00 | Srinagar | 30.12 | 21:00
13 | Bangabhaban | 11 | 11:00 | Fatullah | 53 | 15:00 | Lalbag | 81 | 13:00 | Patuakhali | 53 | 21:00 | Sunamganj | 38 | 18:30
14 | Barapukuria | 58 | 11:00 | Fenchuganj | 24 | 18:30 | Lalmonirhat | 39 | 19:00 | Payra | 18 | 18:30 | Sylhet | 10 | 00:00
15 | Barguna | 14 | 21:00 | Feni | 69 | 18:30 | MI_Cement | 12.5 | 09:00 | Postogola | 44 | 13:00 | Sylhet-132 | 99 | 19:00
16 | Barishal | 79 | 12:00 | GPH | 95 | 00:00 | Madanganj | 32 | 00:00 | Purbachal | 15 | 13:00 | TK | 14 | 18:00
17 | Barishal-230 | 60 | 18:30 | Ghorashal | 64 | 20:00 | Madaripur | 66 | 19:30 | Purbasadipur | 111 | 19:00 | Tangail | 152 | 07:00
18 | Baroaulia | 67 | 10:00 | Goalpara | 22 | 19:00 | Madartek | 60.96 | 21:00 | Rahim | 48 | 02:00 | Thakurgaon | 77 | 18:30
19 | Baroirhat | 41 | 18:00 | Gollamari | 34 | 13:00 | Madunaghat | 34 | 18:00 | Rajbari | 48 | 18:30 | Tongi | 135 | 15:00
20 | Bashundhara | 137 | 18:00 | Gopalganj | 77 | 19:00 | Magura | 45 | 18:30 | Rajendrapur | 78 | 18:30 | Ullahpara | 25 | 07:00
21 | BashundharaCement | 6 | 00:00 | Gulshan | 82 | 13:00 | Mahasthangarh | 56 | 08:00 | Rajshahi | 104 | 20:00 | Ullon | 36 | 18:00
22 | Beanibazar | 42 | 18:30 | Halishahar | 72 | 15:00 | Manikganj | 92 | 18:00 | Rajshahi-230 | 26 | 19:00 | Uttara | 48 | 13:00
23 | Benapole | 50 | 07:00 | HaripurSBU | 156 | 12:00 | Maniknagar | 58 | 13:00 | Ramganj | 68 | 18:30 | UttaraNew | 30 | 12:00
24 | Bhaluka | 96 | 08:00 | Hasnabad | 74 | 13:00 | Matarbari | 33 | 18:30 | Rampur | 19 | 19:00 | Zigatola | 46 | 12:00
25 | Bhandaria | 34 | 22:00 | Hathazari | 57 | 13:00 | Matuail | 60 | 11:00 | Rangamati | 12 | 18:00
26 | Bhangura | 30 | 18:30 | Ishurdi | 51 | 18:30 | Millgate | 89 | 15:00 | Rangpur | 103 | 18:30
27 | Bheramara(GK) | 39 | 18:30 | Jaldhaka | 58 | 19:30 | Mirpur | 98 | 19:00 | Ruppur | 5 | 15:00
28 | Bhulta | 248 | 11:00 | Jamalpur | 114 | 07:00 | Mirsorai | 4 | 00:00 | SSM | 14 | 00:00
29 | Bog-Sherpur | 58 | 07:00 | Jashore | 107 | 12:00 | Mirzapur | 53 | 19:00 | Saidpur | 101 | 10:00
30 | Bogura | 125 | 19:00 | Jhenaidah | 91 | 18:30 | Mithapukur | 44 | 18:00 | Satkhira | 96 | 19:00
31 | Borhanuddin | 49 | 20:00 | Joydebpur | 157 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 83 | 09:00
32 | Brahmanbaria | 114 | 20:00 | Joypurhat | 57 | 08:00 | Mogbazar | 98.3 | 13:00 | Savar | 154 | 12:00
33 | Cantonment | 110 | 18:00 | Juldah | 20 | 05:00 | Mongla | 31 | 04:00 | SevenRings | 4.56 | 19:30
34 | Chandpur | 43 | 21:00 | KSRM | 27 | 08:00 | Motijheel | 33 | 13:00 | ShahCement | 18 | 10:00
35 | Chandraghona | 23 | 17:00 | Kabirpur | 252 | 18:30 | Munshiganj | 64 | 14:00 | Shahjadpur | 63 | 11:00
36 | Chapai | 60 | 12:00 | Kachua | 49 | 18:30 | Mymensingh | 177 | 18:30 | Shahjibazar | 95 | 21:00
37 | Charsaidpur | 42 | 04:00 | Kallyanpur | 76 | 14:00 | Naogaon | 110 | 09:00 | Shahmirpur | 45 | 00:00
38 | Chauddagram | 47 | 18:00 | Kalurghat | 28 | 15:00 | Narail | 41 | 19:00 | Shariatpur | 50 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 04:00 | 381 | 12:00 | Gopalganj | 412 | 04:00 | 389 | 10:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 398 | 21:00 | 358 | 12:00
| Bhulta | 393 | 03:00 | 364 | 12:00 | Madunaghat_I | 413 | 23:00 | 405 | 04:00
| Bibiana | 416 | 19:30 | 403 | 11:00 | Payra | 419 | 04:00 | 408 | 10:00
| BIPTC | 408 | 02:00 | 391 | 18:00 | Rahanpur | 414 | 03:00 | 396 | 10:00
| Bogura | 406 | 04:00 | 382 | 10:00 | Rampal | 415 | 05:00 | 393 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 05:00 | 211 | 12:00 | Haripur | 228 | 00:00 | 212 | 12:00
| AKSML | 266 | 16:00 | 225 | 15:00 | Hasnabad | 229 | 04:00 | 211 | 12:00
| Aminbazar | 232 | 01:00 | 214 | 12:00 | Hathazari | 235 | 21:00 | 225 | 12:00
| Ashuganj | 236 | 00:00 | 223 | 12:00 | Ishurdi | 239 | 05:00 | 224 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 237 | 05:00 | 221 | 10:00
| Baghabari | 237 | 03:00 | 222 | 12:00 | Kaliakoir | 231 | 22:00 | 208 | 12:00
| Barapukuria | 224 | 04:00 | 210 | 10:00 | Keranigonj | 229 | 03:00 | 211 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 242 | 05:00 | 227 | 10:00
| Barishal | 244 | 03:00 | 239 | 08:00 | Madunaghat_I | 234 | 23:00 | 226 | 12:00
| Bheramara | 238 | 06:00 | 225 | 10:00 | Maniknagar | 230 | 03:00 | 210 | 12:00
| Bhulta | 232 | 03:00 | 214 | 12:00 | Meghnaghat | 234 | 04:00 | 219 | 10:00
| Bibiana | 239 | 20:00 | 230 | 12:00 | Mirsorai | 237 | 19:30 | 223 | 15:00
| BIPTC | 238 | 04:00 | 224 | 10:00 | Rajshahi | 241 | 05:00 | 228 | 12:00
| Bogura | 229 | 04:00 | 217 | 12:00 | Rampal | 240 | 05:00 | 225 | 10:00
| Bogura-400 | 235 | 04:00 | 221 | 10:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 04:00 | 243 | 03:00 | Rampura | 231 | 02:00 | 213 | 12:00
| BSRM | 235 | 19:30 | 223 | 15:00 | Shikalbaha | 232 | 19:30 | 225 | 05:00
| Cumilla(N) | 233 | 22:00 | 220 | 12:00 | Shyampur | 230 | 05:00 | 212 | 12:00
| Fenchuganj | 241 | 00:00 | 233 | 13:00 | Siddhirganj | 229 | 03:00 | 218 | 15:00
| Ghorashal | 235 | 00:00 | 220 | 13:00 | Sirajgonj | 237 | 00:00 | 230 | 12:00
| Ghorashal-230 | 232 | 02:00 | 215 | 12:00 | Sreepur | 235 | 05:00 | 220 | 12:00
| GPH | 234 | 19:30 | 224 | 12:00 | Tongi | 230 | 04:00 | 207 | 11:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 131 | 05:00 | 119 | 11:00 | Lalbag | 132 | 21:00 | 121 | 10:00
| Agargaon | 136 | 04:00 | 123 | 12:00 | Lalmonirhat | 131 | 04:00 | 119 | 07:00
| Agrabad | 136 | 19:00 | 131 | 12:00 | Madanganj | 134 | 21:00 | 122 | 10:00
| AKS | 134 | 18:30 | 127 | 13:00 | Madaripur | 137 | 00:00 | 130 | 10:00
| Aminbazar | 132 | 02:00 | 120 | 12:00 | Madartek | 130 | 05:00 | 116 | 12:00
| Amnura | 140 | 17:00 | 124 | 10:00 | Madunaghat | 137 | 20:00 | 130 | 13:00
| Ashuganj | 140 | 00:00 | 130 | 11:00 | Magura | 136 | 00:00 | 127 | 13:00
| Bagerhat | 134 | 01:00 | 123 | 12:00 | Mahasthangarh | 135 | 03:00 | 124 | 10:00
| Bakulia | 137 | 21:00 | 130 | 12:00 | Manikganj | 135 | 22:00 | 114 | 12:00
| Banani | 132 | 22:00 | 120 | 12:00 | Maniknagar | 135 | 03:00 | 118 | 12:00
| Bangabhaban | 132 | 04:00 | 118 | 12:00 | Matarbari | 134 | 08:00 | 122 | 02:00
| Barapukuria | 137 | 04:00 | 125 | 10:00 | Matuail | 133 | 21:00 | 120.5 | 11:00
| Barguna | 132 | 03:00 | 129 | 12:00 | Millgate | 136 | 22:00 | 120 | 10:00
| Barishal | 140 | 20:00 | 126 | 18:30 | Mirpur | 130 | 03:00 | 120 | 11:00
| Barishal-230 | 140 | 03:00 | 134 | 10:00 | Mirzapur | 134 | 19:30 | 120 | 12:00
| Baroaulia | 137 | 20:00 | 131 | 12:00 | Mithapukur | 133 | 04:00 | 121 | 10:00
| Baroirhat | 136 | 19:30 | 128 | 13:00 | MI_Cement | 138 | 18:00 | 123 | 10:00
| Bashundhara | 137 | 22:00 | 120 | 12:00 | Modern | 136 | 00:00 | 131 | 12:00
| BashundharaCement | 134 | 21:00 | 122 | 10:00 | Mogbazar | 130 | 00:00 | 119 | 12:00
| Beanibazar | 136 | 06:00 | 131 | 10:00 | Mongla | 133 | 02:00 | 125 | 13:00
| Benapole | 136 | 03:00 | 123 | 13:00 | Motijheel | 132 | 04:00 | 118 | 12:00
| Bhaluka | 130 | 00:00 | 120 | 12:00 | Munshiganj | 134 | 20:00 | 123 | 11:00
| Bhandaria | 131 | 05:00 | 126 | 14:00 | Mymensingh | 129 | 00:00 | 117 | 12:00
| Bhangura | 139 | 03:00 | 130 | 09:00 | Naogaon | 133 | 05:00 | 120 | 09:00
| Bheramara | 138 | 05:00 | 129 | 12:00 | Narail | 138 | 03:00 | 127 | 12:00
| Bheramara(GK) | 136 | 19:30 | 129 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 123 | 22:00 | 109 | 10:00 | Narshingdi | 132 | 10:00 | 113 | 11:00
| Bog-Sherpur | 136 | 05:00 | 125 | 12:00 | Natore | 136 | 04:00 | 128 | 10:00
| Bogura | 136 | 03:00 | 127 | 10:00 | Nawabganj | 133 | 22:00 | 121 | 12:00
| Bogura-230 | 135 | 21:00 | 127 | 10:00 | Netrakona | 132 | 05:00 | 116 | 12:00
| Brahmanbaria | 135 | 00:00 | 124 | 12:00 | New | 136 | 21:00 | 121 | 12:00
| Cantonment | 135 | 03:00 | 123 | 12:00 | Niamatpur | 135 | 03:00 | 127 | 09:00
| Chandpur | 138 | 20:00 | 127 | 12:00 | Noapara | 134 | 02:00 | 126 | 10:00
| Chandraghona | 138 | 22:00 | 131 | 12:00 | Pabna | 139 | 03:00 | 130 | 12:00
| Chapai | 135 | 03:00 | 127 | 08:00 | Palashbari | 132 | 04:00 | 118 | 10:00
| Charsaidpur | 135 | 21:00 | 123 | 10:00 | Panchagarh | 135 | 20:00 | 115 | 10:00
| Chauddagram | 138 | 16:00 | 129 | 12:00 | Patuakhali | 132 | 22:00 | 129 | 07:00
| Chhatak | 136 | 00:00 | 131 | 15:00 | Payra | 133 | 03:00 | 129 | 10:00
| Chowmuhani | 137 | 19:30 | 126 | 03:00 | PHP | 138 | 22:00 | 128 | 06:00
| Chuadanga | 137 | 04:00 | 124 | 12:00 | Postogola | 136 | 22:00 | 125 | 12:00
| Coxsbazar | 128 | 00:00 | 121 | 16:00 | Purbachal | 132 | 02:00 | 118 | 12:00
| Cumilla(N) | 139 | 21:00 | 130 | 12:00 | Purbasadipur | 132 | 20:00 | 116 | 10:00
| Cumilla(S) | 139 | 22:00 | 128 | 09:00 | Rahanpur | 138 | 03:00 | 130 | 12:00
| Daudkandi | 130 | 21:00 | 117 | 11:00 | Rahim | 134 | 21:00 | 121 | 10:00
| Dhaka | 130 | 01:00 | 118 | 12:00 | Rajbari | 138 | 04:00 | 129 | 10:00
| Dhamrai | 135 | 21:00 | 123 | 09:00 | Rajendrapur | 137 | 19:30 | 122 | 13:00
| Dhanmondi | 134.5 | 22:00 | 122 | 10:00 | Rajshahi | 134 | 05:00 | 127 | 12:00
| Dohazari | 135 | 21:00 | 128 | 07:00 | Rajshahi-230 | 134 | 03:00 | 124 | 10:00
| Faridpur | 137 | 03:00 | 130 | 13:00 | Ramganj | 137 | 20:00 | 126 | 06:00
| Fatullah | 136 | 22:00 | 125 | 12:00 | Rampur | 136 | 20:00 | 130 | 15:00
| Fenchuganj | 137 | 01:00 | 134 | 11:00 | Rampura | 131 | 01:00 | 120 | 12:00
| Feni | 136 | 19:30 | 129 | 13:00 | Rangamati | 137 | 19:30 | 130 | 12:00
| Ghorashal | 139 | 00:00 | 130 | 11:00 | Rangpur | 131 | 02:00 | 119 | 09:00
| Goalpara | 137 | 03:00 | 127 | 12:00 | Ruppur | 137 | 00:00 | 132 | 10:00
| Gollamari | 136 | 03:00 | 127 | 12:00 | Saidpur | 132 | 20:00 | 118 | 10:00
| Gopalganj | 136 | 03:00 | 129 | 10:00 | Satkhira | 134 | 03:00 | 125 | 10:00
| Gopalganj-400 | 137 | 03:00 | 130 | 10:00 | Satmasjid | 135 | 02:00 | 122 | 12:00
| Gulshan | 131 | 03:00 | 119 | 12:00 | Savar | 128 | 01:00 | 117 | 12:00
| Halishahar | 136 | 00:00 | 130 | 12:00 | SevenRings | 139 | 03:00 | 128 | 11:00
| Haripur | 134 | 21:00 | 121 | 10:00 | ShahCement | 135 | 21:00 | 123 | 10:00
| HaripurSBU | 134 | 21:00 | 121 | 10:00 | Shahjadpur | 141 | 01:00 | 131 | 12:00
| Hasnabad | 136 | 21:00 | 124 | 10:00 | Shahjibazar | 134 | 00:00 | 126 | 12:00
| Hathazari | 139 | 01:00 | 132 | 16:00 | Shahmirpur | 136 | 21:00 | 130 | 12:00
| Ishurdi | 141 | 05:00 | 132 | 10:00 | Shariatpur | 138 | 04:00 | 130 | 12:00
| Jaldhaka | 130 | 19:30 | 117 | 07:00 | Sherpur | 123 | 19:30 | 109 | 15:00
| Jamalpur | 126 | 19:30 | 115 | 02:00 | Shikalbaha | 125 | 19:00 | 119 | 12:00
| Jashore | 134 | 02:00 | 124 | 12:00 | Shikalbaha-230 | 136 | 19:30 | 132 | 06:00
| Jhenaidah | 138 | 04:00 | 129 | 10:00 | Shitalakhya | 135 | 22:00 | 123 | 10:00
| Jhenaidah-230 | 140 | 05:00 | 129 | 10:00 | Sholosohor | 136 | 20:00 | 130 | 12:00
| Joydebpur | 141 | 10:00 | 126 | 13:00 | Shyampur | 136 | 21:00 | 125 | 10:00
| Joypurhat | 132 | 03:00 | 117 | 09:00 | Shyampur-230 | 136 | 21:00 | 124 | 10:00
| Juldah | 136 | 17:00 | 130 | 15:00 | Siddhirganj | 133 | 21:00 | 121 | 11:00
| Kabirpur | 139 | 19:30 | 112 | 12:00 | Sirajganj | 135 | 02:00 | 128 | 07:00
| Kachua | 137 | 21:00 | 126 | 13:00 | Sonargaon | 133 | 21:00 | 119 | 10:00
| Kaliakoir | 140 | 21:00 | 125 | 10:00 | Sreemongol | 135 | 01:00 | 130 | 10:00
| Kallyanpur | 135 | 00:00 | 125 | 12:00 | Sreepur | 134 | 04:00 | 125 | 12:00
| Kalurghat | 137 | 00:00 | 130 | 13:00 | Srinagar | 133 | 22:00 | 121 | 12:00
| Kamrangirchar | 134 | 00:00 | 123 | 10:00 | SSM | 140 | 00:00 | 136 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 134 | 01:00 | 131 | 12:00
| Kazla | 133 | 00:00 | 119 | 12:00 | Sylhet | 135 | 00:00 | 132 | 11:00
| Keranigonj | 133 | 22:00 | 121 | 10:00 | Sylhet-132 | 136 | 01:00 | 132 | 13:00
| Khagrachori | 136 | 19:30 | 129 | 12:00 | Tangail | 131 | 19:30 | 118 | 12:00
| Khulna | 136 | 04:00 | 126 | 12:00 | Thakurgaon | 134 | 20:00 | 113 | 10:00
| Khulna(S) | 137 | 04:00 | 127 | 12:00 | TK | 137 | 19:30 | 131 | 12:00
| Khulshi | 135 | 19:30 | 128 | 12:00 | Tongi | 137 | 21:00 | 124 | 11:00
| Kishoreganj | 135 | 03:00 | 123 | 12:00 | Ullahpara | 138 | 03:00 | 128 | 12:00
| Kodda | 138 | 19:30 | 121 | 12:00 | Ullon | 130 | 22:00 | 119 | 11:00
| KSRM | 137 | 00:00 | 130 | 14:00 | Uttara | 135 | 22:00 | 120 | 10:00
| Kulaura | 136 | 00:00 | 133 | 12:00 | UttaraNew | 131 | 02:00 | 118 | 13:00
| Kurigram | 130 | 20:00 | 114 | 07:00 | Zigatola | 135 | 02:00 | 122 | 10:00
| Kushtia | 138 | 03:00 | 128 | 12:00

## L-Curve
Date | 2024-02-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1510 | 5074 | 4178 | 9252 |  |  |  | QF-LDC-11
0:30 | 1390 | 4677.5 | 4283.5 | 8961 | Date: | 2024-02-19
1:00 | 1270 | 4281 | 4389 | 8670
1:30 | 1241 | 4232 | 4235.5 | 8467.5
2:00 | 1212 | 4183 | 4082 | 8265
2:30 | 1176 | 4111.5 | 4015 | 8126.5 | [5 empty] | Gen. at Eve. Peak | 11426 | 11426 MW (19:00 )
3:00 | 1140 | 4040 | 3948 | 7988 | [6 empty] | 19:00
3:30 | 1125 | 3984.5 | 3869.5 | 7854 | [5 empty] | Gen. at Day Peak | 10733 | 10733 MW (12:00 )
4:00 | 1110 | 3929 | 3791 | 7720 | [6 empty] | 12:00
4:30 | 1075 | 3891 | 3791 | 7682 | [5 empty] | Highest Generation | 11426
5:00 | 1040 | 3853 | 3791 | 7644 | [6 empty] | 19:00
5:30 | 955 | 3915 | 3879 | 7794
6:00 | 870 | 3977 | 3967 | 7944
6:30 | 823 | 4318 | 4098.5 | 8416.5
7:00 | 776 | 4659 | 4230 | 8889
7:30 | 861 | 4735 | 4473 | 9208
8:00 | 946 | 4811 | 4716 | 9527
8:30 | 1027 | 4948.5 | 4749 | 9697.5
9:00 | 1108 | 5086 | 4782 | 9868
9:30 | 1289 | 5153.5 | 4800 | 9953.5
10:00 | 1470 | 5221 | 4818 | 10039
10:30 | 1405 | 5218.5 | 4969.5 | 10188
11:00 | 1340 | 5216 | 5121 | 10337
11:30 | 1425 | 5437.5 | 5097.5 | 10535
12:00 | 1510 | 5659 | 5074 | 10733
12:30 | 1491 | 5693.5 | 5027.5 | 10721
13:00 | 1472 | 5728 | 4981 | 10709
13:30 | 1436 | 5625.5 | 4947.5 | 10573
14:00 | 1400 | 5523 | 4914 | 10437
14:30 | 1413 | 5415 | 4825.5 | 10240.5
15:00 | 1426 | 5307 | 4737 | 10044
15:30 | 1403 | 5278.5 | 4726.5 | 10005
16:00 | 1380 | 5250 | 4716 | 9966
16:30 | 1370 | 5217 | 4705.5 | 9922.5
17:00 | 1360 | 5184 | 4695 | 9879
17:30 | 1365 | 5432.5 | 4750 | 10182.5
18:00 | 1370 | 5681 | 4805 | 10486
18:30 | 1295 | 5994.5 | 4961.5 | 10956
19:00 | 1220 | 6308 | 5118 | 11426
19:30 | 1312 | 6211 | 5067 | 11278
20:00 | 1310 | 6157 | 4915 | 11072 |  |  |  | Executive Engineer
20:30 | 1390 | 6059 | 4859 | 10918 |  |  |  | Network Operation Division
21:00 | 1470 | 5961 | 4803 | 10764
21:30 | 1450 | 5770 | 4721.5 | 10491.5
22:00 | 1430 | 5579 | 4640 | 10219 |  |  |  |  | Page 6 of 7
22:30 | 1440 | 5462 | 4469 | 9931
23:00 | 1450 | 5345 | 4298 | 9643
23:30 | 1480 | 5209.5 | 4238 | 9447.5
24:00 | 1510 | 5074 | 4178 | 9252
11426 MW (19:00 )
10733 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-19 |  | Energy |  | 235419893
[15 empty] | 43879 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3011 | 903 | 1604 | 0 | 458 | 2914 | 35 | 0 | 237 | 90 | 0 | 0 | 74
0:30 | 2979 | 905 | 1406 | 0 | 350 | 3012 | 37.5 | 0 | 182.5 | 88 | 0 | 1 | 51.325 |  |  | Date: | 43879
1:00 | 2947 | 907 | 1208 | 0 | 242 | 3110 | 40 | 0 | 128 | 86 | 0 | 2 | 28.65
1:30 | 2955.5 | 806 | 1205.5 | 0 | 231.5 | 3056 | 40 | 0 | 84 | 85 | 0 | 4 | 14.325 | [9 empty] | Total Energy | 235.4199 | 235.4199 | Total Energy Gen 235.420 MKWHr Energy Not Served 3.045 MKWHr Energy Requirement 238.464 MKWHr
2:00 | 2964 | 705 | 1203 | 0 | 221 | 3002 | 40 | 0 | 40 | 84 | 0 | 6 | 0 | [9 empty] | Energy not Served | 3.0446 | 3.0446
2:30 | 2973 | 688.5 | 1183 | 0 | 159.5 | 2974 | 40 | 0 | 20 | 82 | 0 | 6.5 | 0 | [9 empty] | Energy Requirement | 238.4644 | 238.4644
3:00 | 2982 | 672 | 1163 | 0 | 98 | 2946 | 40 | 0 | 0 | 80 | 0 | 7 | 0
3:30 | 2962.5 | 671.5 | 1136.5 | 0 | 70.5 | 2887.5 | 40 | 0 | 0 | 79 | 0 | 6.5 | 0 | [8 empty] | Shortage
4:00 | 2943 | 671 | 1110 | 0 | 43 | 2829 | 40 | 0 | 0 | 78 | 0 | 6 | 0
4:30 | 2905 | 671 | 1110.5 | 0 | 43 | 2826.5 | 40 | 0 | 0 | 79 | 0 | 7 | 0
5:00 | 2867 | 671 | 1111 | 0 | 43 | 2824 | 40 | 0 | 0 | 80 | 0 | 8 | 0
5:30 | 2891 | 715.5 | 1164.5 | 0 | 44.5 | 2844 | 40 | 0 | 8 | 79 | 0 | 7.5 | 12.415
6:00 | 2915 | 760 | 1218 | 0 | 46 | 2864 | 40 | 0 | 16 | 78 | 0 | 7 | 24.83
6:30 | 3043 | 743 | 1272 | 0 | 230.5 | 2964 | 40 | 0 | 24.5 | 82 | 8 | 9.5 | 41.415 | [7 empty] | Coal
7:00 | 3171 | 726 | 1326 | 0 | 415 | 3064 | 40 | 0 | 33 | 86 | 16 | 12 | 58
7:30 | 3132.5 | 678 | 1342 | 0 | 525 | 3303.5 | 40 | 0 | 46 | 73 | 55.5 | 12.5 | 135.5 | [6 empty] | Oil
8:00 | 3094 | 630 | 1358 | 0 | 635 | 3543 | 40 | 0 | 59 | 60 | 95 | 13 | 213
8:30 | 3078.5 | 630 | 1334.5 | 0 | 697.5 | 3560.5 | 40 | 0 | 129.5 | 75 | 145.5 | 6.5 | 241
9:00 | 3063 | 630 | 1311 | 0 | 760 | 3578 | 40 | 0 | 200 | 90 | 196 | 0 | 269
9:30 | 3069.5 | 630 | 1322.5 | 0 | 794.5 | 3530.5 | 40 | 0 | 226 | 94 | 246.5 | 0 | 211.5
10:00 | 3076 | 630 | 1334 | 0 | 829 | 3483 | 40 | 0 | 252 | 98 | 297 | 0 | 154
10:30 | 3009.5 | 766.5 | 1358.5 | 0 | 854 | 3481.5 | 40 | 0 | 250.5 | 99 | 327.5 | 1 | 155
11:00 | 2943 | 903 | 1383 | 0 | 879 | 3480 | 40 | 0 | 249 | 100 | 358 | 2 | 156
11:30 | 2956 | 902.5 | 1532.5 | 0 | 917.5 | 3457 | 40 | 0 | 257 | 103 | 360.5 | 9 | 157.5
12:00 | 2969 | 902 | 1682 | 0 | 956 | 3434 | 40 | 0 | 265 | 106 | 363 | 16 | 159
12:30 | 2999 | 902.5 | 1693 | 0 | 964 | 3381.5 | 40 | 0 | 265.5 | 106 | 356 | 13.5 | 205.0825
13:00 | 3029 | 903 | 1704 | 0 | 972 | 3329 | 40 | 0 | 266 | 106 | 349 | 11 | 251.165
13:30 | 3029 | 903 | 1704 | 0 | 972 | 3329 | 40 | 0 | 266 | 106 | 349 | 11 | 251.165
14:00 | 3029 | 903 | 1704 | 0 | 972 | 3329 | 40 | 0 | 266 | 106 | 349 | 11 | 251.165
14:30 | 2939 | 902.5 | 1578 | 0 | 946.5 | 3317 | 40 | 0 | 259 | 106 | 283 | 5.5 | 266.9225
15:00 | 2849 | 902 | 1452 | 0 | 921 | 3305 | 40 | 0 | 252 | 106 | 217 | 0 | 282.68
15:30 | 2848.5 | 902 | 1445.5 | 0 | 924.5 | 3302.5 | 40 | 0 | 268 | 105 | 169 | 0 | 229.2
16:00 | 2848 | 902 | 1439 | 0 | 928 | 3300 | 40 | 0 | 284 | 104 | 121 | 0 | 175.72
16:30 | 2801 | 902.5 | 1459 | 0 | 988 | 3228.5 | 40 | 0 | 319.5 | 104 | 80 | 0 | 145.6375
17:00 | 2754 | 903 | 1479 | 0 | 1048 | 3157 | 40 | 0 | 355 | 104 | 39 | 0 | 115.555
17:30 | 2771.5 | 903 | 1478.5 | 0 | 1205.5 | 3139.5 | 40 | 0 | 518 | 107 | 19.5 | 0 | 136.0875
18:00 | 2789 | 903 | 1478 | 0 | 1363 | 3122 | 40 | 0 | 681 | 110 | 0 | 0 | 156.62
18:30 | 2934.5 | 785 | 1634.5 | 0 | 1432 | 3299.5 | 40 | 0 | 719.5 | 107 | 0 | 4 | 161.395
19:00 | 3080 | 667 | 1791 | 0 | 1501 | 3477 | 40 | 0 | 758 | 104 | 0 | 8 | 166.17
19:30 | 2947 | 618 | 1754 | 0 | 1499 | 3547 | 40 | 0 | 759 | 108 | 0 | 6 | 163.085
20:00 | 3045 | 618 | 1682 | 0 | 1377 | 3445 | 40 | 0 | 756 | 104 | 0 | 5 | 160
20:30 | 3108 | 618.5 | 1617 | 0 | 1329.5 | 3398.5 | 40 | 0 | 697.5 | 105 | 0 | 4 | 152.5
21:00 | 3171 | 619 | 1552 | 0 | 1282 | 3352 | 40 | 0 | 639 | 106 | 0 | 3 | 145
21:30 | 3160.5 | 721.5 | 1503.5 | 0 | 1145.5 | 3216.5 | 37.5 | 0 | 600 | 103 | 0 | 3.5 | 158.9275
22:00 | 3150 | 824 | 1455 | 0 | 1009 | 3081 | 35 | 0 | 561 | 100 | 0 | 4 | 172.855
22:30 | 3131.5 | 863.5 | 1473.5 | 0 | 865.5 | 3003.5 | 35 | 0 | 456.5 | 98 | 0 | 4 | 146.9275
23:00 | 3113 | 903 | 1492 | 0 | 722 | 2926 | 35 | 0 | 352 | 96 | 0 | 4 | 121
23:30 | 3062 | 903 | 1548 | 0 | 590 | 2920 | 35 | 0 | 294.5 | 93 | 0 | 2 | 97.5 |  |  | Max Temp. in Dhaka |  | 30.2°C
24:00 | 3011 | 903 | 1604 | 0 | 458 | 2914 | 35 | 0 | 237 | 90 | 0 | 0 | 74
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 235.420 MKWHr Energy Not Served 3.045 MKWHr Energy Requirement 238.464 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-02-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 956160
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 1 | 8 | 1 |  | 15 | 17 | 17 | 17 | 17 | 8 | 8 | 162460
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 7 | 13 | 17 | 20 | 20 | 20 |  | 14 | 8 | 2 | [9 empty] | 112320
6 | Sikalbaha 225MW CCPP (Gas) | 213 | 212 | 210 | 214 | 213 | 211 | 213 | 214 | 212 | 214 | 214 | 214 | 215 | 213 | 214 | 213 | 212 | 211 |  | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 4945284
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 51 | 51 | 51 | 51 | 50 | 50 | 48 | 50 | 51 | 65 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 928465
12 | Hathazari 100 MW peaking PP | 48 | 0 | [5 empty] | 3 | 66 | 66 | 42 | 42 | 44 | 40 | 40 | 40 | 40 | 56 |  | 56 | 56 | 56 | 64 | 56 | 64 | 64 | 848736
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 0 |  |  |  | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 350436
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 40 | 40 | 0 | [6 empty] | 31 | 31 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 42 | 49 | 49 | 40 | 40 | 40 | 672400
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 39 | 41 | 42 | 42 | 40 | 41 | 41 | 63 | 105 | 100 | 102 | 100 | 101 | 100 | 97 | 100 | 39 | 40 |  | 102 | 60 | 39 | 40 | 39 |  | 0 | 1581000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 332 | 330 | 330 | 280 | 280 |  | 280 | 260 | 260 | 335 | 335 | 335 | 335 | 7828158
18 | Kodda 300 MW PP Unit-2 (Summit) | [6 empty] | 7 | 47 | 49 | 59 | 77 | 80 | 82 | 51 | 50 | 57 | 50 | 100 |  | 132 | 132 | 130 | 130 | 45 | 45 | 45 | 1344873
19 | Ashuganj 195 MW PP (APSCL-United) | [5 empty] | 8 | 63 | 102 | 148 | 148 | 102 | 102 | 73 | 73 | 73 | 73 | 73 | 73 |  | 102 | 102 | 102 | 55 | 55 | 55 | 55 | 1472000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 140 | 140 | 140 | 140 | 140 | 140 | 190 | 190 | 190 | 190 | 130 | 150 | 143 | 150 | 130 | 130 | 130 | 130 |  | 190 | 160 | 160 | 160 | 160 | 160 | 160 | 3656562
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 340 | 340 | 340 | 341 | 340 | 340 | 340 | 340 | 341 | 340 | 341 | 341 | 341 | 341 | 341 | 340 | 340 | 315 |  | 315 | 360 | 340 | 335 | 282 | 274 | 278 | 7936363
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 44 | 44 | 44 | 41 | 41 | 44 | 44 | 44 | 44 | 44 | 44 | 41 | 44 | 43 | 44 | 44 |  | 44 | 44 | 44 | 44 | 47 | 47 | 47 | 1038456
33 | Ashuganj 225 MW CCPP | 154 | 154 | 153 | 153 | 96 | 0 | [19 empty] | 0 | 772000
34 | Ashuganj 450 MW CCPP(South) | 260 | 280 | 300 | 300 | 300 | 275 | 335 | 285 | 310 | 315 | 275 | 280 | 280 | 280 | 280 | 280 | 280 | 300 |  | 290 | 275 | 265 | 255 | 260 | 335 | 300 | 7089000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 260 | 260 | 260 | 260 | 260 | 393 | 393 | 395 | 395 | 395 | 395 | 395 | 395 | 395 | 360 | 393 | 393 | 340 |  | 393 | 393 | 393 | 393 | 350 | 340 | 325 | 8592500
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 30 | 50 | 53 | 55 | 53 | 52 | 53 | 55 | 54 | 54 | 54 | 53 | 54 |  | 52 | 52 | 54 | 55 | 55 | 55 | 55 | 1090560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [21 empty] | 124 | 188 | 204 | 204 | 204 | 846000
| Meghnaghat Unique power | [10 empty] | 120 | 250 | 250 | 200 | 100 | 70 | 65 | 68 |  | 65 | 65 | 65 | 99 | 128 | 130 | 130 | 1622727
| Summit Meghanghat-2 589 MW(Gas) | [11 empty] | 187 | 187 | 187 | 288 | 290 | 288 | 288 |  | 388 | 400 | 390 | 200 | 150 | 150 | 150 | 2963709
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 74 | 75 | 75 | 75 | 75 | 75 | 67 | 67 | 32 | 32 | 28 | 28 | 28 | 28 | 29 | 30 | 31 | 32 |  | 32 | 34 | 43 | 43 | 43 | 37 | 74 | 1119360
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 12 | 23 | 34 | 39 | 44 | 42 | 38 | 26 | 14 | 4 | 0 | [8 empty] | 277810
44 | Fenchugonj CCPP Phase-1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 822000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 954600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 27 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 680160
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 211 | 211 | 211 | 211 | 212 | 212 | 212 | 212 | 212 | 211 | 211 | 209 | 206 | 206 | 206 | 206 | 206 | 205 |  | 208 | 208 | 208 | 208 | 208 | 212 | 210 | 5256960
51 | Sylhet 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 12 | 12 | 12 | 12 | 12 |  | 16 | 20 | 18 | 18 | 18 | 18 | 18 | 370000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 9 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 206100
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 5 |  |  |  | 0 | 160320
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 369552
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 275 | 280 | 300 | 300 | 315 | 310 | 325 | 300 | 290 | 305 | 285 | 300 | 280 | 285 | 300 | 295 | 280 |  | 310 | 260 | 270 | 295 | 280 | 300 | 305 | 7249000
| Bibiyana South 400 MW | 330 | 320 | 320 | 310 | 300 | 310 | 400 | 340 | 340 | 365 | 340 | 400 | 400 | 340 | 340 | 340 | 340 | 385 |  | 400 | 400 | 400 | 400 | 400 | 380 | 340 | 8633500
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | [5 empty] | 0 | 38823
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 44880
60 | Barabkunda 22 MW PP (Regent) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 171696
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 86 | 84 | 80 | 78 | 80 | 78 | 86 | 60 | 90 | 98 | 100 | 106 | 106 | 110 | 106 | 104 | 104 | 110 |  | 104 | 108 | 104 | 106 | 100 | 96 | 90 | 2256000
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 39 | 40 | 37 | 35 | 12 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 |  | 14 | 14 | 18 | 31 | 31 | 39 | 39 | 500160
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 216720
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 30 | 33 | 33 | 33 | 25 | 25 | 34 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801500
68 | Cumilla 25 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 6 | 6 | 6 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 224160
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 456000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 518760
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 746300
72 | Rupganj 33 MW PP(Summit) | 28 | 30 | 30 | 30 | 32 | 32 | 30 | 30 | 28 | 26 | 26 | 26 | 26 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 22 | 23 | 23 | 622800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [6 empty] | 70 | 105 | 105 | 100 | 88 | 88 | 88 | 88 | 88 | 73 | 88 | 88 |  | 88 | 88 | 88 | 88 | 98 | 98 | 98 | 1618800
| Chowmuhani 113 MW | [8 empty] | 0 | 9 | 18 | 34 | 38 | 38 | 39 | 39 | 39 | 57 |  | 69 | 69 | 68 | 69 | 69 | 65 | 41 | 708120
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 17 |  |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 13 | 8 | 8 | 22 | 25 | 25 | 25 | 15 | 10 | 10 | 17 | 17 |  | 17 | 17 | 14 |  |  |  | 0 | 204480
78 | Gazipur 52 MW PP | [6 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 200640
79 | Kodda 150 MW PP | 32 | 0 |  |  |  | 16 | 16 | 39 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 133 |  | 149 | 149 | 149 | 149 | 115 | 48 | 48 | 1356480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [6 empty] | 3 | 8 | 8 | 8 | 8 | 16 | 16 | 8 | 8 | 8 |  | 1 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 164966
| Gazipur 100 MW PP | [6 empty] | 17 | 17 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 976320
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 29039
| Jodiac Power | [8 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | [10 empty] | 0 | 129824
| Karnaphuli Power Ltd. | 17 | 17 | 0 |  |  |  | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 357125
82 | Madanganj 102 PP(Summit) | 65 | 65 | 55 | 17 | 17 | 17 | 18 | 60 | 82 | 78 | 68 | 76 | 82 | 80 | 80 | 80 | 70 | 80 |  | 80 | 80 | 80 | 80 | 78 | 10 | 0 | 1319788
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 7 | 24 | 27 | 36 | 36 | 31 |  | 25 | 36 | [5 empty] | 191002
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [6 empty] | 9 | 17 | 18 | 17 | 18 | 17 | 12 | 9 | 8 | 8 | 9 | 8 |  | 9 | 9 |  |  |  |  | 0 | 158400
| Meghnaghat 104 MW PP (OPCL) | 0 | 8 | 17 | 0 |  |  |  | 2 | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 16 | 0 | 288000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [6 empty] | 25 | 25 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 |  |  |  |  | 0 | 281880
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 158400
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 35 |  | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 1092315
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 58 | 58 | 58 | 58 | 58 | 16 | 8 | 595008
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 0 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 13 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 210240
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | 0 |  |  |  |  | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 220738
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 40199
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 |  | 163 | 163 | 130 | 163 | 163 | 120 | 163 | 3829500
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | [9 empty] | 11500
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 10 | 35 | [13 empty] | 0 | 52560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 213600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 0 |  |  |  | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 34 |  | 36 | 36 | 36 | 35 | 35 | 26 | 18 | 446688
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 0 |  |  | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 490560
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 0 |  |  | 0 | 12 | 17 | 17 | 17 | 17 | 17 | 23 | 17 | 17 | 17 | 24 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 498240
117 | Ashuganj 150 MW PP (Midland) | 10 | 6 | 0 |  |  |  | 1 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 11 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 260945
118 | Bibiyana-III 400 MW CCPP | 365 | 365 | 365 | 329 | 317 | 347 | 408 | 408 | 372 | 375 | 375 | 315 | 388 | 414 | 352 | 315 | 315 | 335 |  | 410 | 408 | 409 | 410 | 410 | 406 | 358 | 8894000
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 10 | 56 | 56 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 69 |  | 69 | 69 | 69 | 59 | 9 | 9 | 9 | 1004400
| Anwara 300 MW PP (United) | [6 empty] | 16 | 16 | 49 | 49 | 67 | 66 | 66 | 66 | 66 | 66 | 66 | 90 |  | 96 | 96 | 96 | 83 | 16 | 16 | 16 | 968509
| Juldah unit-2 (Acorn) | 25 | 0 |  |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 485760
| Anlima Energy Ltd. | 17 | 17 | 0 |  |  |  | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 355036
| Bhairob 54.5 MW | [11 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 191880
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 7 | 8 | 22 | 26 | 29 | 29 | 23 | 15 | 6 | 2 | [9 empty] | 172448
| Chandpur 115(Doreen) | [12 empty] | 15 | 18 | 18 | 18 | 19 | 36 |  | 37 | 36 | 36 | 36 | 20 | 18 | 0 | 275520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 5 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 67320
| Mirsharai 150 MW (Oil) | 8 | 0 |  |  |  |  | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 145 |  | 145 | 145 | 125 | 17 | 17 | 17 | 17 | 762763
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 2 | 6 | 7 | 6 | 8 | 7 | 12 | 13 | 0 | 0 | 2 | 16 | 11 | 17 | [5 empty] | 8 | 6 | 5 | 3 | 4 | 4 | 0 | 140640
| Matarbari 2*600 MW (CPGCL) | 157 | 157 | 157 | 158 | 157 | 156 | 159 | 159 | 159 | 157 | 155 | 156 | 160 | 160 | 158 | 160 | 155 | 158 |  | 157 | 156 | 155 | 157 | 157 | 158 | 155 | 3832727
120 | Eastern Zone Total | 4281 | 4183 | 4040 | 3929 | 3853 | 3977 | 4659 | 4811 | 5086 | 5221 | 5216 | 5659 | 5728 | 5523 | 5307 | 5250 | 5184 | 5681 |  | 6308 | 6211 | 6157 | 5961 | 5579 | 5345 | 5074 | 122958090
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [13 empty] | 3 | 10 | 10 | 10 | 19 |  | 27 | 22 | 22 | 22 | 22 |  |  | 124320
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [6 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 35 | 36 |  | 36 | 37 | 37 | 37 | 37 |  | 0 | 414720
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 19 | 41 | 60 | 75 | 61 | 62 | 66 | 37 | 24 | 10 | [9 empty] | 473040
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [8 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 254400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 200 | 200 | 200 | 200 | 200 | 200 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 221 | 220 | 220 | 220 | 4969255
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 |  | 0 | 206784
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 194 | 307 | 307 | 250 | 250 | 244 | 200 | 200 | 200 | 200 | 150 | 150 |  | 247 | 250 | 250 | 250 | 223 | 150 | 150 | 4843600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 67 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 40 | 40 | 40 | 40 | 38 | 40 | 40 | 40 | 40 | 40 |  | 70 | 40 | 40 | 40 | 40 |  | 0 | 1139000
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 4 | 3 | 4 | 4 | 5 | 5 | 4 | 4 | 4 | 3 | 6 |  | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 131852
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 5 | 40 | 57 |  | 73 | 67 | 70 | 59 | 43 |  |  | 315648
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 907 | 705 | 672 | 671 | 671 | 760 | 726 | 630 | 630 | 630 | 903 | 902 | 903 | 902 | 902 | 902 | 903 | 903 |  | 667 | 618 | 618 | 619 | 824 | 903 | 903 | 18839272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1080 | 1070 | 1020 | 990 | 990 | 1030 | 1110 | 1244 | 1244 | 1210 | 1200 | 1160 | 1110 | 1170 | 1160 | 1160 | 1080 | 1060 |  | 1190 | 1244 | 1160 | 1110 | 1000 | 960 | 950 | 28599100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4172600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 153461
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 2 | 4 | 3 | 1 | 0 | [9 empty] | 28860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 156 | 156 | 156 | 159 | 162 | 164 | 164 | 164 | 163 | 160 | 156 | 152 | 147 | 146 | 146 | 147 | 147 | 147 |  | 146 | 146 | 146 | 146 | 147 | 149 | 148 | 3930236
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 370 | 370 | 370 | 414 | 414 | 414 | 380 | 414 | 380 | 380 | 414 | 300 | 300 | 300 | 350 | 350 |  | 414 | 414 | 360 | 360 | 300 | 350 | 414 | 9193309
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 4 | 4 | 14 |  | 15 | 15 | 15 | 9 | 5 |  |  | 62118
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 146070
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 |  |  |  |  | 0 | 329820
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 8 |  | 0 | 491038
167 | Katakhali 50 MW Peaking PP | [17 empty] | 8 |  | 33 | 43 | 50 | 50 | 50 |  |  | 158940
168 | Santahar 50 MW Peaking PP | [15 empty] | 21 | 22 | 36 |  | 37 | 37 | 37 | 37 | 30 |  |  | 212892
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | [9 empty] | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 49114
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 21 | 42 | 49 | 49 | 49 | 49 | 49 | 49 | 84 |  | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 892776
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 1 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | [10 empty] | 0 | 263520
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 252768
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 33 | 40 |  | 42 | 42 | 42 | 35 | 6 |  | 0 | 259526
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 6 | 6 | 6 | 5 | 4 | 3 | 1 | [9 empty] | 36529
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 10 | 36 | 53 |  | 53 | 55 | 55 | 55 | 55 | 55 | 0 | 359040
| Intraco Solar 30 MW | [6 empty] | 1 | 7 | 16 | 23 | 29 | 31 | 30 | 26 | 19 | 10 | 3 | 0 | [8 empty] | 193614
| Adani Power Jharkhanda Ltd | 1213 | 1115 | 1109 | 1020 | 1017 | 1018 | 1091 | 1323 | 1357 | 1356 | 1364 | 1363 | 1348 | 1359 | 1276 | 1270 | 1262 | 1269 |  | 1398 | 1367 | 1370 | 1330 | 1249 | 1214 | 1211 | 29940951
178 | Teesta Solar Limited | [6 empty] | 6 | 40 | 87 | 128 | 153 | 162 | 152 | 128 | 95 | 53 | 16 | [9 empty] | 1023630