## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-02-21 | Wednesday
|  | Date (day): | 2024-02-21 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11814.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12456 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-20 | 2024-02-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 190 | 190 | 190
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 139 | 417 | 412 | 412 |  |  | ST synchronized process
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  |  | Line S/D
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 50 | 75 | 25 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 80 | 80 | 80 | 80 |  | 22 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 25 | 15 | 25 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 36 | 13 | 14 | 34 | 41 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 60 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 90 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 25 | 65 | 80 | 80 |  | 22 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 115 | 64 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 38 | 39 | 39 |  | 41 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 18 | 18 | 18 |  | 15 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 105 | 120 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 98 | 17 | 100 | 17 | 132 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 17 | 17 | 145 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 255 | 323 | 250 | 250 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 158 | 105 | 120 | 120 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1720 | 1842 | 2074 | 2271 | 1665 | 1050
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 26 | 6 | 26 | 24 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 190 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 212 | 210 | 210
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 4 | 73 | 40 | 75 | 23 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 68 | 59 | 68 | 34 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 10 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 30 | 30 | 30
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 64 | 80 | 15 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 0 | 17 | 0 | 54 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 145 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 360 | 335 | 350 | 355 | 869 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 20 | 29 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 158 | 157 | 150 | 150 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1133 | 1336 | 1123 | 1381 | 2213 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 0 | 0 | 0 |  | 221 | Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 215 | 250 | 300 | 320 | 40 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 345 | 393 | 350 | 390 | 10 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 46 | 47 | 46
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 53 | 54 | 55 | 55
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 167 | 92 | 68 | 92 | 103 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 8 | 6 | 6 | 6 | 144 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 40 | 48 | 40 | 48
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 34 | 34 | 166 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 108 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 11 | 11 | 11 |  | 14 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 88 | 105 | 98 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 23 | 77 | 38 | 68 | 45 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 42 | 0 | 42 | 73 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1232 | 1384 | 1294 | 1486 | 625 | 817
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 38 | 50 | 65 | 137 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 9 | 9 | 9 | 9 | 191 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 57 | 69 | 46 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 6 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 107 | 122 | 167.6 | 149 | 137 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 38 | 35 | 38 |  | 32 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 28 | 28 | 28 |  | 33 | GT-9 Under maint.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 210 | 208 | 210 | 210 |  | 21 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 315 | 315 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 374 | 374 | 400 | 400
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 340 | 380 | 400 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1515 | 1528 | 1598 | 1621 | 129 | 566
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 785 | 921 | 632
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 46 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 66 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 75 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 320 | 0 | 350 | 350 | 267 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1299 | 897 | 1388 | 1119 | 1607 | 39
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 0 | 32 | 78 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 4 | 7 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 40 | 65 | 60 | 65 |  | 129 | ST, GT-1 Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 1170 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 17 | 35
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 245 | 250 | 250 | 57 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1290 | 1774 | 1754 | 1853 | 135 | 162
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 24 | 24 | 28 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 28 | 28 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 42 | 34 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 46 | 48 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 141 | 140 | 150 | 70 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 410 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 35 | 15 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 0 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 49 | 90 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 35 | 0 | 113 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 0 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1321 | 1410 | 1300 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 2065 | 2274 | 2072 | 2296 | 1149 | 84
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 6 | 35 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 71 | 0 | 75 | 40 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 123 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 327 | 276 | 344 | 280 | 243 | 189
| Total |  |  |  |  | 26504 | 25481 | 10688 | 11433 | 11814.6 | 12456 | 7903 | 3237
A. |  | 2024-02-20 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 11433 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7763 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11600 | MW
3 | Day peak Generation : |  |  | 10688 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11044.37 | MW
4 | Evening peak Generation : |  |  | 11433 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 159 | MW
5 | Total Energy Generation : |  | 233.7921 | MKWHr | By Solar | 1.5276 | MKWHr
| By Gas : | 109.269 | MKWHr |  | By Oil: | 23.6239 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 76.8285 | MKWHr |  | By Hydro: | 0.9006 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0096 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7903 | MW | Dhaka | 4244.77 | 4220.77 |  | 24 |  | 18:00 |  | 149.935
|  |  | For Plants S/D or M/C prob = |  |  | 3237 | MW | Chittagong | 1035.5 | 1035.5 |  | 0 |  | 19:00 |  | 159.485
|  |  | Total = |  |  | 11140 | MW | Khulna | 1295.6 | 1295.6 |  | 0 |  | 19:30 |  | 140.385
7 | Total Gas Supplied : |  |  | 837.15 | MMCFD |  |  | Rajshahi | 1136.4 | 1136.4 |  | 0 |  | 20:00 |  | 100.275
8 | Fuel Cost : | i) Gas : | Taka | 303490964.472 | ii) Oil : | Taka | 431812719.89 | Comilla | 902 | 902 |  | 0 |  | 21:00 |  | 35
|  | iii) Coal : | Taka | 515681133.08 | Total | Taka | 1250984817.442 | Mymensingh | 1004 | 869 |  | 135 |  | 22:00 |  | 120
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.132 | MKWHr. | Sylhet | 376 | 376 |  | 0 |  | 23:00 |  | 50
| ii) During Peak Demand : |  |  | 1440 | MW (W to E) at | 19:00 | hrs | Barisal | 296.1 | 296.1 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 1020 | MW at | 7:00 | hrs | Rangpur | 754 | 754 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29°C |  |  | Total | 11044.37 | 10885.37 |  | 159
B. |  | 2024-02-21 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 30.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12456 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 1456 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 224.9377 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7627 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.3135 | MKWHr. | ii) HVDC Flow at Peak Time |  | 785 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.3194 | MKWHr. | iii) Maximum HVDC Flow : |  | 904 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.99 |  | (b) Today: | 84.87 |  | (c) Rule Curve: |  | 94.2
.

## YesterdayGen
2024-02-20 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 23 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 209 | 0 | 0 | 0 |  | 0 | 56 | 68 | 0 | 0 | 6 | 8 | 39 | 0 | 0 | 0 | 0 | 280 | 0 | 55 | 0 | 47 | 55 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 88 | 53 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 209 | 18 | 0 | 10 | 285 | 17 | 0 | 0 | 45 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 8 | 318 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 98 | 21 | 25 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 17 | 0 | 280 | 0 | 158 | 130 | 150 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1158 | 0 | 0 |  | 4795 | 4063 | 8858 | 2826 | 904 | 1497 | 0 | 413 | 2866 | 35 | 0 | 229 | 88 | 0 | 0 | 40.11 | 85.01
2:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 23 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 39 | 0 | 0 | 0 | 0 | 310 | 0 | 55 | 0 | 41 | 55 | 0 | 51 | 0 | 40 | 0 | 0 | 9 | 33 | 9 | 84 | 51 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 210 | 18 | 0 | 10 | 270 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 322 | 9 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 280 | 0 | 158 | 130 | 150 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1067 | 0 | 0 |  | 4376 | 3894 | 8270 | 2865 | 904 | 1452 | 0 | 165 | 2725 | 35 | 0 | 40 | 84 | 0 | 0 | 0 | 85.01
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 23 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 39 | 0 | 0 | 0 | 0 | 310 | 0 | 55 | 0 | 41 | 55 | 0 | 51 | 0 | 40 | 0 | 0 | 9 | 33 | 9 | 80 | 51 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 210 | 18 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 317 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 280 | 1 | 158 | 140 | 150 |  | 733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1029 | 0 | 0 |  | 4373 | 3677 | 8050 | 2855 | 733 | 1481 | 0 | 148 | 2677 | 35 | 0 | 40 | 80 | 0 | 1 | 0 | 85
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 23 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 39 | 0 | 0 | 0 | 0 | 320 | 0 | 55 | 0 | 41 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 8 | 9 | 78 | 51 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 210 | 18 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 280 | 3 | 157 | 135 | 150 |  | 715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 890 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 971 | 0 | 0 |  | 4158 | 3605 | 7763 | 2843 | 715 | 1471 | 0 | 0 | 2618 | 35 | 0 | 0 | 78 | 0 | 3 | 0 | 85
5:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 24 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 | 0 | 320 | 0 | 55 | 0 | 41 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 8 | 9 | 72 | 51 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 211 | 18 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 280 | 0 | 158 | 135 | 150 |  | 714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 968 | 0 | 0 |  | 4169 | 3616 | 7785 | 2851 | 714 | 1487 | 0 | 0 | 2626 | 35 | 0 | 0 | 72 | 0 | 0 | 0 | 84.99
6:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 38 | 0 | 0 | 0 | 0 | 310 | 0 | 102 | 0 | 41 | 55 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 8 | 9 | 84 | 52 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 215 | 18 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 334 | 0 | 157 | 135 | 150 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 960 | 0 | 0 |  | 4337 | 3827 | 8164 | 2886 | 904 | 1562 | 0 | 6 | 2671 | 35 | 0 | 16 | 84 | 0 | 0 | 91.68 | 84.99
7:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 0 | 4 | 0 | 335 | 0 | 0 | 3 | 20 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 25 | 2 | 0 | 35 | 0 | 0 | 0 | 2 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 3 | 8 | 38 | 0 | 0 | 0 | 0 | 300 | 0 | 117 | 0 | 41 | 55 | 0 | 51 | 0 | 0 | 3 | 0 | 0 | 25 | 9 | 82 | 52 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 140 | 0 | 28 | 0 | 0 | 215 | 18 | 0 | 10 | 295 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 6 | 1 | 12 | 9 | 5 | 375 | 57 | 17 | 0 | 0 | 16 | 0 | 5 | 53 | 0 | 25 | 360 | 15 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 17 | 0 | 340 | 0 | 160 | 232 | 150 |  | 756 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 930 | 220 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 150 | 1116 | 4 | 0 |  | 4950 | 3995 | 8945 | 3064 | 756 | 1733 | 0 | 366 | 2866 | 35 | 0 | 33 | 82 | 10 | 0 | 100 | 84.98
8:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 204 | 0 |  | 0 | 0 | 0 | 6 | 51 | 0 | 335 | 0 | 0 | 9 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 22 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 | 6 | 8 | 12 | 0 | 0 | 0 | 0 | 300 | 0 | 167 | 0 | 41 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 25 | 9 | 94 | 44 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 215 | 18 | 0 | 10 | 315 | 17 | 0 | 0 | 30 | 0 | 0 | 9 | 0 | 17 | 6 | 25 | 34 | 6 | 398 | 57 | 17 | 0 | 1 | 16 | 0 | 17 | 86 | 9 | 25 | 384 | 16 | 4 | 0 | 17 | 0 | 0 | 2 | 0 | 0 | 385 | 17 | 0 | 353 | 0 | 160 | 232 | 150 |  | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 414 | 10 | 0 | 3 | 0 | 6 | 0 | 1 | 0 | 1180 | 220 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 0 | 5 | 150 | 1306 | 20 | 0 |  | 5366 | 4358 | 9724 | 3148 | 620 | 1798 | 0 | 625 | 3319 | 35 | 0 | 33 | 94 | 52 | 0 | 168 | 84.98
9:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 180 | 0 |  | 0 | 0 | 0 | 9 | 64 | 0 | 335 | 0 | 0 | 9 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 22 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 0 | 51 | 25 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 0 | 305 | 0 | 187 | 0 | 41 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 25 | 9 | 96 | 44 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 163 | 0 | 28 | 0 | 0 | 214 | 18 | 0 | 10 | 310 | 17 | 0 | 0 | 20 | 0 | 0 | 9 | 0 | 17 | 12 | 25 | 34 | 6 | 364 | 59 | 17 | 17 | 3 | 49 | 5 | 17 | 83 | 9 | 25 | 340 | 17 | 4 | 0 | 17 | 0 | 0 | 4 | 0 | 0 | 325 | 35 | 0 | 360 | 2 | 157 | 235 | 157 |  | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 414 | 17 | 0 | 33 | 0 | 6 | 0 | 2 | 0 | 1244 | 180 | 0 | 17 | 0 | 33 | 0 | 0 | 0 | 0 | 12 | 180 | 1411 | 42 | 0 |  | 5395 | 4605 | 10000 | 2996 | 619 | 1772 | 0 | 723 | 3522 | 40 | 0 | 118 | 96 | 112 | 2 | 191 | 84.97
10:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 33 | 0 |  | 0 | 0 | 0 | 9 | 64 | 0 | 335 | 0 | 0 | 17 | 25 | 64 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 21 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 0 | 51 | 25 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 0 | 310 | 0 | 187 | 0 | 44 | 54 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 25 | 9 | 98 | 34 | 0 | 0 | 0 | 35 | 40 | 0 | 5 | 120 | 0 | 28 | 0 | 0 | 213 | 16 | 0 | 10 | 290 | 17 | 0 | 0 | 180 | 0 | 0 | 9 | 0 | 32 | 17 | 25 | 34 | 6 | 370 | 59 | 17 | 17 | 3 | 49 | 17 | 17 | 88 | 9 | 25 | 340 | 17 | 5 | 0 | 17 | 0 | 0 | 9 | 0 | 0 | 325 | 35 | 0 | 360 | 0 | 157 | 235 | 157 |  | 619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 34 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 360 | 17 | 0 | 35 | 0 | 6 | 0 | 4 | 0 | 1244 | 180 | 0 | 35 | 1 | 42 | 0 | 0 | 0 | 0 | 9 | 180 | 1361 | 85 | 0 |  | 5488 | 4594 | 10082 | 2856 | 619 | 1658 | 0 | 963 | 3472 | 40 | 0 | 201 | 98 | 175 | 0 | 208 | 84.97
11:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 53 | 0 |  | 0 | 0 | 0 | 0 | 70 | 4 | 335 | 0 | 0 | 17 | 25 | 64 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 0 | 51 | 25 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 0 | 250 | 0 | 187 | 0 | 42 | 52 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 25 | 9 | 104 | 33 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 29 | 0 | 0 | 213 | 0 | 0 | 9 | 305 | 12 | 0 | 0 | 195 | 0 | 0 | 9 | 0 | 94 | 19 | 25 | 34 | 5 | 364 | 59 | 17 | 17 | 4 | 66 | 17 | 17 | 88 | 9 | 25 | 400 | 17 | 5 | 0 | 17 | 0 | 0 | 10 | 0 | 0 | 325 | 54 | 0 | 360 | 0 | 156 | 234 | 160 |  | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 28 | 34 | 37 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 360 | 17 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 1040 | 180 | 0 | 17 | 1 | 43 | 0 | 0 | 0 | 228 | 19 | 150 | 1336 | 97 | 0 |  | 5616 | 4783 | 10399 | 2800 | 753 | 1706 | 0 | 1063 | 3440 | 40 | 0 | 290 | 104 | 203 | 0 | 144 | 84.96
12:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 80 | 15 | 335 | 0 | 0 | 9 | 25 | 64 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 4 | 51 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 167 | 0 | 36 | 53 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 112 | 33 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 210 | 0 | 0 | 10 | 300 | 12 | 0 | 0 | 195 | 0 | 0 | 9 | 0 | 98 | 19 | 25 | 34 | 8 | 374 | 59 | 17 | 17 | 4 | 64 | 17 | 17 | 88 | 23 | 25 | 340 | 17 | 6 | 17 | 17 | 0 | 0 | 22 | 1 | 0 | 345 | 54 | 0 | 360 | 0 | 158 | 255 | 158 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 46 | 16 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 900 | 180 | 0 | 0 | 3 | 75 | 0 | 0 | 0 | 320 | 23 | 150 | 1321 | 123 | 0 |  | 5707 | 4981 | 10688 | 2833 | 904 | 1755 | 0 | 1077 | 3379 | 40 | 0 | 308 | 112 | 280 | 0 | 174 | 84.96
13:00 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 64 | 15 | 0 | 0 | 0 | 0 | 25 | 64 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 25 | 51 | 25 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 120 | 0 | 36 | 51 | 0 | 51 | 0 | 40 | 16 | 0 | 9 | 33 | 9 | 110 | 29 | 0 | 0 | 1 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 209 | 0 | 0 | 9 | 300 | 12 | 0 | 0 | 195 | 0 | 0 | 9 | 0 | 98 | 18 | 25 | 34 | 11 | 363 | 59 | 17 | 17 | 4 | 64 | 17 | 17 | 88 | 37 | 25 | 340 | 0 | 9 | 35 | 17 | 0 | 15 | 18 | 18 | 0 | 325 | 54 | 0 | 360 | 0 | 157 | 281 | 108 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 24 | 16 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 950 | 180 | 0 | 0 | 3 | 82 | 0 | 0 | 0 | 0 | 22 | 150 | 1319 | 95 | 0 |  | 5160 | 4650 | 9810 | 2317 | 904 | 1682 | 0 | 1087 | 3106 | 40 | 0 | 307 | 110 | 257 | 0 | 181 | 84.95
14:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 45 | 15 | 0 | 0 | 0 | 0 | 25 | 48 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 0 | 64 | 51 | 25 | 0 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 120 | 0 | 42 | 53 | 0 | 51 | 0 | 47 | 16 | 0 | 9 | 33 | 5 | 114 | 29 | 0 | 0 | 1 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 207 | 0 | 0 | 9 | 310 | 12 | 0 | 0 | 177 | 0 | 0 | 9 | 0 | 30 | 16 | 25 | 34 | 13 | 397 | 59 | 17 | 17 | 3 | 64 | 17 | 17 | 88 | 39 | 25 | 370 | 6 | 20 | 17 | 17 | 0 | 17 | 0 | 18 | 0 | 354 | 35 | 0 | 360 | 1 | 159 | 280 | 108 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 0 | 35 | 0 | 6 | 0 | 4 | 0 | 1170 | 180 | 0 | 0 | 2 | 66 | 0 | 0 | 0 | 0 | 21 | 150 | 1319 | 106 | 0 |  | 5201 | 4848 | 10049 | 2461 | 897 | 1692 | 0 | 959 | 3328 | 40 | 0 | 318 | 114 | 239 | 1 | 297.005 | 84.96
15:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 7 | 25 | 48 | 25 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 21 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 212 | 0 | 0 | 0 |  | 0 | 64 | 50 | 25 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 120 | 0 | 42 | 54 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 8 | 112 | 29 | 0 | 0 | 1 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 208 | 0 | 0 | 10 | 320 | 12 | 0 | 0 | 50 | 0 | 0 | 9 | 0 | 17 | 12 | 25 | 34 | 13 | 377 | 59 | 17 | 17 | 2 | 66 | 17 | 17 | 88 | 39 | 25 | 360 | 16 | 14 | 17 | 17 | 0 | 17 | 0 | 18 | 0 | 393 | 35 | 0 | 350 | 0 | 157 | 250 | 110 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 40 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 380 | 0 | 0 | 0 | 0 | 6 | 0 | 4 | 0 | 1100 | 180 | 0 | 0 | 2 | 52 | 0 | 0 | 0 | 0 | 16 | 150 | 1313 | 39 | 0 |  | 5102 | 4633 | 9735 | 2470 | 897 | 1643 | 0 | 857 | 3240 | 40 | 0 | 334 | 112 | 142 | 0 | 348.575 | 84.95
16:00 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 36 | 0 |  | 0 | 0 | 0 | 0 | 80 | 15 | 0 | 0 | 0 | 9 | 25 | 48 | 13 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 21 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 0 | 64 | 42 | 25 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 92 | 0 | 45 | 51 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 100 | 29 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 206 | 0 | 0 | 10 | 315 | 12 | 0 | 0 | 47 | 0 | 0 | 9 | 0 | 17 | 7 | 25 | 34 | 18 | 366 | 59 | 17 | 17 | 1 | 66 | 0 | 17 | 88 | 39 | 25 | 350 | 17 | 4 | 17 | 17 | 0 | 17 | 0 | 18 | 0 | 385 | 35 | 0 | 320 | 0 | 159 | 250 | 108 |  | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 350 | 0 | 0 | 0 | 0 | 30 | 0 | 2 | 35 | 1060 | 180 | 0 | 0 | 1 | 32 | 17 | 0 | 0 | 0 | 8 | 150 | 1316 | 13 | 0 |  | 4980 | 4569 | 9549 | 2475 | 898 | 1570 | 0 | 909 | 3175 | 40 | 0 | 314 | 100 | 68 | 0 | 382.955 | 84.94
17:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 98 | 0 |  | 0 | 0 | 0 | 4 | 80 | 15 | 0 | 0 | 0 | 9 | 25 | 82 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 21 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 213 | 0 | 0 | 0 |  | 1 | 64 | 42 | 25 | 0 | 21 | 8 | 12 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 46 | 52 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 102 | 29 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 206 | 0 | 0 | 10 | 315 | 12 | 0 | 0 | 52 | 0 | 0 | 9 | 0 | 0 | 2 | 25 | 34 | 25 | 366 | 59 | 17 | 17 | 0 | 63 | 0 | 17 | 94 | 46 | 25 | 340 | 17 | 2 | 17 | 17 | 0 | 17 | 3 | 24 | 11 | 393 | 35 | 0 | 320 | 0 | 157 | 250 | 110 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 45 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 320 | 0 | 0 | 0 | 0 | 36 | 0 | 1 | 35 | 1040 | 180 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 0 | 2 | 150 | 1318 | 7 | 0 |  | 5132 | 4562 | 9694 | 2542 | 897 | 1555 | 0 | 955 | 3155 | 40 | 0 | 423 | 102 | 25 | 0 | 387.73 | 84.93
18:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 303 | 0 |  | 0 | 0 | 0 | 8 | 80 | 20 | 44 | 0 | 0 | 9 | 58 | 115 | 14 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 10 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 10 | 211 | 0 | 0 | 0 |  | 6 | 73 | 59 | 25 | 0 | 25 | 10 | 16 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 46 | 53 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 108 | 33 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 207 | 0 | 0 | 10 | 285 | 12 | 0 | 0 | 97 | 0 | 0 | 9 | 0 | 16 | 0 | 25 | 34 | 26 | 376 | 69 | 105 | 30 | 0 | 96 | 0 | 17 | 98 | 71 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 41 | 31 | 393 | 145 | 0 | 320 | 0 | 157 | 250 | 105 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 63 | 0 | 40 | 8 | 0 | 0 | 0 | 0 | 25 | 0 | 85 | 28 | 34 | 40 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 370 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 35 | 1040 | 180 | 0 | 3 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 150 | 1316 | 0 | 0 |  | 5865 | 4741 | 10606 | 2792 | 897 | 1583 | 0 | 1326 | 3153 | 40 | 0 | 707 | 108 | 0 | 0 | 149.935 | 84.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 0 | 0 | 9 | 80 | 25 | 90 | 0 | 0 | 9 | 65 | 115 | 13 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 6 | 73 | 68 | 25 | 0 | 26 | 10 | 30 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 46 | 54 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 108 | 38 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 208 | 0 | 0 | 10 | 315 | 12 | 0 | 0 | 105 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 374 | 69 | 105 | 34 | 0 | 80 | 0 | 17 | 105 | 77 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 17 | 393 | 145 | 0 | 335 | 0 | 157 | 323 | 105 |  | 785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 66 | 0 | 65 | 7 | 32 | 0 | 0 | 0 | 25 | 0 | 90 | 28 | 42 | 48 | 0 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1170 | 220 | 0 | 35 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 245 | 1410 | 0 | 0 |  | 6212 | 5221 | 11433 | 3039 | 785 | 1784 | 0 | 1430 | 3487 | 40 | 0 | 760 | 108 | 0 | 0 | 159.485 | 84.91
19:30 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 9 | 50 | 15 | 150 | 0 | 0 | 9 | 65 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 |  | 6 | 73 | 68 | 25 | 0 | 26 | 10 | 30 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 46 | 54 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 106 | 55 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 208 | 0 | 0 | 10 | 290 | 12 | 0 | 0 | 115 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 365 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 114 | 78 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 0 | 393 | 145 | 0 | 335 | 0 | 157 | 323 | 105 |  | 613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 72 | 0 | 65 | 7 | 32 | 0 | 0 | 0 | 25 | 0 | 90 | 0 | 42 | 50 | 8 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 350 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1244 | 220 | 0 | 35 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 250 | 1403 | 0 | 0 |  | 6162 | 5055 | 11217 | 3090 | 613 | 1672 | 0 | 1376 | 3559 | 40 | 0 | 761 | 106 | 0 | 0 | 140.385 | 0
20:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 0 | 0 | 0 | 38 | 15 | 185 | 0 | 0 | 0 | 65 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 73 | 68 | 0 | 0 | 26 | 10 | 30 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 47 | 54 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 106 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 208 | 0 | 0 | 10 | 280 | 12 | 0 | 0 | 115 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 365 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 114 | 78 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 0 | 393 | 145 | 0 | 350 | 0 | 157 | 323 | 100 |  | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 68 | 0 | 65 | 7 | 32 | 0 | 0 | 0 | 25 | 0 | 90 | 0 | 8 | 50 | 8 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 350 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1200 | 220 | 0 | 35 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 250 | 1408 | 0 | 0 |  | 6163 | 4979 | 11142 | 3147 | 612 | 1657 | 0 | 1288 | 3535 | 40 | 0 | 757 | 106 | 0 | 0 | 100.275 | 84.92
21:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 65 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 211 | 0 | 0 | 0 |  | 6 | 81 | 68 | 0 | 0 | 26 | 10 | 35 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 47 | 54 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 106 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 209 | 0 | 0 | 10 | 290 | 12 | 0 | 0 | 112 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 5 | 365 | 69 | 105 | 17 | 0 | 96 | 0 | 17 | 114 | 79 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 19 | 0 | 393 | 17 | 0 | 350 | 0 | 157 | 324 | 100 |  | 612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 90 | 0 | 0 | 50 | 17 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 350 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1110 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 183 | 1417 | 0 | 0 |  | 6121 | 4642 | 10763 | 3308 | 612 | 1673 | 0 | 1107 | 3387 | 40 | 0 | 530 | 106 | 0 | 0 | 35 | 84.91
22:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 418 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 41 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 26 | 10 | 38 | 0 | 0 | 0 | 0 | 220 | 0 | 36 | 0 | 47 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 33 | 11 | 102 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 209 | 0 | 0 | 10 | 305 | 12 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 380 | 9 | 105 | 17 | 0 | 16 | 0 | 17 | 52 | 79 | 25 | 348 | 21 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 393 | 17 | 0 | 350 | 0 | 158 | 320 | 100 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 350 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 150 | 1410 | 0 | 0 |  | 5515 | 4559 | 10074 | 3307 | 897 | 1631 | 0 | 719 | 3318 | 35 | 0 | 65 | 102 | 0 | 0 | 120 | 84.91
23:00 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 2 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 26 | 10 | 38 | 0 | 0 | 0 | 0 | 300 | 0 | 36 | 0 | 47 | 54 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 33 | 11 | 102 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 209 | 0 | 0 | 10 | 290 | 12 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 36 | 6 | 370 | 9 | 105 | 17 | 0 | 16 | 0 | 17 | 52 | 79 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 393 | 17 | 0 | 330 | 0 | 158 | 260 | 100 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1359 | 0 | 0 |  | 5429 | 4363 | 9792 | 3359 | 896 | 1556 | 0 | 612 | 3167 | 35 | 0 | 65 | 102 | 0 | 0 | 50 | 84.9
24:00 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 335 | 0 | 0 | 9 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 33 | 18 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 0 | 355 | 0 | 36 | 0 | 47 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 33 | 11 | 94 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 140 | 0 | 28 | 0 | 0 | 209 | 0 | 0 | 10 | 280 | 12 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 18 | 0 | 25 | 34 | 5 | 303 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 53 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 393 | 17 | 0 | 296 | 0 | 159 | 261 | 100 |  | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 320 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1273 | 0 | 0 |  | 5209 | 4136 | 9345 | 3316 | 896 | 1519 | 0 | 472 | 2948 | 35 | 0 | 65 | 94 | 0 | 0 | 0 | 84.9
KWH | 0 | 0 | 3730406 | 0 | 0 | 0 | 0 | 5119200 | 0 |  | 0 | 0 | 0 | 48960 | 855078 | 230788 | 5835312 | 0 | 0 | 115200 | 596160 | 1232160 | 232319 | 0 | 0 | 0 | 38520 | 40762 | 68256 | 0 | 456000 | 499320 | 817500 | 480300 | 212640 | 0 | 900600 | 0 | 0 | 0 | 177114 | 5083905 | 0 | 0 | 0 |  | 44880 | 688754 | 791297 | 288360 | 0 | 298080 | 197376 | 527520 | 0 | 0 | 0 | 0 | 6718000 | 0 | 2458909 | 0 | 1031688 | 1285440 | 0 | 1255164 | 0 | 689824 | 170414 | 0 | 214020 | 703200 | 220910 | 2319360 | 1082880 | 0 | 0 | 3550 | 864000 | 954720 | 0 | 67392 | 3761754 | 0 | 670752 | 0 | 0 | 4276990 | 195000 | 0 | 231660 | 7302500 | 336384 | 0 | 0 | 1816582 | 0 | 0 | 187200 | 0 | 614160 | 129600 | 522240 | 734400 | 209090 | 8736000 | 969600 | 830400 | 368000 | 26160 | 991091 | 126788 | 375526 | 1672380 | 799680 | 495360 | 8261400 | 290880 | 72810 | 194400 | 370091 | 0 | 183600 | 72932 | 274560 | 66960 | 8458700 | 889890 | 0 | 7887272 | 9600 | 3861818 | 5500454 | 3181045 |  | 19313454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155310 | 254592 | 0 | 738000 | 127694 | 81120 | 0 | 0 | 0 | 100381 | 0 | 682636 | 330050 | 265330 | 363665 | 75634 | 126220 | 0 | 0 | 133326 | 0 | 0 | 4119500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3742209 | 0 | 8957454 | 97920 | 0 | 249888 | 0 | 277958 | 0 | 35493 | 227328 | 27026000 | 5054564 | 0 | 194400 | 14160 | 410400 | 339072 | 0 | 0 | 640000 | 141910 | 3905500 | 29388364 | 620630 | 0 |  | 125601947 | 108190162 | 233792109 | 69557498 | 19313454 | 39711550 | 0 | 17649219 | 76828454 | 900600 | 0 | 5974729 | 2319360 | 1527645 | 9600 | 0
Fuel Cost | 0 | 0 | 16003441.74 | 0 | 0 | 0 | 0 | 14743296 | 0 |  | 0 | 0 | 0 | 967449.6 | 15989958.6 | 4066484.56 | 17797701.6 | 0 | 0 | 2276352 | 10701072 | 23928547.2 | 4332749.35 | 0 | 0 | 0 | 703375.2 | 642409.12 | 1248402.24 | 0 | 342000 | 0 | 0 | 0 | 3808382.4 | 0 | 0 | 0 | 0 | 0 | 3354539.16 | 16217656.95 | 0 | 0 | 0 |  | 789439.2 | 12128957.94 | 14172129.27 | 5496141.6 | 0 | 4906396.8 | 734238.72 | 0 | 0 | 0 | 0 | 0 | 20557080 | 0 | 8237345.15 | 0 | 3476788.56 | 5630227.2 | 0 | 5033207.64 | 0 | 12354747.84 | 3077676.84 | 0 | 160515 | 2615904 | 165682.5 | 15215001.6 | 3367756.8 | 0 | 0 | 0 | 3369600 | 3561105.6 | 0 | 306633.6 | 12865198.68 | 0 | 3722673.6 | 0 | 0 | 11932802.1 | 1283100 | 0 | 926640 | 22564725 | 252288 | 0 | 0 | 37058272.8 | 0 | 0 | 3596112 | 0 | 10815357.6 | 0 | 9301094.4 | 12741840 | 3466712.2 | 23150400 | 18480576 | 15578304 | 6601920 | 0 | 16204337.85 | 2464758.72 | 6736936.44 | 31959181.8 | 15521788.8 | 8822361.6 | 21975324 | 4965321.6 | 0 | 3555576 | 6210126.98 | 0 | 3280932 | 0 | 4947571.2 | 1134302.4 | 25122339 | 12529651.2 | 0 | 54974285.84 | 0 | 22784726.2 | 0 | 0 |  | 54270805.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2921381.1 | 4788875.52 | 0 | 2332080 | 605269.56 | 1398508.8 | 0 | 0 | 0 | 1797823.71 | 0 | 11475111.16 | 7023464 | 5059843.1 | 6513240.15 | 1338721.8 | 2260600.2 | 0 | 0 | 100927.782 | 0 | 0 | 34768580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12461555.97 | 0 | 26155765.68 | 1672473.6 | 0 | 4952780.16 | 0 | 5536923.36 | 0 | 0 | 4510187.52 | 175128480 | 15719694.04 | 0 | 3761640 | 0 | 0 | 5882899.2 | 0 | 0 | 4672000 | 0 | 29095975 | 194257086.04 | 0 | 0 |  | 700007931.59 | 620462693.192 | 1320470624.782 | 205446257.922 | 54270805.74 | 98044706.55 | 0 | 326941654.6 | 515681133.08 | 0 | 0 | 104871065.29 | 15215001.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 139 | 0 |  | 0 | 0 | 0 | 0 | 80 | 15 | 335 | 0 | 0 | 9 | 25 | 64 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 0 | 4 | 51 | 25 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 167 | 0 | 36 | 53 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 9 | 112 | 33 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 210 | 0 | 0 | 10 | 300 | 12 | 0 | 0 | 195 | 0 | 0 | 9 | 0 | 98 | 19 | 25 | 34 | 8 | 374 | 59 | 17 | 17 | 4 | 64 | 17 | 17 | 88 | 23 | 25 | 340 | 17 | 6 | 17 | 17 | 0 | 0 | 22 | 1 | 0 | 345 | 54 | 0 | 360 | 0 | 158 | 255 | 158 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 4 | 16 | 0 | 0 | 0 | 0 | 0 | 49 | 28 | 8 | 46 | 16 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 0 | 0 | 35 | 0 | 6 | 0 | 5 | 0 | 900 | 180 | 0 | 0 | 3 | 75 | 0 | 0 | 0 | 320 | 23 | 150 | 1321 | 123 | 0 |  | 10688 | DayPeak
Yesterday Evening Peak | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 417 | 0 |  | 0 | 0 | 0 | 9 | 80 | 25 | 90 | 0 | 0 | 9 | 65 | 115 | 13 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 17 | 21 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 212 | 0 | 0 | 0 | 0 | 6 | 73 | 68 | 25 | 0 | 26 | 10 | 30 | 0 | 0 | 0 | 0 | 250 | 0 | 92 | 0 | 46 | 54 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 108 | 38 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 208 | 0 | 0 | 10 | 315 | 12 | 0 | 0 | 105 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 374 | 69 | 105 | 34 | 0 | 80 | 0 | 17 | 105 | 77 | 25 | 340 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 17 | 393 | 145 | 0 | 335 | 0 | 157 | 323 | 105 |  | 785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 66 | 0 | 65 | 7 | 32 | 0 | 0 | 0 | 25 | 0 | 90 | 28 | 42 | 48 | 0 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1170 | 220 | 0 | 35 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 245 | 1410 | 0 | 0 |  | 11433 | EvPeak
Forecast for Evening | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 0 | 75 | 80 | 25 | 335 | 0 | 0 | 60 | 80 | 149 | 34 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 22 | 33 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 75 | 68 | 25 | 0 | 26 | 10 | 30 | 0 | 0 | 0 | 0 | 320 | 0 | 92 | 0 | 46 | 55 | 0 | 51 | 0 | 48 | 8 | 0 | 10 | 33 | 11 | 141 | 65 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 210 | 0 | 0 | 10 | 315 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 400 | 69 | 105 | 17 | 0 | 100 | 0 | 17 | 114 | 68 | 25 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 17 | 390 | 145 | 0 | 355 | 29 | 150 | 250 | 120 |  | 632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 0 | 65 | 7 | 32 | 0 | 0 | 0 | 24 | 15 | 90 | 28 | 42 | 50 | 8 | 35 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1244 | 220 | 0 | 35 | 0 | 0 | 75 | 0 | 0 | 350 | 0 | 250 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 50 | 80 | 15 | 335 | 0 | 0 | 60 | 80 | 64 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 0 | 40 | 59 | 25 | 0 | 6 | 10 | 30 | 0 | 0 | 0 | 0 | 300 | 0 | 68 | 0 | 47 | 55 | 0 | 51 | 0 | 40 | 8 | 0 | 10 | 33 | 11 | 128 | 50 | 0 | 0 | 1.6 | 35 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 210 | 0 | 0 | 10 | 315 | 17 | 0 | 0 | 120 | 0 | 0 | 9 | 0 | 100 | 20 | 25 | 34 | 6 | 400 | 57 | 17 | 17 | 5 | 15 | 17 | 17 | 98 | 38 | 25 | 380 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 350 | 17 | 0 | 350 | 20 | 150 | 250 | 120 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 50 | 28 | 34 | 40 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 410 | 17 | 0 | 35 | 0 | 6 | 0 | 8 | 0 | 1200 | 220 |  | 17 | 6 | 100 | 0 | 0 |  | 350 | 30 | 250 | 1300 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 9 | 80 | 0 | 335 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 16 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 40 | 68 | 25 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 0 | 357 | 0 | 36 | 0 | 41 | 55 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 33 | 11 | 84 | 65 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 211 | 0 | 0 | 10 | 310 | 12 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 18 | 5 | 25 | 34 | 3 | 353 | 56 | 17 | 17 | 1 | 16 | 0 | 17 | 80 | 9 | 25 | 265 | 13 | 7 | 0 | 17 | 0 | 0 | 10 | 0 | 0 | 393 | 17 | 0 | 290 | 8 | 156 | 240 | 100 | 0 | 519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 414 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 740 | 220 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 0 | 1 | 150 | 1121 | 21 | 0 | 0 |  |  |  | 109269048 | 19313454 | 0 | 76828454 | 23623948 | 2319360 | 1527645 | 9600 | 900600
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [11 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 109.269 | 19.3135 | 0 | 76.8285 | 23.6239 | 2.3194 | 1.5276 | 0.0096 | 0.9006
| Minimum Generation |  | 7763 | 4:00
| Highest Generation |  | 11433 | 19:00 | [129 empty] | 0 | [70 empty] | 233.7921
| Day Peak Generation |  | 10688 | 12:00
| Evening Peak Generation |  | 11433 | 19:00 | [200 empty] | 202699852
| HVDC Max Flow |  | 904 | 1:00 | [200 empty] | 202.6999
| HVDC EvPeak Flow |  | 785 | 19:00
| Load factor L.F |  | 85.2% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-02-21
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10688 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7627
Evening Peak Generation : |  |  | 11433 | MW Hour : | 19:00 | Available Max Generation : |  | 12456
E.P. Demand (at gen end) : |  |  | 11600 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 11433 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1456
Total Gen. (MKWH) : |  |  | 233.7921 | System Load Factor : | 85.2% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1020 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-21
Actual : |  | 84.87 | Ft.(MSL) , | Rule curve : | 94.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 837.15 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 303490964.472
: |  |  | Coal : | 515681133.08 | Oil : | 431812719.89 | Total : | 1250984817.442
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 24 | 576:00 | 3823.072 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1045.9496 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1463.8103 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1271.063 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1046.4992 |  |  | 0 | 0%
Mymensingh Area |  | 135 | 3240:00 | 777.6683 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 436.6164 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 363.2198 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 710.409 |  |  | 0 | 0%
Total |  | 159 |  | 10938.3077 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Megnaghat-450 MW.
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:15 | 17:05 | Aminbazar-Airport(Old) 230kV Ckt-1 Forced S/D from Agargaon 230/132kV end Due to Aminbazar ckt -01 S/D due to tripping.
08:22 | 12:32 | Bogura 132/33kV S/S Transformer-2 HT Forced S/D Due to Emergency Maintenance.
08:22 | 12:33 | Bogura 132/33kV S/S Transformer-2 LT Forced S/D Due to Emergency Maintenance.
08:33 |  | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Scheduled S/D Due to Armouring Work (Span 45-46) B-Phase
08:35 | 21:58 | Madaripur 132/33kV S/S T1-405T HT Scheduled S/D Due to OC/EF &Lockout Relay Replacement
08:35 | 21:58 | Madaripur 132/33kV S/S T1-405T LT Scheduled S/D Due to Replacement
08:54 |  | Bhola 225 MW CCPP Syncronized with remarks:- GT-1
09:01 | 11:24 | Rajbari 132/33kV S/S Faridpur - 2 Project Work S/D Due to Faulty energy meter change
09:03 |  | Gollamari 132/33kV S/S Tr-1 LT Project Work S/D Due to 80/120 MVA Tr1 upgradation for G2G
09:04 |  | Gollamari 132/33kV S/S Tr-1 HT Project Work S/D Due to 80/120 MVA Tr1 upgradation for G2G
09:29 | 13:11 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Project Work S/D from Cumilla(S) 132/33kV end Due to P/W Cumilla(N)
09:31 | 13:07 | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Cumilla(N) 230/132/33kV end Due to 132 KV Bus modification work.
09:44 | 11:23 | Savar 132/33kV S/S Capacitor Bank-3 Scheduled S/D Due to hot spot maintenance.
09:47 |  | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Project Work S/D Due to Shutdown by NWZPCL for Project work.
09:48 |  | Gollamari 132/33kV S/S E07 Gollamari-Gopalgonj Line - 2 Project Work S/D Due to Shutdown by NWZPCL for Project work.
10:12 | 17:23 | Rampur 230/132/33 S/S 132kV BUS-01 Scheduled S/D Due to Bus Culper PT 108S DS showing cross in SAS over view.
working SPMD
| 10:17 | Shyampur 230/132kV S/S 230 kV APR (D04) is restored.
10:18 | 18:42 | Keraniganj-Nawabganj 132kV Ckt-2 Scheduled S/D from Nawabganj 132/33kV end Due to Deadline checking (Yearly
Maintenance) and from Keranigonj 230/132/33kV end Due to Work at Nawabganj end.
10:18 |  | Rampal 1320 MW (BIFPCL) Syncronized with remarks:- U2
11:12 |  | Haripur 412 MW CCPP Syncronized with remarks:- ST
11:28 |  | Meghnaghat 400/230kV T2 transformer was switched on
11:40 | 17:29 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end Due to Shut down taken by orion
11:40 | 17:33 | Goalpara-Labanchura 132kV Ckt-2 Project Work S/D from Goalpara 132/33kV end Due to TOWER AND LINE CONSTRUCTION
WORK BY NWPGCL
12:00 |  | Day Peak Generation: 10688 MW.
12:12 | 14:33 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-2 Scheduled S/D Due to CB GAS Pressure Meter change
12:12 | 14:35 | Char Saidpur - Madongonj 132kV ckt-2 Project Work S/D from Charsaidpur 132/33kV end Due to GD meter Installation at
various bay
12:28 | 15:06 | Sholosohor 132/33kV S/S TRAFO-02 LT Forced S/D Due to Nest removing & making bird fench ,33kv bus-2 , taken by BPDB
| 12:33 | Bogura 132/33kV S/S Transformer-2 LT is restored.
12:45 | 13:34 | Haripur-Siddirganj 132kV Ckt-2 Tripped from Haripur 230/132kV end showing Distance and aided trip, E/F, CN.
relays Due to Trip
12:45 |  | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Didtance PH R, PH Y. Z-1, Distance Send. relays Due to trip.
12:46 |  | Siddhirganj 335 MW CCPP Shutdown with remarks:- GT
12:46 |  | Siddhirganj 335 MW CCPP Tripped with remarks:- grid trip
12:46 |  | Haripur 412 MW CCPP Tripped with remarks:- V/Hz relay trip
12:46 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U2
12:46 | 13:42 | Haripur-Siddirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing R,Y, & B phase pic up relays Due to |  |  |  |  | 36.0MW load interruption.
Ullon-2 fault
12:46 | 13:23 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Tripped showing LBB initiation,86 relays Due to Ullon -2 fault
12:46 | 13:16 | Siddhirganj 132/33kV S/S 132kV MTR 2 Tripped showing N/A relays Due to Ullon-2 trip |  |  |  |  | 132.0MW load interruption.
12:46 | 13:11 | Siddhirganj 132/33kV S/S 132kV MTR 1 Tripped showing N/A relays Due to Ullon-2 fault
12:46 |  | Siddhirganj 230/132kV S/S MTR 2 HT Tripped showing RET 670 relays Due to trip
12:46 |  | Siddhirganj 230/132kV S/S MTR 1 HT Tripped showing RET 670 relays Due to TRIP
12:48 | 13:21 | Rajbari 132/33kV S/S Transformer-1 LT Tripped showing Scada relays Due to None |  |  |  |  | 17.0MW load interruption.
| 12:50 | Barishal 230/132kV S/S ATR-1 LT is restored.
| 12:55 | Barishal 230/132kV S/S ATR-1 HT is restored.
12:56 | 13:14 | Siddhirganj 132/33kV S/S T-1 HT Forced S/D Due to Ullon-2 fault
12:57 | 13:14 | Siddhirganj 132/33kV S/S T-2 HT Forced S/D Due to Ullon-2 fault
12:59 |  | Siddhirganj-Ullon (T at Haripur) 132kV Ckt-2 Forced S/D from Siddhirganj 132/33kV end Due to Line DS, Post
insulator are broking, R,Y,B -phase loop (Conductor) disconnect
13:03 | 13:16 | Matuail-Siddhirganj 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Ullon-2 fault
13:03 | 13:38 | Siddhirganj 132/33kV S/S 210MW PDB L3 Forced S/D Due to Ullon-2 fault
13:04 | 16:35 | Siddhirganj-Ullon (T at Maniknagar) 132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Ullon-2 fault
13:05 | 13:43 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due to Ullon-2 fault
13:07 | 13:42 | Haripur-Siddirganj 230kV Ckt-2 Forced S/D from Siddhirganj 132/33kV end Due to Ullon-2 fault
13:08 | 13:28 | Siddhirganj 132/33kV S/S T-2 LT Forced S/D Due to Ullon-2 fault
13:08 | 13:27 | Siddhirganj 132/33kV S/S T-1 LT Forced S/D Due to Ullon-2 fault
13:19 | 04:15 | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due to low voltage.
13:19 | 15:55 | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 Project Work S/D from Cumilla(S) 132/33kV end Due to p/w Cumilla(N) End
14:15 | 15:55 | Sholosohor 132/33kV S/S TRAFO-01 LT Forced S/D Due to Nest Removing & making bird fench, 33kV Bus-1,taken by BPDB
14:30 | 14:46 | Rajbari 132/33kV S/S Transformer-2 HT Project Work S/D
14:30 | 14:46 | Rajbari 132/33kV S/S Transformer-2 LT Project Work S/D
14:31 | 17:53 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to Maintenance
14:32 | 17:57 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to Maintenance
14:38 | 16:20 | Charsaidpur 132/33kV S/S 132/33 kV GT-2 HT Project Work S/D Due to Gd meter installation
15:05 |  | Haripur 230/132kV S/S Ullon (Maniknagar-2) Forced S/D Due to Trip and Shuttdown by NLDC.
| 15:06 | Sholosohor 132/33kV S/S TRAFO-02 LT is restored.
15:40 |  | Haripur EGCB 412 MW CCPP GT was sync.
15:40 |  | Haripur 412 MW CCPP Syncronized with remarks:- GT
| 15:44 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 15:55 | Sholosohor 132/33kV S/S TRAFO-01 LT is restored.
15:57 | 17:30 | Cumilla(S) 132/33kV S/S Cumilla North-2 Project Work S/D
16:15 | 16:27 | Kodda 132/33kV S/S Summit 149 MW PS Forced S/D Due to Straw removal
| 16:34 | Saidpur 132/33kV S/S TR-3 (424T) LT is restored.
16:36 |  | Ullon - Siddhirgonj 132KV CKT-1 was switched on.
| 17:05 | Aminbazar-Airport(Old) 230kV Ckt-1 is restored.
17:19 |  | Haripur 412 MW CCPP Syncronized with remarks:- ST
17:25 |  | Meghnaghat- Aminbazar 400 kV Line-2 was switched on.
| 17:30 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT is restored.
17:39 |  | Siddhirganj 335 MW CCPP Syncronized with remarks:- GT
| 17:51 | Aminbazar-Meghnaghat 230kV Ckt-2 is restored.
18:10 |  | Meghnaghat 400/230 kv T-2 tripped showing Lock Out.
18:55 |  | Siddhirganj 335 MW CCPP Syncronized with remarks:- ST
18:55 |  | Siddhirgonj 335 MW CCPP ST was sync.
19:00 |  | Evening Peak Gen. 11434 MW
| 19:43 | Aminbazar-Meghnaghat 230kV Ckt-1 is restored.
19:44 |  | Meghnaghat- Aminbazar 400 kV Line-1 was switched on.
21:20 |  | Meghnaghat 400/230 kv T-2 was switched on.
02:04 | 03:19 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by PBS
02:05 | 03:16 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by PBS. Madhobpur feeder -01 Red hot
maintenance.
04:13 |  | Aminbazar-Meghnaghat 230kV Ckt-2 Tripped from Aminbazar 400/230/132kV end showing * 86-1 Master Relay
operated* 86-2 Master Relay operated* BFP INITIATION* Ground Dist. 1, 2,4 relays.
04:13 |  | Aminbazar-Meghnaghat 230kV Ckt-1 Tripped from Aminbazar 400/230/132kV end showing * 86-1 Master Relay
operated* 86-2 Master Relay operated* BFP INITIATION relays.
04:44 | 05:26 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Tripped showing General TripOC/EF Trip relays.
04:44 | 06:10 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing O/C relays Due to Trip.
04:57 |  | Aminbazar-Airport(Old) 230kV Ckt-2 Tripped from Agargaon 230/132kV end showing Distance Relay, Bay control unit,
Differential Relay relays Due to None and from Aminbazar 400/230/132kV end showing * Diff Trip* Dist Protecton
operated* L1,L2,L3 Operated* Z1,Z2,Z3 Trip* 21 CARR Aided relays.
05:00 | 05:22 | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ghorashal 230kV end showing Distance relay 1 and 2 relays.
06:00 |  | Minimum Generation = 7,627MW
06:15 | 07:47 | Narail 132/33kV S/S TR2 (413-T) LT Scheduled S/D Due to Emergency maintenance work due to snapping of sky |  |  |  |  | 15.0MW
|  | wire of 33 KV feeder No. 07 of JPBS-01. |  |  |  |  | load
06:16 | 07:46 | Narail 132/33kV S/S TR2 (413-T) HT Scheduled S/D Due to Emergency maintenance work due to snapping of sky |  |  |  |  | 15.0MW
wire of 33 KV feeder No. 07 of JPBS-01.
06:41 | 07:04 | Fatullah-Madanganj 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing 67-Directional OC protection Relay
relays Due to Directional OC protection trip
06:43 | 07:05 | Aminbazar-Airport(Old) 230kV Ckt-1 Tripped from Agargaon 230/132kV end showing Distance Relay, Differential |  |  |  |  | 144.0MW
|  | Relay relays. and from Aminbazar 400/230/132kV end showing * Diff Trip* L1,L2,L3 Operated* Z1 Trip* EFCOM |  |  |  |  | load
|  | operated relays. |  |  |  |  | interrup.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 190 | 3730406
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 417 | 5119200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 48960 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 80 | 855078 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 25 | 230788 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 232319 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 115200 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 90 | 5835312 | ST sync. at 18:55.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 65 | 596160 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 38520 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1232160 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 40762 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 68256 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 955320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 18 | 480300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 212640 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 105 | 1816582 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 614160 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 830400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 290880 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 72932
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 66960 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 323 | 5500454 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 105 | 3181045 | On test.
| Dhaka area Total |  |  |  | 5062 | 1842 | 33176694
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 177114 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 129600
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 26 | 298080 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 900600 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 212 | 5083905
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 368000 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 73 | 688754 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 791297 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 288360 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 522240 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 197376 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 527520
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 991091 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 126788 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 375526 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 495360 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 370091 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 889890
| SS Power I |  | SS Power | 2*612 | 1224 | 335 | 7887272
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 9600 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 157 | 3861818 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4344 | 1336 | 25006442
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 0 | Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6718000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 393 | 8458700
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 1031688
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 54 | 1285440
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 92 | 2458909 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1255164
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 209090 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 689824 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 734400 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 214020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2319360
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 703200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 170414 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 11 | 220910 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 105 | 1672380 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 799680 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 183600 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 42 | 274560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1384 | 29399339
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 38 | 1082880 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 187200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 969600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 72810
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 44880 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 122 | 2360920
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 864000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 954720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3761754
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 67392 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 670752 | GT-9 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 208 | 4276990
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 195000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 336384 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7302500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 374 | 8736000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 231660
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8261400 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1528 | 35658552
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 785 | 19313454
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 46 | 155310 | Fuel shortage
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 66 | 254592 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 97920 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 410400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 640000 | Unit-1 U/M & Unit-2 tripped at 12:46
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 897 | 20871676
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 81120 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 7 | 127694 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 738000
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 27026000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5054564
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 194400 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 245 | 3905500 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1774 | 37127278
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 100381 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 330050 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 265330 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 48 | 363665
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 141 | 3742209 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8957454
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 126220 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 133326 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 75634 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 682636 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 249888 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 227328 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 14160
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1410 | 29388364
| Rajshahi Area Total |  |  |  | 3631 | 2274 | 44656645
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4119500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 277958 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35493
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 71 | 339072 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 141910
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 620630
| Rangpur Area Total |  |  |  | 950 | 276 | 5534563
| Total |  |  |  | 25481 | 11433 | 233792109
| Eastern Grid Total |  |  |  | 15398 | 6212 | 125601947
| Western Grid Total |  |  |  | 10083 | 5221 | 108190162
| National Grid Total |  |  |  | 25481 | 11433 | 233792109
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-20
| (a) ENTIRE EASTERN GRID : |  | 7403.27 | MW | (b) ENTIRE WESTERN GRID : |  | 3482.1 | MW
| i) Dhaka area |  | 4220.77 | MW | i) Khulna area |  | 1295.6 | MW
| ii) Chittagong area |  | 1035.5 | MW | ii) Rajshahi area |  | 1136.4 | MW
| iii) Comilla area |  | 902 | MW | iii) Barisal area |  | 296.1 | MW
| iv) Mymensingh area |  | 869 | MW | iv) Rangpur area |  | 754 | MW
| v) Sylhet area |  | 376 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10885.37 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 18:00 | Kamrangirchar | 50.7 | 13:00 | Narinda | 46 | 13:00 | Sherpur | 122 | 18:00
2 | AKSML | 105 | 14:00 | Chowmuhani | 154 | 19:30 | Kaptai | N/A | N/A | Narshingdi | 150 | 19:00 | Shikalbaha | 23 | 11:00
3 | Aftabnagar | 28 | 18:30 | Chuadanga | 77 | 19:00 | Kazla | 78 | 16:00 | Natore | 115 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 56 | 13:00 | Coxsbazar | 106 | 18:30 | Keranigonj | 66 | 18:30 | Nawabganj | 30 | 21:00 | Shitalakhya | 84.6 | 12:00
5 | Agrabad | 56 | 18:30 | Cumilla(N) | 114 | 18:00 | Khagrachori | 28 | 18:30 | Netrakona | 119 | 07:00 | Sholosohor | 32 | 10:00
6 | Amnura | 57 | 08:00 | Cumilla(S) | 114 | 14:00 | Khulna | 81 | 19:00 | New | 20.5 | 12:00 | Shyampur | 160 | 12:00
7 | Ashuganj | 49 | 12:00 | Daudkandi | 101 | 21:00 | Khulshi | 145 | 12:00 | Niamatpur | 82 | 09:00 | Siddhirganj | 106 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 22 | 13:00 | Kishoreganj | 106 | 21:00 | Noapara | 39 | 19:00 | Sirajganj | 94 | 07:00
9 | BSRM | 137 | 07:00 | Dhamrai | 116 | 12:00 | Kodda | 277 | 18:30 | PHP | 4 | 12:00 | Sonargaon | 97 | 12:00
10 | Bagerhat | 71 | 19:00 | Dhanmondi | 92 | 14:00 | Kulaura | 26 | 18:00 | Pabna | 87 | 19:00 | Sreemongol | 44 | 18:30
11 | Bakulia | 68 | 18:30 | Dohazari | 63 | 18:30 | Kurigram | 62 | 08:00 | Palashbari | 96 | 08:00 | Sreepur | 61 | 18:30
12 | Banani | 35.4 | 14:00 | Faridpur | 114 | 18:30 | Kushtia | 114 | 18:30 | Panchagarh | 45 | 18:30 | Srinagar | 31.03 | 21:00
13 | Bangabhaban | 11 | 10:00 | Fatullah | 56 | 12:00 | Lalbag | 83 | 13:00 | Patuakhali | 53.4 | 21:00 | Sunamganj | 35 | 18:30
14 | Barapukuria | 59 | 08:00 | Fenchuganj | 24 | 18:30 | Lalmonirhat | 38 | 18:00 | Payra | 15.4 | 18:30 | Sylhet | 12 | 18:00
15 | Barguna | 14 | 20:00 | Feni | 73 | 19:00 | MI_Cement | 11.8 | 19:30 | Postogola | 43 | 13:00 | Sylhet-132 | 98 | 18:00
16 | Barishal | 79 | 21:00 | GPH | 81 | 01:00 | Madanganj | 40 | 18:30 | Purbachal | 15 | 18:30 | TK | 13.5 | 18:00
17 | Barishal-230 | 64 | 18:30 | Ghorashal | 67 | 18:00 | Madaripur | 67 | 19:00 | Purbasadipur | 111 | 13:00 | Tangail | 162 | 18:30
18 | Baroaulia | 69 | 12:00 | Goalpara | 22 | 13:00 | Madartek | 60.58 | 19:00 | Rahim | 50 | 09:00 | Thakurgaon | 78 | 19:00
19 | Baroirhat | 48 | 19:00 | Gollamari | 39 | 13:00 | Madunaghat | 36 | 18:00 | Rajbari | 52 | 19:00 | Tongi | 119 | 12:00
20 | Bashundhara | 141 | 12:00 | Gopalganj | 81.6 | 19:00 | Magura | 47 | 18:30 | Rajendrapur | 80 | 19:00 | Ullahpara | 23 | 07:00
21 | BashundharaCement | 7 | 11:00 | Gulshan | 84 | 13:00 | Mahasthangarh | 52 | 08:00 | Rajshahi | 105 | 19:00 | Ullon | 36 | 18:00
22 | Beanibazar | 42 | 19:00 | Halishahar | 68 | 15:00 | Manikganj | 95 | 19:30 | Rajshahi-230 | 27 | 19:00 | Uttara | 48 | 15:00
23 | Benapole | 52 | 08:00 | HaripurSBU | 184 | 12:00 | Maniknagar | 60 | 13:00 | Ramganj | 70 | 19:30 | UttaraNew | 32 | 13:00
24 | Bhaluka | 102 | 07:00 | Hasnabad | 71 | 12:00 | Matarbari | 32 | 18:30 | Rampur | 20 | 18:00 | Zigatola | 48 | 18:30
25 | Bhandaria | 34 | 20:00 | Hathazari | 70 | 13:00 | Matuail | 61 | 17:00 | Rangamati | 12 | 18:00
26 | Bhangura | 30 | 18:00 | Ishurdi | 53 | 19:00 | Millgate | 94 | 12:00 | Rangpur | 104 | 18:30
27 | Bheramara(GK) | 42 | 18:30 | Jaldhaka | 66 | 08:00 | Mirpur | 101 | 18:30 | Ruppur | 4.8 | 15:00
28 | Bhulta | 260 | 12:00 | Jamalpur | 139 | 21:00 | Mirsorai | 4 | 18:30 | SSM | 16 | 03:00
29 | Bog-Sherpur | 68 | 09:00 | Jashore | 108 | 13:00 | Mirzapur | 56 | 07:00 | Saidpur | 102 | 10:00
30 | Bogura | 120 | 19:30 | Jhenaidah | 95 | 18:30 | Mithapukur | 50 | 08:00 | Satkhira | 95 | 18:30
31 | Borhanuddin | 52 | 21:00 | Joydebpur | 152 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 87 | 14:00
32 | Brahmanbaria | 112 | 19:00 | Joypurhat | 54 | 09:00 | Mogbazar | 95.5 | 14:00 | Savar | 174 | 11:00
33 | Cantonment | 102 | 19:00 | Juldah | 17 | 15:00 | Mongla | 24 | 10:00 | SevenRings | 21.9 | 21:00
34 | Chandpur | 46 | 19:00 | KSRM | 31 | 18:30 | Motijheel | 33 | 13:00 | ShahCement | 23 | 02:00
35 | Chandraghona | 24 | 18:30 | Kabirpur | 244 | 12:00 | Munshiganj | 65 | 18:30 | Shahjadpur | 65 | 07:00
36 | Chapai | 59 | 09:00 | Kachua | 50 | 21:00 | Mymensingh | 184 | 08:00 | Shahjibazar | 86 | 18:30
37 | Charsaidpur | 42 | 05:00 | Kallyanpur | 90 | 18:00 | Naogaon | 110 | 09:00 | Shahmirpur | 46 | 23:00
38 | Chauddagram | 50 | 18:00 | Kalurghat | 28 | 10:00 | Narail | 41 | 18:30 | Shariatpur | 52 | 19:30
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 411 | 06:00 | 393 | 11:00 | Gopalganj | 415 | 01:00 | 397 | 11:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 396 | 20:00 | 386 | 14:00
| Bhulta | 386 | 01:00 | 372 | 14:00 | Madunaghat_I | 415 | 00:00 | 406 | 05:00
| Bibiana | 415 | 13:00 | 407 | 03:00 | Payra | 420 | 01:00 | 410 | 12:00
| BIPTC | 406 | 03:00 | 389 | 13:00 | Rahanpur | 415 | 04:00 | 394 | 10:00
| Bogura | 407 | 04:00 | 381 | 08:00 | Rampal | 419 | 01:00 | 390 | 11:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 01:00 | 221 | 14:00 | Haripur | 226 | 02:00 | 219 | 14:00
| AKSML | 236 | 19:00 | 225 | 05:00 | Hasnabad | 230 | 05:00 | 222 | 12:00
| Aminbazar | 234 | 06:00 | 224 | 14:00 | Hathazari | 237 | 20:00 | 227 | 06:00
| Ashuganj | 235 | 01:00 | 227 | 12:00 | Ishurdi | 236 | 03:00 | 225 | 11:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 234 | 01:00 | 221 | 11:00
| Baghabari | 233 | 01:00 | 223 | 12:00 | Kaliakoir | 232 | 01:00 | 222 | 14:00
| Barapukuria | 223 | 03:00 | 209 | 08:00 | Keranigonj | 230 | 01:00 | 221 | 11:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 242 | 01:00 | 225 | 11:00
| Barishal | 245 | 01:00 | 238 | 14:00 | Madunaghat_I | 234 | 00:00 | 225 | 05:00
| Bheramara | 235 | 03:00 | 223 | 11:00 | Maniknagar | 229 | 03:00 | 2 | 10:00
| Bhulta | 231 | 01:00 | 220 | 14:00 | Meghnaghat | 234 | 01:00 | 224 | 09:00
| Bibiana | 237 | 01:00 | 233 | 05:00 | Mirsorai | 238 | 19:30 | 224 | 04:00
| BIPTC | 236 | 04:00 | 223 | 11:00 | Rajshahi | 238 | 04:00 | 226 | 22:00
| Bogura | 232 | 05:00 | 218 | 08:00 | Rampal | 238 | 01:00 | 223 | 11:00
| Bogura-400 | 235 | 04:00 | 219 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 19:30 | 242 | 13:00 | Rampura | 231 | 03:00 | 219 | 14:00
| BSRM | 237 | 20:00 | 225 | 05:00 | Shikalbaha | 233 | 19:30 | 225 | 05:00
| Cumilla(N) | 233 | 01:00 | 224 | 13:00 | Shyampur | 236 | 19:00 | 221 | 16:00
| Fenchuganj | 241 | 00:00 | 234 | 18:00 | Siddhirganj | 230 | 23:00 | 220 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 236 | 00:00 | 231 | 14:00
| Ghorashal-230 | 230 | 02:00 | 221 | 11:00 | Sreepur | 231 | 03:00 | 221 | 04:00
| GPH | 236 | 20:00 | 225 | 05:00 | Tongi | 228 | 03:00 | 220 | 08:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 131 | 01:00 | 122 | 14:00 | Lalbag | 135 | 06:00 | 128 | 10:00
| Agargaon | 138 | 01:00 | 130 | 14:00 | Lalmonirhat | 128 | 00:00 | 120 | 05:00
| Agrabad | 136 | 00:00 | 130 | 12:00 | Madanganj | 134 | 05:00 | 129 | 11:00
| AKS | 134 | 00:00 | 129 | 11:00 | Madaripur | 138 | 05:00 | 132 | 12:00
| Aminbazar | 131 | 01:00 | 126 | 08:00 | Madartek | 131 | 01:00 | 122 | 14:00
| Amnura | 139 | 18:00 | 123 | 08:00 | Madunaghat | 137 | 14:00 | 132 | 06:00
| Ashuganj | 137 | 05:00 | 132 | 11:00 | Magura | 139 | 04:00 | 127 | 12:00
| Bagerhat | 134 | 05:00 | 120 | 13:00 | Mahasthangarh | 135 | 03:00 | 122 | 08:00
| Bakulia | 137 | 00:00 | 131 | 12:00 | Manikganj | 138 | 13:00 | 120 | 18:30
| Banani | 132 | 01:00 | 124 | 14:00 | Maniknagar | 134 | 04:00 | 125 | 13:00
| Bangabhaban | 134 | 01:00 | 125 | 13:00 | Matarbari | 130 | 14:00 | 122 | 22:00
| Barapukuria | 136 | 03:00 | 124 | 08:00 | Matuail | 133.7 | 01:00 | 127.4 | 14:00
| Barguna | 132 | 04:00 | 128 | 14:00 | Millgate | 137 | 01:00 | 129 | 14:00
| Barishal | 140 | 01:00 | 126 | 11:00 | Mirpur | 130 | 03:00 | 124 | 11:00
| Barishal-230 | 139 | 01:00 | 135 | 08:00 | Mirzapur | 133 | 00:00 | 127 | 08:00
| Baroaulia | 137 | 00:00 | 132 | 11:00 | Mithapukur | 134 | 03:00 | 116 | 08:00
| Baroirhat | 137 | 01:00 | 129 | 06:00 | MI_Cement | 134 | 05:00 | 129 | 12:00
| Bashundhara | 137 | 02:00 | 124 | 14:00 | Modern | 137 | 19:30 | 131 | 12:00
| BashundharaCement | 134 | 05:00 | 129 | 11:00 | Mogbazar | 132 | 04:00 | 123 | 14:00
| Beanibazar | 135 | 01:00 | 131 | 12:00 | Mongla | 134 | 04:00 | 121 | 12:00
| Benapole | 134 | 02:00 | 12 | 18:30 | Motijheel | 134 | 01:00 | 125 | 13:00
| Bhaluka | 130 | 04:00 | 122 | 12:00 | Munshiganj | 133 | 04:00 | 129 | 11:00
| Bhandaria | 130 | 10:00 | 125 | 01:00 | Mymensingh | 133 | 20:00 | 117 | 12:00
| Bhangura | 136 | 00:00 | 130 | 12:00 | Naogaon | 133 | 03:00 | 120 | 08:00
| Bheramara | 137 | 04:00 | 129 | 11:00 | Narail | 138 | 04:00 | 127 | 11:00
| Bheramara(GK) | 136 | 04:00 | 129 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 123 | 03:00 | 117 | 12:00 | Narshingdi | 132 | 06:00 | 123 | 11:00
| Bog-Sherpur | 136 | 03:00 | 125 | 07:00 | Natore | 135 | 03:00 | 128 | 08:00
| Bogura | 137 | 03:00 | 126 | 08:00 | Nawabganj | 135 | 01:00 | 127 | 14:00
| Bogura-230 | 137 | 04:00 | 126 | 08:00 | Netrakona | 128 | 01:00 | 115 | 12:00
| Brahmanbaria | 131 | 00:00 | 127 | 11:00 | New | 137 | 03:00 | 130 | 14:00
| Cantonment | 138 | 01:00 | 130 | 14:00 | Niamatpur | 135 | 03:00 | 126 | 08:00
| Chandpur | 137 | 17:00 | 130 | 11:00 | Noapara | 135 | 05:00 | 124 | 12:00
| Chandraghona | 138 | 00:00 | 132 | 05:00 | Pabna | 138 | 03:00 | 129 | 12:00
| Chapai | 135 | 03:00 | 126 | 08:00 | Palashbari | 132 | 03:00 | 117 | 08:00
| Charsaidpur | 134 | 01:00 | 130 | 11:00 | Panchagarh | 134 | 21:00 | 108 | 08:00
| Chauddagram | 138 | 19:00 | 130 | 04:00 | Patuakhali | 131 | 00:00 | 8 | 21:00
| Chhatak | 136 | 01:00 | 132 | 11:00 | Payra | 133 | 01:00 | 130 | 14:00
| Chowmuhani | 135 | 18:00 | 130 | 02:00 | PHP | 138 | 20:00 | 129 | 04:00
| Chuadanga | 136 | 03:00 | 123 | 12:00 | Postogola | 135 | 05:00 | 130 | 11:00
| Coxsbazar | 128 | 00:00 | 121 | 18:30 | Purbachal | 134 | 00:00 | 123 | 14:00
| Cumilla(N) | 139 | 01:00 | 133 | 11:00 | Purbasadipur | 130 | 20:00 | 112 | 08:00
| Cumilla(S) | 138 | 00:00 | 126 | 12:00 | Rahanpur | 137 | 03:00 | 130 | 08:00
| Daudkandi | 131 | 01:00 | 119 | 09:00 | Rahim | 133 | 03:00 | 129 | 14:00
| Dhaka | 131 | 03:00 | 122 | 14:00 | Rajbari | 137 | 01:00 | 130 | 11:00
| Dhamrai | 136 | 01:00 | 130 | 11:00 | Rajendrapur | 136 | 10:00 | 130 | 08:00
| Dhanmondi | 135 | 05:00 | 122 | 14:00 | Rajshahi | 134 | 19:00 | 126 | 22:00
| Dohazari | 135 | 00:00 | 129 | 06:00 | Rajshahi-230 | 133 | 04:00 | 123 | 11:00
| Faridpur | 137 | 06:00 | 132 | 08:00 | Ramganj | 135 | 00:00 | 128 | 11:00
| Fatullah | 136 | 01:00 | 32 | 13:00 | Rampur | 136 | 00:00 | 131 | 05:00
| Fenchuganj | 137 | 00:00 | 135 | 10:00 | Rampura | 132 | 01:00 | 124 | 14:00
| Feni | 137 | 00:00 | 127 | 06:00 | Rangamati | 137 | 00:00 | 131 | 12:00
| Ghorashal | 138 | 02:00 | 131 | 12:00 | Rangpur | 131 | 04:00 | 116 | 08:00
| Goalpara | 137 | 01:00 | 124 | 12:00 | Ruppur | 139 | 06:00 | 132 | 11:00
| Gollamari | 137 | 01:00 | 126 | 12:00 | Saidpur | 132 | 04:00 | 114 | 08:00
| Gopalganj | 136 | 01:00 | 130 | 08:00 | Satkhira | 134 | 05:00 | 122 | 18:30
| Gopalganj-400 | 138 | 01:00 | 132 | 10:00 | Satmasjid | 157 | 01:00 | 130 | 11:00
| Gulshan | 132 | 04:00 | 124 | 14:00 | Savar | 138 | 02:00 | 122 | 11:00
| Halishahar | 136 | 00:00 | 131 | 11:00 | SevenRings | 138 | 03:00 | 131 | 12:00
| Haripur | 133 | 03:00 | 129 | 14:00 | ShahCement | 134 | 01:00 | 130 | 11:00
| HaripurSBU | 133 | 03:00 | 129 | 14:00 | Shahjadpur | 142 | 04:00 | 132 | 08:00
| Hasnabad | 135 | 01:00 | 130 | 12:00 | Shahjibazar | 132 | 01:00 | 128 | 11:00
| Hathazari | 139 | 19:00 | 133 | 06:00 | Shahmirpur | 136 | 19:00 | 131 | 12:00
| Ishurdi | 139 | 01:00 | 132 | 11:00 | Shariatpur | 137 | 00:00 | 131 | 10:00
| Jaldhaka | 132 | 21:00 | 110 | 07:00 | Sherpur | 126 | 18:30 | 108 | 04:00
| Jamalpur | 131 | 18:30 | 113 | 04:00 | Shikalbaha | 125 | 00:00 | 119 | 06:00
| Jashore | 135 | 01:00 | 123 | 12:00 | Shikalbaha-230 | 137 | 01:00 | 132 | 05:00
| Jhenaidah | 135 | 00:00 | 128 | 11:00 | Shitalakhya | 134 | 05:00 | 129 | 12:00
| Jhenaidah-230 | 138 | 01:00 | 129 | 11:00 | Sholosohor | 136 | 00:00 | 130 | 12:00
| Joydebpur | 137 | 00:00 | 128 | 12:00 | Shyampur | 136 | 06:00 | 130 | 14:00
| Joypurhat | 132 | 03:00 | 118 | 08:00 | Shyampur-230 | 136 | 20:00 | 128 | 09:00
| Juldah | 136 | 00:00 | 132 | 04:00 | Siddhirganj | 133 | 01:00 | 128 | 14:00
| Kabirpur | 139 | 10:00 | 117 | 18:30 | Sirajganj | 136 | 04:00 | 126 | 07:00
| Kachua | 137 | 19:00 | 129 | 05:00 | Sonargaon | 133 | 05:00 | 125 | 16:00
| Kaliakoir | 139 | 10:00 | 131 | 07:00 | Sreemongol | 133 | 00:00 | 130 | 10:00
| Kallyanpur | 136 | 02:00 | 128 | 18:30 | Sreepur | 132 | 03:00 | 126 | 11:00
| Kalurghat | 136 | 00:00 | 131 | 05:00 | Srinagar | 135 | 02:00 | 128 | 13:00
| Kamrangirchar | 134 | 01:00 | 128 | 13:00 | SSM | 140 | 00:00 | 138 | 04:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 02:00 | 131 | 12:00
| Kazla | 135 | 04:00 | 124 | 15:00 | Sylhet | 135 | 01:00 | 133 | 11:00
| Keranigonj | 135 | 01:00 | 128 | 14:00 | Sylhet-132 | 135 | 00:00 | 134 | 09:00
| Khagrachori | 137 | 01:00 | 131 | 12:00 | Tangail | 132 | 06:00 | 125 | 12:00
| Khulna | 135 | 04:00 | 125 | 12:00 | Thakurgaon | 134 | 21:00 | 109 | 08:00
| Khulna(S) | 137 | 01:00 | 126 | 12:00 | TK | 137 | 17:00 | 132 | 12:00
| Khulshi | 136 | 01:00 | 130 | 06:00 | Tongi | 137 | 04:00 | 132 | 08:00
| Kishoreganj | 136 | 11:00 | 124 | 12:00 | Ullahpara | 138 | 03:00 | 128 | 11:00
| Kodda | 140 | 13:00 | 126 | 12:00 | Ullon | 129 | 00:00 | 121 | 14:00
| KSRM | 137 | 19:30 | 131 | 04:00 | Uttara | 136 | 00:00 | 129 | 16:00
| Kulaura | 136 | 00:00 | 133 | 18:30 | UttaraNew | 134 | 13:00 | 124 | 11:00
| Kurigram | 131 | 05:00 | 111 | 08:00 | Zigatola | 135 | 01:00 | 13 | 10:00
| Kushtia | 138 | 03:00 | 128 | 08:00

## L-Curve
Date | 2024-02-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1460 | 5209 | 4136 | 9345 |  |  |  | QF-LDC-11
0:30 | 1430 | 5002 | 4099.5 | 9101.5 | Date: | 2024-02-20
1:00 | 1400 | 4795 | 4063 | 8858
1:30 | 1360 | 4585.5 | 3978.5 | 8564
2:00 | 1320 | 4376 | 3894 | 8270
2:30 | 1280 | 4374.5 | 3785.5 | 8160 | [5 empty] | Gen. at Eve. Peak | 11433 | 11433 MW (19:00 )
3:00 | 1240 | 4373 | 3677 | 8050 | [6 empty] | 19:00
3:30 | 1250 | 4265.5 | 3641 | 7906.5 | [5 empty] | Gen. at Day Peak | 10688 | 10688 MW (12:00 )
4:00 | 1260 | 4158 | 3605 | 7763 | [6 empty] | 12:00
4:30 | 1245 | 4163.5 | 3610.5 | 7774 | [5 empty] | Highest Generation | 11433
5:00 | 1230 | 4169 | 3616 | 7785 | [6 empty] | 19:00
5:30 | 1225 | 4253 | 3721.5 | 7974.5
6:00 | 1220 | 4337 | 3827 | 8164
6:30 | 1120 | 4643.5 | 3911 | 8554.5
7:00 | 1020 | 4950 | 3995 | 8945
7:30 | 1085 | 5158 | 4176.5 | 9334.5
8:00 | 1150 | 5366 | 4358 | 9724
8:30 | 1260 | 5380.5 | 4481.5 | 9862
9:00 | 1370 | 5395 | 4605 | 10000
9:30 | 1360 | 5441.5 | 4599.5 | 10041
10:00 | 1350 | 5488 | 4594 | 10082
10:30 | 1460 | 5552 | 4688.5 | 10240.5
11:00 | 1570 | 5616 | 4783 | 10399
11:30 | 1605 | 5661.5 | 4882 | 10543.5
12:00 | 1640 | 5707 | 4981 | 10688
12:30 | 1640 | 5433.5 | 4815.5 | 10249
13:00 | 1640 | 5160 | 4650 | 9810
13:30 | 1665 | 5180.5 | 4749 | 9929.5
14:00 | 1690 | 5201 | 4848 | 10049
14:30 | 1705 | 5151.5 | 4740.5 | 9892
15:00 | 1720 | 5102 | 4633 | 9735
15:30 | 1720 | 5041 | 4601 | 9642
16:00 | 1720 | 4980 | 4569 | 9549
16:30 | 1710 | 5056 | 4565.5 | 9621.5
17:00 | 1700 | 5132 | 4562 | 9694
17:30 | 1680 | 5498.5 | 4651.5 | 10150
18:00 | 1660 | 5865 | 4741 | 10606
18:30 | 1550 | 6038.5 | 4981 | 11019.5
19:00 | 1440 | 6212 | 5221 | 11433
19:30 | 1350 | 6162 | 5055 | 11217
20:00 | 1350 | 6163 | 4979 | 11142 |  |  |  | Executive Engineer
20:30 | 1355 | 6142 | 4810.5 | 10952.5 |  |  |  | Network Operation Division
21:00 | 1360 | 6121 | 4642 | 10763
21:30 | 1420 | 5818 | 4600.5 | 10418.5
22:00 | 1480 | 5515 | 4559 | 10074 |  |  |  |  | Page 6 of 7
22:30 | 1475 | 5472 | 4461 | 9933
23:00 | 1470 | 5429 | 4363 | 9792
23:30 | 1465 | 5319 | 4249.5 | 9568.5
24:00 | 1460 | 5209 | 4136 | 9345
11433 MW (19:00 )
10688 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-20 |  | Energy |  | 233792109
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3316 | 896 | 1519 | 0 | 472 | 2948 | 35 | 0 | 65 | 94 | 0 | 0 | 0
0:30 | 3071 | 900 | 1508 | 0 | 442.5 | 2907 | 35 | 0 | 147 | 91 | 0 | 0 | 20.055 |  | Date: | 43880
1:00 | 2826 | 904 | 1497 | 0 | 413 | 2866 | 35 | 0 | 229 | 88 | 0 | 0 | 40.11
1:30 | 2845.5 | 904 | 1474.5 | 0 | 289 | 2795.5 | 35 | 0 | 134.5 | 86 | 0 | 0 | 20.055 | [8 empty] | Total Energy | 233.7921 | 233.7921 | Total Energy Gen 233.792 MKWHr Energy Not Served 3.307 MKWHr Energy Requirement 237.099 MKWHr
2:00 | 2865 | 904 | 1452 | 0 | 165 | 2725 | 35 | 0 | 40 | 84 | 0 | 0 | 0 | [8 empty] | Energy not Served | 3.307 | 3.307
2:30 | 2860 | 818.5 | 1466.5 | 0 | 156.5 | 2701 | 35 | 0 | 40 | 82 | 0 | 0.5 | 0 | [8 empty] | Energy Requirement | 237.0991 | 237.0991
3:00 | 2855 | 733 | 1481 | 0 | 148 | 2677 | 35 | 0 | 40 | 80 | 0 | 1 | 0
3:30 | 2849 | 724 | 1476 | 0 | 74 | 2647.5 | 35 | 0 | 20 | 79 | 0 | 2 | 0 | [7 empty] | Shortage
4:00 | 2843 | 715 | 1471 | 0 | 0 | 2618 | 35 | 0 | 0 | 78 | 0 | 3 | 0
4:30 | 2847 | 714.5 | 1479 | 0 | 0 | 2622 | 35 | 0 | 0 | 75 | 0 | 1.5 | 0
5:00 | 2851 | 714 | 1487 | 0 | 0 | 2626 | 35 | 0 | 0 | 72 | 0 | 0 | 0
5:30 | 2868.5 | 809 | 1524.5 | 0 | 3 | 2648.5 | 35 | 0 | 8 | 78 | 0 | 0 | 45.84
6:00 | 2886 | 904 | 1562 | 0 | 6 | 2671 | 35 | 0 | 16 | 84 | 0 | 0 | 91.68
6:30 | 2975 | 830 | 1647.5 | 0 | 186 | 2768.5 | 35 | 0 | 24.5 | 83 | 5 | 0 | 95.84 | [6 empty] | Coal
7:00 | 3064 | 756 | 1733 | 0 | 366 | 2866 | 35 | 0 | 33 | 82 | 10 | 0 | 100
7:30 | 3106 | 688 | 1765.5 | 0 | 495.5 | 3092.5 | 35 | 0 | 33 | 88 | 31 | 0 | 134 | [5 empty] | Oil
8:00 | 3148 | 620 | 1798 | 0 | 625 | 3319 | 35 | 0 | 33 | 94 | 52 | 0 | 168
8:30 | 3072 | 619.5 | 1785 | 0 | 674 | 3420.5 | 37.5 | 0 | 75.5 | 95 | 82 | 1 | 179.5
9:00 | 2996 | 619 | 1772 | 0 | 723 | 3522 | 40 | 0 | 118 | 96 | 112 | 2 | 191
9:30 | 2926 | 619 | 1715 | 0 | 843 | 3497 | 40 | 0 | 159.5 | 97 | 143.5 | 1 | 199.5
10:00 | 2856 | 619 | 1658 | 0 | 963 | 3472 | 40 | 0 | 201 | 98 | 175 | 0 | 208
10:30 | 2828 | 686 | 1682 | 0 | 1013 | 3456 | 40 | 0 | 245.5 | 101 | 189 | 0 | 176
11:00 | 2800 | 753 | 1706 | 0 | 1063 | 3440 | 40 | 0 | 290 | 104 | 203 | 0 | 144
11:30 | 2816.5 | 828.5 | 1730.5 | 0 | 1070 | 3409.5 | 40 | 0 | 299 | 108 | 241.5 | 0 | 159
12:00 | 2833 | 904 | 1755 | 0 | 1077 | 3379 | 40 | 0 | 308 | 112 | 280 | 0 | 174
12:30 | 2575 | 904 | 1718.5 | 0 | 1082 | 3242.5 | 40 | 0 | 307.5 | 111 | 268.5 | 0 | 235.5025
13:00 | 2317 | 904 | 1682 | 0 | 1087 | 3106 | 40 | 0 | 307 | 110 | 257 | 0 | 297.005
13:30 | 2317 | 904 | 1682 | 0 | 1087 | 3106 | 40 | 0 | 307 | 110 | 257 | 0 | 297.005
14:00 | 2317 | 904 | 1682 | 0 | 1087 | 3106 | 40 | 0 | 307 | 110 | 257 | 0 | 297.005
14:30 | 2393.5 | 900.5 | 1662.5 | 0 | 972 | 3173 | 40 | 0 | 320.5 | 111 | 199.5 | 0 | 322.79
15:00 | 2470 | 897 | 1643 | 0 | 857 | 3240 | 40 | 0 | 334 | 112 | 142 | 0 | 348.575
15:30 | 2472.5 | 897.5 | 1606.5 | 0 | 883 | 3207.5 | 40 | 0 | 324 | 106 | 105 | 0 | 365.765
16:00 | 2475 | 898 | 1570 | 0 | 909 | 3175 | 40 | 0 | 314 | 100 | 68 | 0 | 382.955
16:30 | 2508.5 | 897.5 | 1562.5 | 0 | 932 | 3165 | 40 | 0 | 368.5 | 101 | 46.5 | 0 | 385.3425
17:00 | 2542 | 897 | 1555 | 0 | 955 | 3155 | 40 | 0 | 423 | 102 | 25 | 0 | 387.73
17:30 | 2667 | 897 | 1569 | 0 | 1140.5 | 3154 | 40 | 0 | 565 | 105 | 12.5 | 0 | 268.8325
18:00 | 2792 | 897 | 1583 | 0 | 1326 | 3153 | 40 | 0 | 707 | 108 | 0 | 0 | 149.935
18:30 | 2915.5 | 841 | 1683.5 | 0 | 1378 | 3320 | 40 | 0 | 733.5 | 108 | 0 | 0 | 154.71
19:00 | 3039 | 785 | 1784 | 0 | 1430 | 3487 | 40 | 0 | 760 | 108 | 0 | 0 | 159.485
19:30 | 3090 | 613 | 1672 | 0 | 1376 | 3559 | 40 | 0 | 761 | 106 | 0 | 0 | 129.88
20:00 | 3147 | 612 | 1657 | 0 | 1288 | 3535 | 40 | 0 | 757 | 106 | 0 | 0 | 100.275
20:30 | 3227.5 | 612 | 1665 | 0 | 1197.5 | 3461 | 40 | 0 | 643.5 | 106 | 0 | 0 | 67.6375
21:00 | 3308 | 612 | 1673 | 0 | 1107 | 3387 | 40 | 0 | 530 | 106 | 0 | 0 | 35
21:30 | 3307.5 | 754.5 | 1652 | 0 | 913 | 3352.5 | 37.5 | 0 | 297.5 | 104 | 0 | 0 | 77.5
22:00 | 3307 | 897 | 1631 | 0 | 719 | 3318 | 35 | 0 | 65 | 102 | 0 | 0 | 120
22:30 | 3333 | 896.5 | 1593.5 | 0 | 665.5 | 3242.5 | 35 | 0 | 65 | 102 | 0 | 0 | 85
23:00 | 3359 | 896 | 1556 | 0 | 612 | 3167 | 35 | 0 | 65 | 102 | 0 | 0 | 50
23:30 | 3337.5 | 896 | 1537.5 | 0 | 542 | 3057.5 | 35 | 0 | 65 | 98 | 0 | 0 | 25 |  | Max Temp. in Dhaka |  | 29°C
24:00 | 3316 | 896 | 1519 | 0 | 472 | 2948 | 35 | 0 | 65 | 94 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 233.792 MKWHr Energy Not Served 3.307 MKWHr Energy Requirement 237.099 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-02-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 900600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | [5 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 177114
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 12 | 17 | 19 | 19 | 18 | 16 | 12 | 7 | 2 | [9 empty] | 129600
6 | Sikalbaha 225MW CCPP (Gas) | 209 | 209 | 211 | 213 | 213 | 213 | 212 | 213 | 213 | 213 | 213 | 214 | 214 | 215 | 212 | 213 | 213 | 211 |  | 212 | 212 | 211 | 211 | 212 | 211 | 215 | 5083905
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | [7 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 42 | 42 | 59 |  | 68 | 68 | 68 | 68 | 0 |  | 0 | 791297
12 | Hathazari 100 MW peaking PP | 56 | [10 empty] | 4 | 25 | 64 | 64 | 64 | 64 | 73 |  | 73 | 73 | 73 | 81 | 0 |  |  | 688754
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 |  | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 368000
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 40 | 40 | 40 | [6 empty] | 40 | 40 | 40 | 40 | 47 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 0 |  | 0 | 689824
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | [5 empty] | 44 |  | 90 | 150 | 185 | 335 | 335 | 335 | 335 | 5835312
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | [6 empty] | 30 | 20 | 180 | 195 | 195 | 195 | 177 | 50 | 47 | 52 | 97 |  | 105 | 115 | 115 | 112 | 60 | 60 | 60 | 1816582
19 | Ashuganj 195 MW PP (APSCL-United) | 55 | 55 | 55 | 55 | 55 | 102 | 117 | 167 | 187 | 187 | 187 | 167 | 120 | 120 | 120 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 36 | 36 | 36 | 2458909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 190 | 190 | 190 | 190 | 140 | 140 | 119 | 140 | 140 | 143 | 140 | 140 |  | 190 | 190 | 190 | 190 | 190 | 190 | 160 | 3730406
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 280 | 280 | 280 | 280 | 280 | 334 | 340 | 353 | 360 | 360 | 360 | 360 | 360 | 360 | 350 | 320 | 320 | 320 |  | 335 | 335 | 350 | 350 | 350 | 330 | 296 | 7887272
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 44 | 42 | 36 | 36 | 42 | 42 | 45 | 46 | 46 |  | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 1031688
33 | Ashuganj 225 MW CCPP | [25 empty] | 0 | 0
34 | Ashuganj 450 MW CCPP(South) | 280 | 310 | 310 | 320 | 320 | 310 | 300 | 300 | 305 | 310 | 250 | 215 | 230 | 250 | 250 | 240 | 250 | 250 |  | 250 | 250 | 250 | 250 | 220 | 300 | 355 | 6718000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 285 | 285 | 285 | 285 | 285 | 325 | 335 | 385 | 325 | 325 | 325 | 345 | 325 | 354 | 393 | 385 | 393 | 393 |  | 393 | 393 | 393 | 393 | 393 | 393 | 393 | 8458700
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 54 | 54 | 54 | 52 | 53 | 51 | 53 | 54 | 51 | 52 | 53 |  | 54 | 54 | 54 | 54 | 54 | 54 | 55 | 1285440
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 180 | 33 | 53 | 139 |  |  |  | 36 | 98 | 303 |  | 417 | 400 | 404 | 413 | 418 | 417 | 417 | 5119200
| Meghnaghat Unique power | 130 | 130 | 140 | 135 | 135 | 135 | 232 | 232 | 235 | 235 | 234 | 255 | 281 | 280 | 250 | 250 | 250 | 250 |  | 323 | 323 | 323 | 324 | 320 | 260 | 261 | 5500454
| Summit Meghanghat-2 589 MW(Gas) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 157 | 157 | 160 | 158 | 108 | 108 | 110 | 108 | 110 | 105 |  | 105 | 105 | 100 | 100 | 100 | 100 | 100 | 3181045
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 53 | 51 | 51 | 51 | 51 | 52 | 52 | 44 | 44 | 34 | 33 | 33 | 29 | 29 | 29 | 29 | 29 | 33 |  | 38 | 55 | 72 | 72 | 72 | 72 | 72 | 1082880
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 4 | 4 | 5 | 5 | 6 | 9 | 20 | 14 | 4 | 2 | [9 empty] | 72810
44 | Fenchugonj CCPP Phase-1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 864000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 954720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 670752
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 210 | 210 | 210 | 211 | 215 | 215 | 215 | 214 | 213 | 213 | 210 | 209 | 207 | 208 | 206 | 206 | 207 |  | 208 | 208 | 208 | 209 | 209 | 209 | 209 | 4276990
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | [15 empty] | 0 | 195000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 9 | 9 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 231660
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 336384
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 270 | 290 | 285 | 300 | 300 | 295 | 315 | 310 | 290 | 305 | 300 | 300 | 310 | 320 | 315 | 315 | 285 |  | 315 | 290 | 280 | 290 | 305 | 290 | 280 | 7302500
| Bibiyana South 400 MW | 310 | 320 | 310 | 310 | 310 | 310 | 360 | 384 | 340 | 340 | 400 | 340 | 340 | 370 | 360 | 350 | 340 | 340 |  | 340 | 340 | 340 | 340 | 348 | 340 | 340 | 8261400
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 35 | [7 empty] | 0 | 68256
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 44880
60 | Barabkunda 22 MW PP (Regent) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 197376
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 88 | 84 | 80 | 78 | 72 | 84 | 82 | 94 | 96 | 98 | 104 | 112 | 110 | 114 | 112 | 100 | 102 | 108 |  | 108 | 106 | 106 | 106 | 102 | 102 | 94 | 2319360
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 39 | 40 | 38 | 38 | 12 | 5 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 12 | 16 |  | 30 | 30 | 30 | 35 | 38 | 38 | 39 | 527520
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 214020
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 703200
68 | Cumilla 25 MW PP (Summit) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 220910
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 456000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 10 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 499320
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817500
72 | Rupganj 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 24 | 25 | 25 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 480300
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 98 | [5 empty] | 53 | 86 | 83 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 94 | 98 |  | 105 | 114 | 114 | 114 | 52 | 52 | 52 | 1672380
| Chowmuhani 113 MW | 21 | [6 empty] | 9 | 9 | 9 | 9 | 23 | 37 | 39 | 39 | 39 | 46 | 71 |  | 77 | 78 | 78 | 79 | 79 | 79 | 53 | 799680
| Manikgonj 162MW PP(MPGL) | [11 empty] | 17 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 0 |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [6 empty] | 3 | 9 | 9 | 17 | 17 | 9 |  |  | 7 | 9 | 9 | 9 |  | 9 | 9 |  |  |  | 2 | 9 | 115200
78 | Gazipur 52 MW PP | 8 | 8 |  |  |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 212640
79 | Kodda 150 MW PP | 48 |  |  |  |  | 16 | 16 | 16 | 32 | 64 | 64 | 64 | 64 | 48 | 48 | 48 | 82 | 115 |  | 115 | 115 | 115 | 115 | 48 | 48 | 48 | 1232160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [5 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 170414
| Gazipur 100 MW PP | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 830400
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 3 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 26160
| Jodiac Power | [8 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [9 empty] | 0 | 126788
| Karnaphuli Power Ltd. | 17 | 17 | 17 |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 375526
82 | Madanganj 102 PP(Summit) | [6 empty] | 4 | 51 | 64 | 64 | 70 | 80 | 64 | 45 | 80 | 80 | 80 | 80 |  | 80 | 50 | 38 | 0 |  |  | 17 | 855078
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 10 |  |  | 20 | 36 | 36 | 32 | 24 | 25 | 13 | 24 | 14 |  | 13 | [5 empty] | 0 | 232319
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [7 empty] | 6 | 9 | 9 | [6 empty] | 4 | 8 |  | 9 | 9 |  |  |  |  | 0 | 48960
| Meghnaghat 104 MW PP (OPCL) | [5 empty] | 1 | 15 | 16 | 17 | 17 | 17 | 17 |  | 6 | 16 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 21 | 17 | 17 | 290880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [6 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 |  |  |  |  | 0 | 288360
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [15 empty] | 0 | 67392
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1255164
94 | Gagnagar 102 MW PP (Digital Power) | 8 | [5 empty] | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 58 |  | 65 | 65 | 65 | 65 | 41 | 25 | 25 | 596160
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 |  |  |  | 3 | 6 | 6 | 6 | 6 | 6 | 3 | 10 | 19 | 19 | 21 | 25 |  | 26 | 26 | 26 | 26 | 26 | 26 | 6 | 298080
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 4 | 15 | 15 | 15 | 15 | 15 | 15 | 20 |  | 25 | 15 | 15 | 15 | 15 | 15 | 0 | 230788
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 17 | 17 | 0 | [8 empty] | 0 | 40762
101 | Kushiara 163 MW CCPP (KP) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 163 | 163 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 140 | 140 | 140 | 140 | 140 | 140 | 3761754
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 3550
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 17 | 17 | 17 | 0 |  |  | 0 | 38520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 |  |  |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 187200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 |  |  |  | 6 | 17 | 17 | 32 | 94 | 98 | 98 | 30 | 17 | 17 | 0 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 614160
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 |  |  |  | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 522240
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 |  |  |  | 9 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 36 | 34 | 734400
117 | Ashuganj 150 MW PP (Midland) | 8 | 6 | 6 |  |  |  | 5 | 6 | 6 | 6 | 5 | 8 | 11 | 13 | 13 | 18 | 25 | 26 |  | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 209090
118 | Bibiyana-III 400 MW CCPP | 318 | 322 | 317 | 314 | 315 | 315 | 375 | 398 | 364 | 370 | 364 | 374 | 363 | 397 | 377 | 366 | 366 | 376 |  | 374 | 365 | 365 | 365 | 380 | 370 | 303 | 8736000
| Jamalpur 115 MW PP (United) | 9 | 9 |  |  |  | 5 | 57 | 57 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 69 |  | 69 | 69 | 69 | 69 | 9 | 9 | 9 | 969600
| Anwara 300 MW PP (United) | 16 | [5 empty] | 16 | 16 | 49 | 49 | 66 | 64 | 64 | 64 | 66 | 66 | 63 | 96 |  | 80 | 96 | 96 | 96 | 16 | 16 | 16 | 991091
| Juldah unit-2 (Acorn) | 25 | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 495360
| Anlima Energy Ltd. | 17 | 17 | 17 |  |  |  | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 370091
| Bhairob 54.5 MW | [12 empty] | 15 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 183600
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 4 | 9 | 10 | 22 | 18 |  |  |  | 3 | [9 empty] | 72932
| Chandpur 115(Doreen) | [11 empty] | 1 | 18 | 18 | 18 | 18 | 24 | 41 |  | 42 | 42 | 42 | 19 | 18 | 0 | 0 | 274560
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 11 | 31 |  | 17 | [5 empty] | 0 | 66960
| Mirsharai 150 MW (Oil) | 17 | [5 empty] | 17 | 17 | 35 | 35 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 145 |  | 145 | 145 | 145 | 17 | 17 | 17 | 17 | 889890
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600
| Matarbari 2*600 MW (CPGCL) | 158 | 158 | 158 | 157 | 158 | 157 | 160 | 160 | 157 | 157 | 156 | 158 | 157 | 159 | 157 | 159 | 157 | 157 |  | 157 | 157 | 157 | 157 | 158 | 158 | 159 | 3861818
120 | Eastern Zone Total | 4795 | 4376 | 4373 | 4158 | 4169 | 4337 | 4950 | 5366 | 5395 | 5488 | 5616 | 5707 | 5160 | 5201 | 5102 | 4980 | 5132 | 5865 |  | 6212 | 6162 | 6163 | 6121 | 5515 | 5429 | 5209 | 125601947
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 34 | 38 |  | 46 | 39 | 39 | 0 |  |  |  | 155310
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [7 empty] | 10 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 0 |  |  | 0 | 97920
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 13 | 33 | 42 | 43 | 75 | 82 | 66 | 52 | 32 | 8 | 0 | [8 empty] | 410400
131 | Rampal 1320 MW (BIFPCL) | [10 empty] | 228 | 320 | [14 empty] | 640000
132 | United Payra Power Ltd. | [6 empty] | 17 | 17 | 17 | 35 | 17 | [6 empty] | 3 |  | 35 | 35 | 35 | 0 |  |  | 0 | 194400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5054564
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [11 empty] | 16 | [7 empty] | 32 | 32 | 32 | 0 |  |  | 0 | 81120
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 180 | 180 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 245 | 250 | 250 | 183 | 150 | 150 | 150 | 3905500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | [8 empty] | 15 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 738000
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 1 | 4 | 3 | 4 | 5 | 4 | 5 | 0 | 0 | 8 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 127694
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 45 | 63 |  | 66 | 72 | 68 | 0 |  |  |  | 254592
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 904 | 904 | 733 | 715 | 714 | 904 | 756 | 620 | 619 | 619 | 753 | 904 | 904 | 897 | 897 | 898 | 897 | 897 |  | 785 | 613 | 612 | 612 | 897 | 896 | 896 | 19313454
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 950 | 900 | 890 | 890 | 900 | 900 | 930 | 1180 | 1244 | 1244 | 1040 | 900 | 950 | 1170 | 1100 | 1060 | 1040 | 1040 |  | 1170 | 1244 | 1200 | 1110 | 1080 | 1000 | 900 | 27026000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4119500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 25 |  | 25 | 25 | 25 | 25 | 0 |  | 0 | 100381
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 1 | 1 | 3 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 14160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 149 | 151 | 154 | 158 | 163 | 162 | 163 | 151 | 139 | 121 | 124 | 140 | 140 | 150 | 149 | 149 | 148 | 145 |  | 141 | 141 | 142 | 143 | 143 | 135 | 128 | 3742209
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 320 | 320 | 320 | 320 | 350 | 414 | 414 | 414 | 360 | 360 | 414 | 414 | 414 | 380 | 350 | 320 | 370 |  | 414 | 350 | 350 | 350 | 350 | 350 | 320 | 8957454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 133326
165 | Amnura 50 MW PP(Sinha) | [7 empty] | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 0 |  |  |  |  | 0 | 330050
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 34 |  | 42 | 42 | 8 | 0 |  |  |  | 265330
167 | Katakhali 50 MW Peaking PP | [9 empty] | 11 | 37 | 46 | 24 | 24 | 40 | 24 | 24 | 40 |  | 48 | 50 | 50 | 50 | 0 |  |  | 363665
168 | Santahar 50 MW Peaking PP | [17 empty] | 16 |  | 36 | 36 | 36 | 36 | 0 |  | 0 | 126220
169 | Natore 52 MW PP (Rajlanka) | [10 empty] | 8 | 16 | 16 | [7 empty] | 8 | 8 | 17 | 0 |  | 0 | 75634
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 44 | 49 | 49 | 49 | 49 | 49 | 49 | 85 |  | 90 | 90 | 90 | 90 | 0 |  |  | 682636
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [7 empty] | 3 | 33 | 35 | 35 | 35 | 35 | 35 | [11 empty] | 0 | 249888
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 0 |  | 0 | 227328
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 30 | 36 | 34 |  | 35 | 35 | 35 | 35 | 27 | 6 | 2 | 277958
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 4 | 4 | 2 | 1 | [9 empty] | 35493
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 17 | 17 | 19 |  | 71 | 71 | 72 | 72 | 35 | 0 | 0 | 339072
| Intraco Solar 30 MW | [6 empty] | 1 | 5 | 12 | 9 | 19 | 23 | 22 | 21 | 16 | 8 | 2 | 0 | [8 empty] | 141910
| Adani Power Jharkhanda Ltd | 1158 | 1067 | 1029 | 971 | 968 | 960 | 1116 | 1306 | 1411 | 1361 | 1336 | 1321 | 1319 | 1319 | 1313 | 1316 | 1318 | 1316 |  | 1410 | 1403 | 1408 | 1417 | 1410 | 1359 | 1273 | 29388364
178 | Teesta Solar Limited | [6 empty] | 4 | 20 | 42 | 85 | 97 | 123 | 95 | 106 | 39 | 13 | 7 | [9 empty] | 620630