## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-02-25 | Sunday
|  | Date (day): | 2024-02-25 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11218.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12381 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-02-24 | 2024-02-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 138 | 140 | 180 | 180
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 411 | 411 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  |  | Line S/D
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 9 | 9 | 91 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 17 | 85 | 85 |  | 17 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 25 | 15 | 25 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 14 | 26 | 49 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 16 | 16 | 84 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 64 | 16 | 42 |  | 60 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 115 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 39 | 39 | 39 |  | 41 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 17 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 18 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 63 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 35 | 17 | 35 | 114 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 35 | 17 | 51 | 53 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 35 | 35 | 17 | 145 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 423 | 605 | 240 | 240 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 100 | 100 | 100 | 100 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1631 | 2274 | 1784 | 2147 | 1731 | 1068
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 6 | 44 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 35 | 35 | 195 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 216 | 220 | 220
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 56 | 50 | 0 | 70 | 28 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 18 | 10 | 10
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 69 | 115 | 65 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 13 | 0 | 0 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 144 | 17 | 145 | 18 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 284 | 281 | 340 | 340 | 884 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 3 | 3 | 20 | 29 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 158 | 156 | 150 | 150 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 3 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1003 | 1204 | 1032 | 1326 | 2258 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 149 | 151 | 155 | 155 |  | 66 | ST Under maint.
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 320 | 320 | 40 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 350 | 300 | 330 | 320 | 80 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 45 | 45
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 10 | 10 | 10 | 50 |  | Gas shortage
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 0 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 6 | 6 | 6 | 144 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 33 | 32 | 40 | 48
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 29 | 34 | 34 | 34 | 166 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 9 | 9
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 124 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 10 | 10 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 15 | 11 | 11 |  | 14 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 100 | 100
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 95 | 36 | 78 | 35 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 1 | 53 | 0 | 42 | 73 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1109 | 1216 | 1341 | 1436 | 819 | 662
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 31 | 67 | 35 | 65 | 137 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 19 | 9 | 9 | 9 | 191 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 69 | 57 | 69 | 46 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 20 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 131 | 151 | 152.6 | 149 | 137 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 38 | 38 | 38 |  | 32 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 0 | 0 | 0
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 41 | 0 | 0 | 0 | 50
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 20 | 30 | 30 |  | 36 | GT-9 Under maint.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 92 | 80 | 0 | 0 |  | 100 | Under maint.
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 137 | 138 | 138 |  | 93 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 18 | 18 | 18 | 2 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 310 | 310 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 364 | 366 | 80 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 340 | 380 | 380 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1427 | 1513 | 1224 | 1544 | 60 | 641
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 902 | 618 | 926 | 926
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 10 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 82 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 17 | 88 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 74 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 358 | 357 | 350 | 350 | 267 |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1334 | 1067 | 1393 | 1413 | 1607 | 39
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 32 | 78 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 4 | 7 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 110 | 105 | 140 | 140 |  | 54 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 760 | 950 | 1200 | 1200
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 35 | 50
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 200 | 200 | 107 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1204 | 1448 | 1802 | 1849 | 185 | 87
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 25 | 25 | 27 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 15 |  | 56 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 50 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 150 | 150 | 150 | 70 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 250 | 299 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 16 | 35 | 15 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 35 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1111 | 1291 | 1300 | 1300
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1524 | 1979 | 2146 | 2232 | 1113 | 84
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 56 | 6 | 40 | 73 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 54 | 0 | 75 | 40 |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 199 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 411 | 280 | 344 | 285 | 238 | 189
| Total |  |  |  |  | 26504 | 25481 | 9774 | 11132 | 11218.6 | 12381 | 8148 | 3100
A. |  | 43884 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11132 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 0.79167 | hrs.
2 | Minimum Generation : |  |  | 7133 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11132 | MW
3 | Day peak Generation : |  |  | 9774 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10808.33 | MW
4 | Evening peak Generation : |  |  | 11132 | MW at | 0.79167 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 224.0228 | MKWHr | By Solar | 2.5239 | MKWHr
| By Gas : | 114.7528 | MKWHr |  | By Oil: | 12.5229 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 72.0056 | MKWHr |  | By Hydro: | 0.90642 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.03744 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8148 | MW | Dhaka | 4026.33 | 4026.33 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3100 | MW | Chittagong | 1192 | 1192 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 11248 | MW | Khulna | 1215.4 | 1215.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 881.29 | MMCFD |  |  | Rajshahi | 1093.6 | 1093.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 308750040.524 | ii) Oil : | Taka | 224610064.74 | Comilla | 903 | 903 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 489711838.34 | Total | Taka | 1023071943.604 | Mymensingh | 923 | 923 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0:00 | MKWHr. | Sylhet | 376 | 376 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 930 | MW (W to E) at | 19:00 | hrs | Barisal | 313 | 313 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 760 | MW at | 0.33333 | hrs | Rangpur | 766 | 766 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.0°C |  |  | Total | 10808.33 | 10808.33 |  | 0
B. |  | 43885 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 29.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12381 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
4 | Reserve(Generation end) |  |  |  | 881 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 231.4287 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7439 | MW at | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.8276 | MKWHr. | ii) HVDC Flow at Peak Time |  | 618 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4461 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 0.041667 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.51 |  | (b) Today: | 84.42 |  | (c) Rule Curve: |  | 93.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-02-24 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 270 | 154 | 0 | 0 | 47 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 5 | 33 | 16 | 98 | 95 | 0 | 0 | 0 | 38 | 40 | 11 | 5 | 130 | 0 | 28 | 0 | 0 | 0 | 18 | 0 | 10 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 17 | 0 | 311 | 0 | 158 | 241 | 100 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 150 | 923 | 0 | 0 |  | 4255 | 3835 | 8090 | 2933 | 907 | 1396 | 0 | 30 | 2674 | 35 | 0 | 17 | 98 | 0 | 0 | 0 | 84.53
2:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 270 | 154 | 0 | 0 | 44 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 5 | 33 | 11 | 92 | 95 | 0 | 0 | 0 | 38 | 40 | 11 | 5 | 130 | 0 | 28 | 0 | 0 | 0 | 18 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 311 | 0 | 158 | 240 | 100 | 0 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 818 | 0 | 0 |  | 4203 | 3432 | 7635 | 2925 | 671 | 1405 | 0 | 0 | 2507 | 35 | 0 | 0 | 92 | 0 | 0 | 0 | 84.53
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 270 | 154 | 0 | 0 | 10 | 7 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 33 | 11 | 92 | 95 | 0 | 0 | 0 | 38 | 40 | 5 | 0 | 130 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 290 | 0 | 158 | 241 | 100 | 0 |  | 671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 150 | 817 | 0 | 0 |  | 4057 | 3375 | 7432 | 2874 | 671 | 1316 | 0 | 0 | 2444 | 35 | 0 | 0 | 92 | 0 | 0 | 0 | 84.52
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 339 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 270 | 154 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 33 | 11 | 92 | 95 | 0 | 0 | 0 | 38 | 40 | 5 | 0 | 120 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 280 | 0 | 157 | 240 | 100 | 0 |  | 674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 150 | 821 | 0 | 0 |  | 3938 | 3343 | 7281 | 2769 | 674 | 1273 | 0 | 0 | 2438 | 35 | 0 | 0 | 92 | 0 | 0 | 0 | 84.52
5:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 310 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 270 | 110 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 33 | 11 | 88 | 72 | 0 | 0 | 0 | 38 | 40 | 5 | 0 | 120 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 280 | 0 | 156 | 240 | 100 | 0 |  | 674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 150 | 815 | 0 | 0 |  | 3844 | 3289 | 7133 | 2685 | 674 | 1238 | 0 | 0 | 2413 | 35 | 0 | 0 | 88 | 0 | 0 | 0 | 84.51
6:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 322 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 290 | 110 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 33 | 11 | 84 | 96 | 0 | 0 | 0 | 38 | 40 | 5 | 0 | 120 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 280 | 0 | 157 | 300 | 100 | 0 |  | 678 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 150 | 824 | 0 | 0 |  | 4051 | 3300 | 7351 | 2830 | 678 | 1302 | 0 | 0 | 2422 | 35 | 0 | 0 | 84 | 0 | 0 | 0 | 84.51
7:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 372 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39 | 0 | 0 | 0 | 0 | 315 | 110 | 0 | 0 | 10 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 33 | 11 | 90 | 95 | 0 | 0 | 0 | 38 | 40 | 41 | 0 | 163 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 315 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0 | 1 | 347 | 19 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 340 | 7 | 1 | 0 | 5 | 0 | 0 | 2 | 0 | 0 | 330 | 17 | 0 | 282 | 0 | 157 | 350 | 100 | 0 |  | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 180 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 360 | 1 | 150 | 905 | 7 | 0 |  | 4556 | 3461 | 8017 | 3095 | 631 | 1513 | 0 | 50 | 2554 | 35 | 0 | 33 | 90 | 16 | 0 | 0 | 84.5
8:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 419 | 0 |  | 0 | 0 | 0 | 0 | 4 | 0 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 25 | 8 | 0 | 35 | 0 | 0 | 0 | 2 | 214 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 15 | 0 | 0 | 0 | 0 | 300 | 156 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 0 | 1 | 0 | 5 | 33 | 11 | 96 | 65 | 0 | 0 | 0 | 38 | 40 | 51 | 40 | 163 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 3 | 0 | 0 | 9 | 0 | 7 | 5 | 16 | 20 | 3 | 373 | 56 | 2 | 5 | 0 | 16 | 0 | 2 | 0 | 2 | 24 | 355 | 17 | 5 | 0 | 17 | 0 | 0 | 8 | 0 | 0 | 350 | 17 | 0 | 282 | 0 | 159 | 408 | 100 | 2 |  | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 630 | 180 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 357 | 10 | 150 | 1020 | 42 | 0 |  | 4983 | 3812 | 8795 | 3229 | 631 | 1677 | 0 | 228 | 2768 | 35 | 0 | 33 | 96 | 96 | 0 | 52.525 | 84.5
9:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 56 | 0 | 0 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 0 | 270 | 146 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 7 | 8 | 0 | 5 | 33 | 11 | 76 | 65 | 0 | 0 | 1 | 38 | 40 | 51 | 46 | 130 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 15 | 0 | 0 | 9 | 0 | 17 | 12 | 25 | 34 | 6 | 365 | 56 | 17 | 17 | 2 | 49 | 5 | 17 | 0 | 15 | 25 | 345 | 17 | 19 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 350 | 17 | 0 | 282 | 0 | 157 | 406 | 100 | 2 |  | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 630 | 178 | 0 | 0 | 2 | 49 | 0 | 0 | 0 | 354 | 20 | 150 | 1116 | 97 | 0 |  | 5105 | 4042 | 9147 | 3231 | 631 | 1578 | 0 | 396 | 2859 | 40 | 0 | 112 | 76 | 222 | 0 | 60.165 | 84.49
10:00 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 395 | 0 |  | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 20 | 0 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 56 | 0 | 0 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 0 | 270 | 148 | 0 | 0 | 10 | 5 | 0 | 51 | 0 | 40 | 8 | 0 | 5 | 33 | 11 | 84 | 67 | 0 | 0 | 1 | 38 | 40 | 31 | 43 | 130 | 0 | 20 | 0 | 0 | 0 | 16 | 0 | 10 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 16 | 0 | 17 | 6 | 365 | 59 | 17 | 17 | 3 | 30 | 0 | 17 | 0 | 9 | 0 | 340 | 17 | 39 | 0 | 17 | 0 | 1 | 25 | 0 | 0 | 350 | 17 | 0 | 282 | 0 | 158 | 415 | 100 | 1 |  | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 580 | 160 | 0 | 0 | 2 | 65 | 0 | 0 | 0 | 358 | 26 | 150 | 1015 | 158 | 0 |  | 5004 | 3892 | 8896 | 3175 | 631 | 1476 | 0 | 276 | 2713 | 40 | 0 | 161 | 84 | 339 | 0 | 0 | 84.49
11:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 0 | 0 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 56 | 0 | 0 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 0 | 290 | 151 | 8 | 0 | 10 | 5 | 0 | 0 | 0 | 33 | 8 | 0 | 5 | 33 | 11 | 98 | 63 | 0 | 0 | 2 | 38 | 40 | 31 | 44 | 130 | 0 | 20 | 0 | 0 | 0 | 16 | 0 | 10 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 17 | 0 | 17 | 6 | 379 | 59 | 17 | 17 | 4 | 30 | 0 | 17 | 0 | 9 | 0 | 343 | 17 | 35 | 17 | 17 | 10 | 10 | 29 | 0 | 0 | 350 | 17 | 0 | 282 | 2 | 158 | 417 | 100 | 4 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 640 | 180 | 0 | 0 | 4 | 62 | 0 | 0 | 0 | 358 | 31 | 150 | 1056 | 197 | 0 |  | 5136 | 4266 | 9402 | 3193 | 902 | 1491 | 0 | 317 | 2814 | 40 | 0 | 154 | 98 | 387 | 2 | 0 | 84.49
12:00 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 300 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 56 | 0 | 0 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 0 | 270 | 149 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 33 | 10 | 0 | 5 | 33 | 9 | 104 | 31 | 0 | 0 | 2 | 38 | 40 | 31 | 41 | 130 | 0 | 20 | 0 | 0 | 0 | 15 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 13 | 25 | 29 | 5 | 364 | 59 | 17 | 17 | 3 | 69 | 13 | 17 | 0 | 28 | 25 | 340 | 17 | 20 | 17 | 17 | 92 | 17 | 30 | 1 | 0 | 350 | 17 | 0 | 284 | 3 | 158 | 423 | 100 | 3 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 760 | 180 | 0 | 0 | 5 | 74 | 0 | 0 | 0 | 358 | 36 | 150 | 1111 | 199 | 0 |  | 5301 | 4473 | 9774 | 3208 | 902 | 1517 | 0 | 464 | 2991 | 40 | 0 | 154 | 104 | 388 | 3 | 0 | 84.48
13:00 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 0 | 56 | 0 | 0 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 8 | 0 | 41 | 11 | 0 | 43 | 0 | 32 | 8 | 0 | 5 | 33 | 9 | 110 | 33 | 0 | 0 | 2 | 38 | 40 | 31 | 20 | 163 | 0 | 20 | 0 | 0 | 0 | 16 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 18 | 25 | 34 | 6 | 365 | 59 | 17 | 17 | 3 | 70 | 17 | 17 | 0 | 43 | 25 | 340 | 17 | 49 | 17 | 17 | 0 | 17 | 30 | 16 | 0 | 350 | 17 | 0 | 282 | 4 | 157 | 590 | 100 | 6 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 115 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 800 | 180 | 0 | 0 | 5 | 44 | 0 | 0 | 0 | 357 | 29 | 150 | 1211 | 161 | 0 |  | 5517 | 4638 | 10155 | 3172 | 901 | 1797 | 0 | 493 | 3127 | 40 | 0 | 158 | 110 | 347 | 4 | 0 | 84.48
14:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 420 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 0 | 72 | 0 | 0 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 10 | 12 | 0 | 43 | 0 | 32 | 8 | 0 | 5 | 33 | 9 | 106 | 35 | 0 | 0 | 2 | 38 | 40 | 31 | 20 | 163 | 0 | 20 | 0 | 0 | 85 | 15 | 0 | 10 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 32 | 16 | 25 | 34 | 6 | 365 | 59 | 17 | 17 | 3 | 70 | 17 | 17 | 0 | 49 | 25 | 340 | 17 | 45 | 17 | 17 | 0 | 17 | 27 | 18 | 0 | 300 | 17 | 0 | 282 | 2 | 157 | 597 | 100 | 10 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 700 | 180 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 359 | 25 | 150 | 1217 | 173 | 0 |  | 5573 | 4556 | 10129 | 3225 | 902 | 1746 | 0 | 516 | 3035 | 40 | 0 | 174 | 106 | 373 | 2 | 0 | 84.49
15:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 72 | 0 | 0 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 10 | 10 | 0 | 43 | 0 | 32 | 8 | 0 | 5 | 33 | 9 | 114 | 33 | 0 | 0 | 1 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 135 | 14 | 0 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 29 | 12 | 25 | 34 | 6 | 366 | 59 | 17 | 17 | 2 | 30 | 17 | 17 | 0 | 49 | 25 | 340 | 17 | 34 | 17 | 17 | 0 | 17 | 9 | 18 | 0 | 300 | 17 | 0 | 280 | 4 | 157 | 596 | 100 | 19 |  | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 135 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 680 | 180 | 0 | 0 | 3 | 28 | 0 | 0 | 0 | 357 | 25 | 150 | 1099 | 131 | 0 |  | 5432 | 4345 | 9777 | 3264 | 901 | 1701 | 0 | 450 | 2893 | 40 | 0 | 142 | 114 | 249 | 4 | 0 | 84.47
16:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 374 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 0 | 72 | 0 | 0 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 305 | 148 | 0 | 0 | 10 | 10 | 0 | 43 | 0 | 32 | 8 | 0 | 5 | 33 | 9 | 120 | 33 | 0 | 0 | 1 | 38 | 40 | 0 | 0 | 120 | 0 | 28 | 0 | 0 | 135 | 14 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 7 | 0 | 34 | 5 | 364 | 59 | 17 | 17 | 1 | 30 | 0 | 17 | 0 | 48 | 25 | 340 | 17 | 20 | 17 | 17 | 0 | 17 | 3 | 17 | 0 | 300 | 17 | 0 | 281 | 4 | 156 | 589 | 100 | 6 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 135 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 680 | 180 | 0 | 0 | 1 | 19 | 0 | 0 | 0 | 356 | 15 | 150 | 1016 | 78 | 0 |  | 5256 | 4222 | 9478 | 3213 | 902 | 1696 | 0 | 393 | 2809 | 40 | 0 | 147 | 120 | 148 | 4 | 0 | 84.47
17:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 356 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 0 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 1 | 72 | 0 | 0 | 0 | 9 | 10 | 3 | 0 | 0 | 0 | 0 | 305 | 148 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 32 | 8 | 0 | 5 | 33 | 9 | 116 | 57 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 135 | 14 | 0 | 10 | 305 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 2 | 0 | 34 | 6 | 348 | 69 | 17 | 17 | 0 | 30 | 0 | 17 | 0 | 48 | 25 | 340 | 17 | 6 | 17 | 17 | 100 | 17 | 2 | 17 | 9 | 300 | 17 | 0 | 283 | 0 | 157 | 590 | 100 | 2 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12 | 0 | 110 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 346 | 0 | 0 | 0 | 0 | 11 | 0 | 2 | 0 | 680 | 180 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 359 | 3 | 150 | 1016 | 11 | 0 |  | 5330 | 4121 | 9451 | 3243 | 902 | 1720 | 0 | 429 | 2815 | 40 | 0 | 154 | 116 | 30 | 0 | 0 | 84.47
18:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 0 | 0 | 4 | 11 | 12 | 280 | 0 | 0 | 9 | 16 | 105 | 0 | 0 | 0 | 0 | 11 | 15 | 17 | 0 | 17 | 22 | 17 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 11 | 216 | 0 | 0 | 0 |  | 6 | 78 | 17 | 0 | 0 | 19 | 10 | 6 | 0 | 0 | 0 | 0 | 270 | 151 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 32 | 8 | 0 | 5 | 33 | 12 | 122 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 136 | 16 | 0 | 10 | 290 | 16 | 0 | 0 | 12 | 0 | 0 | 9 | 0 | 21 | 0 | 10 | 34 | 6 | 329 | 69 | 22 | 17 | 0 | 30 | 0 | 17 | 0 | 62 | 25 | 340 | 33 | 0 | 17 | 17 | 90 | 17 | 0 | 21 | 35 | 300 | 144 | 0 | 282 | 6 | 157 | 596 | 100 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49 | 0 | 110 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 48 | 8 | 24 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 312 | 0 | 0 | 15 | 0 | 54 | 0 | 0 | 50 | 720 | 180 | 0 | 7 | 0 | 0 | 17 | 0 | 0 | 358 | 0 | 150 | 1065 | 0 | 0 |  | 5734 | 4489 | 10223 | 3203 | 902 | 1681 | 0 | 805 | 2902 | 40 | 9 | 553 | 122 | 0 | 6 | 0 | 84.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 0 | 0 | 8 | 17 | 25 | 335 | 0 | 0 | 9 | 64 | 115 | 13 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 22 | 17 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 216 | 0 | 0 | 0 |  | 6 | 50 | 34 | 0 | 0 | 19 | 10 | 18 | 0 | 0 | 0 | 0 | 270 | 151 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 32 | 10 | 0 | 5 | 33 | 15 | 124 | 67 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 137 | 18 | 0 | 10 | 285 | 16 | 0 | 0 | 63 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 6 | 366 | 69 | 105 | 17 | 0 | 115 | 0 | 17 | 0 | 95 | 25 | 340 | 35 | 0 | 35 | 17 | 80 | 17 | 0 | 53 | 17 | 300 | 144 | 0 | 281 | 3 | 156 | 605 | 100 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 0 | 105 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 50 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 299 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 50 | 950 | 220 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 357 | 0 | 150 | 1291 | 0 | 0 |  | 6358 | 4774 | 11132 | 3352 | 618 | 1768 | 0 | 1272 | 3355 | 40 | 0 | 600 | 124 | 0 | 3 | 0 | 84.45
19:30 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 2 | 25 | 335 | 0 | 0 | 0 | 41 | 115 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 22 | 20 | 12 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 216 | 0 | 0 | 0 |  | 6 | 60 | 34 | 0 | 0 | 19 | 10 | 17 | 0 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 0 | 16 | 0 | 5 | 33 | 15 | 120 | 66 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 137 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 6 | 365 | 69 | 51 | 17 | 0 | 50 | 0 | 17 | 0 | 65 | 25 | 340 | 35 | 0 | 35 | 17 | 80 | 17 | 0 | 54 | 0 | 300 | 108 | 0 | 280 | 3 | 157 | 604 | 100 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 125 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 10 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 315 | 17 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 1150 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 357 | 0 | 150 | 1308 | 0 | 0 |  | 6002 | 4843 | 10845 | 3365 | 618 | 1787 | 0 | 920 | 3572 | 40 | 0 | 420 | 120 | 0 | 3 | 0 | 0
20:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 0 | 0 | 0 | 4 | 15 | 335 | 0 | 0 | 0 | 8 | 115 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 15 | 25 | 12 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 216 | 0 | 0 | 0 |  | 6 | 64 | 34 | 0 | 0 | 19 | 10 | 20 | 0 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 5 | 33 | 15 | 120 | 67 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 136 | 18 | 0 | 10 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 6 | 365 | 69 | 51 | 17 | 0 | 50 | 0 | 0 | 0 | 65 | 25 | 340 | 35 | 0 | 17 | 17 | 80 | 17 | 0 | 54 | 0 | 300 | 72 | 0 | 282 | 2 | 157 | 602 | 100 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 135 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 381 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 1170 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 357 | 0 | 150 | 1353 | 0 | 0 |  | 5854 | 4902 | 10756 | 3403 | 618 | 1834 | 0 | 716 | 3639 | 40 | 0 | 384 | 120 | 0 | 2 | 0 | 84.46
21:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 12 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 215 | 0 | 0 | 0 |  | 6 | 64 | 34 | 0 | 0 | 19 | 10 | 32 | 0 | 0 | 0 | 0 | 270 | 150 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 15 | 120 | 69 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 136 | 18 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 5 | 365 | 69 | 51 | 17 | 0 | 50 | 0 | 0 | 0 | 65 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 24 | 0 | 330 | 17 | 0 | 283 | 0 | 158 | 606 | 100 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 135 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 369 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 357 | 0 | 150 | 1356 | 0 | 0 |  | 5713 | 4929 | 10642 | 3363 | 618 | 1863 | 0 | 629 | 3718 | 40 | 0 | 291 | 120 | 0 | 0 | 0 | 84.45
22:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 12 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 0 | 19 | 10 | 36 | 0 | 0 | 0 | 0 | 270 | 151 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 15 | 118 | 73 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 136 | 18 | 0 | 10 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 6 | 365 | 9 | 51 | 17 | 0 | 50 | 0 | 0 | 0 | 65 | 25 | 340 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 330 | 17 | 0 | 283 | 2 | 154 | 598 | 100 | 0 |  | 886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 345 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 1253 | 0 | 0 |  | 5499 | 4745 | 10244 | 3340 | 886 | 1835 | 0 | 454 | 3408 | 35 | 0 | 166 | 118 | 0 | 2 | 0 | 84.45
23:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 386 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 14 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 0 | 19 | 10 | 36 | 0 | 0 | 0 | 0 | 280 | 150 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 15 | 112 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 120 | 0 | 28 | 0 | 0 | 136 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 20 | 0 | 25 | 39 | 0 | 374 | 9 | 51 | 17 | 0 | 15 | 0 | 0 | 0 | 65 | 25 | 340 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 290 | 17 | 0 | 282 | 5 | 156 | 301 | 100 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 135 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 1160 | 0 | 0 |  | 4935 | 4757 | 9692 | 3277 | 902 | 1560 | 0 | 351 | 3316 | 35 | 0 | 134 | 112 | 0 | 5 | 0 | 84.45
24:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 14 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 0 | 6 | 10 | 40 | 0 | 0 | 0 | 0 | 310 | 151 | 0 | 0 | 30 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 33 | 15 | 108 | 72 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 28 | 0 | 0 | 138 | 20 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 36 | 0 | 364 | 9 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 25 | 330 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 17 | 0 | 283 | 2 | 156 | 240 | 100 | 0 |  | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 150 | 1015 | 0 | 0 |  | 4922 | 4289 | 9211 | 3400 | 903 | 1435 | 0 | 207 | 2992 | 35 | 0 | 129 | 108 | 0 | 2 | 0 | 84.44
KWH | 0 | 0 | 3336531 | 0 | 0 | 0 | 0 | 9370800 | 0 |  | 0 | 0 | 0 | 14400 | 46464 | 153155 | 7389067 | 0 | 0 | 13440 | 154944 | 933120 | 11101 | 0 | 0 | 0 | 28080 | 40261 | 39199 | 0 | 408000 | 510480 | 513360 | 475600 | 193920 | 0 | 906420 | 0 | 0 | 0 | 142140 | 5059967 | 0 | 0 | 0 |  | 44880 | 978432 | 118407 | 0 | 0 | 181440 | 241920 | 567360 | 0 | 0 | 0 | 0 | 6810000 | 3543000 | 33455 | 0 | 389376 | 212160 | 0 | 939716 | 0 | 339008 | 112433 | 0 | 122220 | 819700 | 292950 | 2446080 | 1566720 | 0 | 0 | 10800 | 903000 | 947040 | 336600 | 260208 | 3556636 | 0 | 531360 | 0 | 0 | 1354780 | 405000 | 0 | 236700 | 7152000 | 385632 | 0 | 0 | 135491 | 0 | 0 | 180000 | 0 | 403920 | 111240 | 314880 | 569280 | 93672 | 8471000 | 919200 | 543360 | 287709 | 22438 | 855600 | 90528 | 213270 | 0 | 796320 | 363840 | 7778000 | 332160 | 271590 | 194400 | 301091 | 454127 | 234720 | 173501 | 275520 | 69840 | 7324600 | 610545 | 0 | 6850908 | 37440 | 3832727 | 10232727 | 2565909 | 162 |  | 18827636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11520 | 157312 | 0 | 2445000 | 135125 | 36192 | 0 | 0 | 0 | 0 | 0 | 217120 | 0 | 12923 | 83827 | 13786 | 68717 | 0 | 0 | 127062 | 0 | 0 | 4144100 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 4081118 | 0 | 7734690 | 50880 | 0 | 67968 | 0 | 194496 | 0 | 42846 | 86688 | 19622200 | 4732145 | 0 | 25200 | 32400 | 457920 | 156096 | 0 | 0 | 8574545 | 232942 | 3643600 | 25337498 | 1168250 | 0 |  | 121491177 | 102531802 | 224022979 | 76057410 | 18827636 | 38695431 | 0 | 8994887 | 72005578 | 906420 | 10000 | 3518008 | 2446080 | 2523927 | 37440 | 0
Fuel Cost | 0 | 0 | 14313717.99 | 0 | 0 | 0 | 0 | 26987904 | 0 |  | 0 | 0 | 0 | 284544 | 868876.8 | 2698591.1 | 22536654.35 | 0 | 0 | 265574.4 | 2781244.8 | 18121190.4 | 207033.65 | 0 | 0 | 0 | 512740.8 | 634513.36 | 716949.71 | 0 | 306000 | 0 | 0 | 0 | 3473107.2 | 0 | 0 | 0 | 0 | 0 | 2692131.6 | 16141294.73 | 0 | 0 | 0 |  | 789439.2 | 17230187.52 | 2120669.37 | 0 | 0 | 2986502.4 | 899942.4 | 0 | 0 | 0 | 0 | 0 | 20838600 | 11762760 | 112074.25 | 0 | 1312197.12 | 929260.8 | 0 | 3768261.16 | 0 | 6071633.28 | 2030539.98 | 0 | 91665 | 3049284 | 219712.5 | 16046284.8 | 4872499.2 | 0 | 0 | 0 | 3521700 | 3532459.2 | 1531530 | 1183946.4 | 12163695.12 | 0 | 2949048 | 0 | 0 | 3779836.2 | 2664900 | 0 | 946800 | 22099680 | 289224 | 0 | 0 | 2764016.4 | 0 | 0 | 3457800 | 0 | 7113031.2 | 0 | 5608012.8 | 9877008 | 1553081.76 | 22448150 | 17519952 | 10193433.6 | 5161499.46 | 0 | 13989060 | 1759864.32 | 3826063.8 | 0 | 15456571.2 | 6479990.4 | 20689480 | 5669971.2 | 0 | 3555576 | 5052306.98 | 1698434.98 | 4194446.4 | 0 | 4964870.4 | 1183089.6 | 21754062 | 8596473.6 | 0 | 47750828.76 | 0 | 22613089.3 | 0 | 0 | 0 |  | 52905657.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216691.2 | 2959038.72 | 0 | 7726200 | 640492.5 | 623950.08 | 0 | 0 | 0 | 0 | 0 | 3649787.2 | 0 | 246441.61 | 1501341.57 | 244012.2 | 1230721.47 | 0 | 0 | 96185.934 | 0 | 0 | 34976204 | 0 | 470200 | 0 | 0 | 0 | 0 | 0 | 0 | 13590122.94 | 0 | 22585294.8 | 869030.4 | 0 | 1347125.76 | 0 | 3874360.32 | 0 | 0 | 1719889.92 | 127151856 | 14716970.95 | 0 | 487620 | 0 | 0 | 2708265.6 | 0 | 0 | 62594178.5 | 0 | 27144820 | 167480861.78 | 0 | 0 |  | 538266564.95 | 553757320.614 | 1092023885.564 | 228072034.544 | 52905657.16 | 80678005.98 | 0 | 162442130.41 | 489711838.34 | 0 | 470200 | 61697734.33 | 16046284.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 0 | 0 | 0 | 0 | 15 | 300 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 18 | 8 | 0 | 40 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 56 | 0 | 0 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 0 | 270 | 149 | 8 | 0 | 10 | 5 | 0 | 43 | 0 | 33 | 10 | 0 | 5 | 33 | 9 | 104 | 31 | 0 | 0 | 2 | 38 | 40 | 31 | 41 | 130 | 0 | 20 | 0 | 0 | 0 | 15 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 13 | 25 | 29 | 5 | 364 | 59 | 17 | 17 | 3 | 69 | 13 | 17 | 0 | 28 | 25 | 340 | 17 | 20 | 17 | 17 | 92 | 17 | 30 | 1 | 0 | 350 | 17 | 0 | 284 | 3 | 158 | 423 | 100 | 3 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 760 | 180 | 0 | 0 | 5 | 74 | 0 | 0 | 0 | 358 | 36 | 150 | 1111 | 199 | 0 |  | 9774 | DayPeak
Yesterday Evening Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 0 | 0 | 8 | 17 | 25 | 335 | 0 | 0 | 9 | 64 | 115 | 13 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 22 | 17 | 18 | 17 | 0 | 40 | 0 | 0 | 0 | 17 | 216 | 0 | 0 | 0 | 0 | 6 | 50 | 34 | 0 | 0 | 19 | 10 | 18 | 0 | 0 | 0 | 0 | 270 | 151 | 0 | 0 | 10 | 10 | 0 | 51 | 0 | 32 | 10 | 0 | 5 | 33 | 15 | 124 | 67 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 137 | 18 | 0 | 10 | 285 | 16 | 0 | 0 | 63 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 6 | 366 | 69 | 105 | 17 | 0 | 115 | 0 | 17 | 0 | 95 | 25 | 340 | 35 | 0 | 35 | 17 | 80 | 17 | 0 | 53 | 17 | 300 | 144 | 0 | 281 | 3 | 156 | 605 | 100 | 0 |  | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 0 | 105 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 8 | 50 | 8 | 32 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 299 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 50 | 950 | 220 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 357 | 0 | 150 | 1291 | 0 | 0 |  | 11132 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 0 | 0 | 9 | 85 | 25 | 335 | 0 | 0 | 16 | 42 | 149 | 26 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 17 | 22 | 33 | 33 | 17 | 0 | 35 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 70 | 51 | 25 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 0 | 320 | 155 | 8 | 0 | 45 | 10 | 0 | 51 | 0 | 48 | 8 | 0 | 9 | 33 | 11 | 141 | 65 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 138 | 18 | 0 | 10 | 310 | 17 | 0 | 0 | 130 | 0 | 0 | 9 | 0 | 35 | 0 | 25 | 34 | 6 | 400 | 69 | 105 | 17 | 0 | 100 | 17 | 17 | 100 | 78 | 25 | 380 | 51 | 0 | 17 | 17 | 0 | 17 | 0 | 42 | 17 | 320 | 145 | 0 | 340 | 29 | 150 | 240 | 100 |  |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 0 | 140 | 7 | 32 | 0 | 0 | 0 | 25 | 15 | 90 | 28 | 42 | 50 | 8 | 35 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 17 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 1200 | 220 | 0 | 50 | 0 | 0 | 75 | 0 | 0 | 350 | 0 | 200 | 1300 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 9 | 85 | 15 | 335 | 0 | 0 | 16 | 16 | 48 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 33 | 33 | 8 | 0 | 35 | 0 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 0 | 320 | 155 | 8 | 0 | 45 | 10 | 0 | 51 | 0 | 40 | 8 | 0 | 9 | 33 | 11 | 128 | 35 | 0 | 0 | 1.6 | 38 | 40 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 138 | 18 | 0 | 10 | 310 | 17 | 0 | 0 | 80 | 0 | 0 | 9 | 0 | 17 | 20 | 25 | 34 | 6 | 80 | 57 | 17 | 17 | 5 | 65 | 0 | 17 | 100 | 36 | 25 | 380 | 17 | 50 | 35 | 17 | 0 | 17 | 35 | 0 | 0 | 330 | 17 | 0 | 340 | 20 | 150 | 240 | 100 |  |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 28 | 42 | 40 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 8 | 35 | 1200 | 220 |  | 35 | 6 | 100 | 0 | 0 |  | 350 | 30 | 200 | 1300 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 15 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 0 | 320 | 152 | 5 | 0 | 46 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 11 | 94 | 69 | 0 | 0 | 0 | 38 | 40 | 0 | 0 | 120 | 0 | 30 | 0 | 0 | 138 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 4 | 0 | 5 | 80 | 9 | 0 | 0 | 1 | 60 | 0 | 0 | 0 | 0 | 6 | 370 | 5 | 1 | 0 | 17 | 0 | 0 | 2 | 0 | 0 | 330 | 17 | 0 | 340 | 0 | 158 | 241 | 100 | 8 | 0 | 624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 910 | 220 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 359 | 9 | 150 | 1109 | 20 | 0 | 0 |  |  |  | 114752841 | 18827636 | 10000 | 72005578 | 12512895 | 2446080 | 2523927 | 37440 | 906420
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [12 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 114.7528 | 18.8276 | 0.01 | 72.0056 | 12.5129 | 2.4461 | 2.5239 | 0.03744 | 0.90642
| Minimum Generation |  | 7133 | 5:00
| Highest Generation |  | 11132 | 19:00 | [129 empty] | 0 | [71 empty] | 224.0228
| Day Peak Generation |  | 9774 | 12:00
| Evening Peak Generation |  | 11132 | 19:00 | [201 empty] | 202699852
| HVDC Max Flow |  | 907 | 1:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 618 | 19:00
| Load factor L.F |  | 87.46% | [166 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
|  |  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  |  | DAILY REPORT |  |  |  |  | Page -1
[7 empty] | Reporting Date : | 2024-02-25
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-02-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9774 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7439 | MW
Evening Peak Generation : |  |  | 11132 | MW Hour : | 19:00 | Available Max Generation : |  | 12381 | MW
E.P. Demand (at gen end) : |  |  | 11132 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  |  | 11132 | MW Hour : | 19:00 | Reserve(Generation end) |  | 881 | MW
Total Gen. (MKWH) : |  |  | 224.0228 | System Load Factor : | 83.85% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 760 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-02-25
Actual : |  | 84.42 | Ft.(MSL) , | Rule curve : | 93.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 881.29 | MMCFD. | Oil Consumed (PDB) :
[7 empty] | HSD : |  | Liter
[7 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 308750040.524
: |  |  | Coal : | 489711838.34 | Oil : | 224610064.74 | Total : | 1023071943.604
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3564.4475 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 973.316 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1361.5937 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1181.7842 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 973.2603 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 722.9661 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 406.2011 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 337.6467 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 660.3978 |  |  | 0 | 0%
Total |  | 0 |  | 10181.6133 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Megnaghat-450 MW.
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:17 | 16:45 | Goalpara-Labanchura 132kV Ckt-2 Scheduled S/D from Goalpara 132/33kV end Due to Maintenence works .
08:19 | 13:46 | Chapainawabganj-Rahanpur 132kV Ckt-1 Scheduled S/D from Chapai 132/33kV end Due to Scada intrgration .
08:20 | 16:43 | Bagerhat-Labanchura 132 kV Ckt-2 Scheduled S/D from Bagerhat 132/33kV end.
08:23 | 15:13 | Bheramara 230/132kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance .
08:23 | 15:13 | Bheramara 230/132kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance.
08:23 | 13:43 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to Ten telta test .
08:27 | 15:35 | Aminbazar-Meghnaghat 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end.
08:40 | 16:36 | Gopalganj(N)-Madaripur 132kV Ckt-3 Scheduled S/D from Madaripur 132/33kV end Due to Annual maintenance and from
Gopalganj 400/132kVend.
08:40 | 16:37 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Scheduled S/D Due to Annual maintenance.
08:41 | 11:44 | Rampur 230/132/33 S/S Khulshi-2 Scheduled S/D Due to Khulshi Gird Maintenance .
08:42 | 11:41 | Halishahar-Khulshi 132kV Ckt-2 Scheduled S/D from Khulshi 132/33kV end Due to Annual Maintenance(BAY).
08:49 | 16:37 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 Scheduled S/D
08:57 | 17:39 | Bibiyana-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Bibiana 400/230kV end Due to A/M.
09:05 | 12:35 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Scheduled S/D Due to Shutdown taken by Satkania PDB for Isolator
maintenance work.
09:05 | 12:35 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Scheduled S/D Due to Shutdown taken by Satkania PDB for Isolator | [5 empty] | 30 MW load interrup.
maintenance work.
| 09:24 | Kaliakoir 400/230/132kV S/S 132 kV Bus-1 is restored.
09:39 | 14:30 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Forced S/D.
09:39 | 14:30 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Forced S/D Due to 132KV DS(Q7) Maintenance.
09:40 | 16:32 | Joydebpur 132/33kV S/S GT-4 HT Scheduled S/D Due to Gas leakage maintenance at 33 kV GIS Bus.
| 10:03 | Dhamrai-Kaliakoir 132 kV Ckt-1 is restored.
| 10:06 | Sirajganj-Ullahpara 132KV Ckt-1 is restored.
| 10:07 | Sirajganj-Ullahpara 132KV Ckt-2 is restored.
10:10 | 17:48 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Project Work S/D Due to Project work .
10:15 | 12:13 | Magura 132/33kV S/S T-1 (405T) HT Forced S/D Due to Oil leakage of radiator of 132kV (T1).
| 10:45 | Chandpur 132/33kV S/S 422T LT is restored.
| 10:45 | Chandpur 132/33kV S/S 422T HT is restored.
10:48 | 20:12 | Kamrangirchar-Keraniganj 132kV Ckt Scheduled S/D from Kamrangirchar 132/33kV end and from Keranigonj
230/132/33kV end Due to Maintenance at Kamrangirchar end.
10:55 | 20:05 | Kamrangirchar 132/33kV S/S Bus-1 Scheduled S/D.
| 11:15 | Sylhet 132/33kV S/S 150MW GT PS is restored.
| 11:20 | Chowmuhani 132/33kV S/S TR1-415T HT is restored.
11:22 | 13:17 | Chowmuhani 132/33kV S/S TR3-435T LT Scheduled S/D Due to Tr-3 33kv bus maintenance.
| 11:22 | Chowmuhani 132/33kV S/S TR1-415T LT is restored. | [5 empty] | 15 MW load interrup.
11:27 | 13:16 | Chowmuhani 132/33kV S/S TR3-435T HT Project Work S/D Due to Tr-3 33kv bus maintenance.
11:42 |  | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to Oil Centrifuge work.
| 11:52 | Chowmuhani 132/33kV S/S TR2-425T HT is restored.
| 11:55 | Chowmuhani 132/33kV S/S TR2-425T LT is restored.
| 12:25 | Meghnaghat 400/230 KV ATR-2 was switched on.
12:46 | 13:08 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to Auxiliary transformer fuse change. | [5 empty] | 30 MW load interrup.
| 13:35 | Sylhet 225 MW CCPP Syncronized with remarks:- GT .
13:46 | 15:52 | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D Due to Ten-Delta Test .
| 14:49 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 is restored.
15:44 | 18:25 | Aminbazar-Meghnaghat 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end.
16:05 | 16:39 | Kabirpur -Tongi 132kV Ckt-2 Forced S/D from Tongi 230/132/33kV end Due to Removing dish wire from line. | [5 empty] | 50 MW load interrup in
| 16:11 | Faridpur 132/33kV S/S Transformer-2 HT is restored. | [5 empty] | Tongi 230/132 kV end.
| 16:12 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
| 16:49 | Cox'sbazar-Dohazari 132 kV Ckt-1 is restored.
| 17:07 | Bogura(New)-Naogaon 132 kV Ckt-1 is restored.
| 17:09 | Bogura(New)-Naogaon 132 kV Ckt-2 is restored.
17:09 |  | Naogaon-Niyamatpur 132kV Ckt-1 Forced S/D from Niamatpur 132/33kV end Due to Naogaon-Niyamatpur CB open.
| 17:09 | Bogura(New)-Naogaon 132 kV Ckt-2 is restored.
| 17:23 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
| 17:23 | Daudkandi-Sonargaon 132 kV Ckt-2 is restored.
21:00 | 22:26 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Forced S/D Due to PBS 33 kV feeder bus side loop Red hot remove purpose. | [5 empty] | 15 MW load interrup.
21:00 | 22:25 | Mirzapur 132/33kV S/S Transformer-02(E07) HT Forced S/D Due to PBS 33 kV feeder bus side loop Red hot remove purpose.
| 22:40 | Feni 132/33kV S/S Bus-1 is restored.
| 22:44 | Feni 132/33kV S/S T-2(415T) LT is restored.
| 22:44 | Feni 132/33kV S/S T-2(415T) HT is restored.
| 23:19 | Chauddagram-Feni 132 kV Ckt-1 is restored.
| 23:19 | Chauddagram-Feni 132 kV Ckt-1 is restored.
| 23:20 | Chauddagram-Feni 132 kV Ckt-2 is restored.
| 23:20 | Chauddagram-Feni 132 kV Ckt-2 is restored.
| 23:30 | Feni 132/33kV S/S Feni-Lanka HFO PS is restored.
02:04 |  | Bibiyana-3 400 MW tripped due to tripping of gas booster compressor.
05:19 | 05:32 | Niamatpur 132/33kV S/S 426T LT Tripped showing DIR O/C & E/F Relay. relays Due to Rajshahi -2 Feeder fault . | [5 empty] | 15 MW load interrup.
| 05:34 | Mirzapur 132/33kV S/S Transformer-01(E05) HT is restored.
05:53 |  | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to Pbs bus side red hot maintenance work. | [5 empty] | 25 MW load interrup.
06:12 | 06:34 | Mirzapur 132/33kV S/S Transformer-02(E07) LT Tripped showing OC, EF relays Due to PBS 33 kV feeder fault.
06:12 | 06:34 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Tripped showing OC,EF relays Due to PBS 33 feeder fault.
06:12 | 06:33 | Mirzapur 132/33kV S/S Transformer-01(E05) HT Tripped showing 87T General Trip relays Due to PBS 33 kV feeder fault.
06:54 |  | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to Pbs bus side red hot maintenance work.
07:03 |  | Aminbazar-Meghnaghat 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end.
07:26 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled S/D Due to General cleaning.
07:26 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D.
07:28 | 07:32 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to 33 kV Bus Coupler DS open from PDB (33 kv side) | [5 empty] | 18 MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-02-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 3336531 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 411 | 9370800
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 14400 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 46464 | Low Demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 25 | 153155 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 11101 | Low Demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 13440 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7389067
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 154944 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 28080 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 933120 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 40261 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 39199 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 918480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 513360 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 18 | 475600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 193920 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 63 | 135491 | Low Demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 403920 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 543360
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 35 | 332160 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 194400 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 173501
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 69840 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 605 | 10232727 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 100 | 2565909 | On test.
| Dhaka area Total |  |  |  | 5062 | 2274 | 38283230
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 142140 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 111240
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 181440 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 906420 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 216 | 5059967
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 287709 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 50 | 978432 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 118407 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 314880 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 241920 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 567360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22438
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 115 | 855600 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 90528 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 213270 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 363840 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 301091 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 144 | 610545 | Low Demand
| SS Power I |  | SS Power | 2*612 | 1224 | 281 | 6850908
| Cox's Bazar Wind |  | IPP | 66 | 0 | 3 | 37440 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 156 | 3832727 | On test.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 162
| Chattogram area Total |  |  |  | 4344 | 1204 | 22088464
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 151 | 3543000 | ST under maint
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6810000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 7324600 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 389376 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 10 | 212160 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 33455 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 939716
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 93672 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 339008 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 569280 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 122220
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2446080
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 819700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 10 | 112433 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 15 | 292950 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Line S/D
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 796320 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 234720 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 53 | 275520 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1216 | 25354210
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 67 | 1566720 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10800
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 9 | 180000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 69 | 919200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 271590
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 44880 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 151 | 2993190
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 903000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 947040 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3556636
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 336600 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 260208 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 531360 | GT-9 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 80 | 454127 | On test.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 137 | 1354780 | ST under maint
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 405000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 385632 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7152000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8471000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 236700
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 7778000 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1513 | 32772083
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 618 | 18827636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 10 | 11520 | Low Demand
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 82 | 157312 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 50880 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 457920
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 357 | 8574545
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1067 | 28079813
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 36192 | Low Demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 7 | 135125 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 105 | 2445000 | GT-2 under maint
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 950 | 19622200 | Increasing
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4732145
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 25200 | Reserve
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 3643600 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1448 | 30639462
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 12923 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 50 | 83827
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4081118 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 299 | 7734690 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 68717 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 127062 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 13786 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 51 | 217120 | Low Demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 67968 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 86688 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32400
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1291 | 25337498
| Rajshahi Area Total |  |  |  | 3631 | 1979 | 37863797
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4144100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 10000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 194496 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42846
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 54 | 156096 | Low Demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232942
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1168250
| Rangpur Area Total |  |  |  | 950 | 280 | 5948730
| Total |  |  |  | 25481 | 11132 | 224022979
| Eastern Grid Total |  |  |  | 15398 | 6358 | 121491177
| Western Grid Total |  |  |  | 10083 | 4774 | 102531802
| National Grid Total |  |  |  | 25481 | 11132 | 224022979
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-02-24
| (a) ENTIRE EASTERN GRID : |  | 7420.33 | MW | (b) ENTIRE WESTERN GRID : |  | 3388 | MW
| i) Dhaka area |  | 4026.33 | MW | i) Khulna area |  | 1215.4 | MW
| ii) Chittagong area |  | 1192 | MW | ii) Rajshahi area |  | 1093.6 | MW
| iii) Comilla area |  | 903 | MW | iii) Barisal area |  | 313 | MW
| iv) Mymensingh area |  | 923 | MW | iv) Rangpur area |  | 766 | MW
| v) Sylhet area |  | 376 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10808.33 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 16 | 13:00 | Kamrangirchar | 47.4 | 13:00 | Narinda | 42 | 13:00 | Sherpur | 120 | 18:30
2 | AKSML | 104 | 14:00 | Chowmuhani | 149 | 18:30 | Kaptai | N/A | N/A | Narshingdi | 142 | 21:00 | Shikalbaha | 20 | 18:30
3 | Aftabnagar | 26 | 18:30 | Chuadanga | 75 | 18:30 | Kazla | 86 | 13:00 | Natore | 110 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 59 | 14:00 | Coxsbazar | 108 | 18:30 | Keranigonj | 68 | 19:00 | Nawabganj | 36.4 | 13:00 | Shitalakhya | 81.8 | 12:00
5 | Agrabad | 58 | 19:00 | Cumilla(N) | 101 | 19:30 | Khagrachori | 22 | 18:00 | Netrakona | 99 | 19:00 | Sholosohor | 36 | 15:00
6 | Amnura | 55 | 10:00 | Cumilla(S) | 127 | 18:30 | Khulna | 72 | 19:00 | New | 18.5 | 12:00 | Shyampur | 156 | 12:00
7 | Ashuganj | 46 | 13:00 | Daudkandi | 104 | 20:00 | Khulshi | 147 | 13:00 | Niamatpur | 73 | 07:00 | Siddhirganj | 108 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 20 | 13:00 | Kishoreganj | 108 | 18:30 | Noapara | 35 | 19:00 | Sirajganj | 86 | 19:00
9 | BSRM | 137 | 04:00 | Dhamrai | 124 | 15:00 | Kodda | 258 | 19:30 | PHP | 3 | 10:00 | Sonargaon | 82 | 11:00
10 | Bagerhat | 68 | 18:30 | Dhanmondi | 103 | 13:00 | Kulaura | 28 | 18:30 | Pabna | 82 | 19:00 | Sreemongol | 39 | 18:30
11 | Bakulia | 73 | 19:00 | Dohazari | 80 | 19:30 | Kurigram | 60 | 08:00 | Palashbari | 99 | 11:00 | Sreepur | 58 | 21:00
12 | Banani | 23.2 | 13:00 | Faridpur | 110 | 18:30 | Kushtia | 110 | 18:30 | Panchagarh | 46 | 18:30 | Srinagar | 28.74 | 22:00
13 | Bangabhaban | 4 | 10:00 | Fatullah | 55 | 12:00 | Lalbag | 75 | 13:00 | Patuakhali | 52 | 19:30 | Sunamganj | 36 | 18:30
14 | Barapukuria | 58 | 10:00 | Fenchuganj | 23 | 20:00 | Lalmonirhat | 40 | 18:30 | Payra | 15 | 19:00 | Sylhet | 10 | 00:00
15 | Barguna | 16 | 21:00 | Feni | 77 | 18:30 | MI_Cement | 11.7 | 03:00 | Postogola | 39 | 18:30 | Sylhet-132 | 104 | 18:00
16 | Barishal | 81 | 19:00 | GPH | 97 | 13:00 | Madanganj | 30 | 00:00 | Purbachal | 13 | 14:00 | TK | 17.5 | 18:00
17 | Barishal-230 | 66 | 18:30 | Ghorashal | 82 | 19:00 | Madaripur | 64 | 21:00 | Purbasadipur | 107 | 08:00 | Tangail | 162 | 07:00
18 | Baroaulia | 64 | 11:00 | Goalpara | 22 | 18:30 | Madartek | 52 | 13:00 | Rahim | 47 | 15:00 | Thakurgaon | 82 | 19:00
19 | Baroirhat | 43 | 19:00 | Gollamari | 49 | 12:00 | Madunaghat | 38 | 18:30 | Rajbari | 48 | 19:00 | Tongi | 123 | 18:00
20 | Bashundhara | 134 | 18:30 | Gopalganj | 68.1 | 20:00 | Magura | 44 | 18:30 | Rajendrapur | 78 | 18:30 | Ullahpara | 23 | 12:00
21 | BashundharaCement | 7 | 11:00 | Gulshan | 68 | 13:00 | Mahasthangarh | 72 | 08:00 | Rajshahi | 105 | 13:00 | Ullon | 35 | 18:30
22 | Beanibazar | 44 | 18:30 | Halishahar | 70.5 | 15:00 | Manikganj | 89 | 21:00 | Rajshahi-230 | 25 | 19:30 | Uttara | 46 | 13:00
23 | Benapole | 49 | 08:00 | HaripurSBU | 129 | 12:00 | Maniknagar | 50 | 18:00 | Ramganj | 78 | 21:00 | UttaraNew | 31 | 13:00
24 | Bhaluka | 122 | 14:00 | Hasnabad | 54 | 21:00 | Matarbari | 40 | 18:00 | Rampur | 21 | 18:00 | Zigatola | 48 | 14:00
25 | Bhandaria | 36 | 19:00 | Hathazari | 56 | 18:30 | Matuail | 60 | 11:00 | Rangamati | 14 | 18:30
26 | Bhangura | 30 | 08:00 | Ishurdi | 52 | 18:30 | Millgate | 84 | 18:30 | Rangpur | 106 | 18:30
27 | Bheramara(GK) | 40 | 18:30 | Jaldhaka | 66 | 18:30 | Mirpur | 100.5 | 18:30 | Ruppur | 2.8 | 11:00
28 | Bhulta | 238 | 09:00 | Jamalpur | 132 | 07:00 | Mirsorai | 3 | 01:00 | SSM | 1 | 21:00
29 | Bog-Sherpur | 52 | 09:00 | Jashore | 113 | 13:00 | Mirzapur | 55 | 18:30 | Saidpur | 100 | 09:00
30 | Bogura | 117 | 09:00 | Jhenaidah | 92 | 18:30 | Mithapukur | 44 | 18:30 | Satkhira | 91 | 18:30
31 | Borhanuddin | 52 | 19:00 | Joydebpur | 128 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 83 | 14:00
32 | Brahmanbaria | 110 | 18:30 | Joypurhat | 58 | 20:00 | Mogbazar | 90.1 | 13:00 | Savar | 146 | 18:00
33 | Cantonment | 95 | 18:30 | Juldah | 19 | 15:00 | Mongla | 30 | 13:00 | SevenRings | 21.63 | 22:00
34 | Chandpur | 44 | 18:30 | KSRM | 27 | 16:00 | Motijheel | 30 | 13:00 | ShahCement | 27 | 00:00
35 | Chandraghona | 24 | 19:00 | Kabirpur | 255 | 18:30 | Munshiganj | 70 | 13:00 | Shahjadpur | 63 | 08:00
36 | Chapai | 57 | 12:00 | Kachua | 50 | 18:30 | Mymensingh | 170 | 19:00 | Shahjibazar | 83 | 19:00
37 | Charsaidpur | 42 | 15:00 | Kallyanpur | 81 | 12:00 | Naogaon | 114 | 10:00 | Shahmirpur | 44 | 17:00
38 | Chauddagram | 48 | 18:00 | Kalurghat | 28 | 12:00 | Narail | 32 | 19:00 | Shariatpur | 53 | 19:30
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-02-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 409 | 05:00 | 390 | 14:00 | Gopalganj | 413 | 05:00 | 398 | 13:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 401 | 03:00 | 382 | 12:00
| Bhulta | 391 | 04:00 | 377 | 12:00 | Madunaghat_I | 412 | 11:00 | 403 | 14:00
| Bibiana | 417 | 19:00 | 407 | 13:00 | Payra | 420 | 02:00 | 410 | 20:00
| BIPTC | 408 | 03:00 | 392 | 12:00 | Rahanpur | 418 | 04:00 | 401 | 20:00
| Bogura | 411 | 04:00 | 389 | 20:00 | Rampal | 411 | 05:00 | 395 | 19:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 03:00 | 221 | 15:00 | Haripur | 230 | 03:00 | 221 | 12:00
| AKSML | 233 | 19:00 | 223 | 01:00 | Hasnabad | 232 | 02:00 | 220 | 12:00
| Aminbazar | 234 | 08:00 | 223 | 15:00 | Hathazari | 232 | 09:00 | 221 | 16:00
| Ashuganj | 236 | 03:00 | 228 | 12:00 | Ishurdi | 240 | 04:00 | 225 | 11:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 238 | 04:00 | 221 | 13:00
| Baghabari | 237 | 04:00 | 225 | 12:00 | Kaliakoir | 234 | 05:00 | 219 | 12:00
| Barapukuria | 223 | 03:00 | 210 | 08:00 | Keranigonj | 233 | 05:00 | 220 | 16:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 241 | 05:00 | 227 | 13:00
| Barishal | 244 | 03:00 | 237 | 14:00 | Madunaghat_I | 232 | 09:00 | 224 | 14:00
| Bheramara | 239 | 04:00 | 222 | 11:00 | Maniknagar | 231 | 04:00 | 221 | 15:00
| Bhulta | 234 | 04:00 | 222 | 12:00 | Meghnaghat | 232 | 07:00 | 223 | 14:00
| Bibiana | 240 | 03:00 | 233 | 15:00 | Mirsorai | 236 | 19:30 | 222 | 14:00
| BIPTC | 240 | 05:00 | 223 | 13:00 | Rajshahi | 241 | 19:00 | 225 | 11:00
| Bogura | 235 | 04:00 | 223 | 13:00 | Rampal | 239 | 05:00 | 225 | 13:00
| Bogura-400 | 237 | 04:00 | 218 | 09:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 03:00 | 243 | 12:00 | Rampura | 231 | 04:00 | 221 | 12:00
| BSRM | 233 | 09:00 | 222 | 16:00 | Shikalbaha | 229 | 09:00 | 221 | 16:00
| Cumilla(N) | 233 | 19:00 | 225 | 11:00 | Shyampur | 232 | 05:00 | 221 | 12:00
| Fenchuganj | 243 | 08:00 | 239 | 12:00 | Siddhirganj | 231 | 01:00 | 223 | 12:00
| Ghorashal | 235 | 00:00 | 222 | 15:00 | Sirajgonj | 242 | 04:00 | 233 | 13:00
| Ghorashal-230 | 233 | 03:00 | 223 | 11:00 | Sreepur | 237 | 05:00 | 226 | 12:00
| GPH | 231 | 09:00 | 220 | 16:00 | Tongi | 238 | 04:00 | 215 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 130 | 01:00 | 123 | 12:00 | Lalbag | 137 | 05:00 | 128 | 11:00
| Agargaon | 139 | 03:00 | 131 | 12:00 | Lalmonirhat | 132 | 05:00 | 120 | 08:00
| Agrabad | 136 | 09:00 | 126 | 17:00 | Madanganj | 135 | 03:00 | 128 | 15:00
| AKS | 133 | 08:00 | 125 | 17:00 | Madaripur | 137 | 00:00 | 133 | 13:00
| Aminbazar | 134 | 07:00 | 125 | 15:00 | Madartek | 131 | 05:00 | 122 | 13:00
| Amnura | 136 | 03:00 | 123 | 13:00 | Madunaghat | 135 | 09:00 | 128 | 14:00
| Ashuganj | 140 | 05:00 | 135 | 15:00 | Magura | 139 | 03:00 | 128 | 13:00
| Bagerhat | 134 | 01:00 | 122 | 13:00 | Mahasthangarh | 136 | 03:00 | 122 | 02:00
| Bakulia | 135 | 09:00 | 127 | 16:00 | Manikganj | 136 | 10:00 | 124 | 12:00
| Banani | 133 | 00:00 | 127 | 12:00 | Maniknagar | 135 | 01:00 | 129 | 11:00
| Bangabhaban | 135 | 01:00 | 129 | 11:00 | Matarbari | 122 | 17:00 | 108 | 00:00
| Barapukuria | 138 | 03:00 | 127 | 08:00 | Matuail | 135.5 | 05:00 | 128.4 | 12:00
| Barguna | 132 | 06:00 | 127 | 19:00 | Millgate | 139 | 04:00 | 126 | 15:00
| Barishal | 140 | 01:00 | 122 | 20:00 | Mirpur | 132 | 02:00 | 124 | 16:00
| Barishal-230 | 140 | 03:00 | 135 | 20:00 | Mirzapur | 135 | 01:00 | 127 | 07:00
| Baroaulia | 133 | 09:00 | 128 | 14:00 | Mithapukur | 134 | 01:00 | 121 | 08:00
| Baroirhat | 134 | 09:00 | 120 | 14:00 | MI_Cement | 135.5 | 05:00 | 128.6 | 12:00
| Bashundhara | 136 | 00:00 | 126 | 12:00 | Modern | 131 | 04:00 | 127 | 16:00
| BashundharaCement | 135 | 01:00 | 128 | 13:00 | Mogbazar | 132 | 05:00 | 125 | 11:00
| Beanibazar | 136 | 04:00 | 132 | 12:00 | Mongla | 132 | 00:00 | 122 | 12:00
| Benapole | 135 | 06:00 | 125 | 11:00 | Motijheel | 135 | 01:00 | 128 | 12:00
| Bhaluka | 134 | 03:00 | 124 | 14:00 | Munshiganj | 135 | 19:00 | 129 | 12:00
| Bhandaria | 133 | 11:00 | 122 | 19:00 | Mymensingh | 133 | 03:00 | 122 | 07:00
| Bhangura | 137 | 00:00 | 131 | 11:00 | Naogaon | 133 | 01:00 | 119 | 12:00
| Bheramara | 139 | 04:00 | 130 | 11:00 | Narail | 140 | 05:00 | 128 | 13:00
| Bheramara(GK) | 138 | 04:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 125 | 18:30 | 116 | 12:00 | Narshingdi | 135 | 04:00 | 124 | 11:00
| Bog-Sherpur | 138 | 04:00 | 123 | 13:00 | Natore | 137 | 04:00 | 127 | 11:00
| Bogura | 138 | 04:00 | 129 | 09:00 | Nawabganj | 136 | 02:00 | 127 | 16:00
| Bogura-230 | 138 | 04:00 | 129 | 08:00 | Netrakona | 132 | 00:00 | 120 | 09:00
| Brahmanbaria | 135 | 09:00 | 131 | 11:00 | New | 138 | 04:00 | 127 | 12:00
| Cantonment | 139 | 04:00 | 130 | 15:00 | Niamatpur | 136 | 04:00 | 128 | 08:00
| Chandpur | 134 | 09:00 | 122 | 00:00 | Noapara | 137 | 04:00 | 125 | 13:00
| Chandraghona | 137 | 09:00 | 128 | 16:00 | Pabna | 140 | 03:00 | 130 | 13:00
| Chapai | 135 | 00:00 | 126 | 09:00 | Palashbari | 132 | 02:00 | 118 | 08:00
| Charsaidpur | 136 | 05:00 | 129 | 12:00 | Panchagarh | 135 | 05:00 | 111 | 08:00
| Chauddagram | 138 | 09:00 | 126 | 00:00 | Patuakhali | 131 | 02:00 | 127 | 19:30
| Chhatak | 136 | 02:00 | 132 | 12:00 | Payra | 134 | 04:00 | 130 | 19:30
| Chowmuhani | 132 | 09:00 | 118 | 14:00 | PHP | 133 | 09:00 | 120 | 16:00
| Chuadanga | 138 | 05:00 | 124 | 13:00 | Postogola | 135 | 03:00 | 130 | 11:00
| Coxsbazar | 124 | 01:00 | 113 | 00:00 | Purbachal | 135 | 04:00 | 126 | 11:00
| Cumilla(N) | 138 | 07:00 | 132 | 00:00 | Purbasadipur | 129 | 04:00 | 115 | 08:00
| Cumilla(S) | 137 | 08:00 | 127 | 16:00 | Rahanpur | 138 | 03:00 | 132 | 12:00
| Daudkandi | 133 | 04:00 | 121 | 14:00 | Rahim | 135 | 03:00 | 129 | 12:00
| Dhaka | 131 | 05:00 | 123 | 13:00 | Rajbari | 139 | 04:00 | 130 | 13:00
| Dhamrai | 137 | 02:00 | 126 | 15:00 | Rajendrapur | 138 | 18:30 | 129 | 13:00
| Dhanmondi | 135 | 07:00 | 129 | 12:00 | Rajshahi | 134 | 03:00 | 125 | 11:00
| Dohazari | 130 | 08:00 | 123 | 17:00 | Rajshahi-230 | 135 | 04:00 | 124 | 09:00
| Faridpur | 139 | 03:00 | 132 | 22:00 | Ramganj | 133 | 09:00 | 118 | 01:00
| Fatullah | 137 | 04:00 | 130 | 11:00 | Rampur | 134 | 09:00 | 125 | 17:00
| Fenchuganj | 138 | 04:00 | 136 | 12:00 | Rampura | 133 | 04:00 | 126 | 15:00
| Feni | 133 | 09:00 | 120 | 14:00 | Rangamati | 136 | 09:00 | 127 | 16:00
| Ghorashal | 140 | 04:00 | 134 | 17:00 | Rangpur | 133 | 04:00 | 118 | 08:00
| Goalpara | 138 | 03:00 | 125 | 18:30 | Ruppur | 141 | 05:00 | 132 | 11:00
| Gollamari | 137 | 04:00 | 127 | 12:00 | Saidpur | 132 | 04:00 | 116 | 08:00
| Gopalganj | 136 | 04:00 | 124 | 13:00 | Satkhira | 134 | 04:00 | 125 | 18:30
| Gopalganj-400 | 138 | 04:00 | 132 | 13:00 | Satmasjid | 138 | 03:00 | 130 | 13:00
| Gulshan | 132 | 01:00 | 126 | 12:00 | Savar | 130 | 00:00 | 122 | 16:00
| Halishahar | 135 | 09:00 | 126 | 16:00 | SevenRings | 140 | 04:00 | 132 | 03:00
| Haripur | 135 | 03:00 | 129 | 12:00 | ShahCement | 136 | 05:00 | 129 | 12:00
| HaripurSBU | 135 | 03:00 | 129 | 12:00 | Shahjadpur | 140 | 00:00 | 134 | 11:00
| Hasnabad | 136 | 07:00 | 129 | 15:00 | Shahjibazar | 134 | 00:00 | 131 | 16:00
| Hathazari | 137 | 09:00 | 130 | 17:00 | Shahmirpur | 134 | 08:00 | 127 | 14:00
| Ishurdi | 142 | 05:00 | 133 | 11:00 | Shariatpur | 138 | 04:00 | 131 | 20:00
| Jaldhaka | 131 | 04:00 | 116 | 08:00 | Sherpur | 127 | 15:00 | 112 | 07:00
| Jamalpur | 129 | 15:00 | 116 | 07:00 | Shikalbaha | 125 | 09:00 | 115 | 17:00
| Jashore | 136 | 02:00 | 124 | 12:00 | Shikalbaha-230 | 135 | 09:00 | 128 | 16:00
| Jhenaidah | 138 | 00:00 | 129 | 13:00 | Shitalakhya | 135.5 | 05:00 | 128.6 | 12:00
| Jhenaidah-230 | 141 | 05:00 | 129 | 13:00 | Sholosohor | 135 | 09:00 | 126 | 16:00
| Joydebpur | 138 | 18:00 | 128 | 15:00 | Shyampur | 136 | 07:00 | 130 | 12:00
| Joypurhat | 133 | 04:00 | 120 | 17:00 | Shyampur-230 | 137 | 02:00 | 130 | 12:00
| Juldah | 135 | 09:00 | 127 | 16:00 | Siddhirganj | 134 | 03:00 | 129 | 12:00
| Kabirpur | 138 | 13:00 | 119 | 17:00 | Sirajganj | 137 | 02:00 | 120 | 09:00
| Kachua | 136 | 09:00 | 125 | 00:00 | Sonargaon | 133 | 04:00 | 126 | 12:00
| Kaliakoir | 140 | 02:00 | 131 | 17:00 | Sreemongol | 135 | 00:00 | 132 | 11:00
| Kallyanpur | 135 | 02:00 | 128 | 12:00 | Sreepur | 136 | 05:00 | 128 | 12:00
| Kalurghat | 135 | 09:00 | 127 | 17:00 | Srinagar | 135 | 03:00 | 128 | 13:00
| Kamrangirchar | 135 | 04:00 | 127 | 12:00 | SSM | 136 | 00:00 | 132 | 15:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 135 | 09:00 | 131 | 12:00
| Kazla | 136 | 05:00 | 128 | 13:00 | Sylhet | 136 | 07:00 | 133 | 11:00
| Keranigonj | 137 | 04:00 | 128 | 12:00 | Sylhet-132 | 136 | 00:00 | 133 | 12:00
| Khagrachori | 136 | 09:00 | 126 | 16:00 | Tangail | 132 | 00:00 | 125 | 07:00
| Khulna | 134 | 04:00 | 127 | 12:00 | Thakurgaon | 133 | 04:00 | 109 | 08:00
| Khulna(S) | 137 | 04:00 | 127 | 13:00 | TK | 136 | 09:00 | 128 | 16:00
| Khulshi | 134 | 09:00 | 125 | 16:00 | Tongi | 138 | 07:00 | 130 | 08:00
| Kishoreganj | 136 | 03:00 | 127 | 12:00 | Ullahpara | 138 | 01:00 | 130 | 13:00
| Kodda | 139 | 19:00 | 125 | 14:00 | Ullon | 130 | 02:00 | 123 | 16:00
| KSRM | 136 | 09:00 | 126 | 17:00 | Uttara | 139 | 05:00 | 126 | 16:00
| Kulaura | 138 | 00:00 | 135 | 12:00 | UttaraNew | 138 | 01:00 | 126 | 16:00
| Kurigram | 131 | 01:00 | 115 | 08:00 | Zigatola | 136 | 02:00 | 127 | 12:00
| Kushtia | 138 | 04:00 | 130 | 11:00

## L-Curve
Date | 2024-02-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1270 | 4922 | 4289 | 9211 |  |  |  | QF-LDC-11
0:30 | 1170 | 4588.5 | 4062 | 8650.5 | Date: | 2024-02-24
1:00 | 1070 | 4255 | 3835 | 8090
1:30 | 1039 | 4229 | 3633.5 | 7862.5
2:00 | 1008 | 4203 | 3432 | 7635
2:30 | 1020 | 4130 | 3403.5 | 7533.5 | [5 empty] | Gen. at Eve. Peak | 9893 | 9893 MW (19:00 )
3:00 | 1032 | 4057 | 3375 | 7432 | [6 empty] | 19:00
3:30 | 1016 | 3997.5 | 3359 | 7356.5 | [5 empty] | Gen. at Day Peak | 9346 | 9346 MW (12:00 )
4:00 | 1000 | 3938 | 3343 | 7281 | [6 empty] | 12:00
4:30 | 985 | 3891 | 3316 | 7207 | [5 empty] | Highest Generation | 9893
5:00 | 970 | 3844 | 3289 | 7133 | [6 empty] | 19:00
5:30 | 950 | 3947.5 | 3294.5 | 7242
6:00 | 930 | 4051 | 3300 | 7351
6:30 | 895 | 4303.5 | 3380.5 | 7684
7:00 | 860 | 4556 | 3461 | 8017
7:30 | 810 | 4769.5 | 3636.5 | 8406
8:00 | 760 | 4983 | 3812 | 8795
8:30 | 770 | 5044 | 3927 | 8971
9:00 | 780 | 5105 | 4042 | 9147
9:30 | 808 | 5054.5 | 3967 | 9021.5
10:00 | 836 | 5004 | 3892 | 8896
10:30 | 988 | 5070 | 4079 | 9149
11:00 | 1140 | 5136 | 4266 | 9402
11:30 | 1200 | 5218.5 | 4369.5 | 9588
12:00 | 1260 | 5301 | 4473 | 9774
12:30 | 1240 | 5409 | 4555.5 | 9964.5
13:00 | 1220 | 5517 | 4638 | 10155
13:30 | 1230 | 5545 | 4597 | 10142
14:00 | 1240 | 5573 | 4556 | 10129
14:30 | 1235 | 5502.5 | 4450.5 | 9953
15:00 | 1230 | 5432 | 4345 | 9777
15:30 | 1205 | 5344 | 4283.5 | 9627.5
16:00 | 1180 | 5256 | 4222 | 9478
16:30 | 1170 | 5293 | 4171.5 | 9464.5
17:00 | 1160 | 5330 | 4121 | 9451
17:30 | 1140 | 5532 | 4305 | 9837
18:00 | 1120 | 5734 | 4489 | 10223
18:30 | 1025 | 6046 | 4631.5 | 10677.5
19:00 | 930 | 6358 | 4774 | 11132
19:30 | 1090 | 6002 | 4843 | 10845
20:00 | 1130 | 5854 | 4902 | 10756 |  |  |  | Executive Engineer
20:30 | 1200 | 5783.5 | 4915.5 | 10699 |  |  |  | Network Operation Division
21:00 | 1270 | 5713 | 4929 | 10642
21:30 | 1295 | 5606 | 4837 | 10443
22:00 | 1320 | 5499 | 4745 | 10244 |  |  |  |  | Page 6 of 7
22:30 | 1300 | 5217 | 4751 | 9968
23:00 | 1280 | 4935 | 4757 | 9692
23:30 | 1275 | 4928.5 | 4523 | 9451.5
24:00 | 1270 | 4922 | 4289 | 9211
9893 MW (19:00 )
9346 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-02-24 |  | Energy |  | 224022979
[14 empty] | 2024-02-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3400 | 903 | 1435 | 0 | 207 | 2992 | 35 | 0 | 129 | 108 | 0 | 2 | 0
0:30 | 3166.5 | 905 | 1415.5 | 0 | 118.5 | 2833 | 35 | 0 | 73 | 103 | 0 | 1 | 0 |  | Date: | 2024-02-24
1:00 | 2933 | 907 | 1396 | 0 | 30 | 2674 | 35 | 0 | 17 | 98 | 0 | 0 | 0
1:30 | 2929 | 789 | 1400.5 | 0 | 15 | 2590.5 | 35 | 0 | 8.5 | 95 | 0 | 0 | 0 | [8 empty] | Total Energy | 224.023 | 224.023 | Total Energy Gen 224.023 MKWHr Energy Not Served 0.108 MKWHr Energy Requirement 224.131 MKWHr
2:00 | 2925 | 671 | 1405 | 0 | 0 | 2507 | 35 | 0 | 0 | 92 | 0 | 0 | 0 | [8 empty] | Energy not Served | 0.10818 | 0.10818
2:30 | 2899.5 | 671 | 1360.5 | 0 | 0 | 2475.5 | 35 | 0 | 0 | 92 | 0 | 0 | 0 | [8 empty] | Energy Requirement | 224.1312 | 224.1312
3:00 | 2874 | 671 | 1316 | 0 | 0 | 2444 | 35 | 0 | 0 | 92 | 0 | 0 | 0
3:30 | 2821.5 | 672.5 | 1294.5 | 0 | 0 | 2441 | 35 | 0 | 0 | 92 | 0 | 0 | 0 | [7 empty] | Shortage
4:00 | 2769 | 674 | 1273 | 0 | 0 | 2438 | 35 | 0 | 0 | 92 | 0 | 0 | 0
4:30 | 2727 | 674 | 1255.5 | 0 | 0 | 2425.5 | 35 | 0 | 0 | 90 | 0 | 0 | 0
5:00 | 2685 | 674 | 1238 | 0 | 0 | 2413 | 35 | 0 | 0 | 88 | 0 | 0 | 0
5:30 | 2757.5 | 676 | 1270 | 0 | 0 | 2417.5 | 35 | 0 | 0 | 86 | 0 | 0 | 0
6:00 | 2830 | 678 | 1302 | 0 | 0 | 2422 | 35 | 0 | 0 | 84 | 0 | 0 | 0
6:30 | 2962.5 | 654.5 | 1407.5 | 0 | 25 | 2488 | 35 | 0 | 16.5 | 87 | 8 | 0 | 0 | [6 empty] | Coal
7:00 | 3095 | 631 | 1513 | 0 | 50 | 2554 | 35 | 0 | 33 | 90 | 16 | 0 | 0
7:30 | 3162 | 631 | 1595 | 0 | 139 | 2661 | 35 | 0 | 33 | 93 | 56 | 0 | 26.2625 | [5 empty] | Oil
8:00 | 3229 | 631 | 1677 | 0 | 228 | 2768 | 35 | 0 | 33 | 96 | 96 | 0 | 52.525
8:30 | 3230 | 631 | 1627.5 | 0 | 312 | 2813.5 | 37.5 | 0 | 72.5 | 86 | 159 | 0 | 56.345
9:00 | 3231 | 631 | 1578 | 0 | 396 | 2859 | 40 | 0 | 112 | 76 | 222 | 0 | 60.165
9:30 | 3203 | 631 | 1527 | 0 | 336 | 2786 | 40 | 0 | 136.5 | 80 | 280.5 | 0 | 30.0825
10:00 | 3175 | 631 | 1476 | 0 | 276 | 2713 | 40 | 0 | 161 | 84 | 339 | 0 | 0
10:30 | 3184 | 766.5 | 1483.5 | 0 | 296.5 | 2763.5 | 40 | 0 | 157.5 | 91 | 363 | 1 | 0
11:00 | 3193 | 902 | 1491 | 0 | 317 | 2814 | 40 | 0 | 154 | 98 | 387 | 2 | 0
11:30 | 3200.5 | 902 | 1504 | 0 | 390.5 | 2902.5 | 40 | 0 | 154 | 101 | 387.5 | 2.5 | 0
12:00 | 3208 | 902 | 1517 | 0 | 464 | 2991 | 40 | 0 | 154 | 104 | 388 | 3 | 0
12:30 | 3190 | 901.5 | 1657 | 0 | 478.5 | 3059 | 40 | 0 | 156 | 107 | 367.5 | 3.5 | 0
13:00 | 3172 | 901 | 1797 | 0 | 493 | 3127 | 40 | 0 | 158 | 110 | 347 | 4 | 0
13:30 | 3172 | 901 | 1797 | 0 | 493 | 3127 | 40 | 0 | 158 | 110 | 347 | 4 | 0
14:00 | 3172 | 901 | 1797 | 0 | 493 | 3127 | 40 | 0 | 158 | 110 | 347 | 4 | 0
14:30 | 3218 | 901 | 1749 | 0 | 471.5 | 3010 | 40 | 0 | 150 | 112 | 298 | 4 | 0
15:00 | 3264 | 901 | 1701 | 0 | 450 | 2893 | 40 | 0 | 142 | 114 | 249 | 4 | 0
15:30 | 3238.5 | 901.5 | 1698.5 | 0 | 421.5 | 2851 | 40 | 0 | 144.5 | 117 | 198.5 | 4 | 0
16:00 | 3213 | 902 | 1696 | 0 | 393 | 2809 | 40 | 0 | 147 | 120 | 148 | 4 | 0
16:30 | 3228 | 902 | 1708 | 0 | 411 | 2812 | 40 | 0 | 150.5 | 118 | 89 | 2 | 0
17:00 | 3243 | 902 | 1720 | 0 | 429 | 2815 | 40 | 0 | 154 | 116 | 30 | 0 | 0
17:30 | 3223 | 902 | 1700.5 | 0 | 617 | 2858.5 | 40 | 4.5 | 353.5 | 119 | 15 | 3 | 0
18:00 | 3203 | 902 | 1681 | 0 | 805 | 2902 | 40 | 9 | 553 | 122 | 0 | 6 | 0
18:30 | 3277.5 | 760 | 1724.5 | 0 | 1038.5 | 3128.5 | 40 | 4.5 | 576.5 | 123 | 0 | 4.5 | 0
19:00 | 3352 | 618 | 1768 | 0 | 1272 | 3355 | 40 | 0 | 600 | 124 | 0 | 3 | 0
19:30 | 3365 | 618 | 1787 | 0 | 920 | 3572 | 40 | 0 | 420 | 120 | 0 | 3 | 0
20:00 | 3403 | 618 | 1834 | 0 | 716 | 3639 | 40 | 0 | 384 | 120 | 0 | 2 | 0
20:30 | 3383 | 618 | 1848.5 | 0 | 672.5 | 3678.5 | 40 | 0 | 337.5 | 120 | 0 | 1 | 0
21:00 | 3363 | 618 | 1863 | 0 | 629 | 3718 | 40 | 0 | 291 | 120 | 0 | 0 | 0
21:30 | 3351.5 | 752 | 1849 | 0 | 541.5 | 3563 | 37.5 | 0 | 228.5 | 119 | 0 | 1 | 0
22:00 | 3340 | 886 | 1835 | 0 | 454 | 3408 | 35 | 0 | 166 | 118 | 0 | 2 | 0
22:30 | 3308.5 | 894 | 1697.5 | 0 | 402.5 | 3362 | 35 | 0 | 150 | 115 | 0 | 3.5 | 0
23:00 | 3277 | 902 | 1560 | 0 | 351 | 3316 | 35 | 0 | 134 | 112 | 0 | 5 | 0
23:30 | 3338.5 | 902.5 | 1497.5 | 0 | 279 | 3154 | 35 | 0 | 131.5 | 110 | 0 | 3.5 | 0 |  | Max Temp. in Dhaka |  | 29.0°C
24:00 | 3400 | 903 | 1435 | 0 | 207 | 2992 | 35 | 0 | 129 | 108 | 0 | 2 | 0
Executive Engineer
Network Operation Division
10756
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 224.023 MKWHr Energy Not Served 0.108 MKWHr Energy Requirement 224.131 MKWHr

## Generation
2024-02-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 906420
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [7 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 |  | 17 | 17 | 17 | 17 | 0 |  | 0 | 142140
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 12 | 16 | 17 | 13 | 18 | 16 | 12 | 7 | 2 | [9 empty] | 111240
6 | Sikalbaha 225MW CCPP (Gas) | 212 | 212 | 212 | 214 | 214 | 213 | 213 | 214 | 217 | 217 | 217 | 217 | 218 | 219 | 217 | 216 | 217 | 216 |  | 216 | 216 | 216 | 215 | 214 | 215 | 215 | 5059967
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 34 | 34 | 34 | 34 | 0 |  | 0 | 118407
12 | Hathazari 100 MW peaking PP | [8 empty] | 56 | 56 | 56 | 56 | 56 | 72 | 72 | 72 | 72 | 78 |  | 50 | 60 | 64 | 64 | 64 | 64 | 64 | 978432
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [7 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 287709
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [8 empty] | 7 | 40 | 33 | 33 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | [5 empty] | 0 | 339008
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 250 | 250 | 280 | 335 | 335 | 300 | 300 | 300 | 300 | 335 | 335 | 335 | 280 | 280 | 280 |  | 335 | 335 | 335 | 335 | 300 | 280 | 335 | 7389067
18 | Kodda 300 MW PP Unit-2 (Summit) | [7 empty] | 3 | 15 | [8 empty] | 12 |  | 63 | [5 empty] | 0 | 135491
19 | Ashuganj 195 MW PP (APSCL-United) | [10 empty] | 8 | 8 | 8 | [12 empty] | 0 | 33455
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 144 | 140 | 138 | 137 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 170 | 170 | 170 | 130 | 130 | 3336531
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 311 | 311 | 290 | 280 | 280 | 280 | 282 | 282 | 282 | 282 | 282 | 284 | 282 | 282 | 280 | 281 | 283 | 282 |  | 281 | 280 | 282 | 283 | 283 | 282 | 283 | 6850908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 44 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 41 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 389376
33 | Ashuganj 225 MW CCPP | 154 | 154 | 154 | 154 | 110 | 110 | 110 | 156 | 146 | 148 | 151 | 149 | 150 | 150 | 150 | 148 | 148 | 151 |  | 151 | 150 | 150 | 150 | 151 | 150 | 151 | 3543000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 290 | 315 | 300 | 270 | 270 | 290 | 270 | 270 | 270 | 270 | 305 | 305 | 270 |  | 270 | 270 | 270 | 270 | 270 | 280 | 310 | 6810000
| Ashuganj 450 MW CCPP(North) | [25 empty] | 0 | 0
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 330 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 330 | 330 | 290 | 325 | 7324600
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 12 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 212160
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 382 | 384 | 384 | 339 | 310 | 322 | 372 | 419 | 416 | 395 | 403 | 411 | 416 | 420 | 400 | 374 | 356 | 340 |  | 411 | 410 | 410 | 401 | 421 | 386 | 412 | 9370800
| Meghnaghat Unique power | 241 | 240 | 241 | 240 | 240 | 300 | 350 | 408 | 406 | 415 | 417 | 423 | 590 | 597 | 596 | 589 | 590 | 596 |  | 605 | 604 | 602 | 606 | 598 | 301 | 240 | 10232727
| Summit Meghanghat-2 589 MW(Gas) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2565909
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 95 | 95 | 95 | 95 | 72 | 96 | 95 | 65 | 65 | 67 | 63 | 31 | 33 | 35 | 33 | 33 | 57 | 72 |  | 67 | 66 | 67 | 69 | 73 | 72 | 72 | 1566720
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 5 | 19 | 39 | 35 | 20 | 49 | 45 | 34 | 20 | 6 | 0 | [8 empty] | 271590
44 | Fenchugonj CCPP Phase-1 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 903000
45 | Fenchugonj CCPP Phase-2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 947040
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 28 | 28 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 28 | 28 | 20 | 20 |  | 20 | 20 | 20 | 28 | 28 | 28 | 28 | 531360
48 | Shahjibazar 86 MW PP (Shahjibazar)
| Shahjibazar 100 MW GTPP | [10 empty] | 10 | 92 |  |  |  |  | 100 | 90 |  | 80 | 80 | 80 |  |  |  |  | 454127
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [13 empty] | 85 | 135 | 135 | 135 | 136 |  | 137 | 137 | 136 | 136 | 136 | 136 | 138 | 1354780
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 16 | 15 | 16 | 15 | 14 | 14 | 14 | 16 |  | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 405000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236700
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 5 | 5 | 5 | 5 | 41 | 51 | 51 | 31 | 31 | 31 | 31 | 31 | [11 empty] | 0 | 336600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 385632
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 295 | 290 | 290 | 285 | 290 | 315 | 300 | 290 | 270 | 310 | 290 | 295 | 285 | 280 | 295 | 305 | 290 |  | 285 | 290 | 270 | 295 | 295 | 290 | 290 | 7152000
| Bibiyana South 400 MW | 280 | 280 | 270 | 270 | 280 | 312 | 340 | 355 | 345 | 340 | 343 | 340 | 340 | 340 | 340 | 340 | 340 | 340 |  | 340 | 340 | 340 | 340 | 340 | 340 | 330 | 7778000
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | 17 | [5 empty] | 39199
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 44880
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 241920
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 98 | 92 | 92 | 92 | 88 | 84 | 90 | 96 | 76 | 84 | 98 | 104 | 110 | 106 | 114 | 120 | 116 | 122 |  | 124 | 120 | 120 | 120 | 118 | 112 | 108 | 2446080
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 15 | 7 | 7 | 6 | 2 | 0 | 0 | 0 | 0 | 3 | 6 |  | 18 | 17 | 20 | 32 | 36 | 36 | 40 | 567360
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 122220
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 819700
68 | Cumilla 25 MW PP (Summit) | 16 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 12 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 292950
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 408000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 15 | 22 | 22 | 22 | 22 | 510480
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 |  | 25 | 25 | 25 |  | 17 |  | 17 | 20 | 25 | 25 | 25 | 25 | 25 | 513360
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 12 | 12 | 12 | 12 | 14 | 14 | 475600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [7 empty] | 2 | 15 | 9 | 9 | 28 | 43 | 49 | 49 | 48 | 48 | 62 |  | 95 | 65 | 65 | 65 | 65 | 65 | 0 | 796320
| Manikgonj 162MW PP(MPGL) | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 17 |  |  |  | 0 | 194400
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 1 | 9 |  | 9 | [5 empty] | 0 | 13440
78 | Gazipur 52 MW PP | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 193920
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 105 |  | 115 | 115 | 115 | 115 | 64 | 48 | 48 | 933120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 1 | 8 | 8 | 8 | 10 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 16 | [5 empty] | 112433
| Gazipur 100 MW PP | [7 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 |  | 105 | 51 | 51 | 51 | 51 | 51 | 17 | 543360
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 2 | 3 | 4 | 3 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 22438
| Jodiac Power | [8 empty] | 5 |  |  | 13 | 17 | 17 | 17 | [10 empty] | 0 | 90528
| Karnaphuli Power Ltd. | [7 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 213270
82 | Madanganj 102 PP(Summit) | [7 empty] | 4 | 17 | 5 | [7 empty] | 11 |  | 17 | 2 | 4 |  |  |  | 0 | 46464
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 13 | [5 empty] | 0 | 11101
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 4 |  | 8 | [5 empty] | 0 | 14400
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 |  | 35 | 35 | 35 | 17 | 17 | 0 | 0 | 332160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima) | 5 | 5 | [5 empty] | 40 | 46 | 43 | 44 | 41 | 20 | 20 | [11 empty] | 0 | 260208
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 5 | 5 | 5 | 5 | 5 | 51 | 51 | 51 |  | 43 | 43 | 43 | 43 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 939716
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 16 |  | 64 | 41 | 8 | 8 | 0 |  | 0 | 154944
95 | Patenga 50MW PP (Baraka) | [7 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 181440
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 10 | 15 | 15 | 15 |  |  |  | 12 |  | 25 | 25 | 15 | 15 | 0 |  | 0 | 153155
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 15 |  | 17 | 17 | 17 |  |  |  | 0 | 40261
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 120 | 120 | 120 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 120 | 120 | 120 |  | 163 | 163 | 163 | 163 | 163 | 120 | 163 | 3556636
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 10800
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 11 |  | 17 | 17 |  |  |  |  | 0 | 28080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 3 | 9 | 9 | 9 | 19 | 19 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 180000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 32 | 29 | 17 | 17 | 21 |  | 35 | 35 | 35 | 35 | 35 | 20 | 17 | 403920
115 | Juldah 100 MW PP Unit-3 (Acorn) | [7 empty] | 16 | 25 |  |  | 25 | 25 | 25 | 25 |  |  | 10 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 314880
116 | Chandpur 200 MW (Desh energy) | [7 empty] | 20 | 34 | 17 | 17 | 29 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 39 | 36 | 569280
117 | Ashuganj 150 MW PP (Midland) | [6 empty] | 1 | 3 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 |  | 6 | 6 | 6 | 5 | 6 | 0 | 0 | 93672
118 | Bibiyana-III 400 MW CCPP | 318 | 316 | 317 | 315 | 317 | 345 | 347 | 373 | 365 | 365 | 379 | 364 | 365 | 365 | 366 | 364 | 348 | 329 |  | 366 | 365 | 365 | 365 | 365 | 374 | 364 | 8471000
| Jamalpur 115 MW PP (United) | [6 empty] | 19 | 56 | 56 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 69 | 69 |  | 69 | 69 | 69 | 69 | 9 | 9 | 9 | 919200
| Anwara 300 MW PP (United) | 30 | [5 empty] | 15 | 16 | 49 | 30 | 30 | 69 | 70 | 70 | 30 | 30 | 30 | 30 |  | 115 | 50 | 50 | 50 | 50 | 15 | 15 | 855600
| Juldah unit-2 (Acorn) | [7 empty] | 24 | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 363840
| Anlima Energy Ltd. | [6 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 301091
| Bhairob 54.5 MW | [9 empty] | 1 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 234720
| Spectra Solar Plant Ltd. | [6 empty] | 2 | 8 | 17 | 25 | 29 | 30 | 30 | 27 | 9 | 3 | 2 | [9 empty] | 173501
| Chandpur 115(Doreen) | [11 empty] | 1 | 16 | 18 | 18 | 17 | 17 | 21 |  | 53 | 54 | 54 | 24 | 18 | 0 | 0 | 275520
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 9 | 35 |  | 17 | [5 empty] | 0 | 69840
| Mirsharai 150 MW (Oil) | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 144 |  | 144 | 108 | 72 | 17 | 17 | 17 | 17 | 610545
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 4 | 2 | 4 | 4 | 0 | 6 |  | 3 | 3 | 2 | 0 | 2 | 5 | 2 | 37440
| Sonagazi 75 MW Solar Plant | [7 empty] | 2 | 2 | 1 | 4 | 3 | 6 | 10 | 19 | 6 | 2 | 0 | [8 empty] | 162
| Matarbari 2*600 MW (CPGCL) | 158 | 158 | 158 | 157 | 156 | 157 | 157 | 159 | 157 | 158 | 158 | 158 | 157 | 157 | 157 | 156 | 157 | 157 |  | 156 | 157 | 157 | 158 | 154 | 156 | 156 | 3832727
120 | Eastern Zone Total | 4255 | 4203 | 4057 | 3938 | 3844 | 4051 | 4556 | 4983 | 5105 | 5004 | 5136 | 5301 | 5517 | 5573 | 5432 | 5256 | 5330 | 5734 |  | 6358 | 6002 | 5854 | 5713 | 5499 | 4935 | 4922 | 121491177
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 5 | 5 |  | 10 | [6 empty] | 11520
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [20 empty] | 17 | 17 | 17 | 17 | 0 | 0 | 50880
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 4 | 24 | 49 | 65 | 62 | 74 | 44 | 72 | 28 | 19 | 4 | [9 empty] | 457920
131 | Rampal 1320 MW (BIFPCL) | 362 | 360 | 359 | 360 | 342 | 341 | 360 | 357 | 354 | 358 | 358 | 358 | 357 | 359 | 357 | 356 | 359 | 358 |  | 357 | 357 | 357 | 357 | 358 | 358 | 358 | 8574545
132 | United Payra Power Ltd. | [17 empty] | 7 | [7 empty] | 0 | 25200
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 178 | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 4732145
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 16 | 16 |  |  |  |  | 0 | 36192
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3643600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 110 | 110 | 110 | 115 | 130 | 135 | 135 | 110 | 110 |  | 105 | 125 | 135 | 135 | 120 | 135 | 110 | 2445000
140 | Bhola 33 MW PP (Venture) | 7 | 6 | 6 | 6 | 6 | 5 | 5 | 4 | 4 | 4 |  | 4 | 5 | 4 | 4 | 4 | 5 | 6 |  | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 135125
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [12 empty] | 5 | 5 | 5 | 10 | 12 | 49 |  | 82 | 10 | 10 | 10 | 5 | 5 |  | 157312
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 907 | 671 | 671 | 674 | 674 | 678 | 631 | 631 | 631 | 631 | 902 | 902 | 901 | 902 | 901 | 902 | 902 | 902 |  | 618 | 618 | 618 | 618 | 886 | 902 | 903 | 18827636
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 600 | 540 | 500 | 500 | 500 | 500 | 530 | 630 | 630 | 580 | 640 | 760 | 800 | 700 | 680 | 680 | 680 | 720 |  | 950 | 1150 | 1170 | 1244 | 1040 | 1040 | 860 | 19622200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4144100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 2 | 4 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 32400
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 140 | 130 | 130 | 130 | 130 | 154 | 220 | 201 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 153 | 193 | 190 | 4081118
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 314 | 315 | 300 | 270 | 240 | 240 | 300 | 350 | 300 | 250 | 250 | 250 | 341 | 301 | 315 | 345 | 346 | 312 |  | 299 | 315 | 381 | 369 | 345 | 414 | 344 | 7734690
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 127062
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 8 | [6 empty] | 12923
167 | Katakhali 50 MW Peaking PP | [17 empty] | 48 |  | 50 | 10 | [5 empty] | 83827
168 | Santahar 50 MW Peaking PP | [17 empty] | 24 |  | 32 | 32 | 38 |  |  |  |  | 68717
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | 8 |  |  |  |  | 0 | 13786
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 51 |  | 51 | 51 | 51 | 51 | 16 | 0 |  | 217120
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 15 |  | 35 | [5 empty] | 0 | 67968
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 50 |  | 50 | [5 empty] | 0 | 86688
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | [17 empty] | 9 | [7 empty] | 0 | 10000
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 11 | 54 |  | 56 | 52 | 35 | 35 | 0 |  | 0 | 194496
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 6 | 6 | 6 | 4 | 3 | 2 | [9 empty] | 42846
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 17 |  | 54 | 72 | 35 | 35 | 0 |  | 0 | 156096
| Intraco Solar 30 MW | [6 empty] | 1 | 10 | 20 | 26 | 31 | 36 | 29 | 25 | 25 | 15 | 3 | 0 | [8 empty] | 232942
| Adani Power Jharkhanda Ltd | 923 | 818 | 817 | 821 | 815 | 824 | 905 | 1020 | 1116 | 1015 | 1056 | 1111 | 1211 | 1217 | 1099 | 1016 | 1016 | 1065 |  | 1291 | 1308 | 1353 | 1356 | 1253 | 1160 | 1015 | 25337498
178 | Teesta Solar Limited | [6 empty] | 7 | 42 | 97 | 158 | 197 | 199 | 161 | 173 | 131 | 78 | 11 | [9 empty] | 1168250
179 | Western Zone Total | 3835 | 3432 | 3375 | 3343 | 3289 | 3300 | 3461 | 3812 | 4042 | 3892 | 4266 | 4473 | 4638 | 4556 | 4345 | 4222 | 4121 | 4489 |  | 4774 | 4843 | 4902 | 4929 | 4745 | 4757 | 4289 | 102531802
| System Total | 8090 | 7635 | 7432 | 7281 | 7133 | 7351 | 8017 | 8795 | 9147 | 8896 | 9402 | 9774 | 10155 | 10129 | 9777 | 9478 | 9451 | 10223 | 0 | 11132 | 10845 | 10756 | 10642 | 10244 | 9692 | 9211 | 224022979