## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-03-09 | Saturday
|  | Date (day): | 2024-03-09 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12204.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12694 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-03-08 | 2024-03-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 375 | 420 | 412 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 17 | 17 | 83 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 155 | 155 | 155 | 180 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 70 | 96 | 96 |  | 6 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 24 | 24 | 24 | 51 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 133 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 31 | 39 | 39 |  | 41 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 21 | 28 | 28 |  | 5 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 17 | 17 | 35 | 114 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 34 | 100 |  |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 17 | 35 | 127 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 1421 | 2141 | 2076 | 2386 | 1683 | 1002
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 6 | 20 | 30 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 207 | 206 | 220 | 220
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 24 | 40 | 64 | 34 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 10 | 25 | 25 | 75 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 20 | 35 | 10 | 20
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 80 | 65 | 135 | 165 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 15 | 15 | 95 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 17 | 25 | 25 | 75 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 108 | 53 | 127 | 36 |  | Fuel shortage
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 293 | 278 | 300 | 300 | 924 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 30 | 34 | 40 | 40 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 575 | 456 | 364 | 364 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 71 | 0 | 25 | 0 |  |  | on test
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1261 | 1394 | 1371 | 1539 | 2280 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 146 | 101 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Under S/D
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 275 | 310 | 310 | 50 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 330 | 335 | 300 | 300 | 100 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 47 | 47 | 47 | 47
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 52 | 32 | 50 | 5
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 83 | 0 | 0 | 195 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 5 | 6 | 6 | 144 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 20 | 0 | 50 |  | 2 | Engine problem
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 33 | 40 | 34 | 34 | 166 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 9 | 9 | 9
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 118 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 17 | 17 | 17 | 17 |  | 16 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 18 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 70 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 55 | 57 | 28 | 78 | 35 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 36 | 0 | 36 | 79 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1208 | 1359 | 1343 | 1510 | 1178 | 248
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 34 | 42 | 35 | 48 | 154 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 59 | 65 | 59 | 68 | 132 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 9 | 9 | 9 | 9 | 106 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 156 | 122 | 154.6 | 131 | 154 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 30 | 30 |  | 60 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 63 | 65 | 65
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 122 | 132 | 132 |  | 99
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 17 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 305 | 290 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 320 | 369 | 365 | 365 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 170 | 190 | 200 | 200 |  |  | ST Under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1210 | 1310 | 1314 | 1324 | 28 | 517
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 635 | 945 | 656
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 10 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 35 | 94 | 11 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 441 | 530 | 500 | 500
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1452 | 1175 | 1580 | 1370 | 1263 | 39
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 0 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 4 | 6 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 80 | 135 | 135 |  | 59 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 810 | 700 | 1200 | 1200
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1164 | 1006 | 1689 | 1707 | 422 | 92
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 25 | 25 | 27 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 21 |  | 50 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28 |  |  | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 161 | 189 | 200 | 200 | 20 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 409 | 380 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 16 | 38 | 12 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 8 | 8 |  | 3 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 0 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 35 | 55 | 58 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 917 | 1097 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1497 | 1671 | 2264 | 2406 | 848 | 75
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Coal Shortage.
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 42 | 33 | 40 | 40 | 73 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 113 | 35 | 111 |  |  | Fuel shortage
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 182 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 434 | 316 | 413 | 321 | 198 | 189
| Total |  |  |  |  | 26504 | 25481 | 9803 | 10494 | 12204.6 | 12694 | 8054 | 2492
A. |  | 2024-03-08 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10494 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8246 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10535 | MW
3 | Day peak Generation : |  |  | 9803 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10200.6 | MW
4 | Evening peak Generation : |  |  | 10494 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 39 | MW
5 | Total Energy Generation : |  | 226.7483 | MKWHr | By Solar | 3.5672 | MKWHr
| By Gas : | 114.2576 | MKWHr |  | By Oil: | 7.5384 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 77.8199 | MKWHr |  | By Hydro: | 0.77166 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.74016 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8054 | MW | Dhaka | 3490 | 3490 |  | 0 |  | 18:00 |  | 47
|  |  | For Plants S/D or M/C prob = |  |  | 2492 | MW | Chittagong | 1031 | 1031 |  | 0 |  | 19:00 |  | 39
|  |  | Total = |  |  | 10546 | MW | Khulna | 1224.3 | 1224.3 |  | 0 |  | 19:30 |  | 32
7 | Total Gas Supplied : |  |  | 876.88 | MMCFD |  |  | Rajshahi | 1147 | 1147 |  | 0 |  | 20:00 |  | 24
8 | Fuel Cost : | i) Gas : | Taka | 348662842.244 | ii) Oil : | Taka | 138935211.62 | Comilla | 907 | 907 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 521539777.52 | Total | Taka | 1009137831.384 | Mymensingh | 968 | 929 |  | 39 |  | 22:00 |  | 41.065
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 363 | 363 |  | 0 |  | 23:00 |  | 21.965
| ii) During Peak Demand : |  |  | 650 | MW (W to E) at | 19:00 | hrs | Barisal | 285.3 | 285.3 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 640 | MW at | 9:00 | hrs | Rangpur | 785 | 785 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31°C |  |  | Total | 10200.6 | 10161.6 |  | 39
B. |  | 2024-03-09 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12694 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10100 | MW
4 | Reserve(Generation end) |  |  |  | 1094 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 250.6462 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7865 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.5171 | MKWHr. | ii) HVDC Flow at Peak Time |  | 635 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5363 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.89 |  | (b) Today: | 82.76 |  | (c) Rule Curve: |  | 91.72
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-03-08 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 380 | 156 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 33 | 20 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 0 | 0 | 280 | 227 | 8 | 0 | 47 | 20 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 17 | 17 | 100 | 73 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 130 | 0 | 61 | 0 | 0 | 25 | 0 | 0 | 10 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 34 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 275 | 32 | 500 | 0 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 613 | 0 | 0 | 967 | 0 | 0 |  | 4841 | 4380 | 9221 | 3026 | 918 | 1609 | 0 | 76 | 3425 | 35 | 0 | 0 | 100 | 0 | 32 | 0 | 82.94
2:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 380 | 156 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 33 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 0 | 0 | 270 | 191 | 8 | 0 | 47 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 17 | 15 | 106 | 73 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 130 | 0 | 61 | 0 | 0 | 120 | 0 | 0 | 0 | 295 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 34 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 275 | 39 | 500 | 0 | 0 | 0 |  | 758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 566 | 0 | 0 | 927 | 0 | 0 |  | 4900 | 4040 | 8940 | 3086 | 758 | 1566 | 0 | 72 | 3278 | 35 | 0 | 0 | 106 | 0 | 39 | 0 | 82.93
3:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 380 | 158 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 33 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 0 | 0 | 270 | 193 | 8 | 0 | 47 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 17 | 15 | 104 | 73 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 130 | 0 | 61 | 0 | 0 | 120 | 0 | 0 | 0 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 17 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 275 | 41 | 450 | 0 | 0 | 0 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 538 | 0 | 0 | 927 | 0 | 0 |  | 4758 | 3872 | 8630 | 3038 | 729 | 1532 | 0 | 31 | 3120 | 35 | 0 | 0 | 104 | 0 | 41 | 0 | 82.92
4:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 380 | 158 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41 | 0 | 0 | 0 | 0 | 280 | 202 | 8 | 0 | 47 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 100 | 73 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 282 | 35 | 400 | 0 | 0 | 0 |  | 729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 529 | 0 | 0 | 828 | 0 | 0 |  | 4680 | 3662 | 8342 | 3043 | 729 | 1551 | 0 | 0 | 2849 | 35 | 0 | 0 | 100 | 0 | 35 | 0 | 82.91
5:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 330 | 0 |  | 0 | 340 | 156 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41 | 0 | 0 | 0 | 0 | 270 | 196 | 8 | 0 | 47 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 98 | 73 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 295 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 282 | 45 | 403 | 0 | 0 | 0 |  | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 0 | 824 | 0 | 0 |  | 4611 | 3635 | 8246 | 3000 | 728 | 1512 | 0 | 0 | 2828 | 35 | 0 | 0 | 98 | 0 | 45 | 0 | 82.9
6:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 344 | 0 |  | 0 | 340 | 157 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 21 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 330 | 72 | 8 | 0 | 47 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 94 | 73 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 282 | 36 | 403 | 0 | 0 | 0 |  | 728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514 | 0 | 0 | 827 | 0 | 0 |  | 4611 | 3695 | 8306 | 2996 | 728 | 1581 | 0 | 0 | 2836 | 35 | 0 | 0 | 94 | 0 | 36 | 0 | 82.89
7:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 400 | 157 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 30 | 21 | 2 | 0 | 35 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42 | 0 | 0 | 0 | 0 | 320 | 150 | 8 | 0 | 45 | 5 | 0 | 9 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 96 | 69 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 2 | 3 | 0 | 0 | 0 | 385 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 70 | 0 | 0 | 205 | 0 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 365 | 0 | 0 | 280 | 37 | 472 | 0 | 0 | 6 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 650 | 180 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 510 | 2 | 0 | 829 | 15 | 0 |  | 5148 | 3651 | 8799 | 3233 | 635 | 1693 | 0 | 102 | 2911 | 35 | 0 | 16 | 96 | 41 | 37 | 25 | 82.88
8:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 428 | 0 |  | 0 | 400 | 155 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 20 | 0 | 20 | 8 | 0 | 35 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 275 | 151 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 98 | 70 | 0 | 0 | 1 | 42 | 30 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 8 | 0 | 0 | 0 | 365 | 9 | 4 | 0 | 2 | 0 | 0 | 0 | 70 | 23 | 0 | 200 | 12 | 20 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 285 | 0 | 0 | 288 | 30 | 575 | 0 | 0 | 25 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 760 | 180 | 0 | 0 | 2 | 30 | 0 | 0 | 0 | 510 | 11 | 0 | 838 | 64 | 0 |  | 5280 | 3840 | 9120 | 3107 | 635 | 1683 | 0 | 199 | 3141 | 35 | 0 | 16 | 98 | 176 | 30 | 24 | 82.87
9:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 427 | 0 |  | 0 | 400 | 147 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 21 | 25 | 20 | 8 | 0 | 40 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 280 | 151 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 94 | 34 | 0 | 0 | 2 | 42 | 30 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 13 | 0 | 0 | 0 | 342 | 9 | 17 | 0 | 3 | 0 | 0 | 0 | 70 | 27 | 0 | 190 | 0 | 35 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 285 | 0 | 0 | 287 | 34 | 575 | 0 | 0 | 43 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 760 | 180 | 0 | 0 | 3 | 53 | 0 | 0 | 0 | 513 | 21 | 0 | 862 | 113 | 0 |  | 5219 | 3865 | 9084 | 3065 | 635 | 1518 | 0 | 204 | 3167 | 40 | 0 | 16 | 94 | 311 | 34 | 39.155 | 82.86
10:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 395 | 0 |  | 0 | 350 | 152 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 25 | 20 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 275 | 149 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 104 | 34 | 0 | 0 | 2 | 42 | 30 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 0 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 18 | 0 | 0 | 0 | 318 | 9 | 17 | 0 | 4 | 0 | 0 | 0 | 70 | 31 | 0 | 170 | 0 | 46 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 285 | 0 | 0 | 288 | 27 | 524 | 0 | 0 | 61 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 320 | 0 | 0 | 0 | 0 | 35 | 0 | 5 | 0 | 770 | 180 | 0 | 0 | 4 | 72 | 0 | 0 | 0 | 484 | 28 | 0 | 865 | 151 | 0 |  | 5060 | 3961 | 9021 | 2931 | 635 | 1514 | 0 | 243 | 3101 | 30 | 0 | 16 | 104 | 420 | 27 | 28 | 82.86
11:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 389 | 0 |  | 0 | 320 | 152 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 20 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 275 | 120 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 10 | 17 | 15 | 108 | 34 | 0 | 0 | 2 | 42 | 30 | 0 | 0 | 120 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 0 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 20 | 0 | 10 | 0 | 317 | 9 | 17 | 0 | 5 | 0 | 0 | 0 | 70 | 41 | 0 | 170 | 0 | 51 | 0 | 0 | 90 | 0 | 31 | 0 | 0 | 285 | 0 | 0 | 287 | 42 | 524 | 0 | 0 | 71 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 323 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 790 | 180 | 0 | 0 | 5 | 85 | 0 | 0 | 0 | 443 | 32 | 0 | 863 | 178 | 0 |  | 5090 | 4275 | 9365 | 2931 | 918 | 1487 | 0 | 270 | 3077 | 30 | 0 | 16 | 108 | 486 | 42 | 19 | 82.85
12:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 375 | 0 |  | 0 | 320 | 150 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 20 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 305 | 146 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 17 | 15 | 118 | 34 | 0 | 0 | 2 | 42 | 30 | 0 | 0 | 163 | 0 | 62 | 0 | 0 | 120 | 0 | 0 | 0 | 295 | 8 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 17 | 20 | 0 | 33 | 0 | 320 | 9 | 17 | 0 | 5 | 0 | 0 | 0 | 70 | 55 | 0 | 170 | 0 | 52 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 330 | 0 | 0 | 293 | 30 | 575 | 0 | 0 | 71 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 409 | 0 | 0 | 0 | 0 | 42 | 0 | 6 | 0 | 810 | 220 | 0 | 0 | 5 | 92 | 0 | 0 | 0 | 441 | 34 | 0 | 917 | 182 | 0 |  | 5256 | 4547 | 9803 | 3026 | 919 | 1645 | 0 | 310 | 3206 | 30 | 0 | 16 | 118 | 503 | 30 | 0 | 82.85
13:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 145 | 0 | 0 | 2 | 328 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 20 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28 | 0 | 0 | 0 | 0 | 300 | 147 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 17 | 17 | 124 | 34 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 0 | 0 | 120 | 0 | 0 | 10 | 300 | 8 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 17 | 0 | 0 | 30 | 0 | 366 | 9 | 17 | 0 | 5 | 0 | 0 | 0 | 114 | 42 | 0 | 190 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 330 | 0 | 0 | 289 | 20 | 575 | 0 | 0 | 68 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 375 | 0 | 0 | 0 | 0 | 42 | 0 | 7 | 0 | 880 | 220 | 0 | 0 | 3 | 89 | 0 | 0 | 0 | 439 | 34 | 0 | 968 | 179 | 0 |  | 5598 | 4657 | 10255 | 3242 | 920 | 1760 | 0 | 352 | 3321 | 30 | 0 | 48 | 124 | 438 | 20 | 43 | 82.84
14:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 376 | 0 |  | 0 | 400 | 133 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 33 | 21 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26 | 0 | 0 | 0 | 0 | 270 | 120 | 8 | 0 | 46 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 17 | 17 | 112 | 34 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 10 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 18 | 0 | 32 | 0 | 314 | 9 | 17 | 0 | 4 | 0 | 0 | 0 | 114 | 37 | 0 | 180 | 4 | 49 | 0 | 0 | 0 | 15 | 30 | 18 | 0 | 285 | 0 | 0 | 290 | 15 | 455 | 0 | 0 | 63 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 720 | 180 | 0 | 0 | 5 | 82 | 36 | 0 | 0 | 409 | 33 | 0 | 821 | 161 | 0 |  | 5114 | 4011 | 9125 | 2842 | 919 | 1477 | 0 | 380 | 2865 | 30 | 0 | 32 | 112 | 453 | 15 | 0 | 82.85
15:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 364 | 0 |  | 0 | 400 | 131 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 33 | 21 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26 | 0 | 0 | 0 | 0 | 290 | 32 | 26 | 0 | 45 | 10 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 17 | 17 | 94 | 34 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 163 | 0 | 61 | 0 | 0 | 120 | 0 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 14 | 0 | 33 | 0 | 316 | 9 | 17 | 0 | 3 | 0 | 0 | 0 | 70 | 37 | 0 | 180 | 0 | 37 | 0 | 0 | 30 | 17 | 23 | 18 | 0 | 285 | 0 | 0 | 288 | 30 | 455 | 0 | 0 | 48 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 700 | 180 | 0 | 0 | 4 | 65 | 0 | 0 | 0 | 405 | 23 | 0 | 825 | 141 | 0 |  | 5046 | 3935 | 8981 | 2849 | 920 | 1551 | 0 | 299 | 2843 | 30 | 0 | 0 | 94 | 365 | 30 | 0 | 82.83
16:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 364 | 0 |  | 0 | 400 | 134 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 33 | 21 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 0 | 0 | 0 | 0 | 305 | 42 | 26 | 0 | 46 | 45 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 17 | 17 | 90 | 40 | 0 | 0 | 1 | 43 | 30 | 0 | 0 | 163 | 0 | 51 | 0 | 0 | 120 | 0 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 9 | 0 | 32 | 0 | 319 | 9 | 17 | 0 | 2 | 0 | 0 | 0 | 52 | 37 | 0 | 180 | 0 | 24 | 0 | 0 | 0 | 17 | 10 | 23 | 0 | 285 | 0 | 0 | 287 | 39 | 454 | 0 | 0 | 28 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 690 | 180 | 0 | 0 | 3 | 39 | 0 | 0 | 0 | 406 | 17 | 0 | 827 | 92 | 0 |  | 5009 | 3852 | 8861 | 2852 | 919 | 1583 | 0 | 285 | 2834 | 30 | 0 | 0 | 90 | 229 | 39 | 0 | 82.83
17:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 333 | 0 |  | 0 | 350 | 133 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 10 | 33 | 21 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32 | 0 | 0 | 0 | 0 | 270 | 49 | 26 | 0 | 46 | 47 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 17 | 17 | 98 | 30 | 0 | 0 | 0 | 43 | 29 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 120 | 0 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 17 | 3 | 0 | 38 | 0 | 322 | 5 | 17 | 0 | 1 | 3 | 0 | 0 | 34 | 31 | 0 | 200 | 0 | 7 | 0 | 0 | 0 | 17 | 4 | 42 | 7 | 290 | 17 | 0 | 285 | 29 | 455 | 0 | 0 | 11 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 180 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 405 | 6 | 0 | 827 | 35 | 0 |  | 4810 | 3649 | 8459 | 2803 | 919 | 1483 | 0 | 253 | 2742 | 30 | 0 | 17 | 98 | 85 | 29 | 0 | 82.82
18:00 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 321 | 0 |  | 0 | 350 | 134 | 1 | 6 | 15 | 280 | 0 | 0 | 4 | 0 | 70 | 13 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 10 | 33 | 7 | 17 | 0 | 30 | 0 | 0 | 0 | 1 | 206 | 0 | 0 | 0 |  | 4 | 16 | 17 | 0 | 0 | 6 | 10 | 35 | 0 | 0 | 0 | 0 | 270 | 56 | 83 | 0 | 47 | 52 | 0 | 51 | 0 | 0 | 1 | 0 | 9 | 17 | 17 | 122 | 52 | 0 | 0 | 0 | 43 | 29 | 0 | 0 | 163 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 0 | 40 | 2 | 315 | 9 | 105 | 3 | 0 | 70 | 7 | 1 | 70 | 45 | 9 | 200 | 1 | 0 | 0 | 5 | 70 | 17 | 0 | 40 | 17 | 285 | 17 | 0 | 280 | 31 | 455 | 0 | 0 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 260 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 600 | 180 | 0 | 0 | 0 | 1 | 60 | 0 | 0 | 440 | 0 | 0 | 835 | 0 | 0 |  | 5466 | 3760 | 9226 | 2880 | 920 | 1624 | 0 | 718 | 2780 | 30 | 0 | 120 | 122 | 1 | 31 | 47 | 82.82
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 420 | 0 |  | 0 | 420 | 155 | 8 | 70 | 15 | 335 | 0 | 0 | 9 | 8 | 133 | 24 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 16 | 15 | 33 | 21 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 |  | 6 | 24 | 17 | 0 | 0 | 6 | 10 | 35 | 0 | 0 | 0 | 0 | 275 | 101 | 83 | 0 | 47 | 52 | 0 | 51 | 0 | 20 | 8 | 0 | 9 | 17 | 18 | 118 | 42 | 0 | 0 | 0 | 42 | 29 | 0 | 0 | 163 | 0 | 63 | 0 | 0 | 122 | 0 | 0 | 10 | 305 | 17 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 10 | 40 | 5 | 369 | 9 | 105 | 17 | 0 | 80 | 17 | 15 | 70 | 57 | 17 | 190 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 335 | 108 | 0 | 278 | 34 | 456 | 0 | 0 | 0 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 700 | 220 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 530 | 0 | 0 | 1097 | 0 | 0 |  | 6326 | 4168 | 10494 | 3206 | 635 | 1880 | 0 | 1048 | 3231 | 30 | 0 | 312 | 118 | 0 | 34 | 39 | 82.8
19:30 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 416 | 0 |  | 0 | 420 | 154 | 0 | 17 | 15 | 335 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 16 | 15 | 33 | 21 | 17 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 6 | 10 | 35 | 0 | 0 | 0 | 0 | 290 | 127 | 83 | 0 | 47 | 52 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 17 | 18 | 116 | 50 | 0 | 0 | 0 | 42 | 29 | 0 | 0 | 163 | 0 | 63 | 0 | 0 | 130 | 0 | 0 | 10 | 315 | 17 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 12 | 40 | 6 | 381 | 9 | 0 | 0 | 0 | 15 | 0 | 10 | 7 | 26 | 25 | 204 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 36 | 17 | 355 | 17 | 0 | 279 | 30 | 510 | 0 | 0 | 0 |  | 634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 380 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 546 | 0 | 0 | 1120 | 0 | 0 |  | 5902 | 4344 | 10246 | 3319 | 634 | 1889 | 0 | 526 | 3525 | 30 | 0 | 177 | 116 | 0 | 30 | 32 | 0
20:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 418 | 0 |  | 0 | 420 | 154 | 0 | 22 | 15 | 335 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 15 | 33 | 21 | 17 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 6 | 10 | 27 | 0 | 0 | 0 | 0 | 270 | 225 | 36 | 0 | 47 | 53 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 17 | 18 | 112 | 50 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 64 | 0 | 0 | 130 | 0 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 12 | 38 | 4 | 365 | 9 | 0 | 0 | 0 | 15 | 0 | 0 | 31 | 40 | 25 | 180 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 36 | 17 | 295 | 17 | 0 | 277 | 26 | 575 | 0 | 0 | 0 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 380 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 980 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 551 | 0 | 0 | 1207 | 0 | 0 |  | 5838 | 4527 | 10365 | 3307 | 635 | 1810 | 0 | 504 | 3760 | 30 | 0 | 181 | 112 | 0 | 26 | 24 | 82.81
21:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 419 | 0 |  | 0 | 420 | 153 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 21 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 6 | 10 | 32 | 0 | 0 | 0 | 0 | 270 | 225 | 0 | 0 | 47 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 17 | 19 | 114 | 67 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 64 | 0 | 0 | 130 | 0 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 0 | 43 | 0 | 365 | 9 | 0 | 0 | 0 | 15 | 0 | 0 | 52 | 26 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 21 | 0 | 285 | 17 | 0 | 277 | 24 | 576 | 0 | 0 | 0 |  | 634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 380 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1090 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 548 | 0 | 0 | 1206 | 0 | 0 |  | 5654 | 4594 | 10248 | 3316 | 634 | 1766 | 0 | 326 | 3867 | 30 | 0 | 171 | 114 | 0 | 24 | 0 | 82.8
22:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 422 | 0 |  | 0 | 420 | 153 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 21 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 10 | 36 | 0 | 0 | 0 | 0 | 270 | 225 | 0 | 0 | 47 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 17 | 19 | 114 | 67 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 64 | 0 | 0 | 130 | 0 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 38 | 0 | 365 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 28 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 18 | 0 | 260 | 0 | 0 | 277 | 25 | 505 | 0 | 0 | 0 |  | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 340 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 960 | 200 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 548 | 0 | 0 | 1120 | 0 | 0 |  | 5359 | 4578 | 9937 | 3294 | 897 | 1705 | 0 | 239 | 3580 | 30 | 0 | 53 | 114 | 0 | 25 | 41.065 | 82.8
23:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 425 | 0 |  | 0 | 420 | 154 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 14 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 0 | 0 | 270 | 226 | 0 | 0 | 47 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 17 | 19 | 108 | 82 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 130 | 0 | 0 | 10 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 48 | 0 | 365 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 26 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 240 | 0 | 0 | 277 | 13 | 505 | 0 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 1112 | 0 | 0 |  | 5285 | 4307 | 9592 | 3284 | 919 | 1699 | 0 | 192 | 3324 | 30 | 0 | 23 | 108 | 0 | 13 | 21.965 | 82.79
24:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 427 | 0 |  | 0 | 420 | 154 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 21 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 0 | 0 | 270 | 227 | 0 | 0 | 44 | 10 | 0 | 43 | 0 | 0 | 8 | 0 | 9 | 17 | 19 | 108 | 68 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 64 | 0 | 0 | 130 | 0 | 0 | 10 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 46 | 0 | 365 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 9 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 277 | 26 | 401 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 1003 | 0 | 0 |  | 5085 | 4043 | 9128 | 3207 | 923 | 1670 | 0 | 138 | 3018 | 30 | 0 | 8 | 108 | 0 | 26 | 0 | 82.79
KWH | 0 | 0 | 4002625 | 0 | 0 | 0 | 0 | 9259200 | 0 |  | 0 | 9348000 | 3606400 | 10560 | 89847 | 112943 | 7293721 | 0 | 0 | 7680 | 10080 | 710400 | 36744 | 0 | 0 | 0 | 28080 | 40718 | 39097 | 0 | 387000 | 366480 | 768552 | 476900 | 143040 | 0 | 771660 | 0 | 0 | 0 | 19243 | 4984818 | 0 | 0 | 0 |  | 41760 | 39975 | 51254 | 0 | 0 | 28800 | 231600 | 822240 | 0 | 0 | 0 | 0 | 6904000 | 3652000 | 384728 | 0 | 1106712 | 472800 | 0 | 977228 | 0 | 9664 | 78763 | 0 | 219060 | 410600 | 409470 | 2536320 | 1221120 | 0 | 0 | 16050 | 1004000 | 702600 | 54600 | 0 | 3654491 | 0 | 1195872 | 0 | 0 | 2778430 | 0 | 0 | 135000 | 7210500 | 345888 | 0 | 0 | 0 | 0 | 0 | 854400 | 0 | 347184 | 134595 | 38400 | 625920 | 13381 | 8099000 | 158400 | 336000 | 29272 | 33121 | 178145 | 29268 | 27600 | 1194720 | 608160 | 80640 | 4789900 | 78720 | 373220 | 41760 | 47673 | 187164 | 199800 | 214485 | 274560 | 68040 | 7086300 | 160582 | 0 | 6779999 | 740160 | 11949090 | 0 | 0 | 501190 |  | 19517090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17024 | 0 | 1969000 | 136164 | 0 | 0 | 0 | 0 | 0 | 21671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123462 | 0 | 0 | 4118500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4325018 | 0 | 8246545 | 0 | 0 | 0 | 0 | 279888 | 0 | 46322 | 0 | 20568700 | 4908409 | 0 | 0 | 40920 | 633600 | 328512 | 0 | 0 | 12072730 | 244718 | 0 | 22330909 | 1329000 | 0 |  | 125490162 | 101258182 | 226748344 | 74300492 | 19517090 | 39957105 | 0 | 6527798 | 77819928 | 771660 | 0 | 1010570 | 2536320 | 3567221 | 740160 | 0
Fuel Cost | 0 | 0 | 17171261.25 | 0 | 0 | 0 | 0 | 26666496 | 0 |  | 0 | 29726640 | 12333888 | 208665.6 | 1680138.9 | 1990055.66 | 22245849.05 | 0 | 0 | 151756.8 | 180936 | 13795968 | 685275.6 | 0 | 0 | 0 | 512740.8 | 641715.68 | 715084.13 | 0 | 290250 | 0 | 0 | 0 | 2561846.4 | 0 | 0 | 0 | 0 | 0 | 364462.42 | 15901569.42 | 0 | 0 | 0 |  | 734558.4 | 703959.75 | 917959.14 | 0 | 0 | 474048 | 861552 | 0 | 0 | 0 | 0 | 0 | 21126240 | 12124640 | 1288838.8 | 0 | 3729619.44 | 2070864 | 0 | 3918684.28 | 0 | 173082.24 | 1422459.78 | 0 | 164295 | 1527432 | 307102.5 | 16638259.2 | 3797683.2 | 0 | 0 | 0 | 3915600 | 2620698 | 248430 | 0 | 12498359.22 | 0 | 6637089.6 | 0 | 0 | 7751819.7 | 0 | 0 | 540000 | 22280445 | 259416 | 0 | 0 | 0 | 0 | 0 | 16413024 | 0 | 6113910.24 | 0 | 683904 | 10859712 | 221856.98 | 21462350 | 3019104 | 6303360 | 525139.68 | 0 | 2912670.75 | 568969.92 | 495144 | 22831099.2 | 11804385.6 | 1436198.4 | 12741134 | 1343750.4 | 0 | 763790.4 | 799952.94 | 699993.36 | 3570426 | 0 | 4947571.2 | 1152597.6 | 21046311 | 2260994.56 | 0 | 47256593.03 | 0 | 70499631 | 0 | 0 | 0 |  | 54843022.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320221.44 | 0 | 6222040 | 645417.36 | 0 | 0 | 0 | 0 | 0 | 397662.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93460.734 | 0 | 0 | 34760140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14402309.94 | 0 | 24079911.4 | 0 | 0 | 0 | 0 | 5575368.96 | 0 | 0 | 0 | 133285176 | 15265151.99 | 0 | 0 | 0 | 0 | 5699683.2 | 0 | 0 | 88130929 | 0 | 0 | 147607308.49 | 0 | 0 |  | 549291309.22 | 531327804.264 | 1080619113.484 | 223766212.194 | 54843022.9 | 124896630.05 | 0 | 120365363.64 | 521539777.52 | 0 | 0 | 18569847.98 | 16638259.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 375 | 0 |  | 0 | 320 | 150 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 33 | 20 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 0 | 305 | 146 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 8 | 17 | 15 | 118 | 34 | 0 | 0 | 2 | 42 | 30 | 0 | 0 | 163 | 0 | 62 | 0 | 0 | 120 | 0 | 0 | 0 | 295 | 8 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 17 | 20 | 0 | 33 | 0 | 320 | 9 | 17 | 0 | 5 | 0 | 0 | 0 | 70 | 55 | 0 | 170 | 0 | 52 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 330 | 0 | 0 | 293 | 30 | 575 | 0 | 0 | 71 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 409 | 0 | 0 | 0 | 0 | 42 | 0 | 6 | 0 | 810 | 220 | 0 | 0 | 5 | 92 | 0 | 0 | 0 | 441 | 34 | 0 | 917 | 182 | 0 |  | 9803 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 420 | 0 |  | 0 | 420 | 155 | 8 | 70 | 15 | 335 | 0 | 0 | 9 | 8 | 133 | 24 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 16 | 15 | 33 | 21 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 | 0 | 6 | 24 | 17 | 0 | 0 | 6 | 10 | 35 | 0 | 0 | 0 | 0 | 275 | 101 | 83 | 0 | 47 | 52 | 0 | 51 | 0 | 20 | 8 | 0 | 9 | 17 | 18 | 118 | 42 | 0 | 0 | 0 | 42 | 29 | 0 | 0 | 163 | 0 | 63 | 0 | 0 | 122 | 0 | 0 | 10 | 305 | 17 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 17 | 0 | 10 | 40 | 5 | 369 | 9 | 105 | 17 | 0 | 80 | 17 | 15 | 70 | 57 | 17 | 190 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 335 | 108 | 0 | 278 | 34 | 456 | 0 | 0 | 0 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 380 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 700 | 220 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 530 | 0 | 0 | 1097 | 0 | 0 |  | 10494 | EvPeak
Forecast for Evening | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 155 | 17 | 96 | 30 | 335 | 0 | 0 | 8 | 8 | 149 | 24 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 18 | 21 | 33 | 28 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 64 | 51 | 25 | 0 | 20 | 10 | 20 | 0 | 0 | 0 | 0 | 310 | 225 | 0 | 0 | 47 | 50 | 0 | 51 | 0 | 50 | 8 | 0 | 9 | 17 | 17 | 141 | 48 | 0 | 0 | 0 | 42 | 30 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 132 | 0 | 0 | 10 | 300 | 17 | 0 | 0 | 130 | 0 | 0 | 68 | 0 | 35 | 0 | 25 | 34 | 6 | 365 | 9 | 100 | 17 | 0 | 135 | 17 | 15 | 114 | 78 | 25 | 200 | 17 | 0 | 35 | 17 | 0 | 17 | 0 | 36 | 17 | 300 | 127 | 0 | 300 | 40 | 364 | 0 | 0 |  |  | 656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 0 | 135 | 7 | 110 | 0 | 0 | 0 | 25 | 21 | 90 | 28 | 42 | 50 | 0 | 38 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 94 | 0 | 35 | 0 | 40 | 0 | 0 | 55 | 1200 | 220 | 0 | 35 | 0 | 0 | 111 | 0 | 0 | 500 | 0 | 0 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 450 | 155 | 17 | 96 | 15 | 335 | 0 | 0 | 8 | 8 | 48 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 33 | 28 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 0 | 40 | 51 | 25 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 0 | 310 | 225 | 0 | 0 | 47 | 32 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 17 | 17 | 128 | 35 | 0 | 0 | 1.6 | 42 | 30 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 132 | 0 | 0 | 10 | 290 | 17 | 0 | 0 | 80 | 0 | 0 | 59 | 0 | 17 | 20 | 25 | 34 | 6 | 365 | 9 | 34 | 17 | 5 | 65 | 0 | 15 | 114 | 28 | 25 | 200 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 0 | 0 | 300 | 53 | 0 | 300 | 40 | 364 | 0 | 0 | 25 |  | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 7 | 110 | 0 | 0 | 0 | 25 | 0 | 50 | 28 | 42 | 40 | 0 | 16 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 35 | 0 | 0 | 0 | 40 | 0 | 8 | 35 | 1200 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 500 | 30 | 0 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 422 | 0 | 0 | 0 | 320 | 154 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 20 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 6 | 10 | 20 | 0 | 0 | 0 | 0 | 290 | 229 | 0 | 0 | 47 | 32 | 0 | 51 | 0 | 0 | 0 | 0 | 9 | 17 | 17 | 94 | 65 | 0 | 0 | 1 | 42 | 30 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 132 | 0 | 0 | 10 | 270 | 17 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 9 | 12 | 34 | 5 | 365 | 9 | 0 | 9 | 2 | 16 | 0 | 0 | 70 | 9 | 25 | 185 | 13 | 21 | 0 | 17 | 0 | 0 | 13 | 0 | 0 | 285 | 53 | 0 | 283 | 30 | 363 | 0 | 0 | 29 | 0 | 642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 4 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 860 | 180 | 0 | 0 | 2 | 33 | 118 | 0 | 0 | 406 | 13 | 0 | 1014 | 76 | 0 | 0 |  |  |  | 114257597 | 19517090 | 0 | 77819928 | 7538368 | 2536320 | 3567221 | 740160 | 771660 |  |  | 226748344
[8 empty] | 299430 | [13 empty] | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [12 empty] | 599468 |  |  |  | 230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 114.2576 | 19.5171 | 0 | 77.8199 | 7.5384 | 2.5363 | 3.5672 | 0.74016 | 0.77166
| Minimum Generation |  | 8246 | 5:00
| Highest Generation |  | 10494 | 19:00 | [129 empty] | 0 | [71 empty] | 226.7483
| Day Peak Generation |  | 9803 | 12:00
| Evening Peak Generation |  | 10494 | 19:00 | [201 empty] | 202699852
| HVDC Max Flow |  | 923 | 24:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 635 | 19:00
| Load factor L.F |  | 90.03% | [167 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-03-09
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-03-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9803 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 7865
Evening Peak Generation : |  |  | 10494 | MW Hour : | 19:00 | Available Max Generation : |  | 12694
E.P. Demand (at gen end) : |  |  | 10535 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11600
Maximum Generation : |  |  | 10494 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1094
Total Gen. (MKWH) : |  |  | 226.7483 | System Load Factor : | 90.03% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 640 | MW at | 9:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-03-09
Actual : |  | 82.76 | Ft.(MSL) , | Rule curve : | 91.72 | Ft.( MSL )
Gas Consumed : |  | Total = | 876.88 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 348662842.244
: |  |  | Coal : | 521539777.52 | Oil : | 138935211.62 | Total : | 1009137831.384
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4049.3685 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1109.504 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1553.2499 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1349.182 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1110.5832 |  |  | 0 | 0%
Mymensingh Area |  | 39 | 936:00 | 825.5327 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 463.2298 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 385.5962 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 754.1689 |  |  | 0 | 0%
Total |  | 39 |  | 11600.4152 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj North
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:26 | 11:34 | Jhenaidah-Khulna 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end Due to Insulator disk cleaning and from
Khulna(S) 230/132kV end Due to jhenaidah S/S Work.
8:35 | 15:51 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Madanganj 132/33kV end. and from Haripur 230/132kV end Due to
From Other End.
8:41 | 19:41 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to By NLDC.
8:43 | 19:42 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end.
8:51 | 14:50 | Kabirpur - Manikganj 132kV Ckt-2 Project Work S/D from Manikganj 132/33kV end Due to Ruppur project.
9:23 | 10:19 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Hotspot maintenance.
9:46 | - | Khulna (S)-Rampal Ckt-1 Project Work S/D from Khulna(S) 230/132kV end. and from Rampal 400/230kV end Due to ALDC
project work at Khulna end.
10:10 | 19:01 | Faridpur 132/33kV S/S 132 KV 50MW Power Station ckt-1 Scheduled S/D Due to Power station inner side maintenance.
10:22 | - | Shahjibazar 100 MW GTPP Syncronized.
- | 10:34 | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 is restored.
- | 10:34 | Niamatpur 132/33kV S/S Main Bus is restored.
- | 10:35 | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 is restored.
- | 11:11 | Kushtia 132/33kV S/S T-1 HT is restored.
- | 11:12 | Kushtia 132/33kV S/S T-1 LT is restored.
11:45 | - | Shahjibazar 100 MW GTPP Shutdown.
- | 11:45 | Tongi 230/132/33kV S/S T-02 HT is restored.
- | 11:47 | Tongi 230/132/33kV S/S T-02 LT is restored.
11:54 | 14:33 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Annual maintenance.
11:54 | 14:33 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Annual maintenance.
- | 11:58 | Ghorasal-Joydeb-B 132kV Ckt-1 is restored.
12:00 | - | Day Peak Generation: 9803 MW.
12:02 | 16:38 | Ghorasal-Joydeb-B 132kV Ckt-2 Project Work S/D from Joydebpur 132/33kV end Due to LILO of Joydebpur Ghorasal 132kV
four ckt line to Pubail 132kV Grid SS.
12:45 | 13:46 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to to control overload of 132 KV Haripur-2 ckt.
14:57 | - | Shahjibazar 100 MW GTPP Syncronized.
15:38 | - | Shahjibazar 100 MW GTPP Shutdown.
16:15 | - | About 410 MW interruption occurred under Mirzapur, Tangail, Sherpur, Jamalpur & Mymensingh T-3 from 16:15 hr to 16:25 hr as
Kaliakoir - Tangail & Kaliakoir - Mirzapur 132 kv lines tripped showing Dist. relay.
16:15 | 16:39 | Kaliakoir-Tangail 132kV Ckt-2 Tripped from Kaliakoir 400/230/132kV end showing REL 650 relays.
16:15 | 16:51 | Kaliakoir-Tangail 132kV Ckt-1 Tripped from Kaliakoir 400/230/132kV end showing REL 650 relays.
- | 17:22 | Dohazari-Sikalbaha 132 kV Ckt-1 is restored.
- | 17:40 | Maniknagar-Siddhirganj 230kV Ckt-1 is restored.
17:48 | - | Shahjibazar 100 MW GTPP Syncronized.
18:19 | - | Ashuganj CCPP 225 MW Syncronized with remarks:- ST.
18:39 | - | Shahjibazar 100 MW GTPP Shutdown.
- | 18:41 | Cumilla(N)-Kachua 132 kV Ckt-2 is restored.
- | 18:42 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
- | 18:42 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
- | 18:42 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
- | 18:48 | Ghorasal- Ishwardi 230 kV Ckt-1 is restored.
- | 18:49 | Ghorasal- Ishwardi 230 kV Ckt-2 is restored.
19:00 | - | Evening Peak Gen. 10494 MW
20:42 | 21:50 | Chowmuhani 132/33kV S/S TR2 Forced S/D Due to TR-2 33kv bus incoming DS R phase red hot maintenance. |  |  |  |  | 30.0MW load interrup.
4:00 | - | minimum generation 7865 MW.
6:13 | - | Bhandaria 132/33kV S/S Transformer-2 LT Project Work S/D Due to Energy pack project work. |  |  |  |  | 22.0MW load interrup.
6:14 | - | Bhandaria 132/33kV S/S Transformer-2 HT Project Work S/D Due to Sane as LT. |  |  |  |  | 22.0MW load interrup.
6:15 | - | Barishal-Bhandaria 132 kV Ckt-1 Project Work S/D from Bhandaria 132/33kV end Due to For 132 kv Main Bus S/D (Project work). |  |  |  |  | 22.0MW load interrup.
Bhandaria 132/33kV end.
6:17 | - | Bagerhat-Bhandaria 132 kV Ckt-1 Scheduled S/D from Bagerhat 132/33kV end.
6:40 | - | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Kachua 132/33kV end Due to None.
6:41 | - | Cumilla(S)-Kachua 132 kV Ckt-1 Project Work S/D from Kachua 132/33kV end. and from Cumilla(N) 230/132/33kVend. and from
Cumilla(S) 132/33kVend.
6:48 | 7:08 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT Scheduled S/D.
6:48 | 7:00 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) LT Scheduled S/D.
6:48 | - | Dohazari-Sikalbaha 132 kV Ckt-2 Project Work S/D from Dohazari 132/33kV end Due to Shut down taken at Shikalbaha Grid.
6:52 | - | Jashore 132/33kV S/S T-2 LT Project Work S/D Due to 33 kV Busbar Upgradation. |  |  |  |  | 60.0MW load interrup.
6:52 | - | Jashore 132/33kV S/S T-2 HT Project Work S/D Due to 33 kV Busbar Upgradation.
7:10 | - | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Annual Maintenance of 33 kV Bus by PBS. |  |  |  |  | 12.0MW load interrup.
7:10 | - | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Annual Maintenance of 33 kV Bus by PBS. |  |  |  |  | 12.0MW load interrup.
7:19 | - | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to 33kV Bus Section-2&3 Maintenance. |  |  |  |  | 39.0MW load interrup.
7:20 | - | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to 33kV Bus Section-2&3 Maintenance. |  |  |  |  | 39.0MW load interrup.
7:22 | - | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Work for other end.
07:03 |  | Aminbazar-Meghnaghat 230kV Ckt-2 Scheduled S/D from
Aminbazar 400/230/132kV end.
07:26 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled
S/D Due to General cleaning
07:26 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled
S/D
07:28 | 07:32 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to 33 kv |  |  |  |  | 18.0MW
|  | Bus Coupler DS open from PDB (33 kv side) |  |  |  |  | load
interrup.
interrup.
06:20 |  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to 33 kv |  |  |  |  | 13.0MW
|  | Bus coupler T5 maintenance. work |  |  |  |  | load
interrup.
06:22 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon
132/33kV end Due to S/D performed by oder of ALDC Bogura.
and from Bogura 230/132kV end Due to project work
06:23 |  | Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon
132/33kV end Due to S/D performed by oder of ALDC Bogura.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-03-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4002625
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 420 | 9259200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9348000 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 10560 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 155 | 3606400 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 70 | 89847 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 112943 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 24 | 36744 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 7680 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7293721
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 10080 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 28080 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 710400 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 40718 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 39097 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 753480 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 768552
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 476900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 143040 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 347184 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 336000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 78720 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 41760 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 214485
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 68040 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5062 | 2141 | 37824256
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 19243 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 134595
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 28800 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 771660 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 206 | 4984818
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 29272 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 39975 | Low demand.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 51254 | Low demand.
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 10 | 38400 | Low demand.
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 231600 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 822240
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 80 | 178145 | Low demand.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 29268 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 27600 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 17 | 80640 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 47673 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 108 | 160582 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 278 | 6779999 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 34 | 740160 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 456 | 11949090
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 501190
| Chattogram area Total |  |  |  | 4344 | 1394 | 27679325
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 101 | 3652000 | ST Sync. Process on 18:19.
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6904000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 335 | 7086300 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 47 | 1106712
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 52 | 472800
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 83 | 384728 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 977228
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 13381 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 20 | 9664 | Low demand.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 40 | 625920 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 219060
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 2536320
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 17 | 410600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 78763 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 409470 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 1194720 | Low demand.
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 608160 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 199800 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 274560
| Cumilla Area Total |  |  |  | 2951 | 1359 | 27164186
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 42 | 1221120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 16050
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 854400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 9 | 158400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 373220
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 41760 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 122 | 2664950
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1004000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 702600 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3654491
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 54600 | Gas shortage
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1195872
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 187164 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 122 | 2778430 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 345888 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7210500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 369 | 8099000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 135000
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 190 | 4789900 | ST Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1310 | 30157445
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 635 | 19517090
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 10 | 17024 | Low demand.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 633600
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 530 | 12072730
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1175 | 32240444
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 6 | 136164 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 1969000 | Frequency control
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 700 | 20568700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4908409
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Under maint.
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1006 | 27582273
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 21671 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 189 | 4325018 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 380 | 8246545 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 123462 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 40920
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1097 | 22330909
| Rajshahi Area Total |  |  |  | 3631 | 1671 | 35088525
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4118500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Fuel shortage
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 33 | 279888 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46322
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 328512
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 244718
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1329000
| Rangpur Area Total |  |  |  | 950 | 316 | 6346940
| Total |  |  |  | 25481 | 10494 | 226748344
| Eastern Grid Total |  |  |  | 15398 | 6326 | 125490162
| Western Grid Total |  |  |  | 10083 | 4168 | 101258182
| National Grid Total |  |  |  | 25481 | 10494 | 226748344
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-03-08
| (a) ENTIRE EASTERN GRID : |  | 6720 | MW | (b) ENTIRE WESTERN GRID : |  | 3441.6 | MW
| i) Dhaka area |  | 3490 | MW | i) Khulna area |  | 1224.3 | MW
| ii) Chittagong area |  | 1031 | MW | ii) Rajshahi area |  | 1147 | MW
| iii) Comilla area |  | 907 | MW | iii) Barisal area |  | 285.3 | MW
| iv) Mymensingh area |  | 929 | MW | iv) Rangpur area |  | 785 | MW
| v) Sylhet area |  | 363 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10161.6 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 20 | 18:30 | Kamrangirchar | 41.4 | 00:00 | Narinda | 36 | 13:00 | Sherpur | 110 | 12:00
2 | AKSML | 102 | 07:00 | Chowmuhani | 151 | 19:30 | Kaptai | N/A | N/A | Narshingdi | 141 | 20:00 | Shikalbaha | 21 | 00:00
3 | Aftabnagar | 26 | 13:00 | Chuadanga | 76 | 08:00 | Kazla | 81 | 13:00 | Natore | 113 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 55 | 13:00 | Coxsbazar | 108 | 18:30 | Keranigonj | 62 | 13:00 | Nawabganj | 31.2 | 13:00 | Shitalakhya | 57.2 | 00:00
5 | Agrabad | 50 | 19:00 | Cumilla(N) | 107 | 18:30 | Khagrachori | 26 | 18:30 | Netrakona | 125 | 19:00 | Sholosohor | 27 | 00:00
6 | Amnura | 73 | 08:00 | Cumilla(S) | 124 | 13:00 | Khulna | 54 | 13:00 | New | 15.4 | 00:00 | Shyampur | 158 | 07:00
7 | Ashuganj | 50 | 15:00 | Daudkandi | 92 | 00:00 | Khulshi | 142 | 17:00 | Niamatpur | 99 | 19:00 | Siddhirganj | 84 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 10 | 10:00 | Kishoreganj | 124 | 19:00 | Noapara | 40 | 18:30 | Sirajganj | 78 | 19:00
9 | BSRM | 110 | 01:00 | Dhamrai | 96 | 11:00 | Kodda | 206 | 00:00 | PHP | 10 | 19:00 | Sonargaon | 84 | 00:00
10 | Bagerhat | 67 | 19:00 | Dhanmondi | 95 | 19:00 | Kulaura | 28 | 18:30 | Pabna | 72 | 20:00 | Sreemongol | 41 | 21:00
11 | Bakulia | 66 | 19:00 | Dohazari | 72 | 18:30 | Kurigram | 63 | 18:30 | Palashbari | 100 | 19:00 | Sreepur | 53 | 00:00
12 | Banani | 24.8 | 19:00 | Faridpur | 101 | 19:00 | Kushtia | 100 | 19:00 | Panchagarh | 48 | 19:00 | Srinagar | 30 | 20:00
13 | Bangabhaban | 4 | 00:00 | Fatullah | 50 | 00:00 | Lalbag | 68 | 00:00 | Patuakhali | 51 | 21:00 | Sunamganj | 36 | 19:00
14 | Barapukuria | 54 | 09:00 | Fenchuganj | 27 | 18:30 | Lalmonirhat | 39 | 18:30 | Payra | 16 | 20:00 | Sylhet | 24 | 11:00
15 | Barguna | 12 | 00:00 | Feni | 80 | 19:00 | MI_Cement | 12.5 | 07:00 | Postogola | 38 | 12:00 | Sylhet-132 | 79 | 18:30
16 | Barishal | 72 | 12:00 | GPH | 88 | 03:00 | Madanganj | 29 | 12:00 | Purbachal | 13 | 12:00 | TK | 22 | 19:30
17 | Barishal-230 | 64 | 19:00 | Ghorashal | 62 | 21:00 | Madaripur | 63 | 20:00 | Purbasadipur | 118 | 11:00 | Tangail | 160 | 19:30
18 | Baroaulia | 62 | 14:00 | Goalpara | 24 | 13:00 | Madartek | 59.59 | 13:00 | Rahim | 50 | 00:00 | Thakurgaon | 86 | 19:00
19 | Baroirhat | 34 | 18:30 | Gollamari | 53 | 13:00 | Madunaghat | 35 | 18:30 | Rajbari | 46 | 19:00 | Tongi | 114 | 11:00
20 | Bashundhara | 143 | 13:00 | Gopalganj | 71.3 | 19:30 | Magura | 45 | 18:30 | Rajendrapur | 90 | 17:00 | Ullahpara | 20 | 09:00
21 | BashundharaCement | 6 | 01:00 | Gulshan | 62 | 18:30 | Mahasthangarh | 66 | 08:00 | Rajshahi | 109 | 13:00 | Ullon | 37 | 13:00
22 | Beanibazar | 33 | 19:00 | Halishahar | 57 | 11:00 | Manikganj | 87 | 19:00 | Rajshahi-230 | 27 | 21:00 | Uttara | 39 | 18:30
23 | Benapole | 65 | 19:00 | HaripurSBU | 137 | 07:00 | Maniknagar | 52 | 13:00 | Ramganj | 68 | 22:00 | UttaraNew | 31 | 13:00
24 | Bhaluka | 106 | 00:00 | Hasnabad | 59 | 22:00 | Matarbari | 42 | 19:00 | Rampur | 20 | 00:00 | Zigatola | 57 | 18:00
25 | Bhandaria | 31 | 19:30 | Hathazari | 54 | 19:00 | Matuail | 57 | 00:00 | Rangamati | 14 | 18:30
26 | Bhangura | 32 | 13:00 | Ishurdi | 47 | 19:00 | Millgate | 69 | 12:00 | Rangpur | 104 | 19:00
27 | Bheramara(GK) | 39 | 19:00 | Jaldhaka | 70 | 08:00 | Mirpur | 92 | 12:00 | Ruppur | 4 | 11:00
28 | Bhulta | 238 | 00:00 | Jamalpur | 138 | 08:00 | Mirsorai | 4 | 09:00 | SSM | 14 | 00:00
29 | Bog-Sherpur | 54 | 08:00 | Jashore | 91 | 20:00 | Mirzapur | 44 | 07:00 | Saidpur | 93 | 09:00
30 | Bogura | 126 | 21:00 | Jhenaidah | 99 | 19:00 | Mithapukur | 54 | 10:00 | Satkhira | 96 | 19:00
31 | Borhanuddin | 50 | 22:00 | Joydebpur | 119 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 82 | 13:00
32 | Brahmanbaria | 124 | 19:30 | Joypurhat | 59 | 09:00 | Mogbazar | 77.6 | 19:00 | Savar | 156 | 12:00
33 | Cantonment | 92 | 13:00 | Juldah | 24 | 00:00 | Mongla | 35 | 20:00 | SevenRings | 16.97 | 03:00
34 | Chandpur | 47 | 13:00 | KSRM | 28 | 09:00 | Motijheel | 26 | 13:00 | ShahCement | 32 | 15:00
35 | Chandraghona | 24 | 19:00 | Kabirpur | 159 | 00:00 | Munshiganj | 70 | 13:00 | Shahjadpur | 61 | 07:00
36 | Chapai | 58 | 09:00 | Kachua | 54 | 18:30 | Mymensingh | 199 | 13:00 | Shahjibazar | 88 | 20:00
37 | Charsaidpur | 44 | 03:00 | Kallyanpur | 84 | 12:00 | Naogaon | 111 | 08:00 | Shahmirpur | 27 | 00:00
38 | Chauddagram | 50 | 18:30 | Kalurghat | 22 | 00:00 | Narail | 40 | 19:00 | Shariatpur | 51 | 21:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-03-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 04:00 | 391 | 12:00 | Gopalganj | 412 | 05:00 | 398 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 399 | 05:00 | 386 | 12:00 | Madunaghat_I | 412 | 18:30 | 403 | 12:00
| Bibiana | 416 | 19:00 | 406 | 00:00 | Payra | 418 | 05:00 | 410 | 12:00
| BIPTC | 406 | 03:00 | 391 | 11:00 | Rahanpur | 416 | 05:00 | 403 | 08:00
| Bogura | 408 | 05:00 | 393 | 08:00 | Rampal | 410 | 05:00 | 396 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 05:00 | 224 | 12:00 | Haripur | 234 | 18:30 | 225 | 12:00
| AKSML | 231 | 18:00 | 222 | 01:00 | Hasnabad | 235 | 18:30 | 226 | 00:00
| Aminbazar | 235 | 03:00 | 225 | 12:00 | Hathazari | 233 | 19:00 | 220 | 13:00
| Ashuganj | 239 | 05:00 | 230 | 04:00 | Ishurdi | 239 | 05:00 | 224 | 11:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 237 | 04:00 | 221 | 11:00
| Baghabari | 236 | 02:00 | 227 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Barapukuria | 225 | 04:00 | 211 | 09:00 | Keranigonj | 233 | 05:00 | 223 | 12:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 241 | 04:00 | 228 | 13:00
| Barishal | 243 | 03:00 | 238 | 12:00 | Madunaghat_I | 231 | 18:30 | 221 | 12:00
| Bheramara | 237 | 05:00 | 221 | 11:00 | Maniknagar | 234 | 19:00 | 226 | 12:00
| Bhulta | 236 | 05:00 | 228 | 12:00 | Meghnaghat | 240 | 06:00 | 233 | 00:00
| Bibiana | 239 | 18:00 | 232 | 00:00 | Mirsorai | 236 | 19:00 | 221 | 01:00
| BIPTC | 239 | 05:00 | 223 | 11:00 | Rajshahi | 239 | 03:00 | 225 | 11:00
| Bogura | 234 | 04:00 | 224 | 08:00 | Rampal | 238 | 05:00 | 227 | 12:00
| Bogura-400 | 235 | 03:00 | 225 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 245 | 03:00 | 242 | 12:00 | Rampura | 234 | 04:00 | 227 | 12:00
| BSRM | 237 | 19:00 | 220 | 01:00 | Shikalbaha | 231 | 18:30 | 218 | 13:00
| Cumilla(N) | 235 | 18:00 | 227 | 12:00 | Shyampur | 234 | 05:00 | 225 | 12:00
| Fenchuganj | 242 | 17:00 | 238 | 12:00 | Siddhirganj | 236 | 19:00 | 229 | 12:00
| Ghorashal | 235 | 00:00 | 232 | 13:00 | Sirajgonj | 242 | 05:00 | 234 | 12:00
| Ghorashal-230 | 235 | 19:00 | 227 | 12:00 | Sreepur | 237 | 05:00 | 228 | 13:00
| GPH | 233 | 19:00 | 218 | 01:00 | Tongi | 232 | 07:00 | 212 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 134 | 04:00 | 128 | 12:00 | Lalbag | 133 | 04:00 | 122 | 18:30
| Agargaon | 136 | 05:00 | 129 | 12:00 | Lalmonirhat | 132 | 04:00 | 121 | 08:00
| Agrabad | 133 | 18:00 | 125 | 13:00 | Madanganj | 135 | 18:30 | 128 | 12:00
| AKS | 130 | 18:00 | 126 | 12:00 | Madaripur | 137 | 04:00 | 134 | 00:00
| Aminbazar | 136 | 03:00 | 130 | 12:00 | Madartek | 133 | 05:00 | 127 | 12:00
| Amnura | 134 | 03:00 | 126 | 08:00 | Madunaghat | 134 | 18:00 | 127 | 13:00
| Ashuganj | 142 | 18:00 | 136 | 12:00 | Magura | 139 | 04:00 | 129 | 13:00
| Bagerhat | 134 | 06:00 | 125 | 19:30 | Mahasthangarh | 135 | 05:00 | 125 | 08:00
| Bakulia | 133 | 18:30 | 125 | 13:00 | Manikganj | 135 | 19:30 | 126 | 16:00
| Banani | 135 | 04:00 | 129 | 12:00 | Maniknagar | 133 | 19:00 | 128 | 12:00
| Bangabhaban | 133 | 01:00 | 128 | 12:00 | Matarbari | 123 | 18:00 | 110 | 13:00
| Barapukuria | 139 | 04:00 | 127 | 09:00 | Matuail | 135.5 | 19:00 | 129.6 | 00:00
| Barguna | 133 | 06:00 | 129 | 19:30 | Millgate | 138 | 03:00 | 131 | 12:00
| Barishal | 140 | 03:00 | 125 | 19:30 | Mirpur | 134 | 05:00 | 127 | 12:00
| Barishal-230 | 140 | 05:00 | 136 | 12:00 | Mirzapur | 133 | 04:00 | 123 | 12:00
| Baroaulia | 135 | 18:30 | 125 | 13:00 | Mithapukur | 134 | 05:00 | 122 | 08:00
| Baroirhat | 133 | 18:30 | 126 | 01:00 | MI_Cement | 136 | 19:00 | 128 | 12:00
| Bashundhara | 138 | 04:00 | 130 | 13:00 | Modern | 133 | 18:00 | 126 | 12:00
| BashundharaCement | 135 | 18:30 | 128 | 12:00 | Mogbazar | 135 | 05:00 | 130 | 12:00
| Beanibazar | 134 | 03:00 | 132 | 00:00 | Mongla | 132 | 04:00 | 125 | 18:30
| Benapole | 137 | 03:00 | 125 | 13:00 | Motijheel | 133 | 01:00 | 128 | 12:00
| Bhaluka | 132 | 03:00 | 127 | 12:00 | Munshiganj | 136 | 19:00 | 129 | 12:00
| Bhandaria | 134 | 08:00 | 125 | 09:00 | Mymensingh | 130 | 04:00 | 118 | 17:00
| Bhangura | 139 | 03:00 | 131 | 11:00 | Naogaon | 134 | 04:00 | 122 | 08:00
| Bheramara | 138 | 05:00 | 129 | 11:00 | Narail | 138 | 04:00 | 128 | 11:00
| Bheramara(GK) | 138 | 04:00 | 130 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 127 | 18:30 | 120 | 10:00 | Narshingdi | 135 | 09:00 | 122 | 19:30
| Bog-Sherpur | 137 | 03:00 | 127 | 08:00 | Natore | 136 | 05:00 | 127 | 11:00
| Bogura | 137 | 04:00 | 128 | 08:00 | Nawabganj | 134 | 05:00 | 127 | 12:00
| Bogura-230 | 137 | 04:00 | 129 | 08:00 | Netrakona | 129 | 05:00 | 120 | 13:00
| Brahmanbaria | 135 | 09:00 | 131 | 00:00 | New | 138 | 04:00 | 131 | 12:00
| Cantonment | 136 | 05:00 | 128 | 12:00 | Niamatpur | 136 | 03:00 | 130 | 12:00
| Chandpur | 134 | 19:00 | 118 | 12:00 | Noapara | 136 | 05:00 | 128 | 12:00
| Chandraghona | 134 | 18:00 | 127 | 12:00 | Pabna | 140 | 06:00 | 131 | 11:00
| Chapai | 134 | 05:00 | 129 | 09:00 | Palashbari | 130 | 18:00 | 119 | 08:00
| Charsaidpur | 136 | 19:00 | 129 | 12:00 | Panchagarh | 134 | 04:00 | 113 | 09:00
| Chauddagram | 136 | 18:00 | 126 | 12:00 | Patuakhali | 133 | 05:00 | 130 | 00:00
| Chhatak | 135 | 06:00 | 131 | 00:00 | Payra | 134 | 03:00 | 132 | 00:00
| Chowmuhani | 132 | 18:00 | 121 | 12:00 | PHP | 133 | 19:00 | 126 | 01:00
| Chuadanga | 136 | 04:00 | 124 | 11:00 | Postogola | 136 | 18:00 | 129 | 12:00
| Coxsbazar | 122 | 17:00 | 114 | 13:00 | Purbachal | 138 | 03:00 | 130 | 12:00
| Cumilla(N) | 139 | 18:00 | 132 | 01:00 | Purbasadipur | 130 | 18:00 | 116 | 08:00
| Cumilla(S) | 137 | 18:00 | 127 | 10:00 | Rahanpur | 136 | 05:00 | 132 | 08:00
| Daudkandi | 130 | 19:00 | 124 | 00:00 | Rahim | 136 | 18:30 | 131 | 00:00
| Dhaka | 135 | 05:00 | 130 | 12:00 | Rajbari | 138 | 05:00 | 130 | 11:00
| Dhamrai | 138 | 03:00 | 129 | 12:00 | Rajendrapur | 137 | 20:00 | 126 | 13:00
| Dhanmondi | 135 | 06:00 | 131 | 00:00 | Rajshahi | 133 | 02:00 | 126 | 11:00
| Dohazari | 129 | 18:00 | 123 | 09:00 | Rajshahi-230 | 134 | 03:00 | 120 | 11:00
| Faridpur | 137 | 06:00 | 132 | 11:00 | Ramganj | 132 | 19:00 | 119 | 12:00
| Fatullah | 136 | 18:00 | 130 | 12:00 | Rampur | 133 | 18:30 | 125 | 12:00
| Fenchuganj | 139 | 16:00 | 134 | 13:00 | Rampura | 135 | 04:00 | 129 | 01:00
| Feni | 132 | 18:30 | 125 | 03:00 | Rangamati | 133 | 18:00 | 126 | 13:00
| Ghorashal | 140 | 06:00 | 137 | 11:00 | Rangpur | 133 | 03:00 | 119 | 09:00
| Goalpara | 138 | 05:00 | 129 | 12:00 | Ruppur | 138 | 01:00 | 132 | 11:00
| Gollamari | 136 | 04:00 | 129 | 12:00 | Saidpur | 132 | 04:00 | 118 | 09:00
| Gopalganj | 137 | 05:00 | 129 | 12:00 | Satkhira | 135 | 05:00 | 126 | 12:00
| Gopalganj-400 | 138 | 05:00 | 132 | 12:00 | Satmasjid | 135 | 05:00 | 128 | 12:00
| Gulshan | 134 | 05:00 | 129 | 15:00 | Savar | 134 | 19:00 | 125 | 12:00
| Halishahar | 133 | 19:00 | 125 | 12:00 | SevenRings | 143 | 19:00 | 136 | 13:00
| Haripur | 136 | 18:30 | 131 | 00:00 | ShahCement | 136 | 19:00 | 130 | 00:00
| HaripurSBU | 136 | 18:30 | 131 | 00:00 | Shahjadpur | 140 | 14:00 | 135 | 11:00
| Hasnabad | 135 | 18:00 | 130 | 12:00 | Shahjibazar | 134 | 07:00 | 131 | 00:00
| Hathazari | 136 | 18:30 | 129 | 12:00 | Shahmirpur | 133 | 19:00 | 126 | 22:00
| Ishurdi | 140 | 03:00 | 132 | 11:00 | Shariatpur | 137 | 04:00 | 132 | 12:00
| Jaldhaka | 132 | 03:00 | 116 | 08:00 | Sherpur | 122 | 13:00 | 109 | 06:00
| Jamalpur | 126 | 14:00 | 113 | 18:00 | Shikalbaha | 122 | 19:00 | 114 | 13:00
| Jashore | 137 | 03:00 | 127 | 13:00 | Shikalbaha-230 | 134 | 18:30 | 125 | 13:00
| Jhenaidah | 139 | 05:00 | 130 | 12:00 | Shitalakhya | 136 | 19:00 | 128 | 12:00
| Jhenaidah-230 | 141 | 05:00 | 130 | 11:00 | Sholosohor | 134 | 19:00 | 125 | 01:00
| Joydebpur | 142 | 18:00 | 135 | 14:00 | Shyampur | 135 | 19:00 | 129 | 00:00
| Joypurhat | 130 | 03:00 | 118 | 08:00 | Shyampur-230 | 136 | 19:00 | 129 | 12:00
| Juldah | 133 | 18:30 | 126 | 12:00 | Siddhirganj | 136 | 19:00 | 130 | 12:00
| Kabirpur | 139 | 20:00 | 128 | 12:00 | Sirajganj | 135 | 01:00 | 128 | 08:00
| Kachua | 136 | 19:00 | 118 | 13:00 | Sonargaon | 134 | 18:00 | 127 | 00:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sreemongol | 134 | 05:00 | 131 | 00:00
| Kallyanpur | 135 | 02:00 | 129 | 12:00 | Sreepur | 135 | 03:00 | 129 | 13:00
| Kalurghat | 134 | 18:00 | 125 | 13:00 | Srinagar | 134 | 19:00 | 127 | 12:00
| Kamrangirchar | 134 | 06:00 | 127 | 12:00 | SSM | 139 | 18:30 | 129 | 08:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 133 | 03:00 | 130 | 00:00
| Kazla | 133 | 05:00 | 127 | 13:00 | Sylhet | 134 | 01:00 | 132 | 00:00
| Keranigonj | 134 | 05:00 | 128 | 12:00 | Sylhet-132 | 135 | 03:00 | 132 | 00:00
| Khagrachori | 133 | 18:00 | 125 | 13:00 | Tangail | 128 | 03:00 | 122 | 12:00
| Khulna | 135 | 04:00 | 128 | 11:00 | Thakurgaon | 133 | 05:00 | 111 | 09:00
| Khulna(S) | 137 | 05:00 | 129 | 13:00 | TK | 134 | 18:30 | 127 | 23:00
| Khulshi | 132 | 18:00 | 124 | 13:00 | Tongi | 139 | 07:00 | 133 | 11:00
| Kishoreganj | 135 | 21:00 | 129 | 07:00 | Ullahpara | 137 | 02:00 | 131 | 08:00
| Kodda | 142 | 19:00 | 126 | 12:00 | Ullon | 134 | 03:00 | 128 | 12:00
| KSRM | 135 | 19:00 | 126 | 12:00 | Uttara | 135 | 05:00 | 128 | 12:00
| Kulaura | 136 | 04:00 | 134 | 00:00 | UttaraNew | 138 | 03:00 | 127 | 12:00
| Kurigram | 131 | 00:00 | 119 | 08:00 | Zigatola | 134 | 18:00 | 127 | 12:00
| Kushtia | 137 | 04:00 | 130 | 13:00

## L-Curve
Date | 2024-03-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1274 | 5085 | 4043 | 9128 |  |  |  | QF-LDC-11
0:30 | 1272 | 4963 | 4211.5 | 9174.5 | Date: | 2024-03-08
1:00 | 1270 | 4841 | 4380 | 9221
1:30 | 1275 | 4870.5 | 4210 | 9080.5
2:00 | 1280 | 4900 | 4040 | 8940
2:30 | 1244 | 4829 | 3956 | 8785 | [5 empty] | Gen. at Eve. Peak | 10494 | 10494 MW (19:00 )
3:00 | 1208 | 4758 | 3872 | 8630 | [6 empty] | 19:00
3:30 | 1184 | 4719 | 3767 | 8486 | [5 empty] | Gen. at Day Peak | 9803 | 9803 MW (12:00 )
4:00 | 1160 | 4680 | 3662 | 8342 | [6 empty] | 12:00
4:30 | 1124 | 4645.5 | 3648.5 | 8294 | [5 empty] | Highest Generation | 10494
5:00 | 1088 | 4611 | 3635 | 8246 | [6 empty] | 19:00
5:30 | 1098 | 4611 | 3665 | 8276
6:00 | 1108 | 4611 | 3695 | 8306
6:30 | 986 | 4879.5 | 3673 | 8552.5
7:00 | 864 | 5148 | 3651 | 8799
7:30 | 827 | 5214 | 3745.5 | 8959.5
8:00 | 790 | 5280 | 3840 | 9120
8:30 | 715 | 5249.5 | 3852.5 | 9102
9:00 | 640 | 5219 | 3865 | 9084
9:30 | 663 | 5139.5 | 3913 | 9052.5
10:00 | 686 | 5060 | 3961 | 9021
10:30 | 758 | 5075 | 4118 | 9193
11:00 | 830 | 5090 | 4275 | 9365
11:30 | 857 | 5173 | 4411 | 9584
12:00 | 884 | 5256 | 4547 | 9803
12:30 | 890 | 5427 | 4602 | 10029
13:00 | 896 | 5598 | 4657 | 10255
13:30 | 876 | 5356 | 4334 | 9690
14:00 | 856 | 5114 | 4011 | 9125
14:30 | 863 | 5080 | 3973 | 9053
15:00 | 870 | 5046 | 3935 | 8981
15:30 | 820 | 5027.5 | 3893.5 | 8921
16:00 | 770 | 5009 | 3852 | 8861
16:30 | 765 | 4909.5 | 3750.5 | 8660
17:00 | 760 | 4810 | 3649 | 8459
17:30 | 785 | 5138 | 3704.5 | 8842.5
18:00 | 810 | 5466 | 3760 | 9226
18:30 | 730 | 5896 | 3964 | 9860
19:00 | 650 | 6326 | 4168 | 10494
19:30 | 710 | 5902 | 4344 | 10246
20:00 | 786 | 5838 | 4527 | 10365 |  |  |  | Executive Engineer
20:30 | 918 | 5746 | 4560.5 | 10306.5 |  |  |  | Network Operation Division
21:00 | 1050 | 5654 | 4594 | 10248
21:30 | 1155 | 5506.5 | 4586 | 10092.5
22:00 | 1260 | 5359 | 4578 | 9937 |  |  |  |  | Page 6 of 7
22:30 | 1287 | 5322 | 4442.5 | 9764.5
23:00 | 1314 | 5285 | 4307 | 9592
23:30 | 1294 | 5185 | 4175 | 9360
24:00 | 1274 | 5085 | 4043 | 9128
10494 MW (19:00 )
9803 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-03-08 |  | Energy |  | 226748344
[14 empty] | Date: | 2024-03-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3207 | 923 | 1670 | 0 | 138 | 3018 | 30 | 0 | 8 | 108 | 0 | 26 | 0
0:30 | 3116.5 | 920.5 | 1639.5 | 0 | 107 | 3221.5 | 32.5 | 0 | 4 | 104 | 0 | 29 | 0 |  |  | Date: | 43897
1:00 | 3026 | 918 | 1609 | 0 | 76 | 3425 | 35 | 0 | 0 | 100 | 0 | 32 | 0
1:30 | 3056 | 838 | 1587.5 | 0 | 74 | 3351.5 | 35 | 0 | 0 | 103 | 0 | 35.5 | 0 | [8 empty] | Total Energy | 226.7483 | 226.7483 | Total Energy Gen 226.748 MKWHr Energy Not Served 0.296 MKWHr Energy Requirement 227.044 MKWHr
2:00 | 3086 | 758 | 1566 | 0 | 72 | 3278 | 35 | 0 | 0 | 106 | 0 | 39 | 0 | [8 empty] | Energy not Served | 0.29586 | 0.29586
2:30 | 3062 | 743.5 | 1549 | 0 | 51.5 | 3199 | 35 | 0 | 0 | 105 | 0 | 40 | 0 | [8 empty] | Energy Requirement | 227.0442 | 227.0442
3:00 | 3038 | 729 | 1532 | 0 | 31 | 3120 | 35 | 0 | 0 | 104 | 0 | 41 | 0
3:30 | 3040.5 | 729 | 1541.5 | 0 | 15.5 | 2984.5 | 35 | 0 | 0 | 102 | 0 | 38 | 0
4:00 | 3043 | 729 | 1551 | 0 | 0 | 2849 | 35 | 0 | 0 | 100 | 0 | 35 | 0
4:30 | 3021.5 | 728.5 | 1531.5 | 0 | 0 | 2838.5 | 35 | 0 | 0 | 99 | 0 | 40 | 0
5:00 | 3000 | 728 | 1512 | 0 | 0 | 2828 | 35 | 0 | 0 | 98 | 0 | 45 | 0
5:30 | 2998 | 728 | 1546.5 | 0 | 0 | 2832 | 35 | 0 | 0 | 96 | 0 | 40.5 | 0
6:00 | 2996 | 728 | 1581 | 0 | 0 | 2836 | 35 | 0 | 0 | 94 | 0 | 36 | 0
6:30 | 3114.5 | 681.5 | 1637 | 0 | 51 | 2873.5 | 35 | 0 | 8 | 95 | 20.5 | 36.5 | 12.5 | [7 empty] | Coal
7:00 | 3233 | 635 | 1693 | 0 | 102 | 2911 | 35 | 0 | 16 | 96 | 41 | 37 | 25
7:30 | 3170 | 635 | 1688 | 0 | 150.5 | 3026 | 35 | 0 | 16 | 97 | 108.5 | 33.5 | 24.5 | [6 empty] | Oil
8:00 | 3107 | 635 | 1683 | 0 | 199 | 3141 | 35 | 0 | 16 | 98 | 176 | 30 | 24
8:30 | 3086 | 635 | 1600.5 | 0 | 201.5 | 3154 | 37.5 | 0 | 16 | 96 | 243.5 | 32 | 31.5775
9:00 | 3065 | 635 | 1518 | 0 | 204 | 3167 | 40 | 0 | 16 | 94 | 311 | 34 | 39.155
9:30 | 2998 | 635 | 1516 | 0 | 223.5 | 3134 | 35 | 0 | 16 | 99 | 365.5 | 30.5 | 33.5775
10:00 | 2931 | 635 | 1514 | 0 | 243 | 3101 | 30 | 0 | 16 | 104 | 420 | 27 | 28
10:30 | 2931 | 776.5 | 1500.5 | 0 | 256.5 | 3089 | 30 | 0 | 16 | 106 | 453 | 34.5 | 23.5
11:00 | 2931 | 918 | 1487 | 0 | 270 | 3077 | 30 | 0 | 16 | 108 | 486 | 42 | 19
11:30 | 2978.5 | 918.5 | 1566 | 0 | 290 | 3141.5 | 30 | 0 | 16 | 113 | 494.5 | 36 | 9.5
12:00 | 3026 | 919 | 1645 | 0 | 310 | 3206 | 30 | 0 | 16 | 118 | 503 | 30 | 0
12:30 | 3134 | 919.5 | 1702.5 | 0 | 331 | 3263.5 | 30 | 0 | 32 | 121 | 470.5 | 25 | 0
13:00 | 3242 | 920 | 1760 | 0 | 352 | 3321 | 30 | 0 | 48 | 124 | 438 | 20 | 0
13:30 | 3242 | 920 | 1760 | 0 | 352 | 3321 | 30 | 0 | 48 | 124 | 438 | 20 | 0
14:00 | 3242 | 920 | 1760 | 0 | 352 | 3321 | 30 | 0 | 48 | 124 | 438 | 20 | 0
14:30 | 3045.5 | 920 | 1655.5 | 0 | 325.5 | 3082 | 30 | 0 | 24 | 109 | 401.5 | 25 | 0
15:00 | 2849 | 920 | 1551 | 0 | 299 | 2843 | 30 | 0 | 0 | 94 | 365 | 30 | 0
15:30 | 2850.5 | 919.5 | 1567 | 0 | 292 | 2838.5 | 30 | 0 | 0 | 92 | 297 | 34.5 | 0
16:00 | 2852 | 919 | 1583 | 0 | 285 | 2834 | 30 | 0 | 0 | 90 | 229 | 39 | 0
16:30 | 2827.5 | 919 | 1533 | 0 | 269 | 2788 | 30 | 0 | 8.5 | 94 | 157 | 34 | 0
17:00 | 2803 | 919 | 1483 | 0 | 253 | 2742 | 30 | 0 | 17 | 98 | 85 | 29 | 0
17:30 | 2841.5 | 919.5 | 1553.5 | 0 | 485.5 | 2761 | 30 | 0 | 68.5 | 110 | 43 | 30 | 23.5
18:00 | 2880 | 920 | 1624 | 0 | 718 | 2780 | 30 | 0 | 120 | 122 | 1 | 31 | 47
18:30 | 3043 | 777.5 | 1752 | 0 | 883 | 3005.5 | 30 | 0 | 216 | 120 | 0.5 | 32.5 | 43
19:00 | 3206 | 635 | 1880 | 0 | 1048 | 3231 | 30 | 0 | 312 | 118 | 0 | 34 | 39
19:30 | 3319 | 634 | 1889 | 0 | 526 | 3525 | 30 | 0 | 177 | 116 | 0 | 30 | 31.5
20:00 | 3307 | 635 | 1810 | 0 | 504 | 3760 | 30 | 0 | 181 | 112 | 0 | 26 | 24
20:30 | 3311.5 | 634.5 | 1788 | 0 | 415 | 3813.5 | 30 | 0 | 176 | 113 | 0 | 25 | 12
21:00 | 3316 | 634 | 1766 | 0 | 326 | 3867 | 30 | 0 | 171 | 114 | 0 | 24 | 0
21:30 | 3305 | 765.5 | 1735.5 | 0 | 282.5 | 3723.5 | 30 | 0 | 112 | 114 | 0 | 24.5 | 20.5325
22:00 | 3294 | 897 | 1705 | 0 | 239 | 3580 | 30 | 0 | 53 | 114 | 0 | 25 | 41.065
22:30 | 3289 | 908 | 1702 | 0 | 215.5 | 3452 | 30 | 0 | 38 | 111 | 0 | 19 | 31.515
23:00 | 3284 | 919 | 1699 | 0 | 192 | 3324 | 30 | 0 | 23 | 108 | 0 | 13 | 21.965
23:30 | 3245.5 | 921 | 1684.5 | 0 | 165 | 3171 | 30 | 0 | 15.5 | 108 | 0 | 19.5 | 10.9825 |  |  | Max Temp. in Dhaka |  | 31°C
24:00 | 3207 | 923 | 1670 | 0 | 138 | 3018 | 30 | 0 | 8 | 108 | 0 | 26 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 226.748 MKWHr Energy Not Served 0.296 MKWHr Energy Requirement 227.044 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-03-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 771660
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 17 | 0 |  |  |  |  | 0 | 19243
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 8 | 13 | 18 | 20 | 20 |  | 18 | 14 | 9 | 3 | [9 empty] | 134595
6 | Sikalbaha 225MW CCPP (Gas) | 210 | 210 | 210 | 210 | 209 | 210 | 209 | 209 | 212 | 212 | 205 | 207 | 206 | 208 | 206 | 206 | 206 | 206 |  | 206 | 206 | 206 | 206 | 206 | 205 | 205 | 4984818
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 17 |  | 17 | 17 | 17 | 17 |  |  | 0 | 51254
12 | Hathazari 100 MW peaking PP | [17 empty] | 16 |  | 24 | [6 empty] | 39975
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [17 empty] | 3 |  | 17 | [5 empty] | 0 | 29272
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [19 empty] | 20 | [6 empty] | 9664
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 300 | 300 | 335 | 335 | 335 | 290 | 260 | 260 | 328 | 250 | 250 | 250 | 250 | 280 |  | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 7293721
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 83 |  | 83 | 83 | 36 | 0 |  |  | 0 | 384728
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 140 | 140 | 170 | 170 | 170 | 170 | 170 | 170 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4002625
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 275 | 275 | 275 | 282 | 282 | 282 | 280 | 288 | 287 | 288 | 287 | 293 | 289 | 290 | 288 | 287 | 285 | 280 |  | 278 | 279 | 277 | 277 | 277 | 277 | 277 | 6779999
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 47 | 47 | 47 | 47 | 47 | 45 | 44 | 47 | 47 | 47 | 47 | 47 | 46 | 45 | 46 | 46 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 1106712
33 | Ashuganj 225 MW CCPP | 227 | 191 | 193 | 202 | 196 | 72 | 150 | 151 | 151 | 149 | 120 | 146 | 147 | 120 | 32 | 42 | 49 | 56 |  | 101 | 127 | 225 | 225 | 225 | 226 | 227 | 3652000
34 | Ashuganj 450 MW CCPP(South) | 280 | 270 | 270 | 280 | 270 | 330 | 320 | 275 | 280 | 275 | 275 | 305 | 300 | 270 | 290 | 305 | 270 | 270 |  | 275 | 290 | 270 | 270 | 270 | 270 | 270 | 6904000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 240 | 285 | 285 | 290 | 285 | 305 | 365 | 285 | 285 | 285 | 285 | 330 | 330 | 285 | 285 | 285 | 290 | 285 |  | 335 | 355 | 295 | 285 | 260 | 240 | 240 | 7086300
35 | Ashuganj 55 MW PP (Precision) | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 45 | 47 | 52 |  | 52 | 52 | 53 | 40 | 40 | 40 | 10 | 472800
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 373 | 351 | 351 | 351 | 330 | 344 | 377 | 428 | 427 | 395 | 389 | 375 | 400 | 376 | 364 | 364 | 333 | 321 |  | 420 | 416 | 418 | 419 | 422 | 425 | 427 | 9259200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 340 | 340 | 400 | 400 | 400 | 350 | 320 | 320 | 450 | 400 | 400 | 400 | 350 | 350 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 9348000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 73 | 73 | 73 | 73 | 73 | 73 | 69 | 70 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 40 | 30 | 52 |  | 42 | 50 | 50 | 67 | 67 | 82 | 68 | 1221120
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 5 | 20 | 35 | 46 | 51 | 52 | 51 | 49 | 37 | 24 | 7 | 0 | [8 empty] | 373220
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1004000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 |  | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 702600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 25 | 62 | 61 | 40 | 61 | 51 | 40 | 25 |  | 63 | 63 | 64 | 64 | 64 | 65 | 64 | 1195872
48 | Shahjibazar 86 MW PP (Shahjibazar)
| Shahjibazar 100 MW GTPP | [10 empty] | 90 |  |  |  | 30 |  |  | 70 | [8 empty] | 187164
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 25 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 122 | 130 | 130 | 130 | 130 | 130 | 130 | 2778430
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [11 empty] | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 135000
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 54600
56 | Shahjahanulla 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 345888
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 295 | 290 | 290 | 295 | 310 | 310 | 310 | 280 | 290 | 290 | 295 | 300 | 290 | 300 | 290 | 290 | 300 |  | 305 | 315 | 290 | 290 | 285 | 280 | 280 | 7210500
| Bibiyana South 400 MW | 260 | 260 | 210 | 210 | 210 | 210 | 205 | 200 | 190 | 170 | 170 | 170 | 190 | 180 | 180 | 180 | 200 | 200 |  | 190 | 204 | 180 | 180 | 180 | 180 | 180 | 4789900
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 17 | [5 empty] | 0 | 39097
59 | Tangail Palli Power Gen 22 MW | [17 empty] | 4 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 41760
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 231600
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 100 | 106 | 104 | 100 | 98 | 94 | 96 | 98 | 94 | 104 | 108 | 118 | 124 | 112 | 94 | 90 | 98 | 122 |  | 118 | 116 | 112 | 114 | 114 | 108 | 108 | 2536320
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 41 | 41 | 42 | 42 | 10 | 13 | 34 | 34 | 20 | 28 | 26 | 26 | 30 | 32 | 35 |  | 35 | 35 | 27 | 32 | 36 | 34 | 40 | 822240
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 219060
67 | Jangalia 33 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 410600
68 | Cumilla 25 MW PP (Summit) | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 409470
69 | Summit Ashulia | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 387000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 15 | 15 | 15 | 15 | 10 | 10 | 10 | 10 | 10 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 366480
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 30 | 30 | 30 | 30 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 768552
72 | Rupganj 33 MW PP(Summit) | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 7 |  | 21 | 21 | 21 | 21 | 21 | 14 | 21 | 476900
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 0 |  |  | 0 | 70 | 70 | 70 | 70 | 70 | 70 | 114 | 114 | 70 | 52 | 34 | 70 |  | 70 | 7 | 31 | 52 | 52 | 52 | 34 | 1194720
| Chowmuhani 113 MW | [6 empty] | 0 | 23 | 27 | 31 | 41 | 55 | 42 | 37 | 37 | 37 | 31 | 45 |  | 57 | 26 | 40 | 26 | 28 | 26 | 9 | 608160
| Manikgonj 162MW PP(MPGL) | [19 empty] | 35 | 17 |  |  |  |  | 0 | 41760
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 4 |  | 9 | [5 empty] | 0 | 7680
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 143040
79 | Kodda 150 MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 32 |  |  |  | 70 |  | 133 | 133 | 133 | 133 | 48 | 16 | 0 | 710400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 0 | 0 | 0 | [11 empty] | 1 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 78763
| Gazipur 100 MW PP | [7 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | [5 empty] | 0 | 336000
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 33121
| Jodiac Power | [17 empty] | 7 |  | 17 | [5 empty] | 0 | 29268
| Karnaphuli Power Ltd. | [17 empty] | 1 |  | 15 | 10 |  |  |  |  | 0 | 27600
82 | Madanganj 102 PP(Summit) | [17 empty] | 6 |  | 70 | 17 | 22 |  |  |  | 0 | 89847
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 13 |  | 24 | [5 empty] | 0 | 36744
86 | Meghnaghat CCPP ( Summit) | 156 | 156 | 158 | 158 | 156 | 157 | 157 | 155 | 147 | 152 | 152 | 150 | 145 | 133 | 131 | 134 | 133 | 134 |  | 155 | 154 | 154 | 153 | 153 | 154 | 154 | 3606400
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 1 |  | 8 | [5 empty] | 0 | 10560
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 0 | 12 | [5 empty] | 4 |  |  |  | 1 |  | 17 | 17 | 17 |  |  |  | 0 | 78720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 977228
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 8 | [5 empty] | 0 | 10080
95 | Patenga 50MW PP (Baraka) | [17 empty] | 6 |  | 6 | 6 | 6 | 6 |  |  | 0 | 28800
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 2 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 |  |  |  | 0 | 112943
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 40718
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 120 | 163 | 163 | 130 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3654491
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 16050
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 17 | 17 |  |  |  |  | 0 | 28080
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 19 | 56 | 56 | 56 | 58 | 59 | 59 | 58 | 58 | 58 | 19 | 65 |  | 65 | 65 | 65 | 65 | 9 | 9 | 9 | 854400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 13 | 6 |  |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 347184
115 | Juldah 100 MW PP Unit-3 (Acorn) | [19 empty] | 10 | 12 | 12 |  |  |  | 0 | 38400
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 17 | [7 empty] | 10 | 33 | 30 | 32 | 33 | 32 | 38 | 40 |  | 40 | 40 | 38 | 43 | 38 | 48 | 46 | 625920
117 | Ashuganj 150 MW PP (Midland) | [17 empty] | 2 |  | 5 | 6 | 4 |  |  |  | 0 | 13381
118 | Bibiyana-III 400 MW CCPP | 316 | 305 | 305 | 310 | 310 | 335 | 385 | 365 | 342 | 318 | 317 | 320 | 366 | 314 | 316 | 319 | 322 | 315 |  | 369 | 381 | 365 | 365 | 365 | 365 | 365 | 8099000
| Jamalpur 115 MW PP (United) | [6 empty] | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 5 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 158400
| Anwara 300 MW PP (United) | [16 empty] | 3 | 70 |  | 80 | 15 | 15 | 15 |  |  | 0 | 178145
| Juldah unit-2 (Acorn) | [17 empty] | 9 |  | 17 | 25 | 25 |  |  |  | 0 | 80640
| Anlima Energy Ltd. | [17 empty] | 5 |  | 17 | 17 |  |  |  |  | 0 | 47673
| Bhairob 54.5 MW | [13 empty] | 15 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 199800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 12 | 22 | 29 | 31 | 34 |  | 30 | 23 | 10 | 4 | [9 empty] | 214485
| Chandpur 115(Doreen) | [12 empty] | 12 | 18 | 18 | 23 | 42 | 40 |  | 36 | 36 | 36 | 21 | 18 |  | 0 | 274560
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 7 | 17 |  | 17 | 17 | 17 |  |  |  |  | 68040
| Mirsharai 150 MW (Oil) | [16 empty] | 17 | 17 |  | 108 | 17 | 17 | 17 |  |  | 0 | 160582
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 32 | 39 | 41 | 35 | 45 | 36 | 37 | 30 | 34 | 27 | 42 | 30 | 20 | 15 | 30 | 39 | 29 | 31 |  | 34 | 30 | 26 | 24 | 25 | 13 | 26 | 740160
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 6 | 25 | 43 | 61 | 71 | 71 | 68 | 63 | 48 | 28 | 11 | 0 | [8 empty] | 501190
| Matarbari 2*600 MW (CPGCL) | 500 | 500 | 450 | 400 | 403 | 403 | 472 | 575 | 575 | 524 | 524 | 575 | 575 | 455 | 455 | 454 | 455 | 455 |  | 456 | 510 | 575 | 576 | 505 | 505 | 401 | 11949090
120 | Eastern Zone Total | 4841 | 4900 | 4758 | 4680 | 4611 | 4611 | 5148 | 5280 | 5219 | 5060 | 5090 | 5256 | 5598 | 5114 | 5046 | 5009 | 4810 | 5466 |  | 6326 | 5902 | 5838 | 5654 | 5359 | 5285 | 5085 | 125490162
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 0
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 0 | 6 | 30 | 53 | 72 | 85 | 92 | 89 | 82 | 65 | 39 | 15 | 1 | [8 empty] | 633600
131 | Rampal 1320 MW (BIFPCL) | 613 | 566 | 538 | 529 | 509 | 514 | 510 | 510 | 513 | 484 | 443 | 441 | 439 | 409 | 405 | 406 | 405 | 440 |  | 530 | 546 | 551 | 548 | 548 | 460 | 367 | 12072730
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 200 | 200 | 203 | 4908409
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 80 | 80 | 76 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1969000
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 6 | 6 | 6 | 6 | 5 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4 | 6 |  | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 136164
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 10 | 10 | 10 |  |  |  |  | 17024
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 918 | 758 | 729 | 729 | 728 | 728 | 635 | 635 | 635 | 635 | 918 | 919 | 920 | 919 | 920 | 919 | 919 | 920 |  | 635 | 634 | 635 | 634 | 897 | 919 | 923 | 19517090
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 900 | 840 | 760 | 640 | 640 | 640 | 650 | 760 | 760 | 770 | 790 | 810 | 880 | 720 | 700 | 690 | 600 | 600 |  | 700 | 900 | 980 | 1090 | 960 | 800 | 800 | 20568700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4118500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 3 | 5 | 4 | 3 | 1 | 0 | [8 empty] | 40920
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 161 | 191 | 130 | 158 | 170 | 170 | 170 |  | 189 | 203 | 209 | 209 | 209 | 207 | 140 | 4325018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 353 | 320 | 330 | 348 | 346 | 398 | 414 | 397 | 310 | 320 | 323 | 409 | 375 | 250 | 250 | 250 | 230 | 260 |  | 380 | 380 | 380 | 380 | 340 | 340 | 340 | 8246545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [21 empty] | 4 | 4 | 5 | 7 | 8 | 21671
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 123462
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [9 empty] | 35 | 40 | 42 | 42 |  |  |  |  | 33 |  | 33 | 35 | 35 | 6 | 2 |  | 0 | 279888
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 3 | 5 | 6 | 6 | 7 | 6 | 5 | 4 | 2 | [9 empty] | 46322
178 | Energypac Power Venture Thakurgaon Ltd. | [13 empty] | 36 |  |  |  | 60 |  | 113 | 35 | 35 | 35 | 35 |  | 0 | 328512
| Intraco Solar 30 MW | [5 empty] | 0 | 2 | 11 | 21 | 28 | 32 | 34 | 34 | 33 | 23 | 17 | 6 | 0 | [8 empty] | 244718
| Adani Power Jharkhanda Ltd | 967 | 927 | 927 | 828 | 824 | 827 | 829 | 838 | 862 | 865 | 863 | 917 | 968 | 821 | 825 | 827 | 827 | 835 |  | 1097 | 1120 | 1207 | 1206 | 1120 | 1112 | 1003 | 22330909
178 | Teesta Solar Limited | [5 empty] | 0 | 15 | 64 | 113 | 151 | 178 | 182 | 179 | 161 | 141 | 92 | 35 | 0 | [8 empty] | 1329000