## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-03-13 | Wednesday
|  | Date (day): | 2024-03-13 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11959.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13474 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-03-12 | 2024-03-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 150 | 150 | 150
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 370 | 270 | 270 | 142 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 450 | 300 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 0 | 10 | 10 | 90 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 85 | 42 | 85 | 85 | 17 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 13 | 0 | 24 | 24 | 51 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 330 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 0 | 54 | 0
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 147 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55 | 0
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 17 | 36 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 12 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 193 | 97 | 300 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 101 | 35 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 18 | 86 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 162 | 0 | 162 | 0
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 0 | 17 | 38 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 450 | 300 | 450 | 350 |  |  | on test
| Dhaka area Total |  |  |  |  | 5763 | 5062 | 2178 | 2553 | 2198 | 2694 | 1669 | 1013
38 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
39 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
40 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
41 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 20 | 30 |  | Fuel shortage
42 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
43 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 207 | 206 | 210 | 210
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 32 | 30 | 32 | 66 |  | Fuel shortage
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 51 | 51 | 51 | 51 |  | Fuel shortage
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 36 | 0 | 36 | 36 | 64 |  | Fuel shortage
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 18 | 12 | 12 | 12 | 88 |  | Fuel shortage
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 22 | 10 | 15
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 68 | 103 | 65 | 100 | 200 |  | Fuel shortage
54 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 0 | 17 | 37 |  | Fuel shortage
55 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 15 | 17 | 93 |  | Fuel shortage
56 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
57 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
58 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 55 | 53 | 162 | 1
59 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 287 | 273 | 275 | 275 | 949 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 4 | 40 | 40 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 402 | 575 | 400 | 500 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 61 | 0 | 25 | 0 |  |  | on test
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1316 | 1489 | 1347 | 1590 | 2350 | 330
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 218 | 191 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 | 360 |  | Under S/D
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 305 | 310 | 310 | 50 |  | Gas shortage
63 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 330 | 350 | 270 | 300 | 100 |  | Gas shortage
64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 44 | 46 | 46 | 46
65 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 52 | 20 | 40 | 40 | 15
66 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 8 | 8 | 8 | 187 |  | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 10 | 51 | 51
68 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 5 | 6 | 8 | 142 |  | Fuel shortage
69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 46 | 0 | 50
70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 50 | 50 | 50 |  | 163 | Machine problem
71 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 34 | 34 | 166 |  | Fuel shortage
72 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Engine problem
73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 9 | 9 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 138 | 128 | 141
74 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 16 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 19 | 19 |  | 6 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 17 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 41 | 78 | 38 | 50 | 63 |  | Fuel shortage
79 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 |  | 37 | Engine problem
80 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 93 | 0 | 115 | 0
| Cumilla Area Total |  |  |  |  | 2959 | 2951 | 1405 | 1566 | 1301 | 1621 | 1127 | 244
81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 32 | 31 | 35 | 50 | 152 |  | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 97 | 56 | 97 | 103 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 0 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 140 | 134 | 142.6 | 153 | 152 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 40 | 40 | 40 |  | 50 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 20 | 65 | 65
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 95 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 206 | 138 | 138 |  | 93
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 20 | 16 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 17 | 17 | 17 | 17 | 8 |  | Gas shortage
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 275 | 310 | 310 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 418 | 362 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 240 | 205 | 75 | 250 |  |  | ST processing
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1464 | 1452 | 1280 | 1455 | 109 | 501
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
| Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 927 | 940 | 940
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 | 115 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 10 | 0 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 64 | 0 | 70 |  | 39 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 47 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 386 | 429 | 450 | 450
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1358 | 1447 | 1507 | 1527 | 1340 | 39
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 0 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 5 | 8 | 7 | 7 |  | 33 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 100 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 760 | 1200 | 1200
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 17 | 54 | 96 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1085 | 1204 | 1574 | 1721 | 403 | 97
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 26 | 25 | 34 | 18 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 0 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 50 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 211 | 146 | 140 | 180 | 40 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 350 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 16 | 30 | 20 |  | Engine problem
136 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 74 | 50 | 90 |  | 14 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 35 | 78 |  | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 35 | 78 |  | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1312 | 1286 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3653 | 3631 | 1954 | 2040 | 2236 | 2363 | 887 | 79
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 |  | 74 | Coal Shortage.
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 28 | 6 | 6 | 35 | 78 |  | Fuel shortage
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 0 | 115
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 184 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 455 | 321 | 374 | 350 | 203 | 159
| Total |  |  |  |  | 26504 | 25481 | 11355 | 12206 | 11959.6 | 13474 | 8240 | 2462
A. |  | 2024-03-12 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 12206 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8544 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12300 | MW
3 | Day peak Generation : |  |  | 11355 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11684.07 | MW
4 | Evening peak Generation : |  |  | 12206 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 90 | MW
5 | Total Energy Generation : |  | 263.7544 | MKWHr | By Solar | 3.137 | MKWHr
| By Gas : | 125.7974 | MKWHr |  | By Oil: | 24.1611 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 85.4449 | MKWHr |  | By Hydro: | 0.7146 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.07008 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 8240 | MW | Dhaka | 4323.27 | 4323.27 |  | 0 |  | 18:00 |  | 74.49
|  |  | For Plants S/D or M/C prob = |  |  | 2462 | MW | Chittagong | 1082.5 | 1082.5 |  | 0 |  | 19:00 |  | 89.77
|  |  | Total = |  |  | 10702 | MW | Khulna | 1429.6 | 1429.6 |  | 0 |  | 19:30 |  | 126.06
7 | Total Gas Supplied : |  |  | 933.59 | MMCFD |  |  | Rajshahi | 1160.4 | 1160.4 |  | 0 |  | 20:00 |  | 89.77
8 | Fuel Cost : | i) Gas : | Taka | 356529572.848 | ii) Oil : | Taka | 438541836.69 | Comilla | 1056 | 1056 |  | 0 |  | 21:00 |  | 62.075
|  | iii) Coal : | Taka | 572184283.83 | Total | Taka | 1367255693.368 | Mymensingh | 1078 | 988 |  | 90 |  | 22:00 |  | 60
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 407 | 407 |  | 0 |  | 23:00 |  | 98
| ii) During Peak Demand : |  |  | 1190 | MW (W to E) at | 19:00 | hrs | Barisal | 356.3 | 356.3 |  | 0 |  | 24:00 |  | 101
| iii) Maximum : |  |  | 920 | MW at | 8:00 | hrs | Rangpur | 791 | 791 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.1°C |  |  | Total | 11684.07 | 11594.07 |  | 90
B. |  | 2024-03-13 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13474 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
4 | Reserve(Generation end) |  |  |  | 774 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 274.429 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9209 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6204 | MKWHr. | ii) HVDC Flow at Peak Time |  | 927 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.809 | MKWHr. | iii) Maximum HVDC Flow : |  | 927 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.4 |  | (b) Today: | 82.18 |  | (c) Rule Curve: |  | 91.08
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-03-12 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 374 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 32 | 51 | 0 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 0 | 270 | 192 | 0 | 0 | 46 | 20 | 0 | 10 | 0 | 0 | 8 | 0 | 9 | 25 | 19 | 112 | 66 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 209 | 20 | 0 | 10 | 275 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 34 | 6 | 318 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 70 | 15 | 12 | 205 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 17 | 0 | 275 | 0 | 452 | 0 | 350 | 0 |  | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 7 | 0 | 0 | 0 | 0 | 34 | 0 | 75 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 250 | 17 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 740 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1256 | 0 | 0 |  | 5453 | 4340 | 9793 | 3152 | 925 | 1641 | 0 | 337 | 3323 | 30 | 0 | 273 | 112 | 0 | 0 | 83.085 | 82.42
2:00 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 31 | 51 | 0 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 0 | 270 | 192 | 0 | 0 | 46 | 15 | 0 | 10 | 0 | 0 | 8 | 0 | 9 | 25 | 19 | 106 | 68 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 209 | 20 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 12 | 34 | 6 | 321 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 34 | 9 | 12 | 180 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 285 | 17 | 0 | 277 | 0 | 452 | 0 | 350 | 0 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 34 | 0 | 75 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 200 | 17 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 700 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 1217 | 0 | 0 |  | 5358 | 4199 | 9557 | 3089 | 926 | 1601 | 0 | 304 | 3229 | 30 | 0 | 272 | 106 | 0 | 0 | 64.94 | 82.42
3:00 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 363 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 31 | 51 | 0 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 0 | 300 | 191 | 0 | 0 | 46 | 5 | 0 | 10 | 0 | 0 | 8 | 0 | 9 | 25 | 17 | 106 | 66 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 209 | 20 | 0 | 10 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 12 | 34 | 6 | 316 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 34 | 9 | 12 | 180 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 385 | 17 | 0 | 286 | 0 | 504 | 0 | 380 | 0 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 34 | 0 | 75 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 300 | 17 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 760 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 1160 | 0 | 0 |  | 5574 | 4345 | 9919 | 3252 | 926 | 1701 | 0 | 321 | 3329 | 30 | 0 | 254 | 106 | 0 | 0 | 125.105 | 82.41
4:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 369 | 0 |  | 0 | 350 | 0 | 0 | 6 | 0 | 335 | 0 | 0 | 6 | 8 | 32 | 16 | 0 | 0 | 0 | 35 | 35 | 30 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 31 | 51 | 25 | 0 | 6 | 10 | 40 | 0 | 0 | 0 | 0 | 300 | 191 | 0 | 0 | 46 | 5 | 0 | 10 | 0 | 0 | 8 | 0 | 9 | 25 | 17 | 118 | 67 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 209 | 20 | 0 | 10 | 290 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 12 | 34 | 5 | 316 | 9 | 17 | 17 | 0 | 16 | 0 | 17 | 64 | 9 | 12 | 180 | 17 | 0 | 130 | 17 | 0 | 0 | 0 | 27 | 0 | 335 | 17 | 0 | 302 | 5 | 501 | 0 | 380 | 0 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 34 | 0 | 75 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 300 | 17 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 880 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 0 | 0 | 1097 | 0 | 0 |  | 5891 | 4411 | 10302 | 3219 | 926 | 1692 | 0 | 643 | 3399 | 30 | 0 | 270 | 118 | 0 | 5 | 88.815 | 82.41
5:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 347 | 0 |  | 0 | 350 | 0 | 0 | 10 | 0 | 280 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 40 | 0 | 0 | 0 | 0 | 270 | 192 | 0 | 0 | 46 | 5 | 0 | 10 | 0 | 0 | 8 | 0 | 9 | 25 | 17 | 108 | 68 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 215 | 20 | 0 | 10 | 250 | 17 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 0 | 12 | 34 | 6 | 306 | 9 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 0 | 12 | 180 | 17 | 0 | 108 | 17 | 0 | 0 | 0 | 34 | 0 | 285 | 17 | 0 | 284 | 9 | 505 | 0 | 370 | 0 |  | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 240 | 17 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 940 | 0 | 0 |  | 5430 | 3948 | 9378 | 3063 | 925 | 1581 | 0 | 477 | 3120 | 30 | 0 | 65 | 108 | 0 | 9 | 0 | 82.4
6:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38 | 0 | 0 | 0 | 0 | 270 | 192 | 0 | 0 | 30 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 25 | 17 | 90 | 68 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 215 | 20 | 0 | 10 | 260 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 278 | 7 | 450 | 0 | 400 | 0 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 814 | 0 | 0 |  | 4876 | 3668 | 8544 | 2999 | 927 | 1618 | 0 | 25 | 2832 | 30 | 0 | 16 | 90 | 0 | 7 | 29.605 | 82.4
7:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 314 | 0 |  | 0 | 350 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 0 | 305 | 216 | 0 | 0 | 30 | 5 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 25 | 17 | 96 | 34 | 0 | 0 | 0 | 42 | 20 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 216 | 20 | 0 | 10 | 285 | 17 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 0 | 0 | 0 | 0 | 336 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 315 | 0 | 0 | 277 | 7 | 405 | 0 | 430 | 9 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 180 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 390 | 2 | 0 | 835 | 15 | 0 |  | 5039 | 3635 | 8674 | 3093 | 926 | 1648 | 0 | 90 | 2727 | 30 | 0 | 16 | 96 | 41 | 7 | 0 | 82.39
8:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 332 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 1 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 0 | 0 | 290 | 206 | 0 | 0 | 44 | 14 | 0 | 20 | 0 | 0 | 1 | 0 | 10 | 25 | 17 | 100 | 32 | 0 | 0 | 1 | 42 | 20 | 0 | 0 | 163 | 0 | 40 | 0 | 0 | 215 | 20 | 0 | 10 | 310 | 17 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 0 | 1 | 1 | 2 | 328 | 9 | 0 | 0 | 2 | 32 | 0 | 0 | 15 | 0 | 12 | 185 | 15 | 17 | 0 | 4 | 0 | 0 | 12 | 0 | 0 | 290 | 17 | 0 | 279 | 2 | 405 | 0 | 500 | 24 |  | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 600 | 220 | 0 | 0 | 1 | 28 | 0 | 0 | 0 | 389 | 11 | 0 | 967 | 60 | 0 |  | 5308 | 3956 | 9264 | 3112 | 784 | 2032 | 0 | 174 | 2840 | 30 | 0 | 33 | 100 | 157 | 2 | 44 | 82.39
9:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 359 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 7 | 207 | 0 | 0 | 0 |  | 0 | 16 | 0 | 0 | 0 | 6 | 10 | 15 | 0 | 0 | 0 | 0 | 300 | 218 | 0 | 0 | 44 | 46 | 0 | 51 | 0 | 0 | 8 | 0 | 10 | 25 | 17 | 100 | 33 | 0 | 0 | 1 | 42 | 30 | 0 | 0 | 163 | 0 | 62 | 0 | 0 | 209 | 20 | 0 | 10 | 315 | 8 | 0 | 0 | 25 | 0 | 0 | 56 | 0 | 17 | 15 | 12 | 30 | 5 | 360 | 9 | 17 | 1 | 3 | 49 | 0 | 4 | 114 | 6 | 12 | 205 | 17 | 30 | 0 | 17 | 0 | 0 | 18 | 0 | 0 | 305 | 17 | 0 | 278 | 0 | 403 | 0 | 450 | 41 |  | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 0 | 33 | 0 | 3 | 0 | 600 | 220 | 0 | 0 | 2 | 24 | 0 | 0 | 0 | 386 | 21 | 0 | 1061 | 107 | 0 |  | 5776 | 4147 | 9923 | 3258 | 784 | 2048 | 0 | 461 | 2928 | 30 | 0 | 49 | 100 | 265 | 0 | 121 | 82.38
10:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 360 | 0 | 0 | 5 | 0 | 320 | 0 | 0 | 0 | 8 | 48 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 0 | 16 | 0 | 36 | 0 | 6 | 10 | 16 | 0 | 0 | 0 | 0 | 300 | 209 | 0 | 0 | 44 | 52 | 0 | 51 | 0 | 10 | 8 | 0 | 10 | 25 | 17 | 110 | 33 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 163 | 0 | 62 | 0 | 0 | 209 | 20 | 0 | 8 | 315 | 17 | 0 | 0 | 49 | 0 | 0 | 60 | 0 | 17 | 18 | 12 | 34 | 6 | 365 | 9 | 17 | 17 | 4 | 49 | 0 | 17 | 98 | 9 | 12 | 206 | 17 | 41 | 0 | 17 | 0 | 0 | 24 | 0 | 0 | 300 | 35 | 0 | 281 | 0 | 404 | 0 | 450 | 49 |  | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 0 | 33 | 0 | 4 | 0 | 680 | 220 | 0 | 0 | 3 | 35 | 0 | 0 | 0 | 388 | 28 | 0 | 1257 | 149 | 0 |  | 6042 | 4492 | 10534 | 3317 | 784 | 2053 | 0 | 564 | 3210 | 30 | 0 | 109 | 110 | 357 | 0 | 63 | 82.38
11:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 362 | 0 |  | 0 | 360 | 0 | 0 | 70 | 7 | 319 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 6 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 0 | 16 | 17 | 36 | 0 | 6 | 10 | 11 | 0 | 0 | 0 | 0 | 310 | 220 | 16 | 0 | 44 | 53 | 0 | 51 | 0 | 17 | 8 | 0 | 10 | 25 | 17 | 114 | 33 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 209 | 20 | 0 | 9 | 290 | 17 | 0 | 0 | 100 | 0 | 0 | 58 | 0 | 17 | 19 | 18 | 34 | 6 | 365 | 9 | 17 | 17 | 4 | 52 | 0 | 17 | 98 | 10 | 12 | 201 | 17 | 47 | 0 | 17 | 0 | 0 | 27 | 0 | 0 | 310 | 35 | 0 | 285 | 0 | 401 | 0 | 450 | 60 |  | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 370 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 790 | 180 | 0 | 0 | 4 | 44 | 0 | 0 | 0 | 385 | 34 | 0 | 1318 | 173 | 0 |  | 6173 | 4744 | 10917 | 3289 | 924 | 1914 | 0 | 698 | 3379 | 30 | 0 | 149 | 114 | 420 | 0 | 55 | 82.37
12:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 360 | 0 | 7 | 85 | 15 | 322 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 0 | 16 | 34 | 36 | 0 | 6 | 10 | 12 | 0 | 0 | 0 | 0 | 325 | 218 | 16 | 0 | 44 | 52 | 0 | 51 | 0 | 23 | 8 | 0 | 7 | 25 | 17 | 110 | 32 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 120 | 0 | 61 | 0 | 0 | 206 | 20 | 0 | 9 | 300 | 17 | 0 | 0 | 193 | 0 | 0 | 58 | 0 | 17 | 19 | 18 | 34 | 6 | 418 | 0 | 17 | 17 | 4 | 68 | 0 | 17 | 98 | 41 | 12 | 240 | 17 | 48 | 0 | 17 | 0 | 0 | 30 | 0 | 0 | 330 | 35 | 0 | 287 | 0 | 402 | 0 | 450 | 61 |  | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 414 | 0 | 0 | 0 | 0 | 28 | 0 | 7 | 0 | 800 | 180 | 0 | 0 | 4 | 47 | 0 | 0 | 0 | 386 | 36 | 0 | 1312 | 184 | 0 |  | 6503 | 4852 | 11355 | 3460 | 925 | 1969 | 0 | 860 | 3387 | 30 | 0 | 172 | 110 | 442 | 0 | 57 | 82.36
13:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 380 | 0 | 9 | 85 | 15 | 328 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 0 | 32 | 34 | 36 | 0 | 6 | 10 | 16 | 0 | 0 | 0 | 0 | 330 | 216 | 55 | 0 | 45 | 50 | 0 | 51 | 0 | 27 | 8 | 0 | 7 | 25 | 17 | 130 | 32 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 163 | 0 | 60 | 0 | 0 | 203 | 20 | 0 | 9 | 315 | 17 | 0 | 0 | 195 | 0 | 0 | 58 | 0 | 23 | 19 | 22 | 34 | 5 | 330 | 0 | 17 | 17 | 4 | 68 | 0 | 17 | 114 | 48 | 12 | 240 | 17 | 46 | 0 | 17 | 0 | 6 | 30 | 0 | 0 | 350 | 35 | 0 | 287 | 1 | 456 | 0 | 350 | 56 |  | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 6 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 900 | 220 | 0 | 0 | 5 | 39 | 0 | 0 | 0 | 385 | 34 | 0 | 1316 | 176 | 0 |  | 6605 | 5053 | 11658 | 3442 | 925 | 2028 | 0 | 943 | 3544 | 30 | 0 | 198 | 130 | 417 | 1 | 64 | 82.35
14:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 380 | 0 | 9 | 85 | 15 | 325 | 0 | 0 | 0 | 8 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 14 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 0 | 32 | 51 | 36 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 0 | 330 | 202 | 55 | 0 | 44 | 48 | 0 | 51 | 0 | 30 | 8 | 0 | 9 | 25 | 17 | 140 | 32 | 0 | 0 | 2 | 43 | 20 | 0 | 0 | 163 | 0 | 60 | 0 | 0 | 200 | 20 | 0 | 9 | 320 | 17 | 0 | 0 | 137 | 0 | 0 | 58 | 0 | 35 | 16 | 22 | 34 | 2 | 386 | 0 | 17 | 17 | 3 | 70 | 0 | 17 | 114 | 48 | 12 | 220 | 17 | 39 | 0 | 17 | 0 | 17 | 27 | 0 | 0 | 335 | 17 | 0 | 287 | 3 | 455 | 0 | 350 | 54 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207 | 0 | 414 | 0 | 0 | 0 | 0 | 11 | 0 | 6 | 0 | 1080 | 220 | 0 | 0 | 4 | 64 | 0 | 0 | 0 | 405 | 31 | 0 | 1314 | 163 | 0 |  | 6558 | 5239 | 11797 | 3431 | 922 | 2017 | 0 | 894 | 3741 | 30 | 0 | 210 | 140 | 409 | 3 | 146.115 | 82.37
15:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 359 | 0 |  | 0 | 400 | 0 | 8 | 65 | 15 | 325 | 0 | 0 | 3 | 8 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 206 | 0 | 0 | 0 |  | 0 | 32 | 51 | 36 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 305 | 212 | 8 | 0 | 43 | 47 | 0 | 51 | 0 | 30 | 8 | 0 | 9 | 25 | 19 | 138 | 31 | 0 | 0 | 2 | 43 | 28 | 0 | 0 | 163 | 0 | 59 | 0 | 0 | 200 | 20 | 0 | 10 | 305 | 17 | 0 | 0 | 45 | 0 | 0 | 58 | 0 | 35 | 13 | 22 | 34 | 2 | 367 | 0 | 17 | 17 | 2 | 69 | 0 | 17 | 114 | 57 | 12 | 260 | 17 | 28 | 0 | 17 | 0 | 17 | 20 | 0 | 0 | 280 | 17 | 0 | 332 | 4 | 505 | 0 | 300 | 40 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 5 | 0 | 1120 | 220 | 0 | 0 | 3 | 41 | 0 | 0 | 0 | 423 | 27 | 0 | 1402 | 121 | 0 |  | 6361 | 5317 | 11678 | 3371 | 922 | 1924 | 0 | 787 | 3982 | 30 | 0 | 218 | 138 | 302 | 4 | 212.01 | 82.33
16:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 400 | 0 | 0 | 65 | 15 | 322 | 0 | 0 | 9 | 8 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 206 | 0 | 0 | 0 |  | 0 | 32 | 51 | 36 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 0 | 305 | 213 | 8 | 0 | 43 | 46 | 0 | 51 | 0 | 38 | 8 | 0 | 9 | 25 | 19 | 130 | 31 | 0 | 0 | 1 | 43 | 28 | 0 | 0 | 163 | 0 | 59 | 0 | 0 | 200 | 20 | 0 | 10 | 300 | 17 | 0 | 0 | 45 | 0 | 0 | 58 | 0 | 35 | 8 | 12 | 34 | 3 | 350 | 0 | 17 | 17 | 1 | 69 | 7 | 17 | 114 | 60 | 12 | 260 | 17 | 17 | 17 | 17 | 0 | 17 | 14 | 0 | 0 | 300 | 17 | 0 | 374 | 6 | 504 | 0 | 300 | 24 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 3 | 35 | 1120 | 220 | 0 | 0 | 2 | 35 | 35 | 0 | 0 | 458 | 16 | 0 | 1404 | 76 | 0 |  | 6398 | 5305 | 11703 | 3342 | 922 | 1917 | 0 | 873 | 4060 | 30 | 0 | 226 | 130 | 197 | 6 | 188.135 | 82.32
17:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 400 | 0 | 0 | 85 | 15 | 326 | 0 | 0 | 9 | 8 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 208 | 0 | 0 | 0 |  | 1 | 32 | 51 | 36 | 0 | 6 | 10 | 15 | 0 | 0 | 0 | 0 | 270 | 215 | 8 | 0 | 44 | 47 | 0 | 51 | 0 | 47 | 8 | 0 | 0 | 25 | 19 | 124 | 28 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 130 | 0 | 40 | 0 | 0 | 200 | 18 | 0 | 10 | 300 | 17 | 0 | 0 | 55 | 0 | 0 | 58 | 0 | 35 | 2 | 12 | 34 | 6 | 318 | 0 | 17 | 17 | 0 | 69 | 17 | 17 | 114 | 67 | 12 | 225 | 17 | 6 | 35 | 17 | 90 | 17 | 5 | 11 | 10 | 300 | 17 | 0 | 297 | 11 | 502 | 0 | 300 | 8 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 40 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 42 | 24 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 380 | 2 | 0 | 10 | 0 | 6 | 0 | 2 | 35 | 1080 | 220 | 0 | 0 | 0 | 13 | 55 | 0 | 0 | 434 | 6 | 0 | 1404 | 31 | 0 |  | 6338 | 5220 | 11558 | 3296 | 922 | 1867 | 0 | 995 | 3917 | 30 | 0 | 323 | 124 | 73 | 11 | 135.61 | 82.31
18:00 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 341 | 0 |  | 0 | 400 | 0 | 0 | 85 | 15 | 310 | 0 | 0 | 9 | 8 | 146 | 24 | 0 | 0 | 0 | 54 | 32 | 55 | 0 | 17 | 14 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 12 | 206 | 0 | 0 | 0 |  | 6 | 32 | 51 | 36 | 0 | 19 | 10 | 19 | 0 | 0 | 0 | 0 | 270 | 190 | 8 | 0 | 45 | 48 | 0 | 51 | 0 | 46 | 8 | 0 | 9 | 25 | 19 | 140 | 28 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 130 | 0 | 20 | 0 | 0 | 205 | 18 | 0 | 10 | 295 | 17 | 0 | 0 | 87 | 0 | 0 | 95 | 0 | 101 | 0 | 12 | 34 | 6 | 318 | 0 | 105 | 17 | 0 | 103 | 17 | 17 | 114 | 77 | 12 | 205 | 17 | 0 | 144 | 17 | 98 | 17 | 0 | 62 | 17 | 280 | 17 | 0 | 277 | 9 | 430 | 0 | 300 | 0 |  | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 71 | 0 | 80 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 42 | 37 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 320 | 17 | 0 | 35 | 0 | 6 | 0 | 0 | 35 | 980 | 180 | 0 | 23 | 0 | 1 | 115 | 0 | 0 | 462 | 0 | 0 | 1307 | 2 | 0 |  | 6807 | 5075 | 11882 | 3150 | 922 | 1768 | 0 | 1756 | 3656 | 30 | 0 | 448 | 140 | 3 | 9 | 74.49 | 82.3
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 42 | 15 | 330 | 0 | 0 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 19 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 |  | 6 | 32 | 51 | 0 | 0 | 19 | 10 | 22 | 0 | 0 | 0 | 0 | 305 | 191 | 8 | 50 | 46 | 20 | 0 | 10 | 0 | 46 | 8 | 0 | 9 | 25 | 19 | 138 | 31 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 206 | 16 | 0 | 10 | 275 | 17 | 0 | 0 | 97 | 0 | 0 | 97 | 0 | 101 | 0 | 12 | 34 | 5 | 362 | 0 | 105 | 17 | 0 | 103 | 17 | 17 | 114 | 78 | 12 | 205 | 17 | 0 | 162 | 17 | 95 | 17 | 0 | 93 | 17 | 350 | 55 | 0 | 273 | 4 | 575 | 0 | 300 | 0 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64 | 0 | 130 | 8 | 32 | 0 | 0 | 0 | 26 | 5 | 74 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 350 | 17 | 0 | 35 | 0 | 6 | 0 | 0 | 35 | 760 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 429 | 0 | 0 | 1286 | 0 | 0 |  | 7194 | 5012 | 12206 | 3458 | 927 | 1836 | 0 | 1702 | 3523 | 30 | 0 | 588 | 138 | 0 | 4 | 89.77 | 0
19:30 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 365 | 0 |  | 0 | 430 | 0 | 0 | 16 | 15 | 335 | 0 | 0 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 21 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 32 | 51 | 0 | 0 | 19 | 10 | 22 | 0 | 0 | 0 | 0 | 270 | 190 | 8 | 50 | 46 | 20 | 0 | 0 | 0 | 46 | 8 | 0 | 9 | 25 | 19 | 130 | 38 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 300 | 17 | 0 | 0 | 97 | 0 | 0 | 97 | 0 | 97 | 0 | 12 | 34 | 8 | 318 | 0 | 70 | 17 | 0 | 105 | 17 | 17 | 59 | 27 | 12 | 205 | 17 | 0 | 162 | 17 | 100 | 17 | 0 | 93 | 17 | 285 | 132 | 0 | 275 | 0 | 575 | 0 | 350 | 0 |  | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 65 | 0 | 130 | 8 | 48 | 0 | 0 | 0 | 26 | 15 | 80 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 300 | 17 | 0 | 35 | 0 | 6 | 0 | 0 | 0 | 880 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 446 | 0 | 0 | 1357 | 0 | 0 |  | 6803 | 5065 | 11868 | 3165 | 779 | 1831 | 0 | 1498 | 3733 | 30 | 0 | 702 | 130 | 0 | 0 | 126.06 | 0
20:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 400 | 0 | 0 | 7 | 15 | 335 | 0 | 0 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 21 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 |  | 6 | 32 | 51 | 0 | 0 | 19 | 10 | 25 | 0 | 0 | 0 | 0 | 270 | 190 | 8 | 50 | 46 | 26 | 0 | 0 | 0 | 38 | 8 | 0 | 9 | 25 | 19 | 136 | 56 | 0 | 0 | 0 | 43 | 40 | 40 | 21 | 163 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 280 | 17 | 0 | 0 | 99 | 0 | 0 | 97 | 0 | 97 | 0 | 12 | 34 | 6 | 318 | 0 | 70 | 17 | 0 | 106 | 0 | 17 | 55 | 26 | 12 | 260 | 17 | 0 | 162 | 17 | 100 | 0 | 0 | 94 | 17 | 288 | 162 | 0 | 272 | 0 | 575 | 0 | 400 | 0 |  | 780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 66 | 0 | 134 | 8 | 48 | 0 | 0 | 0 | 26 | 20 | 83 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 300 | 17 | 0 | 35 | 0 | 6 | 0 | 0 | 0 | 920 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 442 | 0 | 0 | 1364 | 0 | 0 |  | 6926 | 5110 | 12036 | 3244 | 780 | 1901 | 0 | 1417 | 3773 | 30 | 0 | 755 | 136 | 0 | 0 | 89.77 | 82.28
21:00 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 359 | 0 |  | 0 | 380 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 148 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 21 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 205 | 0 | 0 | 0 |  | 6 | 33 | 51 | 0 | 0 | 19 | 10 | 28 | 0 | 0 | 0 | 0 | 270 | 190 | 8 | 50 | 46 | 47 | 0 | 0 | 0 | 15 | 8 | 0 | 9 | 25 | 19 | 130 | 72 | 0 | 0 | 0 | 43 | 40 | 53 | 39 | 163 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 280 | 17 | 0 | 0 | 95 | 0 | 0 | 97 | 0 | 79 | 0 | 12 | 34 | 6 | 318 | 0 | 35 | 17 | 0 | 16 | 0 | 17 | 17 | 17 | 12 | 260 | 17 | 0 | 162 | 17 | 100 | 3 | 0 | 94 | 0 | 288 | 162 | 0 | 277 | 0 | 574 | 0 | 520 | 0 |  | 780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 66 | 0 | 130 | 9 | 48 | 0 | 0 | 0 | 26 | 24 | 83 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 350 | 17 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1030 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 443 | 0 | 0 | 1362 | 0 | 0 |  | 6854 | 5231 | 12085 | 3254 | 780 | 2107 | 0 | 1167 | 3886 | 30 | 0 | 731 | 130 | 0 | 0 | 62.075 | 0
22:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 359 | 0 |  | 0 | 370 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 21 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 204 | 0 | 0 | 0 |  | 6 | 32 | 51 | 0 | 0 | 19 | 10 | 28 | 0 | 0 | 0 | 0 | 270 | 192 | 8 | 50 | 46 | 51 | 0 | 0 | 0 | 15 | 8 | 0 | 9 | 25 | 19 | 134 | 74 | 0 | 0 | 0 | 43 | 40 | 53 | 38 | 163 | 0 | 20 | 0 | 0 | 0 | 18 | 0 | 10 | 295 | 17 | 0 | 0 | 97 | 0 | 0 | 97 | 0 | 79 | 0 | 12 | 34 | 6 | 318 | 0 | 35 | 17 | 0 | 16 | 0 | 17 | 17 | 9 | 12 | 260 | 17 | 0 | 162 | 17 | 80 | 17 | 0 | 94 | 0 | 288 | 162 | 0 | 272 | 0 | 504 | 0 | 540 | 0 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 17 | 27 | 83 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 394 | 0 | 0 | 1417 | 0 | 0 |  | 6749 | 5108 | 11857 | 3186 | 921 | 2135 | 0 | 1050 | 3787 | 30 | 0 | 614 | 134 | 0 | 0 | 60 | 82.26
23:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 359 | 0 |  | 0 | 330 | 0 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 8 | 206 | 0 | 0 | 0 |  | 6 | 32 | 51 | 0 | 0 | 19 | 10 | 29 | 0 | 0 | 0 | 0 | 345 | 216 | 8 | 50 | 46 | 52 | 0 | 0 | 0 | 15 | 8 | 0 | 9 | 25 | 19 | 132 | 74 | 0 | 0 | 0 | 43 | 40 | 53 | 44 | 163 | 0 | 32 | 0 | 0 | 0 | 20 | 0 | 10 | 310 | 8 | 0 | 0 | 97 | 0 | 0 | 19 | 0 | 80 | 0 | 12 | 34 | 5 | 372 | 0 | 35 | 17 | 0 | 16 | 0 | 5 | 52 | 9 | 12 | 260 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 68 | 0 | 366 | 17 | 0 | 270 | 0 | 504 | 0 | 540 | 0 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 17 | 27 | 83 | 0 | 0 | 48 | 0 | 24 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1060 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 1321 | 0 | 0 |  | 6214 | 4863 | 11077 | 3314 | 921 | 1978 | 0 | 599 | 3741 | 30 | 0 | 362 | 132 | 0 | 0 | 98 | 82.25
24:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 330 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 206 | 0 | 0 | 0 |  | 6 | 32 | 51 | 0 | 0 | 6 | 10 | 31 | 0 | 0 | 0 | 0 | 305 | 196 | 8 | 50 | 46 | 52 | 0 | 0 | 0 | 15 | 8 | 0 | 9 | 25 | 19 | 126 | 69 | 0 | 0 | 0 | 43 | 40 | 22 | 0 | 163 | 0 | 63 | 0 | 0 | 80 | 20 | 0 | 10 | 325 | 16 | 0 | 0 | 55 | 0 | 0 | 19 | 0 | 80 | 0 | 12 | 34 | 6 | 328 | 0 | 35 | 17 | 0 | 16 | 0 | 17 | 114 | 9 | 12 | 260 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 0 | 0 | 325 | 17 | 0 | 270 | 0 | 504 | 0 | 590 | 0 |  | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 17 | 24 | 83 | 0 | 0 | 40 | 0 | 24 | 0 | 0 | 2 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 1000 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 1297 | 0 | 0 |  | 6042 | 4777 | 10819 | 3257 | 921 | 1982 | 0 | 527 | 3657 | 30 | 0 | 319 | 126 | 0 | 0 | 101 | 82.24
KWH | 0 | 0 | 3546406 | 0 | 0 | 0 | 0 | 8647200 | 0 |  | 0 | 8363000 | 0 | 32640 | 617847 | 209940 | 7429840 | 0 | 0 | 37440 | 197280 | 1498560 | 186321 | 0 | 0 | 0 | 349200 | 205593 | 315386 | 0 | 408000 | 350640 | 817920 | 269800 | 224160 | 0 | 714600 | 0 | 0 | 0 | 217593 | 4932168 | 0 | 0 | 0 |  | 45120 | 495792 | 859960 | 318000 | 0 | 212640 | 237360 | 556800 | 0 | 0 | 0 | 0 | 7204000 | 4949000 | 200727 | 3139200 | 1043064 | 808320 | 0 | 698448 | 0 | 411792 | 184954 | 0 | 217080 | 610600 | 422350 | 2808960 | 1120320 | 0 | 0 | 14550 | 1007000 | 649920 | 214200 | 129816 | 3607445 | 0 | 985056 | 0 | 0 | 3654940 | 467000 | 0 | 224640 | 7245000 | 363168 | 0 | 0 | 1490400 | 0 | 0 | 1200000 | 0 | 1004544 | 136080 | 307200 | 756000 | 122109 | 8243000 | 92400 | 624000 | 357963 | 29160 | 1036255 | 74875 | 350430 | 1606260 | 661920 | 269760 | 5232700 | 364800 | 326250 | 1090080 | 377618 | 491091 | 187200 | 206501 | 592320 | 68400 | 7445500 | 914981 | 0 | 6921817 | 70080 | 11229090 | 0 | 9570455 | 430310 |  | 21620363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86880 | 272384 | 0 | 2517000 | 147727 | 153312 | 0 | 0 | 0 | 250516 | 95762 | 830752 | 0 | 228316 | 463737 | 0 | 149160 | 0 | 0 | 114624 | 0 | 0 | 4874700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4452355 | 0 | 8413818 | 170880 | 0 | 134880 | 0 | 276729 | 0 | 43272 | 136320 | 22972500 | 4648718 | 0 | 100800 | 34440 | 406800 | 640896 | 0 | 0 | 10058180 | 245645 | 0 | 29388594 | 1264000 | 0 |  | 148560305 | 115194060 | 263754365 | 80968302 | 21620363 | 44829114 | 0 | 17830781 | 85444881 | 714600 | 0 | 6330276 | 2808960 | 3137008 | 70080 | 0
Fuel Cost | 0 | 0 | 15214081.74 | 0 | 0 | 0 | 0 | 24903936 | 0 |  | 0 | 26594340 | 0 | 644966.4 | 11553738.9 | 3699142.8 | 22661012 | 0 | 0 | 739814.4 | 3541176 | 29102035.2 | 3474886.65 | 0 | 0 | 0 | 6376392 | 3240145.68 | 5768409.94 | 0 | 306000 | 0 | 0 | 0 | 4014705.6 | 0 | 0 | 0 | 0 | 0 | 4121211.42 | 15733615.92 | 0 | 0 | 0 |  | 793660.8 | 8730897.12 | 15401883.6 | 6061080 | 0 | 3500054.4 | 882979.2 | 0 | 0 | 0 | 0 | 0 | 22044240 | 16430680 | 672435.45 | 10139616 | 3515125.68 | 3540441.6 | 0 | 2800776.48 | 0 | 7375194.72 | 3340269.24 | 0 | 162810 | 2271432 | 316762.5 | 18426777.6 | 3484195.2 | 0 | 0 | 0 | 3927300 | 2424201.6 | 974610 | 590662.8 | 12337461.9 | 0 | 5467060.8 | 0 | 0 | 10197282.6 | 3072860 | 0 | 898560 | 22387050 | 272376 | 0 | 0 | 30404160 | 0 | 0 | 23052000 | 0 | 17690019.84 | 0 | 5471232 | 13116600 | 2024567.22 | 21843950 | 1761144 | 11706240 | 6421856.22 | 0 | 16942769.25 | 1455570 | 6286714.2 | 30695628.6 | 12847867.2 | 4804425.6 | 13918982 | 6227136 | 0 | 19937563.2 | 6336430.04 | 1836680.34 | 3345264 | 0 | 10673606.4 | 1158696 | 22113135 | 12882932.48 | 0 | 48245064.49 | 0 | 66251631 | 0 | 0 | 0 |  | 60753220.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1634212.8 | 5123543.04 | 0 | 7953720 | 700225.98 | 2643098.88 | 0 | 0 | 0 | 4486741.56 | 1757232.7 | 13964941.12 | 0 | 4353986.12 | 8305529.67 | 0 | 2671455.6 | 0 | 0 | 86770.368 | 0 | 0 | 41142468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14826342.15 | 0 | 24568348.56 | 2918630.4 | 0 | 2673321.6 | 0 | 5512441.68 | 0 | 0 | 2704588.8 | 148861800 | 14457512.98 | 0 | 1950480 | 0 | 0 | 11119545.6 | 0 | 0 | 73424714 | 0 | 0 | 194258606.34 | 0 | 0 |  | 793582213.02 | 652853477.978 | 1446435690.998 | 246007147.098 | 60753220.03 | 110522425.75 | 0 | 327105237.08 | 572184283.83 | 0 | 0 | 111436599.61 | 18426777.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 360 | 0 | 7 | 85 | 15 | 322 | 0 | 0 | 0 | 8 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 207 | 0 | 0 | 0 |  | 0 | 16 | 34 | 36 | 0 | 6 | 10 | 12 | 0 | 0 | 0 | 0 | 325 | 218 | 16 | 0 | 44 | 52 | 0 | 51 | 0 | 23 | 8 | 0 | 7 | 25 | 17 | 110 | 32 | 0 | 0 | 2 | 43 | 30 | 0 | 0 | 120 | 0 | 61 | 0 | 0 | 206 | 20 | 0 | 9 | 300 | 17 | 0 | 0 | 193 | 0 | 0 | 58 | 0 | 17 | 19 | 18 | 34 | 6 | 418 | 0 | 17 | 17 | 4 | 68 | 0 | 17 | 98 | 41 | 12 | 240 | 17 | 48 | 0 | 17 | 0 | 0 | 30 | 0 | 0 | 330 | 35 | 0 | 287 | 0 | 402 | 0 | 450 | 61 |  | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 414 | 0 | 0 | 0 | 0 | 28 | 0 | 7 | 0 | 800 | 180 | 0 | 0 | 4 | 47 | 0 | 0 | 0 | 386 | 36 | 0 | 1312 | 184 | 0 |  | 11355 | DayPeak
Yesterday Evening Peak | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 0 | 0 | 42 | 15 | 330 | 0 | 0 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 19 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 206 | 0 | 0 | 0 | 0 | 6 | 32 | 51 | 0 | 0 | 19 | 10 | 22 | 0 | 0 | 0 | 0 | 305 | 191 | 8 | 50 | 46 | 20 | 0 | 10 | 0 | 46 | 8 | 0 | 9 | 25 | 19 | 138 | 31 | 0 | 0 | 0 | 43 | 40 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 206 | 16 | 0 | 10 | 275 | 17 | 0 | 0 | 97 | 0 | 0 | 97 | 0 | 101 | 0 | 12 | 34 | 5 | 362 | 0 | 105 | 17 | 0 | 103 | 17 | 17 | 114 | 78 | 12 | 205 | 17 | 0 | 162 | 17 | 95 | 17 | 0 | 93 | 17 | 350 | 55 | 0 | 273 | 4 | 575 | 0 | 300 | 0 |  | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64 | 0 | 130 | 8 | 32 | 0 | 0 | 0 | 26 | 5 | 74 | 0 | 0 | 50 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 350 | 17 | 0 | 35 | 0 | 6 | 0 | 0 | 35 | 760 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 429 | 0 | 0 | 1286 | 0 | 0 |  | 12206 | EvPeak
Forecast for Evening | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 270 | 0 |  | 0 | 450 | 0 | 10 | 85 | 30 | 335 | 0 | 0 | 8 | 8 | 149 | 24 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 17 | 21 | 33 | 12 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 210 | 0 | 0 | 0 |  | 6 | 32 | 51 | 36 | 0 | 20 | 10 | 15 | 0 | 0 | 0 | 0 | 310 | 225 | 8 | 50 | 46 | 40 | 0 | 51 | 0 | 50 | 8 | 0 | 10 | 25 | 19 | 141 | 50 | 0 | 0 | 0 | 42 | 40 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 138 | 20 | 0 | 10 | 310 | 17 | 0 | 0 | 130 | 0 | 0 | 97 | 0 | 149 | 0 | 12 | 34 | 8 | 400 | 0 | 105 | 17 | 0 | 100 | 17 | 17 | 114 | 50 | 12 | 250 | 18 | 0 | 162 | 17 | 0 | 17 | 0 | 115 | 17 | 300 | 162 | 0 | 275 | 40 | 500 | 0 | 350 |  |  | 940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 0 | 130 | 7 | 110 | 0 | 0 | 0 | 34 | 20 | 90 | 28 | 42 | 50 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 1200 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 450 | 0 | 0 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 300 | 0 | 10 | 85 | 15 | 335 | 0 | 0 | 8 | 8 | 48 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 210 |  | 0 | 0 | 0 | 0 | 30 | 51 | 36 | 0 | 6 | 10 | 10 | 0 | 0 | 0 | 0 | 310 | 225 | 8 | 50 | 46 | 40 | 0 | 51 | 0 | 0 | 8 | 0 | 9 | 25 | 19 | 128 | 35 | 0 | 0 | 1.6 | 42 | 40 | 0 | 0 | 163 | 0 | 65 | 0 | 0 | 138 | 20 | 0 | 10 | 310 | 17 | 0 | 0 | 300 | 0 | 0 | 56 | 0 | 35 | 20 | 12 | 34 | 6 | 400 | 0 | 17 | 17 | 5 | 65 | 0 | 15 | 17 | 38 | 12 | 75 | 17 | 50 | 0 | 17 | 0 | 17 | 35 | 0 | 0 | 270 | 53 | 0 | 275 | 40 | 400 | 0 | 450 | 25 |  | 940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 50 | 28 | 42 | 40 | 0 | 16 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 414 | 17 | 0 | 35 | 0 | 6 | 0 | 8 | 35 | 1200 | 220 |  | 17 | 6 | 100 | 0 | 0 |  | 450 | 30 | 0 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 300 | 0 | 0 | 26 | 0 | 175 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 21 | 33 | 7 | 0 | 0 | 30 | 0 | 0 | 0 | 1 | 206 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 25 | 0 | 6 | 10 | 13 | 0 | 0 | 0 | 0 | 345 | 212 | 8 | 50 | 46 | 54 | 0 | 0 | 0 | 0 | 4 | 0 | 9 | 25 | 19 | 116 | 34 | 0 | 0 | 0 | 42 | 40 | 0 | 0 | 163 | 0 | 62 | 0 | 0 | 138 | 20 | 0 | 10 | 325 | 16 | 0 | 0 | 30 | 0 | 0 | 56 | 0 | 35 | 8 | 12 | 33 | 0 | 382 | 0 | 2 | 6 | 2 | 49 | 0 | 10 | 17 | 8 | 12 | 50 | 17 | 5 | 0 | 17 | 0 | 0 | 10 | 0 | 0 | 285 | 17 | 0 | 274 | 0 | 407 | 0 | 605 | 21 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 860 | 220 | 0 | 0 | 1 | 17 | 0 | 0 | 0 | 386 | 11 | 0 | 1172 | 64 | 0 | 0 |  |  |  | 125797416 | 21620363 | 0 | 85444881 | 24161057 | 2808960 | 3137008 | 70080 | 714600 |  |  | 263754365
[8 empty] | 299430 | [8 empty] | 299739 |  |  |  |  | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | 299864 | [12 empty] | 599468 |  |  |  | 599230 | [25 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 125.7974 | 21.6204 | 0 | 85.4449 | 24.1611 | 2.809 | 3.137 | 0.07008 | 0.7146
| Minimum Generation |  | 8544 | 6:00
| Highest Generation |  | 12206 | 19:00 | [129 empty] | 0 | [71 empty] | 263.7544
| Day Peak Generation |  | 11355 | 12:00
| Evening Peak Generation |  | 12206 | 19:00 | [201 empty] | 202699852
| HVDC Max Flow |  | 927 | 6:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 927 | 19:00
| Load factor L.F |  | 90.04% | [167 empty] | 1275.5

## P1
P |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-03-13
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-03-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11355 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9209
Evening Peak Generation : |  |  | 12206 | MW Hour : | 19:00 | Available Max Generation : |  | 13474
E.P. Demand (at gen end) : |  |  | 12300 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 12700
Maximum Generation : |  |  | 12206 | MW Hour : | 19:00 | Reserve(Generation end) |  | 774
Total Gen. (MKWH) : |  |  | 263.7544 | System Load Factor : | 90.04% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 920 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-03-13
Actual : |  | 82.18 | Ft.(MSL) , | Rule curve : | 91.08 | Ft.( MSL )
Gas Consumed : |  | Total = | 933.59 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 356529572.848
: |  |  | Coal : | 572184283.83 | Oil : | 438541836.69 | Total : | 1367255693.368
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4049.3685 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1109.504 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1553.2499 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1349.182 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1110.5832 |  |  | 0 | 0%
Mymensingh Area |  | 90 | 2160:00 | 825.5327 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 463.2298 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 385.5962 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 754.1689 |  |  | 0 | 0%
Total |  | 90 |  | 11600.4152 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Ashuganj North
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:20 | 14:38 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D.
08:23 | 14:38 | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end Due to CB Open Line Isolator Open:
08:32 | 17:15 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Annual Maintenance and
Dead line checking.
08:37 | 17:14 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Annual Maintenance and Dead line
checking. and from Tongi 230/132/33kVend.
08:45 | 16:23 | Khulna (S)-Satkhira 132kV Ckt-1 Forced S/D from Satkhira 132/33kV end.
08:56 | 12:14 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Project Work S/D Due to Internal Testing & SAS Integration.
08:58 | 12:13 | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Project Work S/D Due to Internal Testing & SAS Integration.
10:05 | 16:01 | Rampur 230/132/33 S/S ATR-02 (716T) HT Project Work S/D Due to Emergency shutdown needed to check functional test of
NIPES of tr-2
10:20 | 16:03 | Rampur 230/132/33 S/S ATR-02 (716T) LT Project Work S/D Due to NIPEPS functional testing.
11:07 | 16:08 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to Maintenance.
12:40 | 12:49 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing FBCPU relays Due to Over Current. | [5 empty] | 60 MW load interrup.
12:47 |  | Kalurghat 132/33kV S/S TRFO-01(506T) LT Scheduled S/D Due to Red hot maintenance by BPDB.
14:14 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to low Voltage.
14:51 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Scheduled S/D .
14:51 | 14:51 | Aminbazar 400/230/132kV S/S ATR-03 HT Scheduled S/D Due to red hot maintance.
14:51 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Scheduled S/D .
14:59 | 15:37 | BIPTC S/S 20DF43 Forced S/D Due to Corrective maintenance due to CB general Fault incoming .
| 16:23 | Khulna (S)-Satkhira 132kV Ckt-1 is restored.
| 17:02 | Shahjibazar 100 MW GTPP Syncronized
| 17:18 | Khulna (S)-Rampal Ckt-1 is restored.
| 17:18 | Khulna (S)-Rampal Ckt-1 is restored.
| 18:46 | Chandpur 150 MW CCPP Syncronized
19:30 |  | Sylhet 225 MW CCPP Tripped with remarks:- GT.
| 20:23 | Gopalganj- Gopalganj(N) 132kV Ckt-2 is restored.
21:40 | 22:48 | Khulshi-MSML 132kV Ckt-2 Tripped from Khulshi 132/33kV end showing Micom P442 relays Due to Earth Fault .
21:41 | 23:03 | Bakulia-MSML 132 kV Ckt-2 Tripped from Bakulia 132/33kV end showing Relay Trip-01, 02,03 Relay Trip-3ph Zone-01 relays.
22:14 | 22:50 | Barishal 230/132kV S/S T-5 LT Tripped showing O/C Relay relays Due to Due to 33kv wazirpur feeder fault. | [5 empty] | 24 MW load interrup.
22:14 | 22:50 | Barishal 230/132kV S/S T-4 LT Tripped showing O/C Relay relays Due to Due to 33KV Feeder fault.
22:28 |  | Shahjibazar 100 MW GTPP Shutdown
| 23:12 | Sylhet 225 MW CCPP Syncronized with remarks:- GT
06:03 | 06:36 | Joydebpur 132/33kV S/S GT-2 HT Scheduled S/D Due to Cleaning work of Auxiliary Transformer.
07:38 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Dead line checking.
07:42 |  | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Dead line checking.
07:03 |  | Aminbazar-Meghnaghat 230kV Ckt-2 Scheduled S/D from
Aminbazar 400/230/132kV end.
07:26 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled
S/D Due to General cleaning
07:26 |  | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled
S/D
07:28 | 07:32 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to 33 kv |  |  |  |  | 18.0MW
|  | Bus Coupler DS open from PDB (33 kv side) |  |  |  |  | load
interrup.
interrup.
06:20 |  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to 33 kv |  |  |  |  | 13.0MW
|  | Bus coupler T5 maintenance. work |  |  |  |  | load
interrup.
06:22 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon
132/33kV end Due to S/D performed by oder of ALDC Bogura.
and from Bogura 230/132kV end Due to project work
06:23 |  | Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon
132/33kV end Due to S/D performed by oder of ALDC Bogura.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-03-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 150 | 3546406 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8647200 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8363000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 32640 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 42 | 617847 | High Voltage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 209940 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 186321 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 37440 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7429840
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 197280 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 349200
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1498560
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 205593 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 315386 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 36 | 758640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817920
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 269800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 224160 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 97 | 1490400 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 101 | 1004544 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 624000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 364800 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1090080
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 206501
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 68400 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 300 | 9570455 | On test.
| Dhaka area Total |  |  |  | 5062 | 2553 | 48126353
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 217593 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136080
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 212640 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 714600 | Unit-3 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 206 | 4932168
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 357963 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 495792 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 859960 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 318000 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 307200 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 237360 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 556800
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 103 | 1036255 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 74875 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 350430 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 269760 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 377618 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 55 | 914981 | Fuel shortage
| SS Power I |  | SS Power | 2*612 | 1224 | 273 | 6921817 | Coal shortage
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 70080 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 575 | 11229090
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 430310
| Chattogram area Total |  |  |  | 4344 | 1489 | 31050532
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 191 | 4949000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7204000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 350 | 7445500 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 1043064
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 20 | 808320 | Gas shortage
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 10 | 698448
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 122109 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 411792 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 3139200 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 756000 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 217080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 2808960
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 610600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 184954 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 19 | 422350 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1606260
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 661920 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 187200 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 592320 | Fuel shortage
| Cumilla Area Total |  |  |  | 2951 | 1566 | 34069804
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 31 | 1120320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14550
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 97 | 1200000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 0 | 92400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 326250
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 45120 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 134 | 2798640
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1007000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 649920 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3607445
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 214200
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 129816 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 985056 | Gas shortage
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 95 | 491091
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 206 | 3654940
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 467000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 17 | 363168 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7245000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 362 | 8243000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 224640
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 205 | 5232700 | FGMO & ST Under maint.
| Sylhet Area Total |  |  |  | 2427 | 1452 | 32514976
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 927 | 21620363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 10 | 86880 | low demand
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 64 | 272384 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 170880 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 406800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 429 | 10058180
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1447 | 32615487
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 153312 | low demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 8 | 147727 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2517000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 760 | 22972500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4648718
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 100800 | Fuel shortage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1204 | 30540057
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 26 | 250516 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 95762 | low demand
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 228316 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 50 | 463737
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 146 | 4452355 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 350 | 8413818 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 149160 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 114624 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 74 | 830752 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 134880 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 136320 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34440
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1286 | 29388594
| Rajshahi Area Total |  |  |  | 3631 | 2040 | 44693274
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4874700 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Fuel shortage
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 6 | 276729 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43272
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 640896
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 245645
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1264000
| Rangpur Area Total |  |  |  | 950 | 321 | 7345242
| Total |  |  |  | 25481 | 12206 | 263754365
| Eastern Grid Total |  |  |  | 15398 | 7194 | 148560305
| Western Grid Total |  |  |  | 10083 | 5012 | 115194060
| National Grid Total |  |  |  | 25481 | 12206 | 263754365
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-03-12
| (a) ENTIRE EASTERN GRID : |  | 7856.77 | MW | (b) ENTIRE WESTERN GRID : |  | 3737.3 | MW
| i) Dhaka area |  | 4323.27 | MW | i) Khulna area |  | 1429.6 | MW
| ii) Chittagong area |  | 1082.5 | MW | ii) Rajshahi area |  | 1160.4 | MW
| iii) Comilla area |  | 1056 | MW | iii) Barisal area |  | 356.3 | MW
| iv) Mymensingh area |  | 988 | MW | iv) Rangpur area |  | 791 | MW
| v) Sylhet area |  | 407 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11594.07 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 22 | 18:00 | Kamrangirchar | 56.26 | 13:00 | Narinda | 48 | 13:00 | Sherpur | 140 | 21:00
2 | AKSML | 105 | 23:00 | Chowmuhani | 162 | 18:30 | Kaptai | N/A | N/A | Narshingdi | 156 | 19:30 | Shikalbaha | 19 | 12:00
3 | Aftabnagar | 28 | 13:00 | Chuadanga | 86 | 19:00 | Kazla | 96 | 13:00 | Natore | 126 | 19:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 68 | 14:00 | Coxsbazar | 110 | 19:00 | Keranigonj | 70 | 18:30 | Nawabganj | 31.4 | 20:00 | Shitalakhya | 86 | 15:00
5 | Agrabad | 62 | 18:00 | Cumilla(N) | 118 | 20:00 | Khagrachori | 28 | 18:30 | Netrakona | 108 | 00:00 | Sholosohor | 34 | 15:00
6 | Amnura | 64 | 19:00 | Cumilla(S) | 138 | 19:00 | Khulna | 64 | 20:00 | New | 20 | 12:00 | Shyampur | 136 | 23:00
7 | Ashuganj | 54 | 15:00 | Daudkandi | 113 | 19:30 | Khulshi | 157 | 13:00 | Niamatpur | 96 | 08:00 | Siddhirganj | 108 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 28 | 12:00 | Kishoreganj | 130 | 21:00 | Noapara | 42 | 19:00 | Sirajganj | 94 | 19:00
9 | BSRM | 133 | 19:30 | Dhamrai | 116 | 18:00 | Kodda | 275 | 18:30 | PHP | 10 | 04:00 | Sonargaon | 113 | 18:00
10 | Bagerhat | 76 | 19:00 | Dhanmondi | 112 | 13:00 | Kulaura | 30 | 18:00 | Pabna | 90 | 19:00 | Sreemongol | 49 | 19:30
11 | Bakulia | 79 | 18:30 | Dohazari | 68 | 19:00 | Kurigram | 63 | 08:00 | Palashbari | 112 | 08:00 | Sreepur | 61 | 17:00
12 | Banani | 33 | 14:00 | Faridpur | 121 | 19:00 | Kushtia | 108 | 19:00 | Panchagarh | 50 | 19:00 | Srinagar | 33.24 | 20:00
13 | Bangabhaban | 14 | 10:00 | Fatullah | 62 | 12:00 | Lalbag | 85 | 12:00 | Patuakhali | 58 | 21:00 | Sunamganj | 40 | 18:30
14 | Barapukuria | 62 | 10:00 | Fenchuganj | 32 | 18:30 | Lalmonirhat | 48 | 18:30 | Payra | 16 | 18:30 | Sylhet | 22 | 18:00
15 | Barguna | 16 | 19:00 | Feni | 90 | 19:30 | MI_Cement | 12.1 | 20:00 | Postogola | 47 | 00:00 | Sylhet-132 | 99 | 18:30
16 | Barishal | 89 | 20:00 | GPH | 88 | 05:00 | Madanganj | 30 | 21:00 | Purbachal | 14 | 13:00 | TK | 21.5 | 18:30
17 | Barishal-230 | 70 | 19:00 | Ghorashal | 72 | 15:00 | Madaripur | 74 | 19:30 | Purbasadipur | 117 | 12:00 | Tangail | 182 | 19:00
18 | Baroaulia | 71 | 12:00 | Goalpara | 28 | 19:30 | Madartek | 57.02 | 21:00 | Rahim | 54 | 13:00 | Thakurgaon | 89 | 19:30
19 | Baroirhat | 43 | 19:30 | Gollamari | 64 | 19:00 | Madunaghat | 36 | 19:00 | Rajbari | 52 | 19:00 | Tongi | 137 | 11:00
20 | Bashundhara | 163 | 14:00 | Gopalganj | 81 | 19:00 | Magura | 51 | 19:00 | Rajendrapur | 82 | 11:00 | Ullahpara | 24 | 19:00
21 | BashundharaCement | 6 | 00:00 | Gulshan | 94 | 13:00 | Mahasthangarh | 62 | 08:00 | Rajshahi | 118 | 19:00 | Ullon | 43 | 18:30
22 | Beanibazar | 37 | 18:00 | Halishahar | 85 | 15:00 | Manikganj | 101 | 19:00 | Rajshahi-230 | 29 | 20:00 | Uttara | 50 | 14:00
23 | Benapole | 60 | 07:00 | HaripurSBU | 161 | 16:00 | Maniknagar | 58 | 12:00 | Ramganj | 78 | 20:00 | UttaraNew | 33 | 12:00
24 | Bhaluka | 116 | 07:00 | Hasnabad | 64 | 23:00 | Matarbari | 40 | 18:30 | Rampur | 23 | 18:30 | Zigatola | 52 | 14:00
25 | Bhandaria | 34 | 20:00 | Hathazari | 56 | 18:30 | Matuail | 68 | 12:00 | Rangamati | 16 | 19:00
26 | Bhangura | 32 | 19:00 | Ishurdi | 53 | 19:00 | Millgate | 100 | 12:00 | Rangpur | 120 | 19:00
27 | Bheramara(GK) | 45 | 13:00 | Jaldhaka | 71 | 08:00 | Mirpur | 113 | 16:00 | Ruppur | 5.2 | 16:00
28 | Bhulta | 237 | 00:00 | Jamalpur | 131 | 20:00 | Mirsorai | 4 | 15:00 | SSM | 12 | 00:00
29 | Bog-Sherpur | 58 | 08:00 | Jashore | 126 | 19:00 | Mirzapur | 44 | 22:00 | Saidpur | 108 | 09:00
30 | Bogura | 138 | 19:30 | Jhenaidah | 106 | 19:00 | Mithapukur | 44 | 18:30 | Satkhira | 117 | 19:00
31 | Borhanuddin | 55 | 22:00 | Joydebpur | 156 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 87 | 19:00
32 | Brahmanbaria | 136 | 19:30 | Joypurhat | 60 | 18:30 | Mogbazar | 109.6 | 15:00 | Savar | 176 | 11:00
33 | Cantonment | 106 | 13:00 | Juldah | 16 | 12:00 | Mongla | 30 | 15:00 | SevenRings | 15.49 | 15:00
34 | Chandpur | 46 | 18:30 | KSRM | 62 | 06:00 | Motijheel | 38 | 17:00 | ShahCement | 31 | 01:00
35 | Chandraghona | 26 | 18:30 | Kabirpur | 256 | 12:00 | Munshiganj | 74 | 13:00 | Shahjadpur | 70 | 12:00
36 | Chapai | 62 | 08:00 | Kachua | 58 | 19:30 | Mymensingh | 208 | 08:00 | Shahjibazar | 96 | 19:00
37 | Charsaidpur | 41 | 00:00 | Kallyanpur | 84 | 18:30 | Naogaon | 113 | 19:00 | Shahmirpur | 39.6 | 17:00
38 | Chauddagram | 57 | 18:30 | Kalurghat | 30 | 12:00 | Narail | 47 | 19:00 | Shariatpur | 57 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-03-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 04:00 | 392 | 10:00 | Gopalganj | 412 | 04:00 | 398 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 393 | 20:00 | 290 | 03:00
| Bhulta | 398 | 04:00 | 374 | 11:00 | Madunaghat_I | 414 | 20:00 | 406 | 00:00
| Bibiana | 411 | 01:00 | 403 | 10:00 | Payra | 417 | 03:00 | 410 | 10:00
| BIPTC | 399 | 02:00 | 387 | 13:00 | Rahanpur | 414 | 04:00 | 393 | 19:30
| Bogura | 406 | 04:00 | 380 | 08:00 | Rampal | 412 | 04:00 | 396 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 04:00 | 221 | 15:00 | Haripur | 230 | 02:00 | 220 | 10:00
| AKSML | 231 | 20:00 | 221 | 05:00 | Hasnabad | 233 | 19:30 | 223 | 10:00
| Aminbazar | 234 | 07:00 | 220 | 15:00 | Hathazari | 231 | 18:00 | 223 | 15:00
| Ashuganj | 236 | 01:00 | 224 | 15:00 | Ishurdi | 236 | 00:00 | 223 | 07:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 236 | 04:00 | 220 | 07:00
| Baghabari | 234 | 03:00 | 222 | 11:00 | Kaliakoir | 232 | 04:00 | 222 | 15:00
| Barapukuria | 222 | 04:00 | 205 | 08:00 | Keranigonj | 232 | 04:00 | 221 | 10:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 241 | 03:00 | 225 | 07:00
| Barishal | 245 | 04:00 | 239 | 12:00 | Madunaghat_I | 233 | 20:00 | 224 | 00:00
| Bheramara | 236 | 00:00 | 224 | 11:00 | Maniknagar | 232 | 04:00 | 220 | 15:00
| Bhulta | 234 | 03:00 | 221 | 15:00 | Meghnaghat | 236 | 04:00 | 228 | 11:00
| Bibiana | 237 | 03:00 | 231 | 12:00 | Mirsorai | 237 | 20:00 | 221 | 15:00
| BIPTC | 237 | 00:00 | 222 | 07:00 | Rajshahi | 238 | 00:00 | 226 | 07:00
| Bogura | 230 | 03:00 | 216 | 08:00 | Rampal | 237 | 03:00 | 225 | 07:00
| Bogura-400 | 234 | 04:00 | 218 | 08:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 04:00 | 244 | 00:00 | Rampura | 234 | 03:00 | 220 | 11:00
| BSRM | 237 | 20:00 | 224 | 01:00 | Shikalbaha | 232 | 19:30 | 221 | 00:00
| Cumilla(N) | 233 | 05:00 | 225 | 15:00 | Shyampur | 233 | 05:00 | 221 | 15:00
| Fenchuganj | 240 | 20:00 | 236 | 09:00 | Siddhirganj | 233 | 05:00 | 224 | 12:00
| Ghorashal | 235 | 00:00 | 220 | 07:00 | Sirajgonj | 240 | 03:00 | 229 | 12:00
| Ghorashal-230 | 233 | 05:00 | 219 | 15:00 | Sreepur | 234 | 04:00 | 219 | 12:00
| GPH | 234 | 20:00 | 222 | 15:00 | Tongi | 230 | 20:00 | 211 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 04:00 | 123 | 15:00 | Lalbag | 133 | 04:00 | 124 | 12:00
| Agargaon | 158 | 12:00 | 127 | 15:00 | Lalmonirhat | 129 | 00:00 | 116 | 18:30
| Agrabad | 134 | 20:00 | 127 | 15:00 | Madanganj | 134 | 20:00 | 127 | 09:00
| AKS | 131 | 19:00 | 126 | 03:00 | Madaripur | 137 | 22:00 | 132 | 15:00
| Aminbazar | 134 | 20:00 | 129 | 07:00 | Madartek | 133 | 03:00 | 123 | 16:00
| Amnura | 138 | 21:00 | 123 | 08:00 | Madunaghat | 135 | 19:00 | 127 | 07:00
| Ashuganj | 140 | 00:00 | 135 | 08:00 | Magura | 138 | 03:00 | 127 | 12:00
| Bagerhat | 132 | 01:00 | 122 | 12:00 | Mahasthangarh | 133 | 03:00 | 121 | 08:00
| Bakulia | 134 | 20:00 | 128 | 00:00 | Manikganj | 133 | 20:00 | 121 | 15:00
| Banani | 134 | 04:00 | 125 | 12:00 | Maniknagar | 132 | 04:00 | 123 | 15:00
| Bangabhaban | 132 | 01:00 | 123 | 15:00 | Matarbari | 129 | 04:00 | 120 | 07:00
| Barapukuria | 138 | 04:00 | 123 | 08:00 | Matuail | 133.7 | 03:00 | 127.2 | 12:00
| Barguna | 133 | 06:00 | 128 | 22:00 | Millgate | 137 | 04:00 | 124 | 15:00
| Barishal | 140 | 01:00 | 125 | 22:00 | Mirpur | 132 | 01:00 | 126 | 09:00
| Barishal-230 | 141 | 04:00 | 136 | 15:00 | Mirzapur | 132 | 20:00 | 125 | 14:00
| Baroaulia | 136 | 20:00 | 129 | 04:00 | Mithapukur | 132 | 05:00 | 115 | 08:00
| Baroirhat | 135 | 20:00 | 125 | 07:00 | MI_Cement | 133.7 | 20:00 | 125 | 12:00
| Bashundhara | 137 | 01:00 | 124 | 15:00 | Modern | 134 | 20:00 | 127 | 14:00
| BashundharaCement | 134 | 20:00 | 127 | 09:00 | Mogbazar | 134 | 03:00 | 125 | 11:00
| Beanibazar | 135 | 03:00 | 128 | 11:00 | Mongla | 130 | 00:00 | 122 | 11:00
| Benapole | 136 | 03:00 | 122 | 08:00 | Motijheel | 132 | 01:00 | 123 | 15:00
| Bhaluka | 131 | 03:00 | 121 | 09:00 | Munshiganj | 134 | 20:00 | 128 | 09:00
| Bhandaria | 130 | 08:00 | 125 | 19:30 | Mymensingh | 128 | 21:00 | 116 | 08:00
| Bhangura | 138 | 03:00 | 129 | 10:00 | Naogaon | 131 | 04:00 | 119 | 07:00
| Bheramara | 136 | 00:00 | 129 | 11:00 | Narail | 138 | 03:00 | 125 | 18:30
| Bheramara(GK) | 135 | 00:00 | 128 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 122 | 18:00 | 116 | 10:00 | Narshingdi | 138 | 03:00 | 121 | 15:00
| Bog-Sherpur | 136 | 04:00 | 124 | 07:00 | Natore | 134 | 03:00 | 126 | 07:00
| Bogura | 136 | 03:00 | 124 | 08:00 | Nawabganj | 133 | 03:00 | 125 | 11:00
| Bogura-230 | 135 | 03:00 | 124 | 08:00 | Netrakona | 128 | 04:00 | 115 | 09:00
| Brahmanbaria | 133 | 05:00 | 124 | 16:00 | New | 137 | 05:00 | 125 | 15:00
| Cantonment | 134 | 03:00 | 127 | 15:00 | Niamatpur | 135 | 03:00 | 126 | 18:30
| Chandpur | 132 | 17:00 | 125 | 01:00 | Noapara | 134 | 00:00 | 124 | 11:00
| Chandraghona | 135 | 19:30 | 130 | 00:00 | Pabna | 138 | 03:00 | 129 | 07:00
| Chapai | 133 | 01:00 | 124 | 08:00 | Palashbari | 131 | 03:00 | 115 | 08:00
| Charsaidpur | 135 | 20:00 | 128 | 10:00 | Panchagarh | 133 | 03:00 | 104 | 08:00
| Chauddagram | 134 | 20:00 | 127 | 00:00 | Patuakhali | 135 | 07:00 | 129 | 12:00
| Chhatak | 133 | 00:00 | 129 | 18:00 | Payra | 134 | 03:00 | 131 | 12:00
| Chowmuhani | 130 | 17:00 | 125 | 00:00 | PHP | 133 | 17:00 | 126 | 00:00
| Chuadanga | 136 | 04:00 | 122 | 12:00 | Postogola | 135 | 20:00 | 127 | 11:00
| Coxsbazar | 123 | 07:00 | 118 | 18:30 | Purbachal | 137 | 02:00 | 123 | 15:00
| Cumilla(N) | 137 | 20:00 | 131 | 07:00 | Purbasadipur | 128 | 02:00 | 108 | 08:00
| Cumilla(S) | 135 | 20:00 | 126 | 15:00 | Rahanpur | 137 | 03:00 | 131 | 07:00
| Daudkandi | 128 | 05:00 | 121 | 15:00 | Rahim | 134 | 19:30 | 128 | 10:00
| Dhaka | 134 | 03:00 | 125 | 15:00 | Rajbari | 137 | 03:00 | 130 | 07:00
| Dhamrai | 137 | 02:00 | 130 | 15:00 | Rajendrapur | 137 | 21:00 | 125 | 11:00
| Dhanmondi | 135 | 04:00 | 128 | 10:00 | Rajshahi | 133 | 20:00 | 124 | 11:00
| Dohazari | 131 | 10:00 | 125 | 14:00 | Rajshahi-230 | 133 | 03:00 | 122 | 19:00
| Faridpur | 137 | 03:00 | 131 | 11:00 | Ramganj | 130 | 16:00 | 123 | 00:00
| Fatullah | 138 | 15:00 | 128 | 10:00 | Rampur | 135 | 20:00 | 127 | 07:00
| Fenchuganj | 137 | 10:00 | 132 | 15:00 | Rampura | 134 | 03:00 | 123 | 15:00
| Feni | 133 | 17:00 | 124 | 00:00 | Rangamati | 134 | 20:00 | 128 | 07:00
| Ghorashal | 138 | 00:00 | 131 | 15:00 | Rangpur | 130 | 02:00 | 116 | 08:00
| Goalpara | 138 | 04:00 | 126 | 07:00 | Ruppur | 138 | 00:00 | 130 | 12:00
| Gollamari | 136 | 03:00 | 126 | 08:00 | Saidpur | 132 | 04:00 | 112 | 08:00
| Gopalganj | 136 | 03:00 | 129 | 07:00 | Satkhira | 134 | 03:00 | 122 | 08:00
| Gopalganj-400 | 137 | 03:00 | 131 | 15:00 | Satmasjid | 135 | 05:00 | 126 | 15:00
| Gulshan | 132 | 00:00 | 124 | 15:00 | Savar | 132 | 04:00 | 124 | 09:00
| Halishahar | 135 | 20:00 | 126 | 07:00 | SevenRings | 141 | 05:00 | 130 | 15:00
| Haripur | 134 | 06:00 | 128 | 10:00 | ShahCement | 135 | 20:00 | 128 | 10:00
| HaripurSBU | 134 | 19:30 | 128 | 10:00 | Shahjadpur | 141 | 03:00 | 132 | 11:00
| Hasnabad | 133 | 01:00 | 127 | 10:00 | Shahjibazar | 132 | 03:00 | 126 | 11:00
| Hathazari | 138 | 20:00 | 130 | 07:00 | Shahmirpur | 134 | 18:30 | 128 | 15:00
| Ishurdi | 139 | 00:00 | 131 | 07:00 | Shariatpur | 137 | 04:00 | 131 | 10:00
| Jaldhaka | 131 | 04:00 | 110 | 08:00 | Sherpur | 122 | 19:00 | 110 | 01:00
| Jamalpur | 125 | 19:00 | 109 | 23:00 | Shikalbaha | 122 | 22:00 | 117 | 00:00
| Jashore | 137 | 03:00 | 123 | 12:00 | Shikalbaha-230 | 135 | 19:30 | 129 | 01:00
| Jhenaidah | 138 | 00:00 | 128 | 12:00 | Shitalakhya | 133.7 | 20:00 | 125 | 12:00
| Jhenaidah-230 | 140 | 04:00 | 128 | 07:00 | Sholosohor | 134 | 20:00 | 123 | 04:00
| Joydebpur | 140 | 03:00 | 125 | 15:00 | Shyampur | 134 | 20:00 | 127 | 15:00
| Joypurhat | 130 | 03:00 | 116 | 07:00 | Shyampur-230 | 134 | 04:00 | 128 | 10:00
| Juldah | 133 | 18:30 | 129 | 13:00 | Siddhirganj | 134 | 05:00 | 128 | 10:00
| Kabirpur | 137 | 21:00 | 121 | 15:00 | Sirajganj | 135 | 02:00 | 123 | 12:00
| Kachua | 133 | 20:00 | 127 | 00:00 | Sonargaon | 132 | 04:00 | 125 | 17:00
| Kaliakoir | 138 | 20:00 | 131 | 11:00 | Sreemongol | 132 | 01:00 | 127 | 14:00
| Kallyanpur | 133 | 01:00 | 128 | 11:00 | Sreepur | 133 | 03:00 | 124 | 12:00
| Kalurghat | 136 | 20:00 | 127 | 15:00 | Srinagar | 131 | 03:00 | 125 | 16:00
| Kamrangirchar | 133 | 03:00 | 126 | 10:00 | SSM | 140 | 20:00 | 131 | 13:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 133 | 04:00 | 128 | 18:30
| Kazla | 132 | 04:00 | 123 | 12:00 | Sylhet | 134 | 02:00 | 129 | 15:00
| Keranigonj | 133 | 03:00 | 126 | 10:00 | Sylhet-132 | 133 | 00:00 | 131 | 13:00
| Khagrachori | 134 | 20:00 | 127 | 07:00 | Tangail | 128 | 03:00 | 123 | 07:00
| Khulna | 135 | 03:00 | 124 | 12:00 | Thakurgaon | 132 | 03:00 | 103 | 08:00
| Khulna(S) | 137 | 03:00 | 126 | 07:00 | TK | 134 | 21:00 | 128 | 03:00
| Khulshi | 134 | 20:00 | 126 | 07:00 | Tongi | 137 | 20:00 | 128 | 11:00
| Kishoreganj | 135 | 01:00 | 122 | 09:00 | Ullahpara | 136 | 00:00 | 127 | 12:00
| Kodda | 137 | 20:00 | 123 | 15:00 | Ullon | 131 | 01:00 | 124 | 11:00
| KSRM | 137 | 20:00 | 128 | 02:00 | Uttara | 135 | 05:00 | 124 | 15:00
| Kulaura | 135 | 01:00 | 131 | 15:00 | UttaraNew | 135 | 03:00 | 126 | 09:00
| Kurigram | 132 | 05:00 | 114 | 08:00 | Zigatola | 132 | 05:00 | 126 | 12:00
| Kushtia | 136 | 02:00 | 128 | 07:00

## L-Curve
Date | 2024-03-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1606 | 6042 | 4777 | 10819 |  |  |  | QF-LDC-11
0:30 | 1413 | 5747.5 | 4558.5 | 10306 | Date: | 2024-03-12
1:00 | 1220 | 5453 | 4340 | 9793
1:30 | 4355 | 5405.5 | 4269.5 | 9675
2:00 | 7490 | 5358 | 4199 | 9557
2:30 | 4265 | 5466 | 4272 | 9738 | [5 empty] | Gen. at Eve. Peak | 12206 | 12206 MW (19:00 )
3:00 | 1040 | 5574 | 4345 | 9919 | [6 empty] | 19:00
3:30 | 1105 | 5732.5 | 4378 | 10110.5 | [5 empty] | Gen. at Day Peak | 11355 | 11355 MW (12:00 )
4:00 | 1170 | 5891 | 4411 | 10302 | [6 empty] | 12:00
4:30 | 1165 | 5660.5 | 4179.5 | 9840 | [5 empty] | Highest Generation | 12206
5:00 | 1160 | 5430 | 3948 | 9378 | [6 empty] | 19:00
5:30 | 1145 | 5153 | 3808 | 8961
6:00 | 1130 | 4876 | 3668 | 8544
6:30 | 1070 | 4957.5 | 3651.5 | 8609
7:00 | 1010 | 5039 | 3635 | 8674
7:30 | 965 | 5173.5 | 3795.5 | 8969
8:00 | 920 | 5308 | 3956 | 9264
8:30 | 975 | 5542 | 4051.5 | 9593.5
9:00 | 1030 | 5776 | 4147 | 9923
9:30 | 1225 | 5909 | 4319.5 | 10228.5
10:00 | 1420 | 6042 | 4492 | 10534
10:30 | 1450 | 6107.5 | 4618 | 10725.5
11:00 | 1480 | 6173 | 4744 | 10917
11:30 | 1490 | 6338 | 4798 | 11136
12:00 | 1500 | 6503 | 4852 | 11355
12:30 | 1485 | 6554 | 4952.5 | 11506.5
13:00 | 1470 | 6605 | 5053 | 11658
13:30 | 1525 | 6581.5 | 5146 | 11727.5
14:00 | 1580 | 6558 | 5239 | 11797
14:30 | 1585 | 6459.5 | 5278 | 11737.5
15:00 | 1590 | 6361 | 5317 | 11678
15:30 | 1585 | 6379.5 | 5311 | 11690.5
16:00 | 1580 | 6398 | 5305 | 11703
16:30 | 1525 | 6368 | 5262.5 | 11630.5
17:00 | 1470 | 6338 | 5220 | 11558
17:30 | 1280 | 6572.5 | 5147.5 | 11720
18:00 | 1090 | 6807 | 5075 | 11882
18:30 | 1140 | 7000.5 | 5043.5 | 12044
19:00 | 1190 | 7194 | 5012 | 12206
19:30 | 1160 | 6803 | 5065 | 11868
20:00 | 1180 | 6926 | 5110 | 12036 |  |  |  | Executive Engineer
20:30 | 1252 | 6890 | 5170.5 | 12060.5 |  |  |  | Network Operation Division
21:00 | 1324 | 6854 | 5231 | 12085
21:30 | 1342 | 6801.5 | 5169.5 | 11971
22:00 | 1360 | 6749 | 5108 | 11857 |  |  |  |  | Page 6 of 7
22:30 | 1425 | 6481.5 | 4985.5 | 11467
23:00 | 1490 | 6214 | 4863 | 11077
23:30 | 1548 | 6128 | 4820 | 10948
24:00 | 1606 | 6042 | 4777 | 10819
12206 MW (19:00 )
11355 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-03-12 |  | Energy |  | 263754365
[15 empty] | 2024-03-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3257 | 921 | 1982 | 0 | 527 | 3657 | 30 | 0 | 319 | 126 | 0 | 0 | 101
0:30 | 3204.5 | 923 | 1811.5 | 0 | 432 | 3490 | 30 | 0 | 296 | 119 | 0 | 0 | 92.0425 |  |  | Date: | 43901
1:00 | 3152 | 925 | 1641 | 0 | 337 | 3323 | 30 | 0 | 273 | 112 | 0 | 0 | 83.085
1:30 | 3120.5 | 925.5 | 1621 | 0 | 320.5 | 3276 | 30 | 0 | 272.5 | 109 | 0 | 0 | 74.0125 | [9 empty] | Total Energy | 263.7544 | 263.7544 | Total Energy Gen 263.754 MKWHr Energy Not Served 2.098 MKWHr Energy Requirement 265.852 MKWHr
2:00 | 3089 | 926 | 1601 | 0 | 304 | 3229 | 30 | 0 | 272 | 106 | 0 | 0 | 64.94 | [9 empty] | Energy not Served | 2.0977 | 2.0977
2:30 | 3170.5 | 926 | 1651 | 0 | 312.5 | 3279 | 30 | 0 | 263 | 106 | 0 | 0 | 95.0225 | [9 empty] | Energy Requirement | 265.8521 | 265.8521
3:00 | 3252 | 926 | 1701 | 0 | 321 | 3329 | 30 | 0 | 254 | 106 | 0 | 0 | 125.105
3:30 | 3235.5 | 926 | 1696.5 | 0 | 482 | 3364 | 30 | 0 | 262 | 112 | 0 | 2.5 | 106.96 | [8 empty] | Shortage
4:00 | 3219 | 926 | 1692 | 0 | 643 | 3399 | 30 | 0 | 270 | 118 | 0 | 5 | 88.815
4:30 | 3141 | 925.5 | 1636.5 | 0 | 560 | 3259.5 | 30 | 0 | 167.5 | 113 | 0 | 7 | 44.4075
5:00 | 3063 | 925 | 1581 | 0 | 477 | 3120 | 30 | 0 | 65 | 108 | 0 | 9 | 0
5:30 | 3031 | 926 | 1599.5 | 0 | 251 | 2976 | 30 | 0 | 40.5 | 99 | 0 | 8 | 14.8025
6:00 | 2999 | 927 | 1618 | 0 | 25 | 2832 | 30 | 0 | 16 | 90 | 0 | 7 | 29.605
6:30 | 3046 | 926.5 | 1633 | 0 | 57.5 | 2779.5 | 30 | 0 | 16 | 93 | 20.5 | 7 | 14.8025 | [7 empty] | Coal
7:00 | 3093 | 926 | 1648 | 0 | 90 | 2727 | 30 | 0 | 16 | 96 | 41 | 7 | 0
7:30 | 3102.5 | 855 | 1840 | 0 | 132 | 2783.5 | 30 | 0 | 24.5 | 98 | 99 | 4.5 | 22 | [6 empty] | Oil
8:00 | 3112 | 784 | 2032 | 0 | 174 | 2840 | 30 | 0 | 33 | 100 | 157 | 2 | 44
8:30 | 3185 | 784 | 2040 | 0 | 317.5 | 2884 | 30 | 0 | 41 | 100 | 211 | 1 | 82.5
9:00 | 3258 | 784 | 2048 | 0 | 461 | 2928 | 30 | 0 | 49 | 100 | 265 | 0 | 121
9:30 | 3287.5 | 784 | 2050.5 | 0 | 512.5 | 3069 | 30 | 0 | 79 | 105 | 311 | 0 | 92
10:00 | 3317 | 784 | 2053 | 0 | 564 | 3210 | 30 | 0 | 109 | 110 | 357 | 0 | 63
10:30 | 3303 | 854 | 1983.5 | 0 | 631 | 3294.5 | 30 | 0 | 129 | 112 | 388.5 | 0 | 59
11:00 | 3289 | 924 | 1914 | 0 | 698 | 3379 | 30 | 0 | 149 | 114 | 420 | 0 | 55
11:30 | 3374.5 | 924.5 | 1941.5 | 0 | 779 | 3383 | 30 | 0 | 160.5 | 112 | 431 | 0 | 56
12:00 | 3460 | 925 | 1969 | 0 | 860 | 3387 | 30 | 0 | 172 | 110 | 442 | 0 | 57
12:30 | 3451 | 925 | 1998.5 | 0 | 901.5 | 3465.5 | 30 | 0 | 185 | 120 | 429.5 | 0.5 | 101.5575
13:00 | 3442 | 925 | 2028 | 0 | 943 | 3544 | 30 | 0 | 198 | 130 | 417 | 1 | 146.115
13:30 | 3442 | 925 | 2028 | 0 | 943 | 3544 | 30 | 0 | 198 | 130 | 417 | 1 | 146.115
14:00 | 3442 | 925 | 2028 | 0 | 943 | 3544 | 30 | 0 | 198 | 130 | 417 | 1 | 146.115
14:30 | 3406.5 | 923.5 | 1976 | 0 | 865 | 3763 | 30 | 0 | 208 | 134 | 359.5 | 2.5 | 179.0625
15:00 | 3371 | 922 | 1924 | 0 | 787 | 3982 | 30 | 0 | 218 | 138 | 302 | 4 | 212.01
15:30 | 3356.5 | 922 | 1920.5 | 0 | 830 | 4021 | 30 | 0 | 222 | 134 | 249.5 | 5 | 200.0725
16:00 | 3342 | 922 | 1917 | 0 | 873 | 4060 | 30 | 0 | 226 | 130 | 197 | 6 | 188.135
16:30 | 3319 | 922 | 1892 | 0 | 934 | 3988.5 | 30 | 0 | 274.5 | 127 | 135 | 8.5 | 161.8725
17:00 | 3296 | 922 | 1867 | 0 | 995 | 3917 | 30 | 0 | 323 | 124 | 73 | 11 | 135.61
17:30 | 3223 | 922 | 1817.5 | 0 | 1375.5 | 3786.5 | 30 | 0 | 385.5 | 132 | 38 | 10 | 105.05
18:00 | 3150 | 922 | 1768 | 0 | 1756 | 3656 | 30 | 0 | 448 | 140 | 3 | 9 | 74.49
18:30 | 3304 | 924.5 | 1802 | 0 | 1729 | 3589.5 | 30 | 0 | 518 | 139 | 1.5 | 6.5 | 82.13
19:00 | 3458 | 927 | 1836 | 0 | 1702 | 3523 | 30 | 0 | 588 | 138 | 0 | 4 | 89.77
19:30 | 3165 | 779 | 1831 | 0 | 1498 | 3733 | 30 | 0 | 702 | 130 | 0 | 0 | 89.77
20:00 | 3244 | 780 | 1901 | 0 | 1417 | 3773 | 30 | 0 | 755 | 136 | 0 | 0 | 89.77
20:30 | 3249 | 780 | 2004 | 0 | 1292 | 3829.5 | 30 | 0 | 743 | 133 | 0 | 0 | 75.9225
21:00 | 3254 | 780 | 2107 | 0 | 1167 | 3886 | 30 | 0 | 731 | 130 | 0 | 0 | 62.075
21:30 | 3220 | 850.5 | 2121 | 0 | 1108.5 | 3836.5 | 30 | 0 | 672.5 | 132 | 0 | 0 | 61.0375
22:00 | 3186 | 921 | 2135 | 0 | 1050 | 3787 | 30 | 0 | 614 | 134 | 0 | 0 | 60
22:30 | 3250 | 921 | 2056.5 | 0 | 824.5 | 3764 | 30 | 0 | 488 | 133 | 0 | 0 | 79
23:00 | 3314 | 921 | 1978 | 0 | 599 | 3741 | 30 | 0 | 362 | 132 | 0 | 0 | 98
23:30 | 3285.5 | 921 | 1980 | 0 | 563 | 3699 | 30 | 0 | 340.5 | 129 | 0 | 0 | 99.5 |  |  | Max Temp. in Dhaka |  | 33.1°C
24:00 | 3257 | 921 | 1982 | 0 | 527 | 3657 | 30 | 0 | 319 | 126 | 0 | 0 | 101
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 263.754 MKWHr Energy Not Served 2.098 MKWHr Energy Requirement 265.852 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-03-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 |  |  |  | 1 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 217593
| Teknaf 20MW PP (Solartech) | [8 empty] | 15 | 18 | 19 | 19 | 19 | 16 | 13 | 8 | 2 | [9 empty] | 136080
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 205 | 205 | 205 | 205 | 204 | 205 | 206 | 207 | 208 | 207 | 207 | 207 | 207 | 206 | 206 | 208 | 206 |  | 206 | 204 | 206 | 205 | 204 | 206 | 206 | 4932168
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | [6 empty] | 17 | 34 | 34 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 859960
12 | Hathazari 100 MW peaking PP | 32 | 31 | 31 | 31 |  |  |  |  | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 33 | 32 | 32 | 32 | 495792
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 |  |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 357963
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [9 empty] | 10 | 17 | 23 | 27 | 30 | 30 | 38 | 47 | 46 |  | 46 | 46 | 38 | 15 | 15 | 15 | 15 | 411792
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 302 | 335 | 335 | 280 | 280 | 280 | 280 | 280 | 320 | 319 | 322 | 328 | 325 | 325 | 322 | 326 | 310 |  | 330 | 335 | 335 | 335 | 280 | 250 | 250 | 7429840
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 25 | 49 | 100 | 193 | 195 | 137 | 45 | 45 | 55 | 87 |  | 97 | 97 | 99 | 95 | 97 | 97 | 55 | 1490400
19 | Ashuganj 195 MW PP (APSCL-United) | [10 empty] | 16 | 16 | 55 | 55 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 151 | 151 | 149 | 150 | 150 | 140 | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 144 |  | 150 | 150 | 150 | 148 | 150 | 150 | 150 | 3546406
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 275 | 277 | 286 | 302 | 284 | 278 | 277 | 279 | 278 | 281 | 285 | 287 | 287 | 287 | 332 | 374 | 297 | 277 |  | 273 | 275 | 272 | 277 | 272 | 270 | 270 | 6921817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 46 | 46 | 46 | 46 | 46 | 30 | 30 | 44 | 44 | 44 | 44 | 44 | 45 | 44 | 43 | 43 | 44 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1043064
33 | Ashuganj 225 MW CCPP | 192 | 192 | 191 | 191 | 192 | 192 | 216 | 206 | 218 | 209 | 220 | 218 | 216 | 202 | 212 | 213 | 215 | 190 |  | 191 | 190 | 190 | 190 | 192 | 216 | 196 | 4949000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 300 | 300 | 270 | 270 | 305 | 290 | 300 | 300 | 310 | 325 | 330 | 330 | 305 | 305 | 270 | 270 |  | 305 | 270 | 270 | 270 | 270 | 345 | 305 | 7204000
| Ashuganj 450 MW CCPP(North) | [26 empty] | 0
| Ashuganj 420 MW CCPP(East) | 285 | 285 | 385 | 335 | 285 | 285 | 315 | 290 | 305 | 300 | 310 | 330 | 350 | 335 | 280 | 300 | 300 | 280 |  | 350 | 285 | 288 | 288 | 288 | 366 | 325 | 7445500
35 | Ashuganj 55 MW PP (Precision) | 20 | 15 | 5 | 5 | 5 | 5 | 5 | 14 | 46 | 52 | 53 | 52 | 50 | 48 | 47 | 46 | 47 | 48 |  | 20 | 20 | 26 | 47 | 51 | 52 | 52 | 808320
36 | Chandpur 150 MW CCPP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 3139200
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 374 | 360 | 363 | 369 | 347 | 340 | 314 | 332 | 359 | 370 | 362 | 360 | 361 | 361 | 359 | 361 | 367 | 341 |  | 370 | 365 | 361 | 359 | 359 | 359 | 336 | 8647200
Meghnaghat Unique power
| Summit Meghanghat-2 589 MW(Gas) | 350 | 350 | 380 | 380 | 370 | 400 | 430 | 500 | 450 | 450 | 450 | 450 | 350 | 350 | 300 | 300 | 300 | 300 |  | 300 | 350 | 400 | 520 | 540 | 540 | 590 | 9570455
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 350 | 350 | 350 | 350 | 350 | 360 | 360 | 360 | 360 | 360 | 380 | 380 | 400 | 400 | 400 | 400 |  | 450 | 430 | 400 | 380 | 370 | 330 | 330 | 8363000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 66 | 68 | 66 | 67 | 68 | 68 | 34 | 32 | 33 | 33 | 33 | 32 | 32 | 32 | 31 | 31 | 28 | 28 |  | 31 | 38 | 56 | 72 | 74 | 74 | 69 | 1120320
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 17 | 30 | 41 | 47 | 48 | 46 | 39 | 28 | 17 | 6 | 0 | [8 empty] | 326250
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1007000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 20 | 28 | 28 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 649920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 62 | 62 | 40 | 61 | 60 | 60 | 59 | 59 | 40 | 20 |  | 20 | 20 | 20 | 20 | 20 | 32 | 63 | 985056
48 | Shahjibazar 86 MW PP (Shahjibazar)
| Shahjibazar 100 MW GTPP | [16 empty] | 90 | 98 |  | 95 | 100 | 100 | 100 | 80 | 0 |  | 491091
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 209 | 209 | 209 | 215 | 215 | 216 | 215 | 209 | 209 | 209 | 206 | 203 | 200 | 200 | 200 | 200 | 205 |  | 206 | [5 empty] | 80 | 3654940
51 | Sylhet 20 MW GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 |  | 16 | 18 | 18 | 18 | 18 | 20 | 20 | 467000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 224640
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | [21 empty] | 40 | 53 | 53 | 53 | 22 | 214200
56 | Shahjahanulla 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 16 | 363168
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 290 | 300 | 290 | 250 | 260 | 285 | 310 | 315 | 315 | 290 | 300 | 315 | 320 | 305 | 300 | 300 | 295 |  | 275 | 300 | 280 | 280 | 295 | 310 | 325 | 7245000
| Bibiyana South 400 MW | 205 | 180 | 180 | 180 | 180 | 180 | 210 | 185 | 205 | 206 | 201 | 240 | 240 | 220 | 260 | 260 | 225 | 205 |  | 205 | 205 | 260 | 260 | 260 | 260 | 260 | 5232700
58 | Nababganj 55 MW PP (Southern power ) |  |  |  | 30 | [13 empty] | 55 |  | 55 | 55 | 55 | 55 | 55 | 0 |  | 315386
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 1 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 45120
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237360
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 112 | 106 | 106 | 118 | 108 | 90 | 96 | 100 | 100 | 110 | 114 | 110 | 130 | 140 | 138 | 130 | 124 | 140 |  | 138 | 130 | 136 | 130 | 134 | 132 | 126 | 2808960
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 40 | 40 | 38 | 13 | 17 | 15 | 16 | 11 | 12 | 16 | 2 | 0 | 0 | 15 | 19 |  | 22 | 22 | 25 | 28 | 28 | 29 | 31 | 556800
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 9 | 9 | 9 |  | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 217080
67 | Jangalia 33 MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 610600
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 422350
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 408000
70 | Summit Madhabdi | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 14 | 14 | 0 | 21 | 21 | 14 |  | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 350640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817920
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 269800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 70 | 34 | 34 | 64 |  |  |  | 15 | 114 | 98 | 98 | 98 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 59 | 55 | 17 | 17 | 52 | 114 | 1606260
| Chowmuhani 113 MW | 15 | 9 | 9 | 9 |  |  |  |  | 6 | 9 | 10 | 41 | 48 | 48 | 57 | 60 | 67 | 77 |  | 78 | 27 | 26 | 17 | 9 | 9 | 9 | 661920
| Manikgonj 162MW PP(MPGL) |  |  | 17 | 130 | 108 | [10 empty] | 17 | 35 | 144 |  | 162 | 162 | 162 | 162 | 162 | 0 |  | 1090080
77 | Siddhirganj 100 PP(Dutch Bangla) |  |  |  | 6 | [10 empty] | 3 | 9 | 9 | 9 | [8 empty] | 37440
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 224160
79 | Kodda 150 MW PP | 32 | 32 | 16 | 32 | 48 | 16 | 16 | 16 | 16 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 146 |  | 147 | 147 | 147 | 148 | 149 | 48 | 16 | 1498560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 |  |  | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 184954
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105 |  | 105 | 70 | 70 | 35 | 35 | 35 | 35 | 624000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 29160
| Jodiac Power | [15 empty] | 7 | 17 | 17 |  | 17 | 17 | [5 empty] | 74875
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 |  |  |  | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 5 | 17 | 350430
82 | Madanganj 102 PP(Summit) |  |  |  | 6 | 10 |  |  |  |  | 5 | 70 | 85 | 85 | 85 | 65 | 65 | 85 | 85 |  | 42 | 16 | 7 |  |  |  |  | 617847
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) |  |  |  | 16 | [5 empty] | 12 | 13 | 13 | 13 | 24 | 24 | 24 | 24 | 24 | [8 empty] | 186321
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 7 | 9 | 9 | 8 | [11 empty] | 32640
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 |  |  | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 364800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) |  |  |  | 25 | [5 empty] | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | [8 empty] | 318000
92 | Fenchuganj 44 MW (Energyprima) | [21 empty] | 21 | 39 | 38 | 44 | 0 | 129816
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 10 | [6 empty] | 698448
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 197280
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 212640
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [8 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 7 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 209940
100 | Manikganj 55 MW PP (Northern) |  |  |  | 35 | 35 | [12 empty] | 32 |  | 35 | 35 | 35 | 35 | 35 | 0 |  | 205593
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 163 | 163 | 163 | 163 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3607445
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 14550
103 | Kamalaghat 54 MW PP(Banco Energy) |  |  |  | 35 | 54 | [12 empty] | 54 |  | 54 | 54 | 54 | 54 | 54 | 0 |  | 349200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) |  | 9 | 9 | 9 | 9 |  | 56 | 56 | 56 | 60 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 95 |  | 97 | 97 | 97 | 97 | 97 | 19 | 19 | 1200000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 35 | 35 | 35 | 35 | 101 |  | 101 | 97 | 97 | 79 | 79 | 80 | 80 | 1004544
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 |  |  | 1 | 12 | 12 | 18 | 18 | 22 | 22 | 22 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 307200
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 |  |  | 1 | 30 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 756000
117 | Ashuganj 150 MW PP (Midland) | 6 | 6 | 6 | 5 | 6 |  |  | 2 | 5 | 6 | 6 | 6 | 5 | 2 | 2 | 3 | 6 | 6 |  | 5 | 8 | 6 | 6 | 6 | 5 | 6 | 122109
118 | Bibiyana-III 400 MW CCPP | 318 | 321 | 316 | 316 | 306 | 306 | 336 | 328 | 360 | 365 | 365 | 418 | 330 | 386 | 367 | 350 | 318 | 318 |  | 362 | 318 | 318 | 318 | 318 | 372 | 328 | 8243000
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 0 | 9 | 9 | 9 | 9 | 9 | [15 empty] | 92400
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 |  |  | 32 | 49 | 49 | 52 | 68 | 68 | 70 | 69 | 69 | 69 | 103 |  | 103 | 105 | 106 | 16 | 16 | 16 | 16 | 1036255
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 269760
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 |  |  | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 377618
| Bhairob 54.5 MW | [12 empty] | 6 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  | 3 | 17 | 17 | 17 | 187200
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 12 | 18 | 24 | 27 | 30 | 30 | 27 | 20 | 14 | 5 | [9 empty] | 206501
| Chandpur 115(Doreen) |  |  |  | 27 | 34 | [11 empty] | 11 | 62 |  | 93 | 93 | 94 | 94 | 94 | 68 |  | 592320
| Kanchan Purbachal Power Generation Ltd. | [16 empty] | 10 | 17 |  | 17 | 17 | 17 |  |  |  |  | 68400
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 |  |  | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 55 | 132 | 162 | 162 | 162 | 17 | 17 | 914981
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 5 | 9 | 7 | 7 | 2 | 0 | 0 | 0 | 0 | 1 | 3 | 4 | 6 | 11 | 9 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 70080
| Sonagazi 75 MW Solar Plant | [6 empty] | 9 | 24 | 41 | 49 | 60 | 61 | 56 | 54 | 40 | 24 | 8 | 0 | [8 empty] | 430310
| Matarbari 2*600 MW (CPGCL) | 452 | 452 | 504 | 501 | 505 | 450 | 405 | 405 | 403 | 404 | 401 | 402 | 456 | 455 | 505 | 504 | 502 | 430 |  | 575 | 575 | 575 | 574 | 504 | 504 | 504 | 11229090
120 | Eastern Zone Total | 5453 | 5358 | 5574 | 5891 | 5430 | 4876 | 5039 | 5308 | 5776 | 6042 | 6173 | 6503 | 6605 | 6558 | 6361 | 6398 | 6338 | 6807 |  | 7194 | 6803 | 6926 | 6854 | 6749 | 6214 | 6042 | 148560305
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 6 | 6 |  | 10 | 30 | 52 | 45 | 0 |  |  | 86880
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | [11 empty] | 2 | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 170880
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 7 | 28 | 24 | 35 | 44 | 47 | 39 | 64 | 41 | 35 | 13 | 1 | [8 empty] | 406800
131 | Rampal 1320 MW (BIFPCL) | 400 | 383 | 419 | 419 | 391 | 390 | 390 | 389 | 386 | 388 | 385 | 386 | 385 | 405 | 423 | 458 | 434 | 462 |  | 429 | 446 | 442 | 443 | 394 | 386 | 386 | 10058180
132 | United Payra Power Ltd. | [17 empty] | 23 |  | 54 | 35 | [5 empty] | 100800
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 180 |  | 220 | 220 | 220 | 220 | 220 | 18 | 30 | 4648718
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 32 |  | 32 | 48 | 48 | 48 | 0 |  |  | 153312
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 134 | 134 | 134 | 80 | 100 | 130 | 130 | 130 | 80 | 80 | 80 |  | 130 | 130 | 134 | 130 | 130 | 130 | 130 | 2517000
140 | Bhola 33 MW PP (Venture) | 7 | 7 | 7 | 7 | 6 | 5 | 5 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 5 | 6 | 7 |  | 8 | 8 | 8 | 9 | 9 | 7 | 7 | 147727
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 40 | 71 |  | 64 | 65 | 66 | 66 | 0 |  |  | 272384
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 925 | 926 | 926 | 926 | 925 | 927 | 926 | 784 | 784 | 784 | 924 | 925 | 925 | 922 | 922 | 922 | 922 | 922 |  | 927 | 779 | 780 | 780 | 921 | 921 | 921 | 21620363
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 740 | 700 | 760 | 880 | 800 | 700 | 620 | 600 | 600 | 680 | 790 | 800 | 900 | 1080 | 1120 | 1120 | 1080 | 980 |  | 760 | 880 | 920 | 1030 | 1000 | 1060 | 1000 | 22972500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4874700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 34 | 34 | 34 | 34 | [15 empty] | 26 | 26 | 26 | 26 | 17 | 17 | 17 | 250516
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 34440
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 140 | 140 | 149 | 158 | 161 | 130 | 130 | 138 | 149 | 154 | 192 | 211 | 210 | 207 | 206 | 203 | 175 | 148 |  | 146 | 190 | 191 | 194 | 196 | 196 | 196 | 4452355
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 250 | 200 | 300 | 300 | 240 | 240 | 240 | 414 | 414 | 414 | 370 | 414 | 414 | 414 | 414 | 414 | 380 | 320 |  | 350 | 300 | 300 | 350 | 350 | 414 | 414 | 8413818
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 15 | 20 | 24 | 27 | 27 | 24 | 95762
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 114624
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [11 empty] | 8 | 42 | 42 | 42 | 42 | 42 | 42 | [8 empty] | 228316
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 30 | 30 | [8 empty] | 6 | 16 | 24 | 24 | 24 | 37 |  | 50 | 50 | 50 | 50 | 50 | 48 | 40 | 463737
168 | Santahar 50 MW Peaking PP | [19 empty] | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 149160
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 75 | 75 | 75 | 75 | [12 empty] | 42 | 42 |  | 74 | 80 | 83 | 83 | 83 | 83 | 83 | 830752
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 10 | 35 |  | 35 | 35 | 35 |  |  |  |  | 134880
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 35 | 35 | 35 |  | 35 | [6 empty] | 136320
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 6 | 6 | 6 | 6 | 6 |  |  |  | 33 | 33 | 35 | 28 | 35 | 11 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 276729
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 7 | 6 | 6 | 5 | 3 | 2 | 0 | [8 empty] | 43272
178 | Energypac Power Venture Thakurgaon Ltd. | [15 empty] | 35 | 55 | 115 |  | 115 | 115 | 115 | 115 | 55 | 0 |  | 640896
| Intraco Solar 30 MW | [6 empty] | 2 | 11 | 21 | 28 | 34 | 36 | 34 | 31 | 27 | 16 | 6 | 0 | [8 empty] | 245645
| Adani Power Jharkhanda Ltd | 1256 | 1217 | 1160 | 1097 | 940 | 814 | 835 | 967 | 1061 | 1257 | 1318 | 1312 | 1316 | 1314 | 1402 | 1404 | 1404 | 1307 |  | 1286 | 1357 | 1364 | 1362 | 1417 | 1321 | 1297 | 29388594
178 | Teesta Solar Limited | [6 empty] | 15 | 60 | 107 | 149 | 173 | 184 | 176 | 163 | 121 | 76 | 31 | 2 | [8 empty] | 1264000