## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:January 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-01-31 |  | 2023-12-01 |  | 2023-01-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10717 | 2024-01-29 | 10921 | 2023-12-04 | 10330 | 2023-01-30 | 15648 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 4997 | 2024-01-08 | 5635 | 2023-12-17 | 5671 | 2023-01-07 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10717 | 2024-01-29 | 10921 | 2023-12-04 | 10330 | 2023-01-30 | 15648 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 10109 | 2024-01-31 | 9618 | 2023-12-28 | 9332 | 2023-01-29 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10717 | 2024-01-29 | 10921 | 2023-12-30 | 10496 | 2023-01-30 | 16096 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 10054.129 |  | 9939.1935 |  | 9608.0645 |  | - | -
7 | Average Generation (MW) at Day Peak | 9271.871 |  | 8800.1935 |  | 8465.7742 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 935 | 2024-01-31 | 928 | 2023-12-02 | 927 | 2023-01-01 | 956 | 27/3/2019
|  |  | 14:30 |  | 1:00 |  | 18:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 124 | 2024-01-26 | 134 | 2023-12-04 | 136 | 2023-01-28 | 194 | 12/06/19
|  |  | 13:00 |  | 17:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 617 | 2024-01-20 | - | - | 952 | 2023-01-09 | 4395 | 04/10/2022
|  |  | 20:00 |  |  |  | 20:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 9794 | 2024-01-20 | - | - | 8939 | 2023-01-09 | 13200 | 04/10/2022
|  | - | 20:00 |  |  | - | 20:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-01-19 | - | - | 0 | 2023-01-07 | - | -
|  |  | 19:00 |  |  |  | 19:30 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 9530 | 2024-01-19 | - | - | 9795 | 2023-01-07 | - | -
|  |  | 19:00 | - | - |  | 19:30 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 732 | 2024-01-21 | - | - | 944 | 2023-01-09 | - | -
|  |  | 12:00 | - | - |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 9133 | 2024-01-21 | - | - | 7776 | 2023-01-09 | - | -
|  |  | 12:00 | - | - |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-01-21 | - | - | 0 | 2023-01-07 | - | -
|  |  | 12:00 | - | - |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 9087 | 2024-01-21 | - | - | 7958 | 2023-01-07 | - | -
|  |  | 12:00 | - | - |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 2 |  | - | - | 22 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 13 |  | - | - | 22 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1567.6156 |  | 1616.4983 |  | 1441.7073 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 35.6059 |  | 31.8652 |  | 47.6227 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1532.0097 |  | 1584.6331 |  | 1394.0845 |  | - | -
23 | Net Generation of IPP (MKWH) | 3270.8678 |  | 2407.5536 |  | 3451.6051 |  | - | -
24 | Net Generation of REB (MKWH) | 94.171 |  | 75.7392 |  | 122.7522 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 151.7108 |  | 78.4238 |  | 264.3287 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5048.7594 |  | 4146.3497 |  | 5232.7705 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 2952.1447 |  | 3078.1257 |  | 3400.0318 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 12.5617 |  | 8.2293 |  | 52.972 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 589.0162 |  | 366.9347 |  | 946.5709 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 55.9314 |  | 62.1719 |  | 22.1863 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 29.1038 |  | 32.3549 |  | 29.9075 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 699.1873 |  | 700.7034 |  | 828.7249 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 593.312 |  | 585.1283 |  | 647.0711 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 75.2028 |  | 74.6495 |  | 87.0884 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:January 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10717 | 2024-01-29 | 19:00
Generation Period
| Dhaka | MW | 3726.37
| Chattogram | MW | 947.5
| Cumilla | MW | 858
| Mymensingh | MW | 944
| Sylhet | MW | 362
a) | Total supply in East zone | MW | 6837.87
| Khulna | MW | 1196
| Barisal | MW | 285.5
| Rajshahi | MW | 1063.8
| Rangpur | MW | 782
b) | Total supply in West zone | MW | 3327.3
c) | Total supply in both zone ( a+b) | MW | 10165.17
Ref: | 27.21.0000.603.16.087.20.766 | Date: 18/02/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:January 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 210 | 2024-01-12 | 9:00
| b) Ishurdi end | MW | 358 | 2024-01-20 | 14:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 850 | 2024-01-20 | 13:00
| b) Ishurdi end | MW | 72 | 2024-01-13 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.77092
| b) Ishurdi end | MKWH | 92.7143
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 89.9328
| b) Ishurdi end | MKWH | 0.74847
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 240 | 2024-01-14 | 19:30
| b)Serajganj end | MW | 670 | 2024-01-20 | 14:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 390 | 2024-01-20 | 14:00
| b)Sirajganj end | MW | 30 | 2024-01-15 | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.039
| b)Sirajganj end | MKWH | 233.456
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 226.685
| b)Sirajganj end | MKWH | 0.042
30 | Transmission loss of EWI /NO-2 | % | 2.899'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 1898 | 2023-01-20 | 13:00
|  | MW | 1280
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 1876 | 2023-01-20 | 14:30
|  | MW | 1276
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 28696 | 2023-01-20 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 28668 | 1/20/2023
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 449276
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 449810
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | -0.118
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: January 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-01-20 16:55 | 2024-01-20 18:36 | 1:41 | E/O | Maintenance work on ATR-2 Bus-2 Isolator | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2024-01-17 11:36 | 2024-01-17 12:32 | 0:56 | E/O | Trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2024-01-17 13:08 | 2024-01-17 14:53 | 1:45 | E/O | Trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2024-01-20 16:01 | 2024-01-20 18:38 | 2:37 | E/O | Redhot Maintenance work on ATR-2 Bus-2 Isolator | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 HT | 2024-01-17 11:36 | 2024-01-17 12:32 | 0:56 | E/O | Trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 HT | 2024-01-17 13:08 | 2024-01-17 14:53 | 1:45 | E/O | Trip | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 LT | 2024-01-17 15:04 | 2024-01-17 15:52 | 0:48 | E/O | HT side Y-phase bushing red-hot problem | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-01-28 11:06 | 2024-01-28 11:44 | 0:38 | T | 33kv sk vita -1 feeder C.T burst. | 36 | 22.8 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-01-28 20:27 | 2024-01-28 23:35 | 3:08 | E/O | 33 kv bus coupler red hot maintenance. | 20 | 62.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-01-11 12:10 | 2024-01-11 15:24 | 3:14 | E/O | Shutdown taken DPBS-1 due to 33KV Ashuliya feeder Bus DS maintenance purpose | 95 | 307.1667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 LT | 2024-01-11 06:32 | 2024-01-11 07:22 | 0:50 | T | Epz 33kv feeder ct y phase brunt,auxilary-1 y phase bushing brunt,Ashulia 33 kv feeder CB do not trip but relay shows O/C,E/F signal | 88 | 73.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-01-08 13:03 | 2024-01-08 14:30 | 1:27 | E/O | T-1&T-2 33kv Bus DS Red-hot maintenance | 80 | 116 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-01-08 13:04 | 2024-01-08 14:32 | 1:28 | E/O | 33kv T-1&T-2 Bus section DS Red-hot maintenance | 80 | 117.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I LT | 2024-01-11 06:32 | 2024-01-11 07:22 | 0:50 | T | Epz 33kv feeder ct y phase brunt,relay panel shows o/c,e/f,auxilary-1 y phase bushing brunt,ashulia 33kv feeder cb do not trip but relay show o/c,e/f signal | 88 | 73.3333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2024-01-05 22:26 | 2024-01-05 22:34 | 0:08 | T | U/F | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-01-02 11:38 | 2024-01-02 11:53 | 0:15 | T | PBS square feeder trip for earth fault | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 LT | 2024-01-22 12:50 | 2024-01-22 13:10 | 0:20 | T | 33 KV Bus-B grounded by DPBS-3 during shutdown process of L-39 Feeder. | 41 | 13.6667 | Power interruption
Savar 132/33kV Grid Sub-Station | T-2 LT | 2024-01-22 12:50 | 2024-01-22 13:10 | 0:20 | T | 33 KV Bus-B grounded by DPBS-3 during shutdown process of L-39 Feeder. | 41 | 13.6667 | Power interruption
Savar 132/33kV Grid Sub-Station | T-3 LT | 2024-01-22 12:50 | 2024-01-22 13:10 | 0:20 | T | 33 KV Bus-B grounded by DPBS-3 during shutdown process of L-39 Feeder. | 48 | 16 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-01-02 12:11 | 2024-01-02 12:36 | 0:25 | E/O | 33kv T-1 x-former energy meter changed by BPDB. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-02 LT | 2024-01-25 17:10 | 2024-01-26 01:44 | 8:34 | E/O | CT maintenance work | 0 | 0 | No interruption
|  |  | Total : | 32:25 |  | Unserved Energy: |  | 815.9667
Dhaka (South) Grid Circle :
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2024-01-03 15:45 | 2024-01-03 18:15 | 2:30 | E/O | 132 kv main bus isolator box replacement. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 LT | 2024-01-03 17:22 | 2024-01-03 17:52 | 0:30 | T | Trip | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-1 LT | 2024-01-13 07:32 | 2024-01-13 08:58 | 1:26 | T | Trip | 5 | 7.1667 | Power interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-2 HT | 2024-01-23 12:28 | 2024-01-23 13:51 | 1:23 | T | As the oil level in the OLTC drops. | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-3 HT | 2024-01-05 03:58 | 2024-01-05 04:02 | 0:04 | T | Restricted Earth Fault( Due to Heavy Earth Fault on Green Road 33 KV U/G Cable Feeder in short distance) | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-01-09 15:06 | 2024-01-09 17:05 | 1:59 | E/O | Maintenance work by PBS.New feeder cable connect to the 33kv bus section-02. | 15 | 29.75 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-01-02 11:30 | 2024-01-02 16:34 | 5:04 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 12:56 |  | Unserved Energy: |  | 36.9167
Chattogram Grid Circle :
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) HT | 2024-01-27 20:37 | 2024-01-27 21:05 | 0:28 | E/O | Due to T-1(403T) BPDB incomer R(Ph) cable nut bolt red hot | 11 | 5.1333 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2024-01-30 14:21 | 2024-01-30 14:21 | 0:00 | T | 33 KV SIDE CABLE PUNCTURE. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2024-01-30 14:30 | 2024-01-30 16:20 | 1:50 | E/O | B-phase cable puncture. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-01-21 12:00 | 2024-01-21 13:13 | 1:13 | E/O | Redhot maintainance by bpdb | 0 | 0 | No interruption
|  |  | Total : | 3:31 |  | Unserved Energy: |  | 5.1333
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV BUS-1 | 2024-01-21 14:12 | 2024-01-21 16:06 | 1:54 | E/O | For tightening loop of line 1 riser. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-01-18 16:48 | 2024-01-18 16:56 | 0:08 | E/O | 25/41 MVA Transformer draw under tr-03 33KV overhead line | 10 | 1.3333 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 200KVA Aux. T-1 LT | 2024-01-11 12:15 | 2024-01-19 08:20 | 188:05 | E/O | Auxiliary source replaced | 0 | 0 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T LT | 2024-01-09 17:50 | 2024-01-09 18:10 | 0:20 | T | Over current inst trip | 14 | 4.6667 | Power interruption
|  |  | Total : | 190:27 |  | Unserved Energy: |  | 6
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-01-04 14:46 | 2024-01-04 14:52 | 0:06 | T | 33 kV Nolcity (WZPDCL) feeder fault. | 65 | 6.5 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-01-18 11:18 | 2024-01-18 11:29 | 0:11 | T | 33kV Nolcity WZPDCL Feeder Fault | 40 | 7.3333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-01-04 14:46 | 2024-01-04 14:52 | 0:06 | T | 33 kV Nolcity (WZPDCL) feeder fault. | 65 | 6.5 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-01-18 11:18 | 2024-01-18 11:28 | 0:10 | T | 33kV Nolcity WZPDCL Feeder Fault | 25 | 4.1667 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-01-05 13:10 | 2024-01-05 18:45 | 5:35 | E/O | LA burn 33 KV side | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-01-01 07:17 | 2024-01-01 09:29 | 2:12 | E/O | Bpbs Red hot maintenance | 15 | 33 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 LT | 2024-01-10 11:50 | 2024-01-10 12:44 | 0:54 | E/O | Oil Refill OLTC tank | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-01-20 13:01 | 2024-01-20 14:52 | 1:51 | E/O | Breaker Gas leckage | 0 | 0 | No interruption
|  |  | Total : | 11:05 |  | Unserved Energy: |  | 57.5
HVDC Grid Circle :
BIPTC | 400kV Bus-2 | 2024-01-29 14:55 | 2024-01-29 16:06 | 1:11 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) HT | 2024-01-23 15:29 | 2024-01-23 17:49 | 2:20 | E/O | Red hot maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2024-01-25 18:42 | 2024-01-25 19:25 | 0:43 | E/O | for securty reason from fire | 23 | 16.4833 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2024-01-25 18:40 | 2024-01-26 23:19 | 28:39 | T | fire is seen on the 132/33 v xformer | 25 | 716.25 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-01-23 08:14 | 2024-01-23 08:39 | 0:25 | E/O | Emergency Maintenance. | 20 | 8.3333 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-01-29 07:48 | 2024-01-29 08:02 | 0:14 | T | Tripped showing O/C DMT-1,E/F DMT-1 relays. | 30 | 7 | Power interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer -1 HT | 2024-01-04 15:34 | 2024-01-04 16:59 | 1:25 | T | PBS Station Auxiliary X-Fomer primary loop wire Insulation Breakdown. | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer-2 LT | 2024-01-27 13:23 | 2024-01-27 13:44 | 0:21 | E/O | PBS 33KV Feeder Caught fire | 0 | 0 | No interruption
|  |  | Total : | 35:18 |  | Unserved Energy: |  | 748.0667
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2024-01-13 13:36 | 2024-01-13 15:27 | 1:51 | E/O | DS finger maintenance | 0 | 0 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2024-01-05 16:17 | 2024-01-05 17:20 | 1:03 | E/O | Red hot Maintanance | 16 | 16.8 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2024-01-19 16:05 | 2024-01-19 17:45 | 1:40 | E/O | Red Hot | 13 | 21.6667 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-01-21 16:55 | 2024-01-21 19:02 | 2:07 | E/O | 132KV circuit breaker hydrolic oil leakage maintenance work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2024-01-08 09:55 | 2024-01-08 15:09 | 5:14 | E/O | Aux-1 CB and DS Maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) HT | 2024-01-29 16:58 | 2024-01-29 17:17 | 0:19 | T |  | 30 | 9.5 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) HT | 2024-01-04 15:20 | 2024-01-04 16:15 | 0:55 | E/O | Electrical clearance for T-2(50/75) transformer shifting | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2024-01-16 07:31 | 2024-01-16 09:55 | 2:24 | E/O | Due to emergency maint. Of 33 kV Bus | 60 | 144 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) LT | 2024-01-16 07:33 | 2024-01-16 09:58 | 2:25 | E/O | Due to emergency maint. Of 33 kV Bus | 60 | 145 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2024-01-15 11:57 | 2024-01-16 16:34 | 28:37 | T | Cp Signal:1. SF6 Gass Low Alarm 2. Sf6 Gas Locking Alarm Rp Signal:1. Main BCHZ Trip 2. OLTC BCHZ Trip 3. Main PRD Trip 4. OLTC PRD Trip 5 OTI Trip 6. WTI Trip. only HV Side relay Operated LV Side relay has no signal but both HV & LV CB Open | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-01-24 11:51 | 2024-01-24 12:38 | 0:47 | E/O | Due to TRTUD work(IED repalcement work). | 0 | 0 | No interruption
|  |  | Total : | 47:22 |  | Unserved Energy: |  | 336.9667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 333:04 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [9 empty] | 498.6333
Month: January 2024 | [9 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-01-24 06:16 | 2024-01-24 06:38 | 0:22 | T | Trip as Meghnaghat End | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2024-01-01 15:21 | 2024-01-01 15:48 | 0:27 | E/O | Due to emergency maint. Work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-01-08 10:29 | 2024-01-08 16:40 | 6:11 | T | Tripped showing SOTF | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-01-17 12:44 | 2024-01-17 14:10 | 1:26 | E/O | Removing rope from 132kV Kaliakair ckt-1. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-01-25 02:17 | 2024-01-25 02:17 | 0:00 | T | CB-1002B ,Pole discrepancy | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 2024-01-26 10:23 | 2024-01-26 11:27 | 1:04 | E/O | Kodda end working ordered by NLDC. | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-2 | 2024-01-26 11:39 | 2024-01-26 12:19 | 0:40 | E/O | Kodda end working ordered by NLDC. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2024-01-25 19:15 | 2024-01-27 13:12 | 41:57 | E/O | 132 kV Tie CT maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 52:07 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-01-18 05:17 | 2024-01-18 05:50 | 0:33 | T |  | 0 | 0 | No interruption |  | 120.3333 | 251.2167
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-01-29 10:05 | 2024-01-29 18:30 | 8:25 | E/O | For Overload | 0 | 0 | Power interruption |  | 14.7833
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-01-30 01:03 | 2024-01-30 17:18 | 16:15 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-01-28 12:10 | 2024-01-28 12:25 | 0:15 | T |  | 200 | 50 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-01-16 10:27 | 2024-01-16 14:43 | 4:16 | E/O | Work on other side. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-01-28 18:04 | 2024-01-28 18:47 | 0:43 | T |  | 8 | 5.7333 | Power interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-01-30 09:56 | 2024-01-30 17:16 | 7:20 | E/O | Dead line check and hydraulic oil pipe change of CB cabinet. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-01-20 00:30 | 2024-01-20 07:24 | 6:54 | E/O | For Load management purpose Order by NLDC. (Due to Fatulla CKT overload) | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-01-20 00:34 | 2024-01-20 07:09 | 6:35 | E/O | For Load management purpose Order by NLDC. (Due to Fatulla CKT overload 600 Amp) | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 102 MW 132 kv Ckt | 2024-01-20 04:44 | 2024-01-21 12:24 | 31:40 | T | Under ground cable Fault | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2024-01-20 04:44 | 2024-01-20 05:26 | 0:42 | T | Under ground cable Fault | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-01-09 10:02 | 2024-01-09 16:13 | 6:11 | E/O | Ordered by NLDC for load management purpose | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2024-01-03 19:40 | 2024-01-03 21:18 | 1:38 | E/O | Sky wire is torn at Matuail to Siddhirgonj end. | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132 kV Siddhirgonj | 2024-01-24 04:20 | 2024-01-24 11:53 | 7:33 | T | None | 39 | 294.45 | Power interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-01-03 00:23 | 2024-01-03 00:49 | 0:26 | T | Due to Dense Fog | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-01-03 02:28 | 2024-01-03 17:45 | 15:17 | T | Due to dense fog. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-01-18 01:50 | 2024-01-18 02:01 | 0:11 | T | Disdtance relay | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-01-18 02:15 | 2024-01-18 15:12 | 12:57 | T | Distance relay | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-02 | 2024-01-17 03:59 | 2024-01-17 04:10 | 0:11 | T | Due to dense fog. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-01-18 09:04 | 2024-01-18 10:06 | 1:02 | E/O | Remove nest from Tower | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2024-01-04 11:21 | 2024-01-04 14:49 | 3:28 | E/O | à¦à¦¨à¦¾à¦°à§à¦œà¦¿ à¦®à¦¿à¦Ÿà¦¾à¦° à¦¸à¦®à¦¸à§à¦¯à¦¾ à¦¸à¦®à¦¾à¦§à¦¾à¦¨ à¦à¦° à¦œà¦¨à§à¦¯ | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2024-01-31 09:40 | 2024-01-31 16:08 | 6:28 | E/O | Shutdown for NLDC | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-01 | 2024-01-01 17:55 | 2024-01-01 21:03 | 3:08 | E/O | Shutdown for NLDC | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Fatullah-1(E06) | 2024-01-26 08:59 | 2024-01-26 11:50 | 2:51 | E/O | Due to load manage in Maghnaghat line. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Fatullah-2(E05) | 2024-01-26 08:55 | 2024-01-26 11:49 | 2:54 | E/O | Due to load manage in 230 kv Maghnaghat line | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-01-26 09:41 | 2024-01-26 16:40 | 6:59 | E/O | Due to load manage in Maghnaghat line. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Hasnabad-1(D02) | 2024-01-26 09:24 | 2024-01-26 16:40 | 7:16 | E/O | Due to load manage in Maghnaghat line. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-1(D06) | 2024-01-18 10:38 | 2024-01-18 15:08 | 4:30 | E/O | cleanning insulator disc of tower 22 & 23 | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-01-03 13:00 | 2024-01-03 13:00 | 0:00 | T | Pot head LA Fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-01-03 14:15 | 2024-01-08 16:54 | 122:39 | E/O | L.A Change | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-01-03 13:00 | 2024-01-03 13:24 | 0:24 | T | External fault ( At the same time dutch bangla line goes trip) | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-01-03 15:39 | 2024-01-03 16:01 | 0:22 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-01-24 04:19 | 2024-01-24 07:23 | 3:04 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-01-01 14:05 | 2024-01-01 16:31 | 2:26 | E/O | 132 kV TR oil top up | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-01-22 13:23 | 2024-01-22 15:59 | 2:36 | E/O | EEGCT GT-2 lube oil leakage checking | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-01-29 09:41 | 2024-01-29 17:05 | 7:24 | E/O | Maintenance work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-01-31 09:52 | 2024-01-31 16:51 | 6:59 | E/O | Air leakage maintenance bus duct line. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2024-01-07 10:16 | 2024-01-07 11:22 | 1:06 | T | Over Voltage | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2024-01-07 14:12 | 2024-01-07 14:47 | 0:35 | T | Over voltage | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2024-01-08 02:05 | 2024-01-08 10:40 | 8:35 | T | Over voltage | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-01-02 07:37 | 2024-01-04 10:21 | 50:44 | T | CB Lockout | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-01-07 10:16 | 2024-01-07 11:28 | 1:12 | T | Over voltage | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-01-07 14:12 | 2024-01-07 14:47 | 0:35 | T | Over Voltage | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-01-03 13:01 | 2024-01-05 11:35 | 46:34 | T | Due to Fault of Transformer | 10 | 465.6667 | Power interruption
|  |  | Total : | 421:53 |  | Unserved Energy: |  | 815.85
Chattogram Grid Circle :
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-1 | 2024-01-30 09:29 | 2024-01-30 16:44 | 7:15 | E/O | Due to unbalanced current flow | 0 | 0 | No interruption
|  |  | Total : | 7:15 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-01-15 15:58 | 2024-01-15 20:38 | 4:40 | E/O |  | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-01-13 09:55 | 2024-01-13 16:14 | 6:19 | E/O | Annual maintenance and death line check. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-01-10 12:46 | 2024-01-10 17:50 | 5:04 | E/O | Distance relay failure problem maintenance by SPMD. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-01-12 06:48 | 2024-01-12 22:33 | 15:45 | E/O | work for cumilla end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-01-13 08:45 | 2024-01-13 20:03 | 11:18 | E/O | for maintenance work at cumilla(N) ss | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-01-22 11:43 | 2024-01-22 17:47 | 6:04 | E/O | ordered by NLDC | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-01-12 06:50 | 2024-01-12 22:33 | 15:43 | E/O | work for cumilla end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-01-13 08:45 | 2024-01-13 20:04 | 11:19 | E/O | for maintenance work at cumilla(N) ss | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-01-22 11:43 | 2024-01-22 17:47 | 6:04 | E/O | ordered by NLDC | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-01-24 09:08 | 2024-01-24 09:08 | 0:00 | E/O |  | 0 | 0 | No interruption
|  |  | Total : | 82:16 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-01 | 2024-01-29 10:04 | 2024-01-29 12:39 | 2:35 | E/O | Oil leakage repair of B-phase CT | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Magura 1 | 2024-01-08 02:27 | 2024-01-08 07:56 | 5:29 | E/O | Due to high voltage, as per instruction by ALDC khulna magura ckt 01 shutdown. No load interruption. | 0 | 0 | No interruption
|  |  | Total : | 8:04 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2024-01-03 16:28 | 2024-01-03 17:06 | 0:38 | T | PT MCB Failed | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Bghabari-2 | 2024-01-19 20:25 | 2024-01-20 15:27 | 19:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 19:40 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-01 | 2024-01-02 05:14 | 2024-01-02 05:54 | 0:40 | T | 33kv Patgram Feeder 33Kv BUS D/S Fault | 12.5 | 8.3333 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-02 | 2024-01-02 05:14 | 2024-01-02 05:54 | 0:40 | T | 33kv Patgram Feeder 33Kv BUS D/S Fault. | 12.5 | 8.3333 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-01-31 18:47 | 2024-01-31 19:04 | 0:17 | T | Trip | 79 | 22.3833 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2024-01-04 14:38 | 2024-01-04 15:00 | 0:22 | E/O | BUS DS Red hot | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-01-10 10:45 | 2024-01-11 15:30 | 28:45 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Baghabari -02 | 2024-01-17 02:30 | 2024-01-17 17:42 | 15:12 | T | Baghabari end line-2 to line-3 fault | 0 | 0 | No interruption
|  |  | Total : | 45:56 |  | Unserved Energy: |  | 39.05
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 637:11 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: January 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) LT | 2024-01-09 10:33 | 2024-01-09 11:45 | 1:12 | S/O | Relay testing by SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 2024-01-09 11:48 | 2024-01-09 12:49 | 1:01 | S/O | Relay testing by SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2024-01-16 09:58 | 2024-01-16 12:55 | 2:57 | S/O | Relay Test By SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) LT | 2024-01-01 07:39 | 2024-01-01 18:15 | 10:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) LT | 2024-01-17 09:26 | 2024-01-17 11:44 | 2:18 | S/O | Relay Test By SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-1 LT | 2024-01-16 09:57 | 2024-01-16 12:58 | 3:01 | S/O | Relay Test By SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 HT | 2024-01-01 07:37 | 2024-01-01 18:12 | 10:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 LT | 2024-01-17 09:25 | 2024-01-17 11:45 | 2:20 | S/O | Relay Test By SPMD | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2024-01-04 08:55 | 2024-01-04 13:46 | 4:51 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-01-02 09:18 | 2024-01-02 17:46 | 8:28 | S/O | DS change work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-01-03 10:00 | 2024-01-03 14:51 | 4:51 | S/O | DS change work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-01-27 14:03 | 2024-01-27 15:42 | 1:39 | S/O | Schedule shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 HT | 2024-01-09 10:41 | 2024-01-09 15:13 | 4:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 HT | 2024-01-29 11:23 | 2024-01-29 14:32 | 3:09 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2024-01-01 09:39 | 2024-01-01 16:44 | 7:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2024-01-02 09:51 | 2024-01-02 17:43 | 7:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 (400kV) | 2024-01-20 11:10 | 2024-01-20 22:02 | 10:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 HT | 2024-01-17 16:05 | 2024-01-17 16:05 | 0:00 | D/W | GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 LT | 2024-01-17 11:21 | 2024-01-17 14:58 | 3:37 | D/W | GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 LT | 2024-01-17 16:04 | 2024-01-17 16:04 | 0:00 | D/W | GIS project work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-01-02 08:48 | 2024-01-02 16:28 | 7:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-01-03 09:34 | 2024-01-03 13:57 | 4:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-01-21 08:19 | 2024-01-21 16:00 | 7:41 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-01-30 10:01 | 2024-01-30 11:46 | 1:45 | S/O | Annual Maintanance | 15 | 26.25 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-01-20 09:55 | 2024-01-20 16:47 | 6:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-01-21 08:19 | 2024-01-21 15:58 | 7:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-01-30 11:49 | 2024-01-30 12:41 | 0:52 | S/O | Annual Maintanance | 20 | 17.3333 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-01-09 08:30 | 2024-01-09 17:20 | 8:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-01-11 08:20 | 2024-01-11 13:19 | 4:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-01-14 09:16 | 2024-01-14 17:49 | 8:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-01-15 08:19 | 2024-01-15 17:46 | 9:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-01-10 08:41 | 2024-01-10 17:38 | 8:57 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-01-16 08:50 | 2024-01-16 17:24 | 8:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-01-17 08:32 | 2024-01-17 17:18 | 8:46 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-01-18 08:46 | 2024-01-18 17:41 | 8:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-01-20 08:20 | 2024-01-20 17:32 | 9:12 | S/O | Annual maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-A | 2024-01-09 10:40 | 2024-01-09 14:58 | 4:18 | S/O | T4 transformer CT Remove | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Bus-A | 2024-01-27 12:55 | 2024-01-27 13:55 | 1:00 | S/O | Tan Delta test work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2024-01-27 11:27 | 2024-01-27 12:48 | 1:21 | S/O | Tan Delta test work by RTS | 10 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2024-01-29 09:53 | 2024-01-29 11:42 | 1:49 | S/O | HT bushing measurement. | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-01-27 09:25 | 2024-01-27 11:23 | 1:58 | S/O | RTS TanDelta test. | 10 | 19.6667 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-01-09 10:24 | 2024-01-09 10:56 | 0:32 | S/O | SCADA signal work | 20 | 10.6667 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-01-09 11:36 | 2024-01-09 11:47 | 0:11 | S/O | SCADA signal work | 5 | 0.91667 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-01-22 09:22 | 2024-01-22 10:15 | 0:53 | S/O | Auxiliary Transformer(AT-2) Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-4 HT | 2024-01-09 11:10 | 2024-01-09 11:28 | 0:18 | S/O | SCADA signal work | 10 | 3 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 HT | 2024-01-25 09:57 | 2024-01-25 16:19 | 6:22 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 LT | 2024-01-23 10:51 | 2024-01-23 16:46 | 5:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 LT | 2024-01-24 08:55 | 2024-01-24 16:34 | 7:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 HT | 2024-01-01 08:25 | 2024-01-01 17:04 | 8:39 | S/O | Tan delta test | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2024-01-21 17:26 | 2024-01-21 17:30 | 0:04 | S/O | For Flag reset Standby Earth Fault Relay | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2024-01-17 09:27 | 2024-01-17 16:28 | 7:01 | S/O | Ten delta test. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2024-01-28 09:26 | 2024-01-28 19:31 | 10:05 | S/O | Annual maintenance and testing | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2024-01-29 08:34 | 2024-01-29 17:12 | 8:38 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | BUS-B | 2024-01-23 11:28 | 2024-01-23 12:27 | 0:59 | D/W | Project work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2024-01-23 10:27 | 2024-01-23 11:22 | 0:55 | S/O | Project work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2024-01-23 12:06 | 2024-01-23 12:18 | 0:12 | D/W | Project work | 30 | 6 | Power interruption
Kodda 132/33kV Grid Sub-Station | Bus-2 | 2024-01-13 08:08 | 2024-01-13 15:49 | 7:41 | S/O | Annual maintenance work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2024-01-13 10:21 | 2024-01-13 11:13 | 0:52 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2024-01-11 09:13 | 2024-01-11 14:36 | 5:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) HT | 2024-01-13 11:16 | 2024-01-13 12:16 | 1:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) HT | 2024-01-13 12:20 | 2024-01-13 13:03 | 0:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-01-10 09:20 | 2024-01-10 17:39 | 8:19 | S/O | Maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-01-17 15:21 | 2024-01-17 15:31 | 0:10 | S/O | Telecommunication work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-01-17 10:35 | 2024-01-17 16:56 | 6:21 | S/O | Applied SD for AM Work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-01-18 10:40 | 2024-01-18 16:50 | 6:10 | S/O | Annual Maintenance on T1 132kV Main Bus DS | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-01-21 10:11 | 2024-01-21 17:04 | 6:53 | S/O | Annual Maintenance on 132kV T3 Main Bus DS | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-01-04 10:17 | 2024-01-04 16:53 | 6:36 | S/O | annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-01-22 10:27 | 2024-01-22 14:04 | 3:37 | S/O | Annual maintenance @ Reserve Bus Work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-01-27 10:23 | 2024-01-27 13:48 | 3:25 | S/O | Annual Maintenance work of Transformer-2 (T-2) with Reserve Bus bar. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-01-28 10:07 | 2024-01-28 17:25 | 7:18 | S/O | Annual Maintenance Work on 132 KV Reserve Bus Bay of T3 Power Transformer. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-01-30 10:43 | 2024-01-30 17:19 | 6:36 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-01-31 09:58 | 2024-01-31 15:37 | 5:39 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2024-01-22 10:22 | 2024-01-22 14:05 | 3:43 | S/O | Annual maintenance @ Reserve Bus Work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2024-01-18 09:45 | 2024-01-18 16:58 | 7:13 | S/O | Annual Maintenance on 132kV Main Bus DS | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 LT | 2024-01-20 11:34 | 2024-01-20 12:49 | 1:15 | S/O | SF6 Gas filling | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 LT | 2024-01-27 09:55 | 2024-01-27 13:56 | 4:01 | S/O | Annual Maintenance work of Transformer-2 (T-2) with Reserve Bus bar. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 HT | 2024-01-23 13:08 | 2024-01-23 14:24 | 1:16 | S/O | Annual maintenance Relay Test By SPMD -2. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 LT | 2024-01-21 09:30 | 2024-01-21 17:20 | 7:50 | S/O | Annual Maintenance on 132kV T3 Main Bus DS | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 LT | 2024-01-28 08:57 | 2024-01-28 17:45 | 8:48 | S/O | Annual Maintenance Work on 132 KV Reserve Bus Bay of T3 Power Transformer. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus A | 2024-01-23 10:16 | 2024-01-23 14:35 | 4:19 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus A | 2024-01-28 07:56 | 2024-01-28 11:19 | 3:23 | S/O | 132/33kV, 80/120MVA, T-1(404T) A-Bus DS (401S) of maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus B | 2024-01-24 10:28 | 2024-01-24 13:48 | 3:20 | S/O | Annual maintenance works (2023-2024) of 132kV Kish-2 B-Bus DS(202S) & Jamal-2 B-Bus DS(212S). | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus B | 2024-01-25 10:21 | 2024-01-25 14:52 | 4:31 | S/O | Annual maintenance works | 20 | 90.3333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Bus B | 2024-01-27 11:27 | 2024-01-27 15:59 | 4:32 | S/O | Annual maintenance works for 132kV B-Bus DS (102S- Kish ckt-1,112S- Jamal ckt-1) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Bus B | 2024-01-28 11:54 | 2024-01-28 16:35 | 4:41 | S/O | B-Bus DS (222S) & (412S) maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-01-27 11:04 | 2024-01-27 17:15 | 6:11 | S/O | Annual maintenance works for 132kV B-Bus DS (402S- T1) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-01-28 07:05 | 2024-01-28 12:01 | 4:56 | S/O | 132/33kV, 80/120MVA, T-1(404T) A-Bus DS (401S) of maintenance works. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2024-01-28 12:03 | 2024-01-28 17:08 | 5:05 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2024-01-01 09:50 | 2024-01-01 16:45 | 6:55 | S/O | A/M | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2024-01-14 09:14 | 2024-01-14 12:39 | 3:25 | D/W | Oil centrifugeing work. | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | T2(413T) LT | 2024-01-03 09:05 | 2024-01-03 21:05 | 12:00 | D/W | DESCO 33kv section AIS to GIS project work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-01-01 10:36 | 2024-01-01 17:02 | 6:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-01-22 12:37 | 2024-01-22 16:46 | 4:09 | S/O | 33 KV Bus-A shutdown due to DPBS-3 schedule work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-01-02 10:31 | 2024-01-02 16:55 | 6:24 | S/O | Annual maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-01-13 08:50 | 2024-01-13 15:28 | 6:38 | S/O | Bus-B riser upgradation work of 33kV L-39 Feeder by DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-01-23 12:03 | 2024-01-23 18:44 | 6:41 | S/O | Schedule work of DBPS-3. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2024-01-01 10:42 | 2024-01-01 12:52 | 2:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2024-01-24 13:16 | 2024-01-24 16:04 | 2:48 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-01-01 12:53 | 2024-01-01 16:38 | 3:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-01-02 10:42 | 2024-01-02 16:50 | 6:08 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-01-23 10:05 | 2024-01-23 18:30 | 8:25 | S/O | Ten delta test & annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-01-11 13:33 | 2024-01-11 16:52 | 3:19 | S/O | annual maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-01-28 11:52 | 2024-01-28 13:59 | 2:07 | S/O | CT Tan Delta test | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-01-29 11:55 | 2024-01-29 14:31 | 2:36 | S/O | Ten delta test by RTS. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-01-29 09:12 | 2024-01-29 11:37 | 2:25 | S/O | Ten delta test by RTS. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 HT | 2024-01-11 08:51 | 2024-01-11 17:40 | 8:49 | D/W | 230kv Busbar Protection | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-01-14 10:54 | 2024-01-14 17:02 | 6:08 | S/O | Project work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-02 LT | 2024-01-26 08:35 | 2024-01-26 14:10 | 5:35 | S/O | Annual maintenance work | 0 | 0 | No interruption
|  |  | Total : | 531:30 |  | Unserved Energy: |  | 174.1667
Dhaka (South) Grid Circle : | [10 empty] | 39.3333
Cantonment 132/33kV GIS Grid Sub-Station | Auxiliary Transformer, AT-2 LT | 2024-01-20 09:01 | 2024-01-20 16:36 | 7:35 | S/O | Annual Maintenance for the purpose. | 0 | 0 | No interruption
Cantonment 132/33kV GIS Grid Sub-Station | Transformer-1 (T-1) HT | 2024-01-19 09:02 | 2024-01-19 16:43 | 7:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cantonment 132/33kV GIS Grid Sub-Station | Transformer-1 (T-1) LT | 2024-01-16 12:33 | 2024-01-16 15:06 | 2:33 | S/O | Relay function test and GIS inspection of Transformer- TR-01 | 0 | 0 | No interruption
Cantonment 132/33kV GIS Grid Sub-Station | Transformer-2 (T-2) LT | 2024-01-17 11:06 | 2024-01-17 13:17 | 2:11 | S/O | For Annual maintenance(Functional Test by SPMD) | 0 | 0 | No interruption
Cantonment 132/33kV GIS Grid Sub-Station | Transformer-2 (T-2) LT | 2024-01-20 09:01 | 2024-01-20 16:35 | 7:34 | S/O | Annual Maintenance for the purpose. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-1 | 2024-01-30 13:00 | 2024-01-30 13:00 | 0:00 | D/W | 132 KV Bus Bar Protection work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2024-01-10 11:27 | 2024-01-10 16:11 | 4:44 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2024-01-30 13:00 | 2024-01-30 13:00 | 0:00 | D/W | 132 KV Bus Bar Protection work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-01-31 08:45 | 2024-01-31 11:55 | 3:10 | S/O | High temperature Maintanance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-1 | 2024-01-02 09:22 | 2024-01-02 16:06 | 6:44 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2024-01-02 10:32 | 2024-01-02 16:48 | 6:16 | S/O | 33kv reserve bus DS problem | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2024-01-09 11:26 | 2024-01-09 13:45 | 2:19 | S/O | 132 kv side main bus DS problem. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2024-01-09 09:26 | 2024-01-09 11:14 | 1:48 | S/O | Main tank to radiator connecting point oil leakage repair | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132kV Main Bus | 2024-01-02 13:33 | 2024-01-02 13:33 | 0:00 | S/O | T-1 transformer main bus DS operating problem. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2024-01-09 09:47 | 2024-01-09 16:38 | 6:51 | S/O | 33kV feeder maintenance by PBS. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus1 | 2024-01-05 08:35 | 2024-01-05 13:36 | 5:01 | S/O | Preventive maintenace for Bay 3 | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-1 LT | 2024-01-23 09:18 | 2024-01-23 16:30 | 7:12 | S/O | 33 KV Bus -1 Maintenance | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-2 LT | 2024-01-25 09:20 | 2024-01-25 09:20 | 0:00 | S/O | 33 KV Bus-02 Shut Down | 0 | 0 | No interruption
Mogbazar 132/33kV Grid Sub-Station | GT-3 LT | 2024-01-23 09:20 | 2024-01-23 16:32 | 7:12 | S/O | 33 KV Bus -1 Shutdown | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-01-10 10:20 | 2024-01-10 16:23 | 6:03 | S/O | Annual Maintenance | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-01-13 10:45 | 2024-01-13 13:07 | 2:22 | S/O | Annual Maintenance of Power Transformer-02. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | 132kV Main Bus-1 | 2024-01-15 10:05 | 2024-01-15 14:30 | 4:25 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | 132kV Main Bus-2 | 2024-01-16 09:36 | 2024-01-16 13:17 | 3:41 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 LT | 2024-01-04 12:11 | 2024-01-04 13:22 | 1:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-01-03 09:13 | 2024-01-03 16:17 | 7:04 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 2024-01-09 11:46 | 2024-01-09 13:08 | 1:22 | D/W | New Auto TX-04 Project work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2024-01-09 08:40 | 2024-01-09 10:58 | 2:18 | D/W | G to G project work ( t-40 | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2024-01-12 11:00 | 2024-01-12 20:48 | 9:48 | D/W | Auto TX-04 installation work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-1 | 2024-01-25 07:40 | 2024-01-25 16:48 | 9:08 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2024-01-17 08:30 | 2024-01-17 20:33 | 12:03 | D/W | New Auto TX-04 (300/450MVA) related project (development) work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-01-12 10:59 | 2024-01-12 20:51 | 9:52 | D/W | g2g project work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV Bus A | 2024-01-13 11:20 | 2024-01-13 14:24 | 3:04 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV Bus B | 2024-01-15 09:15 | 2024-01-15 12:13 | 2:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2024-01-12 09:30 | 2024-01-12 16:50 | 7:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2024-01-19 09:28 | 2024-01-19 16:13 | 6:45 | S/O | Annual maintenance. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 LT | 2024-01-17 09:28 | 2024-01-17 13:06 | 3:38 | S/O | Due to annual maintenance work of Siddhirganj 132 KV s/s. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2024-01-09 09:30 | 2024-01-09 12:55 | 3:25 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS A | 2024-01-21 09:30 | 2024-01-21 13:10 | 3:40 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2024-01-22 09:45 | 2024-01-22 12:26 | 2:41 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-01-10 09:09 | 2024-01-10 10:58 | 1:49 | S/O | Maintenance work by PBS. | 40 | 72.6667 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-01-13 07:35 | 2024-01-13 13:18 | 5:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2024-01-20 09:05 | 2024-01-20 13:05 | 4:00 | S/O | Annual maintenance | 20 | 80 | Power interruption
|  |  | Total : | 193:11 |  | Unserved Energy: |  | 152.6667
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | 230/33 kV Transformer-2 (125/140 MVA) HT | 2024-01-23 10:03 | 2024-01-23 10:03 | 0:00 | S/O | Yearly Maintenance | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | 230/33 kV Transformer-2 (125/140 MVA) LT | 2024-01-23 10:02 | 2024-01-23 10:02 | 0:00 | S/O | Yearly Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | MAIN BUS-1 | 2024-01-31 09:12 | 2024-01-31 16:18 | 7:06 | S/O | Annual maintenance | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-01-31 07:30 | 2024-01-31 07:53 | 0:23 | S/O | Station Supply Fuse Replace Work | 36 | 13.8 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-01-31 09:50 | 2024-01-31 10:13 | 0:23 | D/W | Station Supply Tx Fuse Replacement | 30 | 11.5 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer-01(D05) HT | 2024-01-02 13:54 | 2024-01-02 14:55 | 1:01 | S/O | General Inspection & tightness checking | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2024-01-26 10:56 | 2024-01-26 10:56 | 0:00 | S/O | Scheduled Shutdown Due to Blast wall foundation work under ESPNER Project. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2024-01-13 08:52 | 2024-01-13 13:22 | 4:30 | S/O | Annual Maintenance | 5 | 22.5 | Power interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2024-01-13 09:07 | 2024-01-13 12:51 | 3:44 | S/O | None | 10 | 37.3333 | Power interruption
Khulshi 132/33kV Grid Sub-Station | Main Bus | 2024-01-27 07:22 | 2024-01-27 11:10 | 3:48 | S/O | Annual Maintenance | 30 | 114 | Power interruption
Mirsorai 230/33kV Grid Sub-Station | Bus-2 | 2024-01-25 12:46 | 2024-01-28 14:48 | 74:02 | D/W | Egcb project work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2024-01-15 10:46 | 2024-01-15 20:54 | 10:08 | D/W | EGCB Feni Sonagazi Solar 230kV Transmission line GIS Bay Busbar protection system testing work. | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2024-01-22 11:43 | 2024-01-22 15:53 | 4:10 | D/W | EGCB Project Work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-02 | 2024-01-30 09:57 | 2024-01-30 09:57 | 0:00 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-01-10 14:14 | 2024-01-10 15:47 | 1:33 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-01-29 11:17 | 2024-01-29 17:56 | 6:39 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-01-14 09:30 | 2024-01-14 19:18 | 9:48 | D/W | High Voltage Test | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-01-31 10:57 | 2024-01-31 20:03 | 9:06 | D/W | Seimens project work. No L/S. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) LT | 2024-01-10 14:14 | 2024-01-10 15:47 | 1:33 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) LT | 2024-01-29 11:17 | 2024-01-29 17:58 | 6:41 | D/W | project work | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 406T HT | 2024-01-19 08:13 | 2024-01-19 12:39 | 4:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 2024-01-19 07:57 | 2024-01-19 13:07 | 5:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T LT | 2024-01-19 07:55 | 2024-01-19 07:55 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 HT | 2024-01-24 14:17 | 2024-01-24 17:00 | 2:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 LT | 2024-01-25 07:37 | 2024-01-25 17:23 | 9:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) HT | 2024-01-30 09:45 | 2024-01-30 09:45 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) LT | 2024-01-30 09:41 | 2024-01-30 09:41 | 0:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 166:40 |  |  |  | 199.1333
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV Transformer TR-01 LT | 2024-01-24 08:56 | 2024-01-24 16:27 | 7:31 | S/O | Annual maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132 KV Transformer TR-01 LT | 2024-01-25 08:56 | 2024-01-25 16:15 | 7:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 HT | 2024-01-23 09:14 | 2024-01-23 16:07 | 6:53 | S/O | Maintenance work. | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2024-01-22 08:56 | 2024-01-22 15:42 | 6:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2024-01-27 09:34 | 2024-01-27 14:48 | 5:14 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2024-01-29 12:33 | 2024-01-29 14:10 | 1:37 | S/O | Relay Testing | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2024-01-29 14:39 | 2024-01-29 15:31 | 0:52 | S/O | relay testing. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 200KVA Aux. T-2 LT | 2024-01-19 08:19 | 2024-01-19 08:19 | 0:00 | S/O | relay testing. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-01-10 08:07 | 2024-01-10 08:40 | 0:33 | S/O | BPDB 33 KV Bus section-1 S/D for 33 kv chandpur -4 loop open work | 7 | 3.85 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-3 HT | 2024-01-22 08:44 | 2024-01-22 14:35 | 5:51 | S/O | Annual maintanance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2024-01-25 12:48 | 2024-01-25 13:58 | 1:10 | S/O | Annual maintanance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-01-27 08:52 | 2024-01-27 11:48 | 2:56 | S/O | 132KV Busbar Modification. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 HT | 2024-01-27 11:53 | 2024-01-27 14:09 | 2:16 | S/O | 132KV Busbar Modification. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-01-22 12:58 | 2024-01-22 21:23 | 8:25 | S/O | Emergency 132KV BUS -1 DS 101-89A Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2024-01-22 09:28 | 2024-01-22 11:42 | 2:14 | S/O | Emergency 132KV BUS -2 DS 107-89B Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 230 KV Bus-1 | 2024-01-03 09:04 | 2024-01-03 17:20 | 8:16 | S/O | Annual maintenance Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 LT | 2024-01-22 10:00 | 2024-01-22 15:37 | 5:37 | S/O | Emergency 132KV BUS -1 DS 101-89A Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-01-15 09:58 | 2024-01-15 19:19 | 9:21 | S/O | Work of SPMD | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-01-17 12:55 | 2024-01-17 16:56 | 4:01 | S/O | Tan Delta test | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-01-22 12:46 | 2024-01-22 21:31 | 8:45 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-01-16 10:32 | 2024-01-16 17:00 | 6:28 | S/O | relay test | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-01-22 09:26 | 2024-01-22 12:42 | 3:16 | S/O | Due to 132KV BUS-2 Shutdown | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-01-30 09:31 | 2024-01-30 17:27 | 7:56 | S/O | Maintenance Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-01-31 12:10 | 2024-01-31 13:47 | 1:37 | S/O | Maintenance Work | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 kV Bus-A | 2024-01-20 09:35 | 2024-01-21 13:25 | 27:50 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 kV Bus-B | 2024-01-22 09:15 | 2024-01-22 15:56 | 6:41 | S/O | Annual maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-01-22 08:38 | 2024-01-22 17:15 | 8:37 | S/O | Annual maintenance. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB LT | 2024-01-23 08:55 | 2024-01-23 14:32 | 5:37 | S/O | Tr-1A Transformer remove & capacity improve. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-01-31 09:19 | 2024-01-31 14:43 | 5:24 | S/O | Annual Maintenance Purpose | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 HT | 2024-01-01 17:40 | 2024-01-01 17:51 | 0:11 | D/W | CCCE Project work | 2 | 0.36667 | Power interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 HT | 2024-01-21 11:42 | 2024-01-21 15:34 | 3:52 | S/O | siemens boundary lighting work on sylhet gis ss | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 LT | 2024-01-21 15:37 | 2024-01-21 15:37 | 0:00 | S/O | project lighting works. | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 HT | 2024-01-01 17:40 | 2024-01-01 17:51 | 0:11 | D/W | CCCE project work | 2 | 0.36667 | Power interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 HT | 2024-01-21 15:37 | 2024-01-21 15:37 | 0:00 | S/O | project lighting works. | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 LT | 2024-01-01 20:01 | 2024-01-01 20:01 | 0:00 | D/W | CCCE project Work | 0 | 0 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2024-01-25 09:40 | 2024-01-25 14:10 | 4:30 | S/O | Yearly Maintenance | 0 | 0 | No interruption
|  |  | Total : | 177:47 |  | Unserved Energy: |  | 4.5833
Khulna Grid Circle : | [9 empty] | 251.2167
Barishal 230/132kV Grid Sub-Station | ATR-1 HT | 2024-01-15 11:05 | 2024-01-15 17:16 | 6:11 | S/O | Oil Leakage Repair | 0 | 0 | No interruption | 113.55
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-01-22 15:37 | 2024-01-22 17:17 | 1:40 | S/O | 33kv busbar red-hot maintenance by pbs | 30 | 50 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-01-01 09:21 | 2024-01-01 10:36 | 1:15 | S/O | 33kV Faridpur feeder Y-phase Bus loop Red hot maintenance. | 15 | 18.75 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-01-01 08:20 | 2024-01-01 11:12 | 2:52 | S/O | 33kV Faridpur feeder Y-phase Bus loop Red hot maintenance. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | 33 kV Bus | 2024-01-26 06:45 | 2024-01-26 17:20 | 10:35 | D/W | Bus-Section 2&3 for G2G project. | 0 | 0 | No interruption | 364.7667
Gollamari 132/33kV Grid Sub-Station | 33 kV Bus | 2024-01-30 07:52 | 2024-01-30 17:30 | 9:38 | D/W | 33kV Bus Section 2 & 3 | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-01-28 07:34 | 2024-01-28 17:34 | 10:00 | D/W | Project work | 7 | 70 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2024-01-10 09:09 | 2024-01-10 09:09 | 0:00 | D/W | 80/120MVA Transformer Commissioning under G2G Project. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-01-10 09:08 | 2024-01-10 09:08 | 0:00 | D/W | 80/120 MVA Transformer Commissionig under G2G Project. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-01 | 2024-01-30 08:36 | 2024-01-30 20:42 | 12:06 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-01 | 2024-01-31 08:36 | 2024-01-31 15:24 | 6:48 | D/W | SAS Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-02 | 2024-01-31 15:28 | 2024-01-31 19:58 | 4:30 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 HT | 2024-01-31 19:25 | 2024-01-31 20:30 | 1:05 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-01-23 10:32 | 2024-01-24 20:56 | 34:24 | D/W | Testing & relay change | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-01-31 16:54 | 2024-01-31 19:18 | 2:24 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2024-01-31 15:50 | 2024-01-31 16:45 | 0:55 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-01-31 16:48 | 2024-01-31 16:48 | 0:00 | D/W | Project work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-01-10 07:37 | 2024-01-10 10:45 | 3:08 | S/O | Main Tank oil leakage maintenance. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-01-09 13:58 | 2024-01-09 15:38 | 1:40 | D/W | Rupsha 800MW Line Project Work (NWPGCL). | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-01-16 13:29 | 2024-01-21 17:39 | 124:10 | D/W | Rupsha 800 MW Transmission Line Project Work (NWPGCL). | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-01-09 16:27 | 2024-01-16 12:48 | 164:21 | D/W | Rupsha 800MW Line Project Work (NWPGCL). | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 LT | 2024-01-13 10:43 | 2024-01-13 12:40 | 1:57 | S/O | maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 LT | 2024-01-16 13:25 | 2024-01-21 17:54 | 124:29 | D/W | Rupsha 800 MW Transmission Line Project Work (NWPGCL). | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-01-12 09:01 | 2024-01-12 10:57 | 1:56 | S/O | Schedule shutdown, 33 kv bus maintenance. | 14 | 27.0667 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) LT | 2024-01-27 14:34 | 2024-01-27 18:24 | 3:50 | S/O | Due to maint.work | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-01-02 12:14 | 2024-01-02 15:24 | 3:10 | S/O | Tan delta test. | 0 | 0 | No interruption
Payra 400kV Sub-Station | Bus-1 | 2024-01-04 11:17 | 2024-01-05 00:49 | 13:32 | S/O | maintenance | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Start-Up Transformer (SUT) HT | 2024-01-14 11:42 | 2024-01-14 20:21 | 8:39 | D/W | Some Maintenance Job. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Start-Up Transformer (SUT) LT | 2024-01-14 11:43 | 2024-01-14 20:19 | 8:36 | D/W | Some Maintenance Job. | 0 | 0 | No interruption
|  |  | Total : | 563:51 |  | Unserved Energy : |  | 165.8167
HVDC Grid Circle
Bheramara 230/132kV Grid Sub-Station | Bus-B (132) | 2024-01-27 12:20 | 2024-01-27 16:29 | 4:09 | D/W | A/m | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-1 LT | 2024-01-23 08:41 | 2024-01-23 13:48 | 5:07 | S/O | Annual maintenance work | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-1 LT | 2024-01-26 10:10 | 2024-01-26 11:52 | 1:42 | D/W | For SACDA Connection By Totaltel. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-1 LT | 2024-01-27 08:29 | 2024-01-27 19:23 | 10:54 | S/O | 132/33 kV BUS shutdown | 30 | 327 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2024-01-24 08:22 | 2024-01-24 13:54 | 5:32 | S/O | Anuual Maintenance | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2024-01-26 12:15 | 2024-01-26 14:17 | 2:02 | D/W | For SCADA Connection BY Totaltel. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2024-01-27 08:29 | 2024-01-27 19:24 | 10:55 | S/O | 132/33 kV Bus shutdown | 30 | 327.5 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-3 LT | 2024-01-25 08:28 | 2024-01-25 14:52 | 6:24 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-3 LT | 2024-01-27 08:29 | 2024-01-27 19:26 | 10:57 | S/O | 132/33 kV Bus shutdown | 30 | 328.5 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-4 LT | 2024-01-27 08:30 | 2024-01-27 19:26 | 10:56 | S/O | 132/33 kV Bus shutdown | 30 | 328 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-4 LT | 2024-01-28 08:51 | 2024-01-28 14:44 | 5:53 | S/O | Annual maintenance work | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T1(416T) LT | 2024-01-10 09:03 | 2024-01-10 14:55 | 5:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) LT | 2024-01-11 09:25 | 2024-01-11 15:02 | 5:37 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T3 LT | 2024-01-09 08:42 | 2024-01-09 15:54 | 7:12 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-01-18 10:55 | 2024-01-18 13:12 | 2:17 | S/O | annual maintanance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-01-31 09:11 | 2024-01-31 17:29 | 8:18 | S/O | annual maintanance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 2024-01-29 10:29 | 2024-01-29 17:13 | 6:44 | S/O | baus bar loop change | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-2 | 2024-01-30 09:20 | 2024-01-30 17:12 | 7:52 | S/O | annual maintanance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2024-01-21 09:34 | 2024-01-21 15:07 | 5:33 | S/O | Annual Maintanance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 HT | 2024-01-24 10:03 | 2024-01-24 17:26 | 7:23 | S/O | annual maintanance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 LT | 2024-01-25 09:55 | 2024-01-25 16:20 | 6:25 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 LT | 2024-01-28 10:16 | 2024-01-28 17:40 | 7:24 | S/O | annual maintanance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 HT | 2024-01-16 08:52 | 2024-01-16 13:00 | 4:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 HT | 2024-01-16 13:02 | 2024-01-16 13:02 | 0:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 LT | 2024-01-16 13:02 | 2024-01-16 13:02 | 0:00 | S/O | A/M | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 HT | 2024-01-15 08:21 | 2024-01-15 15:23 |  | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-01-29 08:19 | 2024-01-29 16:20 | 8:01 | S/O | A/M | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T2 HT | 2024-01-30 08:15 | 2024-01-30 08:15 | 0:00 | S/O | A/M | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-01-30 08:14 | 2024-01-30 08:14 | 0:00 | S/O | A/M | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Main Bus | 2024-01-26 08:32 | 2024-01-26 15:56 | 7:24 | S/O | A/M | 40 | 296 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-01-11 08:19 | 2024-01-13 16:34 | 56:15 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-01-22 12:40 | 2024-01-22 12:50 | 0:10 | S/O | Annual Maintenance work. | 28 | 4.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2024-01-26 08:26 | 2024-01-26 15:59 | 7:33 | S/O | Annual Maintenance work. | 19 | 143.45 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 HT | 2024-01-14 09:00 | 2024-01-14 16:50 | 7:50 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-2 LT | 2024-01-26 08:26 | 2024-01-26 16:11 | 7:45 | S/O | None | 10 | 77.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 LT | 2024-01-22 09:04 | 2024-01-22 17:24 | 8:20 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-3 LT | 2024-01-23 09:22 | 2024-01-23 14:58 | 5:36 | S/O | None | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-3 LT | 2024-01-26 08:26 | 2024-01-26 16:03 | 7:37 | S/O | None | 11 | 83.7833 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | Main Bus | 2024-01-19 08:41 | 2024-01-19 17:20 | 8:39 | S/O | Annual Maintenance for 132Kv Main Bus | 20 | 173 | Power interruption
|  |  | Total : | 274:26 |  | Unserved Energy : |  | 2089.4
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2024-01-27 12:45 | 2024-01-27 14:27 | 1:42 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2024-01-23 08:16 | 2024-01-23 08:16 | 0:00 | S/O | Redhot maintenance at 33kV feeder. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-01-23 08:15 | 2024-01-23 08:15 | 0:00 | S/O | Redhot maintenance at 33kV feeder. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-01-24 07:52 | 2024-01-24 12:02 | 4:10 | S/O | red hot work t-2 33kv isolator | 10 | 41.6667 | Power interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-01-23 06:55 | 2024-01-23 09:12 | 2:17 | S/O | Red Hot Maintenance 230kV Bogura Ckt.-4 | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2024-01-23 10:48 | 2024-01-23 13:15 | 2:27 | S/O | Due to change Energy Meter | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2024-01-23 13:21 | 2024-01-23 14:14 | 0:53 | S/O | Due to Energy Meter Change | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Main Bus | 2024-01-19 06:14 | 2024-01-19 08:03 | 1:49 | D/W | 132kV Main Bus Shutdown for To disconnect the Bus Jumper between Existing Naogaon-1 and New Naogaon-2 for Upper Bus Conductor stringing Under G to G project work | 25 | 45.4167 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-1 (407 T) LT | 2024-01-10 09:18 | 2024-01-10 10:59 | 1:41 | S/O | Shut down to stop oil leakage of T-1 132Kv transformer | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 33KV Main bus T-1 | 2024-01-01 08:29 | 2024-01-01 12:21 | 3:52 | S/O | 33kv Bus & Feeder maintenance | 7 | 27.0667 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 33KV Main bus T-2 | 2024-01-01 08:31 | 2024-01-01 12:15 | 3:44 | S/O | 33kv Bus & Feeder maintenance | 6 | 22.4 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-01-01 07:48 | 2024-01-01 17:09 | 9:21 | D/W | New 80/120 MVA Transformer installation. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2024-01-02 08:06 | 2024-01-02 16:57 | 8:51 | D/W | New Transformer Erection | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2024-01-03 08:20 | 2024-01-03 17:31 | 9:11 | D/W | new Transformer erection | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2024-01-10 09:45 | 2024-01-30 17:45 | 488:00 | D/W | For Project Work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Main Bus | 2024-01-30 07:19 | 2024-01-30 17:45 | 10:26 | D/W | Project work | 65 | 678.1667 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2024-01-29 15:52 | 2024-01-29 17:45 | 1:53 | S/O | Annual Maintenance work. | 30 | 56.5 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2024-01-11 13:04 | 2024-01-11 13:27 | 0:23 | D/W | None | 30 | 11.5 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) HT | 2024-01-11 13:35 | 2024-01-11 13:35 | 0:00 | D/W | Project work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2024-01-11 13:30 | 2024-01-11 13:30 | 0:00 | D/W | Project work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 33 kV T-3 Bus | 2024-01-16 09:14 | 2024-01-16 11:55 | 2:41 | S/O | Due to T-3 (II) 33 KV BUS S/D. | 19.5 | 52.325 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-01-15 11:27 | 2024-01-15 13:26 | 1:59 | S/O | Due to 33 kv BUS S/D. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-01-15 09:25 | 2024-01-15 10:02 | 0:37 | S/O | 33 kv BUS maintenance &cleaning by NESCO. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-01-15 09:06 | 2024-01-15 12:40 | 3:34 | S/O | 33 kv BUS maintenance & cleaning by NESCO. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-01-16 09:14 | 2024-01-16 11:55 | 2:41 | S/O | Due to T-3 (II) 33 KV BUS S/D. | 19.5 | 52.325 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-01-21 10:05 | 2024-01-21 13:46 | 3:41 | D/W | Due to T3 132 kv CB replacing work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2024-01-19 09:39 | 2024-01-19 14:23 | 4:44 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) LT | 2024-01-17 09:50 | 2024-01-17 16:17 | 6:27 | S/O | Nesco Project Work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2024-01-20 07:18 | 2024-01-20 16:16 | 8:58 | D/W | 33 kv Bus Maintenance | 40 | 358.6667 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) HT | 2024-01-20 07:22 | 2024-01-20 16:16 | 8:54 | D/W | 33 kv Bus Maintenance | 40 | 356 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) HT | 2024-01-15 10:06 | 2024-01-15 10:06 | 0:00 | D/W | 132/33KV T-3 Transformer replace. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2024-01-15 10:05 | 2024-01-15 10:05 | 0:00 | D/W | 132/33KV T-3 Transformer replace. | 0 | 0 | No interruption
|  |  | Total : | 594:56 |  | Unserved Energy : |  | 1702.0333
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2502:21 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: January 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-01-09 15:07 | 2024-01-09 15:49 | 0:42 | S/O | Relay Test. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-01-27 08:28 | 2024-01-27 17:27 | 8:59 | S/O | Dead line checking. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-01-28 08:33 | 2024-01-28 16:55 | 8:22 | S/O | Deadline checking and insulator cleaning of 2,3 and 4 No Tower of Aminbazar ckt-1 | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-01-09 12:45 | 2024-01-09 15:04 | 2:19 | S/O | Relay testing by SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-01-29 08:19 | 2024-01-29 19:34 | 11:15 | S/O | Dead line checking | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-1 | 2024-01-15 15:09 | 2024-01-15 16:09 | 1:00 | S/O | Relay Test by SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-2 | 2024-01-15 16:26 | 2024-01-15 17:02 | 0:36 | S/O | Relay Test By SPMD | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-2 | 2024-01-17 12:12 | 2024-01-17 15:03 | 2:51 | S/O | Relay test by SPMD-2 | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-2 | 2024-01-18 10:25 | 2024-01-18 19:15 | 8:50 | S/O | Relay Test by SPMD-02 | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-02 | 2024-01-09 11:03 | 2024-01-09 16:27 | 5:24 | S/O | Deadline checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-02 | 2024-01-11 08:50 | 2024-01-11 17:04 | 8:14 | S/O | Dead Line checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kallyanpur-01 | 2024-01-27 14:18 | 2024-01-27 15:56 | 1:38 | S/O | Dead Line checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-01-13 08:15 | 2024-01-13 15:02 | 6:47 | D/W | Dead Line checking | 38 | 257.7667 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-01-25 08:56 | 2024-01-25 16:13 | 7:17 | S/O | Dead line checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-01-27 09:31 | 2024-01-27 16:47 | 7:16 | S/O | Anual Maintenace | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-01-28 09:27 | 2024-01-28 15:28 | 6:01 | S/O | Anual Maintenace | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2024-01-13 08:15 | 2024-01-13 14:54 | 6:39 | D/W | Due to project work | 38 | 252.7 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2024-01-22 08:41 | 2024-01-22 16:44 | 8:03 | S/O | Anual Maintenace | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2024-01-23 08:34 | 2024-01-23 16:38 | 8:04 | S/O | Dead line cheeking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-01-16 11:10 | 2024-01-16 20:46 | 9:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-01-29 11:06 | 2024-01-29 17:20 | 6:14 | S/O | Deadline checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-01-30 09:43 | 2024-01-30 16:53 | 7:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-01-11 09:07 | 2024-01-11 18:45 | 9:38 | S/O | Frim meghnaghat | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-01-17 10:55 | 2024-01-17 20:22 | 9:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-01-23 10:44 | 2024-01-23 15:52 | 5:08 | S/O | Bay maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2024-01-01 08:07 | 2024-01-01 18:29 | 10:22 | S/O | Jack bus conductor change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2024-01-02 15:23 | 2024-01-02 17:24 | 2:01 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2024-01-29 08:52 | 2024-01-29 15:37 | 6:45 | S/O | annual maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2024-01-30 08:35 | 2024-01-30 16:05 | 7:30 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Shahajibazar 132 kV Ckt-3 | 2024-01-03 09:33 | 2024-01-03 15:39 | 6:06 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Shahajibazar 132 kV Ckt-3 | 2024-01-04 08:47 | 2024-01-04 17:05 | 8:18 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | South -1(230kv) | 2024-01-13 09:22 | 2024-01-13 16:20 | 6:58 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | South -1(230kv) | 2024-01-14 09:12 | 2024-01-14 15:15 | 6:03 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | South-2(230kv) | 2024-01-15 09:27 | 2024-01-15 16:37 | 7:10 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | South-2(230kv) | 2024-01-16 08:50 | 2024-01-17 15:35 | 30:45 | S/O | Asper demand of APSCL substation | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 01 | 2024-01-15 09:24 | 2024-01-15 15:40 | 6:16 | S/O | Annual maintanance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 02 | 2024-01-16 09:29 | 2024-01-16 16:54 | 7:25 | S/O | Annual maintanance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2024-01-09 09:17 | 2024-01-09 17:03 | 7:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2024-01-10 08:28 | 2024-01-10 17:45 | 9:17 | S/O | annual maintenance dead line checking. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2024-01-14 08:46 | 2024-01-14 17:44 | 8:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-01-17 08:18 | 2024-01-17 17:22 | 9:04 | S/O | Due to annual maintenance. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-01-18 08:26 | 2024-01-18 18:01 | 9:35 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-01-19 08:30 | 2024-01-19 17:04 | 8:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2024-01-31 09:10 | 2024-01-31 16:54 | 7:44 | S/O | OPGW armouring work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2024-01-24 10:41 | 2024-01-24 14:40 | 3:59 | S/O | for mymensingh grid work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2024-01-26 09:54 | 2024-01-26 11:16 | 1:22 | S/O | Duty maintenance of kadda powergen. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-2 | 2024-01-26 11:11 | 2024-01-26 12:04 | 0:53 | S/O | Duty maintenance of kadda powergen | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-01-28 09:11 | 2024-01-28 17:15 | 8:04 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-01-29 09:20 | 2024-01-29 09:20 | 0:00 | S/O | Annual maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2024-01-10 09:10 | 2024-01-10 19:24 | 10:14 | S/O | Works at Aminbazar end. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2024-01-20 08:29 | 2024-01-20 16:51 | 8:22 | S/O | NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Kabirpur-1 | 2024-01-20 09:03 | 2024-01-20 14:48 | 5:45 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Kabirpur-2 | 2024-01-21 09:10 | 2024-01-21 15:33 | 6:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2024-01-13 07:39 | 2024-01-13 14:49 | 7:10 | S/O | By NLDC, work at Tangail end | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2024-01-24 09:54 | 2024-01-24 13:07 | 3:13 | S/O | By NLDC | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-01-15 10:00 | 2024-01-15 17:19 | 7:19 | S/O | Annual Maintenance and dead line checking. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-01-16 10:00 | 2024-01-16 15:20 | 5:20 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2024-01-23 09:38 | 2024-01-23 16:54 | 7:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2024-01-24 10:17 | 2024-01-24 17:32 | 7:15 | S/O | Dead line check | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2024-01-25 09:07 | 2024-01-25 14:04 | 4:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-01-30 08:37 | 2024-01-30 16:59 | 8:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-01-31 08:47 | 2024-01-31 17:27 | 8:40 | S/O | Dead line checking | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-01-01 09:50 | 2024-01-01 16:51 | 7:01 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-01-02 09:30 | 2024-01-02 17:12 | 7:42 | S/O | Dead Line Checking (Annual Maintenance) | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-01-03 09:13 | 2024-01-03 17:22 | 8:09 | S/O | Dead line check | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-01-17 09:50 | 2024-01-17 16:54 | 7:04 | S/O | Annual maintenance work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-01-18 09:20 | 2024-01-18 16:48 | 7:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-01-24 10:45 | 2024-01-24 14:33 | 3:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2024-01-23 13:47 | 2024-01-23 15:48 | 2:01 | S/O | AM Work- Relay testing work by SPMD - 2, Dhaka,PGCB. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2024-01-30 10:20 | 2024-01-30 17:18 | 6:58 | S/O | Annual maintenance work . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-01-02 09:28 | 2024-01-02 18:29 | 9:01 | S/O | 132 KV Uttara Old Annual Maintenance Dead Line Checking . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-01-03 10:34 | 2024-01-03 19:32 | 8:58 | S/O | S/D for Deadline Checking & Bay Equipment Maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-01-04 09:45 | 2024-01-04 17:11 | 7:26 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-01-16 10:16 | 2024-01-16 17:11 | 6:55 | S/O | Annual maintenance work . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-01-23 15:02 | 2024-01-23 15:42 | 0:40 | S/O | AM work (Relay testing by SPMD-2, Dhaka, PGCB). | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-01-31 09:07 | 2024-01-31 15:38 | 6:31 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-01-09 10:10 | 2024-01-09 17:56 | 7:46 | S/O | Annual maintenance work, dead line. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-01-10 09:42 | 2024-01-10 16:41 | 6:59 | S/O | Deadline checking | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-01-11 10:31 | 2024-01-11 17:07 | 6:36 | S/O | Annual Maintenance Work on Mirpur SS End. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-01-17 09:52 | 2024-01-17 17:08 | 7:16 | S/O | Applied SD For AM Work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-01-23 15:50 | 2024-01-23 16:22 | 0:32 | S/O | AM work (Relay testing by SPMD-2, Dhaka, PGCB). | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2A(E04) | 2024-01-13 07:31 | 2024-01-13 14:47 | 7:16 | S/O | S/D taken by Tangail 132/33 kv grid s/s for maintenance work. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2B(E03) | 2024-01-13 07:31 | 2024-01-13 14:47 | 7:16 | S/O | S/D taken by Tangail 132/33 kv grid s/s for maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2024-01-23 09:45 | 2024-01-23 20:38 | 10:53 | S/O | Annual maintenance works of A-Bus | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2024-01-24 10:24 | 2024-01-25 16:54 | 30:30 | S/O | Annual maintenance works (2023-2024) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2024-01-28 07:14 | 2024-01-28 11:24 | 4:10 | S/O | 132/33kV, 80/120MVA, T-1(404T) A-Bus DS (401S) of maintenance works. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2024-01-23 10:15 | 2024-01-23 15:23 | 5:08 | S/O | Annual maintenance works of A-Bus DS (301S) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2024-01-25 09:28 | 2024-01-25 14:50 | 5:22 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2024-01-23 10:15 | 2024-01-23 15:23 | 5:08 | S/O | Annual maintenance works of A-Bus DS (311S) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2024-01-25 09:28 | 2024-01-25 15:45 | 6:17 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-1 | 2024-01-27 10:20 | 2024-01-27 13:50 | 3:30 | S/O | Annual maintenance works for 132kV B-Bus DS(112S) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2024-01-09 09:16 | 2024-01-09 17:04 | 7:48 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2024-01-10 09:21 | 2024-01-10 17:20 | 7:59 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2024-01-11 09:31 | 2024-01-11 14:59 | 5:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2024-01-27 10:02 | 2024-01-27 13:50 | 3:48 | S/O | Annual maintenance works for 132kV B-Bus DS(102S) | 50 | 190 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-1 | 2024-01-27 13:56 | 2024-01-27 17:31 | 3:35 | S/O | Annual maintenance works for 132kV B-Bus DS (122S- T1) | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-2 | 2024-01-28 12:27 | 2024-01-28 17:22 | 4:55 | S/O | B-Bus DS (222S) & (412S) maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-RPCL Ckt-1 | 2024-01-25 10:18 | 2024-01-25 14:50 | 4:32 | S/O | Annual maintenance works | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 2024-01-13 13:15 | 2024-01-13 14:41 | 1:26 | S/O | Kodda grid end work purpose. | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-2 | 2024-01-13 14:42 | 2024-01-13 15:27 | 0:45 | S/O | Kodda Grid end work purpose. | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132 KV Agargaon-Satmasjid Line-2 | 2024-01-17 12:12 | 2024-01-17 15:07 | 2:55 | S/O | S/D taken by Agargaon Grid s/s. | 0 | 0 | No interruption
Satmasjid 132/33kV Grid Sub-Station | 132 KV Agargaon-Satmasjid Line-2 | 2024-01-18 10:24 | 2024-01-18 19:16 | 8:52 | S/O | Relay test at Agargaon Grid End | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-01-13 09:45 | 2024-01-13 16:59 | 7:14 | S/O | dead line checking of transmission line | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-01-30 08:31 | 2024-01-30 16:44 | 8:13 | S/O | Dead line checking. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-01-13 09:45 | 2024-01-13 15:15 | 5:30 | S/O | dead line checking of transmission line | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-01-21 09:42 | 2024-01-21 16:30 | 6:48 | S/O | Dead line checking | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-01 | 2024-01-28 09:05 | 2024-01-28 13:05 | 4:00 | S/O | Tan Delta Test | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-02 | 2024-01-25 10:22 | 2024-01-25 16:10 | 5:48 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-02 | 2024-01-28 15:56 | 2024-01-28 17:19 | 1:23 | S/O | CT Tan Delta test | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-01-15 09:40 | 2024-01-15 15:38 | 5:58 | D/W | Busbar testing for protection. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-01-29 10:10 | 2024-01-29 15:24 | 5:14 | S/O | Bhaluka Substation Maintenance Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-01-16 08:54 | 2024-01-16 16:52 | 7:58 | D/W | Basbar protection testinng | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-01-29 15:27 | 2024-01-29 16:56 | 1:29 | S/O | Bhaluka SS Bus Maintenance Work | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-01-24 09:37 | 2024-01-24 13:08 | 3:31 | S/O | Annual Maintenance | 60 | 211 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-01-22 11:01 | 2024-01-22 12:23 | 1:22 | S/O | Relay testing. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2024-01-22 12:28 | 2024-01-22 13:19 | 0:51 | S/O | Relay Testing | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2024-01-20 14:38 | 2024-01-20 14:38 | 0:00 | D/W | Conductor Replacing work by 400 kV GNDP. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-01-25 15:30 | 2024-01-27 15:20 | 47:50 | D/W | Dhaka-Ashulia Express Way Development Work. | 0 | 0 | No interruption
|  |  | Total : | 798:14 |  | Unserved Energy: |  | 911.4667
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-01 10:22 | 2024-01-01 17:04 | 6:42 | S/O |  | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-09 09:19 | 2024-01-09 17:48 | 8:29 | S/O | Due to Deadline checking. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-10 09:42 | 2024-01-10 17:29 | 7:47 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-11 09:26 | 2024-01-11 17:29 | 8:03 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-24 09:40 | 2024-01-24 16:53 | 7:13 | S/O | Dead line checking by B Baria Grid SS | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-25 09:39 | 2024-01-25 16:51 | 7:12 | S/O | Dead line checking by B Baria Grid SS. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-01 | 2024-01-28 09:51 | 2024-01-28 15:52 | 6:01 | S/O | Dead Line Checking by Brahmanbaria Sunstation. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-01-03 10:01 | 2024-01-03 16:10 | 6:09 | S/O | Due to Annual Maintenance Works. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-01-13 10:08 | 2024-01-13 20:12 | 10:04 | S/O | Dead line checking of Bhulta-Ashuganj ckt-2. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-01-15 08:46 | 2024-01-15 20:31 | 11:45 | S/O | Due to Deadline check. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-01-29 08:55 | 2024-01-29 17:03 | 8:08 | S/O | Dead line checking by Brahmanbaria grid substation . | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-01-30 09:23 | 2024-01-30 16:15 | 6:52 | S/O | Dead line checking by B. Baria Grid SS. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-01-31 10:03 | 2024-01-31 16:40 | 6:37 | S/O | Dead Line Checking by B.Baria Grid SS | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-01-23 10:02 | 2024-01-23 17:44 | 7:42 | S/O | Dead line checking by Rampura Grid SS. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-02 | 2024-01-13 11:30 | 2024-01-13 19:57 | 8:27 | S/O | S/D taken by Rampura Grid SS for Dead Line Checking. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Rampura-02 | 2024-01-15 08:41 | 2024-01-15 16:47 | 8:06 | S/O | Due to Deadline check. | 0 | 0 | No interruption
Cantonment 132/33kV GIS Grid Sub-Station | Agargaon-Cantonment U/G line-1 | 2024-01-16 10:28 | 2024-01-16 12:15 | 1:47 | S/O | Relay function test and GIS inspection of Agargaon-Cantonment U/G Line-1 | 0 | 0 | No interruption
Cantonment 132/33kV GIS Grid Sub-Station | Agargaon-Cantonment U/G line-2 | 2024-01-17 09:18 | 2024-01-17 10:56 | 1:38 | S/O | For Annual Maintenance (Functional Test By SPMD) | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2024-01-09 11:25 | 2024-01-09 11:25 | 0:00 | D/W | project work at Rampura 230/132 kv SS. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-1 | 2024-01-15 09:15 | 2024-01-15 20:26 | 11:11 | S/O | Annual Maintenance (Dead Line Checking) | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-1 | 2024-01-16 08:26 | 2024-01-16 16:17 | 7:51 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-2 | 2024-01-18 09:30 | 2024-01-18 16:16 | 6:46 | S/O | Dead line checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-2 | 2024-01-19 09:46 | 2024-01-19 16:47 | 7:01 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Siddhirganj-2 | 2024-01-28 09:05 | 2024-01-28 13:52 | 4:47 | S/O | Annual Dead Line Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | EGCB 412MW | 2024-01-29 08:06 | 2024-01-29 08:06 | 0:00 | S/O | Maintenance work by EGCB at PGCB End. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | HPL-1 | 2024-01-28 15:40 | 2024-01-30 11:39 | 43:59 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | HPL-2 | 2024-01-21 10:25 | 2024-01-21 18:30 | 8:05 | S/O | Annual Deadline Checking(ES and local grounding close) | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2024-01-22 09:50 | 2024-01-22 16:16 | 6:26 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2024-01-23 08:27 | 2024-01-23 15:45 | 7:18 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-01-24 08:47 | 2024-01-24 16:40 | 7:53 | S/O | Annual Deadline Checking | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-01-25 09:02 | 2024-01-25 16:08 | 7:06 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2024-01-09 09:55 | 2024-01-09 16:13 | 6:18 | S/O | Unknown, Shut down bt NLDC. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-01-28 08:42 | 2024-01-28 15:12 | 6:30 | S/O | Deadline Checking | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-01-30 08:28 | 2024-01-30 17:47 | 9:19 | S/O | For CT Tan- delta | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2024-01-27 08:42 | 2024-01-27 15:27 | 6:45 | S/O | Due to Dead line Checking. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2024-01-31 08:34 | 2024-01-31 18:19 | 9:45 | S/O | Maintenance Work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-01-24 09:09 | 2024-01-24 19:35 | 10:26 | S/O | maintenence work at hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-01-23 08:57 | 2024-01-23 13:16 | 4:19 | S/O | Dead line check from Hasnabd End. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-01-30 08:41 | 2024-01-30 17:51 | 9:10 | S/O | For work at Hasanabad end | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-2 | 2024-01-23 13:23 | 2024-01-23 16:19 | 2:56 | S/O | dead line check from Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-2 | 2024-01-31 08:45 | 2024-01-31 18:20 | 9:35 | S/O | work at Hasnabad end | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Kamrangirchar | 2024-01-12 08:45 | 2024-01-12 13:13 | 4:28 | S/O | yearly Maintenance | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Srinagar-2 | 2024-01-04 09:11 | 2024-01-04 17:18 | 8:07 | S/O | for maintenace work at Sreenagar end | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2024-01-02 09:44 | 2024-01-02 20:33 | 10:49 | S/O | Control Cable replacement & MK Box installation | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2024-01-03 09:19 | 2024-01-03 16:32 | 7:13 | S/O | Control Cable repair work Going | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 102 MW 132 kv Ckt | 2024-01-17 09:30 | 2024-01-17 17:38 | 8:08 | S/O | Annual Maintenance at Summit PP end | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2024-01-16 10:44 | 2024-01-16 14:03 | 3:19 | S/O | Maintenance work at Ullon Sub-station. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-1 | 2024-01-20 09:19 | 2024-01-21 20:01 | 34:42 | S/O | Maintenance work by DPDC (Narinda S/S). | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-01-22 09:58 | 2024-01-23 15:05 | 29:07 | S/O | Narinda Ckt-2 Maintenance work at narinda S/S. (Oil centrifuge) | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-1 | 2024-01-17 07:36 | 2024-01-17 17:09 | 9:33 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2024-01-20 07:38 | 2024-01-20 16:11 | 8:33 | S/O | Annual Maintenance (Dead line checking). | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-02 | 2024-01-20 09:16 | 2024-01-20 17:19 | 8:03 | S/O | As per request of NLDC | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-01-20 08:51 | 2024-01-20 16:00 | 7:09 | S/O | As per request of NLDC | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Brahmanbaria-02 | 2024-01-10 09:43 | 2024-01-10 15:42 | 5:59 | S/O | From b baria ss maintenance work | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Brahmanbaria-02 | 2024-01-14 10:12 | 2024-01-14 16:59 | 6:47 | S/O | From b baria ss maintenance work | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Brahmanbaria-02 | 2024-01-15 09:29 | 2024-01-15 16:16 | 6:47 | S/O | From b baria ss maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-01-18 07:58 | 2024-01-18 08:42 | 0:44 | S/O | Remove rope from 132kV Line | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2024-01-14 08:25 | 2024-01-14 17:17 | 8:52 | S/O | Annual Dead Line Check | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2024-01-29 10:43 | 2024-01-29 16:44 | 6:01 | S/O | Dead line checking at Haripur Sub-Station. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-03 | 2024-01-16 07:17 | 2024-01-16 16:39 | 9:22 | S/O | S/D for Annual maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 2024-01-03 08:20 | 2024-01-03 19:00 | 10:40 | S/O | Bhulta 04 (230kV) shutdown due to CT (2133 R-ph) change. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-01 | 2024-01-01 10:03 | 2024-01-01 10:03 | 0:00 | S/O | Command by NLDC. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-02 | 2024-01-03 09:14 | 2024-01-03 15:37 | 6:23 | S/O | Ullon 02(132kV) scheduled shutdown, work at Ullon end. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-01-28 10:06 | 2024-01-28 15:10 | 5:04 | S/O | Deadline Checking | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-01-30 08:29 | 2024-01-30 17:47 | 9:18 | S/O | Hasnabad grid will do their Bay Maintenance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-1(D06) | 2024-01-26 09:45 | 2024-01-26 15:57 | 6:12 | S/O | Due to dead line checking and Insulator disk change. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2024-01-09 10:11 | 2024-01-09 15:19 | 5:08 | S/O | Insulator cleaning | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-01-01 09:18 | 2024-01-01 12:53 | 3:35 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 1 | 2024-01-17 09:26 | 2024-01-17 13:05 | 3:39 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2024-01-09 09:28 | 2024-01-09 12:56 | 3:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 210MW PDB L3 | 2024-01-13 10:11 | 2024-01-13 12:48 | 2:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-01-03 09:24 | 2024-01-03 21:22 | 11:58 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-01-13 10:47 | 2024-01-13 14:56 | 4:09 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2024-01-11 09:46 | 2024-01-11 16:58 | 7:12 | S/O | There is no work at siddhirganj end. work is going on at the other end. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Haripur 1 | 2024-01-27 08:44 | 2024-01-27 16:33 | 7:49 | S/O | maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-01-02 08:39 | 2024-01-02 16:29 | 7:50 | S/O | Annual maintenance Work. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-01 | 2024-01-31 08:33 | 2024-01-31 15:56 | 7:23 | S/O | Dead Line checking | 0 | 0 | No interruption
|  |  | Total : | 608:16 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV Grid Sub-Station | Bar Aulia | 2024-01-19 07:13 | 2024-01-21 19:42 | 60:29 | S/O | CB Commissioning. | 0 | 0 | No interruption
AKS 132/33kV Grid Sub-Station | Khulshi | 2024-01-27 07:26 | 2024-01-27 07:26 | 0:00 | D/W | Comand to Nldc | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | Rampur-01 | 2024-01-22 09:37 | 2024-01-22 14:27 | 4:50 | S/O | Anneal Maintenance. | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | Rampur-02 | 2024-01-17 15:41 | 2024-01-17 17:15 | 1:34 | S/O | Replacing Energy meter | 0 | 0 | No interruption
Agrabad 132/33kV Grid Sub-Station | Rampur-02 | 2024-01-23 08:57 | 2024-01-23 12:07 | 3:10 | S/O | annual maintenance | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | AKSML Ckt | 2024-01-26 08:59 | 2024-01-26 16:01 | 7:02 | S/O | Shutdown taken Baraulia ss for annual maintenance. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | AKSML Ckt | 2024-01-27 09:01 | 2024-01-27 15:50 | 6:49 | S/O | Shutdown taken by Baraulia ss for Deadline checking. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2024-01-27 07:33 | 2024-01-27 07:33 | 0:00 | D/W | Shutdown taken by ESPNER project. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-01-15 08:31 | 2024-01-15 17:14 | 8:43 | S/O | Annual maintenance, S/D done by NLDC instruction. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-01-26 06:38 | 2024-01-26 19:23 | 12:45 | D/W | Shutdown taken by ESPNER Project work. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | GPH Ispat Ckt | 2024-01-19 08:48 | 2024-01-19 15:07 | 6:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | GPH Ispat Ckt | 2024-01-20 09:32 | 2024-01-20 15:26 | 5:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-01-01 08:36 | 2024-01-01 18:16 | 9:40 | S/O | Annual maintenance. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-14 09:28 | 2024-01-14 16:14 | 6:46 | S/O | Annual line maintenance works | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-15 08:46 | 2024-01-15 15:20 | 6:34 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-16 09:34 | 2024-01-16 16:23 | 6:49 | S/O | Annual maintenance | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-17 09:09 | 2024-01-17 16:35 | 7:26 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-18 08:50 | 2024-01-18 16:24 | 7:34 | S/O |  | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-21 09:00 | 2024-01-21 17:26 | 8:26 | S/O | Dead line checking | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-01-22 09:06 | 2024-01-22 17:35 | 8:29 | S/O |  | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-23 08:53 | 2024-01-23 15:26 | 6:33 | S/O | Annual deadline checking. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-24 09:16 | 2024-01-24 15:52 | 6:36 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-25 09:13 | 2024-01-25 17:29 | 8:16 | S/O | Annual deadline checking. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-28 08:54 | 2024-01-28 16:38 | 7:44 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-29 09:07 | 2024-01-29 17:14 | 8:07 | S/O | Dead line checking | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-30 09:07 | 2024-01-30 17:10 | 8:03 | S/O | Annual maintenance work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-01-31 08:47 | 2024-01-31 16:51 | 8:04 | S/O | Dead line checking | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | PHP | 2024-01-01 08:28 | 2024-01-01 18:36 | 10:08 | S/O | For work in PHP S/S | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-01 | 2024-01-17 08:39 | 2024-01-17 15:43 | 7:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-01 | 2024-01-18 09:02 | 2024-01-18 15:40 | 6:38 | S/O | Annual maintenance (Line) | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2024-01-29 08:24 | 2024-01-29 18:20 | 9:56 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2024-01-30 08:44 | 2024-01-30 18:38 | 9:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2024-01-31 11:12 | 2024-01-31 13:30 | 2:18 | S/O | Kaptai end isolator and grounding work | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2024-01-20 08:42 | 2024-01-20 15:10 | 6:28 | S/O | Annual maintenance (ckt-1 bay) | 22 | 142.2667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2024-01-15 10:47 | 2024-01-15 16:22 | 5:35 | S/O | Annual maintenance (Bay) | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2024-01-04 06:12 | 2024-01-04 12:06 | 5:54 | D/W | SD Taken by Shikalbaha SS | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2024-01-16 09:53 | 2024-01-16 16:16 | 6:23 | S/O | annual maintenance (Bay) | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | BSRM CKT-2 | 2024-01-19 08:45 | 2024-01-19 15:03 | 6:18 | S/O | annual line maintenance | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | BSRM CKT-2 | 2024-01-20 09:28 | 2024-01-20 15:26 | 5:58 | S/O | annual maintenance | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2024-01-13 09:05 | 2024-01-13 13:21 | 4:16 | S/O | For 132kv Bus maintenance work in Julda sub-station. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-01-27 07:06 | 2024-01-27 11:25 | 4:19 | S/O | Khulshi grid 132 kV bus shutdown | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | AKSML-02 | 2024-01-12 11:20 | 2024-01-12 17:50 | 6:30 | S/O | Annual Maintenance and Deadline Checking | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | AKSML-02 | 2024-01-13 09:57 | 2024-01-13 17:20 | 7:23 | S/O | Dead line checking. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2024-01-01 09:12 | 2024-01-01 16:42 | 7:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2024-01-02 09:13 | 2024-01-02 16:48 | 7:35 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2024-01-03 09:18 | 2024-01-03 16:24 | 7:06 | S/O | Annual maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2024-01-04 09:03 | 2024-01-04 17:25 | 8:22 | S/O | Annual Maintenance and deadline checking | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Raojan-01 | 2024-01-24 09:50 | 2024-01-24 13:59 | 4:09 | S/O | Raozan power station requirement. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-01 | 2024-01-03 10:41 | 2024-01-03 14:37 | 3:56 | D/W | Project work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2024-01-03 08:45 | 2024-01-03 15:05 | 6:20 | S/O | Annual Maintenance (Line). | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 2024-01-13 09:07 | 2024-01-13 13:03 | 3:56 | S/O |  | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2024-01-13 09:07 | 2024-01-13 13:02 | 3:55 | S/O |  | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2024-01-04 08:50 | 2024-01-04 15:58 | 7:08 | S/O | Annual Dead Line Checking work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2024-01-13 09:07 | 2024-01-13 12:44 | 3:37 | S/O |  | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-1 | 2024-01-13 08:08 | 2024-01-13 13:27 | 5:19 | S/O | 132kV Main Bus Annual Maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-2 & 3 | 2024-01-13 08:50 | 2024-01-13 13:27 | 4:37 | S/O |  | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | KYCR Feeder | 2024-01-15 06:20 | 2024-01-15 22:40 | 16:20 | S/O | To Replace the 132 KV existing R phase cable AIS termination kit of 132KV KSRM-KYCR Transmission Line at KSRM 132/33 KV grid substation. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-AKSPL Line | 2024-01-19 07:17 | 2024-01-21 19:38 | 60:21 | S/O |  | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-MSML Line | 2024-01-02 09:13 | 2024-01-02 15:37 | 6:24 | S/O | Annual maintenance and dead line checking. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-MSML Line | 2024-01-09 11:50 | 2024-01-09 15:13 | 3:23 | D/W | ESPNCA project Materials unload by crane. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Madunaghat CKT-2 | 2024-01-16 08:56 | 2024-01-16 15:01 | 6:05 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Madunaghat CKT-2 | 2024-01-17 08:23 | 2024-01-17 17:00 | 8:37 | S/O | Annual maintenance and dead line checking. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Madunaghat CKT-2 | 2024-01-17 17:01 | 2024-01-18 17:42 | 24:41 | D/W | LILO work of 132/33kV Sholoshahar Grid Sub-Station by 400kV GNDP. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Madunaghat CKT-2 | 2024-01-19 10:54 | 2024-01-19 18:20 | 7:26 | S/O | Relay Setting of SPMD | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Sholoshahar CKT-1(Madunaghat) | 2024-01-14 08:36 | 2024-01-14 15:42 | 7:06 | S/O | Dead Line Checking | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-2 | 2024-01-10 08:40 | 2024-01-10 16:38 | 7:58 | S/O | Bay maintenance of Chahdraghona grid. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-1 | 2024-01-15 08:52 | 2024-01-15 16:03 | 7:11 | S/O | Annual deadline checking by Khushi Grid. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-1 | 2024-01-30 08:50 | 2024-01-30 13:52 | 5:02 | S/O | Annual Maintenance by Khulshi Grid, | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2024-01-11 09:39 | 2024-01-11 16:53 | 7:14 | S/O | annual bay maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | 150 MW Power Station -02 | 2024-01-15 11:01 | 2024-01-15 20:52 | 9:51 | D/W | EGCB Feni Sonagazi Solar powerplant 230kV GIS Bay Busbar protection system testing work. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Agrabad-1 | 2024-01-22 09:42 | 2024-01-22 14:26 | 4:44 | S/O | Agrabad Grid Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Agrabad-2 | 2024-01-17 16:42 | 2024-01-17 17:15 | 0:33 | S/O | The demand of agrabad grid | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Agrabad-2 | 2024-01-23 09:08 | 2024-01-23 12:06 | 2:58 | S/O | Annual Maintenance of Agrabad | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2024-01-27 07:14 | 2024-01-27 11:13 | 3:59 | S/O | Bus shutdown at khulshi Grid | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2024-01-27 07:14 | 2024-01-27 11:13 | 3:59 | S/O | Bus shutdown at khulshi Grid | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Julda-1 | 2024-01-19 07:30 | 2024-01-19 13:03 | 5:33 | S/O | Main BUS Shutdown | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Julda-2 | 2024-01-19 08:12 | 2024-01-19 13:04 | 4:52 | S/O |  | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha-1 | 2024-01-09 08:39 | 2024-01-09 17:16 | 8:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha-1 | 2024-01-19 07:40 | 2024-01-19 12:34 | 4:54 | S/O | Annual Maintenance BUS Shutdown | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha-2 | 2024-01-11 08:49 | 2024-01-11 16:28 | 7:39 | S/O | Deadline checking | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha-2 | 2024-01-19 07:40 | 2024-01-19 13:07 | 5:27 | S/O |  | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Anowara-1 | 2024-01-22 09:34 | 2024-01-22 16:02 | 6:28 | S/O | Dead line checking | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Anwara-2 | 2024-01-23 10:07 | 2024-01-23 16:26 | 6:19 | S/O |  | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2024-01-03 06:08 | 2024-01-03 17:28 | 11:20 | D/W |  | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2024-01-03 10:35 | 2024-01-03 14:36 | 4:01 | D/W |  | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2024-01-14 09:23 | 2024-01-14 15:03 | 5:40 | S/O |  | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Khulshi Ckt-1 | 2024-01-14 08:37 | 2024-01-14 15:41 | 7:04 | S/O | Annual Maintenance (Dead Line Checking) by Khulshi Grid | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Madunaghat Ckt-1 | 2024-01-15 08:50 | 2024-01-15 16:04 | 7:14 | S/O | Annual Maintenance (Dead Line Checking) by Khulshi 132/33kV Grid S/S. | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Madunaghat Ckt-1 | 2024-01-30 08:49 | 2024-01-30 13:53 | 5:04 | S/O | Shutdown | 0 | 0 | No interruption
|  |  | Total : | 695:18 |  | Unserved Energy: |  | 142.2667
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | Sylhet-Fenchugang -T -Branibazar-1 | 2024-01-20 08:15 | 2024-01-20 15:40 | 7:25 | D/W | 1. Line Termination of Beanibazar Line 01 & 02 2. Loop connection of Beanibazar Line 02 | 26 | 192.8333 | Power interruption
Bibiana 400/230kV Sub-Station | Bibi-Fen Ckt-I | 2024-01-01 09:22 | 2024-01-01 17:46 | 8:24 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibiyana-III GTG | 2024-01-19 11:45 | 2024-01-19 11:45 | 0:00 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibiyana-South | 2024-01-27 09:30 | 2024-01-28 00:32 | 15:02 | S/O | Maintenance of UAT | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-01-23 08:56 | 2024-01-23 17:16 | 8:20 | S/O | Annual maintenance. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-01-10 09:27 | 2024-01-10 16:13 | 6:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-01-11 09:41 | 2024-01-11 15:42 | 6:01 | S/O | Annual maintenance. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-01-13 09:33 | 2024-01-13 16:05 | 6:32 | S/O | Annual maintenance and death line check. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-01-14 10:01 | 2024-01-14 17:17 | 7:16 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-01-11 09:58 | 2024-01-11 15:49 | 5:51 | S/O | Annual maintenance. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-01-16 10:13 | 2024-01-16 17:31 | 7:18 | S/O | annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-01-17 09:17 | 2024-01-17 16:02 | 6:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-01-18 09:59 | 2024-01-18 17:15 | 7:16 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2024-01-01 11:05 | 2024-01-01 14:35 | 3:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2024-01-02 08:43 | 2024-01-02 16:25 | 7:42 | S/O | NLDC AE. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2024-01-13 08:43 | 2024-01-13 17:39 | 8:56 | S/O | NLDC. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2024-01-20 09:45 | 2024-01-20 15:53 | 6:08 | S/O | Annual maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2024-01-21 08:53 | 2024-01-21 16:40 | 7:47 | S/O | Annual maintenance. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 2024-01-27 08:36 | 2024-01-27 16:58 | 8:22 | S/O | Annually maintenance | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2024-01-28 08:39 | 2024-01-28 17:36 | 8:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2024-01-01 08:10 | 2024-01-01 17:06 | 8:56 | S/O | For annual maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2024-01-02 08:24 | 2024-01-02 15:30 | 7:06 | S/O | For Annual Maintenance works | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-01-03 07:51 | 2024-01-03 16:44 | 8:53 | S/O | Shut Down For Annual Maintenance works, | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-01-04 08:19 | 2024-01-04 15:38 | 7:19 | S/O | Yearly Deadline Checking. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-01-31 07:19 | 2024-01-31 19:40 | 12:21 | D/W | For Project Works. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2024-01-23 08:48 | 2024-01-23 16:52 | 8:04 | S/O | Due to yearly maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-01-24 08:20 | 2024-01-24 17:24 | 9:04 | S/O | Annual Maintenace ( dead line checking) | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-01-25 08:32 | 2024-01-25 14:40 | 6:08 | S/O | Yearly Schedule Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Cumilla(S) Ckt-3 | 2024-01-24 12:08 | 2024-01-24 14:24 | 2:16 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Cumilla(S) Ckt-3 | 2024-01-29 09:33 | 2024-01-29 20:45 | 11:12 | S/O | Annual maintenance work(Bay) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-01-24 09:09 | 2024-01-24 12:05 | 2:56 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2024-01-22 08:30 | 2024-01-22 16:17 | 7:47 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2024-01-23 08:37 | 2024-01-23 16:15 | 7:38 | S/O | Disc Cleaning | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2024-01-14 09:41 | 2024-01-14 17:24 | 7:43 | S/O | Disc Cleaning | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2024-01-27 07:34 | 2024-01-27 19:18 | 11:44 | D/W | Project work. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-2 | 2024-01-24 07:10 | 2024-01-24 17:34 | 10:24 | D/W |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-2 | 2024-01-25 07:10 | 2024-01-25 18:08 | 10:58 | S/O | Maintenance Work BSRM SS Side | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2024-01-16 10:05 | 2024-01-16 16:17 | 6:12 | S/O | Annual Maintenance(deadline check) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2024-01-17 09:26 | 2024-01-17 14:38 | 5:12 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-1 | 2024-01-12 06:48 | 2024-01-12 10:49 | 4:01 | D/W | Project work in cumilla north end. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-1 | 2024-01-25 08:45 | 2024-01-25 10:53 | 2:08 | S/O |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-1 | 2024-01-30 09:18 | 2024-01-30 16:03 | 6:45 | S/O |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-2 | 2024-01-12 06:49 | 2024-01-12 10:49 | 4:00 | D/W | Project work in cumilla north end. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-2 | 2024-01-21 09:43 | 2024-01-21 15:22 | 5:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-2 | 2024-01-25 10:54 | 2024-01-25 12:45 | 1:51 | S/O |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-01-12 06:49 | 2024-01-12 10:49 | 4:00 | D/W | Project work in cumilla north end. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-01-24 12:07 | 2024-01-24 14:25 | 2:18 | D/W | Project Work at Cumilla (N) | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-01-28 10:08 | 2024-01-28 17:03 | 6:55 | S/O | Annual maintenance. | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-01-29 09:32 | 2024-01-29 20:49 | 11:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-2 | 2024-01-12 09:54 | 2024-01-12 16:06 | 6:12 | S/O | SD Nature Defect Rectification of Line (Agaratala TLM) | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-01-09 08:43 | 2024-01-09 12:26 | 3:43 | S/O | Relay test at Daudkandi Grid. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-01-09 12:28 | 2024-01-09 13:45 | 1:17 | S/O | Relay Testing by SPMD Cumilla | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Bibiyana-1 | 2024-01-02 09:08 | 2024-01-02 17:01 | 7:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Bibiyana-1 | 2024-01-14 09:03 | 2024-01-14 13:45 | 4:42 | S/O | Relay testing by SPMD cumilla. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Bibiyana-2 | 2024-01-14 14:25 | 2024-01-14 17:39 | 3:14 | S/O | SPMD works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-1 | 2024-01-17 10:02 | 2024-01-17 14:35 | 4:33 | S/O | Relay test | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2024-01-17 14:39 | 2024-01-17 16:52 | 2:13 | S/O | Spmd work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2024-01-22 08:37 | 2024-01-22 12:00 | 3:23 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2024-01-25 08:40 | 2024-01-25 15:46 | 7:06 | S/O | Dead line checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-01-20 07:45 | 2024-01-20 15:34 | 7:49 | S/O | As per instructions of NLDC | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-01-22 09:01 | 2024-01-22 21:48 | 12:47 | S/O | Emergency 132KV BUS -1 DS 110-89A Maintenance. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Barayerhat Ckt | 2024-01-10 08:41 | 2024-01-10 14:12 | 5:31 | S/O | AMS-2023-24 | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Barayerhat Ckt | 2024-01-11 08:39 | 2024-01-11 16:00 | 7:21 | S/O | dead line checking | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-01-09 08:36 | 2024-01-09 15:50 | 7:14 | S/O | AMS-2023-24 | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-1 | 2024-01-29 08:41 | 2024-01-30 16:53 | 32:12 | D/W | EEGBPS Project work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2024-01-01 08:45 | 2024-01-01 18:38 | 9:53 | S/O | Annual Maintenance of Php Shat Down | 1 | 9.8833 | Power interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2024-01-13 08:25 | 2024-01-13 14:02 | 5:37 | S/O | Yearly Maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj-Chowmuhani Ckt-01 | 2024-01-22 08:30 | 2024-01-22 15:28 | 6:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj-Desh Energy Ckt-02 | 2024-01-15 08:48 | 2024-01-15 14:44 | 5:56 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Ramgonj-Desh Energy Ckt-02 | 2024-01-16 10:16 | 2024-01-16 16:02 | 5:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-01 | 2024-01-14 08:50 | 2024-01-14 17:09 | 8:19 | S/O | Maintenace work. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2024-01-23 08:47 | 2024-01-23 17:17 | 8:30 | S/O | A/M | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-01-23 08:23 | 2024-01-23 17:02 | 8:39 | S/O | None | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-01-24 08:40 | 2024-01-24 16:36 | 7:56 | S/O | Annual maintenance work at Fenchuganj SS | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2024-01-27 08:47 | 2024-01-27 16:29 | 7:42 | S/O | A/M | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2024-01-28 08:29 | 2024-01-28 15:58 | 7:29 | S/O | A/M | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2024-01-29 08:40 | 2024-01-29 15:35 | 6:55 | S/O | Annual maintenance work at Fenchuganj SS | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-01-20 07:47 | 2024-01-20 15:35 | 7:48 | S/O | biyanibajar line maint.. work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-01-20 07:47 | 2024-01-20 15:35 | 7:48 | S/O | biyanibajar line maint.. work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 150MW GT PS | 2024-01-20 16:33 | 2024-01-31 20:17 | 267:44 | D/W | Annual Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2024-01-04 18:17 | 2024-01-05 09:50 | 15:33 | D/W | Testing Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2024-01-05 17:01 | 2024-01-08 12:13 | 67:12 | D/W | Overhauling and Plant testing Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2024-01-09 10:32 | 2024-01-09 11:11 | 0:39 | D/W | Testing Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-01-16 08:56 | 2024-01-16 15:23 | 6:27 | S/O | Yearly Maintenance purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-01-17 08:36 | 2024-01-17 15:03 | 6:27 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-01-21 09:19 | 2024-01-21 11:37 | 2:18 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
|  |  | Total : | 933:51 |  | Unserved Energy: |  | 202.7167
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Goalpara Line | 2024-01-20 08:27 | 2024-01-20 17:09 | 8:42 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Goalpara Line | 2024-01-21 09:15 | 2024-01-21 17:35 | 8:20 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Goalpara Line | 2024-01-22 08:58 | 2024-01-22 16:08 | 7:10 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Barguna-Bakergonj 132kv line | 2024-01-13 07:53 | 2024-01-13 17:40 | 9:47 | S/O | Annual Maintenance ( Barguna-Bakergonj 132KV line ). | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Barguna-Bakergonj 132kv line | 2024-01-14 07:44 | 2024-01-14 17:08 | 9:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Barguna-Bakergonj 132kv line | 2024-01-15 08:14 | 2024-01-15 17:24 | 9:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kV Barishal north ckt-1 | 2024-01-28 09:29 | 2024-01-28 17:22 | 7:53 | S/O | Due to annual maintenance work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kV Barishal north ckt-2 | 2024-01-29 08:18 | 2024-01-29 17:33 | 9:15 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kV Barishal north ckt-2 | 2024-01-30 10:06 | 2024-01-30 16:51 | 6:45 | S/O | Annual maintenance. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-01-20 09:02 | 2024-01-20 16:14 | 7:12 | S/O | Annual maintenance work. | 12 | 86.4 | Power interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-01-21 09:49 | 2024-01-21 16:04 | 6:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-01-22 09:05 | 2024-01-22 17:04 | 7:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-01-23 09:30 | 2024-01-23 16:36 | 7:06 | S/O | Annual maintenance | 23 | 163.3 | Power interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-1 | 2024-01-16 09:35 | 2024-01-16 17:12 | 7:37 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-1 | 2024-01-17 08:58 | 2024-01-17 16:37 | 7:39 | S/O | Date Line checking | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2024-01-18 08:53 | 2024-01-18 16:10 | 7:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2024-01-19 08:49 | 2024-01-19 16:31 | 7:42 | S/O | Annula Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2024-01-20 08:46 | 2024-01-20 12:25 | 3:39 | S/O | Annual maintenance work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2024-01-21 09:46 | 2024-01-21 13:53 | 4:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Jashore-1 | 2024-01-23 08:15 | 2024-01-23 16:15 | 8:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Jashore-1 | 2024-01-24 08:16 | 2024-01-24 16:59 | 8:43 | S/O | Annual maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Jashore-2 | 2024-01-10 08:29 | 2024-01-10 17:24 | 8:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-01-24 09:32 | 2024-01-24 16:26 | 6:54 | S/O | Annual maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2024-01-24 09:34 | 2024-01-24 16:16 | 6:42 | S/O |  | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2024-01-25 09:24 | 2024-01-25 15:58 | 6:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2024-01-27 09:49 | 2024-01-27 14:46 | 4:57 | S/O | Annual maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2024-01-29 10:45 | 2024-01-29 14:42 | 3:57 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2024-01-29 09:23 | 2024-01-29 15:47 | 6:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2024-01-30 09:20 | 2024-01-30 14:44 | 5:24 | S/O | Annual maintenance. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-NWPGCL | 2024-01-23 08:54 | 2024-01-23 15:40 | 6:46 | S/O | Annual Maintenance works | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-NWPGCL | 2024-01-26 08:10 | 2024-01-26 16:28 | 8:18 | S/O | bythe instruction of ALDC Khulna | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-01-22 08:50 | 2024-01-22 17:22 | 8:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-1 | 2024-01-03 08:50 | 2024-01-03 17:46 | 8:56 | S/O | E/M | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-1 | 2024-01-30 08:48 | 2024-01-30 17:36 | 8:48 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-2 | 2024-01-03 08:50 | 2024-01-03 17:33 | 8:43 | S/O | E/M | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-2 | 2024-01-04 08:37 | 2024-01-04 19:10 | 10:33 | S/O | Y/M | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Modhumoti 100MW PS | 2024-01-16 08:59 | 2024-01-16 17:32 | 8:33 | S/O | Yearly maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Modhumoti 100MW PS | 2024-01-17 09:02 | 2024-01-17 16:32 | 7:30 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-2 | 2024-01-23 09:55 | 2024-01-23 16:29 | 6:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-1 | 2024-01-04 07:41 | 2024-01-04 19:09 | 11:28 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-2 | 2024-01-31 08:28 | 2024-01-31 17:25 | 8:57 | S/O | Annual maintenance work gopalganj end | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2024-01-29 08:51 | 2024-01-29 16:11 | 7:20 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2024-01-23 09:14 | 2024-01-23 16:31 | 7:17 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2024-01-24 09:25 | 2024-01-24 16:23 | 6:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2024-01-25 09:21 | 2024-01-25 15:58 | 6:37 | S/O | Annual Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-3 | 2024-01-15 08:37 | 2024-01-15 17:45 | 9:08 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2024-01-11 08:44 | 2024-01-11 17:02 | 8:18 | S/O | Annual maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2024-01-15 08:37 | 2024-01-15 17:45 | 9:08 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-1 | 2024-01-15 09:38 | 2024-01-15 21:18 | 11:40 | D/W |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-1 | 2024-01-16 08:32 | 2024-01-16 17:49 | 9:17 | D/W | SAS Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-1 | 2024-01-31 14:17 | 2024-01-31 16:15 | 1:58 | D/W |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-2 | 2024-01-17 09:35 | 2024-01-17 17:33 | 7:58 | D/W |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-2 | 2024-01-31 16:25 | 2024-01-31 16:58 | 0:33 | D/W |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-01-22 08:36 | 2024-01-23 19:42 | 35:06 | S/O | Payra ps end maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-01-31 08:41 | 2024-01-31 12:15 | 3:34 | D/W | SAS Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-01-24 08:39 | 2024-01-26 18:30 | 57:51 | S/O |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-01-30 09:24 | 2024-01-30 19:04 | 9:40 | D/W |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2024-01-31 12:30 | 2024-01-31 14:04 | 1:34 | D/W |  | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-2 | 2024-01-31 10:19 | 2024-01-31 12:06 | 1:47 | D/W | SAS Commissioning | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North- West Ckt-2 | 2024-01-26 08:10 | 2024-01-26 17:29 | 9:19 | S/O | Maintenance work North -West side. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North-WestCkt-1 | 2024-01-26 08:10 | 2024-01-26 17:27 | 9:17 | S/O | Maintenance north -west side | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-01-24 10:33 | 2024-01-24 10:33 | 0:00 | S/O | NWPGCL Project Work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-03 | 2024-01-09 09:21 | 2024-01-09 17:04 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2024-01-11 08:40 | 2024-01-11 17:01 | 8:21 | S/O | Annual maintenance. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2024-01-15 08:39 | 2024-01-15 17:46 | 9:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Shariatpur CKT-01 | 2024-01-02 08:20 | 2024-01-02 17:43 | 9:23 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Shariatpur CKT-02 | 2024-01-01 07:52 | 2024-01-01 17:31 | 9:39 | S/O | Annual maintenence. | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Magura 1 | 2024-01-13 08:04 | 2024-01-13 16:37 | 8:33 | S/O | Narail - Magura line-1 & Associated Equipment | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Magura 1 | 2024-01-15 08:24 | 2024-01-15 14:54 | 6:30 | S/O | Annual Maintenance and Associate Equipment. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Barishal-Pautakhali 132kV Line | 2024-01-13 07:56 | 2024-01-13 17:39 | 9:43 | S/O | Annual maintenance. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Barishal-Pautakhali 132kV Line | 2024-01-14 06:46 | 2024-01-14 06:46 | 0:00 | S/O | Annual maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-01-15 08:45 | 2024-01-15 16:37 | 7:52 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-01-16 08:55 | 2024-01-16 15:49 | 6:54 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-1 | 2024-01-17 09:43 | 2024-01-17 16:10 | 6:27 | S/O |  | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-01-20 08:31 | 2024-01-20 16:10 | 7:39 | S/O | Annual maintenance. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Bheramara-2 | 2024-01-21 08:36 | 2024-01-21 15:33 | 6:57 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2024-01-29 09:22 | 2024-01-29 15:47 | 6:25 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2024-01-30 09:21 | 2024-01-30 14:45 | 5:24 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur -1 | 2024-01-27 09:41 | 2024-01-27 14:46 | 5:05 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur -1 | 2024-01-28 08:54 | 2024-01-28 16:25 | 7:31 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur -1 | 2024-01-29 10:44 | 2024-01-29 14:42 | 3:58 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-1 | 2024-01-31 12:33 | 2024-01-31 12:33 | 0:00 | D/W | SAS test at Gopalgonj End | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-2 | 2024-01-31 10:07 | 2024-01-31 12:13 | 2:06 | D/W | SAS testing at gopalgonj end | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Khulna Line-1 | 2024-01-24 10:37 | 2024-01-24 10:37 | 0:00 | D/W | NLDC Requirement (Khulna ALDC) | 0 | 0 | No interruption
|  |  | Total : | 662:44 |  | Unserved Energy: |  | 249.7
HVDC Grid Circle :
BIPTC | Baharampur-1 | 2024-01-20 10:15 | 2024-01-20 18:45 | 8:30 | S/O | Annual shutdown | 0 | 0 | No interruption
BIPTC | Baharampur-1 | 2024-01-21 10:49 | 2024-01-21 17:38 | 6:49 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2024-01-23 10:43 | 2024-01-23 18:45 | 8:02 | S/O | Annual maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-2 | 2024-01-24 09:48 | 2024-01-24 16:57 | 7:09 | S/O | Shutdown is taken for annual maintenance work | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-01-27 10:20 | 2024-01-27 19:00 | 8:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-01-28 09:12 | 2024-01-28 18:57 | 9:45 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2024-01-29 09:05 | 2024-01-29 19:58 | 10:53 | S/O | Annual maintenance | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2024-01-30 10:24 | 2024-01-30 19:10 | 8:46 | S/O | Annual Maintenance. | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2024-01-31 10:38 | 2024-01-31 19:12 | 8:34 | S/O | Annual Maintenance | 0 | 0 | No interruption
BIPTC | Bheramara-1 | 2024-01-09 09:05 | 2024-01-09 15:20 | 6:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-1 | 2024-01-27 07:36 | 2024-01-27 13:57 | 6:21 | D/W | IDRNPP,400kV Rooppur Dhaka Phase-2 Stringing Work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-2 | 2024-01-27 07:39 | 2024-01-27 13:59 | 6:20 | D/W | IDRNPP,400kV Rooppur Dhaka Phase-2 Stringing Work | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | HVDC 2 | 2024-01-10 08:36 | 2024-01-10 16:03 | 7:27 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2024-01-12 09:27 | 2024-01-12 13:29 | 4:02 | S/O | Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2024-01-27 09:04 | 2024-01-27 19:56 | 10:52 | S/O | A/M | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 1 | 2024-01-15 08:44 | 2024-01-15 16:37 | 7:53 | S/O | Annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 1 | 2024-01-16 08:54 | 2024-01-16 15:49 | 6:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 1 | 2024-01-17 09:44 | 2024-01-17 16:12 | 6:28 | S/O | A/M | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 2 | 2024-01-20 08:32 | 2024-01-20 16:11 | 7:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 2 | 2024-01-21 08:36 | 2024-01-21 15:32 | 6:56 | S/O | A/M | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-1 | 2024-01-27 08:32 | 2024-01-27 19:15 | 10:43 | S/O | 132/33 kV Bus shutdown | 30 | 321.5 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-2 | 2024-01-27 08:32 | 2024-01-27 19:17 | 10:45 | S/O | 132/33 kV Bus shutdown | 30 | 322.5 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-01-31 09:21 | 2024-01-31 18:22 | 9:01 | S/O | G to G work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -1 | 2024-01-12 09:26 | 2024-01-12 13:28 | 4:02 | S/O | Annual Maintanance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -2 | 2024-01-28 08:58 | 2024-01-28 15:54 | 6:56 | S/O | conductor replacement | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Pabna | 2024-01-26 08:32 | 2024-01-26 15:55 | 7:23 | S/O | for pabna Bus S/D | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2024-01-31 09:11 | 2024-01-31 17:46 | 8:35 | S/O |  | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2024-01-12 08:47 | 2024-01-12 17:15 | 8:28 | D/W | insulator and hardwire fittings checking | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2024-01-26 08:59 | 2024-01-26 12:02 | 3:03 | D/W | None | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2024-01-26 08:59 | 2024-01-26 12:02 | 3:03 | D/W | None | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | BEN-1 | 2024-01-25 08:16 | 2024-01-25 16:10 | 7:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | BEN-2 | 2024-01-09 08:24 | 2024-01-09 16:51 | 8:27 | S/O | Annual Maintanance Benapole end | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | BEN-2 | 2024-01-11 08:08 | 2024-01-11 17:09 | 9:01 | S/O | Annual Maintenance from Benapole End | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2024-01-22 08:21 | 2024-01-22 13:41 | 5:20 | D/W | For project works | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2024-01-23 08:14 | 2024-01-23 12:13 | 3:59 | D/W | Tower Piling Project work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2024-01-02 07:48 | 2024-01-02 16:19 | 8:31 | S/O | ANNUAL MAINTANANCE FOR NOAPARA END | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2024-01-03 08:08 | 2024-01-03 16:17 | 8:09 | S/O | Annual Maintenance From Noapara End | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2024-01-04 09:13 | 2024-01-04 13:46 | 4:33 | S/O | Annual Maintanance Noapara End | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-HVDC Ckt-1 | 2024-01-01 08:29 | 2024-01-01 16:57 | 8:28 | S/O | annual maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-HVDC Ckt-1 | 2024-01-02 08:26 | 2024-01-02 15:24 | 6:58 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-HVDC Ckt-2 | 2024-01-17 07:47 | 2024-01-17 16:58 | 9:11 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-HVDC Ckt-2 | 2024-01-18 10:17 | 2024-01-18 15:44 | 5:27 | S/O | Annual Maintanance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-2 | 2024-01-09 13:07 | 2024-01-21 19:35 | 294:28 | D/W | Project works Khulna side | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2024-01-22 08:22 | 2024-01-22 13:42 | 5:20 | D/W | Kaligonj line lilo works | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 1 | 2024-01-14 08:14 | 2024-01-14 15:39 | 7:25 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 2024-01-16 08:15 | 2024-01-16 16:18 | 8:03 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 2024-01-17 08:23 | 2024-01-17 15:34 | 7:11 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 2 | 2024-01-18 12:15 | 2024-01-18 15:32 | 3:17 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Ishwardi Line | 2024-01-29 08:34 | 2024-01-29 17:41 | 9:07 | S/O |  | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Ishwardi Line | 2024-01-30 10:38 | 2024-01-30 11:33 | 0:55 | S/O |  | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2024-01-19 08:41 | 2024-01-19 17:00 | 8:19 | S/O | Shahjadpur grid Annual Bus Shutdown. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Pabna | 2024-01-09 08:10 | 2024-01-09 20:05 | 11:55 | S/O | Annal Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Pabna | 2024-01-10 08:48 | 2024-01-10 16:25 | 7:37 | S/O | None | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Pabna | 2024-01-26 08:33 | 2024-01-26 16:09 | 7:36 | S/O | For bus maintenance | 20 | 152 | Power interruption
Ullahpara 132/33kV Grid Sub-Station | Baghabari ckt | 2024-01-19 11:43 | 2024-01-19 19:43 | 8:00 | S/O | None | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Shahjadpur Ckt | 2024-01-19 07:44 | 2024-01-19 19:52 | 12:08 | S/O | None | 0 | 0 | No interruption
|  |  | Total : | 703:34 |  | Unserved Energy: |  | 796
Bogura Grid Circle :
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2024-01-25 09:18 | 2024-01-25 20:16 | 10:58 | D/W | Project work at Bogura SS End. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2024-01-26 09:08 | 2024-01-26 17:42 | 8:34 | D/W |  | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2024-01-27 12:13 | 2024-01-27 14:44 | 2:31 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2024-01-20 07:46 | 2024-01-20 17:46 | 10:00 | D/W | For project work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2024-01-20 07:48 | 2024-01-20 17:47 | 9:59 | D/W |  | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Mahasthangarh-1 | 2024-01-03 08:29 | 2024-01-03 15:06 | 6:37 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Mahasthangarh-2 | 2024-01-13 08:43 | 2024-01-13 16:13 | 7:30 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | New Bogura-1 | 2024-01-15 08:24 | 2024-01-15 15:45 | 7:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogra 132KV Line-2 | 2024-01-16 09:03 | 2024-01-16 18:02 | 8:59 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2024-01-23 07:05 | 2024-01-23 09:09 | 2:04 | S/O | Red Maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-1 | 2024-01-27 09:40 | 2024-01-27 10:45 | 1:05 | S/O | Maintenance Work. (132kV Bogura old S/S) | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-2 | 2024-01-27 10:58 | 2024-01-27 12:02 | 1:04 | S/O | Maintenance work. (132kV Bogura old S/S) | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-02 | 2024-01-01 08:49 | 2024-01-01 17:30 | 8:41 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-02 | 2024-01-02 08:57 | 2024-01-02 17:19 | 8:22 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-02 | 2024-01-23 11:57 | 2024-01-23 12:32 | 0:35 | S/O | Due to Energy Meter Change By Metering Division. | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Bogura 1 | 2024-01-04 09:22 | 2024-01-04 17:29 | 8:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Bogura 2 | 2024-01-14 09:16 | 2024-01-14 16:32 | 7:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari-1 | 2024-01-27 08:16 | 2024-01-27 16:51 | 8:35 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari-2 | 2024-01-30 08:17 | 2024-01-30 15:16 | 6:59 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari-2 | 2024-01-31 08:48 | 2024-01-31 15:38 | 6:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2024-01-19 06:15 | 2024-01-19 08:02 | 1:47 | D/W | Shutdown for Joypurhat Side | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-01-30 07:17 | 2024-01-30 17:45 | 10:28 | S/O | Shut down performed on the oder of ALDC Bogura. | 65 | 680.3333 | Power interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2024-01-09 09:30 | 2024-01-09 11:16 | 1:46 | S/O | Earthing improvement. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2024-01-09 11:49 | 2024-01-09 13:14 | 1:25 | S/O | Earthing improvement. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-1 | 2024-01-10 09:38 | 2024-01-10 11:36 | 1:58 | S/O | L.A earthing improvment. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Rajshahi-2 | 2024-01-10 11:39 | 2024-01-10 13:26 | 1:47 | S/O | LA, earthing improvment | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mithapukur-01 | 2024-01-28 08:36 | 2024-01-28 16:07 | 7:31 | S/O | Maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mithapukur-01 | 2024-01-29 08:15 | 2024-01-29 15:38 | 7:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Bus Coupler | 2024-01-04 09:47 | 2024-01-04 09:47 | 0:00 | S/O | Main Breaker Commissioning work of Rajshahi old to Rajshahi New 132KVT/L-2 | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Bus Coupler | 2024-01-16 09:14 | 2024-01-16 11:55 | 2:41 | S/O | Due to T-3 (II) 33 KV BUS S/D. | 19.5 | 52.325 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2024-01-29 08:29 | 2024-01-29 12:25 | 3:56 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2024-01-04 09:47 | 2024-01-04 17:12 | 7:25 | S/O | same reason | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2024-01-27 12:13 | 2024-01-27 14:43 | 2:30 | S/O | As the instruction of ALDC, Bogura | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-02 | 2024-01-13 11:24 | 2024-01-13 15:37 | 4:13 | S/O | As the instructions of ALDC, Bogura | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Jaldhaka CKT-02 | 2024-01-03 09:01 | 2024-01-03 17:20 | 8:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Purbosadipur CKT-02 | 2024-01-09 10:50 | 2024-01-09 12:17 | 1:27 | S/O | For x-former shifting work of purbasadipur grid | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2024-01-20 07:45 | 2024-01-20 17:45 | 10:00 | D/W | solar project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2024-01-20 07:46 | 2024-01-20 17:46 | 10:00 | D/W | solar project work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Baghabari -01 | 2024-01-01 08:28 | 2024-01-01 17:37 | 9:09 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Baghabari -01 | 2024-01-02 08:50 | 2024-01-02 16:32 | 7:42 | S/O | Due to annual maintenance work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Baghabari -02 | 2024-01-03 08:38 | 2024-01-03 17:17 | 8:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Baghabari -02 | 2024-01-04 08:18 | 2024-01-04 15:37 | 7:19 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 249:32 |  | Unserved Energy: |  | 732.6583
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 4651:29 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:January 2024
| Area | Previous Month (December' 2023) |  |  |  | Current Month (January '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 21 | 6 | 224 | 251 | 11 | 18 | 226 | 255
2 | Dhaka (South) Grid Circle. | 17 | 19 | 114 | 150 | 26 | 25 | 119 | 170
3 | Chattogram Grid Circle. | 2 | 6 | 89 | 97 | 1 | 4 | 116 | 121
4 | Cumilla Grid Circle. | 7 | 3 | 150 | 160 | 1 | 13 | 122 | 136
5 | Khulna Grid Circle. | 4 | 11 | 110 | 125 | 4 | 6 | 113 | 123
6 | HVDC Grid Circle | 7 | 5 | 66 | 78 | 4 | 6 | 95 | 105
7 | Bogura Grid Circle. | 8 | 15 | 234 | 257 | 6 | 11 | 74 | 91
8 | Others | Total number of S/O: 2; Total number of Total: 2; Total number of Total: 2
9 | Total | 66 | 65 | 989 | 1120 | 53 | 83 | 865 | 1003
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:January 2024
| Area | Previous Month (December' 2023) |  |  |  | Current Month (January '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 127.46 | 426.33 | 3895.5 | 4449.29 | 212.8 | 603.17 | 1085.63 | 1901.6
2 | Dhaka (South) Grid Circle. | 724.14 | 910.78 | 594.57 | 2229.49 | 823.02 | 29.75 | 152.67 | 1005.44
3 | Chattogram Grid Circle. |  | 6.5 | 556.45 | 562.95 |  | 5.13 | 341.4 | 346.53
4 | Cumilla Grid Circle. | 7.4 | 18.67 | 4629.07 | 4655.14 | 4.67 | 1.33 | 207.3 | 213.3
5 | Khulna Grid Circle. | 5 | 5.4 | 409.1 | 419.5 | 24.5 | 33 | 415.52 | 473.02
6 | HVDC Grid Circle | 184.92 | 66.67 | 863.38 | 1114.97 | 723.25 | 24.81 | 2885.4 | 3633.46
7 | Bogura Grid Circle. | 138.97 | 36.3 | 4957.15 | 5132.42 | 39.05 | 336.97 | 2434.69 | 2810.71
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1187.89 | 1470.65 | 15905.22 | 18563.76 | 1827.29 | 1034.16 | 7522.61 | 10384.06
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:January 2024
A) Power Interruption | [10 empty] | 2 | 1
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 8 | 18 | 3 | 4 | 11 | 990.13
2 | Dhaka (South) | 5031.6 | 2 | 2 | 4 | - | - | 4 | 189.59
3 | Chattogram | 2042 | 1 | 5 | 6 | 2 | - | 4 | 204.27
4 | Khulna | 2434 | 5 | 4 | 9 | 4 |  | 5 | 223.31
5 | HVDC | 5954.3 | 4 | 10 | 14 | 3 | 1 | 10 | 2837.47
6 | Bogura | 3145.6 | 5 | 11 | 16 | 2 |  | 14 | 2039
7 | Cumilla | 2981 | 2 | 3 | 5 | 4 | 1 |  | 10.58
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 6494.35
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.98%
5 | HVDC | 99.94% | [6 empty] | Executive Engineer
6 | Bogura | 99.97% | [6 empty] | Information Management Division
7 | Cumilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:January 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | 4 | 4 | - | - | 4 | 911.47
2 | Dhaka (South) | 990.29 | - | 4 |  | 4 | 1 | 1 | 2 | 815.85
3 | Chattogram | 917 | - | - | 1 | 1 | - | - | 1 | 142.27
4 | Khulna | 1238.4 | - | - | 2 | 2 | - | - | 2 | 249.7
5 | HVDC | 1325 | - |  | 3 | 3 | - | - | 3 | 796
6 | Bogura | 1803.3 | - | 3 | 2 | 5 | 1 | 2 | 2 | 771.71
7 | Cumilla | 1648.16 | - |  | 2 | 2 | - | - | 2 | 202.72
8 | Others | - | - | 2 | 2 | 4 | - | - | 1 | -
| Total | 10176.6215 | [7 empty] | 3889.72
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.98%
7 | Cumilla | 100%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:January 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-01-01 | 12 | - | 2 | 1hr31 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:January 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Jamalpur 132/33kV Grid Sub-Station | 2 | 3:46 | 85.5
Kabirpur 132/33kV Grid Sub-Station | 5 | 7:49 | 687.17
Savar 132/33kV Grid Sub-Station | 3 | 1:00 | 43.33
Bhaluka 132/33kV Grid Sub-Station | 2 | 6:09 | 43.58
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:58 | 19.6667
Joydebpur 132/33kV Grid Sub-Station | 3 | 1:01 | 14.58
Kishoreganj 132/33kV Grid Sub-Station | 1 | 0:12 | 6
Mymensingh 132/33kV Grid Sub-Station | 1 | 4:31 | 90.3333
Aminbazar 400/230/132kV Grid Sub-Station | 2 | 13:26 | 510.47
Mymensingh 132/33kV Grid Sub-Station | 1 | 3:48 | 190
Tangail 132/33kV Grid Sub-Station | 1 | 3:31 | 211
Madanganj 132/33kV Grid Sub-Station | 1 | 1:26 | 7.1667
Sonargaon 132/33kV Grid Sub-Station | 1 | 1:59 | 29.75
Haripur 230/132kV Grid Sub-Station | 2 | 0:58 | 55.73
Matuail 132/33kV Grid Sub-Station | 1 | 7:33 | 294.45
Sonargaon 132/33kV Grid Sub-Station | 3 | 52:23 | 618.33
Halishahar 132/33kV Grid Sub-Station | 1 | 0:28 | 5.1333
Dohazari 132/33kV Grid Sub-Station | 2 | 1:09 | 25.3
Juldah 132/33kV Grid Sub-Station | 2 | 8:14 | 59.83
Khulshi 132/33kV Grid Sub-Station | 1 | 3:48 | 114
Coxsbazar 132/33kV Grid Sub-Station | 1 | 6:28 | 142.2667
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 0:08 | 1.3333
Chandpur 132/33kV Grid Sub-Station | 2 | 0:53 | 8.52
Sylhet (South) 132/33kV GIS Grid Sub-Station | 1 | 0:22 | 0.73
Beanibazar 132/33kV Grid Sub-Station | 1 | 7:25 | 192.8333
Feni 132/33kV Grid Sub-Station | 1 | 9:53 | 9.8833
Barishal 132/33kV Grid Sub-Station | 4 | 0:33 | 24.5
Gopalganj 132/33kV Grid Sub-Station | 1 | 2:12 | 33
Barishal 230/132kV Grid Sub-Station | 1 | 1:40 | 50
Faridpur 132/33kV Grid Sub-Station | 1 | 1:15 | 18.75
Gollamari 132/33kV Grid Sub-Station | 1 | 10:00 | 70
Narail 132/33kV Grid Sub-Station | 1 | 1:56 | 27.0667
Barishal 132/33kV Grid Sub-Station | 2 | 14:18 | 249.7
Ishurdi 132/33kV Grid Sub-Station | 2 | 29:22 | 732.73
Kushtia 132/33kV Grid Sub-Station | 2 | 0:39 | 15.33
Bheramara(GK) 132/33kV Grid Sub-Station | 1 | 43:42 | 1311
Pabna 132/33kV Grid Sub-Station | 5 | 30:29 | 605.4
Shahjadpur 132/33kV Grid Sub-Station | 2 | 16:15 | 325
Bheramara(GK) 132/33kV Grid Sub-Station | 2 | 21:28 | 644
Barapukuria 230/132/33kV Grid Sub-Station | 2 | 2:43 | 38.47
Purbasadipur 132/33kV Grid Sub-Station | 1 | 0:19 | 9.5
Rangpur 132/33kV Grid Sub-Station | 2 | 4:49 | 289
Jaldhaka 132/33kV Grid Sub-Station | 2 | 1:20 | 16.67
Naogaon 132/33kV Grid Sub-Station | 1 | 0:17 | 22.3833
Bogura 132/33kV Grid Sub-Station | 1 | 4:10 | 41.6667
Joypurhat 132/33kV Grid Sub-Station | 1 | 1:49 | 45.4167
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 3:52 | 27.0667
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 3:44 | 22.4
Niamatpur 132/33kV Grid Sub-Station | 1 | 10:26 | 678.1667
Purbasadipur 132/33kV Grid Sub-Station | 2 | 2:16 | 68
Rajshahi 132/33kV Grid Sub-Station | 2 | 5:22 | 104.65
Rangpur 132/33kV Grid Sub-Station | 2 | 17:52 | 714.67
Naogaon 132/33kV Grid Sub-Station | 1 | 10:28 | 680.3333
Rajshahi 132/33kV Grid Sub-Station | 1 | 2:41 | 52.325
Total Unserved energy : | 89 | 396:15 | 10384.0817
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:January 2024
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2024-01-25 13:00 | 27
2 | Agargaon 230/132kV Grid Sub-Station | 2024-01-23 13:00 | 59
3 | Banani 132/33kV Grid Sub-Station | 2024-01-18 04:00 | 56.1
4 | Bangabhaban 132/33kV Grid Sub-Station | 2024-01-01 13:00 | 9
5 | Bashundhara 132/33kV Grid Sub-Station | 2024-01-18 13:00 | 133
6 | BashundharaCement 132/33kV Sub-Station | 2024-01-25 12:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2024-01-30 12:00 | 259
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2024-01-09 13:00 | 112
9 | Charsaidpur 132/33kV Sub-Station | 2024-01-31 12:00 | 41
10 | Dhaka University 132/33kV Grid Sub-Station | 2024-01-28 12:00 | 18
11 | Dhamrai 132/33kV Grid Sub-Station | 2024-01-23 18:00 | 116
12 | Dhanmondi 132/33kV Grid Sub-Station | 2024-01-31 13:00 | 98
13 | Fatullah 132/33kV Grid Sub-Station | 2024-01-20 12:00 | 58
14 | Ghorashal 230/132/33kV Sub-Station | 2024-01-24 14:00 | 70
15 | Gulshan 132/33kV Grid Sub-Station | 2024-01-01 13:00 | 72
16 | HaripurSBU 132/33kV Sub-Station | 2024-01-14 15:00 | 181
17 | Hasnabad 132/33kV Grid Substation | 2024-01-09 13:00 | 79
18 | Joydebpur 132/33kV Grid Sub-Station | 2024-01-03 12:00 | 140
19 | Kabirpur 132/33kV Grid Sub-Station | 2024-01-03 18:00 | 247
20 | Kallyanpur 132/33kV Grid Sub-Station | 2024-01-19 13:00 | 78
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2024-01-14 13:00 | 57.9
22 | Kazla 132/33kV Grid Sub-Station | 2024-01-22 13:00 | 93
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2024-01-02 13:00 | 70
24 | Kodda 132/33kV Grid Sub-Station | 2024-01-10 15:00 | 278
25 | Lalbag 132/33kV Grid Sub-Station | 2024-01-31 13:00 | 70
26 | Madanganj 132/33kV Grid Sub-Station | 2024-01-15 13:00 | 41
27 | Madartek 132/33kV Grid Sub-Station | 2024-01-12 13:00 | 69.49
28 | Manikganj 132/33kV Grid Sub-Station | 2024-01-21 19:00 | 106
29 | Maniknagar 132/33kV Grid Sub-Station | 2024-01-01 13:00 | 62
30 | Matuail 132/33kV Grid Sub-Station | 2024-01-11 12:00 | 61
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2024-01-04 12:00 | 101
32 | Mirpur 132/33kV Grid Sub-Station | 2024-01-30 14:00 | 96
33 | Mirzapur 132/33kV GIS Grid Sub-Station | 2024-01-21 18:00 | 48
34 | MI_Cement 132/33kV Grid Sub-Station | 2024-01-04 11:00 | 19.8
35 | Mogbazar 132/33kV Grid Sub-Station | 2024-01-04 13:00 | 81.7
36 | Motijheel 132/33kV Grid Sub-Station | 2024-01-02 13:00 | 29
37 | Munshiganj 132/33kV Grid Sub-Station | 2024-01-05 13:00 | 78
38 | Narinda 132/33kV Grid Sub-Station | 2024-01-02 13:00 | 54
39 | Narshingdi 132/33kV Grid Sub-Station | 2024-01-17 18:30 | 153
40 | Nawabganj 132/33kV Grid Sub-Station | 2024-01-15 13:00 | 34.6
41 | New Tongi 132/33kV Grid Sub-Station | 2024-01-28 12:00 | 22
42 | Postogola 132/33kV Grid Sub-Station | 2024-01-24 13:00 | 41
43 | Purbachal 132/33kV Grid Sub-Station | 2024-01-30 12:00 | 18
44 | Rahim Steel 132/33kV Sub-Station | 2024-01-25 20:00 | 65
45 | Rajendrapur 132/33kV Grid Sub-Station | 2024-01-13 13:00 | 94
46 | Satmasjid 132/33kV Grid Sub-Station | 2024-01-23 13:00 | 89
47 | Savar 132/33kV Grid Sub-Station | 2024-01-14 12:00 | 168
48 | SevenRings 132/11kV Sub-Station | 2024-01-30 11:00 | 27.56
49 | ShahCement 132/33kV Grid Sub-Station | 2024-01-19 16:00 | 36
50 | Shitalakhya 132/33kV Grid Sub-Station | 2024-01-17 12:00 | 87.1
51 | Shyampur 132/33kV Grid Sub-Station | 2024-01-17 13:00 | 170
52 | Siddhirganj 132/33kV Grid Sub-Station | 2024-01-16 14:00 | 112
53 | Sonargaon 132/33kV Grid Sub-Station | 2024-01-22 06:00 | 112
54 | Sreepur 230/132/33kV Grid Sub-Station | 2024-01-10 10:00 | 64
55 | Srinagar 132/33kV Grid Sub-Station | 2024-01-14 13:00 | 36.6
56 | Tongi 230/132/33kV Grid Sub-Station | 2024-01-29 11:00 | 137
57 | Ullon 132/33kV Grid Sub-Station | 2024-01-23 13:00 | 37
58 | Uttara 132/33kV Grid Sub-Station | 2024-01-01 13:00 | 47
59 | UttaraNew 132/33kV Grid Sub-Station | 2024-01-30 13:00 | 39
60 | Zigatola 132/33kV Grid Sub-Station | 2024-01-14 13:00 | 52
61 | Agrabad 132/33kV Grid Sub-Station | 2024-01-15 19:00 | 62
62 | AKS 132/33kV Grid Sub-Station | 2024-01-04 10:00 | 19
63 | AKSML 230/33kV Grid Sub-Station | 2024-01-31 11:00 | 126
64 | Bakulia 132/33kV Grid Sub-Station | 2024-01-27 13:00 | 69
65 | Baroaulia 132/33kV Grid Sub-Station | 2024-01-24 12:00 | 74
66 | Baroirhat 132/33kV Grid Sub-Station | 2024-01-19 13:00 | 44
67 | BSRM 230/33kV Grid Sub-Station | 2024-01-25 20:00 | 91
68 | Chandraghona 132/33kV Grid Sub-Station | 2024-01-19 13:00 | 25
69 | Coxsbazar 132/33kV Grid Sub-Station | 2024-01-17 18:00 | 100
70 | Dohazari 132/33kV Grid Sub-Station | 2024-01-19 13:00 | 79
71 | GPH 230/33kV Grid Sub-Station | 2024-01-04 18:00 | 98
72 | Halishahar 132/33kV Grid Sub-Station | 2024-01-20 10:00 | 101.5
73 | Hathazari 230/132/33kV Grid Sub-Station | 2024-01-28 22:00 | 73
74 | Juldah 132/33kV Grid Sub-Station | 2024-01-03 11:00 | 24
75 | Kalurghat 132/33kV Grid Sub-Station | 2024-01-02 12:00 | 34
76 | Khagrachori 132/33kV Grid Sub-Station | 2024-01-17 18:30 | 26
77 | Khulshi 132/33kV Grid Sub-Station | 2024-01-04 18:30 | 151
78 | KSRM 132/33kV Grid Sub-Station | 2024-01-21 | 69.5
79 | Madunaghat 132/33kV Grid Sub-Station | 2024-01-02 18:00 | 78
80 | Matarbari 132/33kV Sub-Station | 2024-01-09 03:00 | 120
81 | Mirsorai 230/33kV Grid Sub-Station | 2024-01-14 18:00 | 5
82 | Modern Steel 132/11kV Grid Sub-Station | 2024-01-01 | 0
83 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2024-01-04 | 32
84 | Rangamati 132/33kV Grid Sub-Station | 2024-01-01 18:00 | 14
85 | Shahmirpur 132/33kV Grid Sub-Station | 2024-01-18 17:00 | 50
86 | Shikalbaha 132/33kV Sub-Station | 2024-01-22 20:00 | 27
87 | Sholosohor 132/33kV Grid Sub-Station | 2024-01-20 11:00 | 38
88 | SSM 132/33kV Grid Sub-Station | 2024-01-01 01:00 | 21
89 | TK chemical 132kV Grid Sub-Station | 2024-01-03 18:00 | 21.5
90 | Ashuganj 230/132/33kV Sub-Station | 2024-01-18 | 58
91 | Brahmanbaria 132/33kV Grid Sub-Station | 2024-01-26 13:00 | 111
92 | Chandpur 132/33kV Grid Sub-Station | 2024-01-20 18:30 | 46
93 | Chauddagram 132/33kV Grid Sub-Station | 2024-01-26 13:00 | 45
94 | Chowmuhani 132/33kV Grid Sub-Station | 2024-01-20 20:00 | 152
95 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2024-01-16 13:00 | 136
96 | Cumilla(S) 132/33kV Grid Sub-Station | 2024-01-31 12:00 | 126
97 | Daudkandi 132/33kV Grid Sub-Station | 2024-01-21 19:30 | 114
98 | Feni 132/33kV Grid Sub-Station | 2024-01-03 18:00 | 74
99 | Kachua 132/33kV Grid Sub-Station | 2024-01-29 19:30 | 48
100 | PHP 132/33kV Sub-Station | 2024-01-10 03:00 | 10
101 | Ramganj 132/33kV Grid Sub-Station | 2024-01-03 21:00 | 84
102 | Bhaluka 132/33kV Grid Sub-Station | 2024-01-20 12:00 | 154
103 | Jamalpur 132/33kV Grid Sub-Station | 2024-01-29 19:00 | 131
104 | Kishoreganj 132/33kV Grid Sub-Station | 2024-01-22 19:00 | 116
105 | Mymensingh 132/33kV Grid Sub-Station | 2024-01-12 13:00 | 195
106 | Netrakona 132/33kV Grid Sub-Station | 2024-01-28 19:30 | 142
107 | Sherpur 132/33kV Grid Sub-Station | 2024-01-18 18:00 | 126
108 | Tangail 132/33kV Grid Sub-Station | 2024-01-13 19:00 | 154
109 | Beanibazar 132/33kV Grid Sub-Station | 2024-01-20 18:00 | 58
110 | Chhatak 132/33kV Grid Sub-Station | 2024-01-06 20:00 | 23
111 | Fenchuganj 230/132/33kV Grid Sub-Station | 2024-01-10 18:00 | 25
112 | Kulaura 132/33kV Grid Sub-Station | 2024-01-02 19:30 | 28
113 | Shahjibazar 132/33kV Grid Sub-Station | 2024-01-13 21:00 | 91
114 | Sreemongol 132/33kV Grid Sub-Station | 2024-01-01 18:00 | 50
115 | Sunamganj 132/33kV Grid Sub-Station | 2024-01-23 18:30 | 36
116 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2024-01-25 18:30 | 28
117 | Sylhet 132/33kV Grid Sub-Station | 2024-01-27 18:00 | 98
118 | Bagerhat 132/33kV Grid Sub-Station | 2024-01-30 18:30 | 74
119 | Benapole 132/33kV Grid Sub-Station | 2024-01-17 08:00 | 62
120 | Bheramara(GK) 132/33kV Grid Sub-Station | 2024-01-27 20:00 | 52
121 | Chuadanga 132/33kV Grid Sub-Station | 2024-01-31 18:30 | 83
122 | Faridpur 132/33kV Grid Sub-Station | 2024-01-23 18:30 | 121
123 | Goalpara 132/33kV Grid Sub-Station | 2024-01-19 13:00 | 28
124 | Gollamari 132/33kV Grid Sub-Station | 2024-01-16 13:00 | 48
125 | Gopalganj 132/33kV Grid Sub-Station | 2024-01-11 18:30 | 81
126 | Jashore 132/33kV Grid Sub-Station | 2024-01-24 13:00 | 115
127 | Jhenaidah 132/33kV Grid Sub-Station | 2024-01-16 18:00 | 96
128 | Khulna (C) 132/33kV Grid Sub-Station | 2024-01-28 12:00 | 102
129 | Kushtia 132/33kV Grid Sub-Station | 2024-01-28 18:30 | 108
130 | Madaripur 132/33kV Grid Sub-Station | 2024-01-25 20:00 | 69
131 | Magura 132/33kV Grid Sub-Station | 2024-01-27 18:30 | 47
132 | Mongla 132/33kV Grid Sub-Station | 2024-01-16 10:00 | 37
133 | Narail 132/33kV Grid Sub-Station | 2024-01-14 18:30 | 43
134 | Noapara 132/33kV Grid Sub-Station | 2024-01-17 18:30 | 40
135 | Rajbari 132/33kV Grid Sub-Station | 2024-01-30 18:30 | 54
136 | Satkhira 132/33kV Grid Sub-Station | 2024-01-29 18:30 | 95
137 | Shariatpur 132/33kV Grid Sub-Station | 2024-01-13 20:00 | 52
138 | Barguna 132/33kV Grid Sub-Station | 2024-01-15 19:30 | 16
139 | Barishal 132/33kV Grid Sub-Station | 2024-01-26 13:00 | 81
140 | Barishal 230/132kV Grid Sub-Station | 2024-01-22 18:00 | 68
141 | Bhandaria 132/33kV Grid Sub-Station | 2024-01-20 22:00 | 35
142 | Borhanuddin 230/33kV Grid Sub-Station | 2024-01-24 21:00 | 53
143 | Patuakhali 132/33kV Grid Sub-Station | 2024-01-18 20:00 | 77
144 | Payra 400/132/33kV Grid Sub-Station | 2024-01-01 18:30 | 20
145 | Amnura 132/33kV Grid Sub-Station | 2024-01-30 09:00 | 66
146 | Bhangura 132/33kV Grid Sub-Station | 2024-01-21 18:30 | 28
147 | Bog-Sherpur 132/33kV Grid Sub-Station | 2024-01-11 13:00 | 56
148 | Bogura 132/33kV Grid Sub-Station | 2024-01-23 19:00 | 118
149 | Chapai 132/33kV Grid Sub-Station | 2024-01-03 13:00 | 60
150 | Ishurdi 132/33kV Grid Sub-Station | 2024-01-25 20:00 | 53
151 | Joypurhat 132/33kV Grid Sub-Station | 2024-01-31 18:30 | 47
152 | Mahasthangarh 132/33kV Grid Sub-Station | 2024-01-30 09:00 | 52
153 | Naogaon 132/33kV Grid Sub-Station | 2024-01-30 13:00 | 106
154 | Natore 132/33kV Grid Sub-Station | 2024-01-20 19:00 | 106
155 | Niamatpur 132/33kV Grid Sub-Station | 2024-01-28 18:30 | 80
156 | Pabna 132/33kV Grid Sub-Station | 2024-01-17 18:30 | 87
157 | Rajshahi 132/33kV Grid Sub-Station | 2024-01-19 13:00 | 127
158 | Rajshahi 230/132/33kV Grid Sub-Station | 2024-01-15 13:00 | 30
159 | Ruppur 132/11kV Grid Sub-Station | 2024-01-13 18:00 | 22
160 | Shahjadpur 132/33kV Grid Sub-Station | 2024-01-15 18:30 | 70
161 | Sirajganj 132/33kV Grid Sub-Station | 2024-01-16 19:00 | 96
162 | Ullahpara 132/33kV Grid Sub-Station | 2024-01-28 19:00 | 90
163 | Barapukuria 230/132/33kV Grid Sub-Station | 2024-01-18 02:00 | 68
164 | Jaldhaka 132/33kV Grid Sub-Station | 2024-01-29 18:30 | 67
165 | Kurigram 132/33kV Grid Sub-Station | 2024-01-29 18:30 | 66
166 | Lalmonirhat 132/33kV Grid Sub-Station | 2024-01-29 18:30 | 45
167 | Mithapukur 132/33kV Grid Sub-Station | 2024-01-28 18:00 | 52
168 | Palashbari 132/33kV Grid Sub-Station | 2024-01-31 18:00 | 100
169 | Panchagarh 132/33kV Grid Sub-Station | 2024-01-29 18:30 | 49
170 | Purbasadipur 132/33kV Grid Sub-Station | 2024-01-29 18:00 | 118
171 | Rangpur 132/33kV Grid Sub-Station | 2024-01-26 13:00 | 120
172 | Saidpur 132/33kV Grid Sub-Station | 2024-01-28 09:00 | 103
172 | Thakurgaon 132/33kV Grid Sub-Station | 2024-01-15 18:30 | 79
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:January 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 3959.76 | 2024-01-11 | 12:00
Chattogram | 1092.4 | 2024-01-18 | 12:00
Cumilla | 874 | 2024-01-29 | 18:00
Mymensingh | 912 | 2024-01-17 | 18:30
Sylhet | 389 | 2024-01-25 | 18:30
Khulna | 1250.6 | 2024-01-28 | 18:30
Barishal | 311.2 | 2024-01-24 | 20:00
Rajshahi | 1130 | 2024-01-28 | 19:00
Rangpur | 838 | 2024-01-29 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:January 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 421 | 2024-01-08 02:00 | 384 | 2024-01-03 12:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 414 | 2024-01-01 05:00 | 375 | 2024-01-29 12:00
3 | Bibiana 400/230kV Sub-Station | 400 | 428 | 2024-01-27 04:00 | 403 | 2024-01-03 12:00
4 | BIPTC | 400 | 422 | 2024-01-27 23:00 | 386 | 2024-01-28 12:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 424 | 2024-01-08 02:00 | 393 | 2024-01-31 12:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 424 | 2024-01-27 03:00 | 385 | 2024-01-03 12:00
7 | Payra 400kV Sub-Station | 400 | 425 | 2024-01-08 02:00 | 408 | 2024-01-03 12:00
8 | Rahanpur 400/132kV Grid Sub-Station | 400 | 418 | 2024-01-18 04:00 | 389 | 2024-01-18 12:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 422 | 2024-01-08 02:00 | 391 | 2024-01-24 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 243 | 2024-01-08 02:00 | 221 | 2024-01-29 13:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 243 | 2024-01-18 17:00 | 221 | 2024-01-03 07:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 242 | 2024-01-07 23:00 | 221 | 2024-01-03 11:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 228 | 2024-01-07 15:00 | 209 | 2024-01-28 08:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 246 | 2024-01-08 04:00 | 232 | 2024-01-19 13:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 243 | 2024-01-08 05:00 | 221 | 2024-01-04 12:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 235 | 2024-01-08 | 214 | 2024-01-16 11:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 243 | 2024-01-19 19:00 | 225 | 2024-01-03 08:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-01-07 10:00 | 226 | 2024-01-28 14:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 247 | 2024-01-22 22:00 | 232 | 2024-01-12 01:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 248 | 2024-01-07 06:00 | 230 | 2024-01-10 12:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 243 | 2024-01-20 19:00 | 214 | 2024-01-04 07:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 245 | 2024-01-07 10:00 | 225 | 2024-01-03 12:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 244 | 2024-01-05 14:00 | 222 | 2024-01-29 12:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-01-20 18:30 | 223 | 2024-01-03 23:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 245 | 2024-01-08 02:00 | 223 | 2024-01-23 12:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 241 | 2024-01-08 | 219 | 2024-01-18 12:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-01-08 02:00 | 221 | 2024-01-29 12:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 248 | 2024-01-08 01:00 | 226 | 2024-01-09 13:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 245 | 2024-01-07 06:00 | 224 | 2024-01-29 12:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 249 | 2024-01-26 10:00 | 232 | 2024-01-03 11:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 243 | 2024-01-09 18:30 | 220 | 2024-01-16 16:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 244 | 2024-01-08 02:00 | 220 | 2024-01-01 12:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 244 | 2024-01-07 11:00 | 222 | 2024-01-29 12:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 241 | 2024-01-19 19:00 | 218 | 2024-01-04
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 245 | 2024-01-08 06:00 | 222 | 2024-01-03 17:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 246 | 2024-01-07 10:00 | 224 | 2024-01-29 11:00
28 | Sirajgonj 230 kV Switching Station | 230 | 246 | 2024-01-08 03:00 | 227 | 2024-01-18 12:00
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-01-08 02:00 | 223 | 2024-01-20 12:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 242 | 2024-01-01 17:00 | 215 | 2024-01-29 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-08 02:00 | 126 | 2024-01-29 12:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-22 22:00 | 130 | 2024-01-03 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-17 20:00 | 129 | 2024-01-03 11:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-19 17:00 | 123 | 2024-01-30 09:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 144 | 2024-01-02 03:00 | 133 | 2024-01-16 12:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-08 02:00 | 123 | 2024-01-03 13:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-03 20:00 | 130 | 2024-01-03 23:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-05 04:00 | 119 | 2024-01-29 12:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-07 10:00 | 120 | 2024-01-20 16:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-12 17:00 | 133 | 2024-01-03 13:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 | 131 | 2024-01-03 12:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-19 19:00 | 130 | 2024-01-03 08:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-19 19:00 | 125 | 2024-01-29 13:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-02 02:00 | 122 | 2024-01-29 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 141 | 2024-01-07 10:00 | 124 | 2024-01-29 12:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-17 20:00 | 116 | 2024-01-22 13:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 04:00 | 122 | 2024-01-16 12:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-04 03:00 | 124 | 2024-01-21 16:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-14 04:00 | 125 | 2024-01-24 11:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-08 01:00 | 130 | 2024-01-03 19:30
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 02:00 | 128 | 2024-01-02 12:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 135 | 2024-01-07 10:00 | 114 | 2024-01-29 11:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-01 05:00 | 125 | 2024-01-16 11:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-27 04:00 | 125 | 2024-01-28 08:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-23 06:00 | 126 | 2024-01-02 12:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 143 | 2024-01-07 06:00 | 128 | 2024-01-16 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-12 17:00 | 122 | 2024-01-29 13:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-03 18:30 | 132 | 2024-01-03 07:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-06 04:00 | 124 | 2024-01-18 12:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 142 | 2024-01-07 06:00 | 126 | 2024-01-18 04:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-18 22:00 | 127 | 2024-01-29 12:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-24 02:00 | 116 | 2024-01-22 14:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-13 08:00 | 123 | 2024-01-28 13:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 01:00 | 123 | 2024-01-16 12:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 130 | 2024-01-01 18:00 | 122 | 2024-01-03 08:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 145 | 2024-01-19 19:00 | 121 | 2024-01-19 21:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-07 10:00 | 122 | 2024-01-29 12:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-07 10:00 | 126 | 2024-01-29 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-08 02:00 | 121 | 2024-01-29 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142.4 | 2024-01-07 06:00 | 125.5 | 2024-01-29 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-20 19:00 | 127 | 2024-01-03 14:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-27 03:00 | 130 | 2024-01-01 11:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-07 10:00 | 127 | 2024-01-29 12:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-18 18:30 | 125 | 2024-01-28 13:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 02:00 | 126 | 2024-01-03 12:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 | 126 | 2024-01-03 12:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 02:00 | 123 | 2024-01-03 12:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-07 09:00 | 125 | 2024-01-29 12:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-21 19:00 | 129 | 2024-01-03 11:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 142 | 2024-01-07 10:00 | 125 | 2024-01-29 11:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 141 | 2024-01-05 07:00 | 128 | 2024-01-30 12:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-08 02:00 | 131 | 2024-01-18 12:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 135 | 2024-01-08 01:00 | 113 | 2024-01-30 09:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-05 11:00 | 114 | 2024-01-27 07:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 01:00 | 123 | 2024-01-23 12:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 | 127 | 2024-01-16 12:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 146 | 2024-01-08 01:00 | 131 | 2024-01-06 15:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-08 01:00 | 115 | 2024-01-27 09:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-20 19:00 | 130 | 2024-01-03 07:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-07 10:00 | 120 | 2024-01-22 12:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-18 18:30 | 126 | 2024-01-29 12:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-12 06:00 | 125 | 2024-01-13 14:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-20 19:00 | 130 | 2024-01-04
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-01 06:00 | 125 | 2024-01-29 12:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-07 11:00 | 122 | 2024-01-03 13:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-20 18:30 | 131 | 2024-01-03 08:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-08 04:00 | 125 | 2024-01-03 12:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-05 09:00 | 129 | 2024-01-03 08:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-02 17:00 | 119 | 2024-01-29 13:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-07 18:30 | 122 | 2024-01-20 16:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-21 19:00 | 129 | 2024-01-07 13:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-24 02:00 | 124 | 2024-01-22 13:00
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 136 | 2024-01-11 19:30 | 113 | 2024-01-22 08:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-08 01:00 | 128 | 2024-01-16 12:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-01 03:00 | 124 | 2024-01-18 23:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 134 | 2024-01-08 | 114 | 2024-01-30 08:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-07 05:00 | 124 | 2024-01-29 12:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-29 04:00 | 129 | 2024-01-16 12:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 02:00 | 125 | 2024-01-29 12:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-19 18:30 | 129 | 2024-01-07 13:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-08 02:00 | 126 | 2024-01-16 12:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-08 | 123 | 2024-01-28 08:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-06 10:00 | 121 | 2024-01-22 12:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-07 10:00 | 123 | 2024-01-03 12:00
85 | Matarbari 132/33kV Sub-Station | 132 | 138 | 2024-01-14 18:30 | 123 | 2024-01-03 12:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 141.8 | 2024-01-07 10:00 | 120.6 | 2024-01-03 12:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-02 02:00 | 121 | 2024-01-29 12:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-11 23:00 | 124 | 2024-01-29 12:00
89 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 139 | 2024-01-07 10:00 | 123 | 2024-01-29 11:00
90 | Mithapukur 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-08 01:00 | 117 | 2024-01-27 13:00
91 | MI_Cement 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-07 10:00 | 126 | 2024-01-30 16:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 141 | 2024-01-05 09:00 | 131 | 2024-01-04
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-06 04:00 | 126 | 2024-01-29 12:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-07 06:00 | 123 | 2024-01-22 08:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-07 10:00 | 120 | 2024-01-20 16:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-05 17:00 | 125 | 2024-01-30 16:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-05 11:00 | 115 | 2024-01-29 15:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 136 | 2024-01-07 05:00 | 116 | 2024-01-27 11:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-08 02:00 | 124 | 2024-01-16 12:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-07 10:00 | 117 | 2024-01-29 12:00
101 | Natore 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 02:00 | 127 | 2024-01-24 13:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-01 05:00 | 126 | 2024-01-29 12:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-01 20:00 | 114 | 2024-01-31 19:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-05 22:00 | 122 | 2024-01-30 12:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-01-07 05:00 | 114 | 2024-01-27 12:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 | 125 | 2024-01-03 12:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-08 02:00 | 126 | 2024-01-29 11:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 135 | 2024-01-07 06:00 | 117 | 2024-01-30 08:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 02:00 | 113 | 2024-01-27 13:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-12 16:00 | 132 | 2024-01-16 12:00
111 | PHP 132/33kV Sub-Station | 132 | 142 | 2024-01-19 19:00 | 126 | 2024-01-28 13:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 143 | 2024-01-07 10:00 | 127 | 2024-01-15 18:30
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 144 | 2024-01-07 09:00 | 120 | 2024-01-29 12:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-05 06:00 | 113 | 2024-01-28 08:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 142 | 2024-01-07 10:00 | 122 | 2024-01-28 10:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-08 02:00 | 123 | 2024-01-02 18:30
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-07 10:00 | 122 | 2024-01-29 11:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-06 05:00 | 127 | 2024-01-26 12:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-20 10:00 | 120 | 2024-01-29 13:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-18 13:00 | 131 | 2024-01-03 12:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-26 19:00 | 117 | 2024-01-27 13:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 144 | 2024-01-07 23:00 | 130 | 2024-01-18 11:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-01-08 01:00 | 113 | 2024-01-27 13:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-08 02:00 | 123 | 2024-01-28 08:00
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-06 05:00 | 128 | 2024-01-29 13:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-05 07:00 | 123 | 2024-01-16 12:00
127 | SevenRings 132/11kV Sub-Station | 132 | 147 | 2024-01-08 03:00 | 134 | 2024-01-20 12:00
128 | ShahCement 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-07 06:00 | 121 | 2024-01-05 18:00
129 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-01-02 01:00 | 133 | 2024-01-16 11:00
130 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-23 06:00 | 127 | 2024-01-22 12:00
131 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-05 09:00 | 128 | 2024-01-04 23:00
132 | Shariatpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-08 03:00 | 128 | 2024-01-16 12:00
133 | Sherpur 132/33kV Grid Sub-Station | 132 | 135 | 2024-01-01 20:00 | 113 | 2024-01-26 07:00
134 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-07 10:00 | 126 | 2024-01-30 16:00
135 | Sholosohor 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-20 19:00 | 130 | 2024-01-03 08:00
136 | Shyampur 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-05 20:00 | 127 | 2024-01-29 12:00
137 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-07 10:00 | 125 | 2024-01-29 12:00
138 | Sirajganj 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-08 02:00 | 124 | 2024-01-19 12:00
139 | Sonargaon 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-05 09:00 | 123 | 2024-01-29 15:00
140 | Sreemongol 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-23 03:00 | 126 | 2024-01-22 12:00
141 | Srinagar 132/33kV Grid Sub-Station | 132 | 140 | 2024-01-01 03:00 | 125 | 2024-01-29 12:00
142 | SSM 132/33kV Grid Sub-Station | 132 | 146 | 2024-01-09 03:00 | 129 | 2024-01-28 09:00
143 | Sunamganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-01-23 05:00 | 116 | 2024-01-22 13:00
144 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 139 | 2024-01-28 05:00 | 117 | 2024-01-22 13:00
145 | Sylhet 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-29 03:00 | 120 | 2024-01-22 13:00
146 | Tangail 132/33kV Grid Sub-Station | 132 | 137 | 2024-01-05 11:00 | 120 | 2024-01-29 11:00
147 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-29 17:00 | 113 | 2024-01-30 08:00
148 | TK chemical 132kV Grid Sub-Station | 132 | 141 | 2024-01-05 10:00 | 130 | 2024-01-08 14:00
149 | Ullahpara 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-07 06:00 | 125 | 2024-01-19 13:00
150 | Ullon 132/33kV Grid Sub-Station | 132 | 139 | 2024-01-08 02:00 | 126 | 2024-01-29 11:00
151 | Uttara 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-06 03:00 | 124 | 2024-01-20 16:00
152 | UttaraNew 132/33kV Grid Sub-Station | 132 | 142 | 2024-01-06 02:00 | 120 | 2024-01-29 15:00
153 | Zigatola 132/33kV Grid Sub-Station | 132 | 141 | 2024-01-01 05:00 | 127 | 2024-01-20 13:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:January 2024
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 475 | 475.0095 | 2024-01-17 12:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 450 | 458.9118 | 2024-01-18 15:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -211 | 256.5872 | 2024-01-01 08:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -211 | 256.5872 | 2024-01-01 08:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 109 | 110.0273 | 2024-01-27 22:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 107 | 108.0463 | 2024-01-27 22:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 231 | 231.2163 | 2024-01-22 18:30
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 289 | 290.9931 | 2024-01-09 23:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -273.92 | 274.2466 | 2024-01-04 18:30
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -412.99 | 413.0579 | 2024-01-12 20:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 257 | 257.3286 | 2024-01-03 13:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -105 | 105.019 | 2024-01-31 18:30
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -103 | 103.0776 | 2024-01-31 20:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -105 | 105.019 | 2024-01-31 18:30
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 243 | 343.6539 | 2024-01-23 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 311 | 327.6126 | 2024-01-29 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -53 | 53.3385 | 2024-01-06 21:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -53 | 53.3385 | 2024-01-06 21:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 99 | 99.0202 | 2024-01-16 01:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 99 | 99.0202 | 2024-01-16 01:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 227 | 234.2926 | 2024-01-01 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 227 | 234.2926 | 2024-01-01 13:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 99 | 102.1078 | 2024-01-14 12:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 130 | 133.6451 | 2024-01-09 12:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 131 | 134.1715 | 2024-01-09 12:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 30 | 138.2932 | 2024-01-13 12:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 240 | 247.3863 | 2024-01-23 13:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 89 | 233.6172 | 2024-01-23 08:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 83 | 89.6939 | 2024-01-29 08:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 186 | 186.172 | 2024-01-22 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 162 | 170.763 | 2024-01-30 09:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 210 | 214.9791 | 2024-01-30 09:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 186 | 186.6869 | 2024-01-01 04:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 246 | 247.0729 | 2024-01-15 16:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -83 | 107.9352 | 2024-01-13 21:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -83 | 107.9352 | 2024-01-13 21:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 210 | 210.0857 | 2024-01-20 03:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 197 | 197.5702 | 2024-01-27 13:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 270 | 270.8948 | 2024-01-27 13:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 185 | 186.8181 | 2024-01-04 22:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 180 | 181.7278 | 2024-01-04 21:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 166 | 180.5464 | 2024-01-21 19:30
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 118 | 118 | 2024-01-15 12:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 118 | 118 | 2024-01-15 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 158 | 161.4094 | 2024-01-29 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 157 | 159.6559 | 2024-01-31
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 158 | 161.4094 | 2024-01-29 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 75 | 84.0773 | 2024-01-10 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 75 | 83.1925 | 2024-01-20 23:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 64 | 85.0412 | 2024-01-11 15:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 95 | 96.026 | 2024-01-31 19:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 95 | 96.026 | 2024-01-31 19:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 95 | 96.026 | 2024-01-31 19:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 95 | 96.026 | 2024-01-31 19:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 79 | 117.516 | 2024-01-18 13:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 83 | 120.2414 | 2024-01-24 13:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 82 | 118.1059 | 2024-01-24 13:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -205 | 217.2763 | 2024-01-16 09:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -235 | 238.7237 | 2024-01-06 19:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 96 | 300.7341 | 2024-01-22 18:30
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 116 | 118.2582 | 2024-01-11 13:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2024-01-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 116 | 118.2582 | 2024-01-11 13:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -118 | 118.8276 | 2024-01-04 18:30
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -118 | 118.8276 | 2024-01-04 18:30
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -151 | 151.9539 | 2024-01-04 18:30
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 180 | 190.3786 | 2024-01-20 16:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 55 | 143.9236 | 2024-01-25 06:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -61 | 61.6604 | 2024-01-04 08:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -62 | 62.6498 | 2024-01-04 08:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 10 | 10 | 2024-01-25 17:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 0 | 3 | 2024-01-06 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 190 | 191.7707 | 2024-01-12 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 181 | 294.2533 | 2024-01-14 09:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 221 | 222.6432 | 2024-01-29 18:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 197 | 204.5336 | 2024-01-24 17:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 225 | 232.3553 | 2024-01-25 12:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 150 | 166.8203 | 2024-01-18 10:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 150 | 166.8203 | 2024-01-18 10:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 181 | 199.1231 | 2024-01-30 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 181 | 199.1231 | 2024-01-30 12:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 230 | 236.0275 | 2024-01-14 12:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 250 | 258.5653 | 2024-01-11 11:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 215 | 215.5226 | 2024-01-25 11:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 186 | 186.7753 | 2024-01-17 12:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 202 | 202.9877 | 2024-01-25 18:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: January 2024 | [5 empty] | (For Evening Peak) | [8 empty] | Month: January 2024 |  |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-01-01 | 9944 | 9944 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-01 | 9084 | 9084 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-02 | 10056 | 10056 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-02 | 9294 | 9294 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-03 | 10131 | 10131 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-03 | 9287 | 9287 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-04 | 10107 | 10107 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-04 | 9508 | 9508 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-05 | 9168 | 9168 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-05 | 8731 | 8731 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-06 | 9113 | 9113 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-06 | 8712 | 8712 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-07 | 7468 | 7468 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-07 | 6132 | 6132 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-08 | 9566 | 9566 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-08 | 8810 | 8810 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-09 | 9759 | 9759 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-09 | 9189 | 9189 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-10 | 10086 | 10086 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-10 | 9280 | 9280 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-11 | 10280 | 10280 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-11 | 8635 | 8635 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-12 | 9084 | 9084 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-12 | 8852 | 8852 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-13 | 10286 | 10286 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-13 | 8914 | 8914 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-14 | 10437 | 10437 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-14 | 9557 | 9557 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-15 | 10368 | 10368 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-15 | 9335 | 9503 | 350 | 12:00 | 57 | 0 | 116 | 37 | 4 | 78 | 0 | 0 | 58 | -
2024-01-16 | 10517 | 10517 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-16 | 9725 | 9800 | 72 | 12:00 | 52 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | -
2024-01-17 | 10515 | 10515 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-17 | 9843 | 9843 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-18 | 10544 | 10544 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-18 | 9746 | 9935 | 180 | 12:00 | 95 | 0 | 0 | 0 | 0 | 62 | 23 | 0 | 0 | -
2024-01-19 | 9530 | 9530 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-19 | 9087 | 9087 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-20 | 9794 | 9794 | 617 | 20:00 | 104 | 0 | 174 | 139 | 20 | 95 | 57 | 28 | 0 | - | 2024-01-20 | 9019 | 9380 | 345 | 12:00 | 153 | 18 | 111 | 36 | 20 | 0 | 0 | 0 | 7 | -
2024-01-21 | 10276 | 10276 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-21 | 9133 | 9900 | 732 | 12:00 | 230 | 100 | 82 | 40 | 85 | 95 | 50 | 15 | 35 | -
2024-01-22 | 10558 | 10558 | 55 | 19:00 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | - | 2024-01-22 | 9918 | 10000 | 78 | 12:00 | 0 | 0 | 0 | 0 | 0 | 40 | 38 | 0 | 0 | -
2024-01-23 | 10713 | 10713 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-23 | 9797 | 9995 | 170 | 12:00 | 50 | 0 | 0 | 0 | 23 | 87 | 10 | 0 | 0 | -
2024-01-24 | 10455 | 10455 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-24 | 9737 | 10009 | 260 | 12:00 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | -
2024-01-25 | 10692 | 10692 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-25 | 9795 | 10200 | 387 | 12:00 | 40 | 0 | 96 | 43 | 15 | 85 | 25 | 27 | 56 | -
2024-01-26 | 9227 | 9227 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-26 | 9186 | 9186 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-01-27 | 10288 | 10288 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-27 | 9118 | 9230 | 107 | 12:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | -
2024-01-28 | 10580 | 10580 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-01-28 | 9930 | 10000 | 67 | 12:00 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | -
2024-01-29 | 10717 | 10717 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-01-29 | 9954 | 9954 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-01-30 | 10715 | 10715 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-01-30 | 10011 | 10100 | 85 | 12:00 | 55 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0
2024-01-31 | 10704 | 10704 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-01-31 | 10109 | 10500 | 182 | 12:00 | 40 | 0 | 0 | 0 | 0 | 80 | 0 | 62 | 0

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:January 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10717 | 2024-01-29 | 19:00
2 | Maximum Day Peak Genaration | MW | 10109 | 2024-01-31 | 12:00
3 | Maximum Evening Peak Demand | MW | 10717 | 2024-01-29 | 19:00
4 | Minimum Generation | MW | 4997 | 2024-01-08 | 6:00
5 | Average of the daily evening peak Genaration | MW | 10054.129 | - | -
6 | Average of the daily day peak Genaration | MW | 9271.871 | - | -
7 | Maximum load shed (Evening Peak) | MW | 617 | 2024-01-20 | 20:00
8 | Minimum load shed | MW | 0 | 2024-01-19 | 19:00
9 | Total nos. of load shed days | Day | 2 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 22.4 | - | -
11 | Total Generation | MkWh | 6364.0985 | - | -
12 | Total Generation by BPDB | MkWh | 1567.6156 | % of total Gen. | 24.63%
13 | Total Generation by IPP | MkWh | 1941.8238 | '' | 30.51%
14 | A) Total Generation by Generation Companies | MkWh | 1329.044 | '' | 20.88%
| B) Total Generation by REB | MkWh | 94.171 | " | 1.48%
| C) Total Generation by RENTAL | MkWh | 151.7108 | " | 2.384%
| D) Total Imported from India (BIPTC) | MkWh | 524.576 | " | 8.243%
| E) Total Imported from Tripura, India (A.C) | MkWh | 755.1572 | " | 11.87%
15 | Fuel wise Generation.
| A) Gas | MkWh | 2952.1448 | % of total Gen. | 46.39%
| B) Oil | MkWh | 601.57 | '' | 9.453%
| C) Hydro | MkWh | 55.9314 | '' | 0.8789%
| D) Solar | MkWh | 47.2875 | '' | 0.743%
| E) Coal | MkWh | 2108.3139 | '' | 33.13%
| F) BIPTC (Import from India) | MkWh | 524.576 | '' | 8.243%
| G) A.C (Import from Tripura, India) | MkWh | 68.736 | '' | 1.08%
| H) Wind | MkWh | 5.531 | '' | 0.08691%
16 | Maximun of the daily total Generation . | MkWh | 217.626 | 2024-01-24
17 | Monthly Load factor | % | 75.2028 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 28691.6677 | - | -
| A) Gas | M.Taka | 5787.3421 | - | -
| B) Liquid fuel | M.Taka | 8262.329 | - | -
| C) Coal | M.Taka | 11814.7592 | - | -
| D) BIPTC (Import from India) | M.Taka | 2376.3292 | - | -
| E) Tripura(Import from India) | M.Taka | 450.9082 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1365.2795 | 2024-01-14
| A) Gas | M.Taka | 312.8682 | 2024-01-18
| B) Liquid fuel | M.Taka | 582.5835 | 2024-01-14
| C) Coal | M.Taka | 567.9944 | 2024-01-14
| D) BIPTC (Import from India) | M.Taka | 86.6334 | 2024-01-07
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.5084
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 4.5867
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 97.4 | 31/01/2024 | 06:00
b) | Actual | FT (MSL) | 87.48 | 31/01/2024 | 6:00
22 | Peak Genaration of January 2023 | MW | 10330 | 2023-01-30 | 19:00
23 | Peak Demand of January 2023 | MW | 10496 | 2023-01-30 | 19:00
24 | Maximum peak Generation recorded upto 31/01/2024 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/01/2024 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 31/01/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:January 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | [15 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [15 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD