## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-04-13 | Saturday
|  | Date (day): | 2024-04-13 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14424.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15709 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-04-12 | 2024-04-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 220 | 180 | 220
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 32 | 12 | 60 | 48 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 303 | 312 | 300 | 300 |  | 100 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 310 | 298 | 330 | 330
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 40 | 40 | 15 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 15 | 15 | 60 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 122 | 201 | 120 | 200 | 10
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 315 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 91 | 91 | 11 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 32 | 145
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 0 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 18 | 21 | 27 | 30 |  | 50 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 16 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 8 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 34 | 149 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 17 | 100
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 53 | 53 | 51 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 0 | 54 | 108 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Fuel shortage
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 83 | 370 | 350 | 350 |  |  | on test
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 150 | 585 | 550 | 550 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 2023 | 3058 | 3640 | 4170 | 578 | 910
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 122 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 8 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 6 | 44 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 0 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 213 | 211 | 211
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 34 | 34 | 71 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 72 | 60 | 80 | 18 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 80 | 20 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 5 | 5 | 5 | 5 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 38 | 38 | 40 | 40
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 12 | 12 | 96 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 16 | 32 | 268 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 0 | 17 | 37 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 17 | 17 | 93 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 11 | 12 | 12 | 88 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 17 | 17 | 99 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 145 | 18 |  | Fuel shortage
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 340 | 420 | 524 | 524 | 700 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 7 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 372 | 428 | 576 | 576
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 76 | 0 | 25 | 0 |  |  | on test
| Chattogram area Total |  |  |  |  | 4404 | 4344 | 1186 | 1446 | 1963 | 2074 | 1912 | 381
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 219 | 220 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 330 | 330 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 240 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 330 | 330 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 33 | 36 | 36 | 9 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 40 | 44 | 52 | 3 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 185 | 185 | 185 | 10 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 33 | 33
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 36 | 155 | 50 | 155 | 45 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10 |  | 5 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 72 | 96 | 152 | 160
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 25 | 30 | 30
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 25 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 70 | 17 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 48 | 38 | 58 | 55 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 6 | 17 | 17 | 35 |  | 19 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 36 | 36 | 36 | 36 |  | 79 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1216 | 1777 | 1930 | 2213 | 266 | 271
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 192 | 199 | 200 | 200 | 2 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 107 | 56 | 105 | 95 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 99 | 50 | 100 | 15 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 24 | 24 |  |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 348 | 429 | 381.6 | 429 | 2 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 37 | 40 | 41 | 41 |  | 29 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 30 | 30 | 30 |  | 60 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 112 | 110 | 110 |  | 53 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 50 | 53 | 53
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 25 | 47 | 47
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 63 | 63 | 63
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 20 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 198 | 205 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 17 | 20 | 20
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 320 | 320 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 378 | 294 | 0 | 0 |  |  | Under maint.
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 212 | 0 | 0 |  |  | Under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1456 | 1367 | 919 | 919 | 0 | 493
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 636 | 777 | 800 | 945
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 16 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 30 | 50 |  | 59 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 70 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 728 | 777 | 1016 | 1127 | 1112 | 71
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 0 | 11 | 7 | 10 |  | 30 | Engine problem
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 620 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 17 |  |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 140 | 150 | 150
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 885 | 1056 | 1816 | 1881 | 0 | 94
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60 | 11 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 50 | 2 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 30 |  | 41 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 35 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 175 | 150 | 200 | 210
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 313 | 380 | 400
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 96 |  | 8 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 70 | 43 |  | Fuel shortage
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 70 | 43 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 811 | 920 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1400 | 1521 | 2321 | 2551 | 703 | 65
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 177 | 200 | 200 | 200 |  | 74 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 56 | 35 | 70 | 43 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 75 | 35 | 75 | 40 |  | Fuel shortage
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 179 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 395 | 331 | 438 | 345 | 208 | 159
| Total |  |  |  |  | 26844 | 25809 | 9637 | 11762 | 14424.6 | 15709 | 4781 | 2444
A. |  | 2024-04-12 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11987 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8664 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11762 | MW
3 | Day peak Generation : |  |  | 9637 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11230.24 | MW
4 | Evening peak Generation : |  |  | 11762 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 245.8608 | MKWHr | By Solar | 3.2635 | MKWHr
| By Gas : | 146.6205 | MKWHr |  | By Oil: | 12.3056 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 63.8713 | MKWHr |  | By Hydro: | 0.336 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.14352 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4781 | MW | Dhaka | 2895.44 | 2895.44 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2444 | MW | Chittagong | 1128.5 | 1128.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7225 | MW | Khulna | 1559.7 | 1559.7 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1150.56 | MMCFD |  |  | Rajshahi | 1417.6 | 1417.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 444384102.54 | ii) Oil : | Taka | 226022672.01 | Comilla | 1314 | 1314 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 427923595.57 | Total | Taka | 1098330370.12 | Mymensingh | 1149 | 1149 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 507 | 507 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 30 | MW (W to E) at | 21:00 | hrs | Barisal | 416 | 416 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 30 | MW at | 21:00 | hrs | Rangpur | 843 | 843 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.9°C |  |  | Total | 11230.24 | 11230.24 |  | 0
B. |  | 2024-04-13 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 36.9°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15709 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
4 | Reserve(Generation end) |  |  |  | 2909 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 262.5359 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9604 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.3265 | MKWHr. | ii) HVDC Flow at Peak Time |  | 777 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9939 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 77.72 |  | (b) Today: | 77.59 |  | (c) Rule Curve: |  | 85.6
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-04-12 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 170 | 180 | 0 | 10 | 0 | 331 | 0 |  | 0 | 400 | 309 | 0 | 0 | 0 | 309 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 16 | 8 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 32 | 51 | 0 | 0 | 6 | 5 | 42 | 0 | 0 | 0 | 280 | 270 | 190 | 73 | 0 | 33 | 5 | 0 | 5 | 0 | 0 | 43 | 0 | 10 | 33 | 17 | 94 | 200 | 0 | 0 | 0 | 41 | 30 | 11 | 10 | 112 | 0 | 62 | 0 | 0 | 206 | 17 | 0 | 0 | 290 | 24 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 93 | 0 | 366 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 11 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 285 | 0 | 0 | 379 | 7 | 376 | 0 | 200 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 812 | 0 | 0 |  | 6648 | 3518 | 10166 | 4161 | 920 | 2060 | 0 | 384 | 2457 | 0 | 0 | 83 | 94 | 0 | 7 | 0 | 77.77
2:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 331 | 0 |  | 0 | 350 | 306 | 0 | 0 | 0 | 280 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 16 | 8 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 32 | 51 | 0 | 0 | 6 | 5 | 42 | 0 | 0 | 0 | 280 | 275 | 196 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 52 | 0 | 10 | 33 | 17 | 92 | 200 | 0 | 0 | 0 | 41 | 30 | 5 | 5 | 112 | 0 | 62 | 0 | 0 | 206 | 17 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 55 | 0 | 320 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 12 | 11 | 345 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 36 | 0 | 285 | 0 | 0 | 377 | 9 | 377 | 0 | 200 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 816 | 0 | 0 |  | 6322 | 3448 | 9770 | 4046 | 920 | 1908 | 0 | 292 | 2420 | 0 | 0 | 83 | 92 | 0 | 9 | 0 | 77.76
3:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 328 | 0 |  | 0 | 330 | 305 | 0 | 0 | 0 | 280 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 32 | 51 | 0 | 0 | 6 | 5 | 42 | 0 | 0 | 0 | 280 | 270 | 190 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 52 | 0 | 10 | 33 | 17 | 90 | 200 | 0 | 0 | 0 | 41 | 30 | 5 | 5 | 80 | 0 | 62 | 0 | 0 | 207 | 17 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 35 | 0 | 318 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 27 | 11 | 300 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 35 | 0 | 286 | 0 | 0 | 376 | 11 | 376 | 0 | 150 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 820 | 0 | 0 |  | 6107 | 3374 | 9481 | 3923 | 919 | 1757 | 0 | 276 | 2422 | 0 | 0 | 83 | 90 | 0 | 11 | 0 | 77.75
4:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 301 | 0 |  | 0 | 330 | 250 | 0 | 0 | 0 | 250 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 32 | 17 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 280 | 270 | 190 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 43 | 0 | 10 | 33 | 17 | 86 | 201 | 0 | 0 | 0 | 41 | 30 | 5 | 5 | 80 | 0 | 63 | 0 | 0 | 206 | 17 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 17 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 11 | 300 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 36 | 0 | 286 | 0 | 0 | 376 | 14 | 372 | 0 | 150 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 821 | 0 | 0 |  | 5878 | 3347 | 9225 | 3860 | 920 | 1662 | 0 | 215 | 2419 | 0 | 0 | 49 | 86 | 0 | 14 | 0 | 77.74
5:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 300 | 0 |  | 0 | 330 | 252 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 32 | 17 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 285 | 275 | 195 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 43 | 0 | 10 | 33 | 17 | 86 | 200 | 0 | 0 | 0 | 41 | 30 | 5 | 5 | 80 | 0 | 63 | 0 | 0 | 209 | 17 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 11 | 300 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 36 | 0 | 285 | 0 | 0 | 377 | 10 | 376 | 0 | 150 | 0 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 816 | 0 | 0 |  | 5915 | 3097 | 9012 | 3885 | 636 | 1709 | 0 | 218 | 2419 | 0 | 0 | 49 | 86 | 0 | 10 | 0 | 77.73
6:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 292 | 0 |  | 0 | 330 | 252 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 280 | 270 | 190 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 80 | 204 | 0 | 0 | 0 | 41 | 30 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 210 | 17 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 300 | 0 | 1 | 0 | 0 | 10 | 0 | 0 | 36 | 0 | 250 | 0 | 0 | 379 | 11 | 375 | 0 | 150 | 1 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 140 | 816 | 3 | 0 |  | 5691 | 2973 | 8664 | 3794 | 635 | 1624 | 0 | 126 | 2380 | 0 | 0 | 8 | 80 | 6 | 11 | 0 | 77.72
7:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 281 | 0 |  | 0 | 330 | 253 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 305 | 295 | 150 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 74 | 204 | 0 | 0 | 0 | 41 | 30 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 211 | 17 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 3 | 0 | 17 | 0 | 348 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 0 | 322 | 0 | 10 | 0 | 0 | 20 | 0 | 3 | 36 | 0 | 250 | 0 | 0 | 378 | 7 | 376 | 0 | 150 | 11 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 3 | 140 | 817 | 31 | 0 |  | 5745 | 3031 | 8776 | 3875 | 636 | 1575 | 0 | 143 | 2381 | 0 | 0 | 8 | 74 | 77 | 7 | 0 | 77.71
8:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 282 | 0 |  | 0 | 330 | 252 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 0 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 335 | 285 | 152 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 33 | 15 | 66 | 201 | 0 | 0 | 1 | 41 | 30 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 211 | 17 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 7 | 0 | 17 | 0 | 332 | 47 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 0 | 317 | 0 | 20 | 0 | 0 | 20 | 0 | 12 | 36 | 0 | 250 | 0 | 0 | 378 | 0 | 375 | 0 | 150 | 32 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 180 | 0 | 0 | 1 | 37 | 0 | 0 | 0 | 0 | 11 | 140 | 818 | 76 | 0 |  | 5795 | 3123 | 8918 | 3872 | 635 | 1574 | 0 | 182 | 2381 | 0 | 0 | 8 | 66 | 200 | 0 | 0 | 77.7
9:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 282 | 0 |  | 0 | 330 | 270 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 280 | 230 | 191 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 31 | 15 | 66 | 198 | 0 | 0 | 2 | 41 | 29 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 204 | 17 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 12 | 0 | 17 | 0 | 317 | 48 | 0 | 0 | 2 | 0 | 0 | 0 | 17 | 0 | 0 | 300 | 0 | 33 | 0 | 0 | 20 | 0 | 19 | 36 | 0 | 230 | 0 | 0 | 380 | 0 | 376 | 0 | 150 | 32 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 180 | 0 | 0 | 3 | 53 | 0 | 0 | 0 | 0 | 18 | 140 | 816 | 114 | 0 |  | 5725 | 3258 | 8983 | 3748 | 635 | 1669 | 0 | 184 | 2382 | 0 | 0 | 8 | 66 | 291 | 0 | 0 | 77.69
10:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 282 | 0 |  | 0 | 330 | 275 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 189 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 31 | 15 | 66 | 197 | 0 | 0 | 2 | 37 | 28 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 205 | 17 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 13 | 0 | 17 | 0 | 324 | 49 | 0 | 0 | 2 | 0 | 0 | 0 | 17 | 0 | 0 | 300 | 0 | 42 | 0 | 0 | 20 | 15 | 26 | 36 | 0 | 230 | 0 | 0 | 380 | 0 | 375 | 0 | 150 | 66 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 500 | 180 | 0 | 0 | 4 | 68 | 0 | 0 | 0 | 0 | 22 | 140 | 816 | 152 | 0 |  | 5843 | 3305 | 9148 | 3736 | 636 | 1720 | 0 | 200 | 2381 | 0 | 0 | 8 | 66 | 401 | 0 | 0 | 77.69
11:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 283 | 0 |  | 0 | 330 | 282 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 195 | 8 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 0 | 15 | 68 | 193 | 0 | 0 | 2 | 37 | 28 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 202 | 15 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 15 | 0 | 28 | 0 | 351 | 49 | 0 | 0 | 2 | 0 | 0 | 0 | 17 | 5 | 0 | 300 | 0 | 48 | 0 | 0 | 20 | 0 | 28 | 36 | 0 | 230 | 0 | 0 | 340 | 0 | 375 | 84 | 150 | 72 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 500 | 180 | 0 | 0 | 4 | 89 | 0 | 0 | 0 | 0 | 29 | 140 | 815 | 175 | 0 |  | 5917 | 3363 | 9280 | 3738 | 635 | 1821 | 0 | 201 | 2340 | 0 | 0 | 8 | 68 | 469 | 0 | 0 | 77.68
12:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 303 | 0 |  | 0 | 360 | 310 | 0 | 0 | 0 | 300 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 210 | 36 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 0 | 17 | 72 | 192 | 0 | 0 | 2 | 37 | 28 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 198 | 15 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 8 | 0 | 36 | 0 | 378 | 49 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 13 | 0 | 340 | 0 | 47 | 0 | 0 | 20 | 6 | 31 | 36 | 0 | 230 | 0 | 0 | 340 | 0 | 372 | 83 | 150 | 76 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 177 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 500 | 180 | 0 | 0 | 4 | 92 | 0 | 0 | 0 | 0 | 32 | 140 | 811 | 179 | 0 |  | 6229 | 3408 | 9637 | 3946 | 636 | 1929 | 0 | 223 | 2340 | 0 | 0 | 8 | 72 | 483 | 0 | 0 | 77.68
13:00 | 0 | 0 | 200 | 180 | 0 | 12 | 0 | 331 | 0 |  | 0 | 420 | 280 | 0 | 0 | 0 | 311 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 184 | 120 | 0 | 23 | 7 | 0 | 16 | 0 | 0 | 9 | 0 | 10 | 31 | 17 | 80 | 193 | 0 | 0 | 2 | 37 | 28 | 47 | 20 | 112 | 0 | 47 | 0 | 0 | 200 | 15 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 7 | 0 | 51 | 0 | 368 | 48 | 0 | 0 | 3 | 0 | 0 | 0 | 57 | 28 | 0 | 340 | 0 | 29 | 0 | 1 | 50 | 17 | 24 | 36 | 0 | 230 | 0 | 0 | 417 | 0 | 373 | 283 | 150 | 70 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 570 | 220 | 0 | 0 | 4 | 84 | 29 | 0 | 0 | 0 | 30 | 140 | 884 | 170 | 0 |  | 7038 | 3707 | 10745 | 4195 | 636 | 2409 | 0 | 374 | 2584 | 30 | 0 | 8 | 80 | 429 | 0 | 0 | 77.67
14:00 | 0 | 0 | 200 | 180 | 0 | 12 | 0 | 317 | 0 |  | 0 | 370 | 270 | 0 | 0 | 0 | 280 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 6 | 38 | 17 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 183 | 120 | 0 | 28 | 20 | 0 | 43 | 0 | 0 | 44 | 0 | 10 | 33 | 17 | 78 | 191 | 0 | 0 | 2 | 37 | 28 | 50 | 20 | 80 | 0 | 50 | 0 | 0 | 204 | 14 | 0 | 0 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 10 | 0 | 51 | 0 | 307 | 48 | 0 | 0 | 3 | 0 | 0 | 0 | 70 | 28 | 0 | 305 | 0 | 37 | 0 | 12 | 50 | 17 | 20 | 36 | 0 | 230 | 0 | 0 | 419 | 0 | 374 | 282 | 150 | 64 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 0 | 600 | 220 | 0 | 0 | 4 | 78 | 70 | 0 | 0 | 0 | 25 | 140 | 871 | 151 | 0 |  | 6824 | 3637 | 10461 | 3908 | 636 | 2270 | 0 | 480 | 2604 | 30 | 0 | 55 | 78 | 400 | 0 | 0 | 77.68
15:00 | 0 | 0 | 200 | 180 | 0 | 12 | 0 | 317 | 0 |  | 0 | 370 | 268 | 0 | 0 | 0 | 280 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 24 | 30 | 33 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 183 | 120 | 0 | 31 | 20 | 0 | 43 | 0 | 0 | 51 | 0 | 10 | 33 | 17 | 78 | 192 | 0 | 0 | 1 | 37 | 28 | 52 | 20 | 80 | 0 | 60 | 0 | 0 | 201 | 14 | 0 | 0 | 275 | 8 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 12 | 0 | 56 | 0 | 307 | 48 | 0 | 0 | 2 | 0 | 0 | 0 | 70 | 29 | 0 | 305 | 0 | 24 | 0 | 17 | 75 | 17 | 22 | 36 | 0 | 230 | 0 | 0 | 420 | 4 | 374 | 284 | 150 | 34 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 42 | 0 | 5 | 0 | 590 | 220 | 0 | 0 | 2 | 70 | 70 | 0 | 0 | 0 | 19 | 140 | 869 | 93 | 0 |  | 6876 | 3540 | 10416 | 3943 | 636 | 2267 | 0 | 518 | 2593 | 30 | 0 | 63 | 78 | 284 | 4 | 0 | 77.66
16:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 318 | 0 |  | 0 | 370 | 295 | 0 | 0 | 0 | 280 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 211 | 0 | 0 | 0 |  | 24 | 30 | 32 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 195 | 120 | 0 | 31 | 18 | 0 | 43 | 0 | 0 | 25 | 0 | 10 | 33 | 17 | 82 | 188 | 0 | 0 | 2 | 37 | 28 | 10 | 10 | 80 | 0 | 40 | 0 | 0 | 201 | 14 | 0 | 0 | 270 | 8 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 4 | 0 | 85 | 0 | 315 | 48 | 0 | 0 | 1 | 0 | 0 | 0 | 70 | 28 | 0 | 317 | 0 | 16 | 0 | 17 | 75 | 17 | 13 | 36 | 0 | 230 | 0 | 0 | 401 | 5 | 375 | 140 | 150 | 29 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 6 | 0 | 4 | 0 | 560 | 220 | 0 | 0 | 1 | 20 | 35 | 0 | 0 | 0 | 13 | 140 | 832 | 55 | 0 |  | 6595 | 3348 | 9943 | 3879 | 636 | 2135 | 0 | 448 | 2508 | 30 | 0 | 62 | 82 | 158 | 5 | 0 | 77.66
17:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 310 | 0 |  | 0 | 330 | 295 | 0 | 0 | 0 | 280 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 16 | 8 | 0 | 0 | 0 | 30 | 122 | 0 | 0 | 211 | 0 | 0 | 0 |  | 24 | 55 | 32 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 189 | 120 | 0 | 30 | 10 | 0 | 43 | 0 | 0 | 25 | 0 | 10 | 33 | 17 | 80 | 191 | 0 | 0 | 0 | 37 | 28 | 10 | 10 | 80 | 0 | 40 | 0 | 0 | 201 | 14 | 0 | 0 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 2 | 0 | 85 | 0 | 315 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 28 | 11 | 305 | 0 | 5 | 0 | 17 | 75 | 17 | 5 | 36 | 0 | 350 | 0 | 0 | 370 | 7 | 376 | 142 | 150 | 6 |  | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 6 | 0 | 2 | 0 | 500 | 180 | 0 | 0 | 0 | 13 | 36 | 0 | 0 | 0 | 7 | 140 | 822 | 23 | 0 |  | 6600 | 3067 | 9667 | 3955 | 635 | 1959 | 0 | 443 | 2408 | 30 | 0 | 87 | 80 | 63 | 7 | 0 | 77.65
18:00 | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 303 | 0 |  | 0 | 300 | 245 | 0 | 0 | 0 | 240 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 16 | 8 | 0 | 0 | 0 | 30 | 122 | 0 | 0 | 184 | 0 | 0 | 0 |  | 24 | 63 | 32 | 0 | 0 | 0 | 5 | 37 | 0 | 0 | 0 | 280 | 240 | 143 | 83 | 0 | 10 | 10 | 0 | 51 | 0 | 0 | 25 | 0 | 10 | 25 | 17 | 78 | 193 | 0 | 0 | 0 | 37 | 29 | 10 | 10 | 80 | 0 | 40 | 0 | 0 | 201 | 14 | 0 | 0 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 1 | 0 | 85 | 0 | 315 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 28 | 11 | 305 | 0 | 1 | 0 | 17 | 20 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 307 | 3 | 373 | 110 | 150 | 1 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 200 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 1 | 36 | 0 | 0 | 0 | 1 | 140 | 819 | 2 | 0 |  | 6176 | 3314 | 9490 | 3654 | 920 | 1826 | 0 | 538 | 2339 | 30 | 0 | 95 | 78 | 7 | 3 | 0 | 77.65
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 220 | 180 | 0 | 30 | 0 | 320 | 0 |  | 0 | 450 | 250 | 0 | 0 | 0 | 316 | 0 | 117 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 16 | 7 | 0 | 0 | 0 | 30 | 123 | 0 | 0 | 208 | 0 | 0 | 0 |  | 24 | 65 | 51 | 0 | 0 | 6 | 5 | 37 | 0 | 0 | 0 | 280 | 240 | 216 | 157 | 0 | 30 | 17 | 0 | 51 | 0 | 0 | 26 | 0 | 10 | 33 | 17 | 92 | 198 | 0 | 0 | 0 | 40 | 30 | 47 | 25 | 80 | 0 | 40 | 0 | 0 | 202 | 17 | 0 | 0 | 285 | 24 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 10 | 0 | 0 | 100 | 0 | 316 | 98 | 0 | 0 | 0 | 15 | 0 | 6 | 103 | 42 | 11 | 340 | 0 | 0 | 0 | 17 | 80 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 332 | 7 | 426 | 278 | 500 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 0 | 0 | 14 | 0 | 54 | 0 | 0 | 20 | 560 | 220 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 160 | 934 | 0 | 0 |  | 7733 | 3717 | 11450 | 4164 | 920 | 2728 | 0 | 749 | 2612 | 30 | 0 | 148 | 92 | 0 | 7 | 0 | 77.63
19:30 | 0 | 0 | 220 | 180 | 0 | 32 | 0 | 312 | 0 |  | 0 | 450 | 256 | 0 | 0 | 0 | 290 | 0 | 122 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 16 | 7 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 214 | 0 | 0 | 0 |  | 24 | 72 | 51 | 0 | 0 | 6 | 5 | 37 | 0 | 0 | 0 | 280 | 240 | 217 | 157 | 0 | 33 | 40 | 0 | 51 | 0 | 0 | 52 | 0 | 10 | 25 | 17 | 90 | 198 | 0 | 0 | 0 | 40 | 30 | 50 | 25 | 80 | 0 | 40 | 0 | 0 | 204 | 17 | 0 | 0 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 35 | 0 | 0 | 155 | 0 | 315 | 99 | 0 | 8 | 0 | 15 | 0 | 17 | 114 | 48 | 11 | 341 | 0 | 0 | 0 | 17 | 50 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 372 | 10 | 434 | 284 | 430 | 0 |  | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 35 | 0 | 54 | 0 | 0 | 35 | 660 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 148 | 962 | 0 | 0 |  | 7832 | 3838 | 11670 | 4089 | 877 | 2689 | 0 | 954 | 2776 | 30 | 0 | 155 | 90 | 0 | 10 | 0 | 0
20:00 | 0 | 0 | 220 | 180 | 0 | 32 | 0 | 312 | 0 |  | 0 | 450 | 278 | 0 | 0 | 0 | 290 | 0 | 120 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 7 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 214 | 0 | 0 | 0 |  | 24 | 72 | 51 | 0 | 0 | 6 | 5 | 38 | 0 | 0 | 0 | 280 | 240 | 215 | 185 | 0 | 33 | 40 | 0 | 51 | 0 | 0 | 46 | 0 | 10 | 25 | 17 | 94 | 197 | 0 | 0 | 0 | 40 | 29 | 49 | 25 | 80 | 0 | 40 | 0 | 0 | 206 | 17 | 0 | 0 | 280 | 24 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 31 | 0 | 0 | 155 | 0 | 315 | 99 | 0 | 16 | 0 | 15 | 0 | 17 | 88 | 48 | 11 | 342 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 373 | 7 | 428 | 292 | 430 | 0 |  | 778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 600 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 150 | 968 | 0 | 0 |  | 7817 | 3751 | 11568 | 4040 | 778 | 2794 | 0 | 951 | 2719 | 30 | 0 | 155 | 94 | 0 | 7 | 0 | 77.64
21:00 | 0 | 0 | 220 | 180 | 0 | 32 | 0 | 312 | 0 |  | 0 | 450 | 298 | 0 | 0 | 0 | 315 | 0 | 201 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 7 | 16 | 8 | 0 | 0 | 0 | 30 | 122 | 0 | 0 | 213 | 0 | 0 | 0 |  | 24 | 72 | 51 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 240 | 219 | 185 | 0 | 33 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 10 | 25 | 17 | 96 | 199 | 0 | 0 | 0 | 40 | 30 | 50 | 25 | 112 | 0 | 63 | 0 | 0 | 205 | 17 | 0 | 0 | 295 | 24 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 34 | 0 | 0 | 155 | 0 | 294 | 99 | 0 | 0 | 0 | 15 | 0 | 17 | 70 | 48 | 11 | 212 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 420 | 7 | 428 | 370 | 585 | 0 |  | 777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 620 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 140 | 920 | 0 | 0 |  | 8077 | 3685 | 11762 | 4034 | 777 | 3075 | 0 | 876 | 2728 | 30 | 0 | 139 | 96 | 0 | 7 | 0 | 77.63
22:00 | 0 | 0 | 200 | 180 | 0 | 32 | 0 | 312 | 0 |  | 0 | 450 | 303 | 0 | 0 | 0 | 320 | 0 | 203 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | 16 | 8 | 0 | 0 | 0 | 30 | 123 | 0 | 0 | 213 | 0 | 0 | 0 |  | 24 | 72 | 51 | 0 | 0 | 0 | 5 | 39 | 0 | 0 | 0 | 280 | 250 | 218 | 185 | 0 | 33 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 10 | 25 | 17 | 100 | 198 | 0 | 0 | 0 | 40 | 30 | 50 | 47 | 112 | 0 | 62 | 0 | 0 | 206 | 17 | 0 | 0 | 230 | 24 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 37 | 0 | 0 | 155 | 0 | 20 | 99 | 0 | 0 | 0 | 15 | 0 | 17 | 73 | 48 | 11 | 116 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 449 | 8 | 581 | 370 | 590 | 0 |  | 777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 840 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 224 | 948 | 0 | 0 |  | 7874 | 4113 | 11987 | 3674 | 777 | 3129 | 0 | 872 | 3242 | 30 | 0 | 155 | 100 | 0 | 8 | 0 | 77.63
23:00 | 0 | 0 | 220 | 180 | 0 | 60 | 0 | 313 | 0 |  | 0 | 450 | 298 | 0 | 0 | 0 | 330 | 0 | 200 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 12 | 16 | 8 | 0 | 0 | 0 | 30 | 121 | 0 | 0 | 213 | 0 | 0 | 0 |  | 24 | 72 | 51 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 280 | 250 | 218 | 185 | 0 | 33 | 32 | 0 | 51 | 0 | 0 | 25 | 0 | 10 | 25 | 17 | 100 | 202 | 0 | 0 | 0 | 41 | 30 | 50 | 47 | 112 | 0 | 58 | 0 | 0 | 207 | 17 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 72 | 0 | 0 | 155 | 0 | 0 | 49 | 0 | 0 | 0 | 15 | 0 | 17 | 70 | 48 | 10 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 450 | 13 | 576 | 368 | 592 | 0 |  | 778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 970 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 307 | 992 | 0 | 0 |  | 7529 | 4266 | 11795 | 3556 | 778 | 2822 | 0 | 814 | 3495 | 30 | 0 | 187 | 100 | 0 | 13 | 0 | 77.62
24:00 | 0 | 0 | 220 | 180 | 0 | 76 | 0 | 319 | 0 |  | 0 | 450 | 285 | 0 | 0 | 0 | 327 | 0 | 211 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 213 | 0 | 0 | 0 |  | 24 | 56 | 51 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 280 | 250 | 221 | 184 | 0 | 33 | 23 | 0 | 51 | 0 | 0 | 25 | 0 | 10 | 25 | 17 | 100 | 202 | 0 | 0 | 0 | 41 | 30 | 50 | 47 | 112 | 0 | 57 | 0 | 0 | 209 | 17 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 65 | 0 | 0 | 155 | 0 | 0 | 49 | 0 | 0 | 0 | 15 | 0 | 0 | 114 | 39 | 10 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 443 | 18 | 573 | 367 | 595 | 0 |  | 778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 0 | 990 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 275 | 942 | 0 | 0 |  | 7533 | 4116 | 11649 | 3567 | 778 | 2812 | 0 | 750 | 3423 | 30 | 0 | 171 | 100 | 0 | 18 | 0 | 77.62
KWH | 0 | 0 | 3830125 | 4362750 | 0 | 485090 | 0 | 7509600 | 0 |  | 0 | 9093000 | 6665484 | 0 | 0 | 0 | 6815530 | 0 | 2809000 | 0 | 0 | 178560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360000 | 155520 | 390800 | 194300 | 0 | 0 | 0 | 336000 | 2800000 | 0 | 0 | 4939080 | 0 | 0 | 0 |  | 255600 | 818592 | 637046 | 0 | 0 | 28320 | 107184 | 977280 | 0 | 0 | 0 | 7196700 | 6156000 | 4645000 | 1873454 | 0 | 436824 | 334560 | 0 | 641872 | 0 | 0 | 682416 | 0 | 225180 | 670500 | 392720 | 1993920 | 4619520 | 0 | 0 | 13750 | 942000 | 678600 | 529200 | 451872 | 2205491 | 0 | 1204320 | 0 | 0 | 5125170 | 385000 | 0 | 0 | 6325830 | 212064 | 0 | 0 | 0 | 0 | 0 | 1550400 | 0 | 264240 | 100170 | 0 | 1665120 | 0 | 7070000 | 1160400 | 0 | 20072 | 23160 | 90327 | 0 | 91614 | 1248300 | 581280 | 153600 | 6911100 | 0 | 312910 | 0 | 186927 | 585455 | 249480 | 205890 | 875520 | 0 | 6184000 | 0 | 0 | 9223635 | 143520 | 9687272 | 3270909 | 5986818 | 462091 |  | 17326545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1503000 | 120156 | 0 | 0 | 0 | 1290000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144720 | 0 | 0 | 4521900 | 0 | 0 | 4012173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7885236 | 0 | 0 | 202368 | 0 | 448473 | 0 | 43789 | 169440 | 16144300 | 4910291 | 0 | 0 | 31440 | 614880 | 747456 | 0 | 0 | 0 | 209664 | 3709100 | 20585062 | 1245750 | 0 |  | 159995034 | 85865743 | 245860777 | 94863935 | 17326545 | 51756543 | 0 | 10671353 | 63871269 | 336000 | 0 | 1634198 | 1993920 | 3263494 | 143520 | 0
Fuel Cost | 0 | 0 | 16431236.25 | 19414237.5 | 0 | 1853043.8 | 0 | 21627648 | 0 |  | 0 | 28915740 | 22795955.28 | 0 | 0 | 0 | 20787366.5 | 0 | 15028150 | 0 | 0 | 3467635.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15288000 | 0 | 0 | 15755665.2 | 0 | 0 | 0 |  | 4496004 | 14415405.12 | 11409493.86 | 0 | 0 | 466147.2 | 398724.48 | 0 | 0 | 0 | 0 | 20078793 | 18837360 | 15421400 | 6276070.9 | 0 | 1472096.88 | 1465372.8 | 0 | 2573906.72 | 0 | 0 | 12324432.96 | 0 | 168885 | 2494260 | 294540 | 13080115.2 | 14366707.2 | 0 | 0 | 0 | 3673800 | 2531178 | 2407860 | 2056017.6 | 7542779.22 | 0 | 6683976 | 0 | 0 | 14299224.3 | 2533300 | 0 | 0 | 19546814.7 | 159048 | 0 | 0 | 0 | 0 | 0 | 29783184 | 0 | 4653266.4 | 0 | 0 | 28889832 | 0 | 18735500 | 22117224 | 0 | 360091.68 | 0 | 1476846.45 | 0 | 1643555.16 | 23855013 | 11282644.8 | 2735616 | 18383526 | 0 | 0 | 0 | 3136635.06 | 2189601.7 | 4458207.6 | 0 | 15776870.4 | 0 | 18366480 | 0 | 0 | 64288735.95 | 0 | 57154904.8 | 0 | 0 | 0 |  | 48687591.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4749480 | 569539.44 | 0 | 0 | 0 | 6295200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109553.04 | 0 | 0 | 38164836 | 0 | 0 | 13240170.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23024889.12 | 0 | 0 | 4010933.76 | 0 | 8933582.16 | 0 | 0 | 3361689.6 | 104615064 | 15271005.01 | 0 | 0 | 0 | 0 | 12968361.6 | 0 | 0 | 0 | 0 | 27632795 | 136067259.82 | 0 | 0 |  | 712396125.87 | 447701950.9 | 1160098076.77 | 310085107.95 | 48687591.45 | 134298994.59 | 0 | 196730137.83 | 427923595.57 | 0 | 0 | 29292534.18 | 13080115.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 303 | 0 |  | 0 | 360 | 310 | 0 | 0 | 0 | 300 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 5 | 16 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 214 | 0 | 0 | 0 |  | 0 | 8 | 0 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 230 | 210 | 36 | 0 | 5 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 10 | 0 | 17 | 72 | 192 | 0 | 0 | 2 | 37 | 28 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 198 | 15 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 8 | 0 | 36 | 0 | 378 | 49 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 13 | 0 | 340 | 0 | 47 | 0 | 0 | 20 | 6 | 31 | 36 | 0 | 230 | 0 | 0 | 340 | 0 | 372 | 83 | 150 | 76 |  | 636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 177 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 500 | 180 | 0 | 0 | 4 | 92 | 0 | 0 | 0 | 0 | 32 | 140 | 811 | 179 | 0 |  | 9637 | DayPeak
Yesterday Evening Peak | 0 | 0 | 220 | 180 | 0 | 32 | 0 | 312 | 0 |  | 0 | 450 | 298 | 0 | 0 | 0 | 315 | 0 | 201 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 7 | 16 | 8 | 0 | 0 | 0 | 30 | 122 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 24 | 72 | 51 | 0 | 0 | 0 | 5 | 38 | 0 | 0 | 0 | 280 | 240 | 219 | 185 | 0 | 33 | 40 | 0 | 51 | 0 | 0 | 25 | 0 | 10 | 25 | 17 | 96 | 199 | 0 | 0 | 0 | 40 | 30 | 50 | 25 | 112 | 0 | 63 | 0 | 0 | 205 | 17 | 0 | 0 | 295 | 24 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 34 | 0 | 0 | 155 | 0 | 294 | 99 | 0 | 0 | 0 | 15 | 0 | 17 | 70 | 48 | 11 | 212 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 36 | 0 | 230 | 0 | 0 | 420 | 7 | 428 | 370 | 585 | 0 |  | 777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 35 | 0 | 56 | 0 | 0 | 35 | 620 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 140 | 920 | 0 | 0 |  | 11762 | EvPeak
Forecast for Evening | 0 | 0 | 220 | 180 | 0 | 60 | 0 | 300 | 0 |  | 0 | 450 | 330 | 0 | 0 | 40 | 335 | 0 | 200 | 0 | 91 | 145 | 15 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 15 | 15 | 33 | 33 | 25 | 0 | 0 | 30 | 120 | 0 | 25 | 211 | 0 | 0 | 0 |  | 24 | 80 | 51 | 80 | 12 | 6 | 5 | 40 | 0 | 0 | 0 | 330 | 300 | 220 | 185 | 0 | 36 | 52 | 0 | 51 | 0 | 33 | 52 | 0 | 10 | 30 | 20 | 160 | 200 | 0 | 0 | 0 | 41 | 30 | 53 | 47 | 110 | 0 | 63 | 0 | 0 | 210 | 20 | 0 | 0 | 320 | 25 | 0 | 0 | 300 | 0 | 0 | 105 | 0 | 149 | 0 | 0 | 155 | 6 | 0 | 100 | 100 | 34 | 0 | 32 | 17 | 17 | 114 | 58 | 12 | 0 | 53 | 0 | 54 | 17 | 0 | 35 | 0 | 36 | 0 | 330 | 145 | 0 | 524 | 40 | 576 | 350 | 550 |  |  | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 50 | 0 | 130 | 10 | 110 | 0 | 0 | 60 | 50 | 30 | 96 | 35 | 34 | 50 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 90 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 1244 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 150 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 180 | 0 | 12 | 0 | 300 | 0 | 0 | 0 | 450 | 330 | 0 | 0 | 40 | 335 | 0 | 120 | 0 | 91 | 32 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 12 | 33 | 33 | 8 | 0 | 0 | 30 | 120 | 0 | 8 | 211 |  | 0 | 0 | 0 | 24 | 60 | 51 | 80 | 12 | 6 | 5 | 40 | 0 | 0 | 0 | 330 | 300 | 220 | 185 | 0 | 36 | 44 | 0 | 51 | 0 | 33 | 25 | 0 | 10 | 30 | 20 | 152 | 200 | 0 | 0 | 1.6 | 41 | 30 | 53 | 47 | 110 | 0 | 63 | 0 | 0 | 210 | 20 | 0 | 0 | 320 | 25 | 0 | 0 | 300 | 0 | 0 | 56 | 0 | 149 | 20 | 0 | 50 | 6 | 0 | 50 | 17 | 34 | 5 | 16 | 0 | 17 | 17 | 38 | 12 | 0 | 53 | 50 | 0 | 17 | 0 | 17 | 35 | 36 | 0 | 330 | 54 | 0 | 524 | 40 | 576 | 350 | 550 | 25 |  | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 30 | 0 | 130 | 7 | 48 | 0 | 0 | 60 | 0 | 0 | 50 | 35 | 34 | 40 | 8 | 30 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 70 | 0 | 35 | 0 | 35 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 0 | 30 | 150 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 130 | 180 | 0 | 12 | 0 | 311 | 0 | 0 | 0 | 400 | 285 | 0 | 0 | 0 | 331 | 0 | 77 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 16 | 8 | 0 | 0 | 0 | 30 | 120 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 32 | 51 | 0 | 0 | 0 | 5 | 42 | 0 | 0 | 0 | 280 | 250 | 190 | 189 | 0 | 27 | 10 | 0 | 10 | 0 | 0 | 28 | 0 | 10 | 25 | 17 | 74 | 202 | 0 | 0 | 1 | 41 | 30 | 50 | 47 | 112 | 0 | 63 | 0 | 0 | 211 | 17 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 3 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 17 | 12 | 36 | 0 | 230 | 0 | 0 | 524 | 10 | 430 | 169 | 400 | 25 | 0 | 757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 650 | 220 | 0 | 0 | 1 | 40 | 10 | 0 | 0 | 0 | 12 | 150 | 817 | 72 | 0 | 0 |  |  |  | 146620478 | 17326545 | 0 | 63871269 | 12305551 | 1993920 | 3263494 | 143520 | 336000 |  |  | 245860777
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  |  |  |  | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [12 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 | [5 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 146.6205 | 17.3265 | 0 | 63.8713 | 12.3056 | 1.9939 | 3.2635 | 0.14352 | 0.336
| Minimum Generation |  | 8664 | 6:00
| Highest Generation |  | 11987 | 22:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 245.8608
| Day Peak Generation |  | 9637 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 11762 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 920 | 1:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 777 | 21:00
| Load factor L.F |  | 85.46% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-04-13
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2024-04-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9637 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9604
Evening Peak Generation : |  |  | 11762 | MW Hour : | 21:00 | Available Max Generation : |  | 15709
E.P. Demand (at gen end) : |  |  | 11762 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12800
Maximum Generation : |  |  | 11987 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2909
Total Gen. (MKWH) : |  |  | 245.8608 | System Load Factor : | 85.46% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 30 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-04-13
Actual : |  | 77.59 | Ft.(MSL) , | Rule curve : | 85.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1150.56 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 444384102.54
: |  |  | Coal : | 427923595.57 | Oil : | 226022672.01 | Total : | 1098330370.12
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3823.072 |  |  | 0 | -42.46%
Chittagong Area |  | 0 | 0:00 | 1045.9496 |  |  | 0 | -40.84%
Khulna Area |  | 0 | 0:00 | 1463.8103 |  |  | 0 | -40.49%
Rajshahi Area |  | 0 | 0:00 | 1271.063 |  |  | 0 | -40.12%
Cumilla Area |  | 0 | 0:00 | 1046.4992 |  |  | 0 | -40.35%
Mymensingh Area |  | 0 | 0:00 | 777.6683 |  |  | 0 | -40.03%
Sylhet Area |  | 0 | 0:00 | 436.6164 |  |  | 0 | -40.64%
Barisal Area |  | 0 | 0:00 | 363.2198 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 710.409 |  |  | 0 | -39.98%
Total |  | 0 |  | 10938.3077 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:16 | 11:56 | BIPTC S/S 20DF11 Forced S/D Due to Shutdown is taken for corrective maintenance due to trip
08:26 | 12:01 | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Another side by NLDC.
08:28 | 12:53 | Meghnaghat-Shyampur 230kV Ckt-1 Tripped from Meghnaghat 230/132kV end showing Distance Relay relays Due to unknown
10:47 |  | Unique Meghnaghat Power Limited (UMPL) Syncronized with remarks:- GT
11:00 | 12:27 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Forced S/D Due to 33KV Busbar S/D due to Summit power 33KV ckt R-phase redhot |  |  |  |  | 30.0MW load interrup.
remove.
11:00 | 12:27 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Forced S/D Due to 33KV Busbar S/D due to Summit power 33KV ckt R-phase redhot |  |  |  |  | 30.0MW load interrup.
remove.
11:47 | 12:15 | Mymensingh-Netrokona 132kV Ckt-1 Tripped from Netrakona 132/33kV end showing E/F relay relays Due to Trip forbE/F |  |  |  |  | 50.0MW load interrup.
Netrakona 132/33 kV end.
12:00 |  | Day peak Generation : 9634 MW
12:05 |  | Ashuganj 230/132/33kV S/S T-4 Kalabagan HT Forced S/D Due to kolabagan-3(33KV) CT burst |  |  |  |  | 12.0MW load interrup.
| 12:15 | Mymensingh-Netrokona 132kV Ckt-1 is restored.
13:08 | 21:39 | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Another side by NLDC. and from
Meghnaghat 230/132kV end Due to Preventive Maintenance Work
| 17:29 | Baroaulia-Hathazari 132 kV Ckt-1 is restored.
21:00 |  | Evening peak generation is 11762MW
21:00 |  | Evening Peak Generation = 11,762MW
21:30 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- ST
21:46 |  | Bibiyana South 400 MW Shutdown with remarks:- st
22:02 |  | Bibiyana-III 400 MW CCPP Shutdown with remarks:- GT
22:12 |  | Rampal 400/230kV S/S Bus Reactor Forced S/D Due to Due To Low voltage.
22:24 |  | Bibiyana South 400 MW Shutdown with remarks:- gt
22:45 |  | Bibiana-II 341 MW CCPP (Summit) Shutdown with remarks:- st was sd at 22:41
22:50 | 00:44 | Shahjibazar 132/33kV S/S TR-02 LT Scheduled S/D Due to Bus D/S 989B Red Hot Maintenance. Load flow by TR-04 and TR-06.
22:55 | 00:28 | Shahjibazar 132/33kV S/S TR-02 HT Scheduled S/D Due to Bus D/S 989B Red Hot Maintenance. Load flow by TR-04 and TR-06.
00:58 |  | SS Power Syncronized with remarks:- Unit-1
06:00 |  | Minimum Generation: 9604 MW.
07:00 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Work on Another Side

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-04-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 3830125
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4362750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 32 | 485090 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 312 | 7509600 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9093000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 6665484 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 201 | 2809000 | Machine problem
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 6815530 | Frequency Control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 178560 | low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 21 | 515520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 390800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 194300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 264240 | low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | Reserve
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 205890
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 370 | 3270909
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 585 | 5986818 | On test.
| Dhaka area Total |  |  |  | 5634 | 3058 | 52577616
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 122 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 100170
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 28320 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 336000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 213 | 4939080
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 20072 | Reserve
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 72 | 818592 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 637046 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 5 | 107184 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 977280
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23160
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 90327 | low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 91614 | low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 11 | 153600 | Reserve
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 186927 | low demand
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 420 | 9223635 | low demand
| Cox's Bazar Wind |  | IPP | 66 | 0 | 7 | 143520 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 428 | 9687272 | low demand
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 462091
| Chattogram area Total |  |  |  | 4344 | 1446 | 30825890
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 219 | 4645000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7196700 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6156000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 6184000 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 436824 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 40 | 334560
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 185 | 1873454
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 641872
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 1665120 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 225180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 96 | 1993920
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 670500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 682416 | low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 392720 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 1248300 | low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 48 | 581280 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 249480 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 36 | 875520 | Fuel shortage
| Cumilla Area Total |  |  |  | 2929 | 1777 | 36052846
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 199 | 4619520 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13750
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 107 | 1550400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1160400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 312910
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 255600 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 429 | 7912580
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 942000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 678600 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2205491 | ST under maint
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 529200
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 25 | 451872 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Gas shortage
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1204320
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 585455
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 205 | 5125170 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 385000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 212064
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 6325830 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 294 | 7070000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 212 | 6911100 | FGMO
| Sylhet Area Total |  |  |  | 2427 | 1367 | 32626102
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 777 | 17326545
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Reserve
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 614880
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 777 | 17941425
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 11 | 120156 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1503000 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 620 | 16144300 | low demand
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4910291
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3709100 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1056 | 26386847
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1290000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 4012173 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 313 | 7885236 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 144720 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Fuel shortage
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 202368 | low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 169440 | low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 31440
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 920 | 20585062
| Rajshahi Area Total |  |  |  | 3431 | 1521 | 34320439
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4521900
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 448473 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43789
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 75 | 747456 | Fuel shortage
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 209664
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1245750
| Rangpur Area Total |  |  |  | 950 | 331 | 7217032
| Total |  |  |  | 25809 | 11762 | 245860777
| Eastern Grid Total |  |  |  | 15926 | 8077 | 159995034
| Western Grid Total |  |  |  | 9883 | 3685 | 85865743
| National Grid Total |  |  |  | 25809 | 11762 | 245860777
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-04-12
| (a) ENTIRE EASTERN GRID : |  | 6993.94 | MW | (b) ENTIRE WESTERN GRID : |  | 4236.3 | MW
| i) Dhaka area |  | 2895.44 | MW | i) Khulna area |  | 1559.7 | MW
| ii) Chittagong area |  | 1128.5 | MW | ii) Rajshahi area |  | 1417.6 | MW
| iii) Comilla area |  | 1314 | MW | iii) Barisal area |  | 416 | MW
| iv) Mymensingh area |  | 1149 | MW | iv) Rangpur area |  | 843 | MW
| v) Sylhet area |  | 507 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11230.24 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 30 | 20:00 | Kamrangirchar | 23.4 | 00:00 | Narinda | 34 | 00:00 | Sherpur | 162 | 19:00
2 | AKSML | 3 | 14:00 | Chowmuhani | 218 | 21:00 | Kaptai | N/A | N/A | Narshingdi | 146 | 23:00 | Shikalbaha | 20 | 18:30
3 | Aftabnagar | 24 | 00:00 | Chuadanga | 110 | 22:00 | Kazla | 43 | 00:00 | Natore | 149 | 19:30 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 65 | 22:00 | Coxsbazar | 127 | 20:00 | Keranigonj | 55 | 23:00 | Nawabganj | 47.8 | 23:00 | Shitalakhya | 55.4 | 00:00
5 | Agrabad | 54 | 00:00 | Cumilla(N) | 181 | 22:00 | Khagrachori | 32 | 19:30 | Netrakona | 151 | 19:30 | Sholosohor | 29 | 00:00
6 | Amnura | 81 | 21:00 | Cumilla(S) | 131 | 23:00 | Khulna | 58 | 22:00 | New | 13.3 | 23:00 | Shyampur | 40 | 13:00
7 | Ashuganj | 60 | 00:00 | Daudkandi | 128 | 22:00 | Khulshi | 93 | 19:30 | Niamatpur | 104 | 22:00 | Siddhirganj | 62 | 23:00
8 | BIPTC | N/A | N/A | Dhaka | 8 | 12:00 | Kishoreganj | 146 | 19:30 | Noapara | 36 | 19:30 | Sirajganj | 102 | 20:00
9 | BSRM | 154 | 20:00 | Dhamrai | 82 | 22:00 | Kodda | 124 | 21:00 | PHP | 3 | 15:00 | Sonargaon | 42 | 19:30
10 | Bagerhat | 79 | 21:00 | Dhanmondi | 67 | 22:00 | Kulaura | 46 | 19:00 | Pabna | 110 | 23:00 | Sreemongol | 60 | 20:00
11 | Bakulia | 68 | 00:00 | Dohazari | 100 | 22:00 | Kurigram | 68 | 19:00 | Palashbari | 124 | 19:00 | Sreepur | 37 | 19:00
12 | Banani | 26.4 | 19:30 | Faridpur | 140 | 22:00 | Kushtia | 104 | 20:00 | Panchagarh | 50 | 19:30 | Srinagar | 45.7 | 22:00
13 | Bangabhaban | 3 | 18:00 | Fatullah | 32 | 00:00 | Lalbag | 19 | 00:00 | Patuakhali | 85 | 23:00 | Sunamganj | 52 | 20:00
14 | Barapukuria | 63 | 22:00 | Fenchuganj | 35 | 19:00 | Lalmonirhat | 60 | 19:30 | Payra | 22 | 00:00 | Sylhet | 36 | 10:00
15 | Barguna | 20 | 00:00 | Feni | 108 | 23:00 | MI_Cement | 0 | 00:00 | Postogola | 37 | 00:00 | Sylhet-132 | 90 | 19:00
16 | Barishal | 94 | 22:00 | GPH | 11 | 20:00 | Madanganj | 25 | 22:00 | Purbachal | 15 | 23:00 | TK | 30 | 00:00
17 | Barishal-230 | 94 | 23:00 | Ghorashal | 59 | 23:00 | Madaripur | 108 | 23:00 | Purbasadipur | 107 | 13:00 | Tangail | 208 | 19:00
18 | Baroaulia | 45 | 20:00 | Goalpara | 32 | 23:00 | Madartek | 59.75 | 23:00 | Rahim | 0 | 00:00 | Thakurgaon | 94 | 13:00
19 | Baroirhat | 54 | 19:00 | Gollamari | 50 | 13:00 | Madunaghat | 43 | 21:00 | Rajbari | 68 | 22:00 | Tongi | 71 | 20:00
20 | Bashundhara | 111 | 20:00 | Gopalganj | 101.2 | 22:00 | Magura | 61 | 21:00 | Rajendrapur | 70 | 19:00 | Ullahpara | 28 | 18:30
21 | BashundharaCement | 0 | 00:00 | Gulshan | 56 | 12:00 | Mahasthangarh | 74 | 19:30 | Rajshahi | 134 | 23:00 | Ullon | 40 | 00:00
22 | Beanibazar | 62 | 19:30 | Halishahar | 50 | 19:00 | Manikganj | 92 | 20:00 | Rajshahi-230 | 35 | 23:00 | Uttara | 41 | 21:00
23 | Benapole | 64 | 19:00 | HaripurSBU | 50 | 22:00 | Maniknagar | 44 | 22:00 | Ramganj | 120 | 23:00 | UttaraNew | 38 | 00:00
24 | Bhaluka | 102 | 19:00 | Hasnabad | 68 | 23:00 | Matarbari | 46 | 21:00 | Rampur | 24 | 00:00 | Zigatola | 55 | 00:00
25 | Bhandaria | 50 | 20:00 | Hathazari | 70 | 19:00 | Matuail | 32 | 23:00 | Rangamati | 16 | 19:00
26 | Bhangura | 42 | 19:00 | Ishurdi | 59 | 22:00 | Millgate | 49 | 22:00 | Rangpur | 115 | 19:00
27 | Bheramara(GK) | 58 | 22:00 | Jaldhaka | 88 | 19:00 | Mirpur | 91 | 00:00 | Ruppur | 4.4 | 15:00
28 | Bhulta | 106 | 23:00 | Jamalpur | 146 | 19:00 | Mirsorai | 6 | 00:00 | SSM | 0 | 00:00
29 | Bog-Sherpur | 48 | 22:00 | Jashore | 126 | 22:00 | Mirzapur | 42 | 19:00 | Saidpur | 87 | 19:30
30 | Bogura | 141 | 23:00 | Jhenaidah | 129 | 19:00 | Mithapukur | 60 | 19:00 | Satkhira | 123 | 22:00
31 | Borhanuddin | 85 | 00:00 | Joydebpur | 105 | 22:00 | Modern | 0 | 00:00 | Satmasjid | 75 | 00:00
32 | Brahmanbaria | 189 | 22:00 | Joypurhat | 62 | 21:00 | Mogbazar | 69.3 | 18:30 | Savar | 104 | 22:00
33 | Cantonment | 72 | 00:00 | Juldah | 12 | 00:00 | Mongla | 15 | 19:00 | SevenRings | 1.42 | 18:00
34 | Chandpur | 68 | 19:00 | KSRM | 3 | 00:00 | Motijheel | 22 | 00:00 | ShahCement | 2 | 10:00
35 | Chandraghona | 31 | 19:30 | Kabirpur | 117 | 22:00 | Munshiganj | 92 | 00:00 | Shahjadpur | 79 | 21:00
36 | Chapai | 64 | 21:00 | Kachua | 83 | 22:00 | Mymensingh | 219 | 21:00 | Shahjibazar | 114 | 22:00
37 | Charsaidpur | 4 | 00:00 | Kallyanpur | 75 | 00:00 | Naogaon | 131 | 22:00 | Shahmirpur | 49 | 04:00
38 | Chauddagram | 73 | 13:00 | Kalurghat | 18 | 00:00 | Narail | 55 | 19:00 | Shariatpur | 86 | 22:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-04-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 06:00 | 391 | 22:00 | Gopalganj | 410 | 06:00 | 393 | 22:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 388 | 05:00 | 379 | 13:00
| Bhulta | 406 | 04:00 | 397 | 18:30 | Madunaghat_I | 398 | 18:30 | 390 | 00:00
| Bibiana | 406 | 03:00 | 391 | 23:00 | Payra | 417 | 06:00 | 408 | 23:00
| BIPTC | 409 | 05:00 | 393 | 19:00 | Rahanpur | 403 | 04:00 | 391 | 12:00
| Bogura | 391 | 04:00 | 375 | 12:00 | Rampal | 408 | 06:00 | 385 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 235 | 04:00 | 228 | 23:00 | Haripur | 237 | 05:00 | 231 | 21:00
| AKSML | 225 | 18:00 | 219 | 01:00 | Hasnabad | 237 | 04:00 | 231 | 22:00
| Aminbazar | 237 | 06:00 | 229 | 21:00 | Hathazari | 223 | 18:00 | 218 | 12:00
| Ashuganj | 238 | 06:00 | 233 | 23:00 | Ishurdi | 237 | 04:00 | 224 | 12:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 228 | 04:00 | 213 | 19:30
| Baghabari | 232 | 06:00 | 223 | 21:00 | Kaliakoir | 237 | 04:00 | 232 | 12:00
| Barapukuria | 220 | 03:00 | 207 | 12:00 | Keranigonj | 236 | 06:00 | 229 | 23:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 232 | 04:00 | 215 | 21:00
| Barishal | 242 | 06:00 | 234 | 22:00 | Madunaghat_I | 225 | 19:30 | 219 | 00:00
| Bheramara | 236 | 04:00 | 223 | 12:00 | Maniknagar | 237 | 04:00 | 23.6 | 10:00
| Bhulta | 239 | 06:00 | 231 | 23:00 | Meghnaghat | 244 | 03:00 | 240 | 19:00
| Bibiana | 233 | 03:00 | 225 | 23:00 | Mirsorai | 225 | 04:00 | 222 | 10:00
| BIPTC | 237 | 04:00 | 221 | 12:00 | Rajshahi | 237 | 05:00 | 223 | 12:00
| Bogura | 231 | 04:00 | 220 | 12:00 | Rampal | 231 | 04:00 | 216 | 22:00
| Bogura-400 | 232 | 04:00 | 222 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 08:00 | 240 | 13:00 | Rampura | 238 | 05:00 | 231 | 20:00
| BSRM | 228 | 18:00 | 221 | 13:00 | Shikalbaha | 220 | 20:00 | 215 | 13:00
| Cumilla(N) | 231 | 15:00 | 225 | 23:00 | Shyampur | 237 | 04:00 | 232 | 23:00
| Fenchuganj | 238 | 15:00 | 231 | 23:00 | Siddhirganj | 240 | 03:00 | 228 | 15:00
| Ghorashal | 240 | 01:00 | 235 | 00:00 | Sirajgonj | 239 | 04:00 | 230 | 23:00
| Ghorashal-230 | 236 | 06:00 | 232 | 00:00 | Sreepur | 233 | 04:00 | 227 | 12:00
| GPH | 224 | 18:00 | 218 | 13:00 | Tongi | 236 | 15:00 | 230 | 23:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 133 | 07:00 | 129 | 22:00 | Lalbag | 135 | 04:00 | 130 | 23:00
| Agargaon | 135 | 04:00 | 130 | 23:00 | Lalmonirhat | 128 | 15:00 | 115 | 12:00
| Agrabad | 128 | 17:00 | 124 | 00:00 | Madanganj | 138 | 06:00 | 134 | 23:00
| AKS | 126 | 17:00 | 123 | 00:00 | Madaripur | 135 | 06:00 | 128 | 22:00
| Aminbazar | 139 | 04:00 | 134 | 21:00 | Madartek | 133 | 06:00 | 129 | 18:30
| Amnura | 131 | 04:00 | 121 | 23:00 | Madunaghat | 129 | 17:00 | 125 | 00:00
| Ashuganj | 140 | 00:00 | 139 | 23:00 | Magura | 136 | 03:00 | 124 | 21:00
| Bagerhat | 133 | 07:00 | 121 | 21:00 | Mahasthangarh | 134 | 05:00 | 124 | 12:00
| Bakulia | 128 | 17:00 | 124 | 13:00 | Manikganj | 139 | 06:00 | 129 | 01:00
| Banani | 135 | 04:00 | 132 | 00:00 | Maniknagar | 135 | 05:00 | 131 | 22:00
| Bangabhaban | 134 | 01:00 | 131 | 22:00 | Matarbari | 114 | 09:00 | 107 | 00:00
| Barapukuria | 136 | 03:00 | 125 | 12:00 | Matuail | 139 | 02:00 | 135 | 23:00
| Barguna | 133 | 07:00 | 123 | 23:00 | Millgate | 136 | 01:00 | 133 | 23:00
| Barishal | 138 | 08:00 | 119 | 23:00 | Mirpur | 138 | 05:00 | 134 | 00:00
| Barishal-230 | 138 | 04:00 | 131 | 22:00 | Mirzapur | 133 | 02:00 | 126 | 13:00
| Baroaulia | 128 | 08:00 | 124 | 06:00 | Mithapukur | 133 | 04:00 | 118 | 12:00
| Baroirhat | 128 | 17:00 | 118 | 00:00 | MI_Cement | 138 | 05:00 | 134 | 23:00
| Bashundhara | 137 | 06:00 | 132 | 00:00 | Modern | 128 | 17:00 | 125 | 00:00
| BashundharaCement | 138 | 06:00 | 134 | 23:00 | Mogbazar | 134 | 03:00 | 131 | 01:00
| Beanibazar | 129 | 06:00 | 126 | 00:00 | Mongla | 134 | 06:00 | 121 | 21:00
| Benapole | 134 | 05:00 | 120 | 19:00 | Motijheel | 134 | 01:00 | 131 | 22:00
| Bhaluka | 131 | 05:00 | 124 | 12:00 | Munshiganj | 138 | 05:00 | 134 | 22:00
| Bhandaria | 135 | 09:00 | 116 | 22:00 | Mymensingh | 131 | 18:00 | 120 | 13:00
| Bhangura | 136 | 05:00 | 131 | 19:00 | Naogaon | 131 | 03:00 | 121 | 12:00
| Bheramara | 136 | 04:00 | 128 | 19:00 | Narail | 136 | 05:00 | 121 | 19:30
| Bheramara(GK) | 134 | 06:00 | 127 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 130 | 05:00 | 126 | 21:00 | Narshingdi | 135 | 05:00 | 129 | 22:00
| Bog-Sherpur | 135 | 04:00 | 126 | 12:00 | Natore | 133 | 04:00 | 124 | 19:30
| Bogura | 136 | 04:00 | 127 | 12:00 | Nawabganj | 134 | 06:00 | 129 | 23:00
| Bogura-230 | 136 | 04:00 | 128 | 12:00 | Netrakona | 130 | 12:00 | 117 | 13:00
| Brahmanbaria | 130 | 07:00 | 125 | 00:00 | New | 137 | 03:00 | 134 | 12:00
| Cantonment | 135 | 05:00 | 130 | 23:00 | Niamatpur | 132 | 03:00 | 126 | 12:00
| Chandpur | 128 | 19:00 | 114 | 01:00 | Noapara | 136 | 06:00 | 123 | 21:00
| Chandraghona | 130 | 18:00 | 125 | 00:00 | Pabna | 136 | 04:00 | 128 | 19:00
| Chapai | 130 | 03:00 | 124 | 12:00 | Palashbari | 130 | 02:00 | 117 | 12:00
| Charsaidpur | 139 | 06:00 | 135 | 22:00 | Panchagarh | 132 | 23:00 | 109 | 12:00
| Chauddagram | 129 | 18:00 | 120 | 00:00 | Patuakhali | 134 | 08:00 | 125 | 23:00
| Chhatak | 130 | 07:00 | 126 | 23:00 | Payra | 136 | 05:00 | 132 | 22:00
| Chowmuhani | 123 | 18:00 | 110 | 01:00 | PHP | 127 | 18:00 | 117 | 00:00
| Chuadanga | 133 | 05:00 | 115 | 22:00 | Postogola | 138 | 05:00 | 135 | 00:00
| Coxsbazar | 115 | 17:00 | 108 | 00:00 | Purbachal | 138 | 07:00 | 132 | 00:00
| Cumilla(N) | 133 | 15:00 | 128 | 00:00 | Purbasadipur | 127 | 03:00 | 108 | 12:00
| Cumilla(S) | 133 | 18:00 | 125 | 00:00 | Rahanpur | 133 | 04:00 | 128 | 12:00
| Daudkandi | 132 | 06:00 | 125 | 22:00 | Rahim | 139 | 01:00 | 136 | 23:00
| Dhaka | 135 | 05:00 | 132 | 00:00 | Rajbari | 135 | 06:00 | 126 | 21:00
| Dhamrai | 135 | 04:00 | 130 | 23:00 | Rajendrapur | 134 | 04:00 | 130 | 00:00
| Dhanmondi | 140 | 06:00 | 136 | 20:00 | Rajshahi | 131 | 05:00 | 123 | 12:00
| Dohazari | 127 | 18:00 | 121 | 22:00 | Rajshahi-230 | 132 | 05:00 | 122 | 12:00
| Faridpur | 135 | 05:00 | 126 | 22:00 | Ramganj | 124 | 18:00 | 108 | 01:00
| Fatullah | 138 | 04:00 | 135 | 22:00 | Rampur | 127 | 06:00 | 124 | 00:00
| Fenchuganj | 134 | 08:00 | 131 | 01:00 | Rampura | 135 | 04:00 | 129 | 21:00
| Feni | 126 | 19:30 | 116 | 00:00 | Rangamati | 128 | 16:00 | 124 | 00:00
| Ghorashal | 142 | 01:00 | 138 | 23:00 | Rangpur | 131 | 04:00 | 116 | 12:00
| Goalpara | 138 | 04:00 | 125 | 20:00 | Ruppur | 136 | 03:00 | 130 | 11:00
| Gollamari | 138 | 06:00 | 127 | 21:00 | Saidpur | 131 | 05:00 | 116 | 12:00
| Gopalganj | 135 | 04:00 | 126 | 22:00 | Satkhira | 135 | 05:00 | 120 | 21:00
| Gopalganj-400 | 136 | 06:00 | 129 | 22:00 | Satmasjid | 134 | 04:00 | 130 | 23:00
| Gulshan | 135 | 05:00 | 131 | 18:30 | Savar | 137 | 05:00 | 133 | 00:00
| Halishahar | 129 | 18:00 | 124 | 00:00 | SevenRings | 142 | 04:00 | 139 | 18:30
| Haripur | 139 | 01:00 | 136 | 22:00 | ShahCement | 139 | 06:00 | 135 | 22:00
| HaripurSBU | 139 | 01:00 | 136 | 23:00 | Shahjadpur | 140 | 03:00 | 135 | 18:30
| Hasnabad | 138 | 06:00 | 135 | 23:00 | Shahjibazar | 129 | 05:00 | 125 | 23:00
| Hathazari | 131 | 02:00 | 127 | 12:00 | Shahmirpur | 129 | 17:00 | 124 | 00:00
| Ishurdi | 139 | 04:00 | 130 | 19:30 | Shariatpur | 134 | 06:00 | 126 | 22:00
| Jaldhaka | 130 | 04:00 | 116 | 11:00 | Sherpur | 124 | 04:00 | 110 | 09:00
| Jamalpur | 128 | 18:00 | 116 | 09:00 | Shikalbaha | 118 | 17:00 | 113 | 13:00
| Jashore | 135 | 06:00 | 121 | 19:30 | Shikalbaha-230 | 129 | 17:00 | 125 | 13:00
| Jhenaidah | 135 | 06:00 | 126 | 19:00 | Shitalakhya | 138 | 05:00 | 134 | 23:00
| Jhenaidah-230 | 138 | 04:00 | 126 | 19:30 | Sholosohor | 129 | 18:00 | 124 | 13:00
| Joydebpur | 139 | 04:00 | 135 | 12:00 | Shyampur | 138 | 06:00 | 135 | 22:00
| Joypurhat | 130 | 04:00 | 119 | 12:00 | Shyampur-230 | 140 | 18:00 | 134 | 21:00
| Juldah | 126 | 02:00 | 125 | 00:00 | Siddhirganj | 139 | 05:00 | 136 | 22:00
| Kabirpur | 136 | 18:00 | 131 | 12:00 | Sirajganj | 134 | 03:00 | 127 | 19:00
| Kachua | 130 | 19:00 | 117 | 06:00 | Sonargaon | 137 | 09:00 | 132 | 22:00
| Kaliakoir | 139 | 04:00 | 133 | 13:00 | Sreemongol | 130 | 18:00 | 126 | 00:00
| Kallyanpur | 135 | 05:00 | 130 | 23:00 | Sreepur | 133 | 06:00 | 127 | 23:00
| Kalurghat | 130 | 18:00 | 125 | 01:00 | Srinagar | 134 | 04:00 | 129 | 23:00
| Kamrangirchar | 134 | 04:00 | 130 | 21:00 | SSM | 130 | 01:00 | 128 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 129 | 07:00 | 125 | 20:00
| Kazla | 134 | 04:00 | 131 | 21:00 | Sylhet | 131 | 06:00 | 129 | 03:00
| Keranigonj | 134 | 03:00 | 130 | 23:00 | Sylhet-132 | 131 | 00:00 | 130 | 11:00
| Khagrachori | 128 | 18:00 | 123 | 01:00 | Tangail | 131 | 03:00 | 122 | 13:00
| Khulna | 137 | 04:00 | 124 | 21:00 | Thakurgaon | 130 | 23:00 | 106 | 12:00
| Khulna(S) | 139 | 06:00 | 128 | 21:00 | TK | 129 | 19:00 | 125 | 00:00
| Khulshi | 128 | 18:00 | 123 | 00:00 | Tongi | 139 | 05:00 | 135 | 00:00
| Kishoreganj | 134 | 05:00 | 127 | 12:00 | Ullahpara | 135 | 17:00 | 130 | 19:00
| Kodda | 139 | 05:00 | 130 | 00:00 | Ullon | 135 | 03:00 | 129 | 22:00
| KSRM | 129 | 18:00 | 125 | 00:00 | Uttara | 139 | 05:00 | 134 | 23:00
| Kulaura | 132 | 00:00 | 130 | 23:00 | UttaraNew | 138 | 03:00 | 132 | 23:00
| Kurigram | 130 | 03:00 | 111 | 12:00 | Zigatola | 135 | 06:00 | 124 | 18:00
| Kushtia | 136 | 02:00 | 126 | 19:30

## L-Curve
Date | 2024-04-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 230 | 7533 | 4116 | 11649 |  |  |  | QF-LDC-11
0:30 | 325 | 7090.5 | 3817 | 10907.5 | Date: | 2024-04-12
1:00 | 420 | 6648 | 3518 | 10166
1:30 | 420 | 6485 | 3483 | 9968
2:00 | 420 | 6322 | 3448 | 9770
2:30 | 425 | 6214.5 | 3411 | 9625.5 | [5 empty] | Gen. at Eve. Peak | 11762 | 11762 MW (21:00 )
3:00 | 430 | 6107 | 3374 | 9481 | [6 empty] | 21:00
3:30 | 420 | 5992.5 | 3360.5 | 9353 | [5 empty] | Gen. at Day Peak | 9637 | 9637 MW (12:00 )
4:00 | 410 | 5878 | 3347 | 9225 | [6 empty] | 12:00
4:30 | 385 | 5896.5 | 3222 | 9118.5 | [5 empty] | Highest Generation | 11987
5:00 | 360 | 5915 | 3097 | 9012 | [6 empty] | 22:00
5:30 | 345 | 5803 | 3035 | 8838
6:00 | 330 | 5691 | 2973 | 8664
6:30 | 240 | 5718 | 3002 | 8720
7:00 | 150 | 5745 | 3031 | 8776
7:30 | 150 | 5770 | 3077 | 8847
8:00 | 150 | 5795 | 3123 | 8918
8:30 | 215 | 5760 | 3190.5 | 8950.5
9:00 | 280 | 5725 | 3258 | 8983
9:30 | 290 | 5784 | 3281.5 | 9065.5
10:00 | 300 | 5843 | 3305 | 9148
10:30 | 290 | 5880 | 3334 | 9214
11:00 | 280 | 5917 | 3363 | 9280
11:30 | 265 | 6073 | 3385.5 | 9458.5
12:00 | 250 | 6229 | 3408 | 9637
12:30 | 233 | 6633.5 | 3557.5 | 10191
13:00 | 216 | 7038 | 3707 | 10745
13:30 | 214 | 6931 | 3672 | 10603
14:00 | 212 | 6824 | 3637 | 10461
14:30 | 209 | 6850 | 3588.5 | 10438.5
15:00 | 206 | 6876 | 3540 | 10416
15:30 | 203 | 6735.5 | 3444 | 10179.5
16:00 | 200 | 6595 | 3348 | 9943
16:30 | 164 | 6597.5 | 3207.5 | 9805
17:00 | 128 | 6600 | 3067 | 9667
17:30 | 174 | 6388 | 3190.5 | 9578.5
18:00 | 220 | 6176 | 3314 | 9490
18:30 | 150 | 6954.5 | 3515.5 | 10470
19:00 | 80 | 7733 | 3717 | 11450
19:30 | 70 | 7832 | 3838 | 11670
20:00 | 50 | 7817 | 3751 | 11568 |  |  |  | Executive Engineer
20:30 | 40 | 7947 | 3718 | 11665 |  |  |  | Network Operation Division
21:00 | 30 | 8077 | 3685 | 11762
21:30 | 100 | 7975.5 | 3899 | 11874.5
22:00 | 170 | 7874 | 4113 | 11987 |  |  |  |  | Page 6 of 7
22:30 | 215 | 7701.5 | 4189.5 | 11891
23:00 | 260 | 7529 | 4266 | 11795
23:30 | 245 | 7531 | 4191 | 11722
24:00 | 230 | 7533 | 4116 | 11649
11762 MW (21:00 )
9637 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-04-12 |  | Energy |  | 245860777
[15 empty] | 2024-04-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3567 | 778 | 2812 | 0 | 750 | 3423 | 30 | 0 | 171 | 100 | 0 | 18 | 0
0:30 | 3864 | 849 | 2436 | 0 | 567 | 2940 | 15 | 0 | 127 | 97 | 0 | 12.5 | 0 |  |  | Date: | 43932
1:00 | 4161 | 920 | 2060 | 0 | 384 | 2457 | 0 | 0 | 83 | 94 | 0 | 7 | 0
1:30 | 4103.5 | 920 | 1984 | 0 | 338 | 2438.5 | 0 | 0 | 83 | 93 | 0 | 8 | 0 | [9 empty] | Total Energy | 245.8608 | 245.8608 | Total Energy Gen 245.861 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 245.861 MKWHr
2:00 | 4046 | 920 | 1908 | 0 | 292 | 2420 | 0 | 0 | 83 | 92 | 0 | 9 | 0 | [9 empty] | Energy not Served | 0 | 0
2:30 | 3984.5 | 919.5 | 1832.5 | 0 | 284 | 2421 | 0 | 0 | 83 | 91 | 0 | 10 | 0 | [9 empty] | Energy Requirement | 245.8608 | 245.8608
3:00 | 3923 | 919 | 1757 | 0 | 276 | 2422 | 0 | 0 | 83 | 90 | 0 | 11 | 0
3:30 | 3891.5 | 919.5 | 1709.5 | 0 | 245.5 | 2420.5 | 0 | 0 | 66 | 88 | 0 | 12.5 | 0 | [8 empty] | Shortage
4:00 | 3860 | 920 | 1662 | 0 | 215 | 2419 | 0 | 0 | 49 | 86 | 0 | 14 | 0
4:30 | 3872.5 | 778 | 1685.5 | 0 | 216.5 | 2419 | 0 | 0 | 49 | 86 | 0 | 12 | 0
5:00 | 3885 | 636 | 1709 | 0 | 218 | 2419 | 0 | 0 | 49 | 86 | 0 | 10 | 0
5:30 | 3839.5 | 635.5 | 1666.5 | 0 | 172 | 2399.5 | 0 | 0 | 28.5 | 83 | 3 | 10.5 | 0
6:00 | 3794 | 635 | 1624 | 0 | 126 | 2380 | 0 | 0 | 8 | 80 | 6 | 11 | 0
6:30 | 3834.5 | 635.5 | 1599.5 | 0 | 134.5 | 2380.5 | 0 | 0 | 8 | 77 | 41.5 | 9 | 0 | [7 empty] | Coal
7:00 | 3875 | 636 | 1575 | 0 | 143 | 2381 | 0 | 0 | 8 | 74 | 77 | 7 | 0
7:30 | 3873.5 | 635.5 | 1574.5 | 0 | 162.5 | 2381 | 0 | 0 | 8 | 70 | 138.5 | 3.5 | 0 | [6 empty] | Oil
8:00 | 3872 | 635 | 1574 | 0 | 182 | 2381 | 0 | 0 | 8 | 66 | 200 | 0 | 0
8:30 | 3810 | 635 | 1621.5 | 0 | 183 | 2381.5 | 0 | 0 | 8 | 66 | 245.5 | 0 | 0
9:00 | 3748 | 635 | 1669 | 0 | 184 | 2382 | 0 | 0 | 8 | 66 | 291 | 0 | 0
9:30 | 3742 | 635.5 | 1694.5 | 0 | 192 | 2381.5 | 0 | 0 | 8 | 66 | 346 | 0 | 0
10:00 | 3736 | 636 | 1720 | 0 | 200 | 2381 | 0 | 0 | 8 | 66 | 401 | 0 | 0
10:30 | 3737 | 635.5 | 1770.5 | 0 | 200.5 | 2360.5 | 0 | 0 | 8 | 67 | 435 | 0 | 0
11:00 | 3738 | 635 | 1821 | 0 | 201 | 2340 | 0 | 0 | 8 | 68 | 469 | 0 | 0
11:30 | 3842 | 635.5 | 1875 | 0 | 212 | 2340 | 0 | 0 | 8 | 70 | 476 | 0 | 0
12:00 | 3946 | 636 | 1929 | 0 | 223 | 2340 | 0 | 0 | 8 | 72 | 483 | 0 | 0
12:30 | 4070.5 | 636 | 2169 | 0 | 298.5 | 2462 | 15 | 0 | 8 | 76 | 456 | 0 | 0
13:00 | 4195 | 636 | 2409 | 0 | 374 | 2584 | 30 | 0 | 8 | 80 | 429 | 0 | 0
13:30 | 4195 | 636 | 2409 | 0 | 374 | 2584 | 30 | 0 | 8 | 80 | 429 | 0 | 0
14:00 | 4195 | 636 | 2409 | 0 | 374 | 2584 | 30 | 0 | 8 | 80 | 429 | 0 | 0
14:30 | 4069 | 636 | 2338 | 0 | 446 | 2588.5 | 30 | 0 | 35.5 | 79 | 356.5 | 2 | 0
15:00 | 3943 | 636 | 2267 | 0 | 518 | 2593 | 30 | 0 | 63 | 78 | 284 | 4 | 0
15:30 | 3911 | 636 | 2201 | 0 | 483 | 2550.5 | 30 | 0 | 62.5 | 80 | 221 | 4.5 | 0
16:00 | 3879 | 636 | 2135 | 0 | 448 | 2508 | 30 | 0 | 62 | 82 | 158 | 5 | 0
16:30 | 3917 | 635.5 | 2047 | 0 | 445.5 | 2458 | 30 | 0 | 74.5 | 81 | 110.5 | 6 | 0
17:00 | 3955 | 635 | 1959 | 0 | 443 | 2408 | 30 | 0 | 87 | 80 | 63 | 7 | 0
17:30 | 3804.5 | 777.5 | 1892.5 | 0 | 490.5 | 2373.5 | 30 | 0 | 91 | 79 | 35 | 5 | 0
18:00 | 3654 | 920 | 1826 | 0 | 538 | 2339 | 30 | 0 | 95 | 78 | 7 | 3 | 0
18:30 | 3909 | 920 | 2277 | 0 | 643.5 | 2475.5 | 30 | 0 | 121.5 | 85 | 3.5 | 5 | 0
19:00 | 4164 | 920 | 2728 | 0 | 749 | 2612 | 30 | 0 | 148 | 92 | 0 | 7 | 0
19:30 | 4089 | 877 | 2689 | 0 | 954 | 2776 | 30 | 0 | 155 | 90 | 0 | 10 | 0
20:00 | 4040 | 778 | 2794 | 0 | 951 | 2719 | 30 | 0 | 155 | 94 | 0 | 7 | 0
20:30 | 4037 | 777.5 | 2934.5 | 0 | 913.5 | 2723.5 | 30 | 0 | 147 | 95 | 0 | 7 | 0
21:00 | 4034 | 777 | 3075 | 0 | 876 | 2728 | 30 | 0 | 139 | 96 | 0 | 7 | 0
21:30 | 3854 | 777 | 3102 | 0 | 874 | 2985 | 30 | 0 | 147 | 98 | 0 | 7.5 | 0
22:00 | 3674 | 777 | 3129 | 0 | 872 | 3242 | 30 | 0 | 155 | 100 | 0 | 8 | 0
22:30 | 3615 | 777.5 | 2975.5 | 0 | 843 | 3368.5 | 30 | 0 | 171 | 100 | 0 | 10.5 | 0
23:00 | 3556 | 778 | 2822 | 0 | 814 | 3495 | 30 | 0 | 187 | 100 | 0 | 13 | 0
23:30 | 3561.5 | 778 | 2817 | 0 | 782 | 3459 | 30 | 0 | 179 | 100 | 0 | 15.5 | 0 |  |  | Max Temp. in Dhaka |  | 36.9°C
24:00 | 3567 | 778 | 2812 | 0 | 750 | 3423 | 30 | 0 | 171 | 100 | 0 | 18 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 245.861 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 245.861 MKWHr
Note on W13: Author:

## Generation
2024-04-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [12 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 336000
3 | Chattogram TPP-1 | 121 | 118 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 122 | 122 |  | 123 | 120 | 120 | 122 | 123 | 121 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 7 | 12 | 13 | 15 | 8 | 7 | 10 | 12 | 4 | 2 | 1 | [8 empty] | 100170
6 | Sikalbaha 225MW CCPP (Gas) | 212 | 213 | 213 | 213 | 212 | 212 | 212 | 212 | 212 | 213 | 213 | 214 | 213 | 213 | 213 | 211 | 211 | 184 |  | 208 | 214 | 214 | 213 | 213 | 213 | 213 | 4939080
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | [8 empty] | 17 | 33 | 32 | 32 | 32 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 637046
12 | Hathazari 100 MW peaking PP | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 38 | 30 | 30 | 55 | 63 |  | 65 | 72 | 72 | 72 | 72 | 72 | 56 | 818592
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [20 empty] | 8 | 16 |  |  |  |  | 20072
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 78 | 80 | 80 | 77 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 122 | 200 | 75 | 76 | 77 | 76 | 78 |  | 117 | 122 | 120 | 201 | 203 | 200 | 211 | 2809000
17 | Siddhirganj 335 MW CCPP | 309 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 300 | 311 | 280 | 280 | 280 | 280 | 240 |  | 316 | 290 | 290 | 315 | 320 | 330 | 327 | 6815530
18 | Kodda 300 MW PP Unit-2 (Summit) | [26 empty] | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 73 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 120 | 120 | 120 | 120 | 120 | 83 |  | 157 | 157 | 185 | 185 | 185 | 185 | 184 | 1873454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 170 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 200 | 200 | 200 | 130 | 130 | 130 |  | 220 | 220 | 220 | 220 | 200 | 220 | 220 | 3830125
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4362750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 379 | 377 | 376 | 376 | 377 | 379 | 378 | 378 | 380 | 380 | 340 | 340 | 417 | 419 | 420 | 401 | 370 | 307 |  | 332 | 372 | 373 | 420 | 449 | 450 | 443 | 9223635
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 23 | 28 | 31 | 31 | 30 | 10 |  | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 436824
33 | Ashuganj 225 MW CCPP | 190 | 196 | 190 | 190 | 195 | 190 | 150 | 152 | 191 | 189 | 195 | 210 | 184 | 183 | 183 | 195 | 189 | 143 |  | 216 | 217 | 215 | 219 | 218 | 218 | 221 | 4645000
34 | Ashuganj 450 MW CCPP(South) | 270 | 275 | 270 | 270 | 275 | 270 | 295 | 285 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 240 |  | 240 | 240 | 240 | 240 | 250 | 250 | 250 | 6156000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 285 | 280 | 305 | 335 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7196700
| Ashuganj 420 MW CCPP(East) | 285 | 285 | 286 | 286 | 285 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 350 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 6184000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 20 | 20 | 18 | 10 | 10 |  | 17 | 40 | 40 | 40 | 40 | 32 | 23 | 334560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 331 | 331 | 328 | 301 | 300 | 292 | 281 | 282 | 282 | 282 | 283 | 303 | 331 | 317 | 317 | 318 | 310 | 303 |  | 320 | 312 | 312 | 312 | 312 | 313 | 319 | 7509600
| Meghnaghat Unique power | [10 empty] | 84 | 83 | 283 | 282 | 284 | 140 | 142 | 110 |  | 278 | 284 | 292 | 370 | 370 | 368 | 367 | 3270909
| Summit Meghanghat-2 589 MW(Gas) | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 500 | 430 | 430 | 585 | 590 | 592 | 595 | 5986818
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 350 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 360 | 420 | 370 | 370 | 370 | 330 | 300 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9093000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 200 | 200 | 200 | 201 | 200 | 204 | 204 | 201 | 198 | 197 | 193 | 192 | 193 | 191 | 192 | 188 | 191 | 193 |  | 198 | 198 | 197 | 199 | 198 | 202 | 202 | 4619520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 10 | 20 | 33 | 42 | 48 | 47 | 29 | 37 | 24 | 16 | 5 | 1 | [8 empty] | 312910
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 942000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 |  | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 678600
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 63 | 63 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 47 | 50 | 60 | 40 | 40 | 40 |  | 40 | 40 | 40 | 63 | 62 | 58 | 57 | 1204320
48 | Shahjibazar 86 MW PP (Shahjibazar)
| Shahjibazar 100 MW GTPP |  | 50 | 10 | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 75 | 75 | 75 | 20 |  | 80 | 50 | [5 empty] | 585455
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 206 | 206 | 207 | 206 | 209 | 210 | 211 | 211 | 204 | 205 | 202 | 198 | 200 | 204 | 201 | 201 | 201 | 201 |  | 202 | 204 | 206 | 205 | 206 | 207 | 209 | 5125170
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 385000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 47 | 50 | 52 | 10 | 10 | 10 |  | 47 | 50 | 49 | 50 | 50 | 50 | 50 | 529200
56 | Shahjahanulla 25 MW PP | 24 | [12 empty] | 8 | 8 | 8 | 8 | 8 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 212064
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 295 | 280 | 290 | 290 | 240 | 240 | 240 | 290 | 300 | 310 | 300 | 270 | 275 | 270 | 280 | 290 |  | 285 | 270 | 280 | 295 | 230 |  |  | 6325830
| Bibiyana South 400 MW | 345 | 345 | 300 | 300 | 300 | 300 | 322 | 317 | 300 | 300 | 300 | 340 | 340 | 305 | 305 | 317 | 305 | 305 |  | 340 | 341 | 342 | 212 | 116 |  |  | 6911100
58 | Nababganj 55 MW PP (Southern power )
59 | Tangail Palli Power Gen 22 MW | [13 empty] | 6 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 255600
60 | Barabkunda 22 MW PP (Regent) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 107184
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 94 | 92 | 90 | 86 | 86 | 80 | 74 | 66 | 66 | 66 | 68 | 72 | 80 | 78 | 78 | 82 | 80 | 78 |  | 92 | 90 | 94 | 96 | 100 | 100 | 100 | 1993920
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 |  | 37 | 37 | 38 | 38 | 39 | 42 | 42 | 977280
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 225180
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 |  |  | 31 | 33 | 33 | 33 | 33 | 25 |  | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 670500
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 392720
69 | Summit Ashulia | 12 | 12 | 10 | 10 | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 15 | 15 |  | 15 | 15 | 15 | 14 | 13 | 13 | 15 | 360000
70 | Summit Madhabdi | 7 | 7 | 7 | 7 | 7 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 7 | 7 | 7 | 12 | 12 | 12 | 155520
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 390800
72 | Rupganj 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 194300
73 | Ghorashal 108 MW PP (Regent) | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 30 | 32 | 32 | 32 | 32 | 60 | 76 | 485090
| Feni Lanka Power | 88 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 57 | 70 | 70 | 70 | 52 | 52 |  | 103 | 114 | 88 | 70 | 73 | 70 | 114 | 1248300
| Chowmuhani 113 MW |  | 12 | 27 | 29 | 29 | [5 empty] | 5 | 13 | 28 | 28 | 29 | 28 | 28 | 28 |  | 42 | 48 | 48 | 48 | 48 | 48 | 39 | 581280
| Manikgonj 162MW PP(MPGL) | [26 empty] | 0
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150 MW PP | [19 empty] | 32 | 32 | 32 | 16 | 32 | 64 | 64 | 178560
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 52 | 52 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 44 | 51 | 25 | 25 | 25 |  | 26 | 52 | 46 | 25 | 25 | 25 | 25 | 682416
| Gazipur 100 MW PP | [26 empty] | 0
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 1 | 2 | 2 | 2 | 5 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 23160
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [19 empty] | 6 | 17 | 17 | 17 | 17 | 17 |  | 91614
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 309 | 306 | 305 | 250 | 252 | 252 | 253 | 252 | 270 | 275 | 282 | 310 | 280 | 270 | 268 | 295 | 295 | 245 |  | 250 | 256 | 278 | 298 | 303 | 298 | 285 | 6665484
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 10 | 10 | 10 |  | 25 | 25 | 25 | 25 | 47 | 47 | 47 | 451872
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 16 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 641872
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | [16 empty] | 6 | 6 | 6 |  |  |  |  | 28320
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [26 empty] | 0
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 2205491
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 0 | [9 empty] | 13750
103 | Kamalaghat 54 MW PP(Banco Energy)
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 58 | 58 | 58 | 45 | 48 | 48 | 57 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 58 | 104 |  | 105 | 106 | 107 | 107 | 97 | 58 | 58 | 1550400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [19 empty] | 10 | 35 | 31 | 34 | 37 | 72 | 65 | 264240
115 | Juldah 100 MW PP Unit-3 (Acorn) | [26 empty] | 0
116 | Chandpur 200 MW (Desh energy) | 93 | 55 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 36 | 51 | 51 | 56 | 85 | 85 | 85 |  | 100 | 155 | 155 | 155 | 155 | 155 | 155 | 1665120
117 | Ashuganj 150 MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 366 | 320 | 318 | 318 | 322 | 318 | 348 | 332 | 317 | 324 | 351 | 378 | 368 | 307 | 307 | 315 | 315 | 315 |  | 316 | 315 | 315 | 294 | 20 |  |  | 7070000
| Jamalpur 115 MW PP (United) | 50 | 28 | 18 |  |  |  | 8 | 47 | 48 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 97 |  | 98 | 99 | 99 | 99 | 99 | 49 | 49 | 1160400
| Anwara 300 MW PP (United) | [19 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 90327
| Juldah unit-2 (Acorn) | 11 | 11 | 11 | 11 | 11 | [11 empty] | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 153600
| Anlima Energy Ltd. | [12 empty] | 1 | 12 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 186927
| Bhairob 54.5 MW | [9 empty] | 15 |  | 6 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 249480
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 12 | 19 | 26 | 28 | 31 | 24 | 20 | 22 | 13 | 5 | 0 | [8 empty] | 205890
| Chandpur 115(Doreen) | 35 | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 875520
| Kanchan Purbachal Power Generation Ltd. | [26 empty] | 0
| Mirsharai 150 MW (Oil) | [26 empty] | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 7 | 9 | 11 | 14 | 10 | 11 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 7 | 3 |  | 7 | 10 | 7 | 7 | 8 | 13 | 18 | 143520
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 11 | 32 | 32 | 66 | 72 | 76 | 70 | 64 | 34 | 29 | 6 | 1 | [8 empty] | 462091
| Matarbari 2*600 MW (CPGCL) | 376 | 377 | 376 | 372 | 376 | 375 | 376 | 375 | 376 | 375 | 375 | 372 | 373 | 374 | 374 | 375 | 376 | 373 |  | 426 | 434 | 428 | 428 | 581 | 576 | 573 | 9687272
120 | Eastern Zone Total | 6648 | 6322 | 6107 | 5878 | 5915 | 5691 | 5745 | 5795 | 5725 | 5843 | 5917 | 6229 | 7038 | 6824 | 6876 | 6595 | 6600 | 6176 |  | 7733 | 7832 | 7817 | 8077 | 7874 | 7529 | 7533 | 159995034
121
122
123 | Khulna 60MW
124 | manik
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [26 empty] | 0
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 15 | 37 | 53 | 68 | 89 | 92 | 84 | 78 | 70 | 20 | 13 | 1 | [8 empty] | 614880
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4910291
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 160 | 148 | 150 | 140 | 224 | 307 | 275 | 3709100
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 63 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 40 | 40 |  | 65 | 65 | 65 | 65 | 65 | 63 | 63 | 1503000
140 | Bhola 33 MW PP (Venture) | [12 empty] | 9 | 10 | 10 | 9 | 9 | 8 |  | 10 | 10 | 10 | 11 | 10 | 10 | 10 | 120156
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [26 empty] | 0
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 920 | 920 | 919 | 920 | 636 | 635 | 636 | 635 | 635 | 636 | 635 | 636 | 636 | 636 | 636 | 636 | 635 | 920 |  | 920 | 877 | 778 | 777 | 777 | 778 | 778 | 17326545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 580 | 540 | 540 | 540 | 540 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 570 | 600 | 590 | 560 | 500 | 500 |  | 560 | 660 | 600 | 620 | 840 | 970 | 990 | 16144300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 177 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4521900
153 | Baghabari 71 MW GTPP | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 1290000
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 2 | 1 | 0 | 0 | [8 empty] | 31440
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 178 | 169 | 145 | 143 | 145 | 143 | 154 | 168 | 164 | 151 | 159 | 175 | 190 | 151 | 149 | 147 | 149 | 156 |  | 166 | 147 | 150 | 150 | 160 | 152 | 144 | 4012173
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 373 | 348 | 335 | 310 | 345 | 260 | 260 | 260 | 337 | 337 | 337 | 350 | 375 | 315 | 305 | 350 | 250 | 250 |  | 291 | 297 | 334 | 313 | 400 | 305 | 300 | 7885236
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 144720
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [26 empty] | 0
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 14 | 35 | 35 | 35 | 35 | 35 | 35 | 202368
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 20 | 35 | 35 | 35 | 35 | 35 |  | 169440
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [12 empty] | 40 | 40 | 42 | 6 | 6 | 6 |  | 54 | 54 | 56 | 56 | 56 | 56 | 56 | 448473
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 2 | 3 | 4 | 5 | 7 | 6 | 6 | 5 | 4 | 2 | 0 | [8 empty] | 43789
178 | Energypac Power Venture Thakurgaon Ltd. | [12 empty] | 29 | 70 | 70 | 35 | 36 | 36 |  | 45 | 70 | 92 | 75 | 75 | 75 | 35 | 747456
| Intraco Solar 30 MW | [5 empty] | 0 | 3 | 11 | 18 | 22 | 29 | 32 | 30 | 25 | 19 | 13 | 7 | 1 | [8 empty] | 209664
| Adani Power Jharkhanda Ltd | 812 | 816 | 820 | 821 | 816 | 816 | 817 | 818 | 816 | 816 | 815 | 811 | 884 | 871 | 869 | 832 | 822 | 819 |  | 934 | 962 | 968 | 920 | 948 | 992 | 942 | 20585062
178 | Teesta Solar Limited | [5 empty] | 3 | 31 | 76 | 114 | 152 | 175 | 179 | 170 | 151 | 93 | 55 | 23 | 2 | [8 empty] | 1245750