## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:February 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-02-02 |  | 2024-01-01 |  | 2023-02-02
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 11433 | 2024-02-20 | 10717 | 2024-01-29 | 11708 | 2023-02-27 | 15648 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 6491 | 2024-02-26 | 4997 | 2024-01-08 | 6484 | 2023-02-04 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11433 | 2024-02-20 | 10717 | 2024-01-29 | 11708 | 2023-02-27 | 15648 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11433 | 2024-02-20 | 10109 | 2024-01-31 | 10493 | 2023-02-27 | 13415 | 2023-04-19
|  |  | 19:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 11600 | 2024-02-29 | 10717 | 2024-01-29 | 11795 | 2023-02-28 | 16096 | 2023-04-19
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 10621.7586 |  | 10054.129 |  | 10536.9643 |  | - | -
7 | Average Generation (MW) at Day Peak | 9975.931 |  | 9271.871 |  | 9326.8214 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 927 | 2024-02-29 | 935 | 2024-01-31 | 919 | 2023-02-28 | 956 | 27/3/2019
|  |  | 22:30 |  | 14:30 |  | 17:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 134 | 2024-02-14 | 124 | 2024-01-26 | 152 | 2023-02-23 | 194 | 12/06/19
|  |  | 14:00 |  | 13:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 166 | 2024-02-19 | 617 | 2024-01-20 | 470 | 2023-02-14 | 4395 | 04/10/2022
|  |  | 19:00 |  | 20:00 |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 11426 | 2024-02-19 | 9794 | 2024-01-20 | 10328 | 44971 | 13200 | 04/10/2022
|  | - | 19:00 | - | 20:00 |  | 0.79167 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-02-21 | 0 | 2024-01-19 | 0 | 44975 | - | -
|  |  | 19:00 |  | 19:00 |  | 19:30 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 9940 | 2024-02-21 | 9530 | 2024-01-19 | 10586 | 2023-02-18 | - | -
|  |  | 19:00 |  | 19:00 |  | 19:30 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 448 | 2024-02-06 | 732 | 2024-01-21 | 986 | 44969 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 9431 | 2024-02-06 | 9133 | 2024-01-21 | 8780 | 44969 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-02-21 | 0 | 2024-01-21 | 0 | 44974 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 9810 | 2024-02-21 | 9087 | 2024-01-21 | 8927 | 44974 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 19 |  | 2 |  | 23 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 20 |  | 13 |  | 25 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1547.5883 |  | 1567.6156 |  | 1366.7592 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 26.3507 |  | 35.6059 |  | 45.9327 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1521.2375 |  | 1532.0097 |  | 1320.8266 |  | - | -
23 | Net Generation of IPP (MKWH) | 3361.366 |  | 3270.8678 |  | 3589.391 |  | - | -
24 | Net Generation of REB (MKWH) | 89.9855 |  | 94.171 |  | 113.7895 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 118.5854 |  | 151.7108 |  | 225.4883 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5091.1744 |  | 5048.7594 |  | 5249.4954 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 3054.7436 |  | 2952.1447 |  | 3202.315 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 16.4698 |  | 12.5617 |  | 17.6361 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 508.5277 |  | 589.0162 |  | 1039.0523 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 28.5971 |  | 55.9314 |  | 22.8708 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 38.0423 |  | 29.1038 |  | 36.208 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 846.7537 |  | 699.1873 |  | 977.3458 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 586.2757 |  | 593.312 |  | 629.869 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 70.7431 |  | 75.2028 |  | 76.3661 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:February 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 11433 | 2024-02-20 | 19:00
Generation Period
| Dhaka | MW | 4220.77
| Chattogram | MW | 1035.5
| Cumilla | MW | 902
| Mymensingh | MW | 869
| Sylhet | MW | 376
a) | Total supply in East zone | MW | 7403.27
| Khulna | MW | 1295.6
| Barisal | MW | 296.1
| Rajshahi | MW | 1136.4
| Rangpur | MW | 754
b) | Total supply in West zone | MW | 3482.1
c) | Total supply in both zone ( a+b) | MW | 10885.37
Ref: | 27.21.0000.603.16.087.20.781 | Date: 20/03/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:February 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 650 | 2024-02-18 | 8:00
| b) Ishurdi end | MW | 316 | 2024-02-25 | 17:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1160 | 2024-02-13 | 13:00
| b) Ishurdi end | MW | 74 | 2024-02-27 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.60874
| b) Ishurdi end | MKWH | 106.3018
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 103.1128
| b) Ishurdi end | MKWH | 0.59101
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2024-02-02 | 8:00
| b)Serajganj end | MW | 630 | 2024-02-15 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 310 | 2024-02-16 | 0:00
| b)Sirajganj end | MW | 26 | 2024-02-02 | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.0302
| b)Sirajganj end | MKWH | 266.192
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 258.3723
| b)Sirajganj end | MKWH | 0.0028
30 | Transmission loss of EWI /NO-2 | % | 2.938'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 1934 | 2023-02-10 | 19:30
|  | MW | 1352
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 1910 | 2023-02-10 | 19:30
|  | MW | 1348
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 26484 | 2023-02-10 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 26452 | 2023-02-10
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 3556414
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 3558002.999
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.0066272
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-02-02 21:29 | 2024-02-02 22:47 | 1:18 | E/O | Red hot maintenance. | 15 | 19.5 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-02-12 16:34 | 2024-02-12 21:25 | 4:51 | E/O | Oil fallen from PRD. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-02-09 09:34 | 2024-02-09 10:09 | 0:35 | T | PBS three feeder fault | 43 | 25.0833 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-02-13 15:53 | 2024-02-13 16:31 | 0:38 | T | O/C fault Show in PBS(33 kv Vadgram Outgoing Feeder), Bird Drop this Feeder. | 22.5 | 14.25 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-02-22 09:40 | 2024-02-22 09:55 | 0:15 | T | for pbs 3nos feeder trip | 48 | 12 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-02-25 06:12 | 2024-02-25 06:33 | 0:21 | T | PBS 33 kV feeder fault | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-02-27 08:25 | 2024-02-27 08:41 | 0:16 | T | Due to pbs 4 feeder trip. | 47 | 12.5333 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-09 09:34 | 2024-02-09 10:29 | 0:55 | T | PBS three feeder trip at a time | 43 | 39.4167 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-13 15:53 | 2024-02-13 16:34 | 0:41 | T | O/C fault Show in PBS(33 kv Vadgram Outgoing Feeder), Bird Drop this Feeder. | 22.5 | 15.375 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-22 09:40 | 2024-02-22 09:57 | 0:17 | T | for pbs 3nos feeder trip | 48 | 13.6 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-23 12:09 | 2024-02-23 12:21 | 0:12 | T | 33 KV PBS OUTGOING FEEDER TRIP | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-24 21:00 | 2024-02-24 22:26 | 1:26 | E/O | PBS 33 kV feeder bus side loop Red hot remove purpose. | 15 | 21.5 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-25 06:12 | 2024-02-25 06:34 | 0:22 | T | PBS 33 kV feeder fault | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-02-27 08:25 | 2024-02-27 08:42 | 0:17 | T | due to pbs 4 feeder trip. | 47 | 13.3167 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-02-14 08:18 | 2024-02-14 10:04 | 1:46 | E/O | To perform high temperature mitigate works of 33kV Bha-1 feeder (B-Phase, Bus DS, Bus loop). | 15 | 26.5 | Power interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-1 LT | 2024-02-16 06:38 | 2024-02-16 08:18 | 1:40 | T | 81U-1 Underfrequency Prot trip | 28 | 46.6667 | Power interruption
Rajendrapur 132/33kV Grid Sub-Station | MTR-2 LT | 2024-02-16 06:38 | 2024-02-16 08:18 | 1:40 | T | 81U-1 Underfrequency Prot trip | 28 | 46.6667 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-02-08 11:42 | 2024-02-08 13:38 | 1:56 | E/O | 33KV T-02, PT Oil Leakage Remove | 0 | 0 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-02-11 12:28 | 2024-02-11 13:17 | 0:49 | E/O | S/D for TRTUD. | 0 | 0 | No interruption
|  |  | Total : | 20:15 |  | Unserved Energy: |  | 306.4083
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-02-29 12:39 | 2024-02-29 12:47 | 0:08 | T | overload | 80 | 10.6667 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Bus Coupler | 2024-02-07 15:52 | 2024-02-07 16:37 | 0:45 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Bus Coupler | 2024-02-25 15:08 | 2024-02-25 20:00 | 4:52 | T | None | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-1 | 2024-02-07 15:52 | 2024-02-07 16:37 | 0:45 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2024-02-07 15:52 | 2024-02-07 16:37 | 0:45 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2024-02-25 15:08 | 2024-02-25 16:02 | 0:54 | T |  | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-1 | 2024-02-07 15:52 | 2024-02-07 19:57 | 4:05 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-2 | 2024-02-25 15:08 | 2024-02-25 20:00 | 4:52 | T |  | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2024-02-07 15:52 | 2024-02-07 16:36 | 0:44 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2024-02-25 15:08 | 2024-02-25 15:41 | 0:33 | T |  | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-02-07 15:52 | 2024-02-07 16:42 | 0:50 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-02-15 09:18 | 2024-02-15 12:27 | 3:09 | E/O | Emergency High Temperature maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 HT | 2024-02-03 10:38 | 2024-02-03 15:30 | 4:52 | E/O | High Temperature Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 HT | 2024-02-25 15:08 | 2024-02-25 15:27 | 0:19 | T |  | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 LT | 2024-02-07 15:52 | 2024-02-07 16:53 | 1:01 | T | Reserve Bus Y Phase PT Burst | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-02-01 18:40 | 2024-02-01 18:57 | 0:17 | T | Unknown | 18 | 5.1 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-02-22 22:42 | 2024-02-22 23:29 | 0:47 | T | 33 kv Zinzira ckt-1, Zinzira ckt-2, Nababganj ckt-1 and Nababganj ckt-2 trip | 20 | 15.6667 | Power interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 LT | 2024-02-08 10:11 | 2024-02-08 14:22 | 4:11 | E/O | Due to red hot at 132kv side. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-2 HT | 2024-02-03 11:48 | 2024-02-03 13:38 | 1:50 | T |  | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Auxiliary Transformer-2 LT | 2024-02-23 00:04 | 2024-02-23 01:04 | 1:00 | T | Auxiliary Transformer -1 (Y&B) phase high loop disconnect for Flashing in bad weather. | 16 | 16 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-02-23 00:04 | 2024-02-23 11:44 | 11:40 | T | Auxiliary Transformer -1 (Y&B) phase high loop disconnect for Flashing in bad weather. | 16 | 186.6667 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2024-02-03 16:38 | 2024-02-03 20:32 | 3:54 | E/O | 132 KV T-2 TCS Relay fail signal work. Load flow continued by T-1 Transformer. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 LT | 2024-02-22 06:47 | 2024-02-22 07:10 | 0:23 | T | Due to Basundhara ckt.-01 Trip. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2024-02-20 12:56 | 2024-02-20 13:14 | 0:18 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 HT | 2024-02-20 12:57 | 2024-02-20 13:14 | 0:17 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 HT | 2024-02-25 15:15 | 2024-02-25 16:06 | 0:51 | T | BUS Trip Haripur end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-02-13 09:52 | 2024-02-22 16:48 | 222:56 | E/O | Maintenace work 132/33 KV Transformer oil centrifuge Maintained by EGCB. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-02-01 10:56 | 2024-02-01 16:37 | 5:41 | E/O | EGCB 132/11 KV Trsnsformer Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-02-20 12:46 | 2024-02-20 13:23 | 0:37 | T | Ullon -2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 1 | 2024-02-20 12:46 | 2024-02-20 13:11 | 0:25 | T | Ullon-2 fault | 132 | 55 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2024-02-20 12:46 | 2024-02-20 13:16 | 0:30 | T | Ullon-2 trip | 132 | 66 | Power interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 HT | 2024-02-20 12:46 | 2024-02-20 13:12 | 0:26 | T | TRIP | 140 | 60.6667 | Power interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2024-02-20 12:46 | 2024-02-20 13:12 | 0:26 | T | trip | 140 | 60.6667 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-02-07 15:54 | 2024-02-07 16:49 | 0:55 | T | Sonargaon grid power failure. | 50 | 45.8333 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-02-25 15:10 | 2024-02-25 16:00 | 0:50 | T | Grid power failure. | 42 | 35 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-02-07 15:54 | 2024-02-07 16:49 | 0:55 | T | Sonargaon grid power failure. | 41 | 37.5833 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-02-22 14:30 | 2024-02-22 15:06 | 0:36 | E/O | Corrective maintenance works | 40 | 24 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-02-22 18:16 | 2024-02-22 18:22 | 0:06 | T | 33 kv side feeder fault showing signals over current trip | 16 | 1.6 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-02-22 23:10 | 2024-02-23 00:04 | 0:54 | T | over current trip | 6 | 5.4 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-02-24 12:46 | 2024-02-24 13:08 | 0:22 | E/O | Auxiliary transformer fuse change | 30 | 11 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-02-25 15:10 | 2024-02-25 15:59 | 0:49 | T | Grid power failure. | 49 | 40.0167 | Power interruption
|  |  | Total : | 290:30 |  | Unserved Energy: |  | 676.8667
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-02-17 01:04 | 2024-02-17 01:48 | 0:44 | E/O | Redhot Maintenance at 33 KV BUS by BPDB Satkania | 38 | 27.8667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 LT | 2024-02-24 09:05 | 2024-02-24 12:35 | 3:30 | E/O | Shutdown taken by Satkania PDB for Isolator maintenance work | 30 | 105 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2024-02-22 14:27 | 2024-02-22 16:35 | 2:08 | E/O | secondary cable reconnect | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 HT | 2024-02-01 08:47 | 2024-02-01 09:32 | 0:45 | E/O | Y phase 33KV cable punctured. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2024-02-16 06:30 | 2024-02-16 08:37 | 2:07 | E/O |  | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | 33 KV BUS-1 | 2024-02-14 13:51 | 2024-02-14 14:52 | 1:01 | E/O | 33 KV Bus maintenance by S&D Kalurghat BPDB | 3 | 3.05 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | 33 KV BUS-2 | 2024-02-14 13:54 | 2024-02-14 14:53 | 0:59 | E/O | 33 KV Bus maintenance by S&D Kalurghat BPDB. | 3 | 2.95 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-02-13 12:15 | 2024-02-13 15:17 | 3:02 | E/O | For checking different joint | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2024-02-19 14:02 | 2024-02-19 16:40 | 2:38 | T | CT Blust of Mohora-02,33kV feeder of BPDB. | 12 | 31.6 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-02-03 06:16 | 2024-02-03 06:43 | 0:27 | T | REF-615=[General trip, 51/51N DMT, Y-Phase fault] ,RET-670=[33KV General trip] | 4 | 1.8 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-02-19 14:11 | 2024-02-19 15:13 | 1:02 | E/O | CT Blust of 33kV Mohora-02 feeder of BPDB. | 10 | 10.3333 | Power interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 LT | 2024-02-20 14:15 | 2024-02-20 15:55 | 1:40 | E/O | Nest Removing & making bird fench, 33kV Bus-1,taken by BPDB | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 LT | 2024-02-12 13:32 | 2024-02-12 14:04 | 0:32 | E/O | Bird nest removing by BPDB | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 LT | 2024-02-20 12:28 | 2024-02-20 15:06 | 2:38 | E/O | Nest removing & making bird fench ,33kv bus-2 , taken by BPDB | 0 | 0 | No interruption
|  |  | Total : | 23:13 |  | Unserved Energy: |  | 182.6
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-02-05 17:43 | 2024-02-05 17:55 | 0:12 | T | Earth Fault | 35 | 7 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-02-22 09:44 | 2024-02-22 09:51 | 0:07 | E/O | Bring down kite from Tr-03 132kv bus | 10 | 1.1667 | Power interruption
Chandpur 132/33kV Grid Sub-Station | Bus-B | 2024-02-08 08:38 | 2024-02-08 17:03 | 8:25 | E/O | Annual Maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-02-24 09:39 | 2024-02-24 14:30 | 4:51 | E/O | Due emergency maint.work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-02-06 19:09 | 2024-02-07 11:46 | 16:37 | E/O | 33kv cable spark. | 0 | 0 | No interruption
|  |  | Total : | 30:12 |  | Unserved Energy: |  | 8.1667
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2024-02-03 12:33 | 2024-02-03 13:38 | 1:05 | E/O | Oil sample collection | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-02-01 16:50 | 2024-02-01 19:38 | 2:48 | T | Due to 33 kv E/F. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-02-10 07:03 | 2024-02-10 17:55 | 10:52 | E/O | Due emergency maint.work | 20 | 217.3333 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2024-02-10 07:05 | 2024-02-10 09:54 | 2:49 | E/O | Due emergency maint.work | 25 | 70.4167 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2024-02-03 00:47 | 2024-02-03 01:33 | 0:46 | E/O | Bus section 1 PT fuse R&Y phase burn. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T HT | 2024-02-02 23:42 | 2024-02-03 00:24 | 0:42 | T | Bus section 1 PT fuse R&Y phase burn. | 22 | 15.4 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2024-02-08 14:33 | 2024-02-08 14:57 | 0:24 | T | Due to 33kv feeder fault | 10 | 4 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2024-02-22 22:57 | 2024-02-22 23:05 | 0:08 | T | For 33kv feeder | 10 | 1.3333 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-02-04 14:36 | 2024-02-04 15:05 | 0:29 | E/O | OLTC Oil sample collection | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-02-08 09:14 | 2024-02-08 09:30 | 0:16 | T | SCADA OPERATION BY NLDC | 18 | 4.8 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-02-16 06:44 | 2024-02-16 08:38 | 1:54 | T | SCADA operation by NLDC | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-02-20 12:48 | 2024-02-20 13:21 | 0:33 | T | None | 17 | 9.35 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-02-08 09:14 | 2024-02-08 09:30 | 0:16 | T | SCADA OPERATION BY NLDC | 18 | 4.8 | Power interruption
|  |  | Total : | 23:02 |  | Unserved Energy: |  | 327.4333
HVDC Grid Circle :
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2024-02-17 02:32 | 2024-02-17 11:45 | 9:13 | T | trip | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2024-02-17 20:28 | 2024-02-18 17:43 | 21:15 | T | Trip | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2024-02-10 11:48 | 2024-02-10 11:48 | 0:00 | T | Buchholz trip main tank | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2024-02-15 20:37 | 2024-02-15 22:01 | 1:24 | E/O | T1 33 kv source side CT R-Phase clamp Red hot Minimize. | 30 | 42 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-02-10 11:48 | 2024-02-10 11:48 | 0:00 | T | Inter trip from 132 kv FDR | 66 | 0 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-02-10 12:00 | 2024-02-10 21:54 | 9:54 | E/O | Due emergency maint.work | 40 | 396 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-02-11 09:37 | 2024-02-11 14:34 | 4:57 | E/O | Due emergency maint.work | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-02-12 11:40 | 2024-02-12 13:39 | 1:59 | E/O | Due emergency maint.work | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-1 (405T) HT | 2024-02-24 10:15 | 2024-02-24 12:13 | 1:58 | E/O | Oil leakage of radiator of 132kV (T1) | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer -1 HT | 2024-02-09 11:22 | 2024-02-09 12:19 | 0:57 | E/O | SF6 GAS leakage maintenance. | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer-2 LT | 2024-02-01 15:59 | 2024-02-01 18:11 | 2:12 | E/O | SPBS-1 Cable connected with Bus-2 | 0 | 0 | No interruption
|  |  | Total : | 53:49 |  | Unserved Energy: |  | 438
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T HT | 2024-02-15 06:24 | 2024-02-15 07:23 | 0:59 | E/O | Gas pressure low. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T LT | 2024-02-15 03:08 | 2024-02-15 03:08 | 0:00 | T | Gas pressure low in 33 KV CB of TR -3. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-02-12 16:26 | 2024-02-12 17:15 | 0:49 | E/O | Oil Leakage of OLTC | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-02-20 08:22 | 2024-02-20 12:32 | 4:10 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2024-02-03 03:20 | 2024-02-03 03:39 | 0:19 | T | Over Voltage V>> Phase AB V>> Phase AB-174.5kV Vt>Phase Relay Display V AB-174.5kV V BC-132.6kV V CA-150.0kV | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 426T LT | 2024-02-25 05:19 | 2024-02-25 05:32 | 0:13 | T | Rajshahi -2 Feeder fault . | 15 | 3.25 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-02-22 07:18 | 2024-02-22 07:38 | 0:20 | E/O | Due to heavy Thundering And Raining, Instruction given by SS Incharge | 20 | 6.6667 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-02-22 07:14 | 2024-02-22 07:58 | 0:44 | T | Due to Faulty Banessor Feeder, LT is been Tripped | 25 | 18.3333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2024-02-28 08:30 | 2024-02-28 09:06 | 0:36 | E/O | RED HOT bolt replaces at bahirgola feeder outgoing DS. | 0 | 0 | No interruption
|  |  | Total : | 8:10 |  | Unserved Energy: |  | 28.25
Others :
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan HT | 2024-02-23 11:54 | 2024-02-23 12:45 | 0:51 | T |  | 0 | 0 | No interruption
|  |  | Total : | 0:51 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 450:02 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-02-21 06:43 | 2024-02-21 07:05 | 0:22 | T | None | 144 | 52.8 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-02-21 04:57 | 2024-02-21 04:57 | 0:00 | T | None | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-02-21 07:59 | 2024-02-21 17:45 | 9:46 | E/O | Tower no-2 & 3 Insulator Disc Cleaning. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Agargaon-01 | 2024-02-20 05:39 | 2024-02-20 17:05 | 11:26 | E/O | Distance Trip, Differential trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Agargaon-02 | 2024-02-20 05:55 | 2024-02-20 06:16 | 0:21 | E/O | Distance trip,Differential trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-20 05:13 | 2024-02-20 19:43 | 14:30 | E/O | Distance Relay, Zone-1 | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-21 04:13 | 2024-02-21 18:33 | 14:20 | T | None | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-23 | 2024-02-23 01:35 | 1:35 | T | None | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-20 05:13 | 2024-02-20 17:51 | 12:38 | E/O | Distance trip,Zone -1 | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-21 04:13 | 2024-02-21 18:36 | 14:23 | T | General Trip 67N Trip | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-23 00:06 | 2024-02-23 01:44 | 1:38 | T | General Trip 67N Trip | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2024-02-18 05:49 | 2024-02-18 06:39 | 0:50 | T | General Trip 67N Trip | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Summit 149 MW PS | 2024-02-20 16:15 | 2024-02-20 16:27 | 0:12 | E/O | Straw removal | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-02-16 17:27 | 2024-02-16 20:24 | 2:57 | E/O | Hydraulic oil leakage repairing works. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-02-26 17:49 | 2024-02-26 18:34 | 0:45 | T | Definitive trip | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2024-02-05 16:03 | 2024-02-05 16:34 | 0:31 | T | 33KV Bus PT Blast at Ghatail S/S End. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2024-02-05 16:03 | 2024-02-05 16:18 | 0:15 | T | 33KV Bus PT Blast at Ghatail S/S End. | 282 | 70.5 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-02-21 15:58 | 2024-02-21 15:58 | 0:00 | T | None | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-02-21 16:00 | 2024-02-21 16:00 | 0:00 | E/O | Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-02-21 16:01 | 2024-02-21 17:09 | 1:08 | E/O | Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2024-02-22 11:05 | 2024-02-22 11:15 | 0:10 | T | None | 72 | 12 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-02-24 16:05 | 2024-02-24 16:39 | 0:34 | E/O | Removing dish wire from line. | 50 | 28.3333 | Power interruption
|  |  | Total : | 88:21 |  | Unserved Energy: |  | 163.6333
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Rampura-04 | 2024-02-22 16:37 | 2024-02-22 17:27 | 0:50 | T |  | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-02-21 06:41 | 2024-02-21 07:04 | 0:23 | T | Directional OC protection trip | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-02-21 05:00 | 2024-02-21 05:22 | 0:22 | T |  | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2024-02-06 20:23 | 2024-02-06 20:23 | 0:00 | T |  | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2024-02-06 21:40 | 2024-02-14 11:14 | 181:34 | E/O | Gulshan-Rampura Circuit - 2 Trip. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-1 | 2024-02-21 04:44 | 2024-02-21 06:10 | 1:26 | T | Trip. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-02-23 14:30 | 2024-02-23 16:33 | 2:03 | E/O | Another Side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2024-02-20 12:45 | 2024-02-20 13:34 | 0:49 | T | Trip | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-02-20 12:45 | 2024-02-20 12:45 | 0:00 | T | Trip. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-02-20 15:05 | 2024-02-23 17:31 | 74:26 | E/O | Trip and Shuttdown by NLDC. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-16 11:04 | 2024-02-16 14:40 | 3:36 | T | Distance Relay operated | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-02-20 07:04 | 2024-02-20 07:20 | 0:16 | T | Distance zone 1 trip R Phase (8.10km). | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-02-07 15:56 | 2024-02-07 16:48 | 0:52 | T |  | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-02-25 15:10 | 2024-02-25 16:01 | 0:51 | T | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-02-26 02:32 | 2024-02-26 10:42 | 8:10 | E/O | Ordered by NLDC to decrease the bus voltage | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-02-07 15:56 | 2024-02-07 16:59 | 1:03 | T | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-02-21 04:44 | 2024-02-21 05:26 | 0:42 | T |  | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-02-25 15:10 | 2024-02-25 16:01 | 0:51 | T | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-02-02 23:58 | 2024-02-03 10:56 | 10:58 | E/O | Ordered by NLDC | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-02-02 23:58 | 2024-02-03 23:59 | 24:01 | E/O | Ordered by NLDC | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Mero Rail - 1 | 2024-02-18 01:02 | 2024-02-18 01:02 | 0:00 | T |  | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-02-20 06:33 | 2024-02-20 07:02 | 0:29 | T |  | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-02-19 12:25 | 2024-02-19 12:37 | 0:12 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-02-22 06:47 | 2024-02-22 07:07 | 0:20 | T |  | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2024-02-05 18:31 | 2024-02-05 18:34 | 0:03 | T | Unknown. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2024-02-06 20:23 | 2024-02-06 20:23 | 0:00 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2024-02-22 16:34 | 2024-02-22 18:51 | 2:17 | T | Unknown | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-02-02 07:31 | 2024-02-02 16:20 | 8:49 | E/O |  | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Shyampur old-2(E10) | 2024-02-12 09:18 | 2024-02-12 12:54 | 3:36 | E/O | Maintenance of Shyampur Old end. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-02-03 01:28 | 2024-02-03 01:28 | 0:00 | T | Unknown | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-02-03 02:09 | 2024-02-03 02:09 | 0:00 | E/O | Emergency occurance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-02-20 05:32 | 2024-02-20 06:25 | 0:53 | T | Unknown | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-02-20 06:34 | 2024-02-20 10:17 | 3:43 | T | Unknown | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-02-23 07:15 | 2024-02-23 11:00 | 3:45 | E/O | Insulatator disc change. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Hasnabad-1(D02) | 2024-02-03 03:24 | 2024-02-03 15:22 | 11:58 | E/O | Emergency Occurance | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-1(D06) | 2024-02-21 12:48 | 2024-02-21 15:28 | 2:40 | E/O | Insulator disc cleaning and changing. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-1(D06) | 2024-02-23 16:36 | 2024-02-23 18:41 | 2:05 | E/O | Maintenance of Meghnaghat End | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2024-02-13 08:55 | 2024-02-13 22:45 | 13:50 | E/O | Maintenance of Meghnaghat ckt-2 End | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2024-02-21 09:20 | 2024-02-21 12:28 | 3:08 | E/O | Insulator disc cleaning and changing. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2024-02-21 15:53 | 2024-02-21 17:47 | 1:54 | E/O | Insulator disc changing Tower-22. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2024-02-23 19:06 | 2024-02-23 21:02 | 1:56 | E/O | Maintenance of Meghnaghat End | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-02-02 08:12 | 2024-02-02 09:36 | 1:24 | T | General trip | 65 | 91 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-02-20 13:05 | 2024-02-20 13:43 | 0:38 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 210MW PDB L3 | 2024-02-20 13:03 | 2024-02-20 13:38 | 0:35 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-02-07 15:52 | 2024-02-07 16:50 | 0:58 | T | ZONE 2 FAULT (PT BRUST HARIPUR SS) | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-02-20 12:46 | 2024-02-20 13:42 | 0:56 | T | Ullon-2 fault | 36 | 33.6 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-02-25 15:08 | 2024-02-25 16:06 | 0:58 | T | Z-2 ,Distance relay trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-02-07 15:52 | 2024-02-07 20:00 | 4:08 | T | ZONE 2 TRIP (PT brust Haripur side) | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-02-20 13:07 | 2024-02-20 13:42 | 0:35 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-02-03 00:57 | 2024-02-03 01:11 | 0:14 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-02-20 13:03 | 2024-02-20 13:16 | 0:13 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2024-02-20 13:04 | 2024-02-20 16:35 | 3:31 | E/O | Ullon-2 fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 2 | 2024-02-20 12:59 | 2024-02-20 12:59 | 0:00 | E/O | Line DS, Post insulator are broking, R,Y,B -phase loop (Conductor) disconnect | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-02-07 15:54 | 2024-02-07 16:58 | 1:04 | T | Over voltage trip. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-02-22 23:12 | 2024-02-23 21:12 | 22:00 | T | 87 T/87trip ( differential Trip) Transformer | 6 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-02-07 15:54 | 2024-02-07 16:46 | 0:52 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-02-25 15:10 | 2024-02-25 15:55 | 0:45 | T | trip. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-2 | 2024-02-25 15:10 | 2024-02-25 15:56 | 0:46 | T | trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-02-12 14:43 | 2024-02-12 14:55 | 0:12 | T | Trip | 16 | 3.2 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-02-12 15:47 | 2024-02-12 18:32 | 2:45 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-02-14 12:17 | 2024-02-14 12:33 | 0:16 | T | Line distance | 16 | 4.2667 | Power interruption
|  |  | Total : | 417:41 |  | Unserved Energy: |  | 132.0667
Chattogram Grid Circle :
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2024-02-26 08:55 | 2024-02-26 17:11 | 8:16 | E/O | Dohazari side. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2024-02-25 08:32 | 2024-02-25 09:40 | 1:08 | T | trip. | 57 | 64.6 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 2024-02-25 08:32 | 2024-02-25 08:43 | 0:11 | T | trip. | 47 | 8.6167 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2024-02-19 14:16 | 2024-02-19 15:25 | 1:09 | E/O | Fire in 33 kV switchyard near this feeder. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-02-17 18:48 | 2024-02-18 00:35 | 5:47 | T | trip. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-02-19 14:14 | 2024-02-19 15:24 | 1:10 | E/O | Fire in 33kV Switchyard near this feeder. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-02-23 06:23 | 2024-02-23 09:58 | 3:35 | E/O | Shut down taken by Nldc | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2024-02-17 18:49 | 2024-02-17 19:36 | 0:47 | T | General trip Zone-1/Zcom trip R -PH trip | 0 | 0 | No interruption
|  |  | Total : | 22:03 |  | Unserved Energy: |  | 73.2167
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-02-02 06:18 | 2024-02-02 06:49 | 0:31 | T | Earth Fault | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-02-18 05:48 | 2024-02-18 06:44 | 0:56 | T | SOTF, Zcom tripped. | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibiyana-South (Back feed) | 2024-02-15 22:17 | 2024-02-25 14:02 | 231:45 | E/O | Emergency maint. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-02-11 08:42 | 2024-02-11 15:07 | 6:25 | E/O | Emergency maint. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-02-18 13:45 | 2024-02-18 14:16 | 0:31 | T | trip. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-02-17 12:08 | 2024-02-17 18:08 | 6:00 | E/O | 132 kV Red Phase CT Top Side Oil Leakage, | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-02-22 09:10 | 2024-02-22 18:55 | 9:45 | E/O | 132kV CT-Y-Ph Maintenance work for Oil Leakage | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-02-14 09:16 | 2024-02-14 13:03 | 3:47 | E/O | Emergency maint. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-02-23 01:08 | 2024-02-23 01:23 | 0:15 | T | Stormy Wether | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-02-23 13:15 | 2024-02-23 13:32 | 0:17 | T | Chatak end ea trip | 26 | 7.3667 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-02-23 13:13 | 2024-02-23 13:32 | 0:19 | T | Chatak end ea trip | 26 | 8.2333 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-02-23 13:15 | 2024-02-23 13:42 | 0:27 | T | Chatak end ea trip | 0 | 0 | No interruption
|  |  | Total : | 260:58 |  | Unserved Energy: |  | 15.6
Khulna Grid Circle :
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2024-02-09 15:30 | 2024-02-09 19:14 | 3:44 | T | Unknown | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2024-02-09 19:20 | 2024-02-09 19:28 | 0:08 | T | trip. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2024-02-09 19:29 | 2024-02-12 17:09 | 69:40 | T | trip. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2024-02-15 05:33 | 2024-02-16 19:44 | 38:11 | E/O | LA Blast of Y-Phase at 50MW Power Station end (LA Replaced Now) | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2024-02-10 06:48 | 2024-02-10 09:57 | 3:09 | E/O | Main bus red hot maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2024-02-10 06:49 | 2024-02-10 12:04 | 5:15 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-02-10 06:45 | 2024-02-10 13:18 | 6:33 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-02-25 23:57 | 2024-02-26 15:08 | 15:11 | T | PT Blast. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Modhumoti 100MW PS | 2024-02-10 06:46 | 2024-02-10 10:12 | 3:26 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2024-02-16 06:38 | 2024-02-16 08:40 | 2:02 | T | Over voltage | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2024-02-16 06:38 | 2024-02-16 08:40 | 2:02 | T | Over Voltage | 0 | 0 | No interruption
|  |  | Total : | 149:21 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara 230/132kV Grid Sub-Station | STG (NW) | 2024-02-03 13:01 | 2024-02-03 15:47 | 2:46 | T | Inter tripping command received from NWPGCL | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV HVDC 3 | 2024-02-15 10:05 | 2024-02-15 12:28 | 2:23 | T | NO PERFECT REASON FOUND | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Bheramara-2 | 2024-02-11 13:14 | 2024-02-11 13:49 | 0:35 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 5:44 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura 132/33kV Grid Sub-Station | Mahasthangarh-2 | 2024-02-07 08:56 | 2024-02-07 16:45 | 7:49 | E/O | S/D. | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Rangpur-Kurigram Ckt-01 | 2024-02-05 08:23 | 2024-02-05 08:42 | 0:19 | T | trip. | 35 | 11.0833 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari-1 | 2024-02-15 11:21 | 2024-02-15 11:50 | 0:29 | T | R-Phase & Y-Phase are O/C & E/F Air Block | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-02-17 19:29 | 2024-02-24 06:20 | 154:51 | E/O | In order to XEN-NLDC. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-02-24 17:09 | 2024-02-25 15:54 | 22:45 | E/O | Due to emergency maint.work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-02-25 17:17 | 2024-02-25 17:17 | 0:00 | E/O | In order of NLDC executive engineer sir. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-2 | 2024-02-29 14:36 | 2024-02-29 22:43 | 8:07 | T | LA Blast of Red phase | 0 | 0 | No interruption
|  |  | Total : | 194:20 |  | Unserved Energy: |  | 11.0833
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1138:28 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) LT | 2024-02-15 07:35 | 2024-02-15 13:21 | 5:46 | S/O | Annual Maintenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2024-02-11 07:29 | 2024-02-11 16:02 | 8:33 | S/O | Annual Maintenanace. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) LT | 2024-02-18 07:33 | 2024-02-18 16:28 | 8:55 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Auxiliary Tr-2 LT | 2024-02-18 07:32 | 2024-02-18 16:39 | 9:07 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-02-28 15:51 | 2024-02-28 20:21 | 4:30 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-02-29 08:20 | 2024-02-29 08:20 | 0:00 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-02-28 12:11 | 2024-02-28 15:01 | 2:50 | S/O | Jack bus change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2024-02-29 07:48 | 2024-02-29 17:58 | 10:10 | S/O | Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 HT | 2024-02-28 12:22 | 2024-02-28 20:17 | 7:55 | S/O | Maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132 kv Busbar-2 | 2024-02-05 07:02 | 2024-02-05 16:25 | 9:23 | S/O | OAT-11(132kv side) Bay upgradation work. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132kv Busbar-1 | 2024-02-06 08:09 | 2024-02-06 16:22 | 8:13 | S/O | OAT-11(132kv side) Bay upgradation work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus Section- 01 | 2024-02-03 07:34 | 2024-02-03 15:55 | 8:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus Section- 02 | 2024-02-03 07:34 | 2024-02-03 12:32 | 4:58 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-02-03 07:38 | 2024-02-03 16:12 | 8:34 | S/O | 33kv Bus Annual Maintenance | 80 | 685.3333 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-02-03 07:38 | 2024-02-03 12:32 | 4:54 | S/O | 33kv Bus Annual Maintenance | 80 | 392 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-02-23 08:42 | 2024-02-23 09:35 | 0:53 | D/W | New T4 transformer road crossing. | 30 | 26.5 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | 132kV Bus | 2024-02-01 07:58 | 2024-02-01 14:42 | 6:44 | S/O | Annual Maintenance | 10 | 67.3333 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-02-05 12:03 | 2024-02-05 12:41 | 0:38 | S/O | Oil filling at main tank. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-02-17 10:01 | 2024-02-17 13:21 | 3:20 | S/O | conservator tank maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2024-02-23 08:43 | 2024-02-25 13:19 | 52:36 | S/O | 132 kv GT-3 Transformer painting | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-4 HT | 2024-02-24 09:40 | 2024-02-24 16:32 | 6:52 | S/O | Gas leakage maintenance at 33 kV GIS Bus. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 132 kV Bus-1 | 2024-02-24 07:33 | 2024-02-24 09:24 | 1:51 | S/O | 132 kv DS-161S maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 230kV Bus 2 | 2024-02-16 12:06 | 2024-02-16 17:08 | 5:02 | S/O | due to 400/230 kv Tr HT LA Change | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 1 | 2024-02-11 09:21 | 2024-02-11 15:50 | 6:29 | D/W | Project Work. | 0 | 0 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 2 | 2024-02-13 09:53 | 2024-02-13 17:00 | 7:07 | S/O | Due to Bay extension work by Rooppur Project. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2024-02-18 09:00 | 2024-02-18 17:10 | 8:10 | S/O | Annual Maintenance of main bus Isolator. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2024-02-25 09:43 | 2024-02-25 13:34 | 3:51 | S/O | annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2024-02-29 09:38 | 2024-02-29 16:51 | 7:13 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2024-02-25 13:42 | 2024-02-25 16:16 | 2:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Main bus | 2024-02-06 09:25 | 2024-02-06 17:24 | 7:59 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Main bus | 2024-02-13 09:34 | 2024-02-13 18:01 | 8:27 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Main bus | 2024-02-17 09:41 | 2024-02-17 15:48 | 6:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Main bus | 2024-02-18 08:55 | 2024-02-18 17:04 | 8:09 | S/O | Annual Maintenance of main bus Isolator. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Main bus | 2024-02-25 09:37 | 2024-02-25 16:04 | 6:27 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Reserve bus | 2024-02-11 09:28 | 2024-02-11 14:59 | 5:31 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Reserve bus | 2024-02-28 09:25 | 2024-02-28 16:17 | 6:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Reserve bus | 2024-02-29 09:35 | 2024-02-29 16:43 | 7:08 | S/O | annul maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2024-02-10 08:38 | 2024-02-10 13:00 | 4:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2024-02-10 08:39 | 2024-02-10 13:55 | 5:16 | S/O | Annual maintenance | 38 | 200.1333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-02-04 08:10 | 2024-02-04 15:45 | 7:35 | D/W | Project work. | 25 | 189.5833 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-02-06 09:20 | 2024-02-07 17:20 | 32:00 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-02-08 07:14 | 2024-02-08 16:48 | 9:34 | D/W | Project Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-02-09 08:05 | 2024-02-09 16:48 | 8:43 | D/W | Project work. | 12 | 104.6 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-02-10 06:36 | 2024-02-10 15:21 | 8:45 | D/W | Project work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2024-02-03 08:16 | 2024-02-03 16:55 | 8:39 | D/W | Project work | 6 | 51.9 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2024-02-05 08:22 | 2024-02-05 16:50 | 8:28 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2024-02-11 07:13 | 2024-02-11 16:08 | 8:55 | D/W | Project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-03 08:33 | 2024-02-03 16:28 | 7:55 | D/W | Project work | 6 | 47.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-04 08:10 | 2024-02-04 16:35 | 8:25 | D/W | Project work. | 25 | 210.4167 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-05 08:41 | 2024-02-05 16:50 | 8:09 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-07 07:31 | 2024-02-07 17:15 | 9:44 | D/W | Project work. | 25 | 243.3333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-08 07:32 | 2024-02-08 16:48 | 9:16 | D/W | Project Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-09 08:05 | 2024-02-09 16:47 | 8:42 | D/W | Project work. | 12 | 104.4 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-10 06:37 | 2024-02-10 15:05 | 8:28 | D/W | Project work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-02-11 07:15 | 2024-02-11 17:40 | 10:25 | D/W | Project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-02-04 08:10 | 2024-02-04 16:35 | 8:25 | D/W | Project work. | 25 | 210.4167 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-02-07 07:31 | 2024-02-07 17:16 | 9:45 | D/W | Project work. | 25 | 243.75 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-02-08 07:33 | 2024-02-08 16:49 | 9:16 | D/W | Project Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-02-09 08:05 | 2024-02-09 16:46 | 8:41 | D/W | Project work. | 12 | 104.2 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-02-10 06:38 | 2024-02-10 15:06 | 8:28 | D/W | Project work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-02-03 08:33 | 2024-02-03 16:33 | 8:00 | D/W | Project work | 6 | 48 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-02-05 08:43 | 2024-02-05 16:50 | 8:07 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-02-11 07:15 | 2024-02-11 17:44 | 10:29 | D/W | Project work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-02-17 10:10 | 2024-02-17 21:09 | 10:59 | S/O | Uttara old ckt with Main Bus DS Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-02-04 10:12 | 2024-02-04 13:50 | 3:38 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T3 LT | 2024-02-13 07:45 | 2024-02-13 18:19 | 10:34 | S/O | T-3, Annual maintenance work . | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Auxiliary Transformer-2 LT | 2024-02-03 09:25 | 2024-02-03 12:06 | 2:41 | S/O | annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-02-01 10:39 | 2024-02-01 16:33 | 5:54 | S/O | Auxiliary Tr-1 oil change & annual maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-02-15 10:00 | 2024-02-15 14:14 | 4:14 | S/O | Red hot maintenace | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-02-03 09:39 | 2024-02-03 11:56 | 2:17 | S/O | annual maintenance of 33/0.4kV Auxiliary Transformer | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-02-06 07:20 | 2024-02-06 11:08 | 3:48 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-02-27 15:35 | 2024-02-27 16:40 | 1:05 | S/O | Kite removing | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-02-19 16:03 | 2024-02-19 16:28 | 0:25 | S/O | kite removing from 132kV T-3 PT | 50 | 20.8333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-02-15 13:06 | 2024-02-15 16:56 | 3:50 | S/O | relay cheeking by SPMD. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2024-02-29 19:48 | 2024-02-29 19:48 | 0:00 | D/W | Differential trip- not restored. So this Event Shifted to Project work Shutdown on 19 February, 2024 at 16:22 | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230 kV BUS-2 | 2024-02-10 11:49 | 2024-02-10 18:18 | 6:29 | D/W | 230kv Bus-2 related DS Maintenance. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230 kV Bus-1 | 2024-02-07 11:35 | 2024-02-07 16:22 | 4:47 | D/W | All Bus-1 DS Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 HT | 2024-02-10 09:59 | 2024-02-10 19:24 | 9:25 | D/W | Due to SAS Integration. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 LT | 2024-02-08 10:03 | 2024-02-08 18:05 | 8:02 | S/O | Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-02-11 09:56 | 2024-02-11 17:48 | 7:52 | D/W | Operation for SAS Integration. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-02-12 10:17 | 2024-02-12 16:52 | 6:35 | D/W | SAS Integration by Siemens | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 1 HT | 2024-02-10 09:59 | 2024-02-10 19:24 | 9:25 | D/W | Due to SAS Integration. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 1 LT | 2024-02-08 09:57 | 2024-02-08 18:08 | 8:11 | S/O | Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 2 HT | 2024-02-11 09:56 | 2024-02-11 17:49 | 7:53 | D/W | Operation for SAS Integration. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Auxiliary Transformer - 2 HT | 2024-02-12 10:17 | 2024-02-12 17:42 | 7:25 | D/W | SAS Integration by Siemens | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2024-02-02 07:11 | 2024-02-02 17:11 | 10:00 | D/W | Project work S/D | 0 | 0 | No interruption
|  |  | Total : | 652:10 |  | Unserved Energy: |  | 2950.2333
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2024-02-09 09:05 | 2024-02-09 14:10 | 5:05 | S/O | Annual Maintenance | 40 | 203.3333 | Power interruption
Bhulta 400/230kV Grid Sub-Station | ATR-02 HT | 2024-02-05 09:22 | 2024-02-05 16:47 | 7:25 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-02 LT | 2024-02-03 09:16 | 2024-02-03 16:10 | 6:54 | S/O | Due to Annual Maintenance Works. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | ATR-02 LT | 2024-02-04 09:09 | 2024-02-04 17:01 | 7:52 | S/O | Annual Maintenance work | 0 | 0 | No interruption
Charsaidpur 132/33kV Sub-Station | 132/33 kV GT-2 HT | 2024-02-20 14:38 | 2024-02-20 16:20 | 1:42 | D/W | Gd meter installation | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | MT-1 LT | 2024-02-18 12:34 | 2024-02-18 16:36 | 4:02 | S/O | relay test by spmd | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-1 | 2024-02-12 12:20 | 2024-02-12 14:37 | 2:17 | S/O | 132 Sonargaon-1 Main Bus Isolator Y-phase to Main Busbar loop changing work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-1 | 2024-02-09 11:39 | 2024-02-09 17:09 | 5:30 | S/O | !132 KV Rahim Still Reserve Bus Bar Isolator finger changing work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-1 | 2024-02-11 09:21 | 2024-02-11 13:26 | 4:05 | S/O | Reserve Bus Y phase PT Change. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-02-25 08:21 | 2024-02-25 19:51 | 11:30 | S/O | Loop and Clamp Changing work. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 HT | 2024-02-08 15:02 | 2024-02-08 16:43 | 1:41 | S/O | red hot | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 HT | 2024-02-12 09:25 | 2024-02-12 13:42 | 4:17 | S/O | Oil Leakage | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | Bus-1 | 2024-02-15 07:10 | 2024-02-16 06:44 | 23:34 | S/O | To do maintenance & renovation work at 132KV bus coupler isolator. | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | Bus-1 | 2024-02-24 10:55 | 2024-02-24 20:05 | 9:10 | S/O |  | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | Bus-2 | 2024-02-16 06:38 | 2024-02-16 15:43 | 9:05 | S/O | To do maintenance & renovation work at 132KV bus coupler isolator and GT3 isolator. | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | GT-2 HT | 2024-02-28 09:40 | 2024-02-28 09:40 | 0:00 | D/W | GtoG project work | 6 | 0 | Power interruption
Kamrangirchar 132/33kV Grid Sub-Station | GT-2 LT | 2024-02-28 09:35 | 2024-02-28 09:35 | 0:00 | D/W | GtoG project work. | 6 | 0 | Power interruption
Kamrangirchar 132/33kV Grid Sub-Station | GT-3 HT | 2024-02-15 07:18 | 2024-02-15 17:55 | 10:37 | S/O | To do maintenance & renovation work at 132KV bus coupler isolator. | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | GT-3 HT | 2024-02-16 06:38 | 2024-02-16 15:06 | 8:28 | S/O | To do maintenance & renovation work at 132KV bus coupler isolator and GT3 isolator. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 HT | 2024-02-04 08:26 | 2024-02-04 15:36 | 7:10 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 HT | 2024-02-06 07:34 | 2024-02-06 15:50 | 8:16 | S/O | Annual MAintenance work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Earthing Trafo-1 HT | 2024-02-04 08:23 | 2024-02-04 15:44 | 7:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-02-03 08:29 | 2024-02-03 18:26 | 9:57 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) LT | 2024-02-02 08:19 | 2024-02-02 17:52 | 9:33 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) HT | 2024-02-12 07:39 | 2024-02-20 17:30 | 201:51 | S/O | Oill lekage rimove of transformer-2 | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus1 | 2024-02-22 11:22 | 2024-02-24 00:44 | 37:22 | S/O | Busbar protection panel replacement work done by spmd. Bus section CT Replacement | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus2 | 2024-02-16 12:20 | 2024-02-21 16:16 | 123:56 | S/O | Busbar protection panel replacement work done by spmd. Bus section CT Replacement | 0 | 0 | No interruption
Postogola 132/33kV Grid Sub-Station | GT-1 LT | 2024-02-22 10:42 | 2024-02-22 14:51 | 4:09 | D/W | Shutdown is taken for changing GD meter of CB | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-1 | 2024-02-03 18:45 | 2024-02-03 21:28 | 2:43 | S/O | S/D after G2G Tx-4 project work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2024-02-03 08:46 | 2024-02-03 16:07 | 7:21 | D/W | Project work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2024-02-04 09:50 | 2024-02-04 22:59 | 13:09 | D/W | G To G project Work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-02-03 08:45 | 2024-02-03 17:46 | 9:01 | D/W | Project work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-02-10 08:39 | 2024-02-10 17:22 | 8:43 | D/W |  | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-02-06 10:39 | 2024-02-06 17:23 | 6:44 | D/W | For G to G project work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-02-12 09:27 | 2024-02-12 09:27 | 0:00 | S/O | TX-3 replacement work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Aux Transformer-02 HT | 2024-02-03 08:45 | 2024-02-03 17:46 | 9:01 | D/W | Project work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Aux Transformer-03 LT | 2024-02-12 09:27 | 2024-02-12 09:27 | 0:00 | S/O | TX-3 replacement work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo HT | 2024-02-06 10:39 | 2024-02-06 17:55 | 7:16 | D/W | For G to G project work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132/33 kV GT-3 HT | 2024-02-02 09:43 | 2024-02-02 15:02 | 5:19 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 602:06 |  | Unserved Energy: |  | 203.3333
Chattogram Grid Circle :
Chandraghona 132/33kV Grid Sub-Station | MAIN BUS-2 | 2024-02-01 09:33 | 2024-02-01 14:49 | 5:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2024-02-05 09:12 | 2024-02-05 14:48 | 5:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | TR-02(416T) LT | 2024-02-06 09:09 | 2024-02-06 14:16 | 5:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 HT | 2024-02-28 14:16 | 2024-02-28 15:53 | 1:37 | S/O | Annual maintenance | 20 | 32.3333 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2024-02-26 09:54 | 2024-02-26 13:04 | 3:10 | S/O | General Inspection and Tightness Checking | 0 | 0 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer-01(D05) HT | 2024-02-25 12:44 | 2024-02-25 15:10 | 2:26 | S/O | General Inspection and Tightness Checking | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | 132KV MAIN BUS-02 | 2024-02-23 06:30 | 2024-02-23 09:15 | 2:45 | S/O | Annual maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 HT | 2024-02-16 11:30 | 2024-02-19 15:50 | 76:20 | S/O | Oil centrifusing | 0 | 0 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-03 HT | 2024-02-05 07:20 | 2024-02-05 17:04 | 9:44 | D/W | Soil Test | 0 | 0 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-03 HT | 2024-02-06 07:03 | 2024-02-06 16:03 | 9:00 | D/W | Soil Test | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2024-02-01 06:00 | 2024-02-07 13:33 | 151:33 | D/W | Project work | 0 | 0 | Power interruption
Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2024-02-12 06:15 | 2024-02-12 07:06 | 0:51 | D/W | project work | 20 | 17 | Power interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2024-02-01 06:30 | 2024-02-01 09:35 | 3:05 | D/W | Project work | 24 | 74 | Power interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2024-02-07 06:25 | 2024-02-07 09:27 | 3:02 | S/O | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T LT | 2024-02-12 06:00 | 2024-02-12 16:55 | 10:55 | D/W | project work | 20 | 218.3333 | Power interruption
KSRM 132/33kV Grid Sub-Station | Transformer-01 LT | 2024-02-03 08:34 | 2024-02-03 17:30 | 8:56 | S/O | 33kV Bus-1 Yellow phase Conductor Change. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2024-02-27 12:58 | 2024-02-27 21:28 | 8:30 | D/W |  | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2024-02-28 09:25 | 2024-02-28 16:28 | 7:03 | D/W |  | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2024-02-27 09:00 | 2024-02-27 12:45 | 3:45 | D/W |  | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) HT | 2024-02-03 07:05 | 2024-02-03 11:47 | 4:42 | S/O | 33kV Breaker (Y Phase ) pole Change. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2024-02-18 15:45 | 2024-02-18 17:42 | 1:57 | S/O | For redhot and bus isolator maintenance work of BPDB 33kv mohora ckt-2 feeder. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) HT | 2024-02-29 13:34 | 2024-02-29 13:34 | 0:00 | S/O | LEEEC 80/120MVA Tr replace at old 25/41 MVA TBEA Tr | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | Bus-1 | 2024-02-12 16:07 | 2024-02-12 16:07 | 0:00 | D/W | Project work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2024-02-05 10:58 | 2024-02-05 17:48 | 6:50 | D/W | Egcb Project Work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2024-02-15 11:43 | 2024-02-15 11:43 | 0:00 | D/W | EGCB WORK BUS | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-2, 728T HT | 2024-02-06 12:03 | 2024-02-06 19:10 | 7:07 | D/W | EGCB Project Work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-01 | 2024-02-10 10:28 | 2024-02-18 17:41 | 199:13 | D/W | TR-2 Bay Coupling to 132 Kv Existing Bus | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-01 | 2024-02-20 10:12 | 2024-02-20 17:23 | 7:11 | S/O | Bus Culper PT 108S DS showing cross in SAS over view. working SPMD | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-02-04 17:24 | 2024-02-04 18:41 | 1:17 | D/W | GNDP Project safety | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-02-10 10:49 | 2024-02-10 19:12 | 8:23 | D/W | TR-2 Bay Coupling to 132 Kv Existing Bus | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-02-11 10:13 | 2024-02-11 17:15 | 7:02 | D/W | No L/S. GNDP project work. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-02-04 17:25 | 2024-02-04 18:39 | 1:14 | D/W | GNDP project | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-02-10 10:50 | 2024-02-10 19:05 | 8:15 | D/W | TR-2 Bay Coupling to 132 Kv Existing Bus | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-02-11 10:14 | 2024-02-11 17:03 | 6:49 | D/W | No L/S. GNDP project work. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 LT | 2024-02-09 08:30 | 2024-02-09 16:11 | 7:41 | S/O | Due project work | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 HT | 2024-02-05 09:21 | 2024-02-05 11:23 | 2:02 | S/O | Nest Removing work of 80/120 MVA T-1, 33 KV Bus | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 HT | 2024-02-05 11:34 | 2024-02-05 13:34 | 2:00 | S/O | Nest Removing work of 120 MVA T-2 , 33KV Bus | 0 | 0 | No interruption
|  |  | Total : | 590:24 |  |  |  | 341.6667
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-02-24 06:20 | 2024-02-24 10:45 | 4:25 | S/O | 33 kv Bus coupler T5 maintenance work | 13 | 57.4167 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2024-02-19 15:32 | 2024-02-19 17:07 | 1:35 | S/O | SCADA Integration Testing | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Bus A | 2024-02-01 08:20 | 2024-02-01 17:30 | 9:10 | S/O | Annual maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2024-02-08 09:41 | 2024-02-08 16:25 | 6:44 | S/O | Annual Maintenance of T-1. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2024-02-07 08:59 | 2024-02-07 15:20 | 6:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2024-02-06 09:02 | 2024-02-06 14:35 | 5:33 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T LT | 2024-02-24 07:10 | 2024-02-24 11:22 | 4:12 | S/O | Tr-1 33 kvBus maintenace. | 15 | 63 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T LT | 2024-02-24 07:11 | 2024-02-24 11:55 | 4:44 | D/W | Tr-2 33 kv Bus maintenace. | 15 | 71 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3-435T LT | 2024-02-24 11:22 | 2024-02-24 13:17 | 1:55 | S/O | Tr-3 33kv bus maintenance | 15 | 28.75 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2024-02-22 08:37 | 2024-02-22 14:34 | 5:57 | D/W |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-02-12 12:39 | 2024-02-12 17:00 | 4:21 | S/O | 132KV Busbar modification. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-02-15 10:00 | 2024-02-15 13:52 | 3:52 | D/W |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-02-22 14:36 | 2024-02-22 21:04 | 6:28 | S/O | 132 KV BUS Modification works. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 HT | 2024-02-18 08:58 | 2024-02-18 19:21 | 10:23 | S/O | For 132 KV Bus Modification Work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 LT | 2024-02-02 07:24 | 2024-02-02 10:56 | 3:32 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 HT | 2024-02-03 07:11 | 2024-02-03 13:54 | 6:43 | S/O | Annual Maintenance & 132 KV Bus Modification | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 HT | 2024-02-23 15:45 | 2024-02-23 17:27 | 1:42 | S/O | 132 Kv Busbar Modification Work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 LT | 2024-02-17 07:28 | 2024-02-17 17:54 | 10:26 | D/W | 132 KV Bus modification work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2024-02-19 07:39 | 2024-02-19 08:36 | 0:57 | S/O |  | 20 | 19 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-02-19 09:14 | 2024-02-19 19:12 | 9:58 | S/O | 132kV bus-1 shutdown for bus conductor & Bus PI placement | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-02-22 10:06 | 2024-02-22 17:11 | 7:05 | S/O | Bus maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 HT | 2024-02-14 08:18 | 2024-02-14 19:11 | 10:53 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 LT | 2024-02-13 08:09 | 2024-02-13 18:08 | 9:59 | S/O | annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-02-10 10:25 | 2024-02-10 12:25 | 2:00 | S/O | 33 KV Bus Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-02-22 10:02 | 2024-02-22 21:27 | 11:25 | S/O | Bus maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2024-02-06 09:19 | 2024-02-06 17:39 | 8:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2024-02-07 09:36 | 2024-02-07 14:54 | 5:18 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2024-02-19 09:00 | 2024-02-19 19:24 | 10:24 | S/O | 132kV bus-1 shutdown for bus conductor & Bus PI placement. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-02-05 09:32 | 2024-02-05 17:35 | 8:03 | S/O | Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-02-10 09:54 | 2024-02-10 17:27 | 7:33 | S/O | 33KV Bus Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 LT | 2024-02-04 09:43 | 2024-02-04 19:23 | 9:40 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Bus-1 | 2024-02-09 08:05 | 2024-02-09 21:23 | 13:18 | S/O | Choddogram CKT01 ,02 Reconducting work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Bus-1 | 2024-02-24 07:58 | 2024-02-24 22:40 | 14:42 | S/O | Main Bus 01 shutdown for Chouddagram Ckt 1,2 (Bay) Re conducting & strengthening work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Bus-2 | 2024-02-10 14:22 | 2024-02-10 14:26 | 0:04 | S/O | For Isolate 33KV Bus-01 and Bus-02. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-02-09 06:36 | 2024-02-09 21:35 | 14:59 | S/O | Choddogram CKT01 ,02 Reconducting work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-02-24 06:55 | 2024-02-24 22:44 | 15:49 | S/O | Main Bus 01 shutdown for Chouddagram Ckt 1,2 (Bay) Re conducting & strengthening work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) LT | 2024-02-10 14:22 | 2024-02-10 14:26 | 0:04 | S/O | Request From BPDB For T-02, 33KV Bus Shutdown. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) LT | 2024-02-25 07:28 | 2024-02-25 07:32 | 0:04 | S/O | 33 kv Bus Coupler DS open from PDB (33 kv side) | 18 | 1.2 | Power interruption
Kulaura 132/33kV Grid Sub-Station | 132 kV Bus-A | 2024-02-21 15:31 | 2024-02-22 11:00 | 19:29 | S/O | For maintenance | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2024-02-21 15:31 | 2024-02-22 10:37 | 19:06 | S/O | SF-6 Gas pressure is down | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2024-02-23 08:52 | 2024-02-23 11:03 | 2:11 | S/O | For auxiliary-1 jumper connection. | 10 | 21.8333 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-02-21 02:04 | 2024-02-21 03:19 | 1:15 | S/O | Shutdown taken by PBS | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-02-10 08:46 | 2024-02-10 14:04 | 5:18 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-02-11 08:54 | 2024-02-11 15:03 | 6:09 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 HT | 2024-02-24 08:23 | 2024-02-24 13:43 | 5:20 | S/O | Ten telta test | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-02-01 09:10 | 2024-02-01 14:21 | 5:11 | S/O | Yearly Annual Maintenance of Tr-2 transformer | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-2 HT | 2024-02-24 13:46 | 2024-02-24 15:52 | 2:06 | S/O | Ten-Delta Test | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 HT | 2024-02-27 10:07 | 2024-02-27 17:50 | 7:43 | D/W | Testing | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 HT | 2024-02-28 09:15 | 2024-02-28 20:32 | 11:17 | D/W | SAS witness work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 HT | 2024-02-29 10:25 | 2024-02-29 18:19 | 7:54 | D/W | SAS Witness work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2024-02-04 08:27 | 2024-02-04 13:50 | 5:23 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2024-02-08 08:42 | 2024-02-08 16:23 | 7:41 | S/O | Ten Delta Testing Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 LT | 2024-02-05 08:13 | 2024-02-05 14:12 | 5:59 | S/O | Annual maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-02-10 08:20 | 2024-02-10 14:56 | 6:36 | S/O | Annual Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-02-11 08:14 | 2024-02-11 14:25 | 6:11 | S/O | Yearly Maintenance | 0 | 0 | No interruption
|  |  | Total : | 383:27 |  | Unserved Energy: |  | 262.2
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 2024-02-07 07:30 | 2024-02-07 08:57 | 1:27 | S/O | WZPDCL, 33kV Dopdapia 2 feeder Bus isolator tightening ( red Hot maintenance) | 26 | 37.7 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-02-25 06:53 | 2024-02-25 08:28 | 1:35 | S/O | Pbs bus side red hot maintenance work. | 25 | 39.5833 | Power interruption
Barishal 230/132kV Grid Sub-Station | ATR-1 LT | 2024-02-19 09:07 | 2024-02-20 12:50 | 27:43 | S/O | Annual maintenance&oil leakage repair | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | ATR-2 HT | 2024-02-17 08:38 | 2024-02-18 21:47 | 37:09 | S/O | Annual Maintenance & Oil leakage Repair | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | ATR-2 LT | 2024-02-20 14:31 | 2024-02-20 17:53 | 3:22 | S/O | Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-02-07 15:44 | 2024-02-07 16:55 | 1:11 | S/O | 33 kV Bus-DS red hot maintenance by PBS | 27 | 31.95 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-02-03 07:45 | 2024-02-03 09:31 | 1:46 | S/O | Nobogram 33 feeder DS maintenance | 25 | 44.1667 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) HT | 2024-02-17 09:06 | 2024-02-17 17:10 | 8:04 | S/O | Schedule Shutdown | 26 | 209.7333 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) HT | 2024-02-17 09:07 | 2024-02-17 17:30 | 8:23 | S/O | Schedule Shutdown | 26 | 217.9667 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-02-25 07:52 | 2024-02-25 07:52 | 0:00 | D/W | T1change | 5 | 0 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-02-25 07:51 | 2024-02-25 07:51 | 0:00 | D/W | T1 change | 5 | 0 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-02-27 14:01 | 2024-02-27 15:20 | 1:19 | D/W | Trasnsformer-1 replacement Work. | 20 | 26.3333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-02-24 06:25 | 2024-02-24 07:48 | 1:23 | D/W | 33 KV BUS DS Replacement. | 12 | 16.6 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Bus-A | 2024-02-03 14:48 | 2024-02-03 21:08 | 6:20 | S/O | A-Bus PT R-phase oil leakage. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-02-24 07:35 | 2024-02-24 16:11 | 8:36 | S/O |  | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | 132kV Bus-2 | 2024-02-11 14:50 | 2024-02-11 17:03 | 2:13 | D/W | Stability Test of T-Ã— | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2024-02-20 09:04 | 2024-02-20 09:04 | 0:00 | D/W | 80/120 MVA Tr1 upgradation for G2G | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-02-15 07:57 | 2024-02-17 17:18 | 57:21 | D/W | 33kV Bus Development Work | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-02-20 09:03 | 2024-02-20 09:03 | 0:00 | D/W | 80/120 MVA Tr1 upgradation for G2G | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2024-02-20 08:35 | 2024-02-20 21:58 | 13:23 | S/O | OC/EF &Lockout Relay Replacement | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2024-02-13 07:12 | 2024-02-13 23:47 | 16:35 | S/O | Incoming CB -Replacement work. | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-02-10 08:02 | 2024-02-10 16:10 | 8:08 | S/O | Magura ckt 1,2 cut off condition due to Jhenaidah bus shutdown(annual maintenance) so narail 132/33 kv s/s is in death condition. | 28 | 227.7333 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2024-02-10 08:03 | 2024-02-10 16:12 | 8:09 | S/O | Magura ckt 1,2 cut off condition due to Jhenaidah bus shutdown(annual maintenance) so narail 132/33 kv s/s is in death condition. | 28 | 228.2 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2024-02-21 06:15 | 2024-02-21 07:47 | 1:32 | S/O | Emergency maintenance work due to snapping of sky wire of 33 KV feeder No. 07 of JPBS-01. | 15 | 23 | Power interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-03 HT | 2024-02-22 06:52 | 2024-02-22 08:50 | 1:58 | S/O | Emergency maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 HT | 2024-02-22 08:57 | 2024-02-22 10:57 | 2:00 | S/O | Emergency maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-02-20 14:30 | 2024-02-20 14:46 | 0:16 | D/W | Due to project work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-02-19 09:38 | 2024-02-19 17:37 | 7:59 | D/W | 132kV faulty anergy meter change. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-02-22 08:51 | 2024-02-22 10:49 | 1:58 | D/W | RTCC-2 work. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Generator Transformer-1 (GT-1) LT | 2024-02-13 12:01 | 2024-02-21 08:34 | 188:33 | D/W | Maintenance purpose | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2024-02-17 09:02 | 2024-02-17 13:50 | 4:48 | S/O | Maintenance purpose | 50 | 240 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2024-02-17 09:02 | 2024-02-17 13:50 | 4:48 | S/O | Maintenance purpose | 35 | 168 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T HT | 2024-02-17 10:25 | 2024-02-17 12:44 | 2:19 | S/O | Temperature Transducer Maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2024-02-17 10:24 | 2024-02-17 12:45 | 2:21 | S/O | Temperature Transducer Maintenance | 0 | 0 | No interruption
|  |  | Total : | 432:39 |  | Unserved Energy : |  | 1510.9667
HVDC Grid Circle
Baghabari 230/132kV Grid Sub-Station | T-1 LT | 2024-02-02 11:35 | 2024-02-03 20:05 | 32:30 | S/O | Emergency Mainteance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-2 Bank LT | 2024-02-22 11:40 | 2024-02-23 17:39 | 29:59 | S/O | T-2 Bank Oil centrifuge | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | 132KV Single Bus | 2024-02-02 09:35 | 2024-02-02 16:38 | 7:03 | S/O |  | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Bus-A (132) | 2024-02-27 08:45 | 2024-02-27 13:39 | 4:54 | S/O | A/M | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Bus-A (230) | 2024-02-25 08:55 | 2024-02-25 12:32 | 3:37 | S/O |  | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Bus-B (132) | 2024-02-28 08:42 | 2024-02-28 15:40 | 6:58 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Bus-B (230) | 2024-02-26 09:42 | 2024-02-26 11:52 | 2:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-1 HT | 2024-02-24 08:23 | 2024-02-24 15:13 | 6:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 HT | 2024-02-29 08:25 | 2024-02-29 14:25 | 6:00 | S/O | a/m | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-1 HT | 2024-02-01 11:22 | 2024-02-01 13:05 | 1:43 | D/W | TRTUD Project work | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2024-02-01 13:19 | 2024-02-01 14:56 | 1:37 | D/W | TRTUD Project work | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-3 LT | 2024-02-01 09:30 | 2024-02-01 11:19 | 1:49 | D/W | TRTUD Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-02-04 09:24 | 2024-02-04 10:04 | 0:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-02-05 15:53 | 2024-02-05 16:46 | 0:53 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2024-02-01 10:09 | 2024-02-01 15:46 | 5:37 | S/O | Tripping Ckt test | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Bus 1 | 2024-02-13 08:55 | 2024-02-13 13:12 | 4:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 LT | 2024-02-06 10:32 | 2024-02-06 11:38 | 1:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 LT | 2024-02-04 09:23 | 2024-02-04 10:04 | 0:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 LT | 2024-02-05 15:52 | 2024-02-05 16:46 | 0:54 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2024-02-03 10:36 | 2024-02-03 11:31 | 0:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2024-02-13 08:55 | 2024-02-13 17:14 | 8:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 LT | 2024-02-04 09:22 | 2024-02-05 16:51 | 31:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | 132 kV Bus-B | 2024-02-17 08:30 | 2024-02-17 16:41 | 8:11 | S/O | Annual maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 HT | 2024-02-17 08:09 | 2024-02-17 16:45 | 8:36 | S/O | Annual maintenance | 32 | 275.2 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2024-02-23 06:52 | 2024-02-23 08:01 | 1:09 | S/O | 33kv T1A side DS Uper side & CT O/T maintenance | 37 | 42.55 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 HT | 2024-02-17 08:29 | 2024-02-17 16:46 | 8:17 | S/O | Annual maintenance | 28 | 231.9333 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-02-23 08:08 | 2024-02-23 08:52 | 0:44 | S/O | 33kv T2A CB & CT O/T maintenance | 35 | 25.6667 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2024-02-10 08:23 | 2024-02-10 15:30 | 7:07 | S/O | Annual Maintenance | 35 | 249.0833 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2024-02-10 08:23 | 2024-02-10 15:27 | 7:04 | S/O | Annual Maintenance | 33 | 233.2 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | 132 kV Bus | 2024-02-22 08:32 | 2024-02-22 14:04 | 5:32 | S/O | 132 kv bus -2 shutdown for annual busbar maintenance. | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | 230 kV Bus | 2024-02-19 09:01 | 2024-02-19 14:24 | 5:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-02-09 08:02 | 2024-02-09 18:36 | 10:34 | S/O | A/M | 40 | 422.6667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-02-09 08:01 | 2024-02-09 15:26 | 7:25 | S/O | A/M | 40 | 296.6667 | Power interruption
Magura 132/33kV Grid Sub-Station | T-1 (405T) HT | 2024-02-06 07:57 | 2024-02-06 16:10 | 8:13 | S/O | Annual maintenance | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-1 (405T) HT | 2024-02-10 07:58 | 2024-02-10 17:10 | 9:12 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2024-02-07 08:05 | 2024-02-07 15:26 | 7:21 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2024-02-10 07:59 | 2024-02-10 17:11 | 9:12 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-02-08 08:09 | 2024-02-08 16:25 | 8:16 | S/O | Annual Maintenance | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-02-10 07:57 | 2024-02-10 16:11 | 8:14 | S/O | Annual Maintenance. | 40 | 329.3333 | Power interruption
Ruppur 132/11kV Grid Sub-Station | TR-02 HT | 2024-02-18 10:27 | 2024-02-18 10:27 | 0:00 | D/W | 11kv Tr-02 Bus section maintenance by NSECO | 0 | 0 | No interruption
|  |  | Total : | 280:31 |  | Unserved Energy : |  | 2106.3
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2024-02-09 09:22 | 2024-02-09 16:11 | 6:49 | S/O | Cooling fan maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-02-01 07:53 | 2024-02-03 16:25 | 56:32 | D/W | T-2 Transformer 33 kv incoming Isolator change work. | 8 | 452.2667 | Power interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 1 | 2024-02-10 07:22 | 2024-02-10 18:01 | 10:39 | S/O | PROJECT WORK | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 2 | 2024-02-11 07:19 | 2024-02-11 17:05 | 9:46 | S/O | project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2024-02-09 07:40 | 2024-02-09 14:54 | 7:14 | D/W | Project work (T#04 Commissioning work) | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-02-05 12:30 | 2024-02-05 14:20 | 1:50 | D/W | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-02-06 11:40 | 2024-02-06 13:04 | 1:24 | D/W | Maintenance work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-02-12 07:05 | 2024-02-12 15:10 | 8:05 | D/W | X-Former T-04 Jack Bus (Upper Bus) Conductor Stringing. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-01 LT | 2024-02-14 11:10 | 2024-02-14 13:26 | 2:16 | D/W | SAS commissioning of A2-B2 Bus section of 230kV Bus (Also S/D of A2 and B2 BUS section of 230kV due to SAS Commissioning ) | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-02 LT | 2024-02-12 10:57 | 2024-02-12 11:59 | 1:02 | D/W | SAS commissioning work | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-03 LT | 2024-02-12 12:08 | 2024-02-12 13:05 | 0:57 | D/W | SAS commissioning work | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-1 (407 T) LT | 2024-02-03 10:34 | 2024-02-03 13:37 | 3:03 | D/W | Design, Supply, Erection,Tasting, Commissioning and Integration with NLDC of 13 Grid Sub-Stations on Turnkey basis. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-2 (417 T) LT | 2024-02-04 09:05 | 2024-02-04 12:34 | 3:29 | D/W | Design,Supply,Erection, Testing, Commissioning and Integration with NLDC of 13 Grid Sub-Station on Turnkey basis Project Work. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2024-02-03 03:40 | 2024-02-04 15:41 | 36:01 | S/O | Under Shutdown for PT and CB Test. Transformer T-4 Tripped by over voltage. | 0 | 0 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-1 425T HT | 2024-02-04 12:15 | 2024-02-04 12:50 | 0:35 | S/O | Oil Filling in Conservator Tank. | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 132KV Main bus 1 | 2024-02-07 08:30 | 2024-02-07 16:20 | 7:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 132KVMain bus 2 | 2024-02-08 08:24 | 2024-02-08 14:52 | 6:28 | S/O | Annual Maintenance | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2024-02-13 07:45 | 2024-02-13 09:52 | 2:07 | S/O | T-3 33kv ds to 33kv bus conductor change. | 30 | 63.5 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2024-02-08 10:05 | 2024-02-13 09:53 | 119:48 | S/O | New 132 kV 80/120 MVA Transformer installation. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 2024-02-06 09:09 | 2024-02-10 20:31 | 107:22 | S/O | Oil centrifuge | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 2024-02-29 09:01 | 2024-02-29 14:08 | 5:07 | S/O | Oil leakage mmaintanance. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2024-02-15 13:50 | 2024-02-15 18:02 | 4:12 | D/W | Niamatpur grid bus stability test | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 407T LT | 2024-02-14 11:27 | 2024-02-14 16:17 | 4:50 | D/W | Bus Stability Test ( Relay Test ) | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2024-02-24 11:42 | 2024-02-24 11:42 | 0:00 | S/O | Oil Centrifuge work. | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 HT | 2024-02-04 10:33 | 2024-02-04 14:20 | 3:47 | D/W | Chowdala & niamotpur line charge | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | LV 132 KV BUS | 2024-02-04 10:37 | 2024-02-04 14:27 | 3:50 | D/W | Chowdala & niamotpur line charge | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-02-25 07:26 | 2024-02-25 09:16 | 1:50 | S/O | Maintenance work of T-2 33kv Bus. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-02-29 07:01 | 2024-02-29 08:20 | 1:19 | S/O | Maintenance work of T-2 33kv Bus. | 13 | 17.1167 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2024-02-03 09:26 | 2024-02-03 11:17 | 1:51 | S/O | Maintenace work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-02-05 12:05 | 2024-02-05 14:15 | 2:10 | S/O | Maintenance work of T-2 33kv Bus. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-02-23 09:05 | 2024-02-23 11:23 | 2:18 | S/O | Maintenance work of T-2 33kv Bus. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-02-29 07:02 | 2024-02-29 08:24 | 1:22 | D/W | general cleaning | 36 | 49.2 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-02-03 11:23 | 2024-02-03 13:38 | 2:15 | S/O | Maintenance work | 40 | 90 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-02-26 07:03 | 2024-02-26 09:19 | 2:16 | S/O | Maintenance work of T-3 (ii) 33kv Bus. | 15 | 34 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-02-29 07:04 | 2024-02-29 08:29 | 1:25 | D/W | general cleaning | 29 | 41.0833 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2024-02-10 09:32 | 2024-02-10 12:10 | 2:38 | D/W | Maintenance work of T-2 33kv Bus. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 33 kV BUS | 2024-02-10 09:32 | 2024-02-10 12:11 | 2:39 | D/W | Annual maintanance of Horogram 33kv feeder | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Main Bus | 2024-02-09 06:58 | 2024-02-09 08:33 | 1:35 | D/W | BCRECL has taken shutdown for 68MW solar power evacuation hooking new bay BUS to sirajgonj 132/33kV Grid Sub Station. | 58 | 91.8333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2024-02-09 06:40 | 2024-02-09 13:55 | 7:15 | S/O | bus coupler maintenance by PBS | 20 | 145 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2024-02-16 07:42 | 2024-02-16 16:52 | 9:10 | S/O | T1-T2 bus coupler modification by PBS | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Auxiliary Transformer-1 LT | 2024-02-14 06:55 | 2024-02-14 10:08 | 3:13 | S/O | RPC Capacitor Bank Bus Isolator RedHot Removal Work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-02-13 07:02 | 2024-02-13 10:45 | 3:43 | S/O | Maintenance work of T-2 33kv Bus. | 12 | 44.6 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-02-14 06:55 | 2024-02-14 10:08 | 3:13 | S/O | RPC Capacitor Bank Bus Isolator RedHot Removal Work | 0 | 0 | No interruption
|  |  | Total : | 465:15 |  | Unserved Energy : |  | 1028.6
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 3406:32 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-02-09 07:40 | 2024-02-09 15:35 | 7:55 | S/O | Insulator disc cleaning(tower no -4). | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-02-22 08:33 | 2024-02-22 17:35 | 9:02 | S/O | Annual Mantenance | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-1 | 2024-02-23 14:11 | 2024-02-23 17:43 | 3:32 | S/O | Disc Cleaning | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-02-03 08:29 | 2024-02-03 17:16 | 8:47 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-02-23 07:57 | 2024-02-23 13:53 | 5:56 | S/O | Tower disc cleaning. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-1 | 2024-02-22 08:23 | 2024-02-22 08:23 | 0:00 | S/O | Annual Mantenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-1 | 2024-02-28 07:13 | 2024-02-28 18:10 | 10:57 | S/O | Dis Cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2024-02-29 08:24 | 2024-02-29 17:41 | 9:17 | S/O | Line Disc Clean | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-02-15 09:39 | 2024-02-15 18:14 | 8:35 | S/O | Dead Line checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-01 | 2024-02-04 09:49 | 2024-02-04 16:09 | 6:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-08 10:15 | 2024-02-08 20:26 | 10:11 | S/O | Dead line Checking for Munshiganj Grid SS | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-10 10:01 | 2024-02-10 15:58 | 5:57 | S/O |  | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-12 07:46 | 2024-02-12 16:33 | 8:47 | S/O | OPGW maintenace | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-22 08:54 | 2024-02-22 18:16 | 9:22 | S/O |  | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-23 08:24 | 2024-02-23 19:25 | 11:01 | S/O | Schedule shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-02-24 08:27 | 2024-02-24 15:35 | 7:08 | S/O |  | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-06 09:56 | 2024-02-06 20:00 | 10:04 | S/O | Annual maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-24 15:44 | 2024-02-24 18:25 | 2:41 | S/O |  | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-25 07:03 | 2024-02-25 18:18 | 11:15 | S/O |  | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-26 07:08 | 2024-02-26 19:15 | 12:07 | S/O | Line isolator Disc Clean | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-02-27 09:48 | 2024-02-27 17:25 | 7:37 | S/O | Maintenance Work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-02-06 08:38 | 2024-02-06 12:58 | 4:20 | S/O | Bus isolator lower clamp some parts of the strain have cut. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Shahajibazar 132 kV Ckt-3 | 2024-02-29 08:41 | 2024-02-29 08:41 | 0:00 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-02-25 09:24 | 2024-02-25 18:17 | 8:53 | S/O | Annual maintenance work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2024-02-26 09:46 | 2024-02-26 18:53 | 9:07 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 02 | 2024-02-03 14:08 | 2024-02-03 17:15 | 3:07 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2024-02-24 07:38 | 2024-02-24 10:03 | 2:25 | S/O | Work on kaliakoir end. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-02-04 12:06 | 2024-02-04 13:14 | 1:08 | S/O | Shutdown taken by NLDC to work Kaliakoir end. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-02-06 14:23 | 2024-02-06 15:11 | 0:48 | S/O | Shutdown from Kaliakoir end | 10 | 8 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-1 | 2024-02-16 10:33 | 2024-02-16 17:59 | 7:26 | S/O | Dead line checking & Bay maintenance | 14 | 104.0667 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-02-17 07:35 | 2024-02-17 17:27 | 9:52 | S/O | Dead line checking & Bay maintenance | 10 | 98.6667 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2024-02-19 08:37 | 2024-02-19 16:37 | 8:00 | S/O | emergency Maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-02-18 09:27 | 2024-02-18 18:48 | 9:21 | S/O | Emergency Line Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-02-08 08:41 | 2024-02-08 13:31 | 4:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-02-17 09:47 | 2024-02-17 12:25 | 2:38 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-02-27 08:08 | 2024-02-27 16:27 | 8:19 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2024-02-17 12:55 | 2024-02-17 15:42 | 2:47 | S/O | Annual maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-02-01 08:30 | 2024-02-01 17:22 | 8:52 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-02-13 09:46 | 2024-02-13 18:27 | 8:41 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-02-28 09:33 | 2024-02-28 16:59 | 7:26 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-02-04 09:43 | 2024-02-04 16:19 | 6:36 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-03 08:38 | 2024-02-03 16:28 | 7:50 | D/W | Project work | 6 | 47 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-04 08:10 | 2024-02-04 16:35 | 8:25 | D/W | Project work. | 25 | 210.4167 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-05 08:44 | 2024-02-05 16:50 | 8:06 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-07 07:56 | 2024-02-07 17:15 | 9:19 | D/W | Project work. | 25 | 232.9167 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-08 07:57 | 2024-02-08 16:49 | 8:52 | D/W | Project Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-09 08:05 | 2024-02-09 16:26 | 8:21 | D/W | Project work. | 12 | 100.2 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-10 06:47 | 2024-02-10 14:53 | 8:06 | D/W | Project work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-11 07:40 | 2024-02-11 17:40 | 10:00 | D/W | Project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-02-23 08:36 | 2024-02-23 15:18 | 6:42 | D/W | 400kV Rup pur project work. | 40 | 268 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-03 08:18 | 2024-02-03 16:48 | 8:30 | D/W | Project work | 6 | 51 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-04 08:10 | 2024-02-04 15:45 | 7:35 | D/W | Project work. | 25 | 189.5833 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-05 08:23 | 2024-02-05 16:50 | 8:27 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-06 09:20 | 2024-02-07 17:20 | 32:00 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-08 07:30 | 2024-02-08 16:48 | 9:18 | D/W | Project Work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-09 08:05 | 2024-02-09 16:25 | 8:20 | D/W | Project work. | 12 | 100 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-10 06:46 | 2024-02-10 14:54 | 8:08 | D/W | Project work. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-11 07:42 | 2024-02-11 16:01 | 8:19 | D/W | Project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-02-23 08:36 | 2024-02-23 15:17 | 6:41 | D/W | 400kV Rup pur project work. | 40 | 267.3333 | Power interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2024-02-17 08:51 | 2024-02-17 21:09 | 12:18 | S/O | Annual Maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-02-01 09:28 | 2024-02-01 18:09 | 8:41 | S/O | Applied SD for AM Work on 132Kv Mirpur Uttara sector 18 Ckt. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-02-27 09:10 | 2024-02-27 17:19 | 8:09 | S/O | CB Hydraulic oil leakage maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-02-05 09:49 | 2024-02-05 16:29 | 6:40 | S/O | Line maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-02-06 09:40 | 2024-02-06 16:29 | 6:49 | S/O | AM | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-02-07 09:49 | 2024-02-07 14:31 | 4:42 | S/O | Annual Maintanance Work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-02-11 10:11 | 2024-02-11 16:03 | 5:52 | S/O | Annual maintenance works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-02-12 09:54 | 2024-02-12 19:31 | 9:37 | S/O | Dead line check | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-02-22 09:17 | 2024-02-22 16:26 | 7:09 | S/O | Tower No-303, R-Phase (Kis-2), suffering jumper loop changing works | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-02-06 07:20 | 2024-02-06 11:48 | 4:28 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-02-27 15:37 | 2024-02-27 16:46 | 1:09 | S/O | Kite removing | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-02-24 10:10 | 2024-02-24 17:48 | 7:38 | D/W | Project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-02-25 10:04 | 2024-02-25 18:16 | 8:12 | D/W | Project Work , SAS | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-02-26 10:02 | 2024-02-26 18:53 | 8:51 | D/W | Internal test & SAS Integration | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-02-27 09:40 | 2024-02-27 17:15 | 7:35 | D/W | Internal test & Pending SAS Integration | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 2024-02-04 08:34 | 2024-02-04 17:27 | 8:53 | D/W | Sreepur-Sirajganj-ckt-01 is shutdown due to SAS integration | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-1 | 2024-02-05 08:54 | 2024-02-05 17:59 | 9:05 | D/W | SAS integration by siemens ind. (Shutdown included Sreepur-sirajganj ckt-2's tie bay) | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2024-02-06 09:05 | 2024-02-06 18:38 | 9:33 | D/W | SAS Integration by Siemens | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2024-02-07 09:16 | 2024-02-07 18:29 | 9:13 | D/W | SAS integration | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-02-03 08:39 | 2024-02-03 13:57 | 5:18 | D/W | SAS Integratioon | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-02-03 14:10 | 2024-02-03 17:13 | 3:03 | D/W | SAS integration | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2024-02-01 08:33 | 2024-02-01 17:32 | 8:59 | D/W | Ghatail grid line connection | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2024-02-02 07:33 | 2024-02-02 17:08 | 9:35 | D/W | Project work S/D | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2024-02-02 07:33 | 2024-02-02 17:04 | 9:31 | D/W | Project work S/D | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-02-14 12:08 | 2024-02-14 14:39 | 2:31 | S/O | Asper Rajuk requirement. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-02-02 08:45 | 2024-02-02 17:37 | 8:52 | S/O | Safety | 0 | 0 | No interruption
|  |  | Total : | 646:29 |  | Unserved Energy: |  | 1677.1833
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-02-17 08:14 | 2024-02-18 18:11 | 33:57 | S/O | due to work of sky wire. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Rampura-04 | 2024-02-04 07:38 | 2024-02-05 00:19 | 16:41 | S/O | Work From Rampura End | 0 | 0 | No interruption
Charsaidpur 132/33kV Sub-Station | Madanganj-2 | 2024-02-20 12:12 | 2024-02-20 14:35 | 2:23 | D/W | GD meter Installation at various bay | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-02-09 09:03 | 2024-02-09 17:18 | 8:15 | S/O | To cleaning the 230 KV line disk | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-02-23 12:27 | 2024-02-23 19:29 | 7:02 | S/O | Disc change and cleaning | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi circuit-1 | 2024-02-08 08:29 | 2024-02-08 16:33 | 8:04 | S/O | 230 KV line disk cleaning. | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi circuit-1 | 2024-02-22 08:44 | 2024-02-23 12:19 | 27:35 | S/O | Disk cleaning by Dhamrai 132/33 kV sub-station. | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-1 | 2024-02-18 13:44 | 2024-02-18 14:40 | 0:56 | S/O | relay test by spmd | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-02-02 09:41 | 2024-02-02 16:09 | 6:28 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-02-03 09:05 | 2024-02-03 16:01 | 6:56 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-02-04 09:34 | 2024-02-04 13:31 | 3:57 | S/O | Annual Maintanance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-02-26 12:51 | 2024-02-26 19:11 | 6:20 | S/O | Reserve Busbar Isolator Finger change. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2024-02-28 08:19 | 2024-02-28 18:38 | 10:19 | S/O | By NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-02-05 10:15 | 2024-02-05 15:30 | 5:15 | S/O | Annual Dead Line Checking | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-02-06 09:38 | 2024-02-06 16:35 | 6:57 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2024-02-08 15:42 | 2024-02-08 17:12 | 1:30 | S/O | For mainbus DS Maintanance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2024-02-27 09:18 | 2024-02-27 16:03 | 6:45 | S/O | From another side by NLDC. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Keraniganj-1 (Pre- Lalbag) | 2024-02-12 09:16 | 2024-02-12 17:36 | 8:20 | S/O | Dead line purpose | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Keraniganj-1 (Pre- Lalbag) | 2024-02-19 08:30 | 2024-02-19 08:30 | 0:00 | S/O | Dead line checking | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Keraniganj-2 (Pre- Aourahati) | 2024-02-12 09:21 | 2024-02-12 17:36 | 8:15 | S/O | Dead line Checking purpose | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Keraniganj-2 (Pre- Aourahati) | 2024-02-19 08:32 | 2024-02-19 08:32 | 0:00 | S/O | Dead line checking | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-1 | 2024-02-13 08:32 | 2024-02-13 16:35 | 8:03 | S/O | Shyampur-Magnaghat one ckt shutdown. Probability is high other ckt Overloaded. So Hasnabad-Keraniganj both ckt CB off at Hasnabad end. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-2 | 2024-02-13 08:33 | 2024-02-13 16:37 | 8:04 | S/O | Shyampur-Magnaghat one ckt shutdown. Probability is high other ckt Overloaded. So Hasnabad-Keraniganj both ckt CB off at Hasnabad end. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-02-22 07:42 | 2024-02-22 12:54 | 5:12 | S/O | Disc Change of tower Number (70-71) | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-02-23 07:13 | 2024-02-23 11:11 | 3:58 | S/O | Maintenance Work. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2024-02-22 13:26 | 2024-02-22 19:07 | 5:41 | S/O | insulator disk change | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2024-02-23 11:12 | 2024-02-23 14:53 | 3:41 | S/O | insulator disk change | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | Keraniganj Ckt | 2024-02-15 07:10 | 2024-02-16 06:44 | 23:34 | S/O | To do maintenance & renovation work at 132KV bus coupler isolator. | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | Keraniganj Ckt | 2024-02-24 10:48 | 2024-02-24 20:12 | 9:24 | S/O |  | 0 | 0 | No interruption
Kamrangirchar 132/33kV Grid Sub-Station | Lalbag | 2024-02-16 06:38 | 2024-02-16 15:43 | 9:05 | S/O | To do maintenance & renovation work at 132KV bus coupler isolator and GT3 isolator. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-03 09:13 | 2024-02-03 11:48 | 2:35 | S/O | Maintenance work at hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-04 09:35 | 2024-02-04 17:00 | 7:25 | S/O | Dead line check from Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-05 09:22 | 2024-02-05 14:40 | 5:18 | S/O | Dead line checking. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-12 09:07 | 2024-02-12 17:43 | 8:36 | S/O | Dead line checking from sreenagar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-19 08:16 | 2024-02-19 17:33 | 9:17 | S/O | Deadline checking from Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-02-25 10:36 | 2024-02-25 17:35 | 6:59 | S/O | Dead Line Checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-02-01 09:55 | 2024-02-01 17:50 | 7:55 | S/O | Dead line checking from Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2024-02-05 08:48 | 2024-02-05 15:38 | 6:50 | S/O | Dead line checking from Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-03 09:13 | 2024-02-03 11:48 | 2:35 | S/O | Maintenance work at hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-04 09:35 | 2024-02-04 17:00 | 7:25 | S/O | Dead line check from Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-05 09:22 | 2024-02-05 14:40 | 5:18 | S/O | Dead line checking . | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-12 09:07 | 2024-02-12 17:42 | 8:35 | S/O | Deadline checking in Hasnabad end. Hasnabad line 1&2 both are shutdown. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-16 12:01 | 2024-02-16 14:40 | 2:39 | S/O | Dead line checking . | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-19 08:15 | 2024-02-19 17:32 | 9:17 | S/O | Deadline checking from Hasnabad end | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-02-25 10:36 | 2024-02-25 17:35 | 6:59 | S/O | Dead Line Checking | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Kamrangirchar | 2024-02-09 11:12 | 2024-02-09 16:47 | 5:35 | S/O | Dead line check. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Lalbagh-3 | 2024-02-16 10:46 | 2024-02-16 15:37 | 4:51 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Nawabganj-1 | 2024-02-13 08:58 | 2024-02-13 16:47 | 7:49 | S/O | Dead line checking from Nawabganj end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Nawabganj-2 | 2024-02-15 08:55 | 2024-02-15 14:27 | 5:32 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Srinagar-1 | 2024-02-19 08:48 | 2024-02-19 17:26 | 8:38 | S/O | Deadline checking for Hasnabad-keraniganj 132kv line 1&2 from Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Srinagar-2 | 2024-02-25 14:48 | 2024-02-25 17:49 | 3:01 | S/O | Dead line check. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2024-02-20 12:12 | 2024-02-20 14:33 | 2:21 | S/O | CB GAS Pressure Meter change | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-02-28 08:17 | 2024-02-28 18:37 | 10:20 | S/O | OPGW works...at Madanganj- Haripur ckt | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-02-28 08:17 | 2024-02-28 18:37 | 10:20 | S/O | OPGW works at Madanganj - Haripur ckt | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2024-02-07 10:14 | 2024-02-07 13:19 | 3:05 | S/O | Dead End line checking | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 102 MW 132 kv Ckt | 2024-02-01 10:17 | 2024-02-01 17:34 | 7:17 | S/O | Under ground cable fault location identification. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-02-26 12:32 | 2024-02-26 15:09 | 2:37 | S/O |  | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-01 | 2024-02-07 09:38 | 2024-02-07 23:31 | 13:53 | S/O | Busbar replacement work by spmd. | 50 | 694.1667 | Power interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-02 | 2024-02-07 09:38 | 2024-02-07 23:31 | 13:53 | S/O | Busbar protection panel replacement work done by spmd. | 50 | 694.1667 | Power interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Haripur-02 | 2024-02-10 09:42 | 2024-02-10 23:36 | 13:54 | S/O | Busbar protection panel replacement work done by spmd. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-02-11 09:16 | 2024-02-11 21:25 | 12:09 | S/O | Busbar protection panel replacement work done by spmd. | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj- Ckt-2 | 2024-02-07 13:21 | 2024-02-07 16:50 | 3:29 | S/O | Dead Line Checking | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP | 2024-02-13 08:18 | 2024-02-13 14:54 | 6:36 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP | 2024-02-14 08:41 | 2024-02-14 15:14 | 6:33 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | Keraniganj-1 | 2024-02-14 09:21 | 2024-02-14 18:23 | 9:02 | S/O | Deadline checking(annual maintenance) | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | Keraniganj-2 | 2024-02-18 10:03 | 2024-02-18 15:58 | 5:55 | S/O | Deadline checking(annual maintenance) | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | Keraniganj-2 | 2024-02-20 10:18 | 2024-02-20 18:42 | 8:24 | S/O | Deadline checking (Yearly Maintenance) | 0 | 0 | No interruption
Postogola 132/33kV Grid Sub-Station | Hasnabad Circuit-1 | 2024-02-22 11:49 | 2024-02-22 14:50 | 3:01 | D/W | Shutdown is taken for changing GD meter of CB | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2024-02-05 18:35 | 2024-02-06 11:54 | 17:19 | S/O | Tripping cause Identification. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-2(D05) | 2024-02-02 08:36 | 2024-02-02 17:45 | 9:09 | S/O | Dead Line Checking | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-02-27 09:40 | 2024-02-27 14:53 | 5:13 | S/O | Deadline Checking. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-02-26 08:22 | 2024-02-26 15:28 | 7:06 | S/O | Dead line checking | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-02-08 15:44 | 2024-02-08 17:11 | 1:27 | S/O | Maintenance work in DS ( Haripur Sub-station end) | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-02-27 09:19 | 2024-02-27 16:02 | 6:43 | S/O | Deadline Checking. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2024-02-02 08:22 | 2024-02-03 18:23 | 34:01 | S/O | Mainteance work for maniknagar end. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2024-02-22 07:12 | 2024-02-22 07:12 | 0:00 | S/O | Due to 8 nos tower work | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2024-02-09 08:40 | 2024-02-09 17:36 | 8:56 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2024-02-14 08:52 | 2024-02-14 15:40 | 6:48 | S/O | Deadline checking. Shutdown taken by Incharge Siddirganj. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-02-12 08:58 | 2024-02-12 18:16 | 9:18 | S/O | Deadline checking. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-2 | 2024-02-13 09:02 | 2024-02-13 16:21 | 7:19 | S/O | Annual maintenance deadline checking.Shutdown taken by Shiddhirganj Sub-station Incharge. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | TCCL | 2024-02-27 10:05 | 2024-02-27 17:36 | 7:31 | S/O | Metering panel meter changed at TCCL end. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-01 | 2024-02-01 08:36 | 2024-02-01 14:45 | 6:09 | S/O | Dead Line checking. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-01 | 2024-02-25 10:43 | 2024-02-25 14:32 | 3:49 | S/O | Keranigonj ckt -01 dead line checking | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-02(Powerpac) | 2024-02-10 08:42 | 2024-02-10 16:27 | 7:45 | S/O | Due to maint.work | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-02(Powerpac) | 2024-02-11 08:30 | 2024-02-11 16:16 | 7:46 | S/O | Due to maint.work | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-02(Powerpac) | 2024-02-12 09:30 | 2024-02-12 17:47 | 8:17 | S/O | Keraniganj-2 Deadline Checking | 0 | 0 | No interruption
|  |  | Total : | 673:11 |  | Unserved Energy: |  | 1388.3333
Chattogram Grid Circle :
AKS 132/33kV Grid Sub-Station | Bar Aulia | 2024-02-13 08:40 | 2024-02-13 08:40 | 0:00 | S/O | AKSPL to Baraulia 132 kv Line Schedule Shutdown. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | AKSML Ckt | 2024-02-04 08:12 | 2024-02-04 16:08 | 7:56 | S/O | Dead line check | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-2 | 2024-02-15 11:02 | 2024-02-15 21:15 | 10:13 | S/O | yearly Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-02-08 08:50 | 2024-02-08 13:45 | 4:55 | S/O | Annual maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-01 | 2024-02-05 08:35 | 2024-02-05 14:47 | 6:12 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-02 | 2024-02-06 08:32 | 2024-02-09 14:44 | 78:12 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-02-16 06:20 | 2024-02-16 10:28 | 4:08 | S/O | Bus maintenance at Hathhazari end. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-02-16 06:20 | 2024-02-16 10:28 | 4:08 | S/O | Bus maintenance at Hathhazari ss. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2024-02-07 09:21 | 2024-02-07 17:21 | 8:00 | S/O |  | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2024-02-08 08:21 | 2024-02-08 17:34 | 9:13 | S/O | Disk change | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2024-02-25 17:32 | 2024-02-25 18:42 | 1:10 | S/O | Line Maintenance | 22 | 25.6667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2024-02-23 09:17 | 2024-02-24 16:49 | 31:32 | S/O | For Disk cleaning & change. Matarbari getting power through Doha-Cox ckt-02. interruption occur during loop opening time only. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2024-02-25 14:21 | 2024-02-25 15:59 | 1:38 | S/O | Shut Down taken by Coxbazar Grid | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | HATHAZARI-2 | 2024-02-27 08:26 | 2024-02-27 16:09 | 7:43 | S/O | Deadline Checking | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | HATHAZARI-2 | 2024-02-28 08:21 | 2024-02-28 16:09 | 7:48 | S/O | Deadline Checking | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2024-02-04 08:36 | 2024-02-04 13:44 | 5:08 | S/O | annual bay maintenance | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2024-02-07 06:16 | 2024-02-07 09:36 | 3:20 | S/O | Due to Julda 132 kV bus shutdown | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-02-03 08:43 | 2024-02-03 12:49 | 4:06 | S/O | Due to Annual Bay Maintenance work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-02-01 09:48 | 2024-02-01 13:16 | 3:28 | S/O | For annual Bay maintenance work. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | GPH-01 | 2024-02-27 08:28 | 2024-02-27 16:12 | 7:44 | S/O | Annual Maintenance and dead line checking. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | GPH-01 | 2024-02-28 08:22 | 2024-02-28 16:24 | 8:02 | S/O | dead line check | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Raojan-01 | 2024-02-02 09:30 | 2024-02-02 17:09 | 7:39 | S/O | Annual Maintenance and Deadline Checking | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Raojan-02 | 2024-02-07 09:50 | 2024-02-07 17:22 | 7:32 | S/O | annual dead line checking | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2024-02-01 06:03 | 2024-02-01 09:44 | 3:41 | D/W | Project work | 24 | 88.4 | Power interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2024-02-10 08:37 | 2024-02-10 13:39 | 5:02 | S/O | Annual Bay equipment maintenance work. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2024-02-12 05:56 | 2024-02-12 07:16 | 1:20 | D/W | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 2024-02-01 06:01 | 2024-02-01 09:32 | 3:31 | D/W | Project work | 24 | 84.4 | Power interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 2024-02-12 05:54 | 2024-02-12 15:18 | 9:24 | D/W | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2024-02-01 06:02 | 2024-02-01 09:45 | 3:43 | D/W | Project work | 24 | 89.2 | Power interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2024-02-07 06:19 | 2024-02-07 09:40 | 3:21 | D/W | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2024-02-12 05:54 | 2024-02-12 07:18 | 1:24 | D/W | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2024-02-07 06:26 | 2024-02-07 09:24 | 2:58 | S/O | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2024-02-11 08:38 | 2024-02-12 07:04 | 22:26 | S/O | Annual Maintanance | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-1 | 2024-02-01 06:05 | 2024-02-01 09:58 | 3:53 | D/W | Project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-1 | 2024-02-07 06:16 | 2024-02-12 13:38 | 127:22 | D/W | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-2 & 3 | 2024-02-01 06:06 | 2024-02-01 09:59 | 3:53 | S/O | Project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-2 & 3 | 2024-02-07 06:17 | 2024-02-07 09:57 | 3:40 | D/W | project work | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-2 & 3 | 2024-02-12 05:54 | 2024-02-12 07:17 | 1:23 | D/W | project work | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2024-02-14 09:06 | 2024-02-14 16:43 | 7:37 | S/O | Dead Line Checking | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2024-02-15 08:28 | 2024-02-15 16:48 | 8:20 | S/O | Dead line checking | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2024-02-17 08:52 | 2024-02-17 16:23 | 7:31 | S/O | Dead line checking | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2024-02-18 08:31 | 2024-02-18 16:33 | 8:02 | S/O | Annual Deadline Checking. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2024-02-19 08:38 | 2024-02-19 16:49 | 8:11 | S/O | Deadline Checking. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-2 | 2024-02-29 08:54 | 2024-02-29 16:38 | 7:44 | S/O | Annual Maintenance Work( Line ) | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2024-02-07 08:50 | 2024-02-07 15:17 | 6:27 | S/O | Annual M/T | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2024-02-25 08:55 | 2024-02-25 12:08 | 3:13 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2024-02-20 08:33 | 2024-02-20 15:00 | 6:27 | S/O | Armouring Work (Span 45-46) B-Phase | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-1(Rampur) | 2024-02-22 08:36 | 2024-02-22 12:54 | 4:18 | S/O | Annual Maintenance( Bay) | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-2(Rampur) | 2024-02-24 08:42 | 2024-02-24 11:41 | 2:59 | S/O | Annual Maintenance(BAY). | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-02-03 08:42 | 2024-02-03 12:52 | 4:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Sholoshahar CKT-1(Madunaghat) | 2024-02-18 09:08 | 2024-02-18 12:56 | 3:48 | S/O | Annual Maintenance Bay | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-1 | 2024-02-16 06:25 | 2024-02-16 10:21 | 3:56 | S/O | Hathazari Maintenance work | 0 | 0 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2024-02-16 06:26 | 2024-02-16 17:17 | 10:51 | S/O | Annual maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2024-02-17 08:23 | 2024-02-17 16:04 | 7:41 | S/O | Dead line checking | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | 150 MW Power Station -02 | 2024-02-05 10:46 | 2024-02-05 17:46 | 7:00 | D/W | Egcb Project Work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | 150 MW Power Station -02 | 2024-02-06 11:50 | 2024-02-06 19:11 | 7:21 | D/W | EGCB Project Work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | 150 MW Power Station -02 | 2024-02-15 00:09 | 2024-02-15 00:09 | 0:00 | D/W | EGCB Work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-2 | 2024-02-05 10:51 | 2024-02-05 17:45 | 6:54 | D/W | EGCB Project Work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-2 | 2024-02-06 11:56 | 2024-02-06 19:10 | 7:14 | D/W | EGCB Project Work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-2 | 2024-02-15 00:06 | 2024-02-15 00:06 | 0:00 | D/W | EGCB work | 0 | 0 | No interruption
Modern Steel 132/11kV Grid Sub-Station | Modern Khulshi Ckt 2 | 2024-02-26 09:05 | 2024-02-26 12:33 | 3:28 | S/O | Modern Khulshu ckt-2 Annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-02-01 09:49 | 2024-02-01 13:16 | 3:27 | S/O | For annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2024-02-22 08:34 | 2024-02-22 12:54 | 4:20 | S/O | For annual maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2024-02-24 08:41 | 2024-02-24 11:44 | 3:03 | S/O | Khulshi Gird Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Julda-1 | 2024-02-07 06:18 | 2024-02-07 09:38 | 3:20 | S/O | Juldha Substation annual BUS Maintenance , | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Julda-2 | 2024-02-14 08:25 | 2024-02-14 15:29 | 7:04 | S/O | Annual Bay Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha-1 | 2024-02-15 08:20 | 2024-02-15 14:14 | 5:54 | S/O | Annual Bay Maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Sikalbaha-2 | 2024-02-17 08:29 | 2024-02-17 13:15 | 4:46 | S/O | yearly Bay Maintenance Work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Bakulia-2 | 2024-02-09 10:41 | 2024-02-09 14:44 | 4:03 | S/O | yearly Bay Maintenance Work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-2 | 2024-02-11 10:17 | 2024-02-11 16:44 | 6:27 | S/O | yearly Bay Maintenance Work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Julda | 2024-02-12 06:18 | 2024-02-14 14:35 | 56:17 | S/O | yearly Bay Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 658:41 |  | Unserved Energy: |  | 287.6667
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-02-18 09:27 | 2024-02-18 18:49 | 9:22 | S/O | Realy test | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-02-04 09:25 | 2024-02-04 15:01 | 5:36 | S/O | Annual maintenance | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-02-05 09:24 | 2024-02-05 17:48 | 8:24 | S/O | Annual Maintenance | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-02-06 08:50 | 2024-02-06 15:57 | 7:07 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-02-14 08:50 | 2024-02-14 17:29 | 8:39 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-02-15 08:38 | 2024-02-15 17:05 | 8:27 | S/O |  | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-02-17 09:46 | 2024-02-17 16:34 | 6:48 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-II | 2024-02-22 09:43 | 2024-02-22 17:32 | 7:49 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-II | 2024-02-24 08:57 | 2024-02-24 17:39 | 8:42 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-II | 2024-02-25 09:06 | 2024-02-25 17:43 | 8:37 | S/O | AM | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-II | 2024-02-27 08:48 | 2024-02-27 16:38 | 7:50 | S/O | AM | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2024-02-06 08:20 | 2024-02-06 10:41 | 2:21 | S/O | NLDC AE. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 100MW(GT) Power Plant Incomer (T4) | 2024-02-07 17:47 | 2024-02-21 11:25 | 329:38 | S/O |  | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 100MW(GT) Power Plant Incomer (T4) | 2024-02-21 12:50 | 2024-02-21 12:50 | 0:00 | S/O | For CB Testing purpose | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-1 | 2024-02-14 07:24 | 2024-02-14 21:36 | 14:12 | S/O | Bay Maintenance for feni grid s/s | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 2024-02-13 07:15 | 2024-02-13 22:57 | 15:42 | S/O | Bay maintenance for feni grid s/s | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 2024-02-15 07:21 | 2024-02-15 20:17 | 12:56 | S/O | Bus upgradation at Feni grid. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Cumilla(S) Ckt-3 | 2024-02-14 14:16 | 2024-02-14 15:21 | 1:05 | D/W |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Cumilla(S) Ckt-3 | 2024-02-20 09:31 | 2024-02-20 13:07 | 3:36 | D/W | 132 KV Bus modification work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-02-14 09:17 | 2024-02-14 13:04 | 3:47 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2024-02-04 11:06 | 2024-02-04 15:02 | 3:56 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2024-02-25 08:58 | 2024-02-25 12:22 | 3:24 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2024-02-28 09:35 | 2024-02-28 17:06 | 7:31 | S/O | Meghnagat Sub-station Annual Maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2024-02-29 08:43 | 2024-02-29 17:11 | 8:28 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2024-02-04 09:24 | 2024-02-04 15:00 | 5:36 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2024-02-05 09:22 | 2024-02-05 17:50 | 8:28 | S/O | Annual maintenance(Dead line check) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2024-02-06 08:26 | 2024-02-06 15:56 | 7:30 | S/O | Annual maintenance work in Bibiana S/S | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2024-02-14 08:52 | 2024-02-14 17:29 | 8:37 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2024-02-15 08:37 | 2024-02-15 17:08 | 8:31 | S/O | Annual Maintenance of Shahjibazar 132 KV SS | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2024-02-08 08:47 | 2024-02-08 17:40 | 8:53 | S/O |  | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2024-02-10 08:30 | 2024-02-10 16:49 | 8:19 | S/O | Deadline Checking | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2024-02-11 08:50 | 2024-02-11 17:01 | 8:11 | S/O | Annual Maintenance works | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2024-02-12 09:27 | 2024-02-12 14:48 | 5:21 | S/O | Annual maintenance(Bay) | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-1 | 2024-02-13 08:46 | 2024-02-13 11:25 | 2:39 | D/W |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-1 | 2024-02-20 13:19 | 2024-02-20 15:55 | 2:36 | D/W | p/w Cumilla(N) End | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-2 | 2024-02-13 11:36 | 2024-02-13 13:06 | 1:30 | D/W |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-2 | 2024-02-20 15:57 | 2024-02-20 17:30 | 1:33 | D/W |  | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-02-14 14:15 | 2024-02-14 15:22 | 1:07 | D/W | Work at Cumilla(N) S/S end | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-02-20 09:29 | 2024-02-20 13:11 | 3:42 | D/W | P/W Cumilla(N) | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-02-06 12:36 | 2024-02-06 19:35 | 6:59 | D/W | Comilla (n) work done. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-02-06 12:36 | 2024-02-06 19:38 | 7:02 | D/W | comilla(n) work done. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-02-19 07:17 | 2024-02-19 14:41 | 7:24 | S/O | maintenance work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2024-02-15 08:30 | 2024-02-15 15:47 | 7:17 | S/O | For Deadline check prupose Shutdown taken by NLDC | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2024-02-16 09:39 | 2024-02-16 16:19 | 6:40 | S/O | annual maintenance of Siddirgonj Substation end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2024-02-17 07:34 | 2024-02-17 17:28 | 9:54 | S/O | Deadline Check | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2024-02-20 07:32 | 2024-02-20 15:41 | 8:09 | S/O | Deadline check by third party Siddirganj 132 KV Grid ss. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2024-02-22 07:40 | 2024-02-22 16:14 | 8:34 | S/O | annual maintenance for Siddirgonj Substation | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2024-02-23 07:26 | 2024-02-23 16:59 | 9:33 | S/O | Deadline check | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-2 | 2024-02-24 07:38 | 2024-02-24 17:23 | 9:45 | S/O | annual maintenance of siddirgonj ss end | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-02-19 09:06 | 2024-02-19 19:17 | 10:11 | S/O | 132kV bus-1 shutdown for bus conductor & Bus PI placement | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-1 | 2024-02-09 07:01 | 2024-02-09 22:10 | 15:09 | S/O | Choddogram CKT01 ,02 Reconducting work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-1 | 2024-02-11 07:08 | 2024-02-11 22:45 | 15:37 | S/O | Reconducting work, | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-1 | 2024-02-24 07:22 | 2024-02-24 23:19 | 15:57 | S/O | Main Bus 01 shutdown for Chouddagram Ckt 1,2 (Bay) Re conducting & strengthening work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-02-09 07:02 | 2024-02-09 22:10 | 15:08 | S/O | Choddogram CKT01 ,02 Reconducting work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-02-18 07:40 | 2024-02-18 17:03 | 9:23 | S/O | Re-Conducting work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-02-24 07:22 | 2024-02-24 23:20 | 15:58 | S/O | Main Bus 01 shutdown for Chouddagram Ckt 1,2 (Bay) Re conducting & strengthening work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Feni-Lanka HFO PS | 2024-02-09 07:54 | 2024-02-09 22:10 | 14:16 | S/O | Choddogram CKT01 ,02 Reconducting work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Feni-Lanka HFO PS | 2024-02-24 07:40 | 2024-02-24 23:30 | 15:50 | S/O | Main Bus 01 shutdown for Chouddagram Ckt 1,2 (Bay) Re conducting & strengthening work. | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-2 | 2024-02-06 08:30 | 2024-02-06 17:16 | 8:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-2 | 2024-02-07 08:51 | 2024-02-07 16:53 | 8:02 | S/O | yearly maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-02-19 16:09 | 2024-02-19 19:32 | 3:23 | D/W | For comilla north grid | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-1 | 2024-02-18 12:24 | 2024-02-18 15:18 | 2:54 | S/O | fenchuganj s/s take this shutdown | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2024-02-18 15:27 | 2024-02-18 16:20 | 0:53 | S/O | By NLDC instructions | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-02-29 08:44 | 2024-02-29 15:07 | 6:23 | S/O | Annual Maintainnance. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 150MW GT PS | 2024-02-23 16:48 | 2024-02-24 11:15 | 18:27 | D/W | Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2024-02-05 12:10 | 2024-02-05 12:45 | 0:35 | D/W | PT Maintenance | 16 | 9.3333 | Power interruption
Sylhet 132/33kV Grid Sub-Station | 75 MW ST PS | 2024-02-02 11:44 | 2024-02-11 17:05 | 221:21 | D/W | Auxiliary Transformer Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2024-02-13 08:27 | 2024-02-13 12:55 | 4:28 | S/O | maintenance | 0 | 0 | No interruption
|  |  | Total : | 1060:28 |  | Unserved Energy: |  | 9.3333
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-02-27 14:05 | 2024-02-27 15:19 | 1:14 | S/O |  | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-20 11:40 | 2024-02-20 17:29 | 5:49 | S/O | Shut down taken by orion | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-21 08:30 | 2024-02-21 16:45 | 8:15 | S/O | Ordered By ALDC, KHULNA due to line maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-22 08:23 | 2024-02-22 17:01 | 8:38 | S/O | Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-23 08:29 | 2024-02-23 17:13 | 8:44 | S/O | Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-24 08:20 | 2024-02-24 16:43 | 8:23 | S/O | Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-25 08:14 | 2024-02-25 16:51 | 8:37 | S/O | Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-26 08:29 | 2024-02-26 17:59 | 9:30 | D/W | Maintenance work. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-02-27 08:31 | 2024-02-27 18:03 | 9:32 | D/W | Maintenance work. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-01 | 2024-02-01 11:22 | 2024-02-01 17:15 | 5:53 | S/O | Oil leakage maintenance of CT (b phase) | 0 | 0 | Power interruption
Benapole 132/33kV Grid Sub-Station | Jashore-1 | 2024-02-17 08:11 | 2024-02-17 17:08 | 8:57 | S/O | Schedule Shutdoown | 50 | 447.5 | Power interruption
Benapole 132/33kV Grid Sub-Station | Jashore-2 | 2024-02-17 08:11 | 2024-02-17 17:08 | 8:57 | S/O | Schedule Shutdoown | 50 | 447.5 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-02-27 14:02 | 2024-02-27 15:20 | 1:18 | D/W | Trasnsformer-1 replacement Work. | 20 | 26 | Power interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-20 11:40 | 2024-02-20 17:33 | 5:53 | D/W | TOWER AND LINE CONSTRUCTION WORK BY NWPGCL | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-21 08:18 | 2024-02-21 16:51 | 8:33 | S/O | Orion- Goalpara 132 kv line Shutdown by NWPGCL. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-22 08:16 | 2024-02-22 16:56 | 8:40 | S/O | NWPGCL taken SD | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-23 08:26 | 2024-02-23 17:14 | 8:48 | S/O | Maintenence works | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-24 08:17 | 2024-02-24 16:45 | 8:28 | S/O | Maintenence works | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-25 08:16 | 2024-02-25 16:48 | 8:32 | S/O | for stringing work by NWPGCL | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-26 08:20 | 2024-02-26 17:59 | 9:39 | S/O | Line construction by NWPGCL | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-02-27 08:31 | 2024-02-27 18:02 | 9:31 | S/O | Maintenence works. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2024-02-20 09:47 | 2024-02-27 19:36 | 177:49 | D/W | Shutdown by NWZPCL for Project work. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E07 Gollamari-Gopalgonj Line - 2 | 2024-02-20 09:48 | 2024-02-27 19:37 | 177:49 | D/W | Shutdown by NWZPCL for Project work. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-1 | 2024-02-10 06:59 | 2024-02-10 09:51 | 2:52 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-2 | 2024-02-10 07:00 | 2024-02-10 09:52 | 2:52 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-4 | 2024-02-24 08:49 | 2024-02-24 16:37 | 7:48 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-1 | 2024-02-28 07:22 | 2024-02-28 18:10 | 10:48 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-2 | 2024-02-29 08:45 | 2024-02-29 17:41 | 8:56 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2024-02-06 09:31 | 2024-02-06 17:25 | 7:54 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2024-02-07 08:22 | 2024-02-07 19:32 | 11:10 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2024-02-08 07:50 | 2024-02-08 15:59 | 8:09 | S/O | Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-03 | 2024-02-15 08:26 | 2024-02-15 17:47 | 9:21 | S/O | ANNUAL MAINTENANCE. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-03 | 2024-02-24 08:40 | 2024-02-24 16:36 | 7:56 | S/O | Annual maintenance. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2024-02-15 08:27 | 2024-02-15 13:36 | 5:09 | S/O | Annual maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2024-02-24 08:40 | 2024-02-24 16:37 | 7:57 | S/O | Annual maintenance. | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | 100MW ERBL Solar PS | 2024-02-12 16:18 | 2024-02-12 19:06 | 2:48 | S/O | Annual maintenance Work. | 20 | 56 | Power interruption
Narail 132/33kV Grid Sub-Station | Magura 1 | 2024-02-10 07:55 | 2024-02-10 16:08 | 8:13 | S/O | Magura ckt 1,2 cut off condition due to Jhenaidah bus shutdown(annual maintenance) so narail 132/33 kv s/s is in death condition. | 28 | 230.0667 | Power interruption
Narail 132/33kV Grid Sub-Station | Magura 2 | 2024-02-10 07:55 | 2024-02-10 16:08 | 8:13 | S/O | Magura ckt 1,2 cut off condition due to Jhenaidah bus shutdown(annual maintenance) so narail 132/33 kv s/s is in death condition. | 28 | 230.0667 | Power interruption
Noapara 132/33kV Grid Sub-Station | Jashore-1 | 2024-02-17 08:12 | 2024-02-17 17:11 | 8:59 | S/O | Maintenance work of Jashore Grid Sub-station. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | Jashore-2 | 2024-02-17 08:13 | 2024-02-17 17:11 | 8:58 | S/O | Maintenance work of Jashore Grid Sub-station. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-1 | 2024-02-03 08:58 | 2024-02-03 16:18 | 7:20 | S/O | Annual Maintenance-2024 | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-1 | 2024-02-04 08:53 | 2024-02-04 16:35 | 7:42 | S/O | annual maintenance-2024 | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-2 | 2024-02-07 08:13 | 2024-02-07 19:36 | 11:23 | S/O | Annual Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-2 | 2024-02-08 08:23 | 2024-02-08 17:23 | 9:00 | S/O | Annual Maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-2 | 2024-02-11 08:12 | 2024-02-11 16:34 | 8:22 | S/O | Annual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-01 | 2024-02-05 08:39 | 2024-02-05 17:34 | 8:55 | S/O | anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-01 | 2024-02-06 08:29 | 2024-02-06 20:12 | 11:43 | S/O | Anual maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-02 | 2024-02-10 08:20 | 2024-02-10 17:00 | 8:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2024-02-20 09:01 | 2024-02-20 11:24 | 2:23 | D/W | Faulty energy meter change | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-1 | 2024-02-06 09:32 | 2024-02-06 17:25 | 7:53 | S/O | Gopalgonj line-1 annual dead line checking work | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-1 | 2024-02-07 08:24 | 2024-02-07 19:31 | 11:07 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-1 | 2024-02-08 07:51 | 2024-02-08 15:58 | 8:07 | S/O | Due to Annual Maintenance | 0 | 0 | No interruption
|  |  | Total : | 748:07 |  | Unserved Energy: |  | 1437.1333
HVDC Grid Circle :
BIPTC | Baharampur-4 | 2024-02-01 12:33 | 2024-02-02 02:32 | 13:59 | S/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | PBEL(Genaration Line) | 2024-02-16 00:06 | 2024-02-16 00:06 | 0:00 | S/O | Disconnect PBEL for expired of contract. | 0 | 0 | No interruption
Bhangura 132/33kV Grid Sub-Station | Bhangura-Bhagabari ckt-1 | 2024-02-02 09:27 | 2024-02-02 16:49 | 7:22 | S/O | A/M | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2024-02-07 08:58 | 2024-02-07 17:27 | 8:29 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-01 06:57 | 2024-02-01 17:26 | 10:29 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-02 07:17 | 2024-02-02 18:38 | 11:21 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-03 07:19 | 2024-02-03 18:49 | 11:30 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-04 07:13 | 2024-02-04 17:59 | 10:46 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-05 07:45 | 2024-02-05 18:48 | 11:03 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-06 07:30 | 2024-02-06 18:52 | 11:22 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-07 07:37 | 2024-02-07 19:23 | 11:46 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-08 08:21 | 2024-02-08 20:33 | 12:12 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-09 07:35 | 2024-02-09 18:52 | 11:17 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-10 08:14 | 2024-02-10 18:56 | 10:42 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-11 07:58 | 2024-02-11 18:40 | 10:42 | D/W | Project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-12 07:52 | 2024-02-12 19:04 | 11:12 | D/W | project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-02-13 08:02 | 2024-02-13 17:23 | 9:21 | D/W | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -1 | 2024-02-08 07:43 | 2024-02-08 17:42 | 9:59 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2024-02-04 09:23 | 2024-02-04 10:04 | 0:41 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2024-02-05 15:52 | 2024-02-05 16:49 | 0:57 | S/O | None | 28 | 26.6 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2024-02-04 09:23 | 2024-02-04 10:04 | 0:41 | S/O | A/M | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2024-02-05 15:52 | 2024-02-05 16:49 | 0:57 | S/O | None | 28 | 26.6 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Jhenaidah (Old) Ckt-1 | 2024-02-10 08:26 | 2024-02-10 15:20 | 6:54 | S/O | 132kv Jhenaidah old S/S Bus Shutdown | 35 | 241.5 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Jhenaidah (Old) Ckt-2 | 2024-02-10 08:26 | 2024-02-10 15:45 | 7:19 | S/O | 132kv Jhenaidah old S/S Bus Shutdown | 35 | 256.0833 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Jhenaidah (Old) Ckt-3 | 2024-02-10 08:27 | 2024-02-10 15:20 | 6:53 | S/O | 132kv Jhenaidah old S/S Bus Shutdown | 35 | 240.9167 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-1 | 2024-02-28 09:38 | 2024-02-28 10:11 | 0:33 | D/W | Khulna ckt -1 d/s change | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2024-02-17 08:18 | 2024-02-17 16:35 | 8:17 | S/O | Annual Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-2 | 2024-02-17 08:30 | 2024-02-17 16:40 | 8:10 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia -Bheramara-1 | 2024-02-09 08:18 | 2024-02-09 14:58 | 6:40 | S/O | A/M | 40 | 266.6667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Bheramara-2 | 2024-02-09 08:18 | 2024-02-09 14:59 | 6:41 | S/O | A/M | 40 | 267.3333 | Power interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Jhenaidah-1 | 2024-02-09 08:17 | 2024-02-09 14:59 | 6:42 | S/O | A/M | 40 | 268 | Power interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia-Jhenaidah-2 | 2024-02-09 08:17 | 2024-02-09 15:00 | 6:43 | S/O | A/M | 40 | 268.6667 | Power interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. - 2 | 2024-02-10 08:02 | 2024-02-10 16:40 | 8:38 | S/O | Annual Maintenance. | 35 | 302.1667 | Power interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. -1 | 2024-02-10 08:01 | 2024-02-10 16:04 | 8:03 | S/O | Annual Maintenance. | 35 | 281.75 | Power interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Ishwardi Line | 2024-02-11 08:50 | 2024-02-12 13:32 | 28:42 | S/O | A/M | 0 | 0 | No interruption
|  |  | Total : | 297:03 |  | Unserved Energy: |  | 2446.2833
Bogura Grid Circle :
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2024-02-09 06:50 | 2024-02-09 08:52 | 2:02 | D/W | Project Work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2024-02-09 06:52 | 2024-02-09 08:53 | 2:01 | D/W | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2024-02-05 08:54 | 2024-02-05 17:05 | 8:11 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2024-02-06 09:30 | 2024-02-06 15:32 | 6:02 | D/W | Project work at 230Kv Bogura(W) S/S. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2024-02-24 08:19 | 2024-02-24 13:46 | 5:27 | S/O | Scada intrgration | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2024-02-25 08:47 | 2024-02-25 13:46 | 4:59 | S/O | scada INTEGRATION | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-1 | 2024-02-09 06:29 | 2024-02-09 09:35 | 3:06 | D/W | Design,supply,erection,testing, commissioning and integration with NLDC of 13 nos new grid sub stations on turnkey basis project work | 30 | 93 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-1 | 2024-02-23 07:05 | 2024-02-23 08:39 | 1:34 | S/O | 132Kv main bus shutdown for to connect the bus jumper between existing naogaon-1 and new naogaon-2 for upper bus conductor stringing under g to g project work | 45 | 70.5 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-1 | 2024-02-24 06:06 | 2024-02-24 06:06 | 0:00 | S/O | 132Kv naogaon joypurhat main line shutdown for conducting from terminal tower to joypurhat grid sub station ganty stringing under g to g project work. | 40 | 0 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-2 | 2024-02-24 06:08 | 2024-02-24 14:49 | 8:41 | S/O | 132Kv naogaon joypurhat main line shutdown for conducting from terminal tower to joypurhat grid sub station ganty stringing under g to g project work. | 45 | 390.75 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari-2 | 2024-02-01 08:29 | 2024-02-01 15:52 | 7:23 | S/O | Annual Maintenance Work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2024-02-24 06:22 | 2024-02-24 17:07 | 10:45 | S/O | S/D performed by oder of ALDC Bogura. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2024-02-24 06:23 | 2024-02-24 17:09 | 10:46 | S/O | S/D performed by oder of ALDC Bogura. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2024-02-24 06:07 | 2024-02-24 14:47 | 8:40 | S/O | S/D performed by oder of ALDC Bogura. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-02-15 17:36 | 2024-02-17 12:23 | 42:47 | D/W | Rahanpur ckt -01 & 02 commissioning. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2024-02-28 08:40 | 2024-02-28 09:19 | 0:39 | S/O | Rahanpur ckt -01 & 02 commissioning. | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2024-02-25 08:47 | 2024-02-25 13:46 | 4:59 | S/O | For scada maintenance | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2024-02-24 06:46 | 2024-02-24 10:06 | 3:20 | D/W | Due to project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -2 | 2024-02-24 06:46 | 2024-02-24 10:07 | 3:21 | D/W | Due to project work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | SNWPCL (Unit-04) | 2024-02-08 08:56 | 2024-02-08 16:45 | 7:49 | S/O | Maintenance work of SNWPCL | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-01 | 2024-02-04 08:35 | 2024-02-04 17:25 | 8:50 | S/O | Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-01 | 2024-02-05 08:56 | 2024-02-05 18:02 | 9:06 | D/W | Sreepur 230 KV Circuit-1 shout down due to project work at Sreepur end. Shout down taken by SDE,NLDC, Dhaka. | 0 | 0 | Power interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2024-02-06 09:07 | 2024-02-06 18:38 | 9:31 | D/W | Maintenance | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2024-02-07 09:00 | 2024-02-07 18:26 | 9:26 | D/W | Project work | 0 | 0 | No interruption
|  |  | Total : | 179:25 |  | Unserved Energy: |  | 554.25
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 4263:24 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:February 2024
| Area | Previous Month (January' 2023) |  |  |  | Current Month (February '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 11 | 18 | 226 | 255 | 25 | 16 | 171 | 213
2 | Dhaka (South) Grid Circle. | 26 | 25 | 119 | 170 | 69 | 33 | 125 | 227
3 | Chattogram Grid Circle. | 1 | 4 | 116 | 121 | 6 | 16 | 108 | 130
4 | Cumilla Grid Circle. | 1 | 13 | 122 | 136 | 8 | 9 | 123 | 140
5 | Khulna Grid Circle. | 4 | 6 | 113 | 123 | 8 | 10 | 86 | 104
6 | HVDC Grid Circle | 4 | 6 | 95 | 105 | 6 | 8 | 75 | 89
7 | Bogura Grid Circle. | 6 | 11 | 74 | 91 | 7 | 9 | 67 | 83
8 | Others | Total number of Total: 2; Total number of T: 1; Total number of Total: 1
9 | Total | 53 | 83 | 865 | 1003 | 130 | 101 | 755 | 987
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:February 2023
| Area | Previous Month (January' 2023) |  |  |  | Current Month (February '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 212.8 | 603.17 | 1085.63 | 1901.6 | 374.21 | 95.83 | 4627.41 | 5097.45
2 | Dhaka (South) Grid Circle. | 823.02 | 29.75 | 152.67 | 1005.44 | 773.94 | 35 | 1591.66 | 2400.6
3 | Chattogram Grid Circle. |  | 5.13 | 341.4 | 346.53 | 106.62 | 149.2 | 4266.54 | 4522.36
4 | Cumilla Grid Circle. | 4.67 | 1.33 | 207.3 | 213.3 | 22.6 | 1.17 | 271.53 | 295.3
5 | Khulna Grid Circle. | 24.5 | 33 | 415.52 | 473.02 | 39.68 | 287.75 | 2948.1 | 3275.53
6 | HVDC Grid Circle | 723.25 | 24.81 | 2885.4 | 3633.46 |  | 438 | 4552.58 | 4990.58
7 | Bogura Grid Circle. | 39.05 | 336.97 | 2434.69 | 2810.71 | 32.66 | 6.67 | 1582.85 | 1622.18
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1827.29 | 1034.16 | 7522.61 | 10384.06 | 1349.71 | 1013.62 | 19840.67 | 22204
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:February 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 12 | 17 | 29 | 5 | 4 | 20 | 3256.64
2 | Dhaka (South) | 5031.6 | 17 | 1 | 18 | 8 | 8 | 2 | 880.2
3 | Chattogram | 2042 | 7 | 5 | 12 | 2 | 1 | 9 | 4161.46
4 | Khulna | 2434 | 8 | 13 | 21 | 4 | 2 | 15 | 1838.4
5 | HVDC | 5954.3 | 2 | 9 | 11 |  |  | 11 | 2544.3
6 | Bogura | 3145.6 | 3 | 10 | 13 | 3 |  | 10 | 1056.85
7 | Cumilla | 2981 | 2 | 7 | 9 | 3 | 1 | 5 | 270.37
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 14008.22
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.95%
4 | Khulna | 99.98%
5 | HVDC | 99.99% | [6 empty] | Executive Engineer
6 | Bogura | 99.98% | [6 empty] | Information Management Division
7 | Cumilla | 99.99% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:February 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 12 | 16 | 3 | 2 | 11 | 1840.82
2 | Dhaka (South) | 990.29 | - | 3 | 2 | 8 | 2 | 1 | 3 | 1520.4
3 | Chattogram | 917 | - | 2 | 4 | 6 | 1 |  | 5 | 360.88
4 | Khulna | 1238.4 | - | - | 6 | 6 | - | - | 6 | 1437.13
5 | HVDC | 1325 | - |  | 11 | 11 | - | 2 | 9 | 2446.2833
6 | Bogura | 1803.3 | - | 1 | 3 | 4 | 1 |  | 3 | 565.33
7 | Cumilla | 1648.16 | - | 2 | 1 | 3 | 2 | 1 |  | 24.93
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 8195.7733
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.98%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:February 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-02-01 | 24 | - | 2 | 58 min | 1 | 34 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:February 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:18 | 19.5
Mirzapur 132/33kV GIS Grid Sub-Station | 9 | 5:20 | 167.07
Mymensingh 132/33kV Grid Sub-Station | 1 | 1:46 | 26.5
Rajendrapur 132/33kV Grid Sub-Station | 2 | 3:20 | 93.33
Agargaon 230/132kV Grid Sub-Station | 1 | 0:22 | 52.8
Tangail 132/33kV Grid Sub-Station | 1 | 0:15 | 70.5
Tongi 230/132/33kV Grid Sub-Station | 2 | 0:44 | 40.33
Bhaluka 132/33kV Grid Sub-Station | 2 | 13:28 | 1077.33
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:53 | 26.5
Joydebpur 132/33kV Grid Sub-Station | 1 | 6:44 | 67.3333
Kodda 132/33kV Grid Sub-Station | 1 | 5:16 | 200.1333
Manikganj 132/33kV Grid Sub-Station | 11 | 94:34 | 1558.1
Savar 132/33kV Grid Sub-Station | 1 | 0:25 | 20.8333
Dhamrai 132/33kV Grid Sub-Station | 1 | 0:48 | 8
Joydebpur 132/33kV Grid Sub-Station | 2 | 27:10 | 202.73
Manikganj 132/33kV Grid Sub-Station | 9 | 71:43 | 1466.45
Bhulta 132/33kV Grid Sub-Station | 1 | 0:08 | 10.6667
Hasnabad 132/33kV Grid Substation | 2 | 1:04 | 20.77
Munshiganj 132/33kV Grid Sub-Station | 2 | 12:40 | 202.67
Siddhirganj 230/132kV Grid Sub-Station | 2 | 2:20 | 124.6
Sonargaon 132/33kV Grid Sub-Station | 8 | 5:27 | 200.43
Siddhirganj 132/33kV Grid Sub-Station | 4 | 1:47 | 242.33
Sonargaon 132/33kV Grid Sub-Station | 2 | 0:28 | 7.47
Bhulta 132/33kV Grid Sub-Station | 1 | 5:05 | 203.3333
Meghnaghat 230/132kV Grid Sub-Station | 2 | 27:46 | 1388.33
Dohazari 132/33kV Grid Sub-Station | 2 | 4:14 | 132.87
Kalurghat 132/33kV Grid Sub-Station | 2 | 2:00 | 6
Madunaghat 132/33kV Grid Sub-Station | 3 | 4:07 | 43.73
Dohazari 132/33kV Grid Sub-Station | 2 | 1:19 | 73.22
Coxsbazar 132/33kV Grid Sub-Station | 1 | 1:37 | 32.3333
Juldah 132/33kV Grid Sub-Station | 4 | 166:24 | 3946.53
Coxsbazar 132/33kV Grid Sub-Station | 1 | 1:10 | 25.6667
Juldah 132/33kV Grid Sub-Station | 3 | 14:46 | 262
Brahmanbaria 132/33kV Grid Sub-Station | 2 | 0:19 | 8.17
Sunamganj 132/33kV Grid Sub-Station | 2 | 0:36 | 15.6
Chandpur 132/33kV Grid Sub-Station | 1 | 4:25 | 57.4167
Chowmuhani 132/33kV Grid Sub-Station | 3 | 10:51 | 162.75
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 0:57 | 19
Feni 132/33kV Grid Sub-Station | 1 | 0:04 | 1.2
Kulaura 132/33kV Grid Sub-Station | 1 | 2:11 | 21.8333
Sylhet 132/33kV Grid Sub-Station | 1 | 0:35 | 9.3333
Gopalganj 132/33kV Grid Sub-Station | 2 | 13:41 | 287.75
Khulna (C) 132/33kV Grid Sub-Station | 3 | 1:14 | 20.73
Rajbari 132/33kV Grid Sub-Station | 3 | 1:05 | 18.95
Barishal 132/33kV Grid Sub-Station | 4 | 5:59 | 153.4
Benapole 132/33kV Grid Sub-Station | 2 | 16:27 | 427.7
Bhandaria 132/33kV Grid Sub-Station | 2 | 2:42 | 42.93
Narail 132/33kV Grid Sub-Station | 3 | 17:49 | 478.93
Satkhira 132/33kV Grid Sub-Station | 2 | 9:36 | 408
Benapole 132/33kV Grid Sub-Station | 2 | 17:54 | 895
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:18 | 26
Mongla 132/33kV Grid Sub-Station | 1 | 2:48 | 56
Narail 132/33kV Grid Sub-Station | 2 | 16:26 | 460.13
Kushtia 132/33kV Grid Sub-Station | 2 | 11:18 | 438
Jashore 132/33kV Grid Sub-Station | 4 | 18:46 | 575.35
Jhenaidah 132/33kV Grid Sub-Station | 1 | 7:07 | 249.0833
Jhenaidah 132/33kV Grid Sub-Station | 1 | 7:04 | 233.2
Kushtia 132/33kV Grid Sub-Station | 1 | 10:34 | 422.6667
Kushtia 132/33kV Grid Sub-Station | 1 | 7:25 | 296.6667
Magura 132/33kV Grid Sub-Station | 1 | 8:14 | 329.3333
Ishurdi 132/33kV Grid Sub-Station | 2 | 1:54 | 53.2
Jhenaidah 230/132kV Grid Sub-Station | 3 | 21:06 | 738.5
Kushtia 132/33kV Grid Sub-Station | 4 | 26:46 | 1070.67
Magura 132/33kV Grid Sub-Station | 1 | 8:38 | 302.1667
Magura 132/33kV Grid Sub-Station | 1 | 8:03 | 281.75
Niamatpur 132/33kV Grid Sub-Station | 1 | 0:13 | 3.25
Rajshahi 132/33kV Grid Sub-Station | 2 | 1:04 | 25
Kurigram 132/33kV Grid Sub-Station | 1 | 0:19 | 11.0833
Bogura 132/33kV Grid Sub-Station | 1 | 56:32 | 452.2667
Naogaon 132/33kV Grid Sub-Station | 1 | 2:07 | 63.5
Rajshahi 132/33kV Grid Sub-Station | 5 | 9:08 | 231.4
Sirajganj 132/33kV Grid Sub-Station | 2 | 8:50 | 236.83
Thakurgaon 132/33kV Grid Sub-Station | 1 | 3:43 | 44.6
Joypurhat 132/33kV Grid Sub-Station | 3 | 13:21 | 554.25
Total Unserved energy : | 166 | 845:37 | 22203.98
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:February 2024
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2024-02-20 18:30 | 28
2 | Agargaon 230/132kV Grid Sub-Station | 2024-02-15 15:00 | 83
3 | Banani 132/33kV Grid Sub-Station | 2024-02-21 14:00 | 36
4 | Bangabhaban 132/33kV Grid Sub-Station | 2024-02-29 12:00 | 15
5 | Bashundhara 132/33kV Grid Sub-Station | 2024-02-28 13:00 | 142
6 | BashundharaCement 132/33kV Sub-Station | 2024-02-03 16:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2024-02-20 12:00 | 260
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2024-02-19 18:00 | 110
9 | Charsaidpur 132/33kV Sub-Station | 2024-02-22 23:00 | 43
10 | Dhaka University 132/33kV Grid Sub-Station | 2024-02-22 12:00 | 24
11 | Dhamrai 132/33kV Grid Sub-Station | 2024-02-12 08:00 | 134
12 | Dhanmondi 132/33kV Grid Sub-Station | 2024-02-22 13:00 | 117
13 | Fatullah 132/33kV Grid Sub-Station | 2024-02-20 12:00 | 56
14 | Ghorashal 230/132/33kV Sub-Station | 2024-02-24 19:00 | 82
15 | Gulshan 132/33kV Grid Sub-Station | 2024-02-29 15:00 | 86
16 | HaripurSBU 132/33kV Sub-Station | 2024-02-20 12:00 | 184
17 | Hasnabad 132/33kV Grid Substation | 2024-02-19 13:00 | 74
18 | Joydebpur 132/33kV Grid Sub-Station | 2024-02-19 18:30 | 157
19 | Kabirpur 132/33kV Grid Sub-Station | 2024-02-18 12:00 | 258
20 | Kallyanpur 132/33kV Grid Sub-Station | 2024-02-20 18:00 | 90
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2024-02-22 13:00 | 51
22 | Kazla 132/33kV Grid Sub-Station | 2024-02-07 13:00 | 94
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2024-02-17 18:30 | 70
24 | Kodda 132/33kV Grid Sub-Station | 2024-02-19 18:30 | 285
25 | Lalbag 132/33kV Grid Sub-Station | 2024-02-28 13:00 | 84
26 | Madanganj 132/33kV Grid Sub-Station | 2024-02-07 21:00 | 42
27 | Madartek 132/33kV Grid Sub-Station | 2024-02-16 13:00 | 65.69
28 | Manikganj 132/33kV Grid Sub-Station | 2024-02-28 18:30 | 97
29 | Maniknagar 132/33kV Grid Sub-Station | 2024-02-20 13:00 | 60
30 | Matuail 132/33kV Grid Sub-Station | 2024-02-28 16:00 | 61.2
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2024-02-20 12:00 | 94
32 | Mirpur 132/33kV Grid Sub-Station | 2024-02-28 19:00 | 103
33 | MI_Cement 132/33kV Grid Sub-Station | 2024-02-07 15:00 | 12.8
34 | Mogbazar 132/33kV Grid Sub-Station | 2024-02-22 15:00 | 103.9
35 | Motijheel 132/33kV Grid Sub-Station | 2024-02-28 13:00 | 35
36 | Munshiganj 132/33kV Grid Sub-Station | 2024-02-22 14:00 | 72
37 | Narinda 132/33kV Grid Sub-Station | 2024-02-03 13:00 | 56
38 | Narshingdi 132/33kV Grid Sub-Station | 2024-02-10 19:00 | 153
39 | Nawabganj 132/33kV Grid Sub-Station | 2024-02-23 13:00 | 37.9
40 | New Tongi 132/33kV Grid Sub-Station | 2024-02-20 12:00 | 20.5
41 | Postogola 132/33kV Grid Sub-Station | 2024-02-06 13:00 | 44
42 | Purbachal 132/33kV Grid Sub-Station | 2024-02-02 12:00 | 15
43 | Rahim Steel 132/33kV Sub-Station | 2024-02-01 12:00 | 53
44 | Rajendrapur 132/33kV Grid Sub-Station | 2024-02-17 12:00 | 94
45 | Satmasjid 132/33kV Grid Sub-Station | 2024-02-22 14:00 | 90
46 | Savar 132/33kV Grid Sub-Station | 2024-02-29 15:00 | 176
47 | SevenRings 132/11kV Sub-Station | 2024-02-22 19:30 | 25.43
48 | ShahCement 132/33kV Grid Sub-Station | 2024-02-08 09:00 | 36
49 | Shitalakhya 132/33kV Grid Sub-Station | 2024-02-29 12:00 | 85.6
50 | Shyampur 132/33kV Grid Sub-Station | 2024-02-28 11:00 | 172
51 | Siddhirganj 132/33kV Grid Sub-Station | 2024-02-19 12:00 | 108
52 | Sonargaon 132/33kV Grid Sub-Station | 2024-02-04 10:00 | 113
53 | Sreepur 230/132/33kV Grid Sub-Station | 2024-02-25 12:00 | 64
54 | Srinagar 132/33kV Grid Sub-Station | 2024-02-21 21:00 | 31.4
55 | Tongi 230/132/33kV Grid Sub-Station | 2024-02-15 11:00 | 144
56 | Ullon 132/33kV Grid Sub-Station | 2024-02-22 13:00 | 37
57 | Uttara 132/33kV Grid Sub-Station | 2024-02-25 18:00 | 53
58 | UttaraNew 132/33kV Grid Sub-Station | 2024-02-02 13:00 | 34
59 | Zigatola 132/33kV Grid Sub-Station | 2024-02-12 18:30 | 58
60 | Agrabad 132/33kV Grid Sub-Station | 2024-02-29 22:00 | 68
61 | AKS 132/33kV Grid Sub-Station | 2024-02-28 13:00 | 19
62 | AKSML 230/33kV Grid Sub-Station | 2024-02-29 03:00 | 211
63 | Bakulia 132/33kV Grid Sub-Station | 2024-02-10 19:30 | 90
64 | Baroaulia 132/33kV Grid Sub-Station | 2024-02-13 11:00 | 76
65 | Baroirhat 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 48
66 | BSRM 230/33kV Grid Sub-Station | 2024-02-23 19:00 | 143
67 | Chandraghona 132/33kV Grid Sub-Station | 2024-02-01 18:00 | 24
68 | Coxsbazar 132/33kV Grid Sub-Station | 2024-02-29 18:30 | 113
69 | Dohazari 132/33kV Grid Sub-Station | 2024-02-24 19:30 | 80
70 | GPH 230/33kV Grid Sub-Station | 2024-02-29 18:00 | 102
71 | Halishahar 132/33kV Grid Sub-Station | 2024-02-29 15:00 | 86.5
72 | Hathazari 230/132/33kV Grid Sub-Station | 2024-02-20 13:00 | 70
73 | Juldah 132/33kV Grid Sub-Station | 2024-02-25 12:00 | 23
74 | Kalurghat 132/33kV Grid Sub-Station | 2024-02-14 12:00 | 29
75 | Khagrachori 132/33kV Grid Sub-Station | 2024-02-04 18:00 | 28
76 | Khulshi 132/33kV Grid Sub-Station | 2024-02-29 19:00 | 156
77 | KSRM 132/33kV Grid Sub-Station | 2024-02-12 08:00 | 41
78 | Madunaghat 132/33kV Grid Sub-Station | 2024-02-27 22:00 | 47
79 | Matarbari 132/33kV Sub-Station | 2024-02-25 19:00 | 46
80 | Mirsorai 230/33kV Grid Sub-Station | 2024-02-04 09:00 | 5
81 | Modern Steel 132/11kV Grid Sub-Station | 2024-02-01 | 0
82 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2024-02-07 19:00 | 27
83 | Rangamati 132/33kV Grid Sub-Station | 2024-02-22 18:30 | 14
84 | Shahmirpur 132/33kV Grid Sub-Station | 2024-02-06 18:00 | 53
85 | Shikalbaha 132/33kV Sub-Station | 2024-02-25 12:00 | 27
86 | Sholosohor 132/33kV Grid Sub-Station | 2024-02-24 15:00 | 36
87 | SSM 132/33kV Grid Sub-Station | 2024-02-05 03:00 | 16
88 | TK chemical 132kV Grid Sub-Station | 2024-02-29 19:00 | 22.3
89 | Ashuganj 230/132/33kV Sub-Station | 2024-02-14 12:00 | 91
90 | Brahmanbaria 132/33kV Grid Sub-Station | 2024-02-21 20:00 | 117
91 | Chandpur 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 46
92 | Chauddagram 132/33kV Grid Sub-Station | 2024-02-16 12:00 | 51
93 | Chowmuhani 132/33kV Grid Sub-Station | 2024-02-10 19:00 | 154
94 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2024-02-21 19:30 | 126
95 | Cumilla(S) 132/33kV Grid Sub-Station | 2024-02-14 14:00 | 134
96 | Daudkandi 132/33kV Grid Sub-Station | 2024-02-01 19:30 | 111
97 | Feni 132/33kV Grid Sub-Station | 2024-02-29 18:30 | 86
98 | Kachua 132/33kV Grid Sub-Station | 2024-02-03 18:00 | 53
99 | PHP 132/33kV Sub-Station | 2024-02-13 14:00 | 11
100 | Ramganj 132/33kV Grid Sub-Station | 2024-02-02 13:00 | 90
101 | Bhaluka 132/33kV Grid Sub-Station | 2024-02-28 18:30 | 132
102 | Jamalpur 132/33kV Grid Sub-Station | 2024-02-17 20:00 | 155
103 | Kishoreganj 132/33kV Grid Sub-Station | 2024-02-12 19:00 | 117
104 | Mirzapur 132/33kV GIS Grid Sub-Station | 2024-02-15 07:00 | 56
105 | Mymensingh 132/33kV Grid Sub-Station | 2024-02-09 13:00 | 206
106 | Netrakona 132/33kV Grid Sub-Station | 2024-02-09 08:00 | 134
107 | Sherpur 132/33kV Grid Sub-Station | 2024-02-02 18:30 | 130
108 | Tangail 132/33kV Grid Sub-Station | 2024-02-17 07:00 | 182
109 | Beanibazar 132/33kV Grid Sub-Station | 2024-02-24 18:30 | 44
110 | Chhatak 132/33kV Grid Sub-Station | 2024-02-10 18:00 | 23
111 | Fenchuganj 230/132/33kV Grid Sub-Station | 2024-02-10 18:30 | 30
112 | Kulaura 132/33kV Grid Sub-Station | 2024-02-10 18:00 | 32
113 | Shahjibazar 132/33kV Grid Sub-Station | 2024-02-19 21:00 | 95
114 | Sreemongol 132/33kV Grid Sub-Station | 2024-02-10 13:00 | 55
115 | Sunamganj 132/33kV Grid Sub-Station | 2024-02-15 19:00 | 38
116 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2024-02-29 20:00 | 24
117 | Sylhet 132/33kV Grid Sub-Station | 2024-02-24 18:00 | 104
118 | Bagerhat 132/33kV Grid Sub-Station | 2024-02-17 19:00 | 74
119 | Benapole 132/33kV Grid Sub-Station | 2024-02-17 18:30 | 74
120 | Bheramara(GK) 132/33kV Grid Sub-Station | 2024-02-01 18:00 | 47
121 | Chuadanga 132/33kV Grid Sub-Station | 2024-02-10 18:30 | 83
122 | Faridpur 132/33kV Grid Sub-Station | 2024-02-07 19:00 | 114
123 | Goalpara 132/33kV Grid Sub-Station | 2024-02-09 13:00 | 28
124 | Gollamari 132/33kV Grid Sub-Station | 2024-02-24 12:00 | 49
125 | Gopalganj 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 81.6
126 | Jashore 132/33kV Grid Sub-Station | 2024-02-12 13:00 | 117
127 | Jhenaidah 132/33kV Grid Sub-Station | 2024-02-10 18:30 | 112
128 | Khulna (C) 132/33kV Grid Sub-Station | 2024-02-02 13:00 | 90
129 | Kushtia 132/33kV Grid Sub-Station | 2024-02-20 18:30 | 114
130 | Madaripur 132/33kV Grid Sub-Station | 2024-02-21 21:00 | 69
131 | Magura 132/33kV Grid Sub-Station | 2024-02-10 18:30 | 54
132 | Mongla 132/33kV Grid Sub-Station | 2024-02-03 13:00 | 42
133 | Narail 132/33kV Grid Sub-Station | 2024-02-03 18:30 | 44
134 | Noapara 132/33kV Grid Sub-Station | 2024-02-11 18:30 | 50
135 | Rajbari 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 52
136 | Satkhira 132/33kV Grid Sub-Station | 2024-02-17 19:00 | 101
137 | Shariatpur 132/33kV Grid Sub-Station | 2024-02-13 21:00 | 53
138 | Barguna 132/33kV Grid Sub-Station | 2024-02-24 21:00 | 16
139 | Barishal 132/33kV Grid Sub-Station | 2024-02-29 13:00 | 95
140 | Barishal 230/132kV Grid Sub-Station | 2024-02-12 18:30 | 72
141 | Bhandaria 132/33kV Grid Sub-Station | 2024-02-24 19:00 | 36
142 | Borhanuddin 230/33kV Grid Sub-Station | 2024-02-25 20:00 | 54
143 | Patuakhali 132/33kV Grid Sub-Station | 2024-02-03 19:30 | 56.5
144 | Payra 400/132/33kV Grid Sub-Station | 2024-02-28 12:00 | 20
145 | Amnura 132/33kV Grid Sub-Station | 2024-02-12 09:00 | 63
146 | Bhangura 132/33kV Grid Sub-Station | 2024-02-29 08:00 | 32
147 | Bog-Sherpur 132/33kV Grid Sub-Station | 2024-02-20 09:00 | 68
148 | Bogura 132/33kV Grid Sub-Station | 2024-02-29 19:00 | 126
149 | Chapai 132/33kV Grid Sub-Station | 2024-02-14 12:00 | 63
150 | Ishurdi 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 53
151 | Joypurhat 132/33kV Grid Sub-Station | 2024-02-29 08:00 | 61
152 | Mahasthangarh 132/33kV Grid Sub-Station | 2024-02-24 08:00 | 72
153 | Naogaon 132/33kV Grid Sub-Station | 2024-02-24 10:00 | 114
154 | Natore 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 115
155 | Niamatpur 132/33kV Grid Sub-Station | 2024-02-16 18:30 | 122
156 | Pabna 132/33kV Grid Sub-Station | 2024-02-20 19:00 | 87
157 | Rajshahi 132/33kV Grid Sub-Station | 2024-02-17 13:00 | 113
158 | Rajshahi 230/132/33kV Grid Sub-Station | 2024-02-16 12:00 | 34
159 | Ruppur 132/11kV Grid Sub-Station | 2024-02-19 15:00 | 5
160 | Shahjadpur 132/33kV Grid Sub-Station | 2024-02-29 07:00 | 70
161 | Sirajganj 132/33kV Grid Sub-Station | 2024-02-06 19:00 | 96
162 | Ullahpara 132/33kV Grid Sub-Station | 2024-02-12 17:00 | 81
163 | Barapukuria 230/132/33kV Grid Sub-Station | 2024-02-03 09:00 | 60
164 | Jaldhaka 132/33kV Grid Sub-Station | 2024-02-29 08:00 | 69
165 | Kurigram 132/33kV Grid Sub-Station | 2024-02-07 18:30 | 66
166 | Lalmonirhat 132/33kV Grid Sub-Station | 2024-02-06 08:00 | 45
167 | Mithapukur 132/33kV Grid Sub-Station | 2024-02-01 08:00 | 54
168 | Palashbari 132/33kV Grid Sub-Station | 2024-02-21 08:00 | 103
169 | Panchagarh 132/33kV Grid Sub-Station | 2024-02-04 18:30 | 47
170 | Purbasadipur 132/33kV Grid Sub-Station | 2024-02-09 12:00 | 120
171 | Rangpur 132/33kV Grid Sub-Station | 2024-02-02 13:00 | 113
172 | Saidpur 132/33kV Grid Sub-Station | 2024-02-29 09:00 | 104
172 | Thakurgaon 132/33kV Grid Sub-Station | 2024-02-24 19:00 | 82
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:February 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 4385.88 | 2024-02-20 | 12:00
Chattogram | 1228 | 2024-02-28 | 19:00
Cumilla | 946 | 2024-02-29 | 18:30
Mymensingh | 970 | 2024-02-29 | 8:00
Sylhet | 395 | 2024-02-10 | 18:30
Khulna | 1295.6 | 2024-02-20 | 19:00
Barishal | 315.4 | 2024-02-22 | 21:00
Rajshahi | 1147.2 | 2024-02-29 | 19:00
Rangpur | 818 | 2024-02-03 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:February 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 421 | 2024-02-16 07:00 | 381 | 2024-02-19 12:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 412 | 2024-02-10 03:00 | 364 | 2024-02-19 12:00
3 | Bibiana 400/230kV Sub-Station | 400 | 426 | 2024-02-01 19:00 | 401 | 2024-02-03 12:00
4 | BIPTC | 400 | 411 | 2024-02-01 04:00 | 389 | 2024-02-12 13:00
5 | Bogura 400/230kV Grid Sub-Station | 400 | 415 | 2024-02-26 05:00 | 381 | 2024-02-20 08:00
6 | Gopalganj 400/132kV Grid Sub-Station | 400 | 419 | 2024-02-14 05:00 | 389 | 2024-02-19 10:00
7 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 413 | 2024-02-03 06:00 | 358 | 2024-02-19 12:00
8 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 419 | 2024-02-14 20:00 | 398 | 2024-02-25 16:00
9 | Payra 400kV Sub-Station | 400 | 422 | 2024-02-02 15:00 | 408 | 2024-02-18 12:00
| Rahanpur 400/132kV Grid Sub-Station | 400 | 421 | 2024-02-10 05:00 | 389 | 2024-02-08 11:00
| Rampal 400/230kV Grid Sub-Station | 400 | 419 | 2024-02-14 03:00 | 389 | 2024-02-14 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 250 | 2024-02-28 16:00 | 211 | 2024-02-19 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 239 | 2024-02-05 20:00 | 221 | 2024-02-29 22:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 241 | 2024-02-26 | 221 | 2024-02-08 10:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 228 | 2024-02-26 05:00 | 206 | 2024-02-12 08:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 246 | 2024-02-15 05:00 | 234 | 2024-02-04 15:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 245 | 2024-02-26 05:00 | 222 | 2024-02-01 12:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 238 | 2024-02-26 05:00 | 211 | 2024-02-08 11:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 242 | 2024-02-08 18:30 | 222 | 2024-02-21 23:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 244 | 2024-02-03 19:00 | 220 | 2024-02-19 12:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 248 | 2024-02-01 18:30 | 233 | 2024-02-15 11:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 246 | 2024-02-02 01:00 | 220 | 2024-02-19 13:00
12 | Ghorashal 230kV Switching Sub-Station | 230 | 242 | 2024-02-09 04:00 | 215 | 2024-02-19 12:00
13 | GPH 230/33kV Grid Sub-Station | 230 | 238 | 2024-02-02 09:00 | 219 | 2024-02-29 22:00
14 | Haripur 230/132kV Grid Sub-Station | 230 | 242 | 2024-02-26 04:00 | 212 | 2024-02-19 12:00
15 | Hasnabad 230/132kV Grid Sub-Station | 230 | 242 | 2024-02-03 18:30 | 211 | 2024-02-19 12:00
16 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 239 | 2024-02-08 18:30 | 219 | 2024-02-29 22:00
17 | Ishurdi 230/132kV Grid Sub-Station | 230 | 255 | 2024-02-16 06:00 | 224 | 2024-02-06 12:00
18 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 242 | 2024-02-26 01:00 | 220 | 2024-02-16 12:00
19 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 240 | 2024-02-10 03:00 | 211 | 2024-02-19 12:00
20 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 246 | 2024-02-26 01:00 | 224 | 2024-02-18 11:00
21 | Maniknagar 230/132kV Grid Sub-Station | 230 | 242 | 2024-02-02 18:00 | 210 | 2024-02-19 12:00
22 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 247 | 2024-02-03 | 219 | 2024-02-19 10:00
23 | Mirsorai 230/33kV Grid Sub-Station | 230 | 242 | 2024-02-03 19:00 | 221 | 2024-02-23 02:00
24 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 245 | 2024-02-26 05:00 | 224 | 2024-02-10 12:00
25 | Rampura 230/132kV Grid Sub-Station | 230 | 244 | 2024-02-10 03:00 | 213 | 2024-02-19 12:00
26 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 236 | 2024-02-11 18:30 | 219 | 2024-02-09 13:00
27 | Shyampur 230/132kV Grid Sub-Station | 230 | 243 | 2024-02-03 04:00 | 212 | 2024-02-19 12:00
28 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 244 | 2024-02-02 07:00 | 218 | 2024-02-19 15:00
29 | Sirajgonj 230 kV Switching Station | 230 | 247 | 2024-02-26 05:00 | 225 | 2024-02-06 12:00
30 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 241 | 2024-02-03 04:00 | 220 | 2024-02-19 12:00
31 | Tongi 230/132/33kV Grid Sub-Station | 230 | 244 | 2024-02-15 12:00 | 207 | 2024-02-19 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 |  | 132 | 139 | 2024-02-10 03:00 | 119 | 2024-02-19 11:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-02 09:00 | 126 | 2024-02-09 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-04 22:00 | 125 | 2024-02-24 17:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-05 18:30 | 122 | 2024-02-08 10:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 143 | 2024-02-09 05:00 | 130 | 2024-02-19 11:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-01 17:00 | 119 | 2024-02-22 12:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-02 13:00 | 126 | 2024-02-09 13:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 143 | 2024-02-01 19:00 | 120 | 2024-02-19 12:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-25 19:00 | 118 | 2024-02-19 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-01 19:00 | 126 | 2024-02-16 21:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-02 17:00 | 122 | 2024-02-24 20:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-07 22:00 | 127 | 2024-02-09 11:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-03 19:30 | 118 | 2024-02-09 13:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 144 | 2024-02-04 19:30 | 120 | 2024-02-19 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 139 | 2024-02-03 19:00 | 122 | 2024-02-19 10:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-02 04:00 | 130 | 2024-02-04 13:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-26 01:00 | 122 | 2024-02-13 12:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 135 | 2024-02-02 15:00 | 120 | 2024-02-19 12:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-02 15:00 | 122 | 2024-02-24 19:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 144 | 2024-02-26 05:00 | 129 | 2024-02-12 13:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 128 | 2024-02-04 12:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 131 | 2024-02-26 02:00 | 113 | 2024-02-03 15:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-26 05:00 | 122 | 2024-02-08 08:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-26 05:00 | 122 | 2024-02-08 10:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-09 05:00 | 124 | 2024-02-19 12:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 142 | 2024-02-09 05:00 | 123 | 2024-02-19 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-08 18:30 | 118 | 2024-02-09 13:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-02 08:00 | 128 | 2024-02-09 12:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-09 05:00 | 124 | 2024-02-08 11:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 141 | 2024-02-26 05:00 | 122 | 2024-02-18 17:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 143 | 2024-02-12 18:30 | 124 | 2024-02-23 21:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-03 02:00 | 130 | 2024-02-01 14:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-12 17:00 | 113 | 2024-02-09 12:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 04:00 | 122 | 2024-02-11 12:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 131 | 2024-02-16 09:00 | 113 | 2024-02-23 18:30
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 144 | 2024-02-03 19:00 | 125 | 2024-02-29 12:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-26 06:00 | 116 | 2024-02-15 12:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-09 05:00 | 118 | 2024-02-19 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 120 | 2024-02-18 16:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-26 05:00 | 122 | 2024-02-18 17:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-03 09:00 | 122 | 2024-02-23 21:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 130 | 2024-02-10 23:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-26 06:00 | 125 | 2024-02-18 16:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-03 19:00 | 118 | 2024-02-09 13:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-10 04:00 | 124 | 2024-02-20 12:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-14 05:00 | 126 | 2024-02-18 11:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-22 17:00 | 124 | 2024-02-24 13:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-03 05:00 | 119 | 2024-02-19 12:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-02 09:00 | 126 | 2024-02-09 12:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 142 | 2024-02-26 04:00 | 121 | 2024-02-19 10:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 142 | 2024-02-26 06:00 | 124 | 2024-02-19 10:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 145 | 2024-02-26 05:00 | 130 | 2024-02-04 12:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-22 05:00 | 113 | 2024-02-07 07:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-22 10:00 | 113 | 2024-02-10 08:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-10 04:00 | 123 | 2024-02-13 12:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-09 06:00 | 128 | 2024-02-13 12:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-02-01 03:00 | 126 | 2024-02-19 13:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 135 | 2024-02-07 01:00 | 113 | 2024-02-10 09:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-13 23:00 | 125 | 2024-02-29 22:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-16 08:00 | 114 | 2024-02-19 11:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-13 20:00 | 120 | 2024-02-23 21:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-16 07:00 | 125 | 2024-02-19 12:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-02 19:00 | 127 | 2024-02-24 17:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-25 23:00 | 123 | 2024-02-19 10:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-25 23:00 | 119 | 2024-02-19 12:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-04 22:00 | 126 | 2024-02-09 12:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-26 03:00 | 125 | 2024-02-20 12:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-02 21:00 | 125 | 2024-02-09 12:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-26 05:00 | 123 | 2024-02-19 12:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-01 03:00 | 121 | 2024-02-19 12:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-08 19:00 | 126 | 2024-02-24 17:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-02 04:00 | 133 | 2024-02-13 11:00
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-23 01:00 | 113 | 2024-02-02 09:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-26 01:00 | 127 | 2024-02-13 12:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-25 23:00 | 121 | 2024-02-19 10:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 135 | 2024-02-22 04:00 | 114 | 2024-02-12 08:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-03 19:00 | 122 | 2024-02-19 10:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-16 06:00 | 130 | 2024-02-02 16:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-10 03:00 | 116 | 2024-02-19 12:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-08 19:00 | 126 | 2024-02-29 22:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-10 03:00 | 126 | 2024-02-18 11:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-26 05:00 | 120 | 2024-02-08 08:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-10 03:00 | 114 | 2024-02-19 12:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-25 19:30 | 118 | 2024-02-19 12:00
85 | Matarbari 132/33kV Sub-Station | 132 | 138 | 2024-02-29 19:30 | 113 | 2024-02-23 17:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-26 05:00 | 120.5 | 2024-02-19 11:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 143 | 2024-02-04 19:30 | 120 | 2024-02-19 10:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-02-01 19:00 | 120 | 2024-02-19 11:00
89 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 138 | 2024-02-03 02:00 | 120 | 2024-02-19 12:00
90 | Mithapukur 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-26 05:00 | 116 | 2024-02-20 08:00
91 | MI_Cement 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 123 | 2024-02-19 10:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 139 | 2024-02-02 09:00 | 126 | 2024-02-09 13:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-14 05:00 | 119 | 2024-02-19 12:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 136 | 2024-02-01 17:00 | 119 | 2024-02-22 12:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-25 19:00 | 118 | 2024-02-19 12:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-26 04:00 | 123 | 2024-02-18 16:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-22 10:00 | 114 | 2024-02-02 12:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-26 04:00 | 113 | 2024-02-08 10:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-09 05:00 | 126 | 2024-02-11 12:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-26 05:00 | 113 | 2024-02-19 11:00
101 | Natore 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-09 05:00 | 126 | 2024-02-01 11:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-25 23:00 | 121 | 2024-02-19 12:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 134 | 2024-02-02 20:00 | 114 | 2024-02-14 19:30
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 144 | 2024-02-04 19:30 | 121 | 2024-02-19 12:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-25 04:00 | 113 | 2024-02-10 13:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-10 04:00 | 124 | 2024-02-18 11:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 143 | 2024-02-26 01:00 | 123 | 2024-02-12 12:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 135 | 2024-02-10 02:00 | 115 | 2024-02-07 08:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-10 03:00 | 113 | 2024-02-12 09:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-01 19:00 | 126 | 2024-02-15 22:00
111 | PHP 132/33kV Sub-Station | 132 | 141 | 2024-02-12 19:00 | 117 | 2024-02-09 13:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-02 18:30 | 125 | 2024-02-19 12:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 143 | 2024-02-05 03:00 | 118 | 2024-02-19 12:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 136 | 2024-02-26 06:00 | 113 | 2024-02-11 08:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 142 | 2024-02-26 04:00 | 121 | 2024-02-19 10:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 129 | 2024-02-18 12:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-03 03:00 | 121 | 2024-02-13 13:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-09 05:00 | 125 | 2024-02-01 11:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-05 17:00 | 115 | 2024-02-23 21:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-02 13:00 | 127 | 2024-02-09 12:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-22 06:00 | 115 | 2024-02-07 07:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 142 | 2024-02-09 05:00 | 130 | 2024-02-04 12:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-02-22 05:00 | 113 | 2024-02-07 08:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-14 03:00 | 122 | 2024-02-20 18:30
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-10 04:00 | 122 | 2024-02-19 12:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-20 02:00 | 117 | 2024-02-19 12:00
127 | SevenRings 132/11kV Sub-Station | 132 | 147 | 2024-02-10 03:00 | 128 | 2024-02-19 11:00
128 | ShahCement 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 122 | 2024-02-18 17:00
129 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 144 | 2024-02-27 01:00 | 130 | 2024-02-05 12:00
130 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-02 06:00 | 126 | 2024-02-19 12:00
131 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-02 04:00 | 125 | 2024-02-09 11:00
132 | Shariatpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-02-18 21:00 | 130 | 2024-02-14 12:00
133 | Sherpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-22 10:00 | 113 | 2024-02-04 07:00
134 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-26 05:00 | 123 | 2024-02-19 10:00
135 | Sholosohor 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-02 09:00 | 125 | 2024-02-09 12:00
136 | Shyampur 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-25 19:00 | 125 | 2024-02-18 12:00
137 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-25 23:00 | 121 | 2024-02-19 11:00
138 | Sirajganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-09 05:00 | 120 | 2024-02-24 09:00
139 | Sonargaon 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-26 05:00 | 119 | 2024-02-19 10:00
140 | Sreemongol 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-02 08:00 | 123 | 2024-02-15 18:00
141 | Srinagar 132/33kV Grid Sub-Station | 132 | 139 | 2024-02-25 23:00 | 121 | 2024-02-19 12:00
142 | SSM 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-02 09:00 | 128 | 2024-02-28 14:00
143 | Sunamganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-02 03:00 | 129 | 2024-02-01 14:00
144 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 140 | 2024-02-02 04:00 | 131 | 2024-02-04 13:00
145 | Sylhet 132/33kV Grid Sub-Station | 132 | 141 | 2024-02-02 04:00 | 132 | 2024-02-01 14:00
146 | Tangail 132/33kV Grid Sub-Station | 132 | 138 | 2024-02-22 10:00 | 117 | 2024-02-12 12:00
147 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-26 05:00 | 113 | 2024-02-02 08:00
148 | TK chemical 132kV Grid Sub-Station | 132 | 140 | 2024-02-02 09:00 | 126 | 2024-02-09 12:00
149 | Ullahpara 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-26 01:00 | 123 | 2024-02-22 07:00
150 | Ullon 132/33kV Grid Sub-Station | 132 | 137 | 2024-02-26 | 119 | 2024-02-19 11:00
151 | Uttara 132/33kV Grid Sub-Station | 132 | 142 | 2024-02-04 10:00 | 120 | 2024-02-18 16:00
152 | UttaraNew 132/33kV Grid Sub-Station | 132 | 143 | 2024-02-05 04:00 | 118 | 2024-02-19 13:00
153 | Zigatola 132/33kV Grid Sub-Station | 132 | 140 | 2024-02-25 23:00 | 122 | 2024-02-19 10:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:February 2024
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 477 | 484.3398 | 2024-02-13 15:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 477 | 484.3398 | 2024-02-13 15:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -206 | 238.403 | 2024-02-03 15:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -198 | 225.5394 | 2024-02-19 10:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -388 | 389.1581 | 2024-02-18 06:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -378 | 378.8931 | 2024-02-18 06:00
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 417 | 417.8098 | 2024-02-15 22:00
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 417 | 417.8098 | 2024-02-15 22:00
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 417 | 417.8098 | 2024-02-15 22:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 198 | 215.4739 | 2024-02-27 14:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 120 | 400.4048 | 2024-02-17 11:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 486 | 516.2093 | 2024-02-29
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -256 | 256.5 | 2024-02-08 07:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -288 | 288.1521 | 2024-02-26 19:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 267 | 273.227 | 2024-02-29 18:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -114 | 114.0175 | 2024-02-15 07:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -114 | 114.0175 | 2024-02-15 07:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -566 | 566.0009 | 2024-02-22 01:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 319 | 321.753 | 2024-02-13 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 319 | 321.753 | 2024-02-13 21:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -69 | 69.1809 | 2024-02-11 19:30
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -69 | 69.1809 | 2024-02-11 19:30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 168 | 172.6963 | 2024-02-17 13:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 82 | 213.3846 | 2024-02-16 23:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 253 | 266.5802 | 2024-02-18 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 233 | 241.1079 | 2024-02-11 13:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 95 | 97.2934 | 2024-02-20 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 95 | 97.2934 | 2024-02-20 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 110 | 114.0175 | 2024-02-04 19:30
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 1 | 1 | 2024-02-28 20:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 220 | 228.0351 | 2024-02-19 19:30
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 156 | 167.869 | 2024-02-23 07:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 143 | 149.3251 | 2024-02-03 18:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 189 | 192.0339 | 2024-02-05 18:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 162 | 179.7999 | 2024-02-14 08:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 214 | 224.544 | 2024-02-12 08:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 227 | 229.9957 | 2024-02-18 18:30
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 234 | 234.6167 | 2024-02-19 19:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -96 | 117.6435 | 2024-02-29 11:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -91 | 114.2016 | 2024-02-24 11:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 198 | 202.4055 | 2024-02-13 08:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 198 | 202.4055 | 2024-02-13 08:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 270 | 275.7463 | 2024-02-13 08:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 197 | 205.3607 | 2024-02-02 10:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 196 | 197.9899 | 2024-02-23 10:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 200 | 211.8962 | 2024-02-07 20:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 100 | 100 | 2024-02-08 09:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 100 | 100 | 2024-02-08 09:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 132 | 163.2176 | 2024-02-25 18:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 137 | 169.0266 | 2024-02-19 15:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 136 | 169.4019 | 2024-02-25 18:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 90 | 90.0888 | 2024-02-23 18:30
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 77 | 85 | 2024-02-08 11:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 48 | 133.8992 | 2024-02-21 15:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 114 | 115.4123 | 2024-02-18 18:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 107 | 109.8818 | 2024-02-24 18:30
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 114 | 115.4123 | 2024-02-18 18:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 114 | 115.4123 | 2024-02-18 18:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 98 | 131.7118 | 2024-02-04 18:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 98 | 131.7118 | 2024-02-04 18:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 98 | 131.7118 | 2024-02-04 18:30
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -168 | 175.5705 | 2024-02-09 13:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -168 | 175.5705 | 2024-02-09 13:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 70 | 263.4692 | 2024-02-26 18:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 227 | 233.8055 | 2024-02-06 13:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 1 | 2024-02-10 18:30
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 213 | 225.8185 | 2024-02-04 13:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -126 | 126.0159 | 2024-02-27 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -126 | 126.0159 | 2024-02-27 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -162 | 162.0278 | 2024-02-27 19:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 224 | 244.4995 | 2024-02-20 14:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 212 | 223.5733 | 2024-02-03 12:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 134 | 138.4955 | 2024-02-09 07:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -58 | 59.6657 | 2024-02-26 13:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 12.0416 | 2024-02-17 05:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 2 | 2 | 2024-02-10 03:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 193 | 193.1269 | 2024-02-18 09:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 350 | 352.881 | 2024-02-22 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 230 | 230.0348 | 2024-02-29 13:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 229 | 239.1694 | 2024-02-09 13:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 229 | 239.1694 | 2024-02-09 13:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 145 | 156.1698 | 2024-02-03 15:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 145 | 156.1698 | 2024-02-03 15:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 44 | 241.0498 | 2024-02-08 07:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 170 | 190.0658 | 2024-02-03 01:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 296 | 311.1784 | 2024-02-11 12:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 295 | 304.1398 | 2024-02-10 18:30
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 220 | 222.7667 | 2024-02-18 11:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 210 | 211.2558 | 2024-02-08 11:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 210 | 211.2558 | 2024-02-08 11:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: February 2024 | [5 empty] | (For Evening Peak) | [8 empty] | Month: February 2024 |  |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-02-01 | 10424 | 10424 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-01 | 9975 | 10260 | 272 | 12:00 | 135 | 0 | 0 | 45 | 23 | 23 | 0 | 0 | 46 | -
2024-02-02 | 9311 | 9311 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-02 | 9253 | 9290 | 35 | 12:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | -
2024-02-03 | 10550 | 10550 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-03 | 9520 | 9562 | 40 | 12:00 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | -
2024-02-04 | 10346 | 10425 | 75 | 19:00 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | - | 2024-02-04 | 9642 | 9750 | 103 | 12:00 | 36 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | -
2024-02-05 | 10437 | 10465 | 27 | 20:00 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | - | 2024-02-05 | 9761 | 10150 | 371 | 12:00 | 55 | 65 | 80 | 23 | 45 | 45 | 43 | 0 | 15 | -
2024-02-06 | 10888 | 10888 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-06 | 9431 | 9900 | 448 | 12:00 | 65 | 110 | 0 | 0 | 60 | 85 | 25 | 0 | 103 | -
2024-02-07 | 10886 | 10980 | 90 | 19:00 | 8 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | - | 2024-02-07 | 9964 | 10400 | 416 | 12:00 | 80 | 46 | 30 | 50 | 40 | 80 | 20 | 20 | 50 | -
2024-02-08 | 10783 | 10850 | 64 | 19:00 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | - | 2024-02-08 | 10172 | 10400 | 218 | 12:00 | 40 | 35 | 5 | 0 | 0 | 113 | 0 | 0 | 25 | -
2024-02-09 | 9282 | 9345 | 60 | 19:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | - | 2024-02-09 | 9108 | 9108 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-10 | 10615 | 10645 | 29 | 19:00 | 0 | 0 | 9 | 0 | 0 | 20 | 0 | 0 | 0 | - | 2024-02-10 | 9394 | 9659 | 58 | 12:00 | 33 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | -
2024-02-11 | 10644 | 10740 | 92 | 19:00 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | - | 2024-02-11 | 10031 | 10150 | 114 | 12:00 | 60 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | -
2024-02-12 | 10798 | 10900 | 97 | 19:00 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | - | 2024-02-12 | 10051 | 10300 | 87 | 12:00 | 15 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | -
2024-02-13 | 10836 | 10286 | 90 | 19:00 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | 2024-02-13 | 10295 | 10407 | 107 | 12:00 | 22 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | -
2024-02-14 | 10980 | 11043 | 60 | 19:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | - | 2024-02-14 | 10428 | 10570 | 136 | 12:00 | 28 | 0 | 0 | 0 | 0 | 108 | 0 | 0 | 0 | -
2024-02-15 | 10944 | 11040 | 92 | 19:00 | 20 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | - | 2024-02-15 | 10886 | 10980 | 90 | 12:00 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | -
2024-02-16 | 9854 | 9925 | 68 | 19:30 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | - | 2024-02-16 | 9592 | 9800 | 199 | 12:00 | 50 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | -
2024-02-17 | 11152 | 11275 | 117 | 19:00 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | - | 2024-02-17 | 9958 | 10050 | 88 | 12:00 | 40 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | -
2024-02-18 | 11192 | 11350 | 151 | 19:00 | 28 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | - | 2024-02-18 | 10561 | 10800 | 233 | 12:00 | 55 | 0 | 0 | 53 | 0 | 80 | 0 | 0 | 45 | -
2024-02-19 | 11426 | 11600 | 166 | 19:00 | 10 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | - | 2024-02-19 | 10733 | 10900 | 159 | 12:00 | 80 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | -
2024-02-20 | 11433 | 11600 | 159 | 19:00 | 24 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | - | 2024-02-20 | 10688 | 10870 | 174 | 12:00 | 74 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | -
2024-02-21 | 9940 | 9940 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-21 | 9810 | 9810 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-22 | 10598 | 10598 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-22 | 10067 | 10067 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-23 | 9893 | 9893 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-23 | 9346 | 9346 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-24 | 11132 | 11132 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-24 | 9774 | 9774 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-25 | 10307 | 10307 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-25 | 10066 | 10066 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-26 | 9551 | 9551 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-02-26 | 8230 | 8230 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-27 | 11041 | 11075 | 32 | 19:00 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | - | 2024-02-27 | 10663 | 10663 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-02-28 | 11403 | 11424 | 20 | 19:00 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | - | 2024-02-28 | 10864 | 10874 | 10 | 12:00 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | -
2024-02-29 | 11385 | 11437 | 50 | 19:00 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 |  | 2024-02-29 | 11039 | 11039 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:February 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 11433 | 2024-02-20 | 19:00
2 | Maximum Day Peak Genaration | MW | 11039 | 2024-02-29 | 12:00
3 | Maximum Evening Peak Demand | MW | 11600 | 2024-02-29 | 19:00
4 | Minimum Generation | MW | 6491 | 2024-02-26 | 6:00
5 | Average of the daily evening peak Genaration | MW | 10621.7586 | - | -
6 | Average of the daily day peak Genaration | MW | 9975.931 | - | -
7 | Maximum load shed | MW | 166 | 2024-02-19 | 19:00
8 | Minimum load shed | MW | 0 | 2024-02-19 | 21:00
9 | Total nos. of load shed days | Day | 19 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 53.069 | - | -
11 | Total Generation | MkWh | 6409.3969 | - | -
12 | Total Generation by BPDB | MkWh | 1547.5883 | % of total Gen. | 24.15%
13 | Total Generation by IPP | MkWh | 1575.967 | '' | 24.59%
14 | A) Total Generation by Generation Companies | MkWh | 1785.399 | '' | 27.86%
| B) Total Generation by REB | MkWh | 89.9855 | " | 1.404%
| C) Total Generation by RENTAL | MkWh | 118.5854 | " | 1.85%
| D) Total Imported from India (BIPTC) | MkWh | 515.7964 | " | 8.048%
| E) Total Imported from Tripura, India (A.C) | MkWh | 776.0754 | " | 12.11%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3054.7437 | % of total Gen. | 47.66%
| B) Oil | MkWh | 524.99 | '' | 8.191%
| C) Hydro | MkWh | 28.5971 | '' | 0.4462%
| D) Solar | MkWh | 65.9163 | '' | 1.028%
| E) Coal | MkWh | 2143.2933 | '' | 33.44%
| F) BIPTC (Import from India) | MkWh | 515.7964 | '' | 8.048%
| G) A.C (Import from Tripura, India) | MkWh | 70.4794 | '' | 1.1%
| H) Wind | MkWh | 5.5733 | '' | 0.08695%
16 | Maximun of the daily total Generation . | MkWh | 236.1408 | 2024-02-28
17 | Monthly Load factor | % | 70.7431 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 34700.756 | - | -
| A) Gas | M.Taka | 8802.6197 | - | -
| B) Liquid fuel | M.Taka | 9209.8124 | - | -
| C) Coal | M.Taka | 13975.1575 | - | -
| D) BIPTC (Import from India) | M.Taka | 2099.2912 | - | -
| E) Tripura(Import from India) | M.Taka | 613.8752 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1290.4636 | 2024-02-12
| A) Gas | M.Taka | 342.8663 | 2024-02-21
| B) Liquid fuel | M.Taka | 449.4526 | 2024-02-12
| C) Coal | M.Taka | 545.6655 | 2024-02-20
| D) BIPTC (Import from India) | M.Taka | 87.8291 | 2024-02-04
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.414
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.4999
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93.07 | 29/02/2024 | 06:00
b) | Actual | FT (MSL) | 83.98 | 29/02/2024 | 6:00
22 | Peak Genaration of February 2023 | MW | 11708 | 2023-02-27 | 19:00
23 | Peak Demand of February 2023 | MW | 11795 | 2023-02-28 | 19:00
24 | Maximum peak Generation recorded upto 29/02/2024 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 29/02/2024 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 29/02/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:February 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | [23 empty] | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 | [10 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [6 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD