## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-04-27 | Saturday
|  | Date (day): | 2024-04-27 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15949.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16908 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-04-26 | 2024-04-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 21 | 64 | 65 | 65 | 43 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 374 | 404 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 300 | 305 | 305 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 32 | 40 | 40 | 40 | 15 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 | 75 |  | Engine problem.
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 189 | 201 | 200 | 200 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 308 | 321 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 73 | 32 | 82 | 20 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 0 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 147 | 32 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 33 | 44 | 44 |  | 36 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 16 | 16 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 273 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 128 | 145 | 130 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 52 | 53 | 72 | 32 |  | Lube oil shortage.
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 35 | 162 |  |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Engine problem
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 250 | 540 | 500 | 500
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 583 | 230 | 590 | 500 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 3194 | 3958 | 3843 | 4285 | 671 | 796
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 114 | 110 | 115 | 115 | 65 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 4 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 6 | 18 | 32 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 60 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 212 | 211 | 211
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 34 | 71 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 32 | 32 | 50 | 48
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 51 | 51 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 5 | 5 | 5 | 5 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 16 | 31 | 15 | 30
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 26 | 12 | 25 | 83 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 16 | 16 | 284
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 13 | 36 | 18 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 34 | 17 | 34 | 76 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 10 | 12 | 12 | 88 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 24 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 270 | 272 | 275 | 275 | 949 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 7 | 0 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 779 | 780 | 580 | 580 |  |  | Unit-2 on test
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 70 | 0 | 33 | 0 |  |  | on test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1742 | 1915 | 1596 | 1779 | 2101 | 381
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 204 | 220 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 285 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 270 | 280 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 300 | 300 | 300 | 300 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 37 | 40 | 40 | 5
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 47 | 45 | 50 | 50 | 5
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 6 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 33 | 33 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 155 | 100 | 150 | 50 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  | 5 | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 94 | 146 | 144
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 16 | 16 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 32 | 50 | 34 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 62 | 114 | 52 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 65 | 55 | 65 | 48 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 97 | 36 | 95 |  | 20 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1690 | 1858 | 1773 | 1996 | 447 | 223
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 66 | 98 | 70 | 100 | 102 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 104 | 56 | 108 | 92 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 97 | 50 | 107 | 8 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 12 | 18 | 4 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 235 | 317 | 239.6 | 333 | 102 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 43 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 27 | 28 | 30 | 30 |  | 60 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 22 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 20 | 44 | 44
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 5 | 5 | 5 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 51 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 80 | 88 | 95 | 95
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 203 | 202 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 396 | 366 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 320 | 380 | 380 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1717 | 1593 | 1772 | 1772 | 0 | 489
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 921 | 636 | 939 | 650
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 0 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 62 | 0 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 345 | 400 | 410
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 73 | 90 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 340 | 378 | 375 | 375
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1748 | 1527 | 1904 | 1629 | 702 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 32 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 9 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 124 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 700 | 800 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 17 | 17 | 133 |  | Fuel shortage
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 250 | 150 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1219 | 1455 | 1819 | 2038 | 133 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 38 | 38 | 14 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 14 | 35 | 35 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 7 | 45 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 156 | 177 | 160 | 200 |  |  | FGMO
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 165 | 188 | 160 | 200 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 304 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 32 | 30 | 33 | 17 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 37 | 80 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 50 | 35 | 77 | 36 |  | Fuel shortage
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 25 | 95 | 35 | 55 | 58 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 751 | 1430 | 1400 | 1400
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1761 | 2547 | 2456 | 2675 | 560 | 71
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 203 | 230 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 48 | 56 | 34 | 56 | 57 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 55 | 94 | 115 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 184 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 531 | 380 | 547 | 401 | 182 | 129
| Total |  |  |  |  | 27054 | 25903 | 13837 | 15550 | 15949.6 | 16908 | 4898 | 2212
A. |  | 2024-04-26 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 15550 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12647 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15870 | MW
3 | Day peak Generation : |  |  | 13837 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15160.92 | MW
4 | Evening peak Generation : |  |  | 15550 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 306 | MW
5 | Total Energy Generation : |  | 336.0321 | MKWHr | By Solar | 3.5567 | MKWHr
| By Gas : | 176.2823 | MKWHr |  | By Oil: | 45.9868 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 88.1129 | MKWHr |  | By Hydro: | 0.74848 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.13344 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4898 | MW | Dhaka | 5175.62 | 5175.62 |  | 0 |  | 18:00 |  | 294
|  |  | For Plants S/D or M/C prob = |  |  | 2212 | MW | Chittagong | 1326.9 | 1326.9 |  | 0 |  | 19:00 |  | 430.705
|  |  | Total = |  |  | 7110 | MW | Khulna | 1941 | 1941 |  | 0 |  | 19:30 |  | 326.61
7 | Total Gas Supplied : |  |  | 1322.59 | MMCFD |  |  | Rajshahi | 1797.4 | 1797.4 |  | 0 |  | 20:00 |  | 388.685
8 | Fuel Cost : | i) Gas : | Taka | 503377843.912 | ii) Oil : | Taka | 848320222.08 | Comilla | 1519 | 1474 |  | 45 |  | 21:00 |  | 306
|  | iii) Coal : | Taka | 589967313.16 | Total | Taka | 1941665379.152 | Mymensingh | 1363 | 1218 |  | 145 |  | 22:00 |  | 352.395
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 527 | 527 |  | 0 |  | 23:00 |  | 462.22
| ii) During Peak Demand : |  |  | 710 | MW (W to E) at | 21:00 | hrs | Barisal | 485 | 485 |  | 0 |  | 24:00 |  | 817.48
| iii) Maximum : |  |  | 710 | MW at | 21:00 | hrs | Rangpur | 1026 | 910 |  | 116
10 | Maximum Temperature in Dhaka was |  |  |  | 38.2°C |  |  | Total | 15160.92 | 14854.92 |  | 306
B. |  | 2024-04-27 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 38.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16908 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14500 | MW
4 | Reserve(Generation end) |  |  |  | 308 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 358.7224 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12445 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.608 | MKWHr. | ii) HVDC Flow at Peak Time |  | 636 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6035 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.1 |  | (b) Today: | 74.86 |  | (c) Rule Curve: |  | 82.8
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-04-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 305 | 0 | 0 | 40 | 324 | 0 | 151 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 210 | 0 | 0 | 0 |  | 12 | 32 | 51 | 0 | 0 | 6 | 5 | 32 | 0 | 0 | 0 | 325 | 280 | 197 | 0 | 0 | 36 | 48 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 16 | 19 | 110 | 70 | 0 | 0 | 0 | 43 | 28 | 52 | 37 | 112 | 0 | 59 | 0 | 0 | 203 | 17 | 0 | 0 | 310 | 16 | 5 | 0 | 263 | 0 | 0 | 77 | 0 | 130 | 0 | 12 | 94 | 6 | 402 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 70 | 40 | 12 | 375 | 46 | 0 | 17 | 17 | 25 | 35 | 0 | 40 | 0 | 230 | 17 | 0 | 269 | 0 | 577 | 470 | 350 | 0 |  | 637 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 33 | 36 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 37 | 17 | 95 | 35 | 34 | 30 | 0 | 38 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 189 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 307 | 1169 | 0 | 0 |  | 8447 | 5896 | 14343 | 4721 | 637 | 2861 | 0 | 1411 | 4136 | 30 | 0 | 437 | 110 | 0 | 0 | 1535 | 75.15
2:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 306 | 0 | 0 | 40 | 326 | 0 | 152 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 112 | 0 | 8 | 210 | 0 | 0 | 0 |  | 12 | 32 | 51 | 0 | 0 | 6 | 5 | 24 | 0 | 0 | 0 | 305 | 280 | 188 | 0 | 0 | 39 | 48 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 16 | 19 | 112 | 74 | 0 | 0 | 0 | 40 | 28 | 53 | 37 | 112 | 0 | 59 | 0 | 0 | 202 | 17 | 0 | 0 | 305 | 16 | 5 | 0 | 281 | 0 | 0 | 77 | 0 | 129 | 0 | 12 | 85 | 5 | 400 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 38 | 12 | 370 | 18 | 0 | 17 | 17 | 25 | 35 | 0 | 36 | 0 | 230 | 17 | 0 | 270 | 0 | 575 | 470 | 350 | 0 |  | 636 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 33 | 36 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 37 | 17 | 95 | 35 | 34 | 30 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 198 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 307 | 1059 | 0 | 0 |  | 8364 | 5759 | 14123 | 4677 | 636 | 2850 | 0 | 1366 | 4023 | 30 | 0 | 429 | 112 | 0 | 0 | 1554 | 75.14
3:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 350 | 0 |  | 0 | 450 | 306 | 0 | 0 | 40 | 327 | 0 | 153 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 210 | 0 | 0 | 0 |  | 9 | 32 | 51 | 0 | 0 | 6 | 5 | 13 | 0 | 0 | 0 | 280 | 280 | 204 | 0 | 0 | 39 | 48 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 16 | 19 | 118 | 81 | 0 | 0 | 0 | 40 | 28 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 205 | 17 | 0 | 0 | 310 | 16 | 5 | 0 | 283 | 0 | 0 | 77 | 0 | 107 | 0 | 12 | 85 | 6 | 369 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 39 | 12 | 345 | 18 | 0 | 17 | 17 | 40 | 35 | 0 | 35 | 0 | 230 | 17 | 0 | 274 | 0 | 575 | 470 | 350 | 0 |  | 919 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 33 | 36 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 38 | 17 | 50 | 35 | 34 | 30 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 198 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 307 | 741 | 0 | 0 |  | 8290 | 5645 | 13935 | 4583 | 919 | 2847 | 0 | 1344 | 3709 | 30 | 0 | 385 | 118 | 0 | 0 | 1495 | 75.13
4:00 | 0 | 0 | 180 | 180 | 0 | 0 | 0 | 344 | 0 |  | 0 | 450 | 307 | 0 | 0 | 40 | 327 | 0 | 153 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 0 | 33 | 8 | 0 | 30 | 0 | 112 | 0 | 8 | 210 | 0 | 0 | 0 |  | 10 | 32 | 51 | 0 | 0 | 6 | 5 | 24 | 0 | 0 | 0 | 280 | 280 | 215 | 0 | 0 | 39 | 49 | 0 | 51 | 0 | 26 | 25 | 0 | 0 | 16 | 19 | 128 | 82 | 0 | 0 | 0 | 40 | 28 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 205 | 17 | 0 | 0 | 290 | 16 | 5 | 0 | 278 | 0 | 0 | 77 | 0 | 127 | 0 | 12 | 85 | 6 | 364 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 37 | 12 | 345 | 16 | 0 | 17 | 17 | 40 | 35 | 0 | 35 | 0 | 230 | 17 | 0 | 274 | 10 | 575 | 470 | 350 | 0 |  | 921 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 33 | 35 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 38 | 17 | 50 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 197 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1200 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 240 | 743 | 0 | 0 |  | 8274 | 5442 | 13716 | 4546 | 921 | 2840 | 0 | 1356 | 3570 | 30 | 0 | 315 | 128 | 0 | 10 | 1417 | 75.12
5:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 344 | 0 |  | 0 | 450 | 309 | 0 | 0 | 40 | 327 | 0 | 150 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 0 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 210 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 0 | 6 | 5 | 25 | 0 | 0 | 0 | 280 | 260 | 213 | 0 | 0 | 39 | 49 | 0 | 51 | 0 | 26 | 25 | 0 | 0 | 16 | 19 | 116 | 83 | 0 | 0 | 0 | 40 | 28 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 206 | 17 | 0 | 0 | 295 | 24 | 5 | 0 | 275 | 0 | 0 | 77 | 0 | 127 | 0 | 12 | 85 | 6 | 369 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 37 | 12 | 350 | 17 | 0 | 17 | 17 | 40 | 35 | 0 | 36 | 0 | 240 | 17 | 0 | 275 | 10 | 579 | 400 | 350 | 0 |  | 920 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 33 | 35 | 0 | 130 | 9 | 48 | 0 | 0 | 0 | 38 | 0 | 50 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 198 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 414 | 91 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1200 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 240 | 745 | 0 | 0 |  | 8152 | 5452 | 13604 | 4533 | 920 | 2777 | 0 | 1358 | 3579 | 30 | 0 | 281 | 116 | 0 | 10 | 1333 | 75.11
6:00 | 0 | 0 | 140 | 180 | 0 | 0 | 0 | 342 | 0 |  | 0 | 450 | 286 | 0 | 0 | 40 | 332 | 0 | 149 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 33 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 0 | 6 | 5 | 25 | 0 | 0 | 0 | 280 | 260 | 216 | 0 | 0 | 39 | 49 | 0 | 51 | 0 | 26 | 25 | 0 | 0 | 16 | 19 | 108 | 82 | 0 | 0 | 0 | 40 | 28 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 205 | 17 | 0 | 0 | 280 | 24 | 5 | 0 | 275 | 0 | 0 | 77 | 0 | 126 | 1 | 12 | 85 | 5 | 364 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 38 | 12 | 345 | 17 | 1 | 17 | 17 | 40 | 17 | 1 | 36 | 0 | 240 | 17 | 0 | 274 | 4 | 574 | 300 | 500 | 3 |  | 920 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 37 | 0 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 210 | 0 | 0 | 197 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 300 | 92 | 0 | 85 | 0 | 34 | 0 | 0 | 0 | 1000 | 220 | 0 | 17 | 0 | 2 | 0 | 0 | 0 | 339 | 1 | 200 | 752 | 8 | 0 |  | 8149 | 5081 | 13230 | 4582 | 920 | 2676 | 0 | 1382 | 3349 | 30 | 0 | 162 | 108 | 17 | 4 | 1213 | 75.1
7:00 | 0 | 0 | 58 | 180 | 0 | 0 | 0 | 339 | 0 |  | 0 | 450 | 275 | 0 | 0 | 40 | 329 | 0 | 145 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 13 | 33 | 33 | 8 | 0 | 30 | 0 | 112 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 0 | 6 | 5 | 25 | 0 | 0 | 0 | 280 | 260 | 216 | 0 | 0 | 39 | 49 | 0 | 51 | 0 | 27 | 25 | 0 | 0 | 16 | 19 | 114 | 71 | 0 | 0 | 0 | 42 | 28 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 206 | 17 | 0 | 0 | 265 | 24 | 5 | 0 | 275 | 0 | 0 | 58 | 0 | 115 | 4 | 12 | 85 | 6 | 366 | 49 | 17 | 17 | 1 | 16 | 1 | 17 | 52 | 38 | 12 | 345 | 17 | 9 | 17 | 17 | 30 | 17 | 5 | 36 | 0 | 240 | 17 | 0 | 275 | 5 | 574 | 300 | 525 | 16 |  | 920 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 48 | 0 | 0 | 0 | 38 | 0 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 173 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 295 | 92 | 0 | 113 | 0 | 34 | 0 | 1 | 0 | 880 | 220 | 0 | 17 | 0 | 18 | 0 | 0 | 0 | 341 | 6 | 200 | 752 | 41 | 0 |  | 8032 | 5062 | 13094 | 4476 | 920 | 2670 | 0 | 1362 | 3252 | 30 | 0 | 164 | 114 | 101 | 5 | 865.23 | 75.09
8:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 351 | 0 |  | 0 | 380 | 294 | 0 | 0 | 40 | 326 | 0 | 150 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 113 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 0 | 6 | 5 | 16 | 0 | 0 | 0 | 280 | 260 | 214 | 0 | 0 | 38 | 49 | 0 | 51 | 0 | 27 | 24 | 0 | 0 | 16 | 19 | 102 | 64 | 0 | 0 | 1 | 42 | 28 | 53 | 40 | 80 | 0 | 61 | 0 | 0 | 206 | 18 | 0 | 0 | 275 | 24 | 8 | 0 | 275 | 0 | 0 | 58 | 0 | 129 | 0 | 12 | 85 | 6 | 364 | 49 | 17 | 17 | 1 | 16 | 17 | 17 | 52 | 38 | 12 | 345 | 17 | 14 | 17 | 17 | 30 | 17 | 13 | 36 | 0 | 240 | 17 | 0 | 275 | 2 | 578 | 300 | 419 | 36 |  | 921 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 314 | 92 | 0 | 113 | 0 | 34 | 0 | 3 | 0 | 800 | 180 | 0 | 17 | 2 | 43 | 0 | 0 | 0 | 340 | 15 | 150 | 740 | 84 | 0 |  | 7844 | 4892 | 12736 | 4442 | 921 | 2459 | 0 | 1359 | 3083 | 30 | 0 | 126 | 102 | 212 | 2 | 586.37 | 75.08
9:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 365 | 0 |  | 0 | 380 | 300 | 0 | 0 | 40 | 290 | 0 | 122 | 0 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 115 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 0 | 6 | 5 | 12 | 0 | 0 | 0 | 280 | 260 | 214 | 0 | 0 | 38 | 49 | 0 | 51 | 0 | 27 | 25 | 0 | 0 | 16 | 19 | 110 | 66 | 0 | 0 | 2 | 43 | 28 | 53 | 40 | 80 | 0 | 40 | 0 | 0 | 207 | 18 | 0 | 0 | 270 | 24 | 11 | 0 | 95 | 0 | 0 | 58 | 0 | 130 | 14 | 12 | 87 | 6 | 316 | 49 | 17 | 17 | 2 | 16 | 17 | 17 | 52 | 38 | 12 | 315 | 17 | 30 | 17 | 17 | 70 | 17 | 21 | 36 | 0 | 240 | 17 | 0 | 270 | 0 | 779 | 300 | 426 | 50 |  | 921 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 8 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 161 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 310 | 17 | 0 | 113 | 0 | 34 | 0 | 5 | 0 | 700 | 180 | 0 | 0 | 3 | 66 | 35 | 0 | 0 | 340 | 23 | 150 | 750 | 128 | 0 |  | 7844 | 4803 | 12647 | 4343 | 921 | 2460 | 0 | 1108 | 3189 | 30 | 0 | 142 | 110 | 344 | 0 | 413.515 | 75.07
10:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 371 | 0 |  | 0 | 420 | 301 | 0 | 0 | 40 | 270 | 0 | 160 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 113 | 0 | 0 | 212 | 0 | 0 | 0 |  | 17 | 32 | 34 | 0 | 12 | 6 | 5 | 13 | 0 | 0 | 0 | 300 | 330 | 210 | 0 | 0 | 38 | 49 | 0 | 51 | 0 | 27 | 25 | 0 | 0 | 16 | 19 | 98 | 66 | 0 | 0 | 2 | 43 | 28 | 50 | 37 | 80 | 0 | 40 | 0 | 0 | 206 | 17 | 0 | 0 | 295 | 24 | 11 | 0 | 95 | 0 | 0 | 57 | 0 | 126 | 6 | 12 | 85 | 6 | 315 | 48 | 17 | 17 | 4 | 16 | 17 | 17 | 52 | 38 | 12 | 320 | 17 | 40 | 17 | 17 | 75 | 17 | 26 | 35 | 0 | 240 | 17 | 0 | 270 | 5 | 582 | 250 | 588 | 61 |  | 920 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 147 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 348 | 17 | 0 | 113 | 0 | 34 | 0 | 6 | 0 | 700 | 180 | 0 | 0 | 4 | 81 | 35 | 0 | 0 | 340 | 29 | 150 | 748 | 156 | 0 |  | 7978 | 4874 | 12852 | 4466 | 920 | 2683 | 0 | 1103 | 2990 | 30 | 0 | 142 | 98 | 415 | 5 | 399.19 | 75.06
11:00 | 0 | 0 | 0 | 180 | 0 | 16 | 0 | 373 | 0 |  | 0 | 450 | 300 | 0 | 0 | 35 | 310 | 0 | 160 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 25 | 8 | 0 | 30 | 0 | 110 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 12 | 6 | 5 | 13 | 0 | 0 | 0 | 330 | 260 | 208 | 0 | 0 | 37 | 48 | 0 | 51 | 0 | 33 | 25 | 0 | 0 | 16 | 19 | 104 | 66 | 0 | 0 | 2 | 43 | 27 | 53 | 36 | 112 | 0 | 40 | 0 | 0 | 204 | 17 | 0 | 0 | 310 | 24 | 11 | 0 | 95 | 0 | 0 | 57 | 0 | 129 | 16 | 12 | 103 | 5 | 338 | 49 | 17 | 17 | 4 | 16 | 17 | 17 | 52 | 38 | 12 | 335 | 17 | 45 | 35 | 17 | 80 | 17 | 29 | 36 | 0 | 340 | 17 | 0 | 270 | 6 | 574 | 250 | 583 | 67 |  | 921 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 0 | 0 | 10 | 0 | 0 | 11 | 0 | 0 | 167 | 0 | 0 | 157 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 113 | 0 | 48 | 0 | 7 | 0 | 700 | 180 | 0 | 0 | 4 | 92 | 50 | 0 | 0 | 339 | 33 | 150 | 751 | 181 | 0 |  | 8246 | 4966 | 13212 | 4641 | 921 | 2761 | 0 | 1160 | 2951 | 30 | 0 | 158 | 104 | 480 | 6 | 303.69 | 75.05
12:00 | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 374 | 0 |  | 0 | 450 | 298 | 0 | 0 | 32 | 308 | 0 | 189 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 25 | 16 | 0 | 30 | 0 | 114 | 0 | 4 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 12 | 6 | 5 | 16 | 0 | 0 | 0 | 310 | 260 | 207 | 0 | 0 | 36 | 47 | 0 | 51 | 0 | 35 | 32 | 0 | 0 | 16 | 19 | 102 | 66 | 0 | 0 | 2 | 40 | 27 | 53 | 36 | 112 | 0 | 56 | 0 | 0 | 203 | 17 | 0 | 0 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 57 | 0 | 128 | 15 | 12 | 100 | 6 | 396 | 48 | 17 | 17 | 5 | 16 | 17 | 17 | 62 | 38 | 12 | 370 | 17 | 44 | 35 | 17 | 80 | 17 | 30 | 52 | 0 | 300 | 24 | 0 | 270 | 7 | 779 | 250 | 583 | 70 |  | 921 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 37 | 14 | 34 | 7 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 203 | 0 | 0 | 156 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 48 | 0 | 7 | 25 | 700 | 220 | 0 | 0 | 4 | 95 | 55 | 0 | 0 | 340 | 34 | 150 | 751 | 184 | 0 |  | 8578 | 5259 | 13837 | 4733 | 921 | 2860 | 0 | 1270 | 3193 | 30 | 0 | 231 | 102 | 490 | 7 | 327.565 | 75.04
13:00 | 0 | 0 | 0 | 180 | 0 | 24 | 0 | 374 | 0 |  | 0 | 450 | 302 | 0 | 0 | 40 | 302 | 0 | 191 | 0 | 48 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 33 | 25 | 16 | 0 | 30 | 0 | 112 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 12 | 6 | 5 | 27 | 0 | 0 | 0 | 280 | 260 | 207 | 0 | 0 | 32 | 44 | 0 | 51 | 0 | 33 | 34 | 0 | 0 | 16 | 19 | 118 | 70 | 0 | 0 | 2 | 40 | 27 | 53 | 36 | 112 | 0 | 55 | 0 | 0 | 202 | 17 | 0 | 0 | 310 | 24 | 11 | 0 | 151 | 0 | 0 | 56 | 0 | 125 | 17 | 12 | 100 | 6 | 366 | 47 | 17 | 17 | 4 | 16 | 17 | 17 | 62 | 37 | 12 | 345 | 51 | 44 | 35 | 17 | 60 | 17 | 29 | 54 | 0 | 300 | 53 | 0 | 278 | 7 | 781 | 250 | 571 | 69 |  | 920 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 16 | 0 | 0 | 0 | 0 | 4 | 32 | 35 | 34 | 16 | 0 | 35 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 169 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 113 | 0 | 48 | 0 | 7 | 55 | 790 | 220 | 0 | 0 | 4 | 92 | 55 | 0 | 0 | 340 | 33 | 150 | 747 | 168 | 0 |  | 8634 | 5389 | 14023 | 4633 | 920 | 2839 | 0 | 1421 | 3316 | 30 | 0 | 270 | 118 | 469 | 7 | 360.035 | 75.03
14:00 | 0 | 0 | 0 | 180 | 0 | 24 | 0 | 372 | 0 |  | 0 | 450 | 298 | 0 | 0 | 40 | 310 | 0 | 121 | 0 | 48 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 12 | 33 | 28 | 8 | 0 | 30 | 0 | 112 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 12 | 6 | 5 | 5 | 0 | 0 | 0 | 295 | 260 | 204 | 0 | 0 | 35 | 43 | 0 | 51 | 0 | 35 | 34 | 0 | 0 | 16 | 19 | 120 | 70 | 0 | 0 | 2 | 39 | 27 | 53 | 35 | 80 | 0 | 40 | 0 | 0 | 202 | 17 | 0 | 0 | 280 | 24 | 11 | 0 | 210 | 0 | 0 | 56 | 0 | 119 | 16 | 12 | 106 | 5 | 378 | 47 | 17 | 17 | 4 | 16 | 17 | 17 | 62 | 37 | 12 | 360 | 51 | 37 | 35 | 17 | 60 | 17 | 25 | 54 | 0 | 300 | 53 | 0 | 275 | 13 | 575 | 253 | 583 | 50 |  | 920 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 10 | 16 | 0 | 0 | 0 | 0 | 17 | 32 | 35 | 34 | 16 | 0 | 36 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 157 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 113 | 0 | 48 | 0 | 6 | 55 | 740 | 220 | 0 | 0 | 4 | 81 | 55 | 0 | 0 | 340 | 28 | 150 | 785 | 158 | 0 |  | 8343 | 5345 | 13688 | 4607 | 920 | 2735 | 0 | 1471 | 3095 | 30 | 0 | 286 | 120 | 411 | 13 | 488.96 | 75.05
15:00 | 0 | 0 | 0 | 180 | 0 | 24 | 0 | 372 | 0 |  | 0 | 450 | 300 | 0 | 0 | 40 | 311 | 0 | 121 | 0 | 48 | 31 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 12 | 33 | 28 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 31 | 37 | 0 | 12 | 6 | 5 | 23 | 0 | 0 | 0 | 285 | 270 | 207 | 0 | 0 | 35 | 38 | 0 | 51 | 0 | 30 | 32 | 0 | 0 | 16 | 19 | 112 | 69 | 0 | 0 | 1 | 39 | 28 | 53 | 35 | 112 | 0 | 55 | 0 | 0 | 200 | 15 | 0 | 0 | 285 | 16 | 11 | 0 | 210 | 0 | 0 | 56 | 0 | 110 | 12 | 12 | 152 | 6 | 367 | 47 | 17 | 17 | 3 | 16 | 17 | 17 | 62 | 37 | 12 | 345 | 51 | 30 | 35 | 17 | 55 | 16 | 20 | 54 | 0 | 320 | 53 | 0 | 275 | 12 | 778 | 404 | 583 | 44 |  | 921 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 10 | 16 | 0 | 0 | 0 | 0 | 16 | 32 | 35 | 34 | 30 | 0 | 35 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 165 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 35 | 0 | 34 | 0 | 5 | 55 | 810 | 220 | 0 | 0 | 3 | 65 | 55 | 0 | 0 | 338 | 22 | 200 | 810 | 125 | 0 |  | 8760 | 5312 | 14072 | 4592 | 921 | 2908 | 0 | 1431 | 3441 | 30 | 0 | 295 | 112 | 330 | 12 | 456.49 | 75.01
16:00 | 0 | 0 | 0 | 180 | 0 | 40 | 0 | 385 | 0 |  | 0 | 450 | 298 | 0 | 0 | 40 | 310 | 0 | 194 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 5 | 0 | 18 | 12 | 33 | 30 | 16 | 0 | 30 | 0 | 111 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 31 | 41 | 0 | 12 | 6 | 5 | 17 | 0 | 0 | 0 | 290 | 280 | 205 | 0 | 0 | 34 | 38 | 0 | 51 | 0 | 31 | 32 | 0 | 0 | 16 | 19 | 114 | 70 | 0 | 0 | 1 | 40 | 28 | 53 | 38 | 112 | 0 | 58 | 0 | 0 | 199 | 14 | 0 | 0 | 300 | 16 | 11 | 0 | 210 | 0 | 0 | 54 | 0 | 98 | 7 | 12 | 152 | 5 | 367 | 46 | 17 | 17 | 2 | 16 | 17 | 17 | 60 | 36 | 12 | 345 | 51 | 20 | 35 | 17 | 55 | 17 | 12 | 54 | 0 | 320 | 17 | 0 | 276 | 19 | 575 | 442 | 0 | 28 |  | 921 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 16 | 0 | 0 | 0 | 0 | 16 | 32 | 35 | 34 | 28 | 0 | 24 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 162 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 346 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 55 | 910 | 180 | 0 | 0 | 2 | 43 | 35 | 0 | 0 | 338 | 15 | 200 | 910 | 79 | 0 |  | 8093 | 5385 | 13478 | 4694 | 921 | 2374 | 0 | 1423 | 3439 | 30 | 0 | 252 | 114 | 212 | 19 | 641.76 | 75
17:00 | 0 | 0 | 0 | 180 | 0 | 50 | 0 | 403 | 0 |  | 0 | 450 | 282 | 0 | 0 | 40 | 312 | 0 | 197 | 0 | 76 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 18 | 12 | 33 | 30 | 16 | 0 | 30 | 0 | 111 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 31 | 49 | 0 | 20 | 6 | 5 | 26 | 0 | 0 | 0 | 285 | 270 | 207 | 0 | 0 | 35 | 39 | 0 | 51 | 0 | 31 | 48 | 0 | 0 | 16 | 18 | 108 | 91 | 0 | 0 | 0 | 39 | 28 | 53 | 35 | 112 | 0 | 55 | 0 | 0 | 199 | 14 | 0 | 0 | 290 | 24 | 11 | 0 | 80 | 0 | 0 | 55 | 0 | 103 | 3 | 12 | 104 | 6 | 366 | 47 | 17 | 17 | 1 | 16 | 31 | 17 | 60 | 42 | 12 | 345 | 50 | 8 | 35 | 17 | 90 | 17 | 5 | 54 | 0 | 320 | 17 | 0 | 274 | 20 | 756 | 584 | 0 | 10 |  | 921 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 16 | 0 | 0 | 0 | 30 | 16 | 32 | 35 | 34 | 18 | 0 | 26 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 174 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 294 | 17 | 0 | 35 | 0 | 55 | 0 | 1 | 75 | 860 | 220 | 0 | 0 | 0 | 19 | 35 | 0 | 0 | 339 | 6 | 190 | 1021 | 34 | 0 |  | 8347 | 5410 | 13757 | 4769 | 921 | 2493 | 0 | 1377 | 3670 | 30 | 0 | 282 | 108 | 87 | 20 | 470.815 | 74.99
18:00 | 0 | 0 | 0 | 180 | 0 | 57 | 0 | 404 | 0 |  | 0 | 450 | 287 | 0 | 0 | 40 | 280 | 0 | 75 | 0 | 82 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 18 | 12 | 33 | 30 | 16 | 0 | 30 | 0 | 112 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 34 | 46 | 0 | 26 | 6 | 5 | 26 | 0 | 0 | 0 | 280 | 270 | 212 | 0 | 0 | 35 | 41 | 0 | 51 | 0 | 31 | 49 | 0 | 0 | 16 | 19 | 94 | 88 | 0 | 0 | 0 | 40 | 28 | 20 | 35 | 80 | 0 | 40 | 0 | 0 | 199 | 14 | 0 | 0 | 260 | 24 | 5 | 0 | 80 | 0 | 0 | 55 | 0 | 132 | 0 | 12 | 120 | 6 | 366 | 47 | 17 | 17 | 0 | 16 | 36 | 17 | 114 | 63 | 10 | 345 | 50 | 1 | 35 | 17 | 90 | 17 | 1 | 56 | 0 | 280 | 17 | 0 | 271 | 7 | 774 | 408 | 60 | 1 |  | 921 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 16 | 0 | 0 | 0 | 38 | 16 | 32 | 35 | 8 | 22 | 0 | 26 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 169 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 295 | 17 | 0 | 35 | 0 | 55 | 0 | 0 | 35 | 680 | 190 | 0 | 0 | 0 | 2 | 68 | 0 | 0 | 341 | 1 | 150 | 1076 | 5 | 0 |  | 8121 | 5121 | 13242 | 4531 | 921 | 2266 | 0 | 1500 | 3522 | 30 | 0 | 360 | 94 | 11 | 7 | 294 | 74.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 404 | 0 |  | 0 | 450 | 302 | 0 | 0 | 40 | 317 | 0 | 197 | 0 | 82 | 148 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 18 | 12 | 33 | 30 | 16 | 0 | 30 | 0 | 110 | 0 | 25 | 211 | 0 | 0 | 0 |  | 18 | 32 | 49 | 0 | 26 | 6 | 5 | 27 | 0 | 0 | 0 | 300 | 285 | 197 | 0 | 0 | 36 | 42 | 0 | 51 | 0 | 33 | 51 | 0 | 0 | 16 | 19 | 100 | 98 | 0 | 0 | 0 | 40 | 29 | 53 | 36 | 112 | 0 | 50 | 0 | 0 | 202 | 15 | 0 | 0 | 305 | 24 | 5 | 0 | 134 | 0 | 0 | 104 | 0 | 149 | 0 | 12 | 155 | 5 | 368 | 97 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 68 | 10 | 335 | 51 | 0 | 72 | 17 | 91 | 17 | 0 | 78 | 0 | 300 | 163 | 0 | 270 | 5 | 777 | 525 | 102 | 0 |  | 921 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 0 | 130 | 10 | 32 | 0 | 0 | 0 | 38 | 16 | 85 | 35 | 34 | 38 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 164 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 352 | 40 | 0 | 42 | 0 | 56 | 0 | 0 | 95 | 710 | 220 | 0 | 12 | 0 | 0 | 94 | 0 | 0 | 378 | 0 | 211 | 1204 | 0 | 0 |  | 9298 | 5751 | 15049 | 4775 | 921 | 2647 | 0 | 2139 | 3750 | 30 | 0 | 682 | 100 | 0 | 5 | 430.705 | 74.95
19:30 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 407 | 0 |  | 0 | 450 | 287 | 0 | 0 | 40 | 317 | 0 | 199 | 0 | 82 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 18 | 15 | 33 | 31 | 16 | 0 | 30 | 0 | 110 | 0 | 25 | 210 | 0 | 0 | 0 |  | 18 | 13 | 49 | 0 | 26 | 6 | 5 | 27 | 0 | 0 | 0 | 285 | 270 | 210 | 0 | 0 | 36 | 43 | 0 | 51 | 0 | 33 | 51 | 0 | 0 | 16 | 19 | 100 | 98 | 0 | 0 | 0 | 41 | 29 | 53 | 38 | 112 | 0 | 51 | 0 | 0 | 202 | 17 | 0 | 0 | 265 | 24 | 5 | 0 | 270 | 0 | 0 | 104 | 0 | 149 | 0 | 12 | 155 | 6 | 367 | 97 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 64 | 10 | 320 | 51 | 0 | 144 | 17 | 90 | 17 | 0 | 98 | 0 | 315 | 163 | 0 | 273 | 5 | 778 | 540 | 230 | 0 |  | 803 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 40 | 35 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 38 | 16 | 85 | 35 | 34 | 38 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 171 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 297 | 53 | 0 | 50 | 0 | 49 | 0 | 0 | 95 | 760 | 220 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 383 | 0 | 250 | 1264 | 0 | 0 |  | 9592 | 5766 | 15358 | 4758 | 803 | 2685 | 0 | 2383 | 3908 | 30 | 0 | 686 | 100 | 0 | 5 | 326.61 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 63 | 0 | 406 | 0 |  | 0 | 450 | 298 | 0 | 0 | 40 | 319 | 0 | 200 | 0 | 73 | 146 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 33 | 31 | 16 | 0 | 30 | 0 | 112 | 0 | 25 | 211 | 0 | 0 | 0 |  | 18 | 13 | 51 | 0 | 26 | 6 | 5 | 30 | 0 | 0 | 0 | 285 | 270 | 206 | 0 | 0 | 36 | 44 | 0 | 51 | 0 | 33 | 51 | 0 | 0 | 16 | 19 | 102 | 98 | 0 | 0 | 0 | 43 | 29 | 53 | 36 | 112 | 0 | 51 | 0 | 0 | 202 | 17 | 0 | 0 | 265 | 24 | 5 | 0 | 250 | 0 | 0 | 104 | 0 | 149 | 0 | 12 | 160 | 6 | 366 | 97 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 65 | 10 | 320 | 52 | 0 | 144 | 17 | 90 | 17 | 0 | 97 | 0 | 320 | 163 | 0 | 272 | 5 | 775 | 540 | 230 | 0 |  | 636 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 40 | 47 | 0 | 126 | 9 | 32 | 0 | 0 | 0 | 38 | 30 | 85 | 35 | 34 | 39 | 0 | 32 | 0 | 0 | 11 | 0 | 0 | 206 | 0 | 0 | 172 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 305 | 55 | 0 | 50 | 0 | 56 | 0 | 0 | 95 | 780 | 220 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 378 | 0 | 250 | 1332 | 0 | 0 |  | 9610 | 5733 | 15343 | 4765 | 636 | 2706 | 0 | 2389 | 3993 | 30 | 0 | 717 | 102 | 0 | 5 | 388.685 | 74.96
21:00 | 0 | 0 | 0 | 180 | 0 | 64 | 0 | 404 | 0 |  | 0 | 450 | 300 | 0 | 0 | 40 | 321 | 0 | 201 | 0 | 73 | 147 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 33 | 25 | 16 | 0 | 30 | 30 | 110 | 0 | 25 | 212 | 0 | 0 | 0 |  | 18 | 32 | 51 | 0 | 26 | 6 | 5 | 31 | 0 | 0 | 0 | 285 | 270 | 204 | 0 | 0 | 37 | 45 | 0 | 51 | 0 | 33 | 50 | 0 | 0 | 16 | 19 | 94 | 98 | 0 | 0 | 0 | 43 | 28 | 22 | 20 | 112 | 0 | 51 | 0 | 0 | 202 | 17 | 0 | 0 | 295 | 24 | 5 | 0 | 273 | 0 | 0 | 104 | 0 | 145 | 0 | 12 | 155 | 6 | 366 | 97 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 65 | 10 | 320 | 52 | 0 | 162 | 17 | 88 | 17 | 0 | 97 | 0 | 300 | 163 | 0 | 272 | 0 | 780 | 540 | 230 | 0 |  | 636 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 33 | 62 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 38 | 20 | 80 | 35 | 34 | 45 | 8 | 32 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 177 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 304 | 73 | 0 | 50 | 0 | 56 | 0 | 0 | 95 | 800 | 220 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 378 | 0 | 250 | 1430 | 0 | 0 |  | 9641 | 5909 | 15550 | 4744 | 636 | 2694 | 0 | 2446 | 4140 | 60 | 0 | 736 | 94 | 0 | 0 | 306 | 74.95
22:00 | 0 | 0 | 0 | 180 | 0 | 64 | 0 | 407 | 0 |  | 0 | 450 | 306 | 0 | 0 | 40 | 322 | 0 | 200 | 0 | 82 | 147 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 33 | 26 | 16 | 0 | 30 | 0 | 112 | 0 | 25 | 210 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 26 | 6 | 5 | 25 | 0 | 0 | 0 | 285 | 270 | 207 | 0 | 0 | 37 | 45 | 0 | 51 | 0 | 33 | 50 | 0 | 0 | 16 | 19 | 100 | 96 | 0 | 0 | 0 | 43 | 28 | 20 | 20 | 112 | 0 | 51 | 0 | 0 | 204 | 12 | 0 | 0 | 285 | 17 | 5 | 0 | 283 | 0 | 0 | 106 | 0 | 135 | 0 | 12 | 155 | 6 | 366 | 97 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 65 | 10 | 330 | 52 | 0 | 126 | 17 | 90 | 17 | 0 | 97 | 0 | 310 | 17 | 0 | 276 | 0 | 780 | 540 | 230 | 0 |  | 636 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 0 | 130 | 8 | 32 | 0 | 0 | 0 | 37 | 19 | 75 | 35 | 34 | 47 | 8 | 32 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 174 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 343 | 73 | 0 | 50 | 0 | 56 | 0 | 0 | 95 | 790 | 220 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 380 | 0 | 250 | 1507 | 0 | 0 |  | 9447 | 6004 | 15451 | 4757 | 636 | 2719 | 0 | 2421 | 4213 | 30 | 0 | 575 | 100 | 0 | 0 | 352.395 | 74.94
23:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 403 | 0 |  | 0 | 450 | 307 | 0 | 0 | 40 | 323 | 0 | 197 | 0 | 82 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 33 | 16 | 0 | 30 | 0 | 114 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 26 | 6 | 5 | 21 | 0 | 0 | 0 | 315 | 295 | 186 | 0 | 0 | 32 | 48 | 0 | 51 | 0 | 33 | 51 | 0 | 0 | 16 | 19 | 104 | 97 | 0 | 0 | 0 | 41 | 28 | 0 | 0 | 80 | 0 | 50 | 0 | 0 | 204 | 0 | 0 | 0 | 305 | 16 | 5 | 0 | 288 | 0 | 0 | 107 | 0 | 134 | 0 | 12 | 155 | 5 | 400 | 98 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 65 | 10 | 370 | 52 | 0 | 17 | 17 | 91 | 17 | 0 | 85 | 0 | 295 | 17 | 0 | 275 | 1 | 730 | 540 | 300 | 0 |  | 635 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 0 | 130 | 10 | 32 | 0 | 0 | 0 | 37 | 19 | 75 | 35 | 34 | 45 | 0 | 32 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 184 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 73 | 0 | 50 | 0 | 56 | 0 | 0 | 95 | 810 | 220 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 375 | 0 | 250 | 1480 | 0 | 0 |  | 9102 | 6114 | 15216 | 4904 | 635 | 2811 | 0 | 2117 | 4150 | 30 | 0 | 464 | 104 | 0 | 1 | 462.22 | 74.93
24:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 404 | 0 |  | 0 | 450 | 309 | 0 | 0 | 40 | 324 | 0 | 200 | 0 | 82 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 33 | 33 | 8 | 0 | 30 | 0 | 110 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 24 | 51 | 0 | 26 | 6 | 5 | 29 | 0 | 0 | 0 | 285 | 270 | 212 | 0 | 0 | 35 | 48 | 0 | 51 | 0 | 34 | 34 | 0 | 0 | 16 | 19 | 104 | 97 | 0 | 0 | 0 | 35 | 20 | 0 | 0 | 80 | 0 | 56 | 0 | 0 | 181 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 290 | 0 | 0 | 107 | 0 | 133 | 0 | 12 | 155 | 6 | 327 | 98 | 17 | 17 | 0 | 16 | 17 | 24 | 114 | 28 | 10 | 340 | 17 | 0 | 17 | 17 | 45 | 17 | 0 | 53 | 0 | 275 | 17 | 0 | 280 | 0 | 640 | 540 | 350 | 0 |  | 635 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 0 | 130 | 10 | 32 | 0 | 0 | 0 | 37 | 20 | 75 | 35 | 34 | 45 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 179 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 73 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 960 | 220 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 250 | 1511 | 0 | 0 |  | 8586 | 6058 | 14644 | 4617 | 635 | 2866 | 0 | 1682 | 4246 | 30 | 0 | 464 | 104 | 0 | 0 | 817.48 | 74.92
KWH | 0 | 0 | 1156125 | 4142250 | 0 | 593818 | 0 | 9075600 | 0 |  | 0 | 10245000 | 7173993 | 0 | 0 | 982751 | 7600259 | 0 | 4045000 | 0 | 1154592 | 1158240 | 0 | 0 | 0 | 0 | 233280 | 251933 | 249498 | 0 | 408000 | 327240 | 692940 | 726100 | 283200 | 0 | 720480 | 28000 | 2700000 | 0 | 206971 | 5006664 | 0 | 0 | 0 |  | 380160 | 714720 | 1009034 | 0 | 294720 | 151200 | 109680 | 527520 | 0 | 0 | 0 | 7509200 | 6665000 | 5012000 | 0 | 0 | 876024 | 1093440 | 0 | 1132877 | 0 | 752912 | 809712 | 0 | 0 | 368200 | 440970 | 2603520 | 1828800 | 0 | 0 | 15550 | 958000 | 654840 | 1084200 | 802152 | 2403082 | 0 | 1266720 | 0 | 0 | 4107610 | 368000 | 0 | 0 | 7118000 | 503280 | 177504 | 0 | 5399564 | 0 | 0 | 1773600 | 0 | 3054384 | 107595 | 286080 | 2762880 | 148872 | 8860000 | 1576800 | 854400 | 423200 | 30480 | 386400 | 450879 | 509340 | 1762440 | 1079400 | 265920 | 8277000 | 815040 | 317410 | 986400 | 416509 | 1492854 | 510120 | 212587 | 1294080 | 0 | 6850000 | 930036 | 0 | 6594544 | 133440 | 16181818 | 9698636 | 8672991 | 477982 |  | 18608000 | 0 | 8798976 | 0 | 0 | 0 | 0 | 0 | 356160 | 456960 | 0 | 2789000 | 224890 | 726528 | 0 | 0 | 0 | 562855 | 239391 | 999968 | 766200 | 621785 | 411492 | 32021 | 477349 | 0 | 0 | 258246 | 0 | 0 | 5300000 | 0 | 0 | 4400264 | 0 | 3459627 | 0 | 0 | 0 | 0 | 0 | 8592800 | 1274400 | 0 | 1672320 | 0 | 1010400 | 0 | 50934 | 802848 | 23503800 | 5006891 | 0 | 260400 | 36240 | 707040 | 996480 | 0 | 0 | 8349091 | 247688 | 5061800 | 23121818 | 1353220 | 0 |  | 204494242 | 131537882 | 336032124 | 111911973 | 18608000 | 64370290 | 0 | 37917707 | 88112871 | 748480 | 0 | 8069117 | 2603520 | 3556726 | 133440 | 0
Fuel Cost | 0 | 0 | 4959776.25 | 18433012.5 | 0 | 2268384.76 | 0 | 26137728 | 0 |  | 0 | 32579100 | 24535056.06 | 0 | 0 | 17316072.62 | 23180789.95 | 0 | 21640750 | 0 | 20724926.4 | 22493020.8 | 0 | 0 | 0 | 0 | 4259692.8 | 3970464.08 | 4563318.42 | 0 | 306000 | 0 | 0 | 0 | 5072112 | 0 | 0 | 0 | 14742000 | 0 | 3920030.74 | 15971258.16 | 0 | 0 | 0 |  | 6687014.4 | 12586219.2 | 18071798.94 | 0 | 5767670.4 | 2488752 | 408009.6 | 0 | 0 | 0 | 0 | 20950668 | 20394900 | 16639840 | 0 | 0 | 2952200.88 | 4789267.2 | 0 | 4542836.77 | 0 | 13484653.92 | 14623398.72 | 0 | 0 | 1369704 | 330727.5 | 17079091.2 | 5687568 | 0 | 0 | 0 | 3736200 | 2442553.2 | 4933110 | 3649791.6 | 8218540.44 | 0 | 7030296 | 0 | 0 | 11460231.9 | 2421440 | 0 | 0 | 21994620 | 377460 | 134903.04 | 0 | 110151105.6 | 0 | 0 | 34070856 | 0 | 53787702.24 | 0 | 5095084.8 | 47935968 | 2468297.76 | 23479000 | 30053808 | 16028544 | 7592208 | 0 | 6317640 | 8765087.76 | 9137559.6 | 33680228.4 | 20951154 | 4736035.2 | 22016820 | 13912732.8 | 0 | 18041256 | 6989021.02 | 5583273.96 | 9115844.4 | 0 | 23319321.6 | 0 | 20344500 | 13094906.88 | 0 | 45963971.68 | 0 | 95472726.2 | 0 | 0 | 0 |  | 52288480 | 0 | 25956979.2 | 0 | 0 | 0 | 0 | 0 | 6699369.6 | 8595417.6 | 0 | 8813240 | 1065978.6 | 12525342.72 | 0 | 0 | 0 | 10080733.05 | 4392824.85 | 16809462.08 | 16304736 | 11857439.95 | 7369821.72 | 566771.7 | 8549320.59 | 0 | 0 | 195492.222 | 0 | 0 | 44732000 | 0 | 0 | 14520871.2 | 0 | 11520557.91 | 0 | 0 | 0 | 0 | 0 | 25090976 | 21766752 | 0 | 33145382.4 | 0 | 20127168 | 0 | 0 | 15928504.32 | 152304624 | 15571431.01 | 0 | 5038740 | 0 | 0 | 17288928 | 0 | 0 | 60948364.3 | 0 | 37710410 | 152835216.98 | 0 | 0 |  | 1190431614.35 | 820601336.002 | 2011032950.352 | 354138751.472 | 52288480 | 149239092.44 | 0 | 706092672.85 | 589967313.16 | 0 | 0 | 142227549.23 | 17079091.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 21 | 0 | 374 | 0 |  | 0 | 450 | 298 | 0 | 0 | 32 | 308 | 0 | 189 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 25 | 16 | 0 | 30 | 0 | 114 | 0 | 4 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 12 | 6 | 5 | 16 | 0 | 0 | 0 | 310 | 260 | 207 | 0 | 0 | 36 | 47 | 0 | 51 | 0 | 35 | 32 | 0 | 0 | 16 | 19 | 102 | 66 | 0 | 0 | 2 | 40 | 27 | 53 | 36 | 112 | 0 | 56 | 0 | 0 | 203 | 17 | 0 | 0 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 57 | 0 | 128 | 15 | 12 | 100 | 6 | 396 | 48 | 17 | 17 | 5 | 16 | 17 | 17 | 62 | 38 | 12 | 370 | 17 | 44 | 35 | 17 | 80 | 17 | 30 | 52 | 0 | 300 | 24 | 0 | 270 | 7 | 779 | 250 | 583 | 70 |  | 921 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 37 | 14 | 34 | 7 | 0 | 30 | 0 | 0 | 11 | 0 | 0 | 203 | 0 | 0 | 156 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 48 | 0 | 7 | 25 | 700 | 220 | 0 | 0 | 4 | 95 | 55 | 0 | 0 | 340 | 34 | 150 | 751 | 184 | 0 |  | 13837 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 64 | 0 | 404 | 0 |  | 0 | 450 | 300 | 0 | 0 | 40 | 321 | 0 | 201 | 0 | 73 | 147 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 33 | 25 | 16 | 0 | 30 | 30 | 110 | 0 | 25 | 212 | 0 | 0 | 0 | 0 | 18 | 32 | 51 | 0 | 26 | 6 | 5 | 31 | 0 | 0 | 0 | 285 | 270 | 204 | 0 | 0 | 37 | 45 | 0 | 51 | 0 | 33 | 50 | 0 | 0 | 16 | 19 | 94 | 98 | 0 | 0 | 0 | 43 | 28 | 22 | 20 | 112 | 0 | 51 | 0 | 0 | 202 | 17 | 0 | 0 | 295 | 24 | 5 | 0 | 273 | 0 | 0 | 104 | 0 | 145 | 0 | 12 | 155 | 6 | 366 | 97 | 105 | 17 | 0 | 16 | 36 | 34 | 114 | 65 | 10 | 320 | 52 | 0 | 162 | 17 | 88 | 17 | 0 | 97 | 0 | 300 | 163 | 0 | 272 | 0 | 780 | 540 | 230 | 0 |  | 636 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 33 | 62 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 38 | 20 | 80 | 35 | 34 | 45 | 8 | 32 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 177 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 304 | 73 | 0 | 50 | 0 | 56 | 0 | 0 | 95 | 800 | 220 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 378 | 0 | 250 | 1430 | 0 | 0 |  | 15550 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 400 | 0 |  | 0 | 450 | 305 | 0 | 0 | 40 | 335 | 0 | 200 | 0 | 82 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 22 | 33 | 33 | 16 | 0 | 30 | 0 | 115 | 0 | 25 | 211 | 0 | 0 | 0 |  | 18 | 50 | 51 | 0 | 25 | 18 | 5 | 30 | 0 | 0 | 0 | 300 | 280 | 220 | 0 | 0 | 40 | 50 | 0 | 51 | 0 | 41 | 52 | 0 | 0 | 33 | 20 | 144 | 100 | 0 | 0 | 0 | 43 | 30 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 210 | 18 | 0 | 0 | 300 | 25 | 5 | 0 | 300 | 0 | 0 | 108 | 0 | 149 | 0 | 12 | 150 | 6 | 400 | 107 | 105 | 34 | 0 | 16 | 36 | 34 | 114 | 65 | 12 | 380 | 72 | 0 | 162 | 17 | 95 | 35 | 0 | 95 | 0 | 300 | 163 | 0 | 275 | 40 | 580 | 500 | 500 |  |  | 650 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 38 | 25 | 95 | 35 | 34 | 50 | 8 | 33 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 77 | 0 | 56 | 0 | 0 | 55 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 375 | 0 | 307 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 400 | 0 | 0 | 0 | 450 | 305 | 0 | 0 | 40 | 335 | 0 | 200 | 0 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 33 | 33 | 16 | 0 | 30 | 0 | 115 | 0 | 8 | 211 |  | 0 | 0 | 0 | 12 | 32 | 51 | 0 | 12 | 6 | 5 | 15 | 0 | 0 | 0 | 300 | 280 | 220 | 0 | 0 | 40 | 50 | 0 | 51 | 0 | 33 | 34 | 0 | 0 | 33 | 20 | 146 | 70 | 0 | 0 | 1.6 | 43 | 30 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 210 | 18 | 0 | 0 | 300 | 25 | 5 | 0 | 300 | 0 | 0 | 56 | 0 | 130 | 20 | 12 | 100 | 6 | 400 | 50 | 35 | 17 | 5 | 16 | 13 | 17 | 52 | 55 | 12 | 380 | 53 | 50 | 35 | 17 | 95 | 17 | 35 | 36 | 0 | 300 | 54 | 0 | 275 | 40 | 580 | 500 | 590 | 33 |  | 939 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 38 | 0 | 50 | 35 | 34 | 40 | 8 | 30 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 35 | 0 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 375 | 30 | 150 | 1400 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 389 | 0 | 0 | 0 | 450 | 307 | 0 | 0 | 15 | 270 | 0 | 121 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 110 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 12 | 24 | 51 | 0 | 0 | 6 | 5 | 3 | 0 | 0 | 0 | 285 | 270 | 217 | 0 | 0 | 35 | 51 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 16 | 19 | 114 | 94 | 0 | 0 | 1 | 42 | 20 | 50 | 15 | 80 | 0 | 62 | 0 | 0 | 206 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 71 | 5 | 12 | 85 | 6 | 330 | 49 | 17 | 0 | 2 | 16 | 17 | 17 | 25 | 28 | 10 | 340 | 0 | 20 | 0 | 17 | 50 | 0 | 12 | 35 | 0 | 270 | 0 | 0 | 267 | 2 | 598 | 400 | 350 | 30 | 0 | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 230 | 0 | 0 | 164 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 18 | 0 | 33 | 0 | 3 | 18 | 780 | 180 | 0 | 0 | 2 | 44 | 0 | 0 | 0 | 340 | 10 | 150 | 1119 | 36 | 0 | 0 |  |  |  | 176282263 | 18608000 | 0 | 88112871 | 45986824 | 2603520 | 3556726 | 133440 | 748480 |  |  | 336032124
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 | [5 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 176.2823 | 18.608 | 0 | 88.1129 | 45.9868 | 2.6035 | 3.5567 | 0.13344 | 0.74848
| Minimum Generation |  | 12647 | 9:00
| Highest Generation |  | 15550 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 336.0321
| Day Peak Generation |  | 13837 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15550 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 921 | 4:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 636 | 21:00
| Load factor L.F |  | 90.04% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-04-27
Till now the maximum generation is : - |  |  |  | 16233 | 21:00 | Hrs on | 2024-04-22
The Summary of Yesterday's |  |  | 2024-04-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13837 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12445
Evening Peak Generation : |  |  | 15550 | MW Hour : | 21:00 | Available Max Generation : |  | 16908
E.P. Demand (at gen end) : |  |  | 15870 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16600
Maximum Generation : |  |  | 15550 | MW Hour : | 21:00 | Reserve(Generation end) |  | 308
Total Gen. (MKWH) : |  |  | 336.0321 | System Load Factor : | 90.04% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 710 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-04-27
Actual : |  | 74.86 | Ft.(MSL) , | Rule curve : | 82.8 | Ft.( MSL )
Gas Consumed : |  | Total = | 1322.59 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 503377843.912
: |  |  | Coal : | 589967313.16 | Oil : | 848320222.08 | Total : | 1941665379.152
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5342.4914 |  |  | 0 | -7.08%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | -5.279%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | -4.894%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | -4.488%
Cumilla Area |  | 45 | 1080:00 | 1476.7776 |  |  | 0 | -4.74%
Mymensingh Area |  | 145 | 3480:00 | 1099.0436 |  |  | 0 | -4.387%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | -5.061%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | 0%
Rangpur Area |  | 116 | 2784:00 | 1004.2252 |  |  | 0 | -4.331%
Total |  | 306 |  | 15383.887 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:13 | Siddhirganj 132/33kV S/S T-1 HT is restored.
| 09:14 | Madaripur 132/33kV S/S T3-426T HT is restored.
09:22 | 10:36 | Siddhirganj 132/33kV S/S T-2 HT Scheduled S/D Due to Corrective maintenance due to abnormal thermal issue in different point
| 10:05 | Pabna 132/33kV S/S T-3 HT is restored.
| 10:32 | Fenchuganj 230/132/33kV S/S TR-02 HT is restored.
| 12:21 | Agargaon 230/132kV S/S 132kV Transformer-2 (415T2) HT is restored.
15:08 | 17:23 | Gopalganj 132/33kV S/S T1 LT Forced S/D Due to Gopalganj PBS-4 Red hot maintenance work. |  |  |  |  | 20 MW load interrup.
15:40 |  | Meghnaghat CCPP(Summit)-2 Tripped
| 16:13 | Bashundhara-Rampura 132 kV Ckt-1 is restored.
| 16:20 | Candpur- Kachua 132kV Ckt-2 is restored.
| 16:20 | Candpur- Kachua 132kV Ckt-1 is restored.
17:36 |  | Meghnaghat CCPP(Summit)-2 Syncronized
| 18:52 | Gopalganj(N)-Payra 400KV Ckt-1 is restored.
| 18:54 | Gopalganj 400/132kV S/S 400kV Payra Ckt-1 is restored.
00:23 |  | Khulna (C) S/S TR-1 425T HT Tripped showing differential relay, 86T relays Due to underground couple fault red phase |  |  |  |  | 30 MW load interrup.
03:19 |  | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Forced S/D from Bog-Sherpur 132/33kV end.
06:07 |  | Daudkandi-Sonargaon 132 kV Ckt-2 S/D from Sonargaon 132/33kV end Due to Shutdown taken by Daudkandi Grid S/S.
06:07 |  | Daudkandi-Sonargaon 132 kV Ckt-1 S/D from Sonargaon 132/33kV end Due to Shutdown taken by Daudkandi S/S
06:08 |  | Mymensingh 132/33kV S/S Transformer-3 S/D Due to High temperature maintenance of T3-HV bush(Y ph),LV bus(B ph), 33kV
bus DS(RYB ph)
06:10 |  | Gopalganj 400/132kV S/S 400kV Payra Ckt-1 Scheduled S/D Due to Maintenance at Payra-end
07:15 |  | Daudkandi 132/33kV S/S Main Forced S/D Due to Remove Nest |  |  |  |  | 110 MW load interrup.
07:20 |  | Gopalganj(N)-Madaripur 132kV Ckt-1 Scheduled S/D from Madaripur 132/33kV end Due to TCS Relay Installation
07:35 |  | Cumilla(S) 132/33kV S/S TR-3 LT Scheduled S/D Due to 33KV Kaliajuri PDB feeder DS- Bus loop Change at Tr-03 Bus . |  |  |  |  | 20 MW load interrup.
21:12 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Tripped showing |  |  |  |  | 70.0MW
|  | lockout relay relays Due to CT of 33kV was damage |  |  |  |  | load
interrup.
06:02 |  | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to |  |  |  |  | 14.0MW
|  | 33 kV Bus coupler rearrange |  |  |  |  | load
interrup.
06:03 |  | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to |  |  |  |  | 14.0MW
|  | 33 kV Bus coupler rearrange |  |  |  |  | load
interrup.
07:00 |  | Minimum generation 12387 MW
07:02 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
33kV Underground Cable Replace
07:11 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
33kV Underground Cable Replace
07:17 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to |  |  |  |  | 20.0MW
|  | 33kV Busbar Maintenance |  |  |  |  | load
interrup.
07:18 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to |  |  |  |  | 20.0MW
|  | 33kV Busbar Maintenance |  |  |  |  | load
interrup.
07:40 |  | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to |  |  |  |  | 20.0MW
|  | Maintenance Work |  |  |  |  | load
interrup.
07:40 |  | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to |  |  |  |  | 20.0MW
|  | Maintenance Work |  |  |  |  | load

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-04-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 1156125
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4142250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 64 | 593818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 404 | 9075600
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10245000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7173993 | Machine problem
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 982751 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 201 | 4045000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 321 | 7600259
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 73 | 1154592 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 233280
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1158240
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 251933
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 249498
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 735240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 692940
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 726100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 283200 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 273 | 5399564 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 145 | 3054384
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 854400
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 52 | 815040 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 986400
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 212587
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Engine problem
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 540 | 9698636
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 230 | 8672991 | On test.
| Dhaka area Total |  |  |  | 5332 | 3958 | 80193821
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 206971
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 107595
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 151200 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 748480 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 212 | 5006664
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 423200 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 714720 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1009034 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired from 17/04/2024
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 286080 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 5 | 109680 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 527520
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 26 | 294720 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30480
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 386400 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 450879 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 509340 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 265920 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 416509 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 930036
60 | SS Power I |  | SS Power | 2*612 | 1224 | 272 | 6594544
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 133440 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 780 | 16181818
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 477982
| Chattogram area Total |  |  |  | 4404 | 1915 | 38663212
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 204 | 5012000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7509200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6665000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 6850000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 876024 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 45 | 1093440 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1132877
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 148872 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 752912 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 2762880 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 94 | 2603520
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 368200 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 50 | 809712
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 19 | 440970 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1762440
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 65 | 1079400 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 510120 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 1294080 | Fuel shortage
| Cumilla Area Total |  |  |  | 2929 | 1858 | 41671647
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 98 | 1828800 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15550
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 104 | 1773600 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1576800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 317410
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 380160 | Engine problem
| Mymensingh Area Total |  |  |  | 592 | 317 | 5892320
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 958000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 654840 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2403082 | ST under maint
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 22 | 1084200 | Line O/L
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 20 | 802152 | Line O/L
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 177504 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 51 | 1266720
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 88 | 1492854
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 202 | 4107610 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 368000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 503280
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7118000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8860000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 8277000 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1593 | 38073242
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 636 | 18608000
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 356160 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 62 | 456960 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8798976 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 73 | 1274400 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 707040
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 378 | 8349091
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1527 | 38550627
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 726528 | Mengnaghat Bus section limitation.
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 224890 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2789000 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 800 | 23503800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5006891
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 260400 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 5061800 | Mengnaghat Bus section limitation.
| Barisal Area Total |  |  |  | 2235 | 1455 | 37573309
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 562855 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 239391 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 766200
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 621785 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 411492 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 177 | 4400264 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 3459627
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 304 | 8592800 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 477349 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 258246
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 32021 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 999968 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 1672320 | Fuel shortage
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 802848 | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 36240
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1430 | 23121818
| Rajshahi Area Total |  |  |  | 3431 | 2547 | 46455224
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5300000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 56 | 1010400 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50934
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 996480 | Fuel shortage
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 247688
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1353220
| Rangpur Area Total |  |  |  | 950 | 380 | 8958722
| Total |  |  |  | 25903 | 15550 | 336032124
| Eastern Grid Total |  |  |  | 15588 | 9641 | 204494242
| Western Grid Total |  |  |  | 10315 | 5909 | 131537882
| National Grid Total |  |  |  | 25903 | 15550 | 336032124
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-04-26
| (a) ENTIRE EASTERN GRID : |  | 9721.52 | MW | (b) ENTIRE WESTERN GRID : |  | 5133.4 | MW
| i) Dhaka area |  | 5175.62 | MW | i) Khulna area |  | 1941 | MW
| ii) Chittagong area |  | 1326.9 | MW | ii) Rajshahi area |  | 1797.4 | MW
| iii) Comilla area |  | 1474 | MW | iii) Barisal area |  | 485 | MW
| iv) Mymensingh area |  | 1218 | MW | iv) Rangpur area |  | 910 | MW
| v) Sylhet area |  | 527 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14854.92 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 37 | 20:00 | Kalurghat | 30 | 02:00 | Narail | 68 | 00:00 | Shariatpur | 97 | 00:00
2 | AKSML | 10 | 14:00 | Chowmuhani | 226 | 18:30 | Kamrangirchar | 48 | 00:00 | Narinda | 61 | 00:00 | Sherpur | 172 | 19:00
3 | Aftabnagar | 44 | 00:00 | Chuadanga | 115 | 21:00 | Kaptai | N/A | N/A | Narshingdi | 181 | 19:00 | Shikalbaha | 25 | 01:00
4 | Agargaon | 120 | 00:00 | Coxsbazar | 127 | 11:00 | Kazla | 107 | 15:00 | Natore | 176 | 19:30 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 70 | 20:00 | Cumilla(N) | 187 | 21:00 | Keranigonj | 86 | 00:00 | Nawabganj | 55.6 | 21:00 | Shitalakhya | 91.4 | 00:00
6 | Amnura | 94 | 21:00 | Cumilla(S) | 176 | 04:00 | Khagrachori | 34 | 19:00 | Netrakona | 101 | 05:00 | Sholosohor | 39 | 19:00
7 | Ashuganj | 95 | 05:00 | Daudkandi | 156 | 20:00 | Khulna | 86 | 13:00 | New | 28.5 | 00:00 | Shyampur | 160 | 07:00
8 | BIPTC | N/A | N/A | Dhaka | 14 | 00:00 | Khulshi | 177 | 00:00 | Niamatpur | 128 | 19:30 | Siddhirganj | 118 | 00:00
9 | BSRM | 156 | 12:00 | Dhamrai | 132 | 20:00 | Kishoreganj | 149 | 19:30 | Noapara | 52.5 | 00:00 | Sirajganj | 126 | 21:00
10 | Bagerhat | 99 | 02:00 | Dhanmondi | 129.3 | 19:00 | Kodda | 258 | 19:00 | PHP | 4 | 16:00 | Sonargaon | 74 | 00:00
11 | Bakulia | 94 | 21:00 | Dohazari | 108 | 20:00 | Kulaura | 50 | 18:30 | Pabna | 134 | 22:00 | Sreemongol | 81 | 19:30
12 | Banani | 32.4 | 00:00 | Faridpur | 178 | 01:00 | Kurigram | 63 | 19:00 | Palashbari | 130 | 10:00 | Sreepur | 67 | 19:00
13 | Bangabhaban | 4 | 12:00 | Fatullah | 64 | 00:00 | Kushtia | 158 | 20:00 | Panchagarh | 56 | 20:00 | Srinagar | 51.88 | 22:00
14 | Barapukuria | 77 | 11:00 | Fenchuganj | 42 | 20:00 | Lalbag | 89 | 00:00 | Patuakhali | 98 | 00:00 | Sunamganj | 52 | 19:00
15 | Barguna | 24 | 00:00 | Feni | 129 | 18:30 | Lalmonirhat | 60 | 17:00 | Payra | 28 | 00:00 | Sylhet | 40 | 18:00
16 | Barishal | 123 | 00:00 | GPH | 76 | 19:30 | MI_Cement | 11.6 | 21:00 | Postogola | 63 | 00:00 | Sylhet-132 | 113 | 19:30
17 | Barishal-230 | 110 | 00:00 | Ghatail | 52 | 22:00 | Madanganj | 37 | 13:00 | Purbachal | 25 | 23:00 | TK | 32.4 | 21:00
18 | Baroaulia | 68 | 06:00 | Ghorashal | 72 | 19:00 | Madaripur | 131 | 00:00 | Purbasadipur | 145 | 12:00 | Tangail | 248 | 21:00
19 | Baroirhat | 66 | 19:00 | Goalpara | 42 | 00:00 | Madartek | 100 | 00:00 | Rahim | 25 | 08:00 | Thakurgaon | 103 | 20:00
20 | Bashundhara | 194 | 00:00 | Gollamari | 86 | 00:00 | Madunaghat | 53 | 21:00 | Rajbari | 84 | 00:00 | Tongi | 152 | 18:30
21 | BashundharaCement | 7 | 00:00 | Gopalganj | 123.5 | 22:00 | Magura | 73 | 22:00 | Rajendrapur | 106 | 23:00 | Ullahpara | 29 | 19:30
22 | Beanibazar | 72 | 19:00 | Gulshan | 112 | 15:00 | Mahasthangarh | 92 | 22:00 | Rajshahi | 184 | 21:00 | Ullon | 68 | 00:00
23 | Benapole | 78 | 21:00 | Halishahar | 67.5 | 21:00 | Manikganj | 142 | 20:00 | Rajshahi-230 | 44 | 22:00 | Uttara | 103 | 19:00
24 | Bhaluka | 112 | 09:00 | HaripurSBU | 145 | 09:00 | Maniknagar | 72 | 00:00 | Ramganj | 118 | 21:00 | UttaraNew | 63 | 23:00
25 | Bhandaria | 57 | 00:00 | Hasnabad | 95 | 00:00 | Matarbari | 50 | 21:00 | Rampur | 34 | 00:00 | Zigatola | 93 | 00:00
26 | Bhangura | 52 | 19:00 | Hathazari | 76 | 18:00 | Matuail | 72 | 00:00 | Rangamati | 18 | 18:30
27 | Bheramara(GK) | 74 | 22:00 | Ishurdi | 80 | 21:00 | Millgate | 116 | 00:00 | Rangpur | 134 | 14:00
28 | Bhulta | 208 | 02:00 | Jaldhaka | 90 | 18:30 | Mirpur | 163 | 16:00 | Ruppur | 6 | 10:00
29 | Bog-Sherpur | 80 | 19:30 | Jamalpur | 150 | 19:30 | Mirsorai | 8 | 00:00 | SSM | 13 | 00:00
30 | Bogura | 196 | 22:00 | Jashore | 159 | 19:30 | Mirzapur | 48 | 19:30 | Saidpur | 103 | 10:00
31 | Borhanuddin | 88 | 21:00 | Jhenaidah | 152 | 19:00 | Mithapukur | 68 | 18:30 | Satkhira | 146 | 21:00
32 | Brahmanbaria | 200 | 20:00 | Joydebpur | 204 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 131 | 00:00
33 | Cantonment | 162 | 16:00 | Joypurhat | 80 | 20:00 | Mogbazar | 132.3 | 17:00 | Savar | 183 | 19:00
34 | Chandpur | 80 | 22:00 | Juldah | 20 | 02:00 | Mongla | 34 | 00:00 | SevenRings | 17.33 | 00:00
35 | Chandraghona | 36 | 19:30 | KSRM | 24 | 06:00 | Motijheel | 49 | 00:00 | ShahCement | 31 | 08:00
36 | Chapai | 88 | 21:00 | Kabirpur | 266 | 15:00 | Munshiganj | 118 | 23:00 | Shahjadpur | 98 | 22:00
37 | Charsaidpur | 44 | 01:00 | Kachua | 93 | 21:00 | Mymensingh | 250 | 21:00 | Shahjibazar | 134 | 23:00
38 | Chauddagram | 83 | 20:00 | Kallyanpur | 129 | 23:00 | Naogaon | 155 | 21:00 | Shahmirpur | 51 | 05:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-04-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 393 | 07:00 | 378 | 15:00 | Kaliakoir | 402 | 11:00 | 391 | 18:00
| Ashuganj | 401 | 9:00 | 394 | 20:00 | Madunaghat_I | 394 | 16:00 | 384 | 03:00
| Bhulta | 397 | 06:00 | 387 | 12:00 | Meghnaghat | 405 | 8:00 | 394 | 19:30
| Bibiana | 399 | 19:30 | 388 | 15:00 | Payra | 414 | 08:00 | 407 | 00:00
| BIPTC | 405 | 20:00 | 389 | 15:00 | Rahanpur | 385 | 00:00 | 362 | 22:00
| Bogura | 368 | 00:00 | 344 | 22:00 | Rampal | 401 | 07:00 | 390 | 13:00
| Gopalganj | 401 | 06:00 | 387 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 06:00 | 218 | 12:00 | Hasnabad | 227 | 05:00 | 219 | 15:00
| AKSML | 223 | 19:00 | 218 | 12:00 | Hathazari | 222 | 16:00 | 218 | 12:00
| Aminbazar | 227 | 06:00 | 218 | 15:00 | Ishurdi | 235 | 00:00 | 227 | 19:00
| Ashuganj | 237 | 13:00 | 228 | 06:00 | Jhenaidah | 225 | 06:00 | 212 | 19:00
| Ashuganj-400 | 230 | 9:00 | 222 | 20:00 | Kaliakoir | 229 | 11:00 | 214 | 19:00
| Baghabari | 231 | 00:00 | 224 | 18:30 | Keranigonj | 226 | 06:00 | 218 | 15:00
| Barapukuria | 216 | 13:00 | 204 | 22:00 | Khulna(S) | 228 | 08:00 | 217 | 23:00
| Barapukuria-230 | 229 | 6:00 | 212 | 17:00 | Madunaghat_I | 222 | 16:00 | 218 | 02:00
| Barishal | 240 | 06:00 | 232 | 23:00 | Maniknagar | 228 | 06:00 | 222 | 12:00
| Bheramara | 235 | 00:00 | 225 | 19:00 | Meghnaghat | 236 | 07:00 | 230 | 00:00
| Bhulta | 230 | 06:00 | 223 | 12:00 | Meghnaghat-400 | 232 | 4:00 | 218 | 17:00
| Bibiana | 230 | 07:00 | 224 | 12:00 | Mirsorai | 228 | 19:30 | 218 | 01:00
| BIPTC | 235 | 00:00 | 224 | 19:00 | Rajshahi | 232 | 00:00 | 223 | 12:00
| Bogura | 228 | 14:00 | 214 | 22:00 | Rampal | 228 | 08:00 | 220 | 13:00
| Bogura-400 | 229 | 00:00 | 216 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 242 | 07:00 | 236 | 21:00 | Rampura | 227 | 03:00 | 221 | 12:00
| BSRM | 228 | 19:30 | 217 | 12:00 | Shikalbaha | 220 | 20:00 | 215 | 01:00
| Cumilla(N) | 228 | 18:00 | 221 | 12:00 | Shyampur | 228 | 07:00 | 221 | 12:00
| Fenchuganj | 233 | 07:00 | 228 | 01:00 | Siddhirganj | 230 | 05:00 | 224 | 15:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 236 | 00:00 | 232 | 19:00
| Ghorashal-230 | 228 | 04:00 | 223 | 15:00 | Sreepur | 228 | 08:00 | 224 | 12:00
| GPH | 224 | 19:30 | 216 | 12:00 | Tongi | 226 | 07:00 | 216 | 11:00
| Haripur | 228 | 03:00 | 222 | 12:00
| 132 kV | 134 | 17:00 | 130 | 11:00 | 132 kV | 131 | 19:00 | 115 | 11:00
| Aftabnagar | 135 | 00:00 | 130 | 19:00 | Kushtia | 129 | 00:00 | 115 | 22:00
| Agargaon | 135 | 00:00 | 131 | 19:00 | Lalbag | 137 | 09:00 | 124 | 19:00
| Agrabad | 126 | 18:00 | 121 | 12:00 | Lalmonirhat | 125 | 17:00 | 116 | 1:00
| AKS | 133 | 00:00 | 123 | 22:00 | Madanganj | 125 | 18:00 | 120 | 11:00
| Aminbazar | 134 | 00:00 | 113 | 19:00 | Madaripur | 130 | 00:00 | 122 | 19:00
| Amnura | 135 | 01:00 | 125 | 22:00 | Madartek | 133 | 01:00 | 127 | 12:00
| Ashuganj | 126 | 17:00 | 120 | 23:00 | Madunaghat | 121 | 19:30 | 113 | 12:00
| Bagerhat | 132 | 06:00 | 126 | 12:00 | Magura | 135 | 9:00 | 126 | 12:00
| Bakulia | 131 | 15:00 | 117 | 01:00 | Mahasthangarh | 131 | 13:00 | 122 | 21:00
| Banani | 130 | 17:00 | 125 | 12:00 | Manikganj | 136 | 05:00 | 125 | 19:00
| Bangabhaban | 130 | 00:00 | 117 | 22:00 | Maniknagar | 134 | 08:00 | 126 | 23:00
| Barapukuria | 133 | 18:00 | 127 | 12:00 | Matarbari | 127 | 13:00 | 114 | 22:00
| Barguna | 129 | 18:00 | 118 | 13:00 | Matuail | 132 | 00:00 | 112 | 10:00
| Barishal | 129 | 04:00 | 124 | 18:30 | Millgate | 135 | 18:00 | 128 | 00:00
| Barishal-230 | 126 | 17:00 | 112 | 02:00 | Mirpur | 136 | 08:00 | 132 | 00:00
| Baroaulia | 130 | 08:00 | 116 | 19:00 | Mirzapur | 127 | 16:00 | 113 | 02:00
| Baroirhat | 121 | 19:00 | 111 | 12:00 | Mithapukur | 133 | 07:00 | 128 | 12:00
| Bashundhara | 133 | 18:00 | 126 | 02:00 | MI_Cement | 134 | 07:00 | 124 | 12:00
| BashundharaCement | 131 | 18:00 | 124 | 02:00 | Modern | 125 | 00:00 | 110 | 06:00
| Beanibazar | 127 | 18:00 | 117 | 23:00 | Mogbazar | 135 | 00:00 | 125 | 22:00
| Benapole | 134 | 06:00 | 129 | 12:00 | Mongla | 133 | 07:00 | 129 | 12:00
| Bhaluka | 134 | 06:00 | 124 | 12:00 | Motijheel | 132 | 08:00 | 126 | 19:00
| Bhandaria | 133 | 18:00 | 129 | 12:00 | Munshiganj | 138 | 19:30 | 129 | 13:00
| Bhangura | 128 | 19:00 | 122 | 09:00 | Mymensingh | 132 | 00:00 | 124 | 19:00
| Bheramara | 133 | 08:00 | 127 | 23:00 | Naogaon | 133 | 00:00 | 113 | 22:00
| Bheramara(GK) | 132 | 07:00 | 128 | 12:00 | Narail | 126 | 18:00 | 112 | 02:00
| Bhulta | 133 | 01:00 | 130 | 02:00 | Narinda | 130 | 18:00 | 125 | 13:00
| Bog-Sherpur | 124 | 18:00 | 115 | 02:00 | Narshingdi | 133 | 06:00 | 126 | 12:00
| Bogura | 130 | 19:30 | 121 | 15:00 | Natore | 128 | 08:00 | 123 | 12:00
| Bogura-230 | 136 | 04:00 | 132 | 13:00 | Nawabganj | 125 | 00:00 | 114 | 22:00
| Brahmanbaria | 139 | 08:00 | 128 | 13:00 | Netrakona | 136 | 05:00 | 131 | 13:00
| Cantonment | 138 | 08:00 | 130 | 19:00 | New | 124 | 00:00 | 113 | 07:00
| Chandpur | 134 | 08:00 | 128 | 13:00 | Niamatpur | 133 | 08:00 | 121 | 23:00
| Chandraghona | 134 | 06:00 | 129 | 15:00 | Noapara | 132 | 06:00 | 126 | 15:00
| Chapai | 133 | 06:00 | 128 | 12:00 | Pabna | 134 | 19:30 | 126 | 12:00
| Charsaidpur | 130 | 18:00 | 125 | 12:00 | Palashbari | 137 | 06:00 | 133 | 11:00
| Chauddagram | 133 | 07:00 | 129 | 12:00 | Panchagarh | 133 | 18:00 | 127 | 12:00
| Chhatak | 133 | 07:00 | 124 | 05:00 | Patuakhali | 137 | 00:00 | 132 | 23:00
| Chowmuhani | 132 | 03:00 | 128 | 13:00 | Payra | 125 | 01:00 | 121 | 19:00
| Chuadanga | 131 | 08:00 | 127 | 19:00 | PHP | 132 | 19:00 | 127 | 12:00
| Coxsbazar | 136 | 00:00 | 131 | 19:00 | Postogola | 132 | 07:00 | 126 | 23:00
| Cumilla(N) | 124 | 00:00 | 110 | 10:00 | Purbachal | 126 | 19:00 | 114 | 01:00
| Cumilla(S) | 130 | 19:30 | 119 | 01:00 | Purbasadipur | 121 | 17:00 | 115 | 12:00
| Daudkandi | 134 | 05:00 | 123 | 19:00 | Rahanpur | 133 | 19:00 | 128 | 12:00
| Dhaka | 137 | 06:00 | 127 | 23:00 | Rahim | 132.7 | 18:00 | 127 | 15:00
| Dhamrai | 137 | 06:00 | 127 | 19:00 | Rajbari | 129 | 18:00 | 124 | 12:00
| Dhanmondi | 133 | 19:30 | 127 | 12:00 | Rajendrapur | 133 | 19:00 | 125 | 11:00
| Dohazari | 125 | 00:00 | 109 | 22:00 | Rajshahi | 132 | 08:00 | 127 | 12:00
| Faridpur | 130 | 00:00 | 128 | 02:00 | Rajshahi-230 | 133 | 07:00 | 129 | 12:00
| Fatullah | 139 | 19:00 | 122 | 12:00 | Ramganj | 131 | 00:00 | 123 | 23:00
| Fenchuganj | 132 | 18:00 | 119 | 02:00 | Rampur | 132 | 18:00 | 124 | 00:00
| Feni | 123 | 17:00 | 116 | 1:00 | Rampura | 127 | 06:00 | 123 | 19:00
| Ghatail | 134 | 09:00 | 123 | 16:00 | Rangamati | 129 | 09:00 | 125 | 12:00
| Ghorashal | 130 | 18:00 | 125 | 12:00 | Rangpur | 133 | 06:00 | 128 | 12:00
| Goalpara | 134 | 05:00 | 122 | 15:00 | Ruppur | 132 | 17:00 | 130 | 00:00
| Gollamari | 135 | 6:00 | 128 | 12:00 | Saidpur | 128 | 06:00 | 122 | 18:30
| Gopalganj | 132 | 06:00 | 127 | 00:00 | Satkhira | 132 | 07:00 | 129 | 12:00
| Gopalganj-400 | 134 | 06:00 | 128 | 15:00 | Satmasjid | 131 | 05:00 | 129 | 01:00
| Gulshan | 127 | 16:00 | 121 | 12:00 | Savar | 132 | 01:00 | 123 | 15:00
| Halishahar | 137 | 08:00 | 128 | 19:00 | SevenRings | 128 | 00:00 | 108 | 08:00
| Haripur | 138 | 07:00 | 130 | 23:00 | ShahCement | 129 | 19:00 | 125 | 12:00
| HaripurSBU | 128 | 16:00 | 124 | 05:00 | Shahjadpur | 134 | 07:00 | 128 | 11:00
| Hasnabad | 131 | 02:00 | 124 | 23:00 | Shahjibazar | 135 | 00:00 | 129 | 19:30
| Hathazari | 138 | 19:00 | 127 | 12:00 | Shahmirpur | 131 | 06:00 | 126 | 12:00
| Ishurdi | 130 | 18:00 | 125 | 22:00 | Shariatpur | 134 | 06:00 | 127 | 23:00
| Jaldhaka | 132 | 04:00 | 128 | 18:30 | Sherpur | 134 | 07:00 | 127 | 12:00
| Jamalpur | 122 | 00:00 | 111 | 22:00 | Shikalbaha | 134 | 06:00 | 128 | 15:00
| Jashore | 131 | 09:00 | 120 | 13:00 | Shikalbaha-230 | 132 | 20:00 | 127 | 09:00
| Jhenaidah | 135 | 18:00 | 127 | 13:00 | Shitalakhya | 131 | 21:00 | 124 | 13:00
| Jhenaidah-230 | 135 | 18:00 | 128 | 19:00 | Sholosohor | 129 | 19:30 | 123 | 09:00
| Joydebpur | 131 | 19:00 | 125 | 10:00 | Shyampur | 130 | 21:00 | 125 | 12:00
| Joypurhat | 125 | 20:00 | 110 | 13:00 | Shyampur-230 | 130 | 06:00 | 125 | 12:00
| Juldah | 131 | 19:00 | 127 | 07:00 | Siddhirganj | 131 | 05:00 | 125 | 15:00
| Kabirpur | 137 | 22:00 | 119 | 09:00 | Sirajganj | 132 | 03:00 | 123 | 13:00
| Kachua | 125 | 19:00 | 117 | 04:00 | Sonargaon | 130 | 11:00 | 122 | 09:00
| Kaliakoir | 132 | 8:00 | 126 | 17:00 | Sreemongol | 126 | 07:00 | 121 | 18:30
| Kallyanpur | 127 | 06:00 | 122 | 12:00 | Sreepur | 131 | 01:00 | 125 | 21:00
| Kalurghat | 130 | 19:30 | 125 | 09:00 | Srinagar | 132 | 06:00 | 125 | 12:00
| Kamrangirchar | 133 | 04:00 | 120 | 13:00 | SSM | 132 | 10:00 | 130 | 00:00
| Kaptai | 134 | 9:00 | 128 | 16:00 | Sunamganj | 129 | 07:00 | 122 | 22:00
| Kazla | 130 | 05:00 | 122 | 13:00 | Sylhet | 132 | 07:00 | 127 | 00:00
| Keranigonj | 132 | 05:00 | 125 | 13:00 | Sylhet-132 | 131 | 06:00 | 128 | 15:00
| Khagrachori | 128 | 19:30 | 120 | 09:00 | Tangail | 130 | 10:00 | 123 | 23:00
| Khulna | 132 | 08:00 | 125 | 13:00 | Thakurgaon | 128 | 19:30 | 106 | 09:00
| Khulna(S) | 134 | 05:00 | 127 | 13:00 | TK | 128 | 18:00 | 125 | 04:00
| Khulshi | 128 | 19:30 | 124 | 08:00 | Tongi | 133 | 03:00 | 126 | 15:00
| Kishoreganj | 129 | 02:00 | 124 | 19:30 | Ullahpara | 134 | 20:00 | 126 | 13:00
| Kodda | 137 | 22:00 | 125 | 12:00 | Ullon | 130 | 06:00 | 122 | 12:00
| KSRM | 129 | 20:00 | 126 | 04:00 | Uttara | 131 | 03:00 | 124 | 15:00
| Kulaura | 131 | 09:00 | 128 | 15:00 | UttaraNew | 133 | 02:00 | 124 | 12:00
| Kurigram | 124 | 13:00 | 111 | 01:00 | Zigatola | 133 | 06:00 | 125 | 13:00

## L-Curve
Date | 2024-04-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 910 | 8586 | 6058 | 14644 |  |  |  | QF-LDC-11
0:30 | 925 | 8516.5 | 5977 | 14493.5 | Date: | 2024-04-26
1:00 | 940 | 8447 | 5896 | 14343
1:30 | 925 | 8405.5 | 5827.5 | 14233
2:00 | 910 | 8364 | 5759 | 14123
2:30 | 925 | 8327 | 5702 | 14029 | [5 empty] | Gen. at Eve. Peak | 15550 | 15550 MW (21:00 )
3:00 | 940 | 8290 | 5645 | 13935 | [6 empty] | 21:00
3:30 | 940 | 8282 | 5543.5 | 13825.5 | [5 empty] | Gen. at Day Peak | 13837 | 13837 MW (12:00 )
4:00 | 940 | 8274 | 5442 | 13716 | [6 empty] | 12:00
4:30 | 940 | 8213 | 5447 | 13660 | [5 empty] | Highest Generation | 15550
5:00 | 940 | 8152 | 5452 | 13604 | [6 empty] | 21:00
5:30 | 885 | 8150.5 | 5266.5 | 13417
6:00 | 830 | 8149 | 5081 | 13230
6:30 | 790 | 8090.5 | 5071.5 | 13162
7:00 | 750 | 8032 | 5062 | 13094
7:30 | 870 | 7938 | 4977 | 12915
8:00 | 990 | 7844 | 4892 | 12736
8:30 | 1115 | 7844 | 4847.5 | 12691.5
9:00 | 1240 | 7844 | 4803 | 12647
9:30 | 1150 | 7911 | 4838.5 | 12749.5
10:00 | 1060 | 7978 | 4874 | 12852
10:30 | 1140 | 8112 | 4920 | 13032
11:00 | 1220 | 8246 | 4966 | 13212
11:30 | 1275 | 8412 | 5112.5 | 13524.5
12:00 | 1330 | 8578 | 5259 | 13837
12:30 | 1315 | 8606 | 5324 | 13930
13:00 | 1300 | 8634 | 5389 | 14023
13:30 | 1305 | 8488.5 | 5367 | 13855.5
14:00 | 1310 | 8343 | 5345 | 13688
14:30 | 1325 | 8551.5 | 5328.5 | 13880
15:00 | 1340 | 8760 | 5312 | 14072
15:30 | 1280 | 8426.5 | 5348.5 | 13775
16:00 | 1220 | 8093 | 5385 | 13478
16:30 | 1235 | 8220 | 5397.5 | 13617.5
17:00 | 1250 | 8347 | 5410 | 13757
17:30 | 1230 | 8234 | 5265.5 | 13499.5
18:00 | 1210 | 8121 | 5121 | 13242
18:30 | 1075 | 8709.5 | 5436 | 14145.5
19:00 | 940 | 9298 | 5751 | 15049
19:30 | 920 | 9592 | 5766 | 15358
20:00 | 820 | 9610 | 5733 | 15343 |  |  |  | Executive Engineer
20:30 | 765 | 9625.5 | 5821 | 15446.5 |  |  |  | Network Operation Division
21:00 | 710 | 9641 | 5909 | 15550
21:30 | 710 | 9544 | 5956.5 | 15500.5
22:00 | 710 | 9447 | 6004 | 15451 |  |  |  |  | Page 6 of 7
22:30 | 770 | 9274.5 | 6059 | 15333.5
23:00 | 830 | 9102 | 6114 | 15216
23:30 | 870 | 8844 | 6086 | 14930
24:00 | 910 | 8586 | 6058 | 14644
15550 MW (21:00 )
13837 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-04-26 |  | Energy |  | 336032124
[15 empty] | 2024-04-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4617 | 635 | 2866 | 0 | 1682 | 4246 | 30 | 0 | 464 | 104 | 0 | 0 | 817.48
0:30 | 4669 | 636 | 2863.5 | 0 | 1546.5 | 4191 | 30 | 0 | 450.5 | 107 | 0 | 0 | 1176.24 |  |  | Date: | 43946
1:00 | 4721 | 637 | 2861 | 0 | 1411 | 4136 | 30 | 0 | 437 | 110 | 0 | 0 | 1535
1:30 | 4699 | 636.5 | 2855.5 | 0 | 1388.5 | 4079.5 | 30 | 0 | 433 | 111 | 0 | 0 | 1544.5 | [9 empty] | Total Energy | 336.0321 | 336.0321 | Total Energy Gen 336.032 MKWHr Energy Not Served 16.752 MKWHr Energy Requirement 352.784 MKWHr
2:00 | 4677 | 636 | 2850 | 0 | 1366 | 4023 | 30 | 0 | 429 | 112 | 0 | 0 | 1554 | [9 empty] | Energy not Served | 16.7518 | 16.7518
2:30 | 4630 | 777.5 | 2848.5 | 0 | 1355 | 3866 | 30 | 0 | 407 | 115 | 0 | 0 | 1524.5 | [9 empty] | Energy Requirement | 352.7839 | 352.7839
3:00 | 4583 | 919 | 2847 | 0 | 1344 | 3709 | 30 | 0 | 385 | 118 | 0 | 0 | 1495
3:30 | 4564.5 | 920 | 2843.5 | 0 | 1350 | 3639.5 | 30 | 0 | 350 | 123 | 0 | 5 | 1456 | [8 empty] | Shortage
4:00 | 4546 | 921 | 2840 | 0 | 1356 | 3570 | 30 | 0 | 315 | 128 | 0 | 10 | 1417
4:30 | 4539.5 | 920.5 | 2808.5 | 0 | 1357 | 3574.5 | 30 | 0 | 298 | 122 | 0 | 10 | 1375
5:00 | 4533 | 920 | 2777 | 0 | 1358 | 3579 | 30 | 0 | 281 | 116 | 0 | 10 | 1333
5:30 | 4557.5 | 920 | 2726.5 | 0 | 1370 | 3464 | 30 | 0 | 221.5 | 112 | 8.5 | 7 | 1273
6:00 | 4582 | 920 | 2676 | 0 | 1382 | 3349 | 30 | 0 | 162 | 108 | 17 | 4 | 1213
6:30 | 4529 | 920 | 2673 | 0 | 1372 | 3300.5 | 30 | 0 | 163 | 111 | 59 | 4.5 | 1039.115 | [7 empty] | Coal
7:00 | 4476 | 920 | 2670 | 0 | 1362 | 3252 | 30 | 0 | 164 | 114 | 101 | 5 | 865.23
7:30 | 4459 | 920.5 | 2564.5 | 0 | 1360.5 | 3167.5 | 30 | 0 | 145 | 108 | 156.5 | 3.5 | 725.8 | [6 empty] | Oil
8:00 | 4442 | 921 | 2459 | 0 | 1359 | 3083 | 30 | 0 | 126 | 102 | 212 | 2 | 586.37
8:30 | 4392.5 | 921 | 2459.5 | 0 | 1233.5 | 3136 | 30 | 0 | 134 | 106 | 278 | 1 | 499.9425
9:00 | 4343 | 921 | 2460 | 0 | 1108 | 3189 | 30 | 0 | 142 | 110 | 344 | 0 | 413.515
9:30 | 4404.5 | 920.5 | 2571.5 | 0 | 1105.5 | 3089.5 | 30 | 0 | 142 | 104 | 379.5 | 2.5 | 406.3525
10:00 | 4466 | 920 | 2683 | 0 | 1103 | 2990 | 30 | 0 | 142 | 98 | 415 | 5 | 399.19
10:30 | 4553.5 | 920.5 | 2722 | 0 | 1131.5 | 2970.5 | 30 | 0 | 150 | 101 | 447.5 | 5.5 | 351.44
11:00 | 4641 | 921 | 2761 | 0 | 1160 | 2951 | 30 | 0 | 158 | 104 | 480 | 6 | 303.69
11:30 | 4687 | 921 | 2810.5 | 0 | 1215 | 3072 | 30 | 0 | 194.5 | 103 | 485 | 6.5 | 315.6275
12:00 | 4733 | 921 | 2860 | 0 | 1270 | 3193 | 30 | 0 | 231 | 102 | 490 | 7 | 327.565
12:30 | 4683 | 920.5 | 2849.5 | 0 | 1345.5 | 3254.5 | 30 | 0 | 250.5 | 110 | 479.5 | 7 | 408.2625
13:00 | 4633 | 920 | 2839 | 0 | 1421 | 3316 | 30 | 0 | 270 | 118 | 469 | 7 | 488.96
13:30 | 4633 | 920 | 2839 | 0 | 1421 | 3316 | 30 | 0 | 270 | 118 | 469 | 7 | 488.96
14:00 | 4633 | 920 | 2839 | 0 | 1421 | 3316 | 30 | 0 | 270 | 118 | 469 | 7 | 488.96
14:30 | 4612.5 | 920.5 | 2873.5 | 0 | 1426 | 3378.5 | 30 | 0 | 282.5 | 115 | 399.5 | 9.5 | 472.725
15:00 | 4592 | 921 | 2908 | 0 | 1431 | 3441 | 30 | 0 | 295 | 112 | 330 | 12 | 456.49
15:30 | 4643 | 921 | 2641 | 0 | 1427 | 3440 | 30 | 0 | 273.5 | 113 | 271 | 15.5 | 549.125
16:00 | 4694 | 921 | 2374 | 0 | 1423 | 3439 | 30 | 0 | 252 | 114 | 212 | 19 | 641.76
16:30 | 4731.5 | 921 | 2433.5 | 0 | 1400 | 3554.5 | 30 | 0 | 267 | 111 | 149.5 | 19.5 | 556.2875
17:00 | 4769 | 921 | 2493 | 0 | 1377 | 3670 | 30 | 0 | 282 | 108 | 87 | 20 | 470.815
17:30 | 4650 | 921 | 2379.5 | 0 | 1438.5 | 3596 | 30 | 0 | 321 | 101 | 49 | 13.5 | 382.4075
18:00 | 4531 | 921 | 2266 | 0 | 1500 | 3522 | 30 | 0 | 360 | 94 | 11 | 7 | 294
18:30 | 4653 | 921 | 2456.5 | 0 | 1819.5 | 3636 | 30 | 0 | 521 | 97 | 5.5 | 6 | 362.3525
19:00 | 4775 | 921 | 2647 | 0 | 2139 | 3750 | 30 | 0 | 682 | 100 | 0 | 5 | 430.705
19:30 | 4758 | 803 | 2685 | 0 | 2383 | 3908 | 30 | 0 | 686 | 100 | 0 | 5 | 409.695
20:00 | 4765 | 636 | 2706 | 0 | 2389 | 3993 | 30 | 0 | 717 | 102 | 0 | 5 | 388.685
20:30 | 4754.5 | 636 | 2700 | 0 | 2417.5 | 4066.5 | 45 | 0 | 726.5 | 98 | 0 | 2.5 | 347.3425
21:00 | 4744 | 636 | 2694 | 0 | 2446 | 4140 | 60 | 0 | 736 | 94 | 0 | 0 | 306
21:30 | 4750.5 | 636 | 2706.5 | 0 | 2433.5 | 4176.5 | 45 | 0 | 655.5 | 97 | 0 | 0 | 329.1975
22:00 | 4757 | 636 | 2719 | 0 | 2421 | 4213 | 30 | 0 | 575 | 100 | 0 | 0 | 352.395
22:30 | 4830.5 | 635.5 | 2765 | 0 | 2269 | 4181.5 | 30 | 0 | 519.5 | 102 | 0 | 0.5 | 407.3075
23:00 | 4904 | 635 | 2811 | 0 | 2117 | 4150 | 30 | 0 | 464 | 104 | 0 | 1 | 462.22
23:30 | 4760.5 | 635 | 2838.5 | 0 | 1899.5 | 4198 | 30 | 0 | 464 | 104 | 0 | 0.5 | 639.85 |  |  | Max Temp. in Dhaka |  | 38.2°C
24:00 | 4617 | 635 | 2866 | 0 | 1682 | 4246 | 30 | 0 | 464 | 104 | 0 | 0 | 817.48
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 336.032 MKWHr Energy Not Served 16.752 MKWHr Energy Requirement 352.784 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-04-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720480
2 | Karnaphuli Hydro PP Unit-4 & 5 | [22 empty] | 30 | 0 |  |  | 28000
3 | Chattogram TPP-1 | 110 | 112 | 110 | 112 | 110 | 110 | 112 | 113 | 115 | 113 | 110 | 114 | 112 | 112 | 110 | 111 | 111 | 112 |  | 110 | 110 | 112 | 110 | 112 | 114 | 110 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 0 | [5 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 206971
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 0 | 14 | 6 | 16 | 15 | 17 | 16 | 12 | 7 | 3 | 0 | [8 empty] | 107595
6 | Sikalbaha 225MW CCPP (Gas) | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 212 | 211 | 211 | 211 | 210 | 211 | 211 | 211 | 210 |  | 211 | 210 | 211 | 212 | 210 | 210 | 210 | 5006664
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 37 | 41 | 49 | 46 |  | 49 | 49 | 51 | 51 | 51 | 51 | 51 | 1009034
12 | Hathazari 100 MW peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 34 |  | 32 | 13 | 13 | 32 | 24 | 24 | 24 | 714720
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 423200
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 35 | 35 | 35 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 33 | 35 | 33 | 35 | 30 | 31 | 31 | 31 |  | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 752912
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 151 | 152 | 153 | 153 | 150 | 149 | 145 | 150 | 122 | 160 | 160 | 189 | 191 | 121 | 121 | 194 | 197 | 75 |  | 197 | 199 | 200 | 201 | 200 | 197 | 200 | 4045000
17 | Siddhirganj 335 MW CCPP | 324 | 326 | 327 | 327 | 327 | 332 | 329 | 326 | 290 | 270 | 310 | 308 | 302 | 310 | 311 | 310 | 312 | 280 |  | 317 | 317 | 319 | 321 | 322 | 323 | 324 | 7600259
18 | Kodda 300 MW PP Unit-2 (Summit) | 263 | 281 | 283 | 278 | 275 | 275 | 275 | 275 | 95 | 95 | 95 | 95 | 151 | 210 | 210 | 210 | 80 | 80 |  | 134 | 270 | 250 | 273 | 283 | 288 | 290 | 5399564
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 180 | 180 | 180 | 140 | 140 | 58 | 0 | [18 empty] | 1156125
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4142250
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 269 | 270 | 274 | 274 | 275 | 274 | 275 | 275 | 270 | 270 | 270 | 270 | 278 | 275 | 275 | 276 | 274 | 271 |  | 270 | 273 | 272 | 272 | 276 | 275 | 280 | 6594544
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 38 | 38 | 37 | 36 | 32 | 35 | 35 | 34 | 35 | 35 |  | 36 | 36 | 36 | 37 | 37 | 32 | 35 | 876024
33 | Ashuganj 225 MW CCPP | 197 | 188 | 204 | 215 | 213 | 216 | 216 | 214 | 214 | 210 | 208 | 207 | 207 | 204 | 207 | 205 | 207 | 212 |  | 197 | 210 | 206 | 204 | 207 | 186 | 212 | 5012000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 260 | 330 | 260 | 260 | 260 | 260 | 270 | 280 | 270 | 270 |  | 285 | 270 | 270 | 270 | 270 | 295 | 270 | 6665000
| Ashuganj 450 MW CCPP(North) | 325 | 305 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 330 | 310 | 280 | 295 | 285 | 290 | 285 | 280 |  | 300 | 285 | 285 | 285 | 285 | 315 | 285 | 7509200
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 240 | 240 | 240 | 240 | 240 | 240 | 340 | 300 | 300 | 300 | 320 | 320 | 320 | 280 |  | 300 | 315 | 320 | 300 | 310 | 295 | 275 | 6850000
35 | Ashuganj 55 MW PP (Precision) | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 47 | 44 | 43 | 38 | 38 | 39 | 41 |  | 42 | 43 | 44 | 45 | 45 | 48 | 48 | 1093440
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 370 | 370 | 350 | 344 | 344 | 342 | 339 | 351 | 365 | 371 | 373 | 374 | 374 | 372 | 372 | 385 | 403 | 404 |  | 404 | 407 | 406 | 404 | 407 | 403 | 404 | 9075600
| Meghnaghat Unique power | 470 | 470 | 470 | 470 | 400 | 300 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 253 | 404 | 442 | 584 | 408 |  | 525 | 540 | 540 | 540 | 540 | 540 | 540 | 9698636
| Summit Meghanghat-2 589 MW(Gas) | 350 | 350 | 350 | 350 | 350 | 500 | 525 | 419 | 426 | 588 | 583 | 583 | 571 | 583 | 583 |  |  | 60 |  | 102 | 230 | 230 | 230 | 230 | 300 | 350 | 8672991
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10245000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 70 | 74 | 81 | 82 | 83 | 82 | 71 | 64 | 66 | 66 | 66 | 66 | 70 | 70 | 69 | 70 | 91 | 88 |  | 98 | 98 | 98 | 98 | 96 | 97 | 97 | 1828800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 9 | 14 | 30 | 40 | 45 | 44 | 44 | 37 | 30 | 20 | 8 | 1 | [8 empty] | 317410
44 | Fenchugonj CCPP Phase-1 | 43 | 40 | 40 | 40 | 40 | 40 | 42 | 42 | 43 | 43 | 43 | 40 | 40 | 39 | 39 | 40 | 39 | 40 |  | 40 | 41 | 43 | 43 | 43 | 41 | 35 | 958000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 |  | 29 | 29 | 29 | 28 | 28 | 28 | 20 | 654840
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 60 | 60 | 60 | 60 | 60 | 61 | 40 | 40 | 40 | 56 | 55 | 40 | 55 | 58 | 55 | 40 |  | 50 | 51 | 51 | 51 | 51 | 50 | 56 | 1266720
48 | Shahjibazar 86 MW PP (Shahjibazar)
| Shahjibazar 100 MW GTPP | 25 | 25 | 40 | 40 | 40 | 40 | 30 | 30 | 70 | 75 | 80 | 80 | 60 | 60 | 55 | 55 | 90 | 90 |  | 91 | 90 | 90 | 88 | 90 | 91 | 45 | 1492854
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 203 | 202 | 205 | 205 | 206 | 205 | 206 | 206 | 207 | 206 | 204 | 203 | 202 | 202 | 200 | 199 | 199 | 199 |  | 202 | 202 | 202 | 202 | 204 | 204 | 181 | 4107610
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 15 | 14 | 14 | 14 |  | 15 | 17 | 17 | 17 | 12 |  |  | 368000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 177504
55 | Fenchugonj 51 MW PP (Barakatullah) | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 20 |  | 53 | 53 | 53 | 22 | 20 |  |  | 1084200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 16 | 16 | 24 | 24 |  | 24 | 24 | 24 | 24 | 17 | 16 |  | 503280
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 305 | 310 | 290 | 295 | 280 | 265 | 275 | 270 | 295 | 310 | 300 | 310 | 280 | 285 | 300 | 290 | 260 |  | 305 | 265 | 265 | 295 | 285 | 305 | 300 | 7118000
| Bibiyana South 400 MW | 375 | 370 | 345 | 345 | 350 | 345 | 345 | 345 | 315 | 320 | 335 | 370 | 345 | 360 | 345 | 345 | 345 | 345 |  | 335 | 320 | 320 | 320 | 330 | 370 | 340 | 8277000
58 | Nababganj 55 MW PP (Southern power ) | [15 empty] | 5 | 17 | 35 |  | 35 | 35 | 55 | 55 | 55 |  |  | 249498
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 9 | 10 | 12 | 12 | 12 | 12 | 12 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 380160
60 | Barabkunda 22 MW PP (Regent) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 109680
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 110 | 112 | 118 | 128 | 116 | 108 | 114 | 102 | 110 | 98 | 104 | 102 | 118 | 120 | 112 | 114 | 108 | 94 |  | 100 | 100 | 102 | 94 | 100 | 104 | 104 | 2603520
64 | Malancha, Ctg. EPZ (United) | 32 | 24 | 13 | 24 | 25 | 25 | 25 | 16 | 12 | 13 | 13 | 16 | 27 | 5 | 23 | 17 | 26 | 26 |  | 27 | 27 | 30 | 31 | 25 | 21 | 29 | 527520
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 368200
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440970
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 408000
70 | Summit Madhabdi | 15 | 15 | 15 | 13 | 13 | 13 | 13 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 327240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 692940
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 28 | 28 | 30 | 30 | 30 |  | 30 | 31 | 31 | 25 | 26 | 33 | 33 | 726100
73 | Ghorashal 108 MW PP (Regent) | [9 empty] | 12 | 16 | 21 | 24 | 24 | 24 | 40 | 50 | 57 |  | 60 | 62 | 63 | 64 | 64 | 65 | 65 | 593818
| Feni Lanka Power | 70 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 62 | 62 | 62 | 62 | 60 | 60 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1762440
| Chowmuhani 113 MW | 40 | 38 | 39 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 36 | 42 | 63 |  | 68 | 64 | 65 | 65 | 65 | 65 | 28 | 1079400
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 72 | 144 | 144 | 162 | 126 | 17 | 17 | 986400
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 8 | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 283200
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 31 | 31 | 31 | 32 | 32 | 98 |  | 148 | 146 | 146 | 147 | 147 | 48 | 48 | 1158240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 32 | 34 | 34 | 32 | 32 | 48 | 49 |  | 51 | 51 | 51 | 50 | 50 | 51 | 34 | 809712
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 854400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 2 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 30480
| Jodiac Power | [6 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 31 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 450879
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 34 | 34 | 34 | 34 | 34 | 34 | 24 | 509340
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 305 | 306 | 306 | 307 | 309 | 286 | 275 | 294 | 300 | 301 | 300 | 298 | 302 | 298 | 300 | 298 | 282 | 287 |  | 302 | 287 | 298 | 300 | 306 | 307 | 309 | 7173993
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 46 | 18 | 18 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 | 51 | 51 | 50 | 50 |  | 51 | 51 | 52 | 52 | 52 | 52 | 17 | 815040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 37 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 36 | 36 | 36 | 35 | 35 | 38 | 35 | 35 |  | 36 | 38 | 36 | 20 | 20 |  |  | 802152
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1132877
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 76 | 82 |  | 82 | 82 | 73 | 73 | 82 | 82 | 82 | 1154592
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 151200
96 | Chattogram 108 MW PP (ECPV) | [9 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 20 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 294720
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 32 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 982751
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 |  |  | 251933
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 112 | 112 | 112 | 80 | 112 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 80 | 80 | 2403082
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15550
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 |  |  | 233280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 77 | 77 | 77 | 77 | 77 | 77 | 58 | 58 | 58 | 57 | 57 | 57 | 56 | 56 | 56 | 54 | 55 | 55 |  | 104 | 104 | 104 | 104 | 106 | 107 | 107 | 1773600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 130 | 129 | 107 | 127 | 127 | 126 | 115 | 129 | 130 | 126 | 129 | 128 | 125 | 119 | 110 | 98 | 103 | 132 |  | 149 | 149 | 149 | 145 | 135 | 134 | 133 | 3054384
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 286080
116 | Chandpur 200 MW (Desh energy) | 94 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 87 | 85 | 103 | 100 | 100 | 106 | 152 | 152 | 104 | 120 |  | 155 | 155 | 160 | 155 | 155 | 155 | 155 | 2762880
117 | Ashuganj 150 MW PP (Midland) | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 6 |  | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 148872
118 | Bibiyana-III 400 MW CCPP | 402 | 400 | 369 | 364 | 369 | 364 | 366 | 364 | 316 | 315 | 338 | 396 | 366 | 378 | 367 | 367 | 366 | 366 |  | 368 | 367 | 366 | 366 | 366 | 400 | 327 | 8860000
| Jamalpur 115 MW PP (United) | 69 | 69 | 69 | 69 | 69 | 69 | 49 | 49 | 49 | 48 | 49 | 48 | 47 | 47 | 47 | 46 | 47 | 47 |  | 97 | 97 | 97 | 97 | 97 | 98 | 98 | 1576800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 386400
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 265920
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 416509
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 510120
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 13 | 21 | 26 | 29 | 30 | 29 | 25 | 20 | 12 | 5 | 1 | [8 empty] | 212587
| Chandpur 115(Doreen) | 40 | 36 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 35 | 36 | 52 | 54 | 54 | 54 | 54 | 54 | 56 |  | 78 | 98 | 97 | 97 | 97 | 85 | 53 | 1294080
| Kanchan Purbachal Power Generation Ltd. | [26 empty] | 0
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 53 | 53 | 53 | 17 | 17 | 17 |  | 163 | 163 | 163 | 163 | 17 | 17 | 17 | 930036
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 10 | 10 | 4 | 5 | 2 | 0 | 5 | 6 | 7 | 7 | 13 | 12 | 19 | 20 | 7 |  | 5 | 5 | 5 | 0 | 0 | 1 | 0 | 133440
| Sonagazi 75 MW Solar Plant | [5 empty] | 3 | 16 | 36 | 50 | 61 | 67 | 70 | 69 | 50 | 44 | 28 | 10 | 1 | [8 empty] | 477982
| Matarbari 2*600 MW (CPGCL) | 577 | 575 | 575 | 575 | 579 | 574 | 574 | 578 | 779 | 582 | 574 | 779 | 781 | 575 | 778 | 575 | 756 | 774 |  | 777 | 778 | 775 | 780 | 780 | 730 | 640 | 16181818
120 | Eastern Zone Total | 8447 | 8364 | 8290 | 8274 | 8152 | 8149 | 8032 | 7844 | 7844 | 7978 | 8246 | 8578 | 8634 | 8343 | 8760 | 8093 | 8347 | 8121 |  | 9298 | 9592 | 9610 | 9641 | 9447 | 9102 | 8586 | 204494242
121
122
123 | Khulna 60MW
124 | manik
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 33 | 33 | 33 | 33 | 0 | [13 empty] | 25 | 40 | 40 | 33 | 33 | 33 | 33 | 356160
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 90 | 90 | 90 | 91 | 92 | 92 | 92 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 40 | 53 | 55 | 73 | 73 | 73 | 73 | 1274400
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 18 | 43 | 66 | 81 | 92 | 95 | 92 | 81 | 65 | 43 | 19 | 2 | [8 empty] | 707040
131 | Rampal 1320 MW (BIFPCL) | 340 | 338 | 338 | 338 | 340 | 339 | 341 | 340 | 340 | 340 | 339 | 340 | 340 | 340 | 338 | 338 | 339 | 341 |  | 378 | 383 | 378 | 378 | 380 | 375 | 375 | 8349091
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [11 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 260400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 220 | 190 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5006891
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 726528
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 240 | 240 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 200 | 190 | 150 |  | 211 | 250 | 250 | 250 | 250 | 250 | 250 | 5061800
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 80 | 80 | 124 | 124 | 124 | 128 | 126 | 126 | 126 |  | 130 | 126 | 126 | 126 | 130 | 130 | 130 | 2789000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 8 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 9 | 7 | 6 |  | 10 | 10 | 9 | 10 | 8 | 10 | 10 | 224890
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 36 | 36 | 36 | 35 | 35 | 0 | [13 empty] | 25 | 35 | 47 | 62 | 60 | 50 | 50 | 456960
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 637 | 636 | 919 | 921 | 920 | 920 | 920 | 921 | 921 | 920 | 921 | 921 | 920 | 920 | 921 | 921 | 921 | 921 |  | 921 | 803 | 636 | 636 | 636 | 635 | 635 | 18608000
147 | Bheramara 410 MW CCPP | 400 | 380 | 350 | 345 | 350 | 345 | 345 | 350 | 350 | 365 | 390 | 375 | 345 | 370 | 345 | 350 | 345 | 345 |  | 365 | 345 | 345 | 345 | 345 | 390 | 350 | 8798976
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1200 | 1200 | 1000 | 880 | 800 | 700 | 700 | 700 | 700 | 790 | 740 | 810 | 910 | 860 | 680 |  | 710 | 760 | 780 | 800 | 790 | 810 | 960 | 23503800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 200 | 200 | 210 | 230 | 200 | 200 | 200 | 167 | 203 | 230 | 230 | 230 | 230 | 230 | 230 |  | 200 | 200 | 206 | 230 | 230 | 230 | 230 | 5300000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 37 | 37 | 38 | 38 | 38 | 37 | 38 | 0 | [8 empty] | 30 | 38 |  | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 562855
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 36240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 189 | 198 | 198 | 197 | 198 | 197 | 173 | 160 | 161 | 147 | 157 | 156 | 169 | 157 | 165 | 162 | 174 | 169 |  | 164 | 171 | 172 | 177 | 174 | 184 | 179 | 4400264
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 16 | 11 | 6 | 7 | 25 | 54 | 128 | 150 | 150 | 155 | 168 | 165 | 190 | 187 | 190 | 189 | 188 | 170 |  | 178 | 185 | 184 | 188 | 183 | 198 | 198 | 3459627
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 300 | 295 | 314 | 310 | 348 | 350 | 414 | 380 | 350 | 320 | 346 | 294 | 295 |  | 352 | 297 | 305 | 304 | 343 | 414 | 414 | 8592800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 17 | 17 | 17 | 17 | 0 | [7 empty] | 4 | 17 | 16 | 16 | 16 | 16 |  | 16 | 16 | 30 | 20 | 19 | 19 | 20 | 239391
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 258246
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 14 | 14 | 14 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 766200
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 8 | 34 | 34 | 34 | 34 | 34 | 34 | 8 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 621785
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 0 | [7 empty] | 7 | 16 | 16 | 30 | 28 | 18 | 22 |  | 38 | 38 | 39 | 45 | 47 | 45 | 45 | 411492
168 | Santahar 50 MW Peaking PP | 38 | 30 | 30 | 0 | [6 empty] | 10 | 30 | 35 | 36 | 35 | 24 | 26 | 26 |  | 30 | 30 | 32 | 32 | 32 | 32 | 30 | 477349
169 | Natore 52 MW PP (Rajlanka) | [8 empty] | 8 | 8 | [12 empty] | 8 | 8 |  |  | 32021
170 | Chapainawabganj 100 MW Peaking PP | 95 | 95 | 50 | 50 | 50 | 0 | [5 empty] | 37 | 32 | 32 | 32 | 32 | 32 | 32 |  | 85 | 85 | 85 | 80 | 75 | 75 | 75 | 999968
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 85 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 |  | 42 | 50 | 50 | 50 | 50 | 50 | 35 | 1672320
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 25 | 55 | 55 | 55 | 55 | 75 | 35 |  | 95 | 95 | 95 | 95 | 95 | 95 | 35 | 802848
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 48 | 48 | 48 | 48 | 34 | 34 | 55 | 55 |  | 56 | 49 | 56 | 56 | 56 | 56 | 34 | 1010400
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 6 | 7 | 7 | 7 | 6 | 5 | 3 | 1 | 0 | [8 empty] | 50934
178 | Energypac Power Venture Thakurgaon Ltd. | [8 empty] | 35 | 35 | 50 | 55 | 55 | 55 | 55 | 35 | 35 | 68 |  | 94 | 94 | 94 | 94 | 94 | 94 |  | 996480
| Intraco Solar 30 MW | [5 empty] | 1 | 6 | 15 | 23 | 29 | 33 | 34 | 33 | 28 | 22 | 15 | 6 | 1 | [8 empty] | 247688
| Adani Power Jharkhanda Ltd | 1169 | 1059 | 741 | 743 | 745 | 752 | 752 | 740 | 750 | 748 | 751 | 751 | 747 | 785 | 810 | 910 | 1021 | 1076 |  | 1204 | 1264 | 1332 | 1430 | 1507 | 1480 | 1511 | 23121818
178 | Teesta Solar Limited | [5 empty] | 8 | 41 | 84 | 128 | 156 | 181 | 184 | 168 | 158 | 125 | 79 | 34 | 5 | [8 empty] | 1353220