## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-03 | Friday
|  | Date (day): | 2024-05-03 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15265.6 | MW |  |  | (b) At Evening Peak Hour : |  | 17276 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-02 | 2024-05-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 69 | 78 | 75 | 75 | 33 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 403 | 403 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 19 | 91 | 25 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 278 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 25 | 65 | 25 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 40 | 40 | 15 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 15 | 60 |  | Engine problem.
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 110 |  | Titas gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 24 | 67 | 60 | 80
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 295 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 49 | 82 | 48 | 90 | 12 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 2 | 0 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 147 | 32 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 41 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 22 | 35 | 36 |  | 44 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 28 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 11 | 16 | 16 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 275 | 210 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 93 | 129 | 52 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 50 | 17 | 53 | 51 |  | Lube oil shortage.
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 90 | 162 | 90 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 450 | 400 | 500 | 500
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 400 | 350 | 360 | 450 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 3209 | 3855 | 3483 | 4326 | 657 | 804
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 114 | 117 | 115 | 115 | 65 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 6 | 44 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 212 | 211 | 211
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 17 | 34 | 71 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 48 | 40 | 64 | 34
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 51 | 35 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 61 | 36 | 60 | 40 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 7 | 7 | 5 | 5 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 22 | 15 | 30
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 19 | 80 | 20 | 90 | 18 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 16 | 16 | 284
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 22 | 54 | 17 | 54 |  |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 34 | 17 | 34 | 76 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 34 | 60 | 40 | 70 | 30 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 72 | 35 | 52 | 64 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 61 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 272 | 265 | 270 | 270 | 954 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 43 | 37 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 391 | 776 | 360 | 800 |  |  | Unit-2 on test
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 46 | 0 | 33 | 0 |  |  | on test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1450 | 2081 | 1445 | 2220 | 1880 | 381
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 213 | 0 | 0 |  | 221 | Under maint
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 305 | 345 | 345 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 280 | 300 | 335 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 345 | 300 | 280 | 330 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 31 | 37 | 34 | 34 | 11
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 41 | 42 | 50 | 50 | 5
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 90 | 90 | 105 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 5 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 34 | 36 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 162 | 90 | 100 | 120 | 80
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 106 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 0 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 0 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 52 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 36 | 63 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 30 | 33 | 17 | 35 |  | 19 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 94 | 54 | 95 |  | 20 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1834 | 1827 | 1675 | 1977 | 383 | 439
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 108 | 97 | 100 | 100 | 102 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 104 | 56 | 108 | 92 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 96 | 50 | 97 | 18 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 40 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 12 | 22
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 272 | 315 | 269.6 | 327 | 102 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 42 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 28 | 28 | 28 |  | 62 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 37 | 37 | 44 | 44
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 5 | 5 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 62 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 202 | 206 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 16 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 285 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 366 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 345 | 345 | 380 | 380 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1574 | 1576 | 1674 | 1674 | 0 | 491
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 875 | 940 | 651
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 29 | 25 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 49 | 44 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 355 | 400 | 410
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 55 | 90 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 78 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 309 | 307 | 375 | 375
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1674 | 1670 | 1974 | 1630 | 702 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 48 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 8 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 740 | 1160 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 27 | 123 |  | fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 230 | 200 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1277 | 1815 | 1869 | 2048 | 123 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 39 | 40 | 38 | 38 | 14 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 25 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 31 | 40 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 174 | 167 | 0 | 0 |  |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 204 | 185 | 200 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 5 | 180 | 200 |  |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 414 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 23 | 23 | 33 | 17 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 57 | 113 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 95 | 35 | 95 | 18 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1166 | 436 | 1200 | 1200 |  |  | Engine problem
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 2240 | 1719 | 2317 | 2574 | 214 | 63
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 72 | 70 | 75 | 10
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 53 | 85 | 56 | 80 | 33 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 55 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 170 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 619 | 502 | 559 | 500 | 83 | 129
| Total |  |  |  |  | 27054 | 25903 | 14149 | 15360 | 15265.6 | 17276 | 4144 | 2430
A. |  | 2024-05-02 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 15360 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 13298 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15850 | MW
3 | Day peak Generation : |  |  | 14149 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14990.68 | MW
4 | Evening peak Generation : |  |  | 15360 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 468 | MW
5 | Total Energy Generation : |  | 342.8393 | MKWHr | By Solar | 2.9553 | MKWHr
| By Gas : | 180.1466 | MKWHr |  | By Oil: | 52.3472 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 84.2018 | MKWHr |  | By Hydro: | 0.67564 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.6912 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4144 | MW | Dhaka | 5482.48 | 5321.48 |  | 161 |  | 18:00 |  | 495.645
|  |  | For Plants S/D or M/C prob = |  |  | 2430 | MW | Chittagong | 1344 | 1344 |  | 0 |  | 19:00 |  | 490.87
|  |  | Total = |  |  | 6574 | MW | Khulna | 1937.9 | 1937.9 |  | 0 |  | 19:30 |  | 467.95
7 | Total Gas Supplied : |  |  | 1306.01 | MMCFD |  |  | Rajshahi | 1760.8 | 1760.8 |  | 0 |  | 20:00 |  | 380.09
8 | Fuel Cost : | i) Gas : | Taka | 500985239.668 | ii) Oil : | Taka | 961314843.86 | Comilla | 1087 | 1087 |  | 0 |  | 21:00 |  | 293.185
|  | iii) Coal : | Taka | 573172017.79 | Total | Taka | 2035472101.318 | Mymensingh | 1368 | 1173 |  | 195 |  | 22:00 |  | 317
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 499 | 499 |  | 0 |  | 23:00 |  | 673
| ii) During Peak Demand : |  |  | 690 | MW (W to E) at | 19:30 | hrs | Barisal | 467.5 | 467.5 |  | 0 |  | 24:00 |  | 1019
| iii) Maximum : |  |  | 500 | MW at | 24:00 | hrs | Rangpur | 1044 | 932 |  | 112
10 | Maximum Temperature in Dhaka was |  |  |  | 38.3°C |  |  | Total | 14990.68 | 14522.68 |  | 468
B. |  | 2024-05-03 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 38.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 17276 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13500 | MW
4 | Reserve(Generation end) |  |  |  | 1276 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 357.1242 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11149 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.2429 | MKWHr. | ii) HVDC Flow at Peak Time |  | 875 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5786 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.73 |  | (b) Today: | 73.62 |  | (c) Rule Curve: |  | 81.62
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-02 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 402 | 0 |  | 0 | 450 | 308 | 68 | 80 | 40 | 318 | 0 | 0 | 33 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 33 | 30 | 8 | 0 | 25 | 0 | 110 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 6 | 6 | 42 | 0 | 0 | 0 | 24 | 310 | 200 | 157 | 0 | 30 | 44 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 126 | 179 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 112 | 0 | 59 | 0 | 0 | 201 | 17 | 0 | 0 | 305 | 0 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 36 | 0 | 36 | 100 | 6 | 402 | 68 | 17 | 17 | 0 | 16 | 17 | 17 | 52 | 36 | 34 | 376 | 27 | 0 | 0 | 35 | 0 | 33 | 0 | 44 | 0 | 290 | 17 | 0 | 272 | 17 | 372 | 555 | 500 | 0 |  | 644 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 19 | 47 | 0 | 130 | 10 | 48 | 0 | 0 | 50 | 40 | 11 | 85 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 172 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 349 | 83 | 0 | 37 | 0 | 34 | 0 | 0 | 18 | 1244 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 305 | 0 | 307 | 1187 | 0 | 0 |  | 8238 | 6080 | 14318 | 4496 | 644 | 3268 | 0 | 1354 | 3990 | 25 | 0 | 398 | 126 | 0 | 17 | 1224.31 | 73.75
2:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 0 |  | 0 | 450 | 310 | 82 | 80 | 40 | 319 | 0 | 0 | 33 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 33 | 30 | 8 | 0 | 25 | 0 | 110 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 6 | 6 | 42 | 0 | 0 | 0 | 26 | 280 | 201 | 157 | 0 | 27 | 44 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 128 | 180 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 112 | 0 | 59 | 0 | 0 | 198 | 17 | 0 | 0 | 310 | 16 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 19 | 0 | 36 | 85 | 5 | 375 | 68 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 36 | 34 | 345 | 17 | 0 | 17 | 35 | 0 | 33 | 0 | 18 | 0 | 245 | 17 | 0 | 275 | 20 | 371 | 555 | 500 | 0 |  | 641 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 130 | 10 | 95 | 0 | 0 | 50 | 40 | 6 | 85 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 172 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 348 | 83 | 0 | 18 | 0 | 34 | 0 | 0 | 18 | 1244 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 306 | 0 | 307 | 1158 | 0 | 0 |  | 8082 | 6028 | 14110 | 4343 | 641 | 3276 | 0 | 1327 | 3964 | 25 | 0 | 386 | 128 | 0 | 20 | 1231.95 | 73.75
3:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 0 |  | 0 | 450 | 309 | 83 | 80 | 40 | 322 | 0 | 0 | 33 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 105 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 6 | 6 | 42 | 0 | 0 | 0 | 75 | 270 | 205 | 157 | 0 | 27 | 44 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 122 | 192 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 112 | 0 | 59 | 0 | 0 | 197 | 17 | 0 | 0 | 290 | 16 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 17 | 0 | 36 | 85 | 6 | 365 | 68 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 37 | 34 | 345 | 17 | 0 | 17 | 35 | 0 | 34 | 0 | 18 | 0 | 270 | 17 | 0 | 274 | 18 | 373 | 500 | 400 | 0 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 19 | 40 | 0 | 130 | 10 | 110 | 0 | 0 | 50 | 40 | 5 | 50 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 171 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 363 | 87 | 0 | 18 | 0 | 34 | 0 | 0 | 18 | 1244 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 307 | 0 | 307 | 1165 | 0 | 0 |  | 7969 | 6290 | 14259 | 4382 | 926 | 3115 | 0 | 1348 | 3973 | 25 | 0 | 350 | 122 | 0 | 18 | 803.155 | 73.74
4:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 0 |  | 0 | 450 | 302 | 83 | 80 | 40 | 326 | 0 | 0 | 33 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 110 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 0 | 6 | 15 | 0 | 0 | 0 | 170 | 270 | 216 | 102 | 0 | 27 | 44 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 118 | 193 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 80 | 0 | 59 | 0 | 0 | 197 | 17 | 0 | 0 | 265 | 16 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 17 | 0 | 36 | 85 | 6 | 318 | 68 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 36 | 34 | 345 | 17 | 0 | 17 | 35 | 0 | 33 | 0 | 18 | 0 | 285 | 17 | 0 | 273 | 40 | 373 | 500 | 350 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 130 | 10 | 110 | 0 | 0 | 50 | 40 | 0 | 38 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 171 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 334 | 88 | 0 | 18 | 0 | 34 | 0 | 0 | 18 | 1100 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 310 | 0 | 272 | 1161 | 0 | 0 |  | 7867 | 6057 | 13924 | 4463 | 925 | 2890 | 0 | 1341 | 3791 | 25 | 0 | 331 | 118 | 0 | 40 | 550.08 | 73.74
5:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 401 | 0 |  | 0 | 450 | 310 | 83 | 80 | 40 | 322 | 0 | 0 | 32 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 110 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 6 | 5 | 25 | 0 | 0 | 0 | 345 | 270 | 214 | 8 | 0 | 27 | 46 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 114 | 193 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 80 | 0 | 59 | 0 | 0 | 197 | 17 | 0 | 0 | 290 | 16 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 17 | 0 | 36 | 85 | 5 | 316 | 68 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 36 | 34 | 345 | 16 | 0 | 17 | 35 | 0 | 34 | 0 | 18 | 0 | 330 | 17 | 0 | 275 | 40 | 371 | 500 | 350 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 130 | 9 | 110 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 172 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 349 | 88 | 0 | 18 | 0 | 34 | 0 | 0 | 18 | 1000 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 308 | 0 | 200 | 1179 | 0 | 0 |  | 8026 | 5880 | 13906 | 4674 | 925 | 2855 | 0 | 1345 | 3635 | 25 | 0 | 293 | 114 | 0 | 40 | 424.02 | 73.73
6:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 0 |  | 0 | 450 | 310 | 48 | 44 | 40 | 322 | 0 | 0 | 24 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 113 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 6 | 6 | 30 | 0 | 0 | 0 | 345 | 285 | 213 | 8 | 0 | 27 | 42 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 112 | 193 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 80 | 0 | 59 | 0 | 0 | 196 | 17 | 0 | 0 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 78 | 0 | 17 | 0 | 36 | 85 | 6 | 321 | 68 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 36 | 34 | 345 | 17 | 2 | 17 | 35 | 0 | 25 | 1 | 18 | 0 | 340 | 17 | 0 | 270 | 28 | 374 | 500 | 350 | 3 |  | 926 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 15 | 38 | 0 | 130 | 10 | 16 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 172 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 347 | 89 | 0 | 18 | 0 | 34 | 0 | 0 | 18 | 840 | 220 | 0 | 17 | 0 | 3 | 36 | 0 | 0 | 309 | 1 | 170 | 1171 | 6 | 0 |  | 7863 | 5605 | 13468 | 4718 | 926 | 2840 | 0 | 1078 | 3436 | 25 | 0 | 289 | 112 | 16 | 28 | 412.56 | 73.73
7:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 0 |  | 0 | 450 | 310 | 8 | 17 | 40 | 322 | 0 | 0 | 9 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 111 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 12 | 6 | 6 | 26 | 0 | 0 | 0 | 350 | 315 | 213 | 8 | 0 | 27 | 42 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 110 | 154 | 0 | 0 | 0 | 40 | 29 | 53 | 39 | 80 | 0 | 59 | 0 | 0 | 197 | 17 | 0 | 0 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 17 | 3 | 36 | 85 | 6 | 317 | 48 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 36 | 34 | 345 | 17 | 5 | 17 | 35 | 0 | 17 | 6 | 18 | 0 | 336 | 17 | 0 | 271 | 16 | 374 | 505 | 350 | 13 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 15 | 39 | 0 | 130 | 10 | 16 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 16 | 30 | 8 | 30 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 172 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 327 | 88 | 0 | 18 | 0 | 35 | 0 | 1 | 18 | 780 | 220 | 0 | 17 | 0 | 7 | 36 | 0 | 0 | 309 | 5 | 170 | 1179 | 10 | 0 |  | 7749 | 5549 | 13298 | 4700 | 925 | 2841 | 0 | 956 | 3385 | 25 | 0 | 290 | 110 | 50 | 16 | 575 | 73.72
8:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 405 | 0 |  | 0 | 450 | 310 | 8 | 17 | 40 | 317 | 0 | 0 | 9 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 10 | 0 | 20 | 15 | 33 | 32 | 8 | 0 | 25 | 0 | 115 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 13 | 6 | 7 | 13 | 0 | 0 | 0 | 345 | 305 | 205 | 8 | 0 | 27 | 42 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 16 | 104 | 151 | 0 | 0 | 1 | 40 | 29 | 50 | 39 | 80 | 0 | 59 | 0 | 0 | 196 | 17 | 0 | 0 | 285 | 8 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 21 | 3 | 36 | 85 | 5 | 320 | 48 | 17 | 17 | 2 | 16 | 0 | 17 | 52 | 36 | 34 | 353 | 17 | 11 | 17 | 35 | 0 | 17 | 13 | 19 | 0 | 290 | 17 | 0 | 270 | 35 | 373 | 504 | 350 | 2 |  | 926 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 0 | 130 | 9 | 16 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 16 | 30 | 8 | 30 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 173 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 348 | 55 | 0 | 37 | 0 | 34 | 0 | 3 | 35 | 780 | 220 | 0 | 17 | 2 | 29 | 55 | 0 | 0 | 309 | 9 | 170 | 1166 | 31 | 0 |  | 7716 | 5637 | 13353 | 4642 | 926 | 2831 | 0 | 1027 | 3370 | 25 | 0 | 287 | 104 | 106 | 35 | 475 | 73.72
9:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 403 | 0 |  | 0 | 450 | 278 | 9 | 17 | 40 | 309 | 0 | 0 | 9 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 116 | 0 | 0 | 211 | 0 | 0 | 0 |  | 13 | 32 | 34 | 0 | 20 | 6 | 7 | 4 | 0 | 0 | 0 | 356 | 290 | 213 | 8 | 0 | 26 | 42 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 32 | 16 | 110 | 109 | 0 | 0 | 1 | 43 | 29 | 50 | 39 | 80 | 0 | 56 | 0 | 0 | 195 | 17 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 57 | 0 | 36 | 13 | 36 | 92 | 6 | 318 | 48 | 17 | 17 | 0 | 16 | 0 | 17 | 52 | 36 | 34 | 345 | 16 | 21 | 90 | 35 | 0 | 17 | 20 | 48 | 0 | 290 | 17 | 0 | 269 | 49 | 427 | 503 | 350 | 40 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 0 | 126 | 8 | 16 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 16 | 30 | 8 | 30 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 174 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 304 | 55 | 0 | 37 | 0 | 41 | 0 | 5 | 35 | 780 | 220 | 0 | 17 | 1 | 26 | 55 | 0 | 0 | 308 | 22 | 170 | 1162 | 131 | 0 |  | 7933 | 5694 | 13627 | 4580 | 926 | 2741 | 0 | 1191 | 3418 | 30 | 0 | 302 | 110 | 280 | 49 | 547 | 73.71
10:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 405 | 0 |  | 0 | 450 | 300 | 8 | 17 | 40 | 312 | 0 | 0 | 9 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 20 | 14 | 33 | 30 | 8 | 0 | 30 | 0 | 115 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 19 | 6 | 7 | 12 | 0 | 0 | 0 | 330 | 315 | 207 | 8 | 0 | 28 | 43 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 25 | 16 | 112 | 109 | 0 | 0 | 2 | 40 | 29 | 47 | 37 | 80 | 0 | 54 | 0 | 0 | 200 | 17 | 0 | 0 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 57 | 0 | 48 | 13 | 36 | 161 | 6 | 384 | 48 | 35 | 17 | 0 | 16 | 0 | 17 | 17 | 37 | 34 | 370 | 17 | 10 | 90 | 35 | 0 | 22 | 22 | 54 | 0 | 315 | 17 | 0 | 270 | 44 | 371 | 450 | 400 | 10 |  | 925 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 126 | 8 | 16 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 16 | 30 | 0 | 30 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 174 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 380 | 54 | 0 | 57 | 0 | 47 | 0 | 6 | 55 | 740 | 220 | 0 | 17 | 4 | 62 | 55 | 0 | 0 | 307 | 29 | 150 | 1165 | 162 | 0 |  | 8028 | 5808 | 13836 | 4715 | 925 | 2815 | 0 | 1316 | 3306 | 30 | 0 | 253 | 112 | 320 | 44 | 539 | 73.71
11:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 403 | 0 |  | 0 | 450 | 301 | 19 | 25 | 40 | 315 | 0 | 0 | 24 | 49 | 32 | 0 | 0 | 0 | 0 | 2 | 35 | 35 | 0 | 20 | 14 | 33 | 28 | 11 | 0 | 0 | 30 | 114 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 19 | 6 | 7 | 12 | 0 | 0 | 0 | 335 | 290 | 206 | 8 | 0 | 31 | 41 | 0 | 43 | 0 | 35 | 25 | 0 | 0 | 32 | 16 | 124 | 108 | 0 | 0 | 2 | 41 | 29 | 50 | 37 | 112 | 0 | 54 | 0 | 0 | 202 | 17 | 0 | 0 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 56 | 0 | 93 | 0 | 36 | 162 | 5 | 363 | 48 | 35 | 17 | 2 | 16 | 22 | 17 | 17 | 36 | 34 | 345 | 16 | 40 | 90 | 35 | 0 | 30 | 25 | 53 | 0 | 345 | 54 | 0 | 272 | 43 | 391 | 450 | 400 | 46 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 16 | 0 | 0 | 50 | 39 | 0 | 0 | 0 | 25 | 31 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 174 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 57 | 0 | 53 | 0 | 7 | 75 | 740 | 220 | 0 | 17 | 4 | 78 | 55 | 0 | 0 | 309 | 32 | 150 | 1166 | 170 | 0 |  | 8339 | 5810 | 14149 | 4663 | 925 | 2915 | 0 | 1456 | 3330 | 30 | 0 | 257 | 124 | 406 | 43 | 526 | 73.7
12:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 396 | 0 |  | 0 | 450 | 298 | 39 | 68 | 40 | 310 | 0 | 0 | 54 | 49 | 32 | 0 | 0 | 0 | 0 | 37 | 35 | 35 | 0 | 20 | 14 | 33 | 28 | 16 | 0 | 0 | 30 | 114 | 0 | 6 | 212 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 24 | 6 | 7 | 12 | 0 | 0 | 0 | 325 | 310 | 206 | 16 | 0 | 29 | 38 | 0 | 43 | 0 | 35 | 25 | 0 | 0 | 32 | 16 | 120 | 96 | 0 | 0 | 2 | 40 | 29 | 50 | 35 | 112 | 0 | 54 | 0 | 0 | 201 | 17 | 0 | 0 | 300 | 16 | 8 | 0 | 95 | 0 | 0 | 57 | 0 | 96 | 19 | 40 | 162 | 6 | 378 | 48 | 35 | 17 | 5 | 16 | 36 | 17 | 44 | 36 | 35 | 340 | 16 | 45 | 90 | 35 | 0 | 31 | 26 | 53 | 0 | 365 | 54 | 0 | 270 | 50 | 432 | 550 | 450 | 75 |  | 925 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 8 | 16 | 0 | 0 | 40 | 28 | 0 | 0 | 0 | 25 | 8 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 173 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 57 | 0 | 51 | 0 | 7 | 75 | 800 | 220 | 0 | 25 | 2 | 88 | 55 | 0 | 0 | 308 | 33 | 180 | 451 | 191 | 0 |  | 8873 | 5182 | 14055 | 4672 | 925 | 3061 | 0 | 1738 | 2743 | 30 | 0 | 223 | 120 | 493 | 50 | 711 | 73.7
13:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 400 | 0 |  | 0 | 450 | 297 | 56 | 68 | 40 | 307 | 0 | 0 | 56 | 73 | 32 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 14 | 30 | 28 | 16 | 0 | 0 | 30 | 113 | 0 | 8 | 212 | 0 | 0 | 0 |  | 18 | 35 | 40 | 0 | 37 | 6 | 7 | 14 | 0 | 0 | 0 | 315 | 295 | 205 | 16 | 0 | 30 | 37 | 0 | 43 | 0 | 35 | 32 | 0 | 0 | 32 | 16 | 130 | 92 | 0 | 0 | 2 | 40 | 29 | 50 | 36 | 112 | 0 | 54 | 0 | 0 | 201 | 17 | 0 | 0 | 290 | 16 | 8 | 0 | 158 | 0 | 0 | 56 | 0 | 96 | 6 | 49 | 162 | 5 | 366 | 48 | 35 | 17 | 4 | 16 | 36 | 17 | 70 | 38 | 49 | 340 | 25 | 42 | 90 | 35 | 0 | 31 | 25 | 51 | 0 | 365 | 72 | 0 | 274 | 35 | 571 | 500 | 450 | 70 |  | 926 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 9 | 16 | 0 | 0 | 45 | 28 | 0 | 0 | 0 | 25 | 8 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 172 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 57 | 0 | 49 | 0 | 7 | 75 | 960 | 220 | 0 | 17 | 4 | 39 | 55 | 0 | 0 | 308 | 32 | 180 | 449 | 176 | 0 |  | 9134 | 5278 | 14412 | 4637 | 926 | 3011 | 0 | 1942 | 3044 | 30 | 0 | 250 | 130 | 407 | 35 | 752.54 | 73.69
14:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 398 | 0 |  | 0 | 450 | 295 | 56 | 68 | 40 | 301 | 0 | 0 | 56 | 73 | 64 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 14 | 30 | 28 | 16 | 0 | 0 | 30 | 114 | 0 | 8 | 212 | 0 | 0 | 0 |  | 18 | 35 | 51 | 0 | 33 | 6 | 0 | 2 | 0 | 0 | 0 | 320 | 305 | 197 | 8 | 0 | 30 | 38 | 0 | 43 | 0 | 33 | 33 | 0 | 0 | 31 | 16 | 126 | 88 | 0 | 0 | 2 | 40 | 29 | 50 | 33 | 112 | 0 | 54 | 0 | 0 | 201 | 16 | 0 | 0 | 310 | 16 | 8 | 0 | 228 | 0 | 0 | 54 | 0 | 97 | 5 | 49 | 162 | 6 | 376 | 46 | 17 | 17 | 0 | 16 | 36 | 17 | 70 | 36 | 49 | 354 | 32 | 17 | 90 | 35 | 0 | 31 | 22 | 52 | 0 | 340 | 72 | 0 | 276 | 33 | 573 | 500 | 450 | 25 |  | 926 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 16 | 0 | 0 | 45 | 28 | 5 | 0 | 0 | 25 | 8 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 172 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 57 | 0 | 58 | 0 | 7 | 75 | 980 | 220 | 0 | 17 | 4 | 45 | 55 | 0 | 0 | 308 | 28 | 180 | 450 | 157 | 0 |  | 9130 | 5307 | 14437 | 4634 | 926 | 3007 | 0 | 2004 | 3069 | 30 | 0 | 296 | 126 | 312 | 33 | 776.415 | 73.7
15:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 394 | 0 |  | 0 | 450 | 294 | 66 | 68 | 40 | 298 | 0 | 0 | 56 | 73 | 64 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 18 | 30 | 28 | 16 | 0 | 0 | 30 | 115 | 0 | 8 | 212 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 30 | 6 | 7 | 2 | 0 | 0 | 0 | 315 | 290 | 205 | 8 | 0 | 31 | 38 | 0 | 43 | 0 | 34 | 33 | 0 | 0 | 31 | 16 | 138 | 89 | 0 | 0 | 2 | 40 | 29 | 50 | 35 | 112 | 0 | 54 | 0 | 0 | 202 | 16 | 0 | 0 | 310 | 16 | 11 | 0 | 223 | 0 | 0 | 54 | 0 | 87 | 9 | 49 | 162 | 5 | 368 | 46 | 17 | 17 | 0 | 16 | 36 | 17 | 70 | 36 | 48 | 345 | 34 | 31 | 108 | 35 | 0 | 31 | 18 | 53 | 0 | 310 | 54 | 0 | 270 | 42 | 548 | 471 | 450 | 34 |  | 926 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 16 | 0 | 0 | 45 | 28 | 5 | 7 | 0 | 25 | 23 | 0 | 0 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 171 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 76 | 0 | 60 | 0 | 5 | 75 | 980 | 220 | 0 | 17 | 3 | 34 | 55 | 0 | 0 | 308 | 23 | 180 | 435 | 127 | 0 |  | 9062 | 5282 | 14344 | 4580 | 926 | 2976 | 0 | 2036 | 3024 | 30 | 0 | 306 | 138 | 286 | 42 | 989.38 | 73.68
16:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 390 | 0 |  | 0 | 450 | 295 | 74 | 68 | 40 | 298 | 0 | 0 | 28 | 73 | 64 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 19 | 30 | 28 | 16 | 0 | 0 | 30 | 120 | 0 | 8 | 212 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 38 | 6 | 0 | 2 | 0 | 0 | 0 | 315 | 280 | 205 | 8 | 0 | 32 | 37 | 0 | 43 | 0 | 34 | 33 | 0 | 0 | 31 | 16 | 132 | 89 | 0 | 0 | 1 | 40 | 29 | 50 | 33 | 112 | 0 | 54 | 0 | 0 | 202 | 16 | 0 | 0 | 310 | 16 | 8 | 0 | 225 | 0 | 0 | 54 | 0 | 82 | 3 | 49 | 161 | 6 | 371 | 46 | 17 | 17 | 2 | 16 | 36 | 17 | 70 | 32 | 49 | 345 | 43 | 19 | 108 | 35 | 0 | 31 | 11 | 72 | 0 | 310 | 17 | 0 | 270 | 47 | 547 | 420 | 420 | 20 |  | 925 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 9 | 16 | 0 | 0 | 45 | 40 | 8 | 8 | 0 | 25 | 38 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 170 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 414 | 18 | 0 | 76 | 0 | 67 | 0 | 3 | 75 | 1020 | 220 | 0 | 17 | 2 | 43 | 55 | 0 | 0 | 306 | 15 | 180 | 433 | 88 | 0 |  | 8900 | 5306 | 14206 | 4559 | 925 | 2894 | 0 | 2054 | 3058 | 30 | 0 | 300 | 132 | 207 | 47 | 1025.67 | 73.68
17:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 399 | 0 |  | 0 | 450 | 297 | 87 | 70 | 40 | 298 | 0 | 0 | 50 | 73 | 64 | 13 | 0 | 0 | 0 | 39 | 35 | 35 | 0 | 20 | 15 | 0 | 28 | 16 | 0 | 0 | 30 | 115 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 37 | 6 | 7 | 9 | 0 | 0 | 0 | 310 | 270 | 206 | 8 | 0 | 32 | 36 | 0 | 43 | 0 | 34 | 33 | 0 | 0 | 31 | 0 | 122 | 91 | 0 | 0 | 0 | 40 | 28 | 53 | 33 | 112 | 0 | 54 | 0 | 0 | 205 | 16 | 0 | 0 | 280 | 16 | 8 | 0 | 228 | 0 | 0 | 64 | 0 | 87 | 1 | 49 | 105 | 5 | 365 | 48 | 17 | 17 | 1 | 16 | 47 | 20 | 70 | 32 | 48 | 345 | 50 | 8 | 108 | 35 | 0 | 32 | 4 | 88 | 0 | 310 | 17 | 0 | 265 | 36 | 749 | 352 | 300 | 8 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 16 | 0 | 0 | 45 | 40 | 6 | 8 | 0 | 25 | 38 | 0 | 23 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 170 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 373 | 35 | 0 | 76 | 0 | 81 | 0 | 2 | 75 | 1000 | 220 | 0 | 17 | 0 | 20 | 55 | 0 | 0 | 306 | 6 | 180 | 434 | 35 | 0 |  | 8800 | 5205 | 14005 | 4497 | 926 | 2646 | 0 | 2106 | 3236 | 30 | 0 | 321 | 122 | 85 | 36 | 854.725 | 73.67
18:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 399 | 0 |  | 0 | 370 | 300 | 92 | 72 | 39 | 300 | 0 | 0 | 56 | 65 | 110 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 15 | 0 | 28 | 16 | 0 | 0 | 30 | 117 | 0 | 11 | 211 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 37 | 16 | 7 | 14 | 0 | 0 | 0 | 310 | 270 | 207 | 8 | 0 | 33 | 36 | 0 | 51 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 96 | 91 | 0 | 0 | 0 | 40 | 28 | 53 | 33 | 112 | 0 | 60 | 0 | 0 | 206 | 16 | 0 | 0 | 270 | 16 | 8 | 0 | 225 | 0 | 0 | 57 | 0 | 117 | 0 | 61 | 85 | 6 | 365 | 56 | 17 | 17 | 0 | 16 | 54 | 34 | 114 | 60 | 60 | 345 | 50 | 1 | 108 | 72 | 0 | 33 | 1 | 94 | 0 | 310 | 17 | 0 | 265 | 24 | 751 | 348 | 300 | 1 |  | 926 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 3 | 9 | 0 | 80 | 8 | 16 | 0 | 0 | 50 | 40 | 6 | 8 | 0 | 25 | 38 | 0 | 23 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 170 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 350 | 55 | 0 | 76 | 0 | 83 | 0 | 0 | 95 | 800 | 180 | 0 | 17 | 0 | 3 | 75 | 0 | 0 | 308 | 1 | 150 | 435 | 7 | 0 |  | 8900 | 4881 | 13781 | 4424 | 926 | 2506 | 0 | 2371 | 3011 | 30 | 0 | 379 | 96 | 14 | 24 | 495.645 | 73.67
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 400 | 0 |  | 0 | 450 | 301 | 91 | 75 | 30 | 300 | 0 | 0 | 67 | 90 | 145 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 15 | 33 | 28 | 16 | 0 | 0 | 30 | 120 | 0 | 25 | 211 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 55 | 19 | 7 | 20 | 0 | 0 | 0 | 320 | 280 | 211 | 8 | 0 | 35 | 42 | 0 | 51 | 0 | 34 | 50 | 0 | 0 | 32 | 0 | 116 | 94 | 0 | 0 | 0 | 40 | 28 | 53 | 36 | 112 | 0 | 56 | 0 | 0 | 206 | 16 | 0 | 0 | 295 | 16 | 8 | 0 | 265 | 0 | 0 | 104 | 0 | 121 | 0 | 61 | 90 | 5 | 370 | 86 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 63 | 60 | 350 | 50 | 0 | 162 | 72 | 0 | 33 | 0 | 94 | 0 | 340 | 17 | 0 | 270 | 24 | 780 | 405 | 350 | 0 |  | 926 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 26 | 45 | 0 | 130 | 10 | 36 | 0 | 0 | 50 | 40 | 10 | 80 | 0 | 25 | 38 | 0 | 23 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 168 | 0 | 173 | 0 | 0 | 0 | 5 | 0 | 414 | 55 | 0 | 113 | 0 | 85 | 0 | 0 | 95 | 910 | 220 | 0 | 17 | 0 | 0 | 112 | 0 | 0 | 306 | 0 | 209 | 435 | 0 | 0 |  | 9757 | 5429 | 15186 | 4610 | 926 | 2845 | 0 | 2874 | 3212 | 30 | 0 | 549 | 116 | 0 | 24 | 490.87 | 73.65
19:30 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 403 | 0 |  | 0 | 450 | 278 | 91 | 65 | 40 | 295 | 0 | 0 | 67 | 82 | 147 | 13 | 0 | 0 | 0 | 0 | 55 | 41 | 0 | 22 | 0 | 33 | 28 | 16 | 0 | 0 | 30 | 117 | 0 | 25 | 212 | 0 | 0 | 0 |  | 18 | 48 | 51 | 0 | 80 | 19 | 7 | 22 | 0 | 0 | 0 | 305 | 280 | 213 | 8 | 0 | 37 | 42 | 0 | 51 | 0 | 34 | 52 | 0 | 0 | 0 | 0 | 106 | 97 | 0 | 0 | 0 | 42 | 28 | 53 | 37 | 112 | 0 | 62 | 0 | 0 | 206 | 16 | 0 | 0 | 285 | 16 | 8 | 0 | 275 | 0 | 0 | 104 | 0 | 129 | 0 | 61 | 90 | 5 | 366 | 96 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 63 | 60 | 345 | 50 | 0 | 162 | 72 | 0 | 33 | 0 | 94 | 0 | 300 | 61 | 0 | 265 | 37 | 776 | 400 | 350 | 0 |  | 875 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 29 | 49 | 0 | 130 | 10 | 48 | 0 | 0 | 50 | 40 | 11 | 85 | 0 | 25 | 40 | 0 | 23 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 167 | 0 | 204 | 0 | 0 | 0 | 5 | 0 | 414 | 55 | 0 | 113 | 0 | 85 | 0 | 0 | 95 | 1160 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 307 | 0 | 230 | 436 | 0 | 0 |  | 9654 | 5706 | 15360 | 4540 | 875 | 2810 | 0 | 2868 | 3476 | 30 | 0 | 618 | 106 | 0 | 37 | 467.95 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 403 | 0 |  | 0 | 450 | 305 | 89 | 68 | 38 | 310 | 0 | 0 | 67 | 82 | 146 | 13 | 0 | 0 | 0 | 22 | 55 | 55 | 0 | 22 | 0 | 33 | 30 | 16 | 0 | 0 | 30 | 120 | 0 | 25 | 212 | 0 | 0 | 0 |  | 18 | 48 | 51 | 0 | 79 | 19 | 7 | 26 | 0 | 0 | 0 | 320 | 300 | 214 | 8 | 0 | 37 | 43 | 0 | 51 | 0 | 15 | 52 | 0 | 0 | 28 | 0 | 110 | 96 | 0 | 0 | 0 | 41 | 28 | 53 | 37 | 112 | 0 | 59 | 0 | 0 | 206 | 16 | 0 | 0 | 270 | 16 | 8 | 0 | 275 | 0 | 0 | 107 | 0 | 126 | 0 | 61 | 90 | 6 | 368 | 97 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 65 | 60 | 345 | 50 | 0 | 162 | 72 | 0 | 33 | 0 | 96 | 0 | 300 | 108 | 0 | 265 | 27 | 779 | 400 | 350 | 0 |  | 639 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 40 | 39 | 0 | 130 | 10 | 64 | 0 | 0 | 45 | 40 | 11 | 85 | 0 | 25 | 40 | 8 | 23 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 166 | 0 | 203 | 0 | 0 | 0 | 5 | 0 | 414 | 55 | 0 | 113 | 0 | 92 | 0 | 0 | 95 | 1120 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 306 | 0 | 200 | 433 | 0 | 0 |  | 9816 | 5436 | 15252 | 4629 | 639 | 2827 | 0 | 2939 | 3405 | 30 | 0 | 646 | 110 | 0 | 27 | 380.09 | 73.66
21:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 406 | 0 |  | 0 | 450 | 293 | 91 | 51 | 40 | 313 | 0 | 0 | 67 | 82 | 147 | 0 | 0 | 0 | 0 | 42 | 55 | 55 | 0 | 20 | 15 | 33 | 30 | 16 | 0 | 0 | 30 | 117 | 0 | 25 | 212 | 0 | 0 | 0 |  | 18 | 48 | 51 | 0 | 82 | 19 | 7 | 26 | 0 | 0 | 0 | 300 | 280 | 218 | 16 | 0 | 38 | 49 | 0 | 51 | 0 | 14 | 52 | 0 | 0 | 21 | 0 | 6 | 100 | 0 | 0 | 0 | 41 | 28 | 53 | 37 | 112 | 0 | 62 | 0 | 0 | 207 | 16 | 0 | 0 | 310 | 16 | 8 | 0 | 180 | 0 | 0 | 107 | 0 | 130 | 0 | 61 | 90 | 5 | 365 | 98 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 66 | 60 | 345 | 50 | 0 | 162 | 72 | 0 | 34 | 0 | 96 | 0 | 300 | 108 | 0 | 265 | 19 | 781 | 506 | 350 | 0 |  | 643 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 30 | 47 | 0 | 130 | 10 | 64 | 0 | 0 | 50 | 40 | 11 | 85 | 0 | 25 | 38 | 8 | 23 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 167 | 0 | 205 | 0 | 0 | 0 | 4 | 0 | 414 | 55 | 0 | 113 | 0 | 92 | 0 | 0 | 95 | 1150 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 307 | 0 | 200 | 435 | 0 | 0 |  | 9741 | 5452 | 15193 | 4590 | 643 | 2975 | 0 | 2847 | 3441 | 30 | 0 | 642 | 6 | 0 | 19 | 293.185 | 73.65
22:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 405 | 0 |  | 0 | 450 | 307 | 25 | 28 | 40 | 318 | 0 | 0 | 70 | 82 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 22 | 15 | 33 | 30 | 16 | 0 | 0 | 30 | 115 | 0 | 25 | 212 | 0 | 0 | 0 |  | 18 | 48 | 51 | 0 | 82 | 19 | 8 | 28 | 0 | 0 | 0 | 300 | 280 | 215 | 16 | 0 | 38 | 49 | 0 | 51 | 0 | 14 | 52 | 0 | 0 | 28 | 0 | 58 | 101 | 0 | 0 | 0 | 43 | 29 | 53 | 37 | 112 | 0 | 61 | 0 | 0 | 207 | 18 | 0 | 0 | 280 | 16 | 8 | 0 | 178 | 0 | 0 | 107 | 0 | 133 | 0 | 61 | 89 | 6 | 373 | 98 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 67 | 60 | 350 | 17 | 0 | 162 | 72 | 0 | 34 | 0 | 96 | 0 | 270 | 90 | 0 | 265 | 7 | 781 | 505 | 350 | 0 |  | 645 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 30 | 41 | 0 | 130 | 8 | 64 | 0 | 0 | 50 | 40 | 16 | 85 | 0 | 25 | 38 | 0 | 23 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 166 | 0 | 208 | 0 | 0 | 0 | 6 | 0 | 414 | 55 | 0 | 113 | 0 | 92 | 0 | 0 | 95 | 1200 | 220 | 0 | 17 | 0 | 0 | 75 | 0 | 0 | 308 | 0 | 200 | 438 | 0 | 0 |  | 9622 | 5476 | 15098 | 4606 | 645 | 2959 | 0 | 2675 | 3495 | 30 | 0 | 623 | 58 | 0 | 7 | 317 | 73.65
23:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 400 | 0 |  | 0 | 450 | 307 | 18 | 30 | 40 | 325 | 0 | 0 | 65 | 82 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 22 | 0 | 33 | 16 | 16 | 0 | 0 | 30 | 112 | 0 | 8 | 212 | 0 | 0 | 0 |  | 14 | 48 | 51 | 0 | 63 | 19 | 8 | 30 | 0 | 0 | 0 | 290 | 250 | 214 | 45 | 0 | 38 | 50 | 0 | 51 | 0 | 14 | 52 | 0 | 0 | 0 | 0 | 86 | 102 | 0 | 0 | 0 | 43 | 29 | 53 | 37 | 112 | 0 | 59 | 0 | 0 | 207 | 18 | 0 | 0 | 310 | 16 | 8 | 0 | 180 | 0 | 0 | 108 | 0 | 129 | 0 | 61 | 89 | 6 | 395 | 99 | 70 | 17 | 0 | 16 | 54 | 34 | 114 | 61 | 60 | 350 | 17 | 0 | 162 | 53 | 0 | 33 | 0 | 96 | 0 | 230 | 17 | 0 | 267 | 1 | 780 | 505 | 450 | 0 |  | 644 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 30 | 44 | 0 | 128 | 9 | 64 | 0 | 0 | 50 | 40 | 14 | 85 | 0 | 16 | 38 | 0 | 23 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 166 | 0 | 209 | 0 | 0 | 0 | 30 | 0 | 414 | 55 | 0 | 57 | 0 | 85 | 0 | 0 | 95 | 1220 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 308 | 0 | 230 | 437 | 0 | 0 |  | 9357 | 5438 | 14795 | 4511 | 644 | 3122 | 0 | 2436 | 3545 | 30 | 0 | 420 | 86 | 0 | 1 | 673 | 73.64
24:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 402 | 0 |  | 0 | 450 | 306 | 17 | 82 | 40 | 331 | 0 | 0 | 68 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 20 | 0 | 33 | 32 | 8 | 0 | 0 | 30 | 114 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 48 | 51 | 0 | 20 | 6 | 8 | 28 | 0 | 0 | 0 | 285 | 265 | 216 | 63 | 0 | 37 | 50 | 0 | 51 | 0 | 26 | 25 | 0 | 0 | 0 | 0 | 86 | 76 | 0 | 0 | 0 | 43 | 30 | 53 | 37 | 112 | 0 | 59 | 0 | 0 | 207 | 17 | 0 | 0 | 305 | 16 | 5 | 0 | 180 | 0 | 0 | 108 | 0 | 68 | 0 | 49 | 89 | 5 | 365 | 99 | 17 | 17 | 0 | 16 | 36 | 34 | 70 | 40 | 60 | 345 | 17 | 0 | 17 | 35 | 0 | 35 | 0 | 91 | 0 | 260 | 17 | 0 | 273 | 16 | 780 | 450 | 450 | 0 |  | 645 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 24 | 44 | 0 | 130 | 10 | 64 | 0 | 0 | 55 | 40 | 14 | 35 | 0 | 16 | 38 | 0 | 23 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 166 | 0 | 211 | 0 | 0 | 0 | 80 | 0 | 388 | 55 | 0 | 57 | 0 | 56 | 0 | 0 | 55 | 1244 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 307 | 0 | 260 | 436 | 0 | 0 |  | 8803 | 5380 | 14183 | 4550 | 645 | 3052 | 0 | 1825 | 3603 | 30 | 0 | 376 | 86 | 0 | 16 | 1019 | 73.64
KWH | 0 | 0 | 0 | 4047750 | 0 | 1744863 | 0 | 9676800 | 0 |  | 0 | 10287000 | 7226851 | 1289280 | 1243550 | 970588 | 7516194 | 0 | 0 | 955824 | 1223280 | 1269600 | 91003 | 0 | 0 | 0 | 601200 | 671604 | 659578 | 0 | 480000 | 317520 | 698500 | 709400 | 296304 | 0 | 263640 | 412000 | 2600000 | 0 | 212958 | 4886949 | 0 | 0 | 0 |  | 389280 | 889632 | 1001489 | 0 | 785280 | 215040 | 142560 | 435840 | 0 | 0 | 0 | 7016200 | 6990000 | 5070000 | 886545 | 0 | 733896 | 1014240 | 0 | 1058786 | 0 | 767296 | 785251 | 0 | 0 | 621000 | 245750 | 2578560 | 2926080 | 0 | 0 | 14450 | 967000 | 679920 | 1243800 | 877392 | 2406845 | 0 | 1392768 | 0 | 0 | 5046850 | 401000 | 0 | 0 | 7178500 | 368112 | 162624 | 0 | 3171491 | 0 | 0 | 1771200 | 0 | 1716336 | 73710 | 1088640 | 2677920 | 143854 | 8708000 | 1536000 | 890880 | 470873 | 13320 | 381382 | 669513 | 553670 | 1696320 | 1045800 | 1062720 | 8442300 | 655680 | 261840 | 1949760 | 1035000 | 0 | 730080 | 186366 | 1367040 | 0 | 7474200 | 871490 | 0 | 6507272 | 691200 | 12960000 | 11416363 | 9353182 | 310709 |  | 19242909 | 0 | 8606304 | 0 | 0 | 0 | 0 | 0 | 310560 | 625792 | 0 | 2986000 | 218110 | 1030368 | 0 | 0 | 1170000 | 907707 | 103314 | 706864 | 0 | 449131 | 620420 | 33077 | 446762 | 0 | 0 | 263034 | 1676072 | 0 | 5559000 | 0 | 0 | 4321800 | 0 | 4915327 | 0 | 0 | 0 | 164145 | 0 | 8972509 | 1306080 | 0 | 1376256 | 0 | 1366800 | 0 | 52266 | 1394592 | 26165000 | 5077773 | 0 | 445200 | 32160 | 537120 | 1420608 | 0 | 0 | 7389091 | 236692 | 4974500 | 18970909 | 1236690 | 0 |  | 207528333 | 135310942 | 342839275 | 110747983 | 19242909 | 69398599 | 0 | 43826291 | 84201844 | 675640 | 0 | 8520926 | 2578560 | 2955323 | 691200 | 0
Fuel Cost | 0 | 0 | 0 | 18012487.5 | 0 | 6665376.66 | 0 | 27869184 | 0 |  | 0 | 32712660 | 24715830.42 | 25476172.8 | 23254385 | 17101760.56 | 22924391.7 | 0 | 0 | 18887082.24 | 21957876 | 24655632 | 1697205.95 | 0 | 0 | 0 | 10977912 | 10584479.04 | 12063681.62 | 0 | 360000 | 0 | 0 | 0 | 5306804.64 | 0 | 0 | 0 | 14196000 | 0 | 4033424.52 | 15589367.31 | 0 | 0 | 0 |  | 6847435.2 | 15666419.52 | 17936667.99 | 0 | 15367929.6 | 3539558.4 | 530323.2 | 0 | 0 | 0 | 0 | 19575198 | 21389400 | 16832400 | 2969925.75 | 0 | 2473229.52 | 4442371.2 | 0 | 4245731.86 | 0 | 13742271.36 | 14181633.06 | 0 | 0 | 2310120 | 184312.5 | 16915353.6 | 9100108.8 | 0 | 0 | 0 | 3771300 | 2536101.6 | 5659290 | 3992133.6 | 8231409.9 | 0 | 7729862.4 | 0 | 0 | 14080711.5 | 2638580 | 0 | 0 | 22181565 | 276084 | 123594.24 | 0 | 64698416.4 | 0 | 0 | 34024752 | 0 | 30224676.96 | 0 | 19388678.4 | 46461912 | 2385099.32 | 23076200 | 29276160 | 16712908.8 | 8447461.62 | 0 | 6235595.7 | 13015332.72 | 9932839.8 | 32416675.2 | 20298978 | 18927043.2 | 22456518 | 11192457.6 | 0 | 35661110.4 | 17367300 | 0 | 13046529.6 | 0 | 24634060.8 | 0 | 22198374 | 12270579.2 | 0 | 45355685.84 | 0 | 76464000 | 0 | 0 | 0 |  | 54072574.29 | 0 | 25388596.8 | 0 | 0 | 0 | 0 | 0 | 5841633.6 | 11771147.52 | 0 | 9435760 | 1033841.4 | 17763544.32 | 0 | 0 | 5709600 | 16257032.37 | 1895811.9 | 11882383.84 | 0 | 8564928.17 | 11111722.2 | 585462.9 | 8001507.42 | 0 | 0 | 199116.738 | 18487074.16 | 0 | 46917960 | 0 | 0 | 14261940 | 0 | 16368038.91 | 0 | 0 | 0 | 546602.85 | 0 | 26199726.28 | 22307846.4 | 0 | 27277393.92 | 0 | 27226656 | 0 | 0 | 27668705.28 | 169549200 | 15791874.03 | 0 | 8614620 | 0 | 0 | 24647548.8 | 0 | 0 | 53940364.3 | 0 | 37060025 | 125397708.49 | 0 | 0 |  | 1254682081.32 | 851777947.888 | 2106460029.208 | 342143503.568 | 54072574.29 | 158841736.1 | 0 | 810282034.94 | 573172017.79 | 0 | 0 | 151032808.92 | 16915353.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 403 | 0 |  | 0 | 450 | 301 | 19 | 25 | 40 | 315 | 0 | 0 | 24 | 49 | 32 | 0 | 0 | 0 | 0 | 2 | 35 | 35 | 0 | 20 | 14 | 33 | 28 | 11 | 0 | 0 | 30 | 114 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 34 | 0 | 19 | 6 | 7 | 12 | 0 | 0 | 0 | 335 | 290 | 206 | 8 | 0 | 31 | 41 | 0 | 43 | 0 | 35 | 25 | 0 | 0 | 32 | 16 | 124 | 108 | 0 | 0 | 2 | 41 | 29 | 50 | 37 | 112 | 0 | 54 | 0 | 0 | 202 | 17 | 0 | 0 | 300 | 16 | 8 | 0 | 15 | 0 | 0 | 56 | 0 | 93 | 0 | 36 | 162 | 5 | 363 | 48 | 35 | 17 | 2 | 16 | 22 | 17 | 17 | 36 | 34 | 345 | 16 | 40 | 90 | 35 | 0 | 30 | 25 | 53 | 0 | 345 | 54 | 0 | 272 | 43 | 391 | 450 | 400 | 46 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 16 | 0 | 0 | 50 | 39 | 0 | 0 | 0 | 25 | 31 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 174 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 57 | 0 | 53 | 0 | 7 | 75 | 740 | 220 | 0 | 17 | 4 | 78 | 55 | 0 | 0 | 309 | 32 | 150 | 1166 | 170 | 0 |  | 14149 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 403 | 0 |  | 0 | 450 | 278 | 91 | 65 | 40 | 295 | 0 | 0 | 67 | 82 | 147 | 13 | 0 | 0 | 0 | 0 | 55 | 41 | 0 | 22 | 0 | 33 | 28 | 16 | 0 | 0 | 30 | 117 | 0 | 25 | 212 | 0 | 0 | 0 | 0 | 18 | 48 | 51 | 0 | 80 | 19 | 7 | 22 | 0 | 0 | 0 | 305 | 280 | 213 | 8 | 0 | 37 | 42 | 0 | 51 | 0 | 34 | 52 | 0 | 0 | 0 | 0 | 106 | 97 | 0 | 0 | 0 | 42 | 28 | 53 | 37 | 112 | 0 | 62 | 0 | 0 | 206 | 16 | 0 | 0 | 285 | 16 | 8 | 0 | 275 | 0 | 0 | 104 | 0 | 129 | 0 | 61 | 90 | 5 | 366 | 96 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 63 | 60 | 345 | 50 | 0 | 162 | 72 | 0 | 33 | 0 | 94 | 0 | 300 | 61 | 0 | 265 | 37 | 776 | 400 | 350 | 0 |  | 875 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 29 | 49 | 0 | 130 | 10 | 48 | 0 | 0 | 50 | 40 | 11 | 85 | 0 | 25 | 40 | 0 | 23 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 167 | 0 | 204 | 0 | 0 | 0 | 5 | 0 | 414 | 55 | 0 | 113 | 0 | 85 | 0 | 0 | 95 | 1160 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 307 | 0 | 230 | 436 | 0 | 0 |  | 15360 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 |  | 0 | 450 | 310 | 100 | 100 | 40 | 335 | 0 | 0 | 80 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 16 | 33 | 33 | 16 | 0 | 0 | 30 | 115 | 0 | 25 | 211 | 0 | 0 | 0 |  | 22 | 64 | 51 | 0 | 90 | 6 | 5 | 30 | 0 | 0 | 0 | 345 | 335 | 0 | 90 | 0 | 34 | 50 | 0 | 51 | 0 | 41 | 52 | 0 | 0 | 33 | 20 | 151 | 100 | 0 | 0 | 0 | 43 | 28 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 210 | 17 | 0 | 0 | 300 | 25 | 5 | 0 | 300 | 0 | 0 | 108 | 0 | 149 | 0 | 60 | 120 | 6 | 400 | 97 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 75 | 70 | 380 | 53 | 0 | 162 | 52 | 0 | 35 | 0 | 95 | 0 | 330 | 163 | 0 | 270 | 40 | 800 | 500 | 450 |  |  | 651 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 50 | 38 | 25 | 95 | 0 | 42 | 50 | 8 | 33 | 0 | 0 | 11 | 75 | 0 | 230 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 414 | 90 | 0 | 113 | 0 | 80 | 0 | 0 | 95 | 1244 | 220 | 0 | 27 | 0 | 0 | 115 | 0 | 0 | 375 | 0 | 307 | 1200 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 | 0 | 0 | 450 | 310 | 25 | 25 | 40 | 335 | 0 | 0 | 60 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 20 | 15 | 33 | 33 | 16 | 0 | 0 | 30 | 115 | 0 | 8 | 211 |  | 0 | 0 | 0 | 12 | 40 | 35 | 0 | 20 | 6 | 5 | 15 | 0 | 0 | 0 | 345 | 300 | 0 | 90 | 0 | 34 | 50 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 33 | 20 | 146 | 100 | 0 | 0 | 1.6 | 43 | 28 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 210 | 17 | 0 | 0 | 300 | 25 | 5 | 0 | 210 | 0 | 0 | 56 | 0 | 52 | 20 | 36 | 100 | 6 | 400 | 50 | 35 | 17 | 5 | 16 | 17 | 17 | 52 | 36 | 40 | 380 | 17 | 50 | 90 | 35 | 0 | 17 | 35 | 54 | 0 | 280 | 54 | 0 | 270 | 40 | 360 | 500 | 360 | 33 |  | 940 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 25 | 44 | 0 | 130 | 10 | 48 | 0 | 0 | 50 | 38 | 0 | 50 | 0 | 42 | 40 | 8 | 23 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 180 | 0 | 414 | 90 | 0 | 35 | 0 | 56 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 375 | 30 | 200 | 1200 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 401 | 0 | 0 | 0 | 330 | 260 | 0 | 25 | 40 | 331 | 0 | 0 | 17 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 10 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 120 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 0 | 0 | 0 | 295 | 240 | 0 | 92 | 0 | 37 | 50 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 0 | 72 | 85 | 0 | 0 | 1 | 43 | 30 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 201 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 23 | 0 | 0 | 51 | 0 | 315 | 49 | 17 | 0 | 3 | 0 | 0 | 0 | 52 | 9 | 0 | 310 | 0 | 21 | 0 | 0 | 0 | 17 | 12 | 17 | 0 | 230 | 0 | 0 | 271 | 0 | 729 | 350 | 350 | 35 | 0 | 929 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 157 | 0 | 345 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 700 | 180 | 0 | 0 | 1 | 38 | 35 | 0 | 0 | 309 | 13 | 150 | 418 | 88 | 0 | 0 |  |  |  | 180146582 | 19242909 | 0 | 84201844 | 52347217 | 2578560 | 2955323 | 691200 | 675640 |  |  | 342839275
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 | [5 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 180.1466 | 19.2429 | 0 | 84.2018 | 52.3472 | 2.5786 | 2.9553 | 0.6912 | 0.67564
| Minimum Generation |  | 13298 | 7:00
| Highest Generation |  | 15360 | 19:30 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 342.8393
| Day Peak Generation |  | 14149 | 11:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15360 | 19:30 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 926 | 3:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 875 | 19:30
| Load factor L.F |  | 93% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-03
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 14149 | MW Hour : | 11:00 | Min. Gen. at | 8:00 | 11149
Evening Peak Generation : |  |  | 15360 | MW Hour : | 19:30 | Available Max Generation : |  | 17276
E.P. Demand (at gen end) : |  |  | 15850 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 16000
Maximum Generation : |  |  | 15360 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1276
Total Gen. (MKWH) : |  |  | 342.8393 | System Load Factor : | 93% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 500 | MW at | 24:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-03
Actual : |  | 73.62 | Ft.(MSL) , | Rule curve : | 81.62 | Ft.( MSL )
Gas Consumed : |  | Total = | 1306.01 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 500985239.668
: |  |  | Coal : | 573172017.79 | Oil : | 961314843.86 | Total : | 2035472101.318
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 161 | 3864:00 | 5342.4914 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1476.7776 |  |  | 0 | 0%
Mymensingh Area |  | 195 | 4680:00 | 1099.0436 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | 0%
Rangpur Area |  | 112 | 2688:00 | 1004.2252 |  |  | 0 | 0%
Total |  | 468 |  | 15383.887 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
- | 8:31 | Bakulia-Khulshi 132 kV Ckt-1 is restored.
- | 8:36 | BSRM-Cumilla(N) 230 kV Ckt-1 is restored.
8:40 | 10:14 | BSRM-Cumilla(N) 230 kV Ckt-2 Forced S/D from BSRM 230/33kV end Due to spark and from Cumilla(N) 230/132/33kV end Due
to Sparking remove in 71 & 83 No tower
8:53 | 16:30 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Project Work S/D Due to AR Modification
9:07 | 17:49 | Sunamganj 132/33kV S/S Chhatak-Sunamgonj CKT-2 Project Work S/D
9:08 | 11:14 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to Fixing high temperature at Ashuganj-2, |  |  |  |  | 50.0MW load interrup.
|  | B-Bus D/S, Y-Phase |  |  |  |  | Kishoreganj 132/33kV end
- | 9:26 | Madaripur 132/33kV S/S T1-405T HT is restored.
- | 9:27 | Madaripur 132/33kV S/S T1-405T LT is restored.
10:09 | 13:44 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Shutdown taken from Bhandaria grid and
from Bhandaria 132/33kV end Due to Emergency Row.
10:22 | 10:41 | BSRM-GPH 230 kV Ckt-2 Tripped from GPH 230/33kV end showing Zone-1/1B Trip, B phase Trip, CR Rec/ DT Trip,
67N/51N EF Trip. relays Due to Zone-1 Trip
10:24 | 10:42 | BSRM-GPH 230 kV Ckt-1 Tripped from BSRM 230/33kV end showing Distance relay relays.
10:42 | 12:01 | Khulshi-MSML 132kV Ckt-2 Project Work S/D from Khulshi 132/33kV end Due to Transfer bus dismantling work by ESPNCA
10:51 | 12:47 | Bheramara-HVDC Bheramara 230 kV Ckt-2 Scheduled S/D from BIPTC end Due to Red hot maintenance
- | 11:04 | Kishoreganj 132/33kV S/S Bus-A is restored.
11:17 | 15:06 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-1 Scheduled S/D Due to EMS tuning for SCADA connection
11:27 | - | Adani Power Jharkhand Ltd. Unit-2 tripped at 11:27 hrs. |  |  |  |  | 748MW generation interrup.
12:00 | - | Day peak generation:14055 MW
12:30 | - | Ghorashal AIS- Ghorashal GIS 230 kV line-3 was switched on at 12:30 hrs.
12:30 | 12:41 | Naogaon 132/33kV S/S T-2 LT Tripped showing O/C relays Due to Adamdhighi PBS 33 kv C Phase LA burst. |  |  |  |  | 37.0MW load interrup.
12:30 | 12:47 | Naogaon 132/33kV S/S T-1 LT Tripped showing O/C, relay relays Due to Adamdhighi PBS 33 kv C Phase LA burst. |  |  |  |  | 37.0MW load interrup.
- | 13:55 | Shahjibazar 132/33kV S/S SPCL 86 MW is restored.
14:02 | 14:25 | Shikalbaha 230/132kV S/S Hathazari - 01 Tripped showing FN 1 relays.
14:03 | 14:14 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing Distance C relays Due to i) Distance Trip
ii) Distance B iii) Distance G
14:03 | - | Halishahar-Khulshi 132kV Ckt-1 Tripped from Khulshi 132/33kV end showing Lockout relay relays Due to Directional Earth Fault
14:03 | 14:12 | Hathazari-Madunaghat 132kV Ckt-2 Tripped from Madunaghat 132/33kV end showing REL-670 relays.
14:03 | 14:52 | Baroaulia-Hathazari 132 kV Ckt-2 Tripped from Baroaulia 132/33kV end showing Distance C Zone 2 relays Due to High storm
14:03 | 14:14 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Baroaulia 132/33kV end showing Distance C relays Due to i) Distance Trip
ii) Distance B iii) Distance G
14:04 | 14:26 | GPH 230/33kV S/S HATHAZARI-2 Tripped showing Y phase Trip, B phase Trip, Zone-1 Trip, relays Due to Zone-1 Trip
14:04 | 14:49 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Baroirhat 132/33kV end showing Distance Trip Trip Relay K31,K34 & K34X relays.
14:35 | 15:30 | Chandraghona-Madunaghat 132 kV Ckt-2 Tripped from Chandraghona 132/33kV end showing REL670 relays. and from
Madunaghat 132/33kV end showing General Trip zcom R-ph relays Due to None
14:35 | 15:14 | Chandraghona-Madunaghat 132 kV Ckt-1 Tripped from Chandraghona 132/33kV end showing REL 670 relays. and from
Madunaghat 132/33kV end showing Rel-670 relays.
16:13 | 17:06 | BSRM-GPH 230 kV Ckt-1 Forced S/D from BSRM 230/33kV end Due to Kite hanging
16:13 | 17:06 | BSRM-GPH 230 kV Ckt-2 Forced S/D from GPH 230/33kV end Due to Emergency Maintenance.
16:31 | 16:54 | BIPTC S/S 10CF15 Forced S/D Due to None
17:25 | 21:22 | Rampur 230/132/33 S/S Halishahar-1 Project Work S/D Due to 400kv GNDP Project stability test.
17:30 | 20:20 | BIPTC S/S Baharampur-2 Forced S/D Due to For rectification/replacement of porcelain disc insulator caused due to
lightning by Grid India.
18:02 | - | Sirajgonj 225MW CCPP Unit-3 Syncronized with remarks:- GT
19:12 | 19:25 | Cumilla(S)-Kachua 132 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Distance relay relays.
19:15 | 20:43 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Tripped showing Overcurrent relay relays Due to 33 KV Kotbari feeder faulty |  |  |  |  | 15.0MW load interrup.
19:15 | 19:29 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Tripped showing overcurrent relay relays. |  |  |  |  | 15.0MW load interrup.
19:15 | 20:40 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Tripped showing Overcurrent relay relays Due to 33 KV Kotbari feeder fault |  |  |  |  | 15.0MW load interrup.
19:30 | - | Peak generation 15360 MW
19:50 | 20:47 | Cumilla(S)-Kachua 132 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Distance relay relays.
21:32 | - | Sirajgonj 225MW CCPP Unit-3 Syncronized with remarks:- ST
22:04 | - | Baroaulia 132/33kV S/S SASM HT Tripped showing O/C operated relays.
22:40 | 1:07 | Bhulta-Ghorasal 230 kV Ckt-2 Tripped from Bhulta 400/230kV end showing Distance Relay relays.
23:01 | - | Madunaghat-TKCL 132kV Ckt-1 Tripped from Madunaghat 132/33kV end showing REL-670 relays.
23:32 | - | Ashuganj- Bhulta 400kV ckt-1 tripped from Ashuganj end showing distance relay.
- | 23:45 | Sikalbaha-TKCL 132kV Ckt-1 is restored.
23:53 | 0:12 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Distance relays.
0:11 | 0:47 | BSRM-Cumilla(N) 230 kV Ckt-1 Tripped from BSRM 230/33kV end showing Distance trip relays. and from Cumilla(N) 230/132/33kV
end showing Secondary Distance Protection B,C Phase. V-Fail. Auto Reclosed Relay 1 & 3 Pole. relays.
0:20 | 2:12 | Bhulta-Rampura 230 kV Ckt-1 Tripped from Bhulta 400/230kV end showing Distance Relay relays. and from Rampura 230/132kV
end showing #Distance (Primary) 21P C N Z1 AIDED Trip #Auto Reclose 79 Alarms 1 #Distance (Backup) 21B Z1 CN Trip relays
Due to Due to heavy thunderstorm & rainfall.
0:26 | - | Maniknagar-Matuail 132kV Ckt-1 Tripped from Matuail 132/33kV end showing Over current Relay (SEL-551) & Protection and
Automation (SEL-311C) relays Due to Over Current & Earth fault
0:46 | 1:02 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing DIR O/C & E/F relay. relays Due to PBS Norsingdi feeder phase B&C E/F |  |  |  |  | 45.0MW load interrup.
1:43 | 2:11 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Optimho: Z1, CN. relays Due to Storm. |  |  |  |  | 90.0MW load interrup. Haripur 230/132kV end
1:43 | 2:11 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Z1 & CN relays Due to Unknown. |  |  |  |  | 80.0MW load interrup. Haripur 230/132kV end
2:06 | 2:30 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-1 Tripped showing Zone-1 trip, Y phase,
B phase trip, protection lockout relays.
2:49 | 3:20 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Baroirhat 132/33kV end showing Distance Trip Trip Relay K31,34& k34X relays.
3:45 | - | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
3:57 | - | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
4:33 | - | Rampur 230/132/33 S/S Halishahar-1 Tripped showing Distance Protection-REL670 relays Due to Thundering and Raining
5:37 | - | Coxsbazar 132/33kV S/S Main Bus Project Work S/D Due to Conductor connection in mainbus |  |  |  |  | 120.0MW load interrup.
5:52 | - | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Tower no-2 Replacement work on Amin Bazar Ckt-1.
6:06 | - | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to From Sonargaon Grid SS end CB
Open Instructions to NLDC.
6:06 | - | Haripur-Sonargaon 132kV Ckt-2 Scheduled S/D from Sonargaon 132/33kV end Due to From Sonargaon Grid SS end CB
Open Instructions to NLDC.
6:14 | - | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to High temperature maintenance.
- | 6:31 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
6:33 | 6:41 | Bogura(New)-Naogaon 132 kV Ckt-1 Project Work S/D from Bogura 230/132kV end Due to Project Work
6:33 | 6:56 | Bogura(New)-Naogaon 132 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to Project Work
6:42 | - | Naogaon-Niyamatpur 132kV Ckt-1 Scheduled S/D from Niamatpur 132/33kV end Due to ALDC,Bogura এর নির্দেশক্রমে
Naogaon Ckt-1 এর CB Open করা হলো।
6:49 | - | Adani Power Jharkhand Ltd. Unit-2 was sync.
7:00 | - | Minimum Generation: 11188 MW.
7:02 | - | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to Maintenance work at 33 kv CT connector (R&YPhase). |  |  |  |  | 20.0MW load interrup.
7:02 | - | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Maintenance work at 33 kv CT connector(R&Y Phase). |  |  |  |  | 20.0MW load interrup.
7:14 | - | Baroirhat-Hathazari 132 kV Ckt-1 Project Work S/D from Baroirhat 132/33kV end.
7:15 | - | Baroirhat-Hathazari 132 kV Ckt-2 Project Work S/D from Baroirhat 132/33kV end.
7:19 | 7:48 | Natore-Rajshahi 132kV Ckt-1 Tripped from Rajshahi 132/33kV end showing Distance Trip, A/R Block. relays Due to Distance
Trip, A/R Block.
21:12 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Tripped showing
lockout relay relays Due to CT of 33kV was damage
06:02 |  | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to
33 kV Bus coupler rearrange
06:03 |  | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to
33 kV Bus coupler rearrange
07:00 |  | Minimum generation 12387 MW
07:02 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
33kV Underground Cable Replace
07:11 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
33kV Underground Cable Replace
07:17 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to
33kV Busbar Maintenance
07:18 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to
33kV Busbar Maintenance
07:40 |  | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
Maintenance Work
07:40 |  | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
Maintenance Work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4047750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 78 | 1744863 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 403 | 9676800
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10287000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 91 | 1289280
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 278 | 7226851 | Meghna Bus section Over Load
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 65 | 1243550 | High Voltage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 970588 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 91003 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 67 | 955824
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 295 | 7516194 | Frequency Control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 1223280 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 601200 | Tripped
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1269600
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 671604
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 41 | 659578 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 22 | 797520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 698500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 709400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 296304 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 3171491 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 129 | 1716336 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 890880
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 50 | 655680 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1949760
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 186366
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 400 | 11416363 | Meghna Bus section Over Load
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 350 | 9353182 | On test.
| Dhaka area Total |  |  |  | 5332 | 3855 | 81316747
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 117 | 2600000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 212958
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 73710
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 215040 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 675640 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 212 | 4886949
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 470873
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 889632 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1001489 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired from 17/04/2024
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 61 | 1088640 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 7 | 142560 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 435840
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 785280 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 13320
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 381382 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 669513
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 553670
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 1062720 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 1035000 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 61 | 871490 | Bad Weather
60 | SS Power I |  | SS Power | 2*612 | 1224 | 265 | 6507272 | Madunaghat Transformer Over Load
| Cox's Bazar Wind |  | IPP | 66 | 60 | 37 | 691200 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 776 | 12960000 | Unit-2 On test
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 310709
| Chattogram area Total |  |  |  | 4404 | 2081 | 38534887
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 5070000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7016200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6990000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 7474200 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 733896 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 42 | 1014240 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 886545 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1058786
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 5 | 143854 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 767296 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 90 | 2677920 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 106 | 2578560
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 621000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 785251
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 245750 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1696320
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 63 | 1045800 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 33 | 730080
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1367040 | Engine problem
| Cumilla Area Total |  |  |  | 2929 | 1827 | 42902738
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 97 | 2926080 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14450
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 104 | 1771200 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1536000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 261840
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 389280 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 315 | 6898850
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 967000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 679920 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2406845 | ST under maint
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1243800
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 37 | 877392 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 162624 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1392768
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 206 | 5046850 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 401000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 368112
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7178500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 8708000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8442300 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1576 | 37875111
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 875 | 19242909
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 29 | 310560 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 49 | 625792 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 8606304 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 1306080 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 537120
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 307 | 7389091
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1670 | 38017856
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 1030368
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 218110 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2986000 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1160 | 26165000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5077773
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 445200 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 230 | 4974500
| Barisal Area Total |  |  |  | 2235 | 1815 | 40896951
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1170000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 907707 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 103314 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 449131 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 620420
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 167 | 4321800 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 204 | 4915327
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 5 | 164145 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8972509
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 446762 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 263034
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 33077
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 706864 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1376256
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1394592 | Engine problem
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32160
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 436 | 18970909 | Machine problem
| Rajshahi Area Total |  |  |  | 3431 | 1719 | 44848007
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1676072
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5559000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 85 | 1366800 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 52266
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1420608
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 236692
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1236690
| Rangpur Area Total |  |  |  | 950 | 502 | 11548128
| Total |  |  |  | 25903 | 15360 | 342839275
| Eastern Grid Total |  |  |  | 15588 | 9654 | 207528333
| Western Grid Total |  |  |  | 10315 | 5706 | 135310942
| National Grid Total |  |  |  | 25903 | 15360 | 342839275
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-02
| (a) ENTIRE EASTERN GRID : |  | 9424.48 | MW | (b) ENTIRE WESTERN GRID : |  | 5098.2 | MW
| i) Dhaka area |  | 5321.48 | MW | i) Khulna area |  | 1937.9 | MW
| ii) Chittagong area |  | 1344 | MW | ii) Rajshahi area |  | 1760.8 | MW
| iii) Comilla area |  | 1087 | MW | iii) Barisal area |  | 467.5 | MW
| iv) Mymensingh area |  | 1173 | MW | iv) Rangpur area |  | 932 | MW
| v) Sylhet area |  | 499 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14522.68 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 28 | 00:00 | Kalurghat | 34 | 09:00 | Narail | 67 | 00:00 | Shariatpur | 97 | 00:00
2 | AKSML | 13 | 13:00 | Chowmuhani | 252 | 21:00 | Kamrangirchar | 58.2 | 13:00 | Narinda | 82 | 13:00 | Sherpur | 162 | 21:00
3 | Aftabnagar | 46 | 00:00 | Chuadanga | 121 | 02:00 | Kaptai | N/A | N/A | Narshingdi | 167 | 19:30 | Shikalbaha | 26 | 18:30
4 | Agargaon | 127 | 12:00 | Coxsbazar | 135 | 18:30 | Kazla | 116 | 13:00 | Natore | 180 | 21:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 88 | 16:00 | Cumilla(N) | 186 | 05:00 | Keranigonj | 91 | 23:00 | Nawabganj | 58.3 | 23:00 | Shitalakhya | 110 | 13:00
6 | Amnura | 97 | 23:00 | Cumilla(S) | 183 | 15:00 | Khagrachori | 30 | 06:00 | Netrakona | 104 | 22:00 | Sholosohor | 47 | 16:00
7 | Ashuganj | 85 | 06:00 | Daudkandi | 154 | 18:30 | Khulna | 96 | 00:00 | New | 56.5 | 16:00 | Shyampur | 172 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 12:00 | Khulshi | 195 | 21:00 | Niamatpur | 123 | 19:30 | Siddhirganj | 118 | 15:00
9 | BSRM | 158 | 01:00 | Dhamrai | 134 | 18:30 | Kishoreganj | 148 | 19:30 | Noapara | 52 | 20:00 | Sirajganj | 130 | 19:30
10 | Bagerhat | 101 | 02:00 | Dhanmondi | 183 | 12:00 | Kodda | 275 | 21:00 | PHP | 9 | 18:00 | Sonargaon | 94 | 09:00
11 | Bakulia | 104 | 21:00 | Dohazari | 102 | 20:00 | Kulaura | 42 | 00:00 | Pabna | 126 | 20:00 | Sreemongol | 67 | 03:00
12 | Banani | 69.8 | 13:00 | Faridpur | 188 | 23:00 | Kurigram | 60 | 18:00 | Palashbari | 131 | 21:00 | Sreepur | 60 | 08:00
13 | Bangabhaban | 19 | 10:00 | Fatullah | 72 | 15:00 | Kushtia | 158 | 19:30 | Panchagarh | 56 | 19:00 | Srinagar | 54.5 | 23:00
14 | Barapukuria | 78 | 13:00 | Fenchuganj | 39 | 03:00 | Lalbag | 98 | 13:00 | Patuakhali | 100.5 | 23:00 | Sunamganj | 54 | 04:00
15 | Barguna | 24 | 22:00 | Feni | 126 | 20:00 | Lalmonirhat | 55 | 18:00 | Payra | 26 | 00:00 | Sylhet | 36 | 18:30
16 | Barishal | 127 | 23:00 | GPH | 79 | 11:00 | MI_Cement | 11.5 | 21:00 | Postogola | 66 | 23:00 | Sylhet-132 | 118 | 14:00
17 | Barishal-230 | 116 | 23:00 | Ghatail | 60 | 00:00 | Madanganj | 31 | 23:00 | Purbachal | 16 | 15:00 | TK | 30 | 20:00
18 | Baroaulia | 68 | 12:00 | Ghorashal | 81 | 11:00 | Madaripur | 128 | 23:00 | Purbasadipur | 143 | 13:00 | Tangail | 226 | 00:00
19 | Baroirhat | 60 | 20:00 | Goalpara | 38 | 00:00 | Madartek | 102.31 | 23:00 | Rahim | 33 | 09:00 | Thakurgaon | 102 | 21:00
20 | Bashundhara | 212 | 15:00 | Gollamari | 84 | 00:00 | Madunaghat | 49 | 00:00 | Rajbari | 86 | 00:00 | Tongi | 153 | 11:00
21 | BashundharaCement | 12 | 11:00 | Gopalganj | 122.4 | 00:00 | Magura | 75 | 23:00 | Rajendrapur | 112 | 21:00 | Ullahpara | 31 | 20:00
22 | Beanibazar | 53 | 21:00 | Gulshan | 160 | 13:00 | Mahasthangarh | 92 | 19:30 | Rajshahi | 178 | 23:00 | Ullon | 69 | 23:00
23 | Benapole | 82 | 20:00 | Halishahar | 87 | 12:00 | Manikganj | 145 | 21:00 | Rajshahi-230 | 57 | 00:00 | Uttara | 112 | 15:00
24 | Bhaluka | 108 | 19:30 | HaripurSBU | 162 | 09:00 | Maniknagar | 90 | 13:00 | Ramganj | 118 | 22:00 | UttaraNew | 40 | 23:00
25 | Bhandaria | 57 | 23:00 | Hasnabad | 104 | 19:00 | Matarbari | 40 | 21:00 | Rampur | 32 | 21:00 | Zigatola | 100 | 13:00
26 | Bhangura | 53 | 21:00 | Hathazari | 69 | 23:00 | Matuail | 78 | 11:00 | Rangamati | 13 | 05:00
27 | Bheramara(GK) | 73 | 19:30 | Ishurdi | 85 | 19:30 | Millgate | 130 | 12:00 | Rangpur | 144 | 13:00
28 | Bhulta | 219 | 16:00 | Jaldhaka | 85 | 20:00 | Mirpur | 165 | 23:00 | Ruppur | 7.2 | 15:00
29 | Bog-Sherpur | 78 | 19:30 | Jamalpur | 148 | 00:00 | Mirsorai | 9 | 21:00 | SSM | 3 | 01:00
30 | Bogura | 192 | 22:00 | Jashore | 163 | 21:00 | Mirzapur | 46 | 19:00 | Saidpur | 114 | 19:00
31 | Borhanuddin | 85 | 02:00 | Jhenaidah | 150 | 23:00 | Mithapukur | 61 | 18:30 | Satkhira | 145 | 22:00
32 | Brahmanbaria | 180 | 21:00 | Joydebpur | 203 | 20:00 | Modern | 0 | 00:00 | Satmasjid | 128 | 16:00
33 | Cantonment | 186 | 00:00 | Joypurhat | 84 | 23:00 | Mogbazar | 153.6 | 16:00 | Savar | 222 | 09:00
34 | Chandpur | 81 | 23:00 | Juldah | 17 | 18:30 | Mongla | 40 | 11:00 | SevenRings | 17.54 | 20:00
35 | Chandraghona | 27 | 00:00 | KSRM | 34 | 08:00 | Motijheel | 61 | 13:00 | ShahCement | 27 | 05:00
36 | Chapai | 83 | 00:00 | Kabirpur | 274 | 20:00 | Munshiganj | 116 | 00:00 | Shahjadpur | 99 | 00:00
37 | Charsaidpur | 47 | 16:00 | Kachua | 93 | 22:00 | Mymensingh | 249 | 19:00 | Shahjibazar | 127 | 21:00
38 | Chauddagram | 80 | 05:00 | Kallyanpur | 135 | 23:00 | Naogaon | 161 | 22:00 | Shahmirpur | 58 | 19:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 394 | 07:00 | 386 | 10:00 | Kaliakoir | 374 | 19:00 | 358 | 10:00
| Ashuganj | 408 | 24:00 | 391 | 10:00 | Madunaghat_I | 398 | 20:00 | 393 | 10:00
| Bhulta | 399 | 04:00 | 386 | 10:00 | Meghnaghat | 392 | 7:00 | 385 | 11:00
| Bibiana | 398 | 21:00 | 389 | 10:00 | Payra | 413 | 09:00 | 405 | 23:00
| BIPTC | 406 | 02:00 | 390 | 17:00 | Rahanpur | 410 | 15:00 | 390 | 02:00
| Bogura | 407 | 16:00 | 389 | 07:00 | Rampal | 404 | 09:00 | 393 | 22:00
| Gopalganj | 401 | 06:00 | 393 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 04:00 | 217 | 10:00 | Hasnabad | 228 | 00:00 | 219 | 10:00
| AKSML | 227 | 19:30 | 217 | 06:00 | Hathazari | 228 | 21:00 | 220 | 10:00
| Aminbazar | 226 | 21:00 | 212 | 19:00 | Ishurdi | 227 | 21:00 | 220 | 05:00
| Ashuganj | 234 | 00:00 | 227 | 10:00 | Jhenaidah | 236 | 18:30 | 229 | 19:00
| Ashuganj-400 | 232 | 7:00 | 225 | 4:00 | Kaliakoir | 226 | 09:00 | 215 | 19:00
| Baghabari | 231 | 17:00 | 224 | 10:00 | Keranigonj | 227 | 18:00 | 216 | 10:00
| Barapukuria | 215 | 15:00 | 204 | 07:00 | Khulna(S) | 225 | 03:00 | 217 | 10:00
| Barapukuria-230 | 215 | 15:00 | 204 | 7:00 | Madunaghat_I | 229 | 07:00 | 218 | 19:00
| Barishal | 239 | 05:00 | 230 | 00:00 | Maniknagar | 227 | 20:00 | 221 | 10:00
| Bheramara | 234 | 00:00 | 226 | 19:00 | Meghnaghat | 228 | 21:00 | 218 | 10:00
| Bhulta | 229 | 04:00 | 219 | 10:00 | Meghnaghat-400 | 236 | 19:00 | 230 | 07:00
| Bibiana | 230 | 18:00 | 224 | 10:00 | Mirsorai | 230 | 10:00 | 216 | 8:00
| BIPTC | 236 | 18:30 | 226 | 19:00 | Rajshahi | 230 | 22:00 | 216 | 08:00
| Bogura | 222 | 16:00 | 211 | 07:00 | Rampal | 234 | 09:00 | 223 | 19:00
| Bogura-400 | 222 | 16:00 | 212 | 07:00 | Rampur | 229 | 06:00 | 220 | 19:00
| Borhanuddin | 241 | 04:00 | 235 | 09:00 | Rampura | N/A | N/A | N/A | N/A
| BSRM | 228 | 21:00 | 218 | 06:00 | Shikalbaha | 228 | 21:00 | 217 | 11:00
| Cumilla(N) | 230 | 21:00 | 221 | 10:00 | Shyampur | 223 | 18:00 | 218 | 02:00
| Fenchuganj | 234 | 17:00 | 228 | 11:00 | Siddhirganj | 229 | 22:00 | 219 | 10:00
| Ghorashal | 230 | 00:00 | 225 | 10:00 | Sirajgonj | 231 | 21:00 | 222 | 10:00
| Ghorashal-230 | 228 | 04:00 | 222 | 11:00 | Sreepur | 235 | 18:00 | 231 | 08:00
| GPH | 226 | 19:30 | 218 | 08:00 | Tongi | 228 | 00:00 | 27 | 04:00
| Haripur | 228 | 09:00 | 219 | 00:00 |  | 226 | 22:00 | 212 | 08:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 130 | 03:00 | 123 | 10:00 | Kushtia | 135 | 09:00 | 129 | 19:00
| Agargaon | 135 | 03:00 | 129 | 10:00 | Lalbag | 136 | 03:00 | 130 | 10:00
| Agrabad | 133 | 19:30 | 127 | 07:00 | Lalmonirhat | 125 | 15:00 | 114 | 07:00
| AKS | 130 | 18:00 | 126 | 05:00 | Madanganj | 133 | 20:00 | 124 | 10:00
| Aminbazar | 136 | 02:00 | 125 | 22:00 | Madaripur | 134 | 09:00 | 129 | 00:00
| Amnura | 136 | 18:30 | 120 | 00:00 | Madartek | 130 | 03:00 | 122 | 10:00
| Ashuganj | 137 | 01:00 | 135 | 10:00 | Madunaghat | 132 | 09:00 | 127 | 03:00
| Bagerhat | 135 | 09:00 | 119 | 13:00 | Magura | 137 | 09:00 | 126 | 19:00
| Bakulia | 135 | 04:00 | 130 | 01:00 | Mahasthangarh | 130 | 15:00 | 120 | 03:00
| Banani | 133 | 04:00 | 124 | 10:00 | Manikganj | 133 | 23:00 | 123 | 10:00
| Bangabhaban | 132 | 01:00 | 124 | 10:00 | Maniknagar | 132 | 00:00 | 124 | 10:00
| Barapukuria | 132 | 15:00 | 123 | 07:00 | Matarbari | 127 | 08:00 | 108 | 01:00
| Barguna | 138 | 12:00 | 124 | 23:00 | Matuail | 133.2 | 21:00 | 125 | 10:00
| Barishal | 136 | 05:00 | 120 | 23:00 | Millgate | 131 | 03:00 | 121 | 10:00
| Barishal-230 | 138 | 05:00 | 130 | 00:00 | Mirpur | 134 | 02:00 | 129 | 10:00
| Baroaulia | 133 | 18:00 | 127 | 08:00 | Mirzapur | 134 | 23:00 | 125 | 10:00
| Baroirhat | 130 | 17:00 | 120 | 05:00 | Mithapukur | 125 | 17:00 | 115 | 06:00
| Bashundhara | 133 | 02:00 | 120 | 10:00 | MI_Cement | 134 | 19:30 | 125 | 10:00
| BashundharaCement | 133 | 20:00 | 124 | 10:00 | Modern | 133 | 04:00 | 130 | 00:00
| Beanibazar | 132 | 09:00 | 127 | 00:00 | Mogbazar | 131 | 03:00 | 124 | 11:00
| Benapole | 134 | 09:00 | 122 | 19:00 | Mongla | 134 | 09:00 | 124 | 14:00
| Bhaluka | 124 | 00:00 | 118 | 10:00 | Motijheel | 132 | 01:00 | 124 | 10:00
| Bhandaria | 134 | 18:00 | 114 | 23:00 | Munshiganj | 133 | 19:30 | 124 | 10:00
| Bhangura | 133 | 18:30 | 129 | 07:00 | Mymensingh | 134 | 23:00 | 114 | 14:00
| Bheramara | 135 | 06:00 | 131 | 19:00 | Naogaon | 126 | 15:00 | 115 | 04:00
| Bheramara(GK) | 136 | 04:00 | 132 | 19:00 | Narail | 136 | 06:00 | 125 | 19:00
| Bhulta | 127 | 23:00 | 115 | 10:00 | Narinda | 132 | 00:00 | 124 | 10:00
| Bog-Sherpur | 131 | 15:00 | 122 | 07:00 | Narshingdi | 127 | 00:00 | 118 | 09:00
| Bogura | 133 | 15:00 | 116 | 19:00 | Natore | 130 | 07:00 | 123 | 19:00
| Bogura-230 | 132 | 16:00 | 123 | 07:00 | Nawabganj | 135 | 00:00 | 131 | 10:00
| Brahmanbaria | 127 | 00:00 | 124 | 10:00 | Netrakona | 120 | 00:00 | 114 | 15:00
| Cantonment | 135 | 04:00 | 128 | 10:00 | New | 130 | 06:00 | 123 | 10:00
| Chandpur | 132 | 09:00 | 113 | 06:00 | Niamatpur | 136 | 14:00 | 127 | 04:00
| Chandraghona | 133 | 14:00 | 127 | 05:00 | Noapara | 136 | 07:00 | 126 | 22:00
| Chapai | 133 | 16:00 | 124 | 00:00 | Pabna | 132 | 09:00 | 128 | 19:00
| Charsaidpur | 134 | 21:00 | 125 | 10:00 | Palashbari | 155 | 10:00 | 114 | 03:00
| Chauddagram | 132 | 09:00 | 119 | 01:00 | Panchagarh | 131 | 15:00 | 112 | 07:00
| Chhatak | 130 | 09:00 | 127 | 00:00 | Patuakhali | 134 | 12:00 | 126 | 23:00
| Chowmuhani | 127 | 18:00 | 111 | 02:00 | Payra | 136 | 18:30 | 132 | 01:00
| Chuadanga | 131 | 09:00 | 117 | 19:00 | PHP | 131 | 18:30 | 112 | 01:00
| Coxsbazar | 126 | 14:00 | 113 | 03:00 | Postogola | 134 | 21:00 | 127 | 10:00
| Cumilla(N) | 135 | 21:00 | 127 | 05:00 | Purbachal | 133 | 03:00 | 121 | 10:00
| Cumilla(S) | 136 | 21:00 | 124 | 14:00 | Purbasadipur | 126 | 16:00 | 112 | 07:00
| Daudkandi | 136 | 19:30 | 116 | 10:00 | Rahanpur | 138 | 16:00 | 132 | 00:00
| Dhaka | 133 | 03:00 | 125 | 10:00 | Rahim | 133 | 19:30 | 126 | 10:00
| Dhamrai | 132 | 00:00 | 124 | 10:00 | Rajbari | 132 | 08:00 | 127 | 00:00
| Dhanmondi | 133 | 00:00 | 124 | 10:00 | Rajendrapur | 136 | 18:30 | 126 | 11:00
| Dohazari | 132 | 04:00 | 125 | 03:00 | Rajshahi | 131 | 07:00 | 125 | 19:00
| Faridpur | 133 | 08:00 | 126 | 00:00 | Rajshahi-230 | 135 | 18:30 | 119 | 00:00
| Fatullah | 138 | 12:00 | 126 | 10:00 | Ramganj | 127 | 13:00 | 113 | 01:00
| Fenchuganj | 133 | 07:00 | 131 | 01:00 | Rampur | 131 | 00:00 | 127 | 08:00
| Feni | 129 | 18:00 | 115 | 01:00 | Rampura | 133 | 03:00 | 124 | 10:00
| Ghatail | 132 | 23:00 | 120 | 11:00 | Rangamati | 133 | 20:00 | 125 | 06:00
| Ghorashal | 137 | 18:30 | 130 | 10:00 | Rangpur | 127 | 16:00 | 116 | 07:00
| Goalpara | 140 | 09:00 | 127 | 22:00 | Ruppur | 136 | 09:00 | 132 | 18:00
| Gollamari | 139 | 09:00 | 130 | 13:00 | Saidpur | 127 | 16:00 | 115 | 07:00
| Gopalganj | 135 | 09:00 | 127 | 22:00 | Satkhira | 134 | 09:00 | 121 | 22:00
| Gopalganj-400 | 134 | 06:00 | 130 | 00:00 | Satmasjid | 135 | 04:00 | 125 | 11:00
| Gulshan | 133 | 03:00 | 124 | 10:00 | Savar | 134 | 19:30 | 129 | 08:00
| Halishahar | 134 | 19:30 | 128 | 10:00 | SevenRings | 137 | 18:30 | 130 | 10:00
| Haripur | 133 | 00:00 | 126 | 10:00 | ShahCement | 134 | 21:00 | 125 | 10:00
| HaripurSBU | 133 | 19:30 | 126 | 10:00 | Shahjadpur | 138 | 23:00 | 132 | 10:00
| Hasnabad | 133 | 01:00 | 127 | 10:00 | Shahjibazar | 125 | 00:00 | 123 | 15:00
| Hathazari | 134 | 07:00 | 130 | 04:00 | Shahmirpur | 135 | 04:00 | 130 | 10:00
| Ishurdi | 137 | 18:30 | 132 | 00:00 | Shariatpur | 133 | 08:00 | 126 | 00:00
| Jaldhaka | 125 | 16:00 | 113 | 07:00 | Sherpur | 129 | 23:00 | 112 | 11:00
| Jamalpur | 132 | 23:00 | 117 | 13:00 | Shikalbaha | 124 | 19:30 | 119 | 10:00
| Jashore | 134 | 09:00 | 124 | 19:00 | Shikalbaha-230 | 135 | 19:00 | 132 | 01:00
| Jhenaidah | 137 | 05:00 | 128 | 19:00 | Shitalakhya | 134 | 18:30 | 125 | 10:00
| Jhenaidah-230 | 138 | 09:00 | 129 | 19:00 | Sholosohor | 133 | 20:00 | 127 | 07:00
| Joydebpur | 137 | 10:00 | 129 | 09:00 | Shyampur | 134 | 04:00 | 125 | 10:00
| Joypurhat | 123 | 15:00 | 109 | 05:00 | Shyampur-230 | 133 | 21:00 | 125 | 10:00
| Juldah | 135 | 18:00 | 131 | 02:00 | Siddhirganj | 133 | 20:00 | 126 | 10:00
| Kabirpur | 138 | 18:00 | 117 | 10:00 | Sirajganj | 129 | 00:00 | 124 | 10:00
| Kachua | 131 | 00:00 | 118 | 01:00 | Sonargaon | 135 | 19:30 | 122 | 10:00
| Kaliakoir | 138 | 18:00 | 130 | 10:00 | Sreemongol | 127 | 00:00 | 124 | 19:00
| Kallyanpur | 128 | 06:00 | 124 | 11:00 | Sreepur | 129 | 00:00 | 123 | 10:00
| Kalurghat | 134 | 19:30 | 127 | 08:00 | Srinagar | 136 | 03:00 | 130 | 10:00
| Kamrangirchar | 138 | 06:00 | 122 | 12:00 | SSM | 136 | 18:00 | 130 | 07:00
| Kaptai | 135 | 18:00 | 130 | 6:00 | Sunamganj | 129 | 18:00 | 124 | 04:00
| Kazla | 132 | 05:00 | 124 | 11:00 | Sylhet | 132 | 06:00 | 129 | 00:00
| Keranigonj | 137 | 03:00 | 131 | 10:00 | Sylhet-132 | 131 | 07:00 | 129 | 01:00
| Khagrachori | 133 | 18:00 | 125 | 06:00 | Tangail | 139 | 02:00 | 122 | 10:00
| Khulna | 137 | 07:00 | 128 | 13:00 | Thakurgaon | 129 | 19:30 | 111 | 07:00
| Khulna(S) | 139 | 07:00 | 130 | 13:00 | TK | 132 | 19:30 | 127 | 07:00
| Khulshi | 131 | 18:00 | 126 | 08:00 | Tongi | 133 | 07:00 | 125 | 09:00
| Kishoreganj | 131 | 13:00 | 122 | 10:00 | Ullahpara | 133 | 17:00 | 128 | 07:00
| Kodda | 136 | 18:00 | 123 | 11:00 | Ullon | 130 | 04:00 | 123 | 10:00
| KSRM | 134 | 19:30 | 128 | 05:00 | Uttara | 134 | 04:00 | 127 | 01:00
| Kulaura | 131 | 08:00 | 130 | 00:00 | UttaraNew | 134 | 04:00 | 128 | 01:00
| Kurigram | 128 | 15:00 | 112 | 07:00 | Zigatola | 137 | 06:00 | 131 | 10:00

## L-Curve
Date | 2024-05-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 500 | 8803 | 5380 | 14183 |  |  |  | QF-LDC-11
0:30 | 595 | 8520.5 | 5730 | 14250.5 | Date: | 2024-05-02
1:00 | 690 | 8238 | 6080 | 14318
1:30 | 685 | 8160 | 6054 | 14214
2:00 | 680 | 8082 | 6028 | 14110
2:30 | 686 | 8025.5 | 6159 | 14184.5 | [5 empty] | Gen. at Eve. Peak | 15360 | 15360 MW (19:30 )
3:00 | 692 | 7969 | 6290 | 14259 | [6 empty] | 19:30
3:30 | 706 | 7918 | 6173.5 | 14091.5 | [5 empty] | Gen. at Day Peak | 14149 | 14149 MW (11:00 )
4:00 | 720 | 7867 | 6057 | 13924 | [6 empty] | 11:00
4:30 | 705 | 7946.5 | 5968.5 | 13915 | [5 empty] | Highest Generation | 15360
5:00 | 690 | 8026 | 5880 | 13906 | [6 empty] | 19:30
5:30 | 660 | 7944.5 | 5742.5 | 13687
6:00 | 630 | 7863 | 5605 | 13468
6:30 | 605 | 7806 | 5577 | 13383
7:00 | 580 | 7749 | 5549 | 13298
7:30 | 600 | 7732.5 | 5593 | 13325.5
8:00 | 620 | 7716 | 5637 | 13353
8:30 | 610 | 7824.5 | 5665.5 | 13490
9:00 | 600 | 7933 | 5694 | 13627
9:30 | 620 | 7980.5 | 5751 | 13731.5
10:00 | 640 | 8028 | 5808 | 13836
10:30 | 645 | 8183.5 | 5809 | 13992.5
11:00 | 650 | 8339 | 5810 | 14149
11:30 | 650 | 8606 | 5496 | 14102
12:00 | 650 | 8873 | 5182 | 14055
12:30 | 680 | 9003.5 | 5230 | 14233.5
13:00 | 710 | 9134 | 5278 | 14412
13:30 | 725 | 9132 | 5292.5 | 14424.5
14:00 | 740 | 9130 | 5307 | 14437
14:30 | 752 | 9096 | 5294.5 | 14390.5
15:00 | 764 | 9062 | 5282 | 14344
15:30 | 777 | 8981 | 5294 | 14275
16:00 | 790 | 8900 | 5306 | 14206
16:30 | 793 | 8850 | 5255.5 | 14105.5
17:00 | 796 | 8800 | 5205 | 14005
17:30 | 843 | 8850 | 5043 | 13893
18:00 | 890 | 8900 | 4881 | 13781
18:30 | 862 | 9328.5 | 5155 | 14483.5
19:00 | 834 | 9757 | 5429 | 15186
19:30 | 690 | 9654 | 5706 | 15360
20:00 | 570 | 9816 | 5436 | 15252 |  |  |  | Executive Engineer
20:30 | 550 | 9778.5 | 5444 | 15222.5 |  |  |  | Network Operation Division
21:00 | 530 | 9741 | 5452 | 15193
21:30 | 520 | 9681.5 | 5464 | 15145.5
22:00 | 510 | 9622 | 5476 | 15098 |  |  |  |  | Page 6 of 7
22:30 | 510 | 9489.5 | 5457 | 14946.5
23:00 | 510 | 9357 | 5438 | 14795
23:30 | 505 | 9080 | 5409 | 14489
24:00 | 500 | 8803 | 5380 | 14183
15360 MW (19:30 )
14149 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-02 |  | Energy |  | 342839275
[14 empty] | Date: | 2024-05-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4550 | 645 | 3052 | 0 | 1825 | 3603 | 30 | 0 | 376 | 86 | 0 | 16 | 1019
0:30 | 4523 | 644.5 | 3160 | 0 | 1589.5 | 3796.5 | 27.5 | 0 | 387 | 106 | 0 | 16.5 | 1121.655 |  |  | Date: | 43952
1:00 | 4496 | 644 | 3268 | 0 | 1354 | 3990 | 25 | 0 | 398 | 126 | 0 | 17 | 1224.31
1:30 | 4419.5 | 642.5 | 3272 | 0 | 1340.5 | 3977 | 25 | 0 | 392 | 127 | 0 | 18.5 | 1228.13 | [9 empty] | Total Energy | 342.8393 | 342.8393 | Total Energy Gen 342.839 MKWHr Energy Not Served 15.955 MKWHr Energy Requirement 358.794 MKWHr
2:00 | 4343 | 641 | 3276 | 0 | 1327 | 3964 | 25 | 0 | 386 | 128 | 0 | 20 | 1231.95 | [9 empty] | Energy not Served | 15.9552 | 15.9552
2:30 | 4362.5 | 783.5 | 3195.5 | 0 | 1337.5 | 3968.5 | 25 | 0 | 368 | 125 | 0 | 19 | 1017.5525 | [9 empty] | Energy Requirement | 358.7944 | 358.7944
3:00 | 4382 | 926 | 3115 | 0 | 1348 | 3973 | 25 | 0 | 350 | 122 | 0 | 18 | 803.155
3:30 | 4422.5 | 925.5 | 3002.5 | 0 | 1344.5 | 3882 | 25 | 0 | 340.5 | 120 | 0 | 29 | 676.6175 | [8 empty] | Shortage
4:00 | 4463 | 925 | 2890 | 0 | 1341 | 3791 | 25 | 0 | 331 | 118 | 0 | 40 | 550.08
4:30 | 4568.5 | 925 | 2872.5 | 0 | 1343 | 3713 | 25 | 0 | 312 | 116 | 0 | 40 | 487.05
5:00 | 4674 | 925 | 2855 | 0 | 1345 | 3635 | 25 | 0 | 293 | 114 | 0 | 40 | 424.02
5:30 | 4696 | 925.5 | 2847.5 | 0 | 1211.5 | 3535.5 | 25 | 0 | 291 | 113 | 8 | 34 | 418.29
6:00 | 4718 | 926 | 2840 | 0 | 1078 | 3436 | 25 | 0 | 289 | 112 | 16 | 28 | 412.56
6:30 | 4709 | 925.5 | 2840.5 | 0 | 1017 | 3410.5 | 25 | 0 | 289.5 | 111 | 33 | 22 | 493.78 | [7 empty] | Coal
7:00 | 4700 | 925 | 2841 | 0 | 956 | 3385 | 25 | 0 | 290 | 110 | 50 | 16 | 575
7:30 | 4671 | 925.5 | 2836 | 0 | 991.5 | 3377.5 | 25 | 0 | 288.5 | 107 | 78 | 25.5 | 525 | [6 empty] | Oil
8:00 | 4642 | 926 | 2831 | 0 | 1027 | 3370 | 25 | 0 | 287 | 104 | 106 | 35 | 475
8:30 | 4611 | 926 | 2786 | 0 | 1109 | 3394 | 27.5 | 0 | 294.5 | 107 | 193 | 42 | 511
9:00 | 4580 | 926 | 2741 | 0 | 1191 | 3418 | 30 | 0 | 302 | 110 | 280 | 49 | 547
9:30 | 4647.5 | 925.5 | 2778 | 0 | 1253.5 | 3362 | 30 | 0 | 277.5 | 111 | 300 | 46.5 | 543
10:00 | 4715 | 925 | 2815 | 0 | 1316 | 3306 | 30 | 0 | 253 | 112 | 320 | 44 | 539
10:30 | 4689 | 925 | 2865 | 0 | 1386 | 3318 | 30 | 0 | 255 | 118 | 363 | 43.5 | 532.5
11:00 | 4663 | 925 | 2915 | 0 | 1456 | 3330 | 30 | 0 | 257 | 124 | 406 | 43 | 526
11:30 | 4667.5 | 925 | 2988 | 0 | 1597 | 3036.5 | 30 | 0 | 240 | 122 | 449.5 | 46.5 | 618.5
12:00 | 4672 | 925 | 3061 | 0 | 1738 | 2743 | 30 | 0 | 223 | 120 | 493 | 50 | 711
12:30 | 4654.5 | 925.5 | 3036 | 0 | 1840 | 2893.5 | 30 | 0 | 236.5 | 125 | 450 | 42.5 | 743.7075
13:00 | 4637 | 926 | 3011 | 0 | 1942 | 3044 | 30 | 0 | 250 | 130 | 407 | 35 | 776.415
13:30 | 4637 | 926 | 3011 | 0 | 1942 | 3044 | 30 | 0 | 250 | 130 | 407 | 35 | 776.415
14:00 | 4637 | 926 | 3011 | 0 | 1942 | 3044 | 30 | 0 | 250 | 130 | 407 | 35 | 776.415
14:30 | 4608.5 | 926 | 2993.5 | 0 | 1989 | 3034 | 30 | 0 | 278 | 134 | 346.5 | 38.5 | 882.8975
15:00 | 4580 | 926 | 2976 | 0 | 2036 | 3024 | 30 | 0 | 306 | 138 | 286 | 42 | 989.38
15:30 | 4569.5 | 925.5 | 2935 | 0 | 2045 | 3041 | 30 | 0 | 303 | 135 | 246.5 | 44.5 | 1007.525
16:00 | 4559 | 925 | 2894 | 0 | 2054 | 3058 | 30 | 0 | 300 | 132 | 207 | 47 | 1025.67
16:30 | 4528 | 925.5 | 2770 | 0 | 2080 | 3147 | 30 | 0 | 310.5 | 127 | 146 | 41.5 | 940.1975
17:00 | 4497 | 926 | 2646 | 0 | 2106 | 3236 | 30 | 0 | 321 | 122 | 85 | 36 | 854.725
17:30 | 4460.5 | 926 | 2576 | 0 | 2238.5 | 3123.5 | 30 | 0 | 350 | 109 | 49.5 | 30 | 675.185
18:00 | 4424 | 926 | 2506 | 0 | 2371 | 3011 | 30 | 0 | 379 | 96 | 14 | 24 | 495.645
18:30 | 4517 | 926 | 2675.5 | 0 | 2622.5 | 3111.5 | 30 | 0 | 464 | 106 | 7 | 24 | 493.2575
19:00 | 4610 | 926 | 2845 | 0 | 2874 | 3212 | 30 | 0 | 549 | 116 | 0 | 24 | 490.87
19:30 | 4540 | 875 | 2810 | 0 | 2868 | 3476 | 30 | 0 | 618 | 106 | 0 | 37 | 435.48
20:00 | 4629 | 639 | 2827 | 0 | 2939 | 3405 | 30 | 0 | 646 | 110 | 0 | 27 | 380.09
20:30 | 4609.5 | 641 | 2901 | 0 | 2893 | 3423 | 30 | 0 | 644 | 58 | 0 | 23 | 336.6375
21:00 | 4590 | 643 | 2975 | 0 | 2847 | 3441 | 30 | 0 | 642 | 6 | 0 | 19 | 293.185
21:30 | 4598 | 644 | 2967 | 0 | 2761 | 3468 | 30 | 0 | 632.5 | 32 | 0 | 13 | 305.0925
22:00 | 4606 | 645 | 2959 | 0 | 2675 | 3495 | 30 | 0 | 623 | 58 | 0 | 7 | 317
22:30 | 4558.5 | 644.5 | 3040.5 | 0 | 2555.5 | 3520 | 30 | 0 | 521.5 | 72 | 0 | 4 | 495
23:00 | 4511 | 644 | 3122 | 0 | 2436 | 3545 | 30 | 0 | 420 | 86 | 0 | 1 | 673
23:30 | 4530.5 | 644.5 | 3087 | 0 | 2130.5 | 3574 | 30 | 0 | 398 | 86 | 0 | 8.5 | 846 |  |  | Max Temp. in Dhaka |  | 38.3°C
24:00 | 4550 | 645 | 3052 | 0 | 1825 | 3603 | 30 | 0 | 376 | 86 | 0 | 16 | 1019
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 342.839 MKWHr Energy Not Served 15.955 MKWHr Energy Requirement 358.794 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | [16 empty] | 263640
2 | Karnaphuli Hydro PP Unit-4 & 5 | [10 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 412000
3 | Chattogram TPP-1 | 110 | 110 | 105 | 110 | 110 | 113 | 111 | 115 | 116 | 115 | 114 | 114 | 113 | 114 | 115 | 120 | 115 | 117 |  | 120 | 117 | 120 | 117 | 115 | 112 | 114 | 2600000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 0 | [5 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 11 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 212958
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 3 | 13 | 13 |  | 19 | 6 | 5 | 9 | 3 | 1 | 0 | [8 empty] | 73710
6 | Sikalbaha 225MW CCPP (Gas) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 212 | 212 | 212 | 212 | 212 | 211 | 211 |  | 211 | 212 | 212 | 212 | 212 | 212 | 211 | 4886949
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 40 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1001489
12 | Hathazari 100 MW peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 35 | 35 | 40 | 40 | 40 | 40 |  | 40 | 48 | 48 | 48 | 48 | 48 | 48 | 889632
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 470873
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 35 | 35 | 35 | 33 | 34 | 34 | 34 | 34 |  | 34 | 34 | 15 | 14 | 14 | 14 | 26 | 767296
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 318 | 319 | 322 | 326 | 322 | 322 | 322 | 317 | 309 | 312 | 315 | 310 | 307 | 301 | 298 | 298 | 298 | 300 |  | 300 | 295 | 310 | 313 | 318 | 325 | 331 | 7516194
18 | Kodda 300 MW PP Unit-2 (Summit) | 80 | 80 | 80 | 80 | 80 | 0 |  |  |  |  | 15 | 95 | 158 | 228 | 223 | 225 | 228 | 225 |  | 265 | 275 | 275 | 180 | 178 | 180 | 180 | 3171491
19 | Ashuganj 195 MW PP (APSCL-United) | 157 | 157 | 157 | 102 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 16 | 16 | 45 | 63 | 886545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4047750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 272 | 275 | 274 | 273 | 275 | 270 | 271 | 270 | 269 | 270 | 272 | 270 | 274 | 276 | 270 | 270 | 265 | 265 |  | 270 | 265 | 265 | 265 | 265 | 267 | 273 | 6507272
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 28 | 31 | 29 | 30 | 30 | 31 | 32 | 32 | 33 |  | 35 | 37 | 37 | 38 | 38 | 38 | 37 | 733896
33 | Ashuganj 225 MW CCPP | 200 | 201 | 205 | 216 | 214 | 213 | 213 | 205 | 213 | 207 | 206 | 206 | 205 | 197 | 205 | 205 | 206 | 207 |  | 211 | 213 | 214 | 218 | 215 | 214 | 216 | 5070000
34 | Ashuganj 450 MW CCPP(South) | 310 | 280 | 270 | 270 | 270 | 285 | 315 | 305 | 290 | 315 | 290 | 310 | 295 | 305 | 290 | 280 | 270 | 270 |  | 280 | 280 | 300 | 280 | 280 | 250 | 265 | 6990000
| Ashuganj 450 MW CCPP(North) | 24 | 26 | 75 | 170 | 345 | 345 | 350 | 345 | 356 | 330 | 335 | 325 | 315 | 320 | 315 | 315 | 310 | 310 |  | 320 | 305 | 320 | 300 | 300 | 290 | 285 | 7016200
| Ashuganj 420 MW CCPP(East) | 290 | 245 | 270 | 285 | 330 | 340 | 336 | 290 | 290 | 315 | 345 | 365 | 365 | 340 | 310 | 310 | 310 | 310 |  | 340 | 300 | 300 | 300 | 270 | 230 | 260 | 7474200
35 | Ashuganj 55 MW PP (Precision) | 44 | 44 | 44 | 44 | 46 | 42 | 42 | 42 | 42 | 43 | 41 | 38 | 37 | 38 | 38 | 37 | 36 | 36 |  | 42 | 42 | 43 | 49 | 49 | 50 | 50 | 1014240
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 402 | 403 | 403 | 403 | 401 | 403 | 403 | 405 | 403 | 405 | 403 | 396 | 400 | 398 | 394 | 390 | 399 | 399 |  | 400 | 403 | 403 | 406 | 405 | 400 | 402 | 9676800
| Meghnaghat Unique power | 555 | 555 | 500 | 500 | 500 | 500 | 505 | 504 | 503 | 450 | 450 | 550 | 500 | 500 | 471 | 420 | 352 | 348 |  | 405 | 400 | 400 | 506 | 505 | 505 | 450 | 11416363
| Summit Meghanghat-2 589 MW(Gas) | 500 | 500 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 450 | 450 | 450 | 450 | 420 | 300 | 300 |  | 350 | 350 | 350 | 350 | 350 | 450 | 450 | 9353182
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 370 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10287000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 179 | 180 | 192 | 193 | 193 | 193 | 154 | 151 | 109 | 109 | 108 | 96 | 92 | 88 | 89 | 89 | 91 | 91 |  | 94 | 97 | 96 | 100 | 101 | 102 | 76 | 2926080
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 5 | 11 | 21 | 10 | 40 | 45 | 42 | 17 | 31 | 19 | 8 | 1 | [8 empty] | 261840
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 43 | 40 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 42 | 41 | 41 | 43 | 43 | 43 | 967000
45 | Fenchugonj CCPP Phase-2 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 |  | 28 | 28 | 28 | 28 | 29 | 29 | 30 | 679920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 56 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 60 |  | 56 | 62 | 59 | 62 | 61 | 59 | 59 | 1392768
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 201 | 198 | 197 | 197 | 197 | 196 | 197 | 196 | 195 | 200 | 202 | 201 | 201 | 201 | 202 | 202 | 205 | 206 |  | 206 | 206 | 206 | 207 | 207 | 207 | 207 | 5046850
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 18 | 18 | 17 | 401000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 162624
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1243800
56 | Shahjahanulla 25 MW PP | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 368112
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 310 | 290 | 265 | 290 | 275 | 295 | 285 | 290 | 265 | 300 | 300 | 290 | 310 | 310 | 310 | 280 | 270 |  | 295 | 285 | 270 | 310 | 280 | 310 | 305 | 7178500
| Bibiyana South 400 MW | 376 | 345 | 345 | 345 | 345 | 345 | 345 | 353 | 345 | 370 | 345 | 340 | 340 | 354 | 345 | 345 | 345 | 345 |  | 350 | 345 | 345 | 345 | 350 | 350 | 345 | 8442300
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 41 | 55 | 55 | 55 | 55 | 35 | 659578
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 14 | 18 | 389280
60 | Barabkunda 22 MW PP (Regent) | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 142560
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 126 | 128 | 122 | 118 | 114 | 112 | 110 | 104 | 110 | 112 | 124 | 120 | 130 | 126 | 138 | 132 | 122 | 96 |  | 116 | 106 | 110 | 6 | 58 | 86 | 86 | 2578560
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 15 | 25 | 30 | 26 | 13 | 4 | 12 | 12 | 12 | 14 | 2 | 2 | 2 | 9 | 14 |  | 20 | 22 | 26 | 26 | 28 | 30 | 28 | 435840
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 32 | 32 | 32 | 31 | 31 | 31 | 31 |  |  | 32 |  | 28 | 21 | 28 |  | 0 | 621000
68 | Cumilla 25 MW PP (Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [9 empty] | 0 | 245750
69 | Summit Ashulia | 21 | 21 | 20 | 21 | 20 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 17 | 22 | 22 | 20 | 22 | 22 | 20 | 480000
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 18 | 19 | 15 | 15 |  | 15 | 0 | 0 | 15 | 15 | 0 | 0 | 317520
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 |  |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 698500
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 30 | 30 | 30 | 16 | 32 | 709400
73 | Ghorashal 108 MW PP (Regent) | 73 | 75 | 75 | 75 | 75 | 75 | 75 | 72 | 72 | 72 | 69 | 65 | 73 | 73 | 69 | 71 | 71 | 73 |  | 78 | 78 | 78 | 78 | 79 | 79 | 79 | 1744863
| Feni Lanka Power | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 17 | 17 | 44 | 70 | 70 | 70 | 70 | 70 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 70 | 1696320
| Chowmuhani 113 MW | 36 | 36 | 37 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 36 | 36 | 38 | 36 | 36 | 32 | 32 | 60 |  | 63 | 63 | 65 | 66 | 67 | 61 | 40 | 1045800
| Manikgonj 162MW PP(MPGL) | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 90 | 90 | 90 | 90 | 90 | 90 | 108 | 108 | 108 | 108 |  | 162 | 162 | 162 | 162 | 162 | 162 | 17 | 1949760
77 | Siddhirganj 100 PP(Dutch Bangla) | 33 | 33 | 33 | 33 | 32 | 24 | 9 | 9 | 9 | 9 | 24 | 54 | 56 | 56 | 56 | 28 | 50 | 56 |  | 67 | 67 | 67 | 67 | 70 | 65 | 68 | 955824
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 296304
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 64 | 64 | 64 | 64 | 110 |  | 145 | 147 | 146 | 147 | 147 | 16 | 16 | 1269600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 | 33 | 33 | 33 | 33 | 34 |  | 50 | 52 | 52 | 52 | 52 | 52 | 25 | 785251
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 105 | 105 | 105 | 105 | 105 | 70 | 17 | 890880
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 0 | 0 | 2 | 5 | 4 | 0 | 0 | 2 | 1 | [9 empty] | 13320
| Jodiac Power | 17 | 0 | [8 empty] | 22 | 36 | 36 | 36 | 36 | 36 | 47 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 669513
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 553670
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 44 | 17 | 17 | 17 | 17 | 25 | 68 | 68 | 68 | 68 | 68 | 70 | 72 |  | 75 | 65 | 68 | 51 | 28 | 30 | 82 | 1243550
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 |  |  |  | 0 | 91003
86 | Meghnaghat CCPP ( Summit) | 308 | 310 | 309 | 302 | 310 | 310 | 310 | 310 | 278 | 300 | 301 | 298 | 297 | 295 | 294 | 295 | 297 | 300 |  | 301 | 278 | 305 | 293 | 307 | 307 | 306 | 7226851
87 | Meghnaghat 100 MW(IEL) | 68 | 82 | 83 | 83 | 83 | 48 | 8 | 8 | 9 | 8 | 19 | 39 | 56 | 56 | 66 | 74 | 87 | 92 |  | 91 | 91 | 89 | 91 | 25 | 18 | 17 | 1289280
| Meghnaghat 104 MW PP (OPCL) | 27 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 16 | 17 | 16 | 16 | 25 | 32 | 34 | 43 | 50 | 50 |  | 50 | 50 | 50 | 50 | 17 | 17 | 17 | 655680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37 | 37 | 35 | 36 | 33 | 35 | 33 | 33 | 33 |  | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 877392
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1058786
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 49 | 49 | 73 | 73 | 73 | 73 | 73 | 65 |  | 90 | 82 | 82 | 82 | 82 | 82 | 24 | 1223280
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 215040
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 20 | 19 | 19 | 24 | 37 | 33 | 30 | 38 | 37 | 37 |  | 55 | 80 | 79 | 82 | 82 | 63 | 20 | 785280
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 |  | 30 | 40 | 38 | 40 | 40 | 40 | 40 | 970588
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 671604
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2406845
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 14450
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 2 | 37 | 54 | 54 | 54 | 54 | 39 | 54 |  | 54 |  | 22 | 42 | 35 | 35 | 35 | 601200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 78 | 78 | 78 | 78 | 78 | 58 | 58 | 57 | 57 | 56 | 57 | 56 | 54 | 54 | 54 | 64 | 57 |  | 104 | 104 | 107 | 107 | 107 | 108 | 108 | 1771200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 36 | 19 | 17 | 17 | 17 | 17 | 17 | 21 | 36 | 48 | 93 | 96 | 96 | 97 | 87 | 82 | 87 | 117 |  | 121 | 129 | 126 | 130 | 133 | 129 | 68 | 1716336
115 | Juldah 100 MW PP Unit-3 (Acorn) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 40 | 49 | 49 | 49 | 49 | 49 | 61 |  | 61 | 61 | 61 | 61 | 61 | 61 | 49 | 1088640
116 | Chandpur 200 MW (Desh energy) | 100 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 92 | 161 | 162 | 162 | 162 | 162 | 162 | 161 | 105 | 85 |  | 90 | 90 | 90 | 90 | 89 | 89 | 89 | 2677920
117 | Ashuganj 150 MW PP (Midland) | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 6 |  | 5 | 5 | 6 | 5 | 6 | 6 | 5 | 143854
118 | Bibiyana-III 400 MW CCPP | 402 | 375 | 365 | 318 | 316 | 321 | 317 | 320 | 318 | 384 | 363 | 378 | 366 | 376 | 368 | 371 | 365 | 365 |  | 370 | 366 | 368 | 365 | 373 | 395 | 365 | 8708000
| Jamalpur 115 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 46 | 46 | 46 | 48 | 56 |  | 86 | 96 | 97 | 98 | 98 | 99 | 99 | 1536000
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 381382
| Juldah unit-2 (Acorn) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 49 | 49 | 48 | 49 | 48 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1062720
| Anlima Energy Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 72 |  | 72 | 72 | 72 | 72 | 72 | 53 | 35 | 1035000
| Bhairob 54.5 MW | 33 | 33 | 34 | 33 | 34 | 25 | 17 | 17 | 17 | 22 | 30 | 31 | 31 | 31 | 31 | 31 | 32 | 33 |  | 33 | 33 | 33 | 34 | 34 | 33 | 35 | 730080
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 6 | 13 | 20 | 22 | 25 | 26 | 25 | 22 | 18 | 11 | 4 | 1 | [8 empty] | 186366
| Chandpur 115(Doreen) | 44 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 48 | 54 | 53 | 53 | 51 | 52 | 53 | 72 | 88 | 94 |  | 94 | 94 | 96 | 96 | 96 | 96 | 91 | 1367040
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 72 | 72 | 54 | 17 | 17 | 17 |  | 17 | 61 | 108 | 108 | 90 | 17 | 17 | 871490
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 17 | 20 | 18 | 40 | 40 | 28 | 16 | 35 | 49 | 44 | 43 | 50 | 35 | 33 | 42 | 47 | 36 | 24 |  | 24 | 37 | 27 | 19 | 7 | 1 | 16 | 691200
| Sonagazi 75 MW Solar Plant |  |  |  |  | 0 | 3 | 13 | 2 | 40 | 10 | 46 | 75 | 70 | 25 | 34 | 20 | 8 | 1 | [8 empty] | 310709
| Matarbari 2*600 MW (CPGCL) | 372 | 371 | 373 | 373 | 371 | 374 | 374 | 373 | 427 | 371 | 391 | 432 | 571 | 573 | 548 | 547 | 749 | 751 |  | 780 | 776 | 779 | 781 | 781 | 780 | 780 | 12960000
120 | Eastern Zone Total | 8238 | 8082 | 7969 | 7867 | 8026 | 7863 | 7749 | 7716 | 7933 | 8028 | 8339 | 8873 | 9134 | 9130 | 9062 | 8900 | 8800 | 8900 |  | 9757 | 9654 | 9816 | 9741 | 9622 | 9357 | 8803 | 207528333
121
122
123 | Khulna 60MW
124 | manik
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 19 | 19 | 19 | 15 | 15 | 15 | 15 | 2 | [7 empty] | 3 |  | 26 | 29 | 40 | 30 | 30 | 30 | 24 | 310560
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 83 | 83 | 87 | 88 | 88 | 89 | 88 | 55 | 55 | 54 | 17 | 17 | 17 | 17 | 17 | 18 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1306080
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 7 | 29 | 26 | 62 | 78 | 88 | 39 | 45 | 34 | 43 | 20 | 3 | [8 empty] | 537120
131 | Rampal 1320 MW (BIFPCL) | 305 | 306 | 307 | 310 | 308 | 309 | 309 | 309 | 308 | 307 | 309 | 308 | 308 | 308 | 308 | 306 | 306 | 308 |  | 306 | 307 | 306 | 307 | 308 | 308 | 307 | 7389091
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 445200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5077773
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 95 | 110 | 110 | 110 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 36 | 48 | 64 | 64 | 64 | 64 | 64 | 1030368
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 272 | 200 | 170 | 170 | 170 | 170 | 150 | 150 | 180 | 180 | 180 | 180 | 180 | 180 | 150 |  | 209 | 230 | 200 | 200 | 200 | 230 | 260 | 4974500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 126 | 126 | 126 | 127 | 128 | 124 | 126 | 128 | 126 | 80 |  | 130 | 130 | 130 | 130 | 130 | 128 | 130 | 2986000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 9 | 8 | 8 | 8 | 8 | 9 | 9 | 10 | 9 | 9 | 8 |  | 10 | 10 | 10 | 10 | 8 | 9 | 10 | 218110
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 47 | 40 | 40 | 38 | 38 | 38 | 39 | 36 | 36 | [8 empty] | 9 |  | 45 | 49 | 39 | 47 | 41 | 44 | 44 | 625792
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 644 | 641 | 926 | 925 | 925 | 926 | 925 | 926 | 926 | 925 | 925 | 925 | 926 | 926 | 926 | 925 | 926 | 926 |  | 926 | 875 | 639 | 643 | 645 | 644 | 645 | 19242909
147 | Bheramara 410 MW CCPP | 395 | 360 | 345 | 345 | 345 | 355 | 345 | 360 | 345 | 380 | 345 | 350 | 350 | 365 | 360 | 350 | 345 | 340 |  | 360 | 355 | 370 | 345 | 360 | 360 | 340 | 8606304
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1100 | 1000 | 840 | 780 | 780 | 780 | 740 | 740 | 800 | 960 | 980 | 980 | 1020 | 1000 | 800 |  | 910 | 1160 | 1120 | 1150 | 1200 | 1220 | 1244 | 26165000
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 73 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 72 | 72 | 72 | 72 | 73 | 72 | 72 | 72 |  | 72 | 72 | 72 | 73 | 73 | 73 | 73 | 1676072
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5559000
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 45 | 45 | 45 | 45 | 45 | 50 |  | 50 | 50 | 45 | 50 | 50 | 50 | 55 | 1170000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 28 | 28 | 28 | 28 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 907707
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 1 | 4 | 4 | 2 | 4 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 32160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 172 | 172 | 171 | 171 | 172 | 172 | 172 | 173 | 174 | 174 | 174 | 173 | 172 | 172 | 171 | 170 | 170 | 170 |  | 168 | 167 | 166 | 167 | 166 | 166 | 166 | 4321800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 202 | 201 | 188 | 184 | 186 | 185 | 190 | 185 | 192 | 187 | 194 | 195 | 199 | 199 | 197 | 199 | 200 | 191 |  | 173 | 204 | 203 | 205 | 208 | 209 | 211 | 4915327
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [19 empty] | 5 | 5 | 5 | 4 | 6 | 30 | 80 | 164145
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 349 | 348 | 363 | 334 | 349 | 347 | 327 | 348 | 304 | 380 | 414 | 414 | 414 | 414 | 414 | 414 | 373 | 350 |  | 414 | 414 | 414 | 414 | 414 | 414 | 388 | 8972509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 11 | 6 | 5 | 0 | [9 empty] | 5 | 5 | 8 | 6 | 6 |  | 10 | 11 | 11 | 11 | 16 | 14 | 14 | 103314
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 263034
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 449131
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 8 | 8 | 8 | 23 | 38 | 38 | 38 |  | 38 | 40 | 40 | 38 | 38 | 38 | 38 | 620420
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [6 empty] | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 446762
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 8 | [12 empty] | 8 | 8 |  |  | 0 | 33077
170 | Chapainawabganj 100 MW Peaking PP | 85 | 85 | 50 | 38 | 0 | [9 empty] | 7 | 8 | 8 | 8 |  | 80 | 85 | 85 | 85 | 85 | 85 | 35 | 706864
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 37 | 18 | 18 | 18 | 18 | 18 | 18 | 37 | 37 | 57 | 57 | 57 | 57 | 57 | 76 | 76 | 76 | 76 |  | 113 | 113 | 113 | 113 | 113 | 57 | 57 | 1376256
172 | Confidence Power Bogura Unit-1 113 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 35 | 35 | 55 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 55 | 1394592
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 34 | 41 | 47 | 53 | 51 | 49 | 58 | 60 | 67 | 81 | 83 |  | 85 | 85 | 92 | 92 | 92 | 85 | 56 | 1366800
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 6 | 7 | 7 | 7 | 7 | 5 | 3 | 2 | 0 | [8 empty] | 52266
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 75 |  | 112 | 115 | 115 | 115 | 75 | 36 | 36 | 1420608
| Intraco Solar 30 MW |  |  |  |  | 0 | 1 | 5 | 9 | 22 | 29 | 32 | 33 | 32 | 28 | 23 | 15 | 6 | 1 | [8 empty] | 236692
| Adani Power Jharkhanda Ltd | 1187 | 1158 | 1165 | 1161 | 1179 | 1171 | 1179 | 1166 | 1162 | 1165 | 1166 | 451 | 449 | 450 | 435 | 433 | 434 | 435 |  | 435 | 436 | 433 | 435 | 438 | 437 | 436 | 18970909
178 | Teesta Solar Limited |  |  |  |  | 0 | 6 | 10 | 31 | 131 | 162 | 170 | 191 | 176 | 157 | 127 | 88 | 35 | 7 | [8 empty] | 1236690