## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-04 | Saturday
|  | Date (day): | 2024-05-04 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15198.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16951 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-03 | 2024-05-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 52 | 77 | 75 | 75 | 33 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 407 | 407 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 50 | 79 | 25 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 306 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 51 | 60 | 25 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 40 | 40 | 40 | 15 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 15 | 60 |  | Engine problem.
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 110 |  | Titas gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 64 | 65 | 60 | 80
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 319 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 41 | 48 | 48 | 90 | 12 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 80 | 132 | 32 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 13 | 36 | 40 | 40 |  | 40 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 16 | 16 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 45 | 210 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 129 | 132 | 52 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 16 | 50 | 17 | 53 | 51 |  | Lube oil shortage.
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 90 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 450 | 470 | 500 | 500
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 350 | 480 | 360 | 450 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 3181 | 3888 | 3488 | 4330 | 657 | 800
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 111 | 118 | 118 | 62 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 5 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 8 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 6 | 6 | 44 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 210 | 211 | 211
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 34 | 71 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 56 | 40 | 64 | 34
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 35 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 49 | 62 | 36 | 60 | 40 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 9 | 5 | 5 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 13 | 40 | 5 | 25
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 48 | 20 | 90 | 18 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 16 | 16 | 284
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 54 |  |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 10 | 17 | 17 | 34 | 76 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 60 | 40 | 70 | 30 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 72 | 35 | 72 | 44 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 54 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 265 | 270 | 270 | 270 | 954 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 50 | 2 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 316 | 424 | 300 | 400 |  |  | Unit-2 on test
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 62 | 0 | 33 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1291 | 1543 | 1378 | 1838 | 1857 | 381
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 190 | 205 | 205 |  | 16 | Under maint
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 295 | 180 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 300 | 250 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 315 | 275 | 350 | 350 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 35 | 34 | 34 | 11
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 46 | 49 | 50 | 50 | 5
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 92 | 8 | 90 | 90 | 105 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 3 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 39 | 36 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 120 | 100 | 120 | 80
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 104 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 51 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 12 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 70 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 45 | 66 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 34 | 42 | 17 | 42 |  | 12 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 96 | 54 | 95 |  | 20 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1588 | 1882 | 1753 | 2109 | 383 | 227
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 74 | 120 | 100 | 100 | 102 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 107 | 56 | 108 | 92 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 99 | 50 | 97 | 18 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 12 | 22
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 247 | 344 | 269.6 | 327 | 102 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 42 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 29 | 28 | 28 |  | 62 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 112 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 37 | 44 | 44
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 5 | 5 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 59 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 195 | 162 | 162 | 162 |  | 69 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 322 | 365 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 340 | 340 | 340 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1427 | 1556 | 1586 | 1586 | 0 | 539
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 930 | 645 | 945 | 655
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 25 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 44 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 345 | 400 | 410
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 48 | 90 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 305 | 307 | 375 | 375
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1679 | 1345 | 1979 | 1634 | 702 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 8 | 1 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 920 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 27 | 123 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 292 | 200 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1414 | 1579 | 1869 | 2048 | 123 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 38 | 38 | 14 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 16 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 40 | 50
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 195 | 185 | 200 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 163 | 195 | 180 | 200
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 345 | 414 | 414 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 23 | 33 | 17 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 50 | 95 |  | 9 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 56 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 35 | 95 | 18 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 954 | 1173 | 1200 | 1200 |  |  | Engine problem
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1698 | 2292 | 2317 | 2574 | 214 | 63
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 70 | 70 | 75 | 10
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 59 | 85 | 56 | 85 | 28 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 55 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 192 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 647 | 500 | 559 | 505 | 78 | 129
| Total |  |  |  |  | 27054 | 25903 | 13172 | 14929 | 15198.6 | 16951 | 4116 | 2262
A. |  | 2024-05-03 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 14994 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11149 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15075 | MW
3 | Day peak Generation : |  |  | 13172 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14487.79 | MW
4 | Evening peak Generation : |  |  | 14929 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 139 | MW
5 | Total Energy Generation : |  | 318.0337 | MKWHr | By Solar | 3.4833 | MKWHr
| By Gas : | 170.3738 | MKWHr |  | By Oil: | 37.458 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 83.09 | MKWHr |  | By Hydro: | 0.732 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.432 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4116 | MW | Dhaka | 4963.89 | 4963.89 |  | 0 |  | 18:00 |  | 293
|  |  | For Plants S/D or M/C prob = |  |  | 2262 | MW | Chittagong | 1397.5 | 1397.5 |  | 0 |  | 19:00 |  | 245
|  |  | Total = |  |  | 6378 | MW | Khulna | 1871 | 1871 |  | 0 |  | 19:30 |  | 170.945
7 | Total Gas Supplied : |  |  | 1253.33 | MMCFD |  |  | Rajshahi | 1694.4 | 1694.4 |  | 0 |  | 20:00 |  | 169.99
8 | Fuel Cost : | i) Gas : | Taka | 479080437.024 | ii) Oil : | Taka | 683969346.82 | Comilla | 1341 | 1341 |  | 0 |  | 21:00 |  | 139.43
|  | iii) Coal : | Taka | 565799213.53 | Total | Taka | 1728848997.374 | Mymensingh | 1356 | 1217 |  | 139 |  | 22:00 |  | 148.98
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.033 | MKWHr. | Sylhet | 482 | 482 |  | 0 |  | 23:00 |  | 296.05
| ii) During Peak Demand : |  |  | 438 | MW (W to E) at | 21:00 | hrs | Barisal | 423 | 423 |  | 0 |  | 24:00 |  | 788.83
| iii) Maximum : |  |  | 185 | MW at | 6:00 | hrs | Rangpur | 959 | 959 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 38.1°C |  |  | Total | 14487.79 | 14348.79 |  | 139
B. |  | 2024-05-04 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 38.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16951 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14000 | MW
4 | Reserve(Generation end) |  |  |  | 1451 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 328.7664 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12323 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.4189 | MKWHr. | ii) HVDC Flow at Peak Time |  | 645 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0458 | MKWHr. | iii) Maximum HVDC Flow : |  | 930 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.62 |  | (b) Today: | 0 |  | (c) Rule Curve: |  | 81.43
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-03 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 401 | 0 |  | 0 | 450 | 305 | 17 | 88 | 40 | 334 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 114 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 32 | 51 | 0 | 19 | 6 | 8 | 28 | 0 | 0 | 0 | 285 | 275 | 213 | 63 | 0 | 37 | 50 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 0 | 0 | 74 | 95 | 0 | 0 | 0 | 43 | 30 | 53 | 40 | 112 | 0 | 59 | 0 | 0 | 207 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 37 | 0 | 49 | 89 | 6 | 365 | 69 | 17 | 17 | 0 | 16 | 17 | 17 | 70 | 38 | 48 | 345 | 17 | 0 | 17 | 35 | 0 | 34 | 0 | 58 | 0 | 230 | 17 | 0 | 271 | 5 | 779 | 420 | 400 | 0 |  | 645 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 20 | 44 | 0 | 130 | 10 | 16 | 0 | 0 | 55 | 38 | 10 | 0 | 0 | 16 | 30 | 0 | 23 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 65 | 0 | 194 | 0 | 0 | 0 | 122 | 0 | 414 | 66 | 0 | 35 | 0 | 39 | 0 | 0 | 18 | 1200 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 306 | 0 | 260 | 436 | 0 | 0 |  | 8258 | 5102 | 13360 | 4425 | 645 | 2976 | 0 | 1332 | 3555 | 30 | 0 | 318 | 74 | 0 | 5 | 898 | 73.63
2:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 400 | 0 |  | 0 | 450 | 293 | 0 | 78 | 40 | 327 | 0 | 0 | 42 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 115 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 25 | 51 | 0 | 19 | 6 | 0 | 28 | 0 | 0 | 0 | 285 | 230 | 220 | 63 | 0 | 38 | 50 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 32 | 0 | 30 | 95 | 0 | 0 | 0 | 43 | 30 | 53 | 40 | 112 | 0 | 59 | 0 | 0 | 200 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 80 | 0 | 0 | 78 | 0 | 17 | 0 | 49 | 89 | 5 | 365 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 70 | 38 | 48 | 345 | 17 | 0 | 17 | 35 | 0 | 20 | 0 | 19 | 0 | 230 | 17 | 0 | 271 | 1 | 781 | 400 | 400 | 0 |  | 645 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 0 | 126 | 10 | 16 | 0 | 0 | 50 | 38 | 10 | 0 | 0 | 16 | 30 | 0 | 23 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 135 | 0 | 381 | 73 | 0 | 35 | 0 | 34 | 0 | 0 | 18 | 1100 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 307 | 0 | 231 | 437 | 0 | 0 |  | 8020 | 4848 | 12868 | 4326 | 645 | 2911 | 0 | 1208 | 3430 | 30 | 0 | 287 | 30 | 0 | 1 | 699 | 73.63
3:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 407 | 0 |  | 0 | 450 | 297 | 0 | 34 | 40 | 328 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 120 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 25 | 51 | 0 | 17 | 6 | 7 | 28 | 0 | 0 | 0 | 285 | 230 | 219 | 63 | 0 | 38 | 48 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 29 | 0 | 64 | 98 | 0 | 0 | 0 | 43 | 30 | 53 | 40 | 112 | 0 | 59 | 0 | 0 | 200 | 0 | 0 | 0 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 78 | 0 | 17 | 0 | 49 | 89 | 6 | 365 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 70 | 38 | 48 | 345 | 17 | 0 | 17 | 35 | 0 | 17 | 0 | 19 | 0 | 230 | 17 | 0 | 269 | 3 | 779 | 350 | 350 | 0 |  | 929 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 10 | 16 | 0 | 0 | 50 | 40 | 5 | 0 | 0 | 16 | 30 | 0 | 0 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 176 | 0 | 398 | 73 | 0 | 35 | 0 | 34 | 0 | 0 | 18 | 980 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 306 | 0 | 150 | 434 | 0 | 0 |  | 7798 | 4923 | 12721 | 4390 | 929 | 2825 | 0 | 1038 | 3221 | 30 | 0 | 221 | 64 | 0 | 3 | 457 | 73.63
4:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 406 | 0 |  | 0 | 450 | 309 | 0 | 0 | 40 | 328 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 120 | 0 | 8 | 211 | 0 | 0 | 0 |  | 12 | 25 | 34 | 0 | 12 | 6 | 7 | 28 | 0 | 0 | 0 | 295 | 280 | 0 | 73 | 0 | 38 | 51 | 0 | 51 | 0 | 7 | 25 | 0 | 0 | 26 | 0 | 60 | 99 | 0 | 0 | 0 | 43 | 30 | 53 | 37 | 112 | 0 | 59 | 0 | 0 | 200 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 78 | 0 | 17 | 0 | 49 | 90 | 6 | 370 | 69 | 17 | 17 | 0 | 16 | 0 | 17 | 70 | 38 | 48 | 349 | 33 | 0 | 17 | 35 | 0 | 17 | 0 | 20 | 0 | 285 | 17 | 0 | 272 | 6 | 781 | 350 | 350 | 0 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 208 | 0 | 414 | 73 | 0 | 35 | 0 | 34 | 0 | 0 | 18 | 980 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 308 | 0 | 150 | 434 | 0 | 0 |  | 7683 | 4828 | 12511 | 4286 | 929 | 2848 | 0 | 985 | 3228 | 30 | 0 | 139 | 60 | 0 | 6 | 371 | 73.62
5:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 406 | 0 |  | 0 | 450 | 307 | 0 | 0 | 40 | 330 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 120 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 25 | 34 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 285 | 265 | 0 | 92 | 0 | 38 | 51 | 0 | 51 | 0 | 7 | 25 | 0 | 0 | 20 | 0 | 50 | 99 | 0 | 0 | 0 | 43 | 30 | 53 | 40 | 80 | 0 | 59 | 0 | 0 | 200 | 0 | 0 | 0 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 78 | 0 | 17 | 0 | 25 | 90 | 5 | 315 | 69 | 17 | 0 | 0 | 16 | 0 | 0 | 34 | 38 | 48 | 310 | 33 | 0 | 17 | 35 | 0 | 17 | 0 | 21 | 0 | 285 | 0 | 0 | 274 | 0 | 726 | 350 | 350 | 0 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 189 | 0 | 347 | 73 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 980 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 307 | 0 | 150 | 441 | 0 | 0 |  | 7299 | 4713 | 12012 | 4126 | 929 | 2726 | 0 | 848 | 3181 | 30 | 0 | 122 | 50 | 0 | 0 | 371 | 73.62
6:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 403 | 0 |  | 0 | 400 | 285 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 122 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 2 | 0 | 0 | 0 | 0 | 7 | 5 | 0 | 0 | 0 | 285 | 265 | 0 | 92 | 0 | 38 | 52 | 0 | 51 | 0 | 7 | 25 | 0 | 0 | 22 | 0 | 58 | 99 | 0 | 0 | 0 | 43 | 30 | 11 | 40 | 80 | 0 | 60 | 0 | 0 | 201 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 77 | 0 | 17 | 0 | 0 | 90 | 6 | 318 | 69 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 38 | 0 | 310 | 33 | 2 | 17 | 17 | 0 | 17 | 1 | 18 | 0 | 250 | 0 | 0 | 272 | 0 | 725 | 350 | 350 | 4 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 155 | 0 | 296 | 73 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 900 | 180 | 0 | 0 | 0 | 3 | 36 | 0 | 0 | 309 | 0 | 150 | 440 | 10 | 0 |  | 6997 | 4547 | 11544 | 4055 | 929 | 2551 | 0 | 738 | 3098 | 30 | 0 | 65 | 58 | 20 | 0 | 340 | 73.62
7:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 401 | 0 |  | 0 | 330 | 260 | 0 | 14 | 40 | 335 | 0 | 0 | 8 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 122 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 285 | 275 | 0 | 92 | 0 | 35 | 52 | 0 | 51 | 0 | 7 | 8 | 0 | 0 | 32 | 0 | 60 | 94 | 0 | 0 | 0 | 43 | 30 | 11 | 10 | 80 | 0 | 60 | 0 | 0 | 200 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 57 | 0 | 17 | 0 | 0 | 51 | 6 | 318 | 49 | 17 | 0 | 1 | 0 | 0 | 0 | 19 | 15 | 0 | 310 | 16 | 10 | 0 | 17 | 0 | 17 | 6 | 17 | 0 | 250 | 0 | 0 | 271 | 0 | 725 | 350 | 350 | 16 |  | 930 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 155 | 0 | 316 | 35 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 780 | 180 | 0 | 0 | 0 | 19 | 35 | 0 | 0 | 311 | 6 | 150 | 471 | 42 | 0 |  | 6763 | 4425 | 11188 | 4068 | 930 | 2449 | 0 | 517 | 3010 | 30 | 0 | 23 | 60 | 101 | 0 | 393 | 73.61
8:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 401 | 0 |  | 0 | 330 | 260 | 0 | 25 | 40 | 331 | 0 | 0 | 17 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 10 | 0 | 22 | 0 | 33 | 0 | 8 | 0 | 0 | 30 | 120 | 0 | 0 | 211 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 0 | 0 | 0 | 295 | 240 | 0 | 92 | 0 | 37 | 50 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 0 | 72 | 85 | 0 | 0 | 1 | 43 | 30 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 201 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 23 | 0 | 0 | 51 | 0 | 315 | 49 | 17 | 0 | 3 | 0 | 0 | 0 | 52 | 9 | 0 | 310 | 0 | 21 | 0 | 0 | 0 | 17 | 12 | 17 | 0 | 230 | 0 | 0 | 271 | 0 | 729 | 350 | 350 | 35 |  | 929 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 157 | 0 | 345 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 700 | 180 | 0 | 0 | 1 | 38 | 35 | 0 | 0 | 309 | 13 | 150 | 418 | 88 | 0 |  | 6780 | 4369 | 11149 | 4002 | 929 | 2466 | 0 | 540 | 2879 | 30 | 0 | 16 | 72 | 215 | 0 | 411.605 | 73.61
9:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 400 | 0 |  | 0 | 330 | 260 | 0 | 17 | 40 | 329 | 0 | 0 | 22 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 0 | 7 | 33 | 28 | 8 | 0 | 0 | 30 | 120 | 0 | 0 | 217 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 0 | 0 | 7 | 14 | 0 | 0 | 0 | 345 | 240 | 0 | 92 | 0 | 37 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 0 | 82 | 84 | 0 | 0 | 2 | 41 | 29 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 199 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 35 | 3 | 0 | 51 | 0 | 314 | 49 | 17 | 0 | 4 | 0 | 0 | 0 | 52 | 9 | 0 | 310 | 0 | 32 | 0 | 0 | 0 | 19 | 19 | 17 | 0 | 230 | 0 | 0 | 265 | 0 | 727 | 350 | 350 | 52 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 160 | 0 | 348 | 0 | 0 | 0 | 0 | 41 | 0 | 4 | 0 | 700 | 180 | 0 | 0 | 3 | 65 | 30 | 0 | 0 | 310 | 21 | 150 | 636 | 130 | 0 |  | 6929 | 4676 | 11605 | 4062 | 929 | 2484 | 0 | 561 | 3090 | 30 | 0 | 32 | 82 | 335 | 0 | 405.875 | 73.61
10:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 407 | 0 |  | 0 | 330 | 261 | 3 | 45 | 15 | 324 | 0 | 0 | 42 | 40 | 82 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 13 | 7 | 33 | 32 | 16 | 0 | 0 | 30 | 120 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 0 | 0 | 0 | 285 | 240 | 0 | 92 | 0 | 37 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 0 | 88 | 84 | 0 | 0 | 2 | 42 | 29 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 199 | 0 | 0 | 0 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 45 | 17 | 0 | 57 | 0 | 316 | 49 | 35 | 0 | 4 | 0 | 0 | 0 | 52 | 21 | 0 | 310 | 0 | 41 | 0 | 0 | 0 | 33 | 23 | 20 | 0 | 230 | 0 | 0 | 265 | 0 | 725 | 350 | 350 | 63 |  | 930 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 158 | 0 | 348 | 0 | 0 | 0 | 0 | 58 | 0 | 5 | 0 | 700 | 180 | 0 | 0 | 4 | 81 | 35 | 0 | 0 | 308 | 27 | 150 | 811 | 164 | 0 |  | 7107 | 4920 | 12027 | 4011 | 930 | 2476 | 0 | 719 | 3260 | 30 | 0 | 82 | 88 | 431 | 0 | 365.765 | 73.61
11:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 408 | 0 |  | 0 | 360 | 303 | 39 | 51 | 15 | 317 | 0 | 0 | 55 | 49 | 82 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 13 | 7 | 33 | 32 | 16 | 0 | 0 | 30 | 115 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 1 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 300 | 310 | 0 | 92 | 0 | 34 | 47 | 0 | 51 | 0 | 0 | 12 | 0 | 0 | 32 | 0 | 96 | 82 | 0 | 0 | 2 | 40 | 29 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 196 | 0 | 0 | 0 | 320 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 108 | 0 | 10 | 91 | 1 | 328 | 49 | 35 | 0 | 5 | 16 | 0 | 0 | 52 | 36 | 15 | 320 | 16 | 46 | 0 | 2 | 0 | 34 | 26 | 34 | 0 | 280 | 0 | 0 | 265 | 37 | 316 | 350 | 350 | 54 |  | 929 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 178 | 0 | 350 | 0 | 0 | 0 | 0 | 59 | 0 | 6 | 0 | 720 | 220 | 0 | 0 | 4 | 91 | 55 | 0 | 0 | 309 | 30 | 150 | 899 | 182 | 0 |  | 7234 | 5231 | 12465 | 4257 | 929 | 2614 | 0 | 1013 | 2960 | 30 | 0 | 83 | 96 | 446 | 37 | 377.225 | 73.6
12:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 407 | 0 |  | 0 | 420 | 301 | 50 | 51 | 15 | 315 | 0 | 0 | 64 | 41 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 13 | 0 | 33 | 32 | 16 | 0 | 0 | 30 | 115 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 280 | 305 | 0 | 92 | 0 | 33 | 46 | 0 | 51 | 0 | 23 | 25 | 0 | 0 | 32 | 0 | 116 | 74 | 0 | 0 | 2 | 40 | 28 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 195 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 129 | 8 | 49 | 100 | 5 | 322 | 48 | 35 | 0 | 4 | 16 | 0 | 10 | 52 | 45 | 48 | 380 | 16 | 47 | 17 | 35 | 0 | 34 | 27 | 34 | 0 | 315 | 17 | 0 | 265 | 50 | 316 | 450 | 350 | 62 |  | 930 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 163 | 0 | 345 | 0 | 0 | 0 | 0 | 59 | 0 | 7 | 0 | 860 | 220 | 0 | 0 | 4 | 94 | 55 | 0 | 0 | 305 | 32 | 200 | 954 | 192 | 0 |  | 7734 | 5438 | 13172 | 4252 | 930 | 2749 | 0 | 1212 | 3202 | 30 | 0 | 152 | 116 | 479 | 50 | 389.64 | 73.61
13:00 | 0 | 0 | 0 | 180 | 0 | 71 | 0 | 406 | 0 |  | 0 | 450 | 295 | 49 | 51 | 15 | 309 | 0 | 0 | 55 | 57 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 20 | 0 | 13 | 7 | 33 | 32 | 16 | 0 | 0 | 30 | 108 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 17 | 0 | 0 | 5 | 10 | 13 | 0 | 0 | 0 | 285 | 285 | 0 | 150 | 0 | 33 | 45 | 0 | 51 | 0 | 29 | 28 | 0 | 0 | 32 | 0 | 120 | 73 | 0 | 0 | 2 | 40 | 28 | 53 | 33 | 112 | 0 | 55 | 0 | 0 | 195 | 0 | 0 | 0 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 130 | 7 | 49 | 116 | 6 | 318 | 48 | 35 | 0 | 3 | 16 | 0 | 17 | 103 | 48 | 60 | 345 | 16 | 45 | 17 | 35 | 0 | 34 | 25 | 43 | 0 | 300 | 54 | 0 | 268 | 46 | 315 | 450 | 300 | 64 |  | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 163 | 0 | 295 | 0 | 0 | 3 | 0 | 56 | 0 | 7 | 0 | 990 | 220 | 0 | 0 | 4 | 92 | 55 | 0 | 0 | 308 | 30 | 250 | 1113 | 182 | 0 |  | 7989 | 5689 | 13678 | 4164 | 928 | 2842 | 0 | 1329 | 3546 | 30 | 0 | 212 | 120 | 461 | 46 | 403 | 73.61
14:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 398 | 0 |  | 0 | 380 | 294 | 24 | 63 | 15 | 310 | 0 | 0 | 60 | 57 | 78 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 7 | 30 | 32 | 16 | 0 | 0 | 30 | 108 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 32 | 17 | 0 | 0 | 6 | 10 | 13 | 0 | 0 | 0 | 315 | 280 | 0 | 120 | 0 | 32 | 44 | 0 | 51 | 0 | 28 | 34 | 0 | 0 | 32 | 2 | 116 | 72 | 0 | 0 | 2 | 40 | 28 | 53 | 32 | 80 | 0 | 50 | 0 | 0 | 194 | 0 | 0 | 0 | 270 | 20 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 126 | 0 | 62 | 117 | 6 | 322 | 48 | 17 | 0 | 3 | 16 | 0 | 17 | 114 | 54 | 60 | 315 | 16 | 40 | 17 | 35 | 0 | 34 | 22 | 54 | 0 | 285 | 17 | 0 | 268 | 49 | 319 | 350 | 300 | 47 |  | 929 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 157 | 0 | 350 | 0 | 0 | 35 | 0 | 61 | 0 | 7 | 0 | 900 | 180 | 0 | 0 | 4 | 80 | 55 | 0 | 0 | 309 | 27 | 150 | 1151 | 147 | 0 |  | 7669 | 5502 | 13171 | 4102 | 929 | 2595 | 0 | 1400 | 3399 | 30 | 0 | 172 | 116 | 379 | 49 | 385.82 | 73.6
15:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 384 | 0 |  | 0 | 380 | 295 | 9 | 50 | 15 | 307 | 0 | 0 | 61 | 57 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 7 | 30 | 32 | 16 | 0 | 0 | 30 | 110 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 32 | 17 | 0 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 325 | 305 | 26 | 120 | 0 | 31 | 42 | 0 | 51 | 0 | 28 | 33 | 0 | 0 | 32 | 2 | 120 | 90 | 0 | 0 | 2 | 37 | 28 | 52 | 32 | 80 | 0 | 40 | 0 | 0 | 159 | 0 | 0 | 0 | 310 | 20 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 96 | 11 | 62 | 121 | 6 | 351 | 48 | 17 | 0 | 3 | 16 | 0 | 17 | 114 | 38 | 60 | 350 | 16 | 31 | 17 | 35 | 0 | 33 | 17 | 72 | 0 | 315 | 17 | 0 | 276 | 46 | 317 | 422 | 400 | 31 |  | 929 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 176 | 0 | 351 | 0 | 0 | 35 | 0 | 53 | 0 | 4 | 0 | 900 | 180 | 0 | 0 | 3 | 70 | 55 | 0 | 0 | 309 | 21 | 150 | 1171 | 129 | 0 |  | 7901 | 5549 | 13450 | 4282 | 929 | 2799 | 0 | 1339 | 3425 | 30 | 0 | 158 | 120 | 322 | 46 | 429.75 | 73.61
16:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 397 | 0 |  | 0 | 380 | 298 | 15 | 47 | 15 | 305 | 0 | 0 | 61 | 57 | 63 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 19 | 14 | 30 | 24 | 16 | 0 | 0 | 30 | 108 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 32 | 17 | 0 | 0 | 6 | 10 | 6 | 0 | 0 | 0 | 295 | 305 | 43 | 120 | 0 | 31 | 41 | 0 | 51 | 0 | 29 | 33 | 0 | 0 | 32 | 2 | 116 | 96 | 0 | 0 | 1 | 37 | 27 | 52 | 32 | 112 | 0 | 54 | 0 | 0 | 160 | 0 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 64 | 8 | 62 | 121 | 5 | 325 | 48 | 17 | 0 | 2 | 16 | 0 | 17 | 114 | 36 | 60 | 322 | 16 | 19 | 17 | 35 | 0 | 26 | 11 | 74 | 0 | 320 | 17 | 0 | 270 | 42 | 321 | 420 | 400 | 20 |  | 929 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 176 | 0 | 402 | 0 | 0 | 35 | 0 | 80 | 0 | 3 | 0 | 900 | 180 | 0 | 0 | 2 | 45 | 55 | 0 | 0 | 308 | 14 | 150 | 1170 | 86 | 0 |  | 7836 | 5578 | 13414 | 4275 | 929 | 2883 | 0 | 1349 | 3421 | 30 | 0 | 158 | 116 | 211 | 42 | 416.38 | 73.61
17:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 403 | 0 |  | 0 | 380 | 288 | 48 | 62 | 15 | 306 | 0 | 0 | 69 | 65 | 63 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 21 | 6 | 30 | 30 | 16 | 0 | 0 | 30 | 108 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 32 | 17 | 0 | 0 | 6 | 10 | 16 | 0 | 0 | 0 | 290 | 300 | 53 | 128 | 0 | 32 | 41 | 0 | 51 | 0 | 36 | 34 | 0 | 0 | 32 | 14 | 114 | 101 | 0 | 0 | 0 | 39 | 27 | 52 | 35 | 112 | 0 | 55 | 0 | 0 | 160 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 57 | 0 | 70 | 0 | 62 | 120 | 8 | 318 | 48 | 17 | 0 | 0 | 16 | 0 | 17 | 114 | 27 | 60 | 310 | 23 | 8 | 17 | 35 | 0 | 33 | 5 | 81 | 0 | 320 | 17 | 0 | 270 | 42 | 320 | 330 | 300 | 13 |  | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 190 | 0 | 383 | 0 | 0 | 0 | 0 | 84 | 0 | 2 | 0 | 900 | 180 | 0 | 0 | 0 | 16 | 55 | 0 | 0 | 306 | 6 | 150 | 1169 | 35 | 0 |  | 7702 | 5416 | 13118 | 4270 | 928 | 2668 | 0 | 1402 | 3414 | 30 | 0 | 165 | 114 | 85 | 42 | 412.56 | 73.61
18:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 409 | 0 |  | 0 | 350 | 258 | 37 | 68 | 0 | 309 | 0 | 0 | 69 | 65 | 63 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 21 | 5 | 30 | 30 | 16 | 0 | 0 | 30 | 111 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 41 | 17 | 0 | 0 | 6 | 10 | 16 | 0 | 0 | 0 | 290 | 300 | 55 | 103 | 0 | 32 | 44 | 0 | 51 | 0 | 36 | 34 | 0 | 0 | 28 | 0 | 72 | 105 | 0 | 0 | 0 | 40 | 27 | 22 | 20 | 80 | 0 | 56 | 0 | 0 | 160 | 18 | 0 | 0 | 260 | 19 | 5 | 0 | 0 | 0 | 0 | 57 | 0 | 129 | 0 | 25 | 120 | 5 | 317 | 57 | 17 | 0 | 0 | 16 | 0 | 17 | 52 | 27 | 24 | 310 | 33 | 1 | 17 | 35 | 0 | 34 | 1 | 94 | 0 | 325 | 17 | 0 | 270 | 28 | 375 | 330 | 300 | 2 |  | 930 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 1 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 166 | 0 | 298 | 8 | 0 | 0 | 0 | 84 | 0 | 0 | 0 | 760 | 180 | 0 | 0 | 0 | 3 | 55 | 0 | 0 | 310 | 1 | 150 | 1056 | 7 | 0 |  | 7446 | 4947 | 12393 | 4207 | 930 | 2391 | 0 | 1326 | 3220 | 30 | 0 | 174 | 72 | 15 | 28 | 293 | 73.61
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 406 | 0 |  | 0 | 390 | 306 | 34 | 80 | 0 | 313 | 0 | 0 | 69 | 90 | 148 | 15 | 0 | 0 | 0 | 33 | 55 | 55 | 0 | 21 | 4 | 30 | 32 | 16 | 0 | 0 | 30 | 110 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 56 | 29 | 0 | 0 | 6 | 7 | 16 | 0 | 0 | 0 | 295 | 300 | 142 | 88 | 0 | 33 | 42 | 0 | 51 | 0 | 37 | 50 | 0 | 0 | 28 | 10 | 78 | 112 | 0 | 0 | 0 | 39 | 28 | 50 | 34 | 112 | 0 | 59 | 0 | 0 | 162 | 18 | 0 | 0 | 290 | 24 | 5 | 0 | 105 | 0 | 0 | 104 | 0 | 132 | 0 | 48 | 120 | 6 | 340 | 97 | 105 | 1 | 0 | 16 | 6 | 17 | 95 | 36 | 60 | 340 | 50 | 0 | 144 | 38 | 0 | 41 | 0 | 94 | 0 | 325 | 90 | 0 | 270 | 28 | 378 | 405 | 300 | 0 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 0 | 124 | 1 | 32 | 0 | 0 | 50 | 0 | 5 | 85 | 0 | 8 | 4 | 0 | 23 | 0 | 0 | 11 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 174 | 0 | 396 | 20 | 0 | 18 | 0 | 88 | 0 | 0 | 35 | 760 | 220 | 0 | 6 | 0 | 0 | 75 | 0 | 0 | 307 | 0 | 210 | 1135 | 0 | 0 |  | 8716 | 5577 | 14293 | 4455 | 929 | 2780 | 0 | 2118 | 3361 | 30 | 0 | 514 | 78 | 0 | 28 | 245 | 73.61
19:30 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 413 | 0 |  | 0 | 390 | 274 | 66 | 80 | 0 | 316 | 0 | 0 | 69 | 90 | 148 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 21 | 15 | 30 | 32 | 16 | 0 | 0 | 30 | 112 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 56 | 34 | 0 | 0 | 6 | 7 | 19 | 0 | 0 | 0 | 295 | 300 | 206 | 88 | 0 | 33 | 47 | 0 | 51 | 0 | 37 | 51 | 0 | 0 | 28 | 12 | 74 | 112 | 0 | 0 | 0 | 42 | 29 | 50 | 36 | 112 | 0 | 59 | 0 | 0 | 162 | 18 | 0 | 0 | 280 | 24 | 5 | 0 | 155 | 0 | 0 | 104 | 0 | 132 | 0 | 62 | 120 | 6 | 366 | 98 | 105 | 17 | 0 | 16 | 34 | 17 | 105 | 65 | 60 | 340 | 50 | 0 | 162 | 72 | 0 | 51 | 0 | 96 | 0 | 295 | 108 | 0 | 270 | 25 | 371 | 400 | 300 | 0 |  | 851 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 40 | 36 | 0 | 124 | 1 | 40 | 0 | 0 | 50 | 0 | 5 | 85 | 0 | 8 | 10 | 0 | 23 | 0 | 0 | 11 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 182 | 0 | 372 | 53 | 0 | 109 | 0 | 92 | 0 | 0 | 35 | 790 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 310 | 0 | 230 | 1167 | 0 | 0 |  | 9041 | 5805 | 14846 | 4557 | 851 | 2719 | 0 | 2569 | 3439 | 30 | 0 | 582 | 74 | 0 | 25 | 170.945 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 411 | 0 |  | 0 | 390 | 293 | 58 | 80 | 1 | 316 | 0 | 0 | 71 | 90 | 148 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 21 | 15 | 0 | 32 | 16 | 0 | 0 | 30 | 116 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 56 | 34 | 0 | 6 | 6 | 9 | 19 | 0 | 0 | 0 | 300 | 305 | 197 | 56 | 0 | 35 | 46 | 0 | 51 | 0 | 37 | 51 | 0 | 0 | 28 | 12 | 82 | 120 | 0 | 0 | 0 | 40 | 28 | 50 | 37 | 112 | 0 | 58 | 0 | 0 | 162 | 18 | 0 | 0 | 275 | 24 | 5 | 0 | 210 | 0 | 0 | 107 | 0 | 132 | 0 | 62 | 120 | 5 | 365 | 98 | 105 | 17 | 0 | 16 | 35 | 17 | 105 | 64 | 60 | 340 | 50 | 0 | 162 | 72 | 0 | 51 | 0 | 96 | 0 | 285 | 108 | 0 | 270 | 20 | 373 | 400 | 300 | 0 |  | 646 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 45 | 49 | 0 | 130 | 1 | 48 | 0 | 0 | 50 | 0 | 20 | 85 | 0 | 8 | 20 | 0 | 26 | 0 | 0 | 11 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 183 | 0 | 414 | 54 | 0 | 113 | 0 | 85 | 0 | 0 | 35 | 800 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 306 | 0 | 230 | 1161 | 0 | 0 |  | 9060 | 5712 | 14772 | 4546 | 646 | 2744 | 0 | 2635 | 3441 | 30 | 0 | 628 | 82 | 0 | 20 | 169.99 | 73.61
21:00 | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 407 | 0 |  | 0 | 450 | 306 | 79 | 60 | 40 | 319 | 0 | 0 | 65 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 21 | 15 | 33 | 32 | 16 | 0 | 0 | 30 | 111 | 0 | 5 | 210 | 0 | 0 | 0 |  | 18 | 56 | 34 | 0 | 48 | 6 | 9 | 40 | 0 | 0 | 0 | 295 | 300 | 190 | 8 | 0 | 35 | 49 | 0 | 51 | 0 | 39 | 51 | 0 | 0 | 32 | 12 | 104 | 120 | 0 | 0 | 0 | 42 | 29 | 50 | 37 | 112 | 0 | 59 | 0 | 0 | 162 | 18 | 0 | 0 | 310 | 24 | 8 | 0 | 45 | 0 | 0 | 107 | 0 | 132 | 0 | 62 | 120 | 3 | 365 | 99 | 105 | 17 | 0 | 16 | 0 | 17 | 114 | 66 | 60 | 340 | 50 | 0 | 162 | 72 | 0 | 42 | 0 | 96 | 0 | 275 | 54 | 0 | 270 | 2 | 424 | 470 | 480 | 0 |  | 645 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 1 | 16 | 0 | 0 | 50 | 0 | 16 | 85 | 0 | 0 | 40 | 0 | 22 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 195 | 0 | 414 | 48 | 0 | 56 | 0 | 85 | 0 | 0 | 35 | 920 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 307 | 0 | 292 | 1173 | 0 | 0 |  | 9213 | 5716 | 14929 | 4569 | 645 | 3075 | 0 | 2340 | 3686 | 30 | 0 | 478 | 104 | 0 | 2 | 139.43 | 73.61
22:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 409 | 0 |  | 0 | 450 | 301 | 0 | 8 | 40 | 320 | 0 | 0 | 0 | 48 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 21 | 19 | 33 | 32 | 16 | 0 | 0 | 30 | 110 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 56 | 34 | 0 | 77 | 6 | 9 | 40 | 0 | 0 | 0 | 295 | 300 | 197 | 8 | 0 | 35 | 51 | 0 | 51 | 0 | 39 | 51 | 0 | 0 | 32 | 13 | 114 | 117 | 0 | 0 | 0 | 42 | 29 | 50 | 37 | 112 | 0 | 59 | 0 | 0 | 162 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 45 | 0 | 0 | 107 | 0 | 132 | 0 | 62 | 110 | 5 | 365 | 99 | 105 | 17 | 0 | 16 | 0 | 17 | 114 | 66 | 60 | 340 | 50 | 0 | 162 | 72 | 0 | 33 | 0 | 96 | 0 | 300 | 54 | 0 | 270 | 16 | 574 | 420 | 400 | 0 |  | 645 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 3 | 16 | 0 | 0 | 50 | 0 | 16 | 85 | 0 | 0 | 40 | 8 | 22 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 183 | 0 | 414 | 0 | 0 | 35 | 0 | 85 | 0 | 0 | 35 | 1210 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 307 | 0 | 307 | 1151 | 0 | 0 |  | 9063 | 5931 | 14994 | 4596 | 645 | 2915 | 0 | 2098 | 4119 | 30 | 0 | 461 | 114 | 0 | 16 | 148.98 | 73.61
23:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 405 | 0 |  | 0 | 450 | 304 | 0 | 0 | 40 | 322 | 0 | 0 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 19 | 33 | 32 | 16 | 0 | 0 | 30 | 110 | 0 | 8 | 210 | 0 | 0 | 0 |  | 15 | 48 | 34 | 0 | 71 | 6 | 9 | 40 | 0 | 0 | 0 | 310 | 310 | 195 | 8 | 0 | 35 | 50 | 0 | 51 | 0 | 39 | 51 | 0 | 0 | 32 | 13 | 112 | 121 | 0 | 0 | 0 | 42 | 29 | 50 | 40 | 112 | 0 | 60 | 0 | 0 | 162 | 18 | 0 | 0 | 300 | 24 | 5 | 0 | 45 | 0 | 0 | 107 | 0 | 111 | 0 | 62 | 107 | 5 | 400 | 99 | 70 | 17 | 0 | 16 | 0 | 17 | 114 | 66 | 60 | 381 | 50 | 0 | 162 | 56 | 0 | 34 | 0 | 96 | 0 | 270 | 17 | 0 | 270 | 5 | 579 | 455 | 430 | 0 |  | 646 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 32 | 0 | 0 | 0 | 0 | 14 | 85 | 0 | 0 | 38 | 8 | 22 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 202 | 0 | 414 | 7 | 0 | 35 | 0 | 85 | 0 | 0 | 70 | 1244 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 307 | 0 | 307 | 1003 | 0 | 0 |  | 8996 | 5844 | 14840 | 4673 | 646 | 3008 | 0 | 2025 | 4012 | 30 | 0 | 329 | 112 | 0 | 5 | 296.05 | 73.61
24:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 405 | 0 |  | 0 | 450 | 149 | 19 | 12 | 38 | 327 | 0 | 0 | 20 | 82 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 22 | 15 | 33 | 32 | 8 | 0 | 0 | 30 | 110 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 41 | 34 | 0 | 18 | 6 | 9 | 35 | 0 | 0 | 0 | 310 | 310 | 199 | 8 | 0 | 35 | 46 | 0 | 51 | 0 | 39 | 51 | 0 | 0 | 32 | 13 | 114 | 119 | 0 | 0 | 0 | 42 | 29 | 50 | 40 | 112 | 0 | 60 | 0 | 0 | 162 | 18 | 0 | 0 | 310 | 24 | 0 | 0 | 95 | 0 | 0 | 108 | 0 | 56 | 0 | 49 | 107 | 6 | 365 | 99 | 17 | 17 | 0 | 16 | 26 | 17 | 114 | 47 | 60 | 340 | 50 | 0 | 162 | 35 | 0 | 34 | 0 | 92 | 0 | 280 | 17 | 0 | 276 | 7 | 575 | 455 | 430 | 0 |  | 646 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 48 | 0 | 0 | 0 | 0 | 14 | 25 | 0 | 25 | 38 | 0 | 22 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 196 | 0 | 394 | 41 | 0 | 76 | 0 | 34 | 0 | 0 | 95 | 1244 | 220 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 303 | 0 | 307 | 756 | 0 | 0 |  | 8632 | 5522 | 14154 | 4553 | 646 | 2834 | 0 | 1961 | 3763 | 30 | 0 | 246 | 114 | 0 | 7 | 788.83 | 73.61
KWH | 0 | 0 | 0 | 4063500 | 0 | 1711409 | 0 | 9763200 | 0 |  | 0 | 9641000 | 6797295 | 495360 | 904351 | 669597 | 7754349 | 0 | 0 | 879360 | 1097856 | 1403520 | 25001 | 0 | 0 | 0 | 616680 | 660677 | 596390 | 0 | 506000 | 147600 | 717200 | 466000 | 317280 | 0 | 0 | 732000 | 2700000 | 0 | 63498 | 4995047 | 0 | 0 | 0 |  | 388560 | 658848 | 504976 | 0 | 295680 | 99360 | 181536 | 497760 | 0 | 0 | 0 | 7432100 | 6898000 | 2006000 | 1973818 | 0 | 842184 | 1133760 | 0 | 1152304 | 0 | 561440 | 724099 | 0 | 0 | 667900 | 96140 | 2045760 | 2211840 | 0 | 0 | 16300 | 974000 | 681480 | 922800 | 727416 | 2393673 | 0 | 1280640 | 0 | 0 | 4762140 | 124000 | 0 | 0 | 7127500 | 436248 | 121872 | 0 | 900764 | 0 | 0 | 1773600 | 0 | 1810944 | 59670 | 946560 | 2408160 | 122109 | 8305000 | 1567200 | 868800 | 161416 | 31441 | 301091 | 114481 | 311126 | 1852500 | 955920 | 966720 | 8000500 | 612480 | 343630 | 1101600 | 839291 | 0 | 714960 | 193934 | 1296960 | 0 | 6813800 | 518545 | 0 | 6512726 | 432000 | 13076363 | 9253181 | 8640909 | 428218 |  | 20418909 | 0 | 8745696 | 0 | 0 | 0 | 0 | 0 | 112320 | 143616 | 0 | 2515000 | 170609 | 234912 | 0 | 0 | 1060000 | 251475 | 94777 | 431536 | 0 | 73990 | 217580 | 16190 | 173270 | 0 | 0 | 244152 | 1686109 | 0 | 5574000 | 0 | 0 | 149800 | 0 | 4530045 | 0 | 0 | 0 | 4352782 | 0 | 8857090 | 688800 | 0 | 769728 | 0 | 1375526 | 0 | 48538 | 343488 | 24264400 | 4827491 | 0 | 37200 | 35520 | 689040 | 1385856 | 0 | 0 | 7381818 | 230215 | 4669100 | 19925454 | 1406810 | 0 |  | 189900903 | 128132842 | 318033745 | 104545751 | 20418909 | 65828015 | 0 | 32386121 | 83089970 | 732000 | 0 | 5071903 | 2045760 | 3483316 | 432000 | 0
Fuel Cost | 0 | 0 | 0 | 18082575 | 0 | 6537582.38 | 0 | 28118016 | 0 |  | 0 | 30658380 | 23246748.9 | 9788313.6 | 16911363.7 | 11798299.14 | 23650764.45 | 0 | 0 | 17376153.6 | 19706515.2 | 27256358.4 | 466268.65 | 0 | 0 | 0 | 11260576.8 | 10412269.52 | 10907973.1 | 0 | 379500 | 0 | 0 | 0 | 5682484.8 | 0 | 0 | 0 | 14742000 | 0 | 1202652.12 | 15934199.93 | 0 | 0 | 0 |  | 6834770.4 | 11602313.28 | 9044120.16 | 0 | 5786457.6 | 1635465.6 | 675313.92 | 0 | 0 | 0 | 0 | 20735559 | 21107880 | 6659920 | 6612290.3 | 0 | 2838160.08 | 4965868.8 | 0 | 4620739.04 | 0 | 10055390.4 | 13077227.94 | 0 | 0 | 2484588 | 72105 | 13420185.6 | 6878822.4 | 0 | 0 | 0 | 3798600 | 2541920.4 | 4198740 | 3309742.8 | 8186361.66 | 0 | 7107552 | 0 | 0 | 13286370.6 | 815920 | 0 | 0 | 22023975 | 327186 | 92622.72 | 0 | 18375585.6 | 0 | 0 | 34070856 | 0 | 31890723.84 | 0 | 16858233.6 | 41781576 | 2024567.22 | 22008250 | 29870832 | 16298688 | 2895803.04 | 0 | 4922837.85 | 2225510.64 | 5581600.44 | 35401275 | 18554407.2 | 17217283.2 | 21281330 | 10455033.6 | 0 | 20148264 | 14083302.98 | 0 | 12776335.2 | 0 | 23371219.2 | 0 | 20236986 | 7301113.6 | 0 | 45393700.22 | 0 | 77150541.7 | 0 | 0 | 0 |  | 57377134.29 | 0 | 25799803.2 | 0 | 0 | 0 | 0 | 0 | 2112739.2 | 2701416.96 | 0 | 7947400 | 808686.66 | 4049882.88 | 0 | 0 | 5172800 | 4503917.25 | 1739157.95 | 7254120.16 | 0 | 1410989.3 | 3896857.8 | 286563 | 3103265.7 | 0 | 0 | 184823.064 | 18597782.27 | 0 | 47044560 | 0 | 0 | 494340 | 0 | 15085049.85 | 0 | 0 | 0 | 14494764.06 | 0 | 25862702.8 | 11764704 | 0 | 15256008.96 | 0 | 27400477.92 | 0 | 0 | 6814801.92 | 157233312 | 15013497.01 | 0 | 719820 | 0 | 0 | 24044601.6 | 0 | 0 | 53887271.4 | 0 | 34784795 | 131707250.94 | 0 | 0 |  | 1071091020.12 | 728555297.144 | 1799646317.264 | 323035121.674 | 57377134.29 | 156045315.35 | 0 | 593398575.96 | 565799213.53 | 0 | 0 | 90570770.86 | 13420185.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 407 | 0 |  | 0 | 420 | 301 | 50 | 51 | 15 | 315 | 0 | 0 | 64 | 41 | 80 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 13 | 0 | 33 | 32 | 16 | 0 | 0 | 30 | 115 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 0 | 0 | 0 | 0 | 10 | 13 | 0 | 0 | 0 | 280 | 305 | 0 | 92 | 0 | 33 | 46 | 0 | 51 | 0 | 23 | 25 | 0 | 0 | 32 | 0 | 116 | 74 | 0 | 0 | 2 | 40 | 28 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 195 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 129 | 8 | 49 | 100 | 5 | 322 | 48 | 35 | 0 | 4 | 16 | 0 | 10 | 52 | 45 | 48 | 380 | 16 | 47 | 17 | 35 | 0 | 34 | 27 | 34 | 0 | 315 | 17 | 0 | 265 | 50 | 316 | 450 | 350 | 62 |  | 930 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 163 | 0 | 345 | 0 | 0 | 0 | 0 | 59 | 0 | 7 | 0 | 860 | 220 | 0 | 0 | 4 | 94 | 55 | 0 | 0 | 305 | 32 | 200 | 954 | 192 | 0 |  | 13172 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 77 | 0 | 407 | 0 |  | 0 | 450 | 306 | 79 | 60 | 40 | 319 | 0 | 0 | 65 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 21 | 15 | 33 | 32 | 16 | 0 | 0 | 30 | 111 | 0 | 5 | 210 | 0 | 0 | 0 | 0 | 18 | 56 | 34 | 0 | 48 | 6 | 9 | 40 | 0 | 0 | 0 | 295 | 300 | 190 | 8 | 0 | 35 | 49 | 0 | 51 | 0 | 39 | 51 | 0 | 0 | 32 | 12 | 104 | 120 | 0 | 0 | 0 | 42 | 29 | 50 | 37 | 112 | 0 | 59 | 0 | 0 | 162 | 18 | 0 | 0 | 310 | 24 | 8 | 0 | 45 | 0 | 0 | 107 | 0 | 132 | 0 | 62 | 120 | 3 | 365 | 99 | 105 | 17 | 0 | 16 | 0 | 17 | 114 | 66 | 60 | 340 | 50 | 0 | 162 | 72 | 0 | 42 | 0 | 96 | 0 | 275 | 54 | 0 | 270 | 2 | 424 | 470 | 480 | 0 |  | 645 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 1 | 16 | 0 | 0 | 50 | 0 | 16 | 85 | 0 | 0 | 40 | 0 | 22 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 195 | 0 | 414 | 48 | 0 | 56 | 0 | 85 | 0 | 0 | 35 | 920 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 307 | 0 | 292 | 1173 | 0 | 0 |  | 14929 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 |  | 0 | 450 | 310 | 100 | 100 | 40 | 335 | 0 | 0 | 80 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 18 | 33 | 33 | 16 | 0 | 0 | 30 | 118 | 0 | 25 | 211 | 0 | 0 | 0 |  | 22 | 64 | 51 | 0 | 90 | 6 | 5 | 25 | 0 | 0 | 0 | 300 | 280 | 205 | 90 | 0 | 34 | 50 | 0 | 51 | 0 | 41 | 52 | 0 | 0 | 33 | 20 | 151 | 100 | 0 | 0 | 0 | 43 | 28 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 162 | 17 | 0 | 0 | 300 | 25 | 5 | 0 | 300 | 0 | 0 | 108 | 0 | 149 | 0 | 60 | 120 | 6 | 400 | 97 | 105 | 34 | 0 | 16 | 54 | 34 | 114 | 75 | 70 | 340 | 53 | 0 | 162 | 72 | 0 | 42 | 0 | 95 | 0 | 350 | 163 | 0 | 270 | 40 | 400 | 500 | 450 |  |  | 655 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 50 | 38 | 25 | 95 | 0 | 42 | 50 | 8 | 33 | 0 | 0 | 11 | 75 | 0 | 230 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 414 | 90 | 0 | 113 | 0 | 85 | 0 | 0 | 95 | 1244 | 220 | 0 | 27 | 0 | 0 | 115 | 0 | 0 | 375 | 0 | 307 | 1200 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 | 0 | 0 | 450 | 310 | 25 | 25 | 40 | 335 | 0 | 0 | 60 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 18 | 33 | 33 | 16 | 0 | 0 | 30 | 118 | 0 | 8 | 211 |  | 0 | 0 | 0 | 12 | 40 | 35 | 0 | 20 | 6 | 5 | 5 | 0 | 0 | 0 | 180 | 250 | 205 | 90 | 0 | 34 | 50 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 33 | 20 | 146 | 100 | 0 | 0 | 1.6 | 43 | 28 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 162 | 17 | 0 | 0 | 300 | 25 | 5 | 0 | 210 | 0 | 0 | 56 | 0 | 52 | 20 | 36 | 100 | 6 | 400 | 50 | 35 | 17 | 5 | 16 | 17 | 17 | 70 | 36 | 40 | 340 | 17 | 50 | 90 | 35 | 0 | 17 | 35 | 54 | 0 | 350 | 54 | 0 | 270 | 40 | 300 | 500 | 360 | 33 |  | 945 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 25 | 44 | 0 | 130 | 10 | 48 | 0 | 0 | 50 | 38 | 0 | 50 | 0 | 42 | 40 | 8 | 23 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 180 | 0 | 414 | 90 | 0 | 35 | 0 | 56 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 375 | 30 | 200 | 1200 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 401 | 0 | 0 | 0 | 370 | 280 | 8 | 17 | 15 | 324 | 0 | 0 | 8 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 10 | 0 | 22 | 18 | 25 | 32 | 8 | 0 | 0 | 30 | 118 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 12 | 25 | 0 | 0 | 19 | 6 | 5 | 2 | 0 | 0 | 0 | 180 | 150 | 205 | 0 | 0 | 35 | 46 | 0 | 51 | 0 | 33 | 25 | 0 | 0 | 32 | 17 | 96 | 111 | 0 | 0 | 1 | 41 | 29 | 50 | 40 | 80 | 0 | 60 | 0 | 0 | 162 | 17 | 0 | 0 | 265 | 22 | 8 | 0 | 80 | 0 | 0 | 58 | 0 | 30 | 0 | 49 | 102 | 6 | 366 | 49 | 35 | 17 | 3 | 16 | 17 | 17 | 70 | 37 | 50 | 340 | 16 | 19 | 17 | 35 | 0 | 5 | 12 | 19 | 0 | 365 | 17 | 0 | 270 | 0 | 573 | 350 | 300 | 36 | 0 | 925 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 22 | 0 | 0 | 10 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 155 | 0 | 300 | 74 | 0 | 18 | 0 | 34 | 0 | 2 | 35 | 760 | 220 | 0 | 0 | 1 | 43 | 36 | 0 | 0 | 308 | 6 | 200 | 746 | 28 | 0 | 0 |  |  |  | 170373766 | 20418909 | 0 | 83089970 | 37458024 | 2045760 | 3483316 | 432000 | 732000 |  |  | 318033745
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 | [5 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 170.3738 | 20.4189 | 0 | 83.09 | 37.458 | 2.0458 | 3.4833 | 0.432 | 0.732
| Minimum Generation |  | 11149 | 8:00
| Highest Generation |  | 14994 | 22:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 318.0337
| Day Peak Generation |  | 13172 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 14929 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 930 | 7:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 645 | 21:00
| Load factor L.F |  | 88.38% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-04
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13172 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 12323
Evening Peak Generation : |  |  | 14929 | MW Hour : | 21:00 | Available Max Generation : |  | 16951
E.P. Demand (at gen end) : |  |  | 15075 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15500
Maximum Generation : |  |  | 14994 | MW Hour : | 22:00 | Reserve(Generation end) |  | 1451
Total Gen. (MKWH) : |  |  | 318.0337 | System Load Factor : | 88.38% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 185 | MW at | 6:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-04
Actual : |  | 0 | Ft.(MSL) , | Rule curve : | 81.43 | Ft.( MSL )
Gas Consumed : |  | Total = | 1253.33 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 479080437.024
: |  |  | Coal : | 565799213.53 | Oil : | 683969346.82 | Total : | 1728848997.374
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5342.4914 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1476.7776 |  |  | 0 | 0%
Mymensingh Area |  | 139 | 3336:00 | 1099.0436 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 1004.2252 |  |  | 0 | 0%
Total |  | 139 |  | 15383.887 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:23 | 15:09 | Naogaon-Niyamatpur 132kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to Emergency maintenance work.
| 08:44 | Coxsbazar 132/33kV S/S Main Bus is restored.
| 08:45 | Maniknagar-Matuail 132kV Ckt-1 is restored.
| 09:42 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
| 09:42 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
09:54 | 19:58 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-2 Scheduled S/D Due to Project work.
09:54 | 19:58 | Haripur 230/132kV S/S 132kV Reserve Bus Sec-1 Scheduled S/D Due to Project work.
09:55 | 20:50 | Haripur 230/132kV S/S 132kV Bus Coupler Scheduled S/D Due to Project work.
10:03 | 18:29 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Scheduled S/D Due to Another side by NLDC.
10:42 | 16:49 | Rampur 230/132/33 S/S Halishahar-1 Project Work S/D Due to p/w
10:43 | 16:38 | Rampur 230/132/33 S/S 132kV BUS-02 Project Work S/D Due to p/w
11:07 | 11:36 | HVDC Bheramera- Rajshahi 230kV Ckt-2 Forced S/D from BIPTC end Due to Only line breaker shutdown for sf6 alarm
11:40 |  | Sikalbaha-TKCL 132kV Ckt-1 Forced S/D from Shikalbaha 230/132kV end.
12:00 |  | Day Peak Generation = 13,173MW
| 12:59 | Baroirhat-Hathazari 132 kV Ckt-1 is restored.
13:07 | 15:47 | BIPTC S/S 10CF23 Tripped showing - relays.
13:43 | 13:59 | Joypurhat 132/33kV S/S Transformer T-2 (417 T) LT Tripped showing Maicom P127 tIe>>> Phase |  |  |  |  | 9.0MW load interrup.
A 2.94kA IA 2.94kA In 2.94kA relays Due to 33 kV Feeder CB to CT Jumper out and touch E76
Ground
13:43 | 13:58 | Joypurhat 132/33kV S/S Transformer T-1 (407 T) LT Tripped showing Maicom P127 tIe>>> Phase |  |  |  |  | 9.0MW load interrup.
A 2.94kA IA 2.94kA In 2.94kA relays Due to 33 kV Feeder CB to CT Jumper out and touch
Ground
| 14:13 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
14:27 | 19:03 | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to High temperature junction point
maintenance.
14:32 |  | Ashuganj CCPP 225MW GT was sync. at 14:32 hrs.
14:32 |  | Ashuganj CCPP 225 MW Syncronized with remarks:- GT
14:42 | 15:20 | Narshingdi 132/33kV S/S T-1 HT Scheduled S/D Due to T-1, 33KV Incoming City (R-Phase) Loop Terminal Point Oil
Leakage Maintenance Work .
14:42 | 15:20 | Narshingdi 132/33kV S/S T-1 LT Scheduled S/D Due to T-1, 33KV Incoming City (R-Phase) Loop Terminal Point Oil |  |  |  |  | 40.0MW load interrup.
Leakage Maintenance Work .
14:54 | 15:47 | BIPTC S/S 10CF23 Scheduled S/D Due to Tripped by ACFM1P response phase C and element failure. A dead bird is
spotted.
| 17:37 | Baroirhat-Hathazari 132 kV Ckt-2 is restored.
17:45 |  | Ashuganj CCPP 225MW ST was sync. at 17:45 hrs.
21:00 |  | Evening Peak Generation : 14929 MW
| 21:02 | Haripur-Sonargaon 132kV Ckt-1 is restored.
| 21:03 | Haripur-Sonargaon 132kV Ckt-2 is restored.
22:48 |  | Baghabari 71 MW GTPP Tripped
23:12 |  | Meghnaghat Summit CCPP 305MW GT2 tripped due to GBC trip.
23:20 |  | Adani Power Jharkhand Ltd. unit-1 was shutdown
00:32 | 01:12 | Hathazari 230/132/33kV S/S Raojan-02 Tripped showing b ph distance relays.
00:33 | 00:46 | Cox'sbazar-Dohazari 132 kV Ckt-1 Tripped from Coxsbazar 132/33kV end showing Siemens relays. and from Dohazari |  |  |  |  | 120.0MW load interrup.
Coxsbazar 132/33kV end
132/33kV end showing Distance relays Due to storm weather
00:35 | 00:43 | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Dohazari 132/33kV end showing Distance relays Due to Storm weather
00:39 | 00:49 | Ashuganj-Brahmanbaria 132kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Distance, Zone-1, 7.429 km, Ib=2.42
kA, Ic=2.45 kA relays.
00:48 | 01:24 | Bakulia-Sikalbaha 132 kV Ckt-2 Tripped from Shikalbaha 230/132kV end showing FN1 relays. and from Bakulia 132/33kV
end showing Distance Relay relays Due to thunderstorm.
01:03 |  | Ashuganj South 360MW ST tripped due to CW pump trip.
01:22 |  | Ashuganj 420 MW CCPP(East) ST tripped due to CW pump trip.
03:12 |  | Ashuganj 420 MW CCPP(East) ST was sync.
03:32 |  | Ashugonj North 360MW ST was forced shutdown due to water intake level low.
04:33 |  | Meghnaghat CCPP(Summit) Syncronized with remarks:- GT2
04:48 | 05:05 | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Coxsbazar 132/33kV end showing Siemens relays. and from Dohazari
132/33kV end showing Zone 1 relays Due to Storm weather
06:16 |  | Bogura(New)-Naogaon 132 kV Ckt-2 Scheduled S/D from Naogaon 132/33kV end Due to Project work (Bogura 230KV S/S Side) |  |  |  |  | 60.0MW load interrup under Naogaon
132/33kV& Joypurhat 132/33kV end
and from Bogura 230/132kVend.
06:16 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Naogaon 132/33kV end Due to Project work (Bogura 230KV S/S Side) |  |  |  |  | 60.0MW load interrup under Naogaon
132/33kV& Joypurhat 132/33kV end
and from Bogura 230/132kVend.
06:31 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Bypass Insulatot & Operating Finger Maintenance of Nobogram 33 |  |  |  |  | 22.0MW load interrup.
Feeder
06:31 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Bypass Insulatot & Operating Finger Maintenance of Nobogram 33 |  |  |  |  | 22.0MW load interrup.
Feeder
07:00 |  | Minimum generation 12323 MW
07:23 |  | Bogura 230/132kV S/S 132KV Main 1 Scheduled S/D Due to project work
07:42 |  | Sylhet (South) S/S Trafo-2 LT Scheduled S/D Due to 33 kv bus section 2 maintenance work for PDB
07:42 |  | Sylhet (South) S/S Trafo-2 HT Scheduled S/D Due to 33 kv bus section 2 maintenance work for PDB
07:54 |  | Bogura 230/132kV S/S 230KV Main 1 Scheduled S/D Due to project work
21:12 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Tripped showing
lockout relay relays Due to CT of 33kV was damage
06:02 |  | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to
33 kV Bus coupler rearrange
06:03 |  | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to
33 kV Bus coupler rearrange
07:00 |  | Minimum generation 12387 MW
07:02 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
33kV Underground Cable Replace
07:11 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
33kV Underground Cable Replace
07:17 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to
33kV Busbar Maintenance
07:18 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to
33kV Busbar Maintenance
07:40 |  | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
Maintenance Work
07:40 |  | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
Maintenance Work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4063500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 77 | 1711409 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 407 | 9763200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9641000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 79 | 495360 | low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 306 | 6797295 | Meghna Bus section Over Load
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 60 | 904351 | low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 669597 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 25001 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 65 | 879360 | low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 319 | 7754349
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 1097856 | low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 616680
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1403520
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 660677
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 596390
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 36 | 653600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 717200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 466000
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 317280 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 900764 | low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1810944 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 868800
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 50 | 612480 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1101600
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 193934
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 470 | 9253181 | Meghna Bus section Over Load
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 480 | 8640909 | On test.
| Dhaka area Total |  |  |  | 5332 | 3888 | 72616237
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 111 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 5 | 63498 | low demand
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 59670
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 99360 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 732000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 210 | 4995047
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 161416 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 56 | 658848 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 504976 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired from 17/04/2024
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 946560 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 9 | 181536 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 497760
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 48 | 295680 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31441
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 301091 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 114481
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 311126 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 966720 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 839291 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 54 | 518545 | low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 270 | 6512726 | Madunaghat Transformer Over Load
| Cox's Bazar Wind |  | IPP | 66 | 60 | 2 | 432000 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 424 | 13076363
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 428218
| Chattogram area Total |  |  |  | 4404 | 1543 | 35428353
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 190 | 2006000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7432100 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6898000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 275 | 6813800 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 842184 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 49 | 1133760
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1973818 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1152304
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 3 | 122109 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 561440 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2408160 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 104 | 2045760
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 667900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 51 | 724099
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 96140 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1852500
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 66 | 955920 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 42 | 714960
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1296960 | Engine problem
| Cumilla Area Total |  |  |  | 2929 | 1882 | 39697914
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 120 | 2211840 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 16300
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 107 | 1773600 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1567200 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 343630
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 388560 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 344 | 6301130
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 974000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 681480 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2393673 | ST under maint
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 922800
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 37 | 727416 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 121872 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1280640
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 4762140 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 124000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 436248
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7127500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8305000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8000500 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1556 | 35857269
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 645 | 20418909
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 112320 | low demand
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 143616 | low demand
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8745696 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 48 | 688800 | low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 689040
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 307 | 7381818
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1345 | 38180199
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 234912 | low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 1 | 170609 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2515000 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 920 | 24264400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4827491
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 37200 | low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 292 | 4669100
| Barisal Area Total |  |  |  | 2235 | 1579 | 36718712
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1060000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 251475 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 16 | 94777 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 73990 | low demand
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 217580 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 149800 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 195 | 4530045
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 195 | 4352782 | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8857090
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 173270 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244152
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 16190
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 431536 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 56 | 769728 | low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 343488 | low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35520
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1173 | 19925454
| Rajshahi Area Total |  |  |  | 3431 | 2292 | 41526877
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1686109
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5574000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 85 | 1375526 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 48538
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1385856
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 230215
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1406810
| Rangpur Area Total |  |  |  | 950 | 500 | 11707054
| Total |  |  |  | 25903 | 14929 | 318033745
| Eastern Grid Total |  |  |  | 15588 | 9213 | 189900903
| Western Grid Total |  |  |  | 10315 | 5716 | 128132842
| National Grid Total |  |  |  | 25903 | 14929 | 318033745
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-03
| (a) ENTIRE EASTERN GRID : |  | 9401.39 | MW | (b) ENTIRE WESTERN GRID : |  | 4947.4 | MW
| i) Dhaka area |  | 4963.89 | MW | i) Khulna area |  | 1871 | MW
| ii) Chittagong area |  | 1397.5 | MW | ii) Rajshahi area |  | 1694.4 | MW
| iii) Comilla area |  | 1341 | MW | iii) Barisal area |  | 423 | MW
| iv) Mymensingh area |  | 1217 | MW | iv) Rangpur area |  | 959 | MW
| v) Sylhet area |  | 482 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14348.79 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 28 | 00:00 | Kalurghat | 34 | 09:00 | Narail | 67 | 00:00 | Shariatpur | 97 | 00:00
2 | AKSML | 13 | 13:00 | Chowmuhani | 252 | 21:00 | Kamrangirchar | 58.2 | 13:00 | Narinda | 82 | 13:00 | Sherpur | 162 | 21:00
3 | Aftabnagar | 46 | 00:00 | Chuadanga | 121 | 02:00 | Kaptai | N/A | N/A | Narshingdi | 167 | 19:30 | Shikalbaha | 26 | 18:30
4 | Agargaon | 127 | 12:00 | Coxsbazar | 135 | 18:30 | Kazla | 116 | 13:00 | Natore | 180 | 21:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 88 | 16:00 | Cumilla(N) | 186 | 05:00 | Keranigonj | 91 | 23:00 | Nawabganj | 58.3 | 23:00 | Shitalakhya | 110 | 13:00
6 | Amnura | 97 | 23:00 | Cumilla(S) | 183 | 15:00 | Khagrachori | 30 | 06:00 | Netrakona | 104 | 22:00 | Sholosohor | 47 | 16:00
7 | Ashuganj | 85 | 06:00 | Daudkandi | 154 | 18:30 | Khulna | 96 | 00:00 | New | 56.5 | 16:00 | Shyampur | 172 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 12:00 | Khulshi | 195 | 21:00 | Niamatpur | 123 | 19:30 | Siddhirganj | 118 | 15:00
9 | BSRM | 158 | 01:00 | Dhamrai | 134 | 18:30 | Kishoreganj | 148 | 19:30 | Noapara | 52 | 20:00 | Sirajganj | 130 | 19:30
10 | Bagerhat | 101 | 02:00 | Dhanmondi | 183 | 12:00 | Kodda | 275 | 21:00 | PHP | 9 | 18:00 | Sonargaon | 94 | 09:00
11 | Bakulia | 104 | 21:00 | Dohazari | 102 | 20:00 | Kulaura | 42 | 00:00 | Pabna | 126 | 20:00 | Sreemongol | 67 | 03:00
12 | Banani | 69.8 | 13:00 | Faridpur | 188 | 23:00 | Kurigram | 60 | 18:00 | Palashbari | 131 | 21:00 | Sreepur | 60 | 08:00
13 | Bangabhaban | 19 | 10:00 | Fatullah | 72 | 15:00 | Kushtia | 158 | 19:30 | Panchagarh | 56 | 19:00 | Srinagar | 54.5 | 23:00
14 | Barapukuria | 78 | 13:00 | Fenchuganj | 39 | 03:00 | Lalbag | 98 | 13:00 | Patuakhali | 100.5 | 23:00 | Sunamganj | 54 | 04:00
15 | Barguna | 24 | 22:00 | Feni | 126 | 20:00 | Lalmonirhat | 55 | 18:00 | Payra | 26 | 00:00 | Sylhet | 36 | 18:30
16 | Barishal | 127 | 23:00 | GPH | 79 | 11:00 | MI_Cement | 11.5 | 21:00 | Postogola | 66 | 23:00 | Sylhet-132 | 118 | 14:00
17 | Barishal-230 | 116 | 23:00 | Ghatail | 60 | 00:00 | Madanganj | 31 | 23:00 | Purbachal | 16 | 15:00 | TK | 30 | 20:00
18 | Baroaulia | 68 | 12:00 | Ghorashal | 81 | 11:00 | Madaripur | 128 | 23:00 | Purbasadipur | 143 | 13:00 | Tangail | 226 | 00:00
19 | Baroirhat | 60 | 20:00 | Goalpara | 38 | 00:00 | Madartek | 102.31 | 23:00 | Rahim | 33 | 09:00 | Thakurgaon | 102 | 21:00
20 | Bashundhara | 212 | 15:00 | Gollamari | 84 | 00:00 | Madunaghat | 49 | 00:00 | Rajbari | 86 | 00:00 | Tongi | 153 | 11:00
21 | BashundharaCement | 12 | 11:00 | Gopalganj | 122.4 | 00:00 | Magura | 75 | 23:00 | Rajendrapur | 112 | 21:00 | Ullahpara | 31 | 20:00
22 | Beanibazar | 53 | 21:00 | Gulshan | 160 | 13:00 | Mahasthangarh | 92 | 19:30 | Rajshahi | 178 | 23:00 | Ullon | 69 | 23:00
23 | Benapole | 82 | 20:00 | Halishahar | 87 | 12:00 | Manikganj | 145 | 21:00 | Rajshahi-230 | 57 | 00:00 | Uttara | 112 | 15:00
24 | Bhaluka | 108 | 19:30 | HaripurSBU | 162 | 09:00 | Maniknagar | 90 | 13:00 | Ramganj | 118 | 22:00 | UttaraNew | 40 | 23:00
25 | Bhandaria | 57 | 23:00 | Hasnabad | 104 | 19:00 | Matarbari | 40 | 21:00 | Rampur | 32 | 21:00 | Zigatola | 100 | 13:00
26 | Bhangura | 53 | 21:00 | Hathazari | 69 | 23:00 | Matuail | 78 | 11:00 | Rangamati | 13 | 05:00
27 | Bheramara(GK) | 73 | 19:30 | Ishurdi | 85 | 19:30 | Millgate | 130 | 12:00 | Rangpur | 144 | 13:00
28 | Bhulta | 219 | 16:00 | Jaldhaka | 85 | 20:00 | Mirpur | 165 | 23:00 | Ruppur | 7.2 | 15:00
29 | Bog-Sherpur | 78 | 19:30 | Jamalpur | 148 | 00:00 | Mirsorai | 9 | 21:00 | SSM | 3 | 01:00
30 | Bogura | 192 | 22:00 | Jashore | 163 | 21:00 | Mirzapur | 46 | 19:00 | Saidpur | 114 | 19:00
31 | Borhanuddin | 85 | 02:00 | Jhenaidah | 150 | 23:00 | Mithapukur | 61 | 18:30 | Satkhira | 145 | 22:00
32 | Brahmanbaria | 180 | 21:00 | Joydebpur | 203 | 20:00 | Modern | 0 | 00:00 | Satmasjid | 128 | 16:00
33 | Cantonment | 186 | 00:00 | Joypurhat | 84 | 23:00 | Mogbazar | 153.6 | 16:00 | Savar | 222 | 09:00
34 | Chandpur | 81 | 23:00 | Juldah | 17 | 18:30 | Mongla | 40 | 11:00 | SevenRings | 17.54 | 20:00
35 | Chandraghona | 27 | 00:00 | KSRM | 34 | 08:00 | Motijheel | 61 | 13:00 | ShahCement | 27 | 05:00
36 | Chapai | 83 | 00:00 | Kabirpur | 274 | 20:00 | Munshiganj | 116 | 00:00 | Shahjadpur | 99 | 00:00
37 | Charsaidpur | 47 | 16:00 | Kachua | 93 | 22:00 | Mymensingh | 249 | 19:00 | Shahjibazar | 127 | 21:00
38 | Chauddagram | 80 | 05:00 | Kallyanpur | 135 | 23:00 | Naogaon | 161 | 22:00 | Shahmirpur | 58 | 19:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 394 | 07:00 | 386 | 10:00 | Kaliakoir | 374 | 19:00 | 358 | 10:00
| Ashuganj | 408 | 24:00 | 391 | 10:00 | Madunaghat_I | 398 | 20:00 | 393 | 10:00
| Bhulta | 399 | 04:00 | 386 | 10:00 | Meghnaghat | 392 | 7:00 | 385 | 11:00
| Bibiana | 398 | 21:00 | 389 | 10:00 | Payra | 413 | 09:00 | 405 | 23:00
| BIPTC | 406 | 02:00 | 390 | 17:00 | Rahanpur | 410 | 15:00 | 390 | 02:00
| Bogura | 407 | 16:00 | 389 | 07:00 | Rampal | 404 | 09:00 | 393 | 22:00
| Gopalganj | 401 | 06:00 | 393 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 04:00 | 217 | 10:00 | Hasnabad | 228 | 00:00 | 219 | 10:00
| AKSML | 227 | 19:30 | 217 | 06:00 | Hathazari | 228 | 21:00 | 220 | 10:00
| Aminbazar | 226 | 21:00 | 212 | 19:00 | Ishurdi | 227 | 21:00 | 220 | 05:00
| Ashuganj | 234 | 00:00 | 227 | 10:00 | Jhenaidah | 236 | 18:30 | 229 | 19:00
| Ashuganj-400 | 232 | 7:00 | 225 | 4:00 | Kaliakoir | 226 | 09:00 | 215 | 19:00
| Baghabari | 231 | 17:00 | 224 | 10:00 | Keranigonj | 227 | 18:00 | 216 | 10:00
| Barapukuria | 215 | 15:00 | 204 | 07:00 | Khulna(S) | 225 | 03:00 | 217 | 10:00
| Barapukuria-230 | 215 | 15:00 | 204 | 7:00 | Madunaghat_I | 229 | 07:00 | 218 | 19:00
| Barishal | 239 | 05:00 | 230 | 00:00 | Maniknagar | 227 | 20:00 | 221 | 10:00
| Bheramara | 234 | 00:00 | 226 | 19:00 | Meghnaghat | 228 | 21:00 | 218 | 10:00
| Bhulta | 229 | 04:00 | 219 | 10:00 | Meghnaghat-400 | 236 | 19:00 | 230 | 07:00
| Bibiana | 230 | 18:00 | 224 | 10:00 | Mirsorai | 230 | 10:00 | 216 | 8:00
| BIPTC | 236 | 18:30 | 226 | 19:00 | Rajshahi | 230 | 22:00 | 216 | 08:00
| Bogura | 222 | 16:00 | 211 | 07:00 | Rampal | 234 | 09:00 | 223 | 19:00
| Bogura-400 | 222 | 16:00 | 212 | 07:00 | Rampur | 229 | 06:00 | 220 | 19:00
| Borhanuddin | 241 | 04:00 | 235 | 09:00 | Rampura | N/A | N/A | N/A | N/A
| BSRM | 228 | 21:00 | 218 | 06:00 | Shikalbaha | 228 | 21:00 | 217 | 11:00
| Cumilla(N) | 230 | 21:00 | 221 | 10:00 | Shyampur | 223 | 18:00 | 218 | 02:00
| Fenchuganj | 234 | 17:00 | 228 | 11:00 | Siddhirganj | 229 | 22:00 | 219 | 10:00
| Ghorashal | 230 | 00:00 | 225 | 10:00 | Sirajgonj | 231 | 21:00 | 222 | 10:00
| Ghorashal-230 | 228 | 04:00 | 222 | 11:00 | Sreepur | 235 | 18:00 | 231 | 08:00
| GPH | 226 | 19:30 | 218 | 08:00 | Tongi | 228 | 00:00 | 27 | 04:00
| Haripur | 228 | 09:00 | 219 | 00:00 |  | 226 | 22:00 | 212 | 08:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 130 | 03:00 | 123 | 10:00 | Kushtia | 135 | 09:00 | 129 | 19:00
| Agargaon | 135 | 03:00 | 129 | 10:00 | Lalbag | 136 | 03:00 | 130 | 10:00
| Agrabad | 133 | 19:30 | 127 | 07:00 | Lalmonirhat | 125 | 15:00 | 114 | 07:00
| AKS | 130 | 18:00 | 126 | 05:00 | Madanganj | 133 | 20:00 | 124 | 10:00
| Aminbazar | 136 | 02:00 | 125 | 22:00 | Madaripur | 134 | 09:00 | 129 | 00:00
| Amnura | 136 | 18:30 | 120 | 00:00 | Madartek | 130 | 03:00 | 122 | 10:00
| Ashuganj | 137 | 01:00 | 135 | 10:00 | Madunaghat | 132 | 09:00 | 127 | 03:00
| Bagerhat | 135 | 09:00 | 119 | 13:00 | Magura | 137 | 09:00 | 126 | 19:00
| Bakulia | 135 | 04:00 | 130 | 01:00 | Mahasthangarh | 130 | 15:00 | 120 | 03:00
| Banani | 133 | 04:00 | 124 | 10:00 | Manikganj | 133 | 23:00 | 123 | 10:00
| Bangabhaban | 132 | 01:00 | 124 | 10:00 | Maniknagar | 132 | 00:00 | 124 | 10:00
| Barapukuria | 132 | 15:00 | 123 | 07:00 | Matarbari | 127 | 08:00 | 108 | 01:00
| Barguna | 138 | 12:00 | 124 | 23:00 | Matuail | 133.2 | 21:00 | 125 | 10:00
| Barishal | 136 | 05:00 | 120 | 23:00 | Millgate | 131 | 03:00 | 121 | 10:00
| Barishal-230 | 138 | 05:00 | 130 | 00:00 | Mirpur | 134 | 02:00 | 129 | 10:00
| Baroaulia | 133 | 18:00 | 127 | 08:00 | Mirzapur | 134 | 23:00 | 125 | 10:00
| Baroirhat | 130 | 17:00 | 120 | 05:00 | Mithapukur | 125 | 17:00 | 115 | 06:00
| Bashundhara | 133 | 02:00 | 120 | 10:00 | MI_Cement | 134 | 19:30 | 125 | 10:00
| BashundharaCement | 133 | 20:00 | 124 | 10:00 | Modern | 133 | 04:00 | 130 | 00:00
| Beanibazar | 132 | 09:00 | 127 | 00:00 | Mogbazar | 131 | 03:00 | 124 | 11:00
| Benapole | 134 | 09:00 | 122 | 19:00 | Mongla | 134 | 09:00 | 124 | 14:00
| Bhaluka | 124 | 00:00 | 118 | 10:00 | Motijheel | 132 | 01:00 | 124 | 10:00
| Bhandaria | 134 | 18:00 | 114 | 23:00 | Munshiganj | 133 | 19:30 | 124 | 10:00
| Bhangura | 133 | 18:30 | 129 | 07:00 | Mymensingh | 134 | 23:00 | 114 | 14:00
| Bheramara | 135 | 06:00 | 131 | 19:00 | Naogaon | 126 | 15:00 | 115 | 04:00
| Bheramara(GK) | 136 | 04:00 | 132 | 19:00 | Narail | 136 | 06:00 | 125 | 19:00
| Bhulta | 127 | 23:00 | 115 | 10:00 | Narinda | 132 | 00:00 | 124 | 10:00
| Bog-Sherpur | 131 | 15:00 | 122 | 07:00 | Narshingdi | 127 | 00:00 | 118 | 09:00
| Bogura | 133 | 15:00 | 116 | 19:00 | Natore | 130 | 07:00 | 123 | 19:00
| Bogura-230 | 132 | 16:00 | 123 | 07:00 | Nawabganj | 135 | 00:00 | 131 | 10:00
| Brahmanbaria | 127 | 00:00 | 124 | 10:00 | Netrakona | 120 | 00:00 | 114 | 15:00
| Cantonment | 135 | 04:00 | 128 | 10:00 | New | 130 | 06:00 | 123 | 10:00
| Chandpur | 132 | 09:00 | 113 | 06:00 | Niamatpur | 136 | 14:00 | 127 | 04:00
| Chandraghona | 133 | 14:00 | 127 | 05:00 | Noapara | 136 | 07:00 | 126 | 22:00
| Chapai | 133 | 16:00 | 124 | 00:00 | Pabna | 132 | 09:00 | 128 | 19:00
| Charsaidpur | 134 | 21:00 | 125 | 10:00 | Palashbari | 155 | 10:00 | 114 | 03:00
| Chauddagram | 132 | 09:00 | 119 | 01:00 | Panchagarh | 131 | 15:00 | 112 | 07:00
| Chhatak | 130 | 09:00 | 127 | 00:00 | Patuakhali | 134 | 12:00 | 126 | 23:00
| Chowmuhani | 127 | 18:00 | 111 | 02:00 | Payra | 136 | 18:30 | 132 | 01:00
| Chuadanga | 131 | 09:00 | 117 | 19:00 | PHP | 131 | 18:30 | 112 | 01:00
| Coxsbazar | 126 | 14:00 | 113 | 03:00 | Postogola | 134 | 21:00 | 127 | 10:00
| Cumilla(N) | 135 | 21:00 | 127 | 05:00 | Purbachal | 133 | 03:00 | 121 | 10:00
| Cumilla(S) | 136 | 21:00 | 124 | 14:00 | Purbasadipur | 126 | 16:00 | 112 | 07:00
| Daudkandi | 136 | 19:30 | 116 | 10:00 | Rahanpur | 138 | 16:00 | 132 | 00:00
| Dhaka | 133 | 03:00 | 125 | 10:00 | Rahim | 133 | 19:30 | 126 | 10:00
| Dhamrai | 132 | 00:00 | 124 | 10:00 | Rajbari | 132 | 08:00 | 127 | 00:00
| Dhanmondi | 133 | 00:00 | 124 | 10:00 | Rajendrapur | 136 | 18:30 | 126 | 11:00
| Dohazari | 132 | 04:00 | 125 | 03:00 | Rajshahi | 131 | 07:00 | 125 | 19:00
| Faridpur | 133 | 08:00 | 126 | 00:00 | Rajshahi-230 | 135 | 18:30 | 119 | 00:00
| Fatullah | 138 | 12:00 | 126 | 10:00 | Ramganj | 127 | 13:00 | 113 | 01:00
| Fenchuganj | 133 | 07:00 | 131 | 01:00 | Rampur | 131 | 00:00 | 127 | 08:00
| Feni | 129 | 18:00 | 115 | 01:00 | Rampura | 133 | 03:00 | 124 | 10:00
| Ghatail | 132 | 23:00 | 120 | 11:00 | Rangamati | 133 | 20:00 | 125 | 06:00
| Ghorashal | 137 | 18:30 | 130 | 10:00 | Rangpur | 127 | 16:00 | 116 | 07:00
| Goalpara | 140 | 09:00 | 127 | 22:00 | Ruppur | 136 | 09:00 | 132 | 18:00
| Gollamari | 139 | 09:00 | 130 | 13:00 | Saidpur | 127 | 16:00 | 115 | 07:00
| Gopalganj | 135 | 09:00 | 127 | 22:00 | Satkhira | 134 | 09:00 | 121 | 22:00
| Gopalganj-400 | 134 | 06:00 | 130 | 00:00 | Satmasjid | 135 | 04:00 | 125 | 11:00
| Gulshan | 133 | 03:00 | 124 | 10:00 | Savar | 134 | 19:30 | 129 | 08:00
| Halishahar | 134 | 19:30 | 128 | 10:00 | SevenRings | 137 | 18:30 | 130 | 10:00
| Haripur | 133 | 00:00 | 126 | 10:00 | ShahCement | 134 | 21:00 | 125 | 10:00
| HaripurSBU | 133 | 19:30 | 126 | 10:00 | Shahjadpur | 138 | 23:00 | 132 | 10:00
| Hasnabad | 133 | 01:00 | 127 | 10:00 | Shahjibazar | 125 | 00:00 | 123 | 15:00
| Hathazari | 134 | 07:00 | 130 | 04:00 | Shahmirpur | 135 | 04:00 | 130 | 10:00
| Ishurdi | 137 | 18:30 | 132 | 00:00 | Shariatpur | 133 | 08:00 | 126 | 00:00
| Jaldhaka | 125 | 16:00 | 113 | 07:00 | Sherpur | 129 | 23:00 | 112 | 11:00
| Jamalpur | 132 | 23:00 | 117 | 13:00 | Shikalbaha | 124 | 19:30 | 119 | 10:00
| Jashore | 134 | 09:00 | 124 | 19:00 | Shikalbaha-230 | 135 | 19:00 | 132 | 01:00
| Jhenaidah | 137 | 05:00 | 128 | 19:00 | Shitalakhya | 134 | 18:30 | 125 | 10:00
| Jhenaidah-230 | 138 | 09:00 | 129 | 19:00 | Sholosohor | 133 | 20:00 | 127 | 07:00
| Joydebpur | 137 | 10:00 | 129 | 09:00 | Shyampur | 134 | 04:00 | 125 | 10:00
| Joypurhat | 123 | 15:00 | 109 | 05:00 | Shyampur-230 | 133 | 21:00 | 125 | 10:00
| Juldah | 135 | 18:00 | 131 | 02:00 | Siddhirganj | 133 | 20:00 | 126 | 10:00
| Kabirpur | 138 | 18:00 | 117 | 10:00 | Sirajganj | 129 | 00:00 | 124 | 10:00
| Kachua | 131 | 00:00 | 118 | 01:00 | Sonargaon | 135 | 19:30 | 122 | 10:00
| Kaliakoir | 138 | 18:00 | 130 | 10:00 | Sreemongol | 127 | 00:00 | 124 | 19:00
| Kallyanpur | 128 | 06:00 | 124 | 11:00 | Sreepur | 129 | 00:00 | 123 | 10:00
| Kalurghat | 134 | 19:30 | 127 | 08:00 | Srinagar | 136 | 03:00 | 130 | 10:00
| Kamrangirchar | 138 | 06:00 | 122 | 12:00 | SSM | 136 | 18:00 | 130 | 07:00
| Kaptai | 135 | 18:00 | 130 | 6:00 | Sunamganj | 129 | 18:00 | 124 | 04:00
| Kazla | 132 | 05:00 | 124 | 11:00 | Sylhet | 132 | 06:00 | 129 | 00:00
| Keranigonj | 137 | 03:00 | 131 | 10:00 | Sylhet-132 | 131 | 07:00 | 129 | 01:00
| Khagrachori | 133 | 18:00 | 125 | 06:00 | Tangail | 139 | 02:00 | 122 | 10:00
| Khulna | 137 | 07:00 | 128 | 13:00 | Thakurgaon | 129 | 19:30 | 111 | 07:00
| Khulna(S) | 139 | 07:00 | 130 | 13:00 | TK | 132 | 19:30 | 127 | 07:00
| Khulshi | 131 | 18:00 | 126 | 08:00 | Tongi | 133 | 07:00 | 125 | 09:00
| Kishoreganj | 131 | 13:00 | 122 | 10:00 | Ullahpara | 133 | 17:00 | 128 | 07:00
| Kodda | 136 | 18:00 | 123 | 11:00 | Ullon | 130 | 04:00 | 123 | 10:00
| KSRM | 134 | 19:30 | 128 | 05:00 | Uttara | 134 | 04:00 | 127 | 01:00
| Kulaura | 131 | 08:00 | 130 | 00:00 | UttaraNew | 134 | 04:00 | 128 | 01:00
| Kurigram | 128 | 15:00 | 112 | 07:00 | Zigatola | 137 | 06:00 | 131 | 10:00

## L-Curve
Date | 2024-05-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 342 | 8632 | 5522 | 14154 |  |  |  | QF-LDC-11
0:30 | 318 | 8445 | 5312 | 13757 | Date: | 2024-05-03
1:00 | 294 | 8258 | 5102 | 13360
1:30 | 278.5 | 8139 | 4975 | 13114
2:00 | 263 | 8020 | 4848 | 12868
2:30 | 238 | 7909 | 4885.5 | 12794.5 | [5 empty] | Gen. at Eve. Peak | 14929 | 14377 MW (21:00 )
3:00 | 213 | 7798 | 4923 | 12721 | [6 empty] | 21:00
3:30 | 229.5 | 7740.5 | 4875.5 | 12616 | [5 empty] | Gen. at Day Peak | 13172 | 11960 MW (12:00 )
4:00 | 246 | 7683 | 4828 | 12511 | [6 empty] | 12:00
4:30 | 217.5 | 7491 | 4770.5 | 12261.5 | [5 empty] | Highest Generation | 14994
5:00 | 189 | 7299 | 4713 | 12012 | [6 empty] | 22:00
5:30 | 187 | 7148 | 4630 | 11778
6:00 | 185 | 6997 | 4547 | 11544
6:30 | 199 | 6880 | 4486 | 11366
7:00 | 213 | 6763 | 4425 | 11188
7:30 | 280 | 6771.5 | 4397 | 11168.5
8:00 | 347 | 6780 | 4369 | 11149
8:30 | 422 | 6854.5 | 4522.5 | 11377
9:00 | 497 | 6929 | 4676 | 11605
9:30 | 597.5 | 7018 | 4798 | 11816
10:00 | 698 | 7107 | 4920 | 12027
10:30 | 703.5 | 7170.5 | 5075.5 | 12246
11:00 | 709 | 7234 | 5231 | 12465
11:30 | 733 | 7484 | 5334.5 | 12818.5
12:00 | 757 | 7734 | 5438 | 13172
12:30 | 688 | 7861.5 | 5563.5 | 13425
13:00 | 619 | 7989 | 5689 | 13678
13:30 | 756.5 | 7829 | 5595.5 | 13424.5
14:00 | 894 | 7669 | 5502 | 13171
14:30 | 920 | 7785 | 5525.5 | 13310.5
15:00 | 946 | 7901 | 5549 | 13450
15:30 | 942.5 | 7868.5 | 5563.5 | 13432
16:00 | 939 | 7836 | 5578 | 13414
16:30 | 894 | 7769 | 5497 | 13266
17:00 | 849 | 7702 | 5416 | 13118
17:30 | 775.5 | 7574 | 5181.5 | 12755.5
18:00 | 702 | 7446 | 4947 | 12393
18:30 | 551 | 8081 | 5262 | 13343
19:00 | 400 | 8716 | 5577 | 14293
19:30 | 398 | 9041 | 5805 | 14846
20:00 | 443 | 9060 | 5712 | 14772 |  |  |  | Executive Engineer
20:30 | 440.5 | 9136.5 | 5714 | 14850.5 |  |  |  | Network Operation Division
21:00 | 438 | 9213 | 5716 | 14929
21:30 | 433.5 | 9138 | 5823.5 | 14961.5
22:00 | 429 | 9063 | 5931 | 14994 |  |  |  |  | Page 6 of 7
22:30 | 421.5 | 9029.5 | 5887.5 | 14917
23:00 | 414 | 8996 | 5844 | 14840
23:30 | 378 | 8814 | 5683 | 14497
24:00 | 342 | 8632 | 5522 | 14154
14377 MW (21:00 )
11960 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-03 |  | Energy |  | 318033745
[15 empty] | 2024-05-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4553 | 646 | 2834 | 0 | 1961 | 3763 | 30 | 0 | 246 | 114 | 0 | 7 | 788.83
0:30 | 4489 | 645.5 | 2905 | 0 | 1646.5 | 3659 | 30 | 0 | 282 | 94 | 0 | 6 | 843.415 |  |  | Date: | 43953
1:00 | 4425 | 645 | 2976 | 0 | 1332 | 3555 | 30 | 0 | 318 | 74 | 0 | 5 | 898
1:30 | 4375.5 | 645 | 2943.5 | 0 | 1270 | 3492.5 | 30 | 0 | 302.5 | 52 | 0 | 3 | 798.5 | [9 empty] | Total Energy | 318.0337 | 318.0337 | Total Energy Gen 318.034 MKWHr Energy Not Served 9.586 MKWHr Energy Requirement 327.619 MKWHr
2:00 | 4326 | 645 | 2911 | 0 | 1208 | 3430 | 30 | 0 | 287 | 30 | 0 | 1 | 699 | [9 empty] | Energy not Served | 9.5857 | 9.5857
2:30 | 4358 | 787 | 2868 | 0 | 1123 | 3325.5 | 30 | 0 | 254 | 47 | 0 | 2 | 578 | [9 empty] | Energy Requirement | 327.6195 | 327.6195
3:00 | 4390 | 929 | 2825 | 0 | 1038 | 3221 | 30 | 0 | 221 | 64 | 0 | 3 | 457
3:30 | 4338 | 929 | 2836.5 | 0 | 1011.5 | 3224.5 | 30 | 0 | 180 | 62 | 0 | 4.5 | 414 | [8 empty] | Shortage
4:00 | 4286 | 929 | 2848 | 0 | 985 | 3228 | 30 | 0 | 139 | 60 | 0 | 6 | 371
4:30 | 4206 | 929 | 2787 | 0 | 916.5 | 3204.5 | 30 | 0 | 130.5 | 55 | 0 | 3 | 371
5:00 | 4126 | 929 | 2726 | 0 | 848 | 3181 | 30 | 0 | 122 | 50 | 0 | 0 | 371
5:30 | 4090.5 | 929 | 2638.5 | 0 | 793 | 3139.5 | 30 | 0 | 93.5 | 54 | 10 | 0 | 355.5
6:00 | 4055 | 929 | 2551 | 0 | 738 | 3098 | 30 | 0 | 65 | 58 | 20 | 0 | 340
6:30 | 4061.5 | 929.5 | 2500 | 0 | 627.5 | 3054 | 30 | 0 | 44 | 59 | 60.5 | 0 | 366.5 | [7 empty] | Coal
7:00 | 4068 | 930 | 2449 | 0 | 517 | 3010 | 30 | 0 | 23 | 60 | 101 | 0 | 393
7:30 | 4035 | 929.5 | 2457.5 | 0 | 528.5 | 2944.5 | 30 | 0 | 19.5 | 66 | 158 | 0 | 402.3025 | [6 empty] | Oil
8:00 | 4002 | 929 | 2466 | 0 | 540 | 2879 | 30 | 0 | 16 | 72 | 215 | 0 | 411.605
8:30 | 4032 | 929 | 2475 | 0 | 550.5 | 2984.5 | 30 | 0 | 24 | 77 | 275 | 0 | 408.74
9:00 | 4062 | 929 | 2484 | 0 | 561 | 3090 | 30 | 0 | 32 | 82 | 335 | 0 | 405.875
9:30 | 4036.5 | 929.5 | 2480 | 0 | 640 | 3175 | 30 | 0 | 57 | 85 | 383 | 0 | 385.82
10:00 | 4011 | 930 | 2476 | 0 | 719 | 3260 | 30 | 0 | 82 | 88 | 431 | 0 | 365.765
10:30 | 4134 | 929.5 | 2545 | 0 | 866 | 3110 | 30 | 0 | 82.5 | 92 | 438.5 | 18.5 | 371.495
11:00 | 4257 | 929 | 2614 | 0 | 1013 | 2960 | 30 | 0 | 83 | 96 | 446 | 37 | 377.225
11:30 | 4254.5 | 929.5 | 2681.5 | 0 | 1112.5 | 3081 | 30 | 0 | 117.5 | 106 | 462.5 | 43.5 | 383.4325
12:00 | 4252 | 930 | 2749 | 0 | 1212 | 3202 | 30 | 0 | 152 | 116 | 479 | 50 | 389.64
12:30 | 4208 | 929 | 2795.5 | 0 | 1270.5 | 3374 | 30 | 0 | 182 | 118 | 470 | 48 | 387.73
13:00 | 4164 | 928 | 2842 | 0 | 1329 | 3546 | 30 | 0 | 212 | 120 | 461 | 46 | 385.82
13:30 | 4164 | 928 | 2842 | 0 | 1329 | 3546 | 30 | 0 | 212 | 120 | 461 | 46 | 385.82
14:00 | 4164 | 928 | 2842 | 0 | 1329 | 3546 | 30 | 0 | 212 | 120 | 461 | 46 | 385.82
14:30 | 4223 | 928.5 | 2820.5 | 0 | 1334 | 3485.5 | 30 | 0 | 185 | 120 | 391.5 | 46 | 407.785
15:00 | 4282 | 929 | 2799 | 0 | 1339 | 3425 | 30 | 0 | 158 | 120 | 322 | 46 | 429.75
15:30 | 4278.5 | 929 | 2841 | 0 | 1344 | 3423 | 30 | 0 | 158 | 118 | 266.5 | 44 | 423.065
16:00 | 4275 | 929 | 2883 | 0 | 1349 | 3421 | 30 | 0 | 158 | 116 | 211 | 42 | 416.38
16:30 | 4272.5 | 928.5 | 2775.5 | 0 | 1375.5 | 3417.5 | 30 | 0 | 161.5 | 115 | 148 | 42 | 414.47
17:00 | 4270 | 928 | 2668 | 0 | 1402 | 3414 | 30 | 0 | 165 | 114 | 85 | 42 | 412.56
17:30 | 4238.5 | 929 | 2529.5 | 0 | 1364 | 3317 | 30 | 0 | 169.5 | 93 | 50 | 35 | 352.78
18:00 | 4207 | 930 | 2391 | 0 | 1326 | 3220 | 30 | 0 | 174 | 72 | 15 | 28 | 293
18:30 | 4331 | 929.5 | 2585.5 | 0 | 1722 | 3290.5 | 30 | 0 | 344 | 75 | 7.5 | 28 | 269
19:00 | 4455 | 929 | 2780 | 0 | 2118 | 3361 | 30 | 0 | 514 | 78 | 0 | 28 | 245
19:30 | 4557 | 851 | 2719 | 0 | 2569 | 3439 | 30 | 0 | 582 | 74 | 0 | 25 | 207.495
20:00 | 4546 | 646 | 2744 | 0 | 2635 | 3441 | 30 | 0 | 628 | 82 | 0 | 20 | 169.99
20:30 | 4557.5 | 645.5 | 2909.5 | 0 | 2487.5 | 3563.5 | 30 | 0 | 553 | 93 | 0 | 11 | 154.71
21:00 | 4569 | 645 | 3075 | 0 | 2340 | 3686 | 30 | 0 | 478 | 104 | 0 | 2 | 139.43
21:30 | 4582.5 | 645 | 2995 | 0 | 2219 | 3902.5 | 30 | 0 | 469.5 | 109 | 0 | 9 | 144.205
22:00 | 4596 | 645 | 2915 | 0 | 2098 | 4119 | 30 | 0 | 461 | 114 | 0 | 16 | 148.98
22:30 | 4634.5 | 645.5 | 2961.5 | 0 | 2061.5 | 4065.5 | 30 | 0 | 395 | 113 | 0 | 10.5 | 222.515
23:00 | 4673 | 646 | 3008 | 0 | 2025 | 4012 | 30 | 0 | 329 | 112 | 0 | 5 | 296.05
23:30 | 4613 | 646 | 2921 | 0 | 1993 | 3887.5 | 30 | 0 | 287.5 | 113 | 0 | 6 | 542.44 |  |  | Max Temp. in Dhaka |  | 38.1°C
24:00 | 4553 | 646 | 2834 | 0 | 1961 | 3763 | 30 | 0 | 246 | 114 | 0 | 7 | 788.83
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 318.034 MKWHr Energy Not Served 9.586 MKWHr Energy Requirement 327.619 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 732000
3 | Chattogram TPP-1 | 114 | 115 | 120 | 120 | 120 | 122 | 122 | 120 | 120 | 120 | 115 | 115 | 108 | 108 | 110 | 108 | 108 | 111 |  | 110 | 112 | 116 | 111 | 110 | 110 | 110 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 0 | [17 empty] | 5 | 8 | 8 |  | 63498
| Teknaf 20MW PP (Solartech) | [8 empty] | 3 | 17 |  | 8 | 7 |  | 11 | 8 |  | 0 | [8 empty] | 59670
6 | Sikalbaha 225MW CCPP (Gas) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 217 | 212 | 212 | 211 | 211 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 211 | 210 | 210 | 210 | 210 | 4995047
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 34 | 34 | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 29 | 34 | 34 | 34 | 34 | 34 | 34 | 504976
12 | Hathazari 100 MW peaking PP | 32 | 25 | 25 | 25 | 25 | 2 |  |  |  |  | 1 | 32 | 32 | 32 | 32 | 32 | 32 | 41 |  | 56 | 56 | 56 | 56 | 56 | 48 | 41 | 658848
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 0 | [14 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 161416
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 37 | 37 | 37 | 7 | 7 | 7 | 7 |  |  |  |  | 23 | 29 | 28 | 28 | 29 | 36 | 36 |  | 37 | 37 | 37 | 39 | 39 | 39 | 39 | 561440
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 334 | 327 | 328 | 328 | 330 | 335 | 335 | 331 | 329 | 324 | 317 | 315 | 309 | 310 | 307 | 305 | 306 | 309 |  | 313 | 316 | 316 | 319 | 320 | 322 | 327 | 7754349
18 | Kodda 300 MW PP Unit-2 (Summit) | 80 | 80 | 0 | [16 empty] | 105 | 155 | 210 | 45 | 45 | 45 | 95 | 900764
19 | Ashuganj 195 MW PP (APSCL-United) | 63 | 63 | 63 | 73 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 150 | 120 | 120 | 120 | 128 | 103 |  | 88 | 88 | 56 | 8 | 8 | 8 | 8 | 1973818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4063500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 271 | 271 | 269 | 272 | 274 | 272 | 271 | 271 | 265 | 265 | 265 | 265 | 268 | 268 | 276 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 276 | 6512726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 38 | 38 | 38 | 38 | 38 | 35 | 37 | 37 | 37 | 34 | 33 | 33 | 32 | 31 | 31 | 32 | 32 |  | 33 | 33 | 35 | 35 | 35 | 35 | 35 | 842184
33 | Ashuganj 225 MW CCPP | 213 | 220 | 219 | 0 | [10 empty] | 26 | 43 | 53 | 55 |  | 142 | 206 | 197 | 190 | 197 | 195 | 199 | 2006000
34 | Ashuganj 450 MW CCPP(South) | 275 | 230 | 230 | 280 | 265 | 265 | 275 | 240 | 240 | 240 | 310 | 305 | 285 | 280 | 305 | 305 | 300 | 300 |  | 300 | 300 | 305 | 300 | 300 | 310 | 310 | 6898000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 295 | 285 | 285 | 285 | 295 | 345 | 285 | 300 | 280 | 285 | 315 | 325 | 295 | 290 | 290 |  | 295 | 295 | 300 | 295 | 295 | 310 | 310 | 7432100
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 285 | 285 | 250 | 250 | 230 | 230 | 230 | 280 | 315 | 300 | 285 | 315 | 320 | 320 | 325 |  | 325 | 295 | 285 | 275 | 300 | 270 | 280 | 6813800
35 | Ashuganj 55 MW PP (Precision) | 50 | 50 | 48 | 51 | 51 | 52 | 52 | 50 | 48 | 48 | 47 | 46 | 45 | 44 | 42 | 41 | 41 | 44 |  | 42 | 47 | 46 | 49 | 51 | 50 | 46 | 1133760
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 400 | 407 | 406 | 406 | 403 | 401 | 401 | 400 | 407 | 408 | 407 | 406 | 398 | 384 | 397 | 403 | 409 |  | 406 | 413 | 411 | 407 | 409 | 405 | 405 | 9763200
| Meghnaghat Unique power | 420 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 450 | 450 | 350 | 422 | 420 | 330 | 330 |  | 405 | 400 | 400 | 470 | 420 | 455 | 455 | 9253181
| Summit Meghanghat-2 589 MW(Gas) | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 400 | 400 | 300 | 300 |  | 300 | 300 | 300 | 480 | 400 | 430 | 430 | 8640909
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 330 | 330 | 330 | 330 | 360 | 420 | 450 | 380 | 380 | 380 | 380 | 350 |  | 390 | 390 | 390 | 450 | 450 | 450 | 450 | 9641000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 95 | 95 | 98 | 99 | 99 | 99 | 94 | 85 | 84 | 84 | 82 | 74 | 73 | 72 | 90 | 96 | 101 | 105 |  | 112 | 112 | 120 | 120 | 117 | 121 | 119 | 2211840
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 10 | 21 | 32 | 41 | 46 | 47 | 45 | 40 | 31 | 19 | 8 | 1 | [8 empty] | 343630
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 42 | 40 | 40 | 40 | 40 | 37 | 37 | 39 | 40 |  | 39 | 42 | 40 | 42 | 42 | 42 | 42 | 974000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 27 | 27 | 27 |  | 28 | 29 | 28 | 29 | 29 | 29 | 29 | 681480
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 59 | 59 | 59 | 60 | 60 | 40 | 40 | 40 | 40 | 40 | 55 | 50 | 40 | 54 | 55 | 56 |  | 59 | 59 | 58 | 59 | 59 | 60 | 60 | 1280640
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 207 | 200 | 200 | 200 | 200 | 201 | 200 | 201 | 199 | 199 | 196 | 195 | 195 | 194 | 159 | 160 | 160 | 160 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 4762140
51 | Sylhet 20 MW GTPP | [17 empty] | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 124000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 8 | 8 | 5 |  | 121872
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 53 | 53 | 52 | 52 | 52 | 22 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 922800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 16 | 16 | 19 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 436248
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 275 | 300 | 285 | 270 | 280 | 290 | 300 | 295 | 320 | 300 | 295 | 270 | 310 | 310 | 290 | 260 |  | 290 | 280 | 275 | 310 | 280 | 300 | 310 | 7127500
| Bibiyana South 400 MW | 345 | 345 | 345 | 349 | 310 | 310 | 310 | 310 | 310 | 310 | 320 | 380 | 345 | 315 | 350 | 322 | 310 | 310 |  | 340 | 340 | 340 | 340 | 340 | 381 | 340 | 8000500
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 10 | 17 | 17 | 17 | 17 | 20 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 596390
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 15 | 18 | 388560
60 | Barabkunda 22 MW PP (Regent) | 8 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 181536
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 74 | 30 | 64 | 60 | 50 | 58 | 60 | 72 | 82 | 88 | 96 | 116 | 120 | 116 | 120 | 116 | 114 | 72 |  | 78 | 74 | 82 | 104 | 114 | 112 | 114 | 2045760
64 | Malancha, Ctg. EPZ (United) | 28 | 28 | 28 | 28 | 0 | 5 | 0 | 9 | 14 | 10 | 10 | 13 | 13 | 13 | 6 | 6 | 16 | 16 |  | 16 | 19 | 19 | 40 | 40 | 40 | 35 | 497760
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 0 | 32 | 29 | 26 | 20 | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 28 |  | 28 | 28 | 28 | 32 | 32 | 32 | 32 | 667900
68 | Cumilla 25 MW PP (Summit) | [6 empty] | 0 | [5 empty] | 0 | 2 | 2 | 2 | 14 |  |  | 10 | 12 | 12 | 12 | 13 | 13 | 13 | 96140
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 13 | 13 | 13 | 13 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 506000
70 | Summit Madhabdi | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | 7 |  | 7 | 7 | 7 | 14 | 6 | 5 |  | 4 | 15 | 15 | 15 | 19 | 19 | 15 | 147600
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 |  | 33 | 33 | 33 | 33 | 717200
72 | Rupganj 33 MW PP(Summit) | [8 empty] | 28 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 30 | 30 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 466000
73 | Ghorashal 108 MW PP (Regent) | 80 | 80 | 80 | 80 | 80 | 80 | 79 | 52 | 52 | 52 | 52 | 52 | 71 | 69 | 68 | 70 | 73 | 78 |  | 79 | 79 | 80 | 77 | 78 | 78 | 78 | 1711409
| Feni Lanka Power | 70 | 70 | 70 | 70 | 34 | 34 | 19 | 52 | 52 | 52 | 52 | 52 | 103 | 114 | 114 | 114 | 114 | 52 |  | 95 | 105 | 105 | 114 | 114 | 114 | 114 | 1852500
| Chowmuhani 113 MW | 38 | 38 | 38 | 38 | 38 | 38 | 15 | 9 | 9 | 21 | 36 | 45 | 48 | 54 | 38 | 36 | 27 | 27 |  | 36 | 65 | 64 | 66 | 66 | 66 | 47 | 955920
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 144 | 162 | 162 | 162 | 162 | 162 | 162 | 1101600
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 42 | 0 |  |  |  | 8 | 17 | 22 | 42 | 55 | 64 | 55 | 60 | 61 | 61 | 69 | 69 |  | 69 | 69 | 71 | 65 |  |  | 20 | 879360
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 317280
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 82 | 82 | 80 | 80 | 78 | 64 | 63 | 63 | 63 |  | 148 | 148 | 148 | 132 | 115 | 32 | 16 | 1403520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 12 | 25 | 28 | 34 | 33 | 33 | 34 | 34 |  | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 724099
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 105 | 105 | 105 | 105 | 105 | 70 | 17 | 868800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 4 | 3 | 3 | 3 | 2 | 0 | [9 empty] | 31441
| Jodiac Power | 17 | 0 | [17 empty] | 6 | 34 | 35 |  |  |  | 26 | 114481
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 0 | [6 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 311126
82 | Madanganj 102 PP(Summit) | 88 | 78 | 34 | 0 |  |  | 14 | 25 | 17 | 45 | 51 | 51 | 51 | 63 | 50 | 47 | 62 | 68 |  | 80 | 80 | 80 | 60 | 8 |  | 12 | 904351
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 15 | 13 | 15 |  |  |  |  | 25001
86 | Meghnaghat CCPP ( Summit) | 305 | 293 | 297 | 309 | 307 | 285 | 260 | 260 | 260 | 261 | 303 | 301 | 295 | 294 | 295 | 298 | 288 | 258 |  | 306 | 274 | 293 | 306 | 301 | 304 | 149 | 6797295
87 | Meghnaghat 100 MW(IEL) | 17 | 0 | [7 empty] | 3 | 39 | 50 | 49 | 24 | 9 | 15 | 48 | 37 |  | 34 | 66 | 58 | 79 |  |  | 19 | 495360
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 33 | 33 | 33 | 16 |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 23 | 33 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 612480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 40 | 40 | 40 | 37 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 33 | 32 | 32 | 32 | 35 | 20 |  | 34 | 36 | 37 | 37 | 37 | 40 | 40 | 727416
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1152304
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 | 49 | 41 | 57 | 57 | 57 | 57 | 65 | 65 |  | 90 | 90 | 90 | 48 | 48 | 48 | 82 | 1097856
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 0 | [7 empty] | 5 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 99360
96 | Chattogram 108 MW PP (ECPV) | 19 | 19 | 17 | 12 | 0 | [16 empty] | 6 | 48 | 77 | 71 | 18 | 295680
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  |  | 1 | 40 | 40 | 40 | 38 | 669597
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 |  | 660677
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 80 | 80 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2393673
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 16300
103 | Kamalaghat 54 MW PP(Banco Energy) | [7 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 33 | 54 | 54 | 54 | 54 | 54 | 54 | 616680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 78 | 78 | 78 | 78 | 77 | 57 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 57 |  | 104 | 104 | 107 | 107 | 107 | 107 | 108 | 1773600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 37 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 35 | 45 | 108 | 129 | 130 | 126 | 96 | 64 | 70 | 129 |  | 132 | 132 | 132 | 132 | 132 | 111 | 56 | 1810944
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 25 | 0 |  |  |  |  | 10 | 49 | 49 | 62 | 62 | 62 | 62 | 25 |  | 48 | 62 | 62 | 62 | 62 | 62 | 49 | 946560
116 | Chandpur 200 MW (Desh energy) | 89 | 89 | 89 | 90 | 90 | 90 | 51 | 51 | 51 | 57 | 91 | 100 | 116 | 117 | 121 | 121 | 120 | 120 |  | 120 | 120 | 120 | 120 | 110 | 107 | 107 | 2408160
117 | Ashuganj 150 MW PP (Midland) | 6 | 5 | 6 | 6 | 5 | 6 | 6 |  |  |  | 1 | 5 | 6 | 6 | 6 | 5 | 8 | 5 |  | 6 | 6 | 5 | 3 | 5 | 5 | 6 | 122109
118 | Bibiyana-III 400 MW CCPP | 365 | 365 | 365 | 370 | 315 | 318 | 318 | 315 | 314 | 316 | 328 | 322 | 318 | 322 | 351 | 325 | 318 | 317 |  | 340 | 366 | 365 | 365 | 365 | 400 | 365 | 8305000
| Jamalpur 115 MW PP (United) | 69 | 69 | 69 | 69 | 69 | 69 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 57 |  | 97 | 98 | 98 | 99 | 99 | 99 | 99 | 1567200
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 301091
| Juldah unit-2 (Acorn) | 48 | 48 | 48 | 48 | 48 | 0 |  |  |  |  | 15 | 48 | 60 | 60 | 60 | 60 | 60 | 24 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 966720
| Anlima Energy Ltd. | 35 | 35 | 35 | 35 | 35 | 17 | 17 |  |  |  | 2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 38 | 72 | 72 | 72 | 72 | 56 | 35 | 839291
| Bhairob 54.5 MW | 34 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 33 | 34 | 34 | 34 | 34 | 33 | 26 | 33 | 34 |  | 41 | 51 | 51 | 42 | 33 | 34 | 34 | 714960
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 6 | 12 | 19 | 23 | 26 | 27 | 25 | 22 | 17 | 11 | 5 | 1 | [8 empty] | 193934
| Chandpur 115(Doreen) | 58 | 19 | 19 | 20 | 21 | 18 | 17 | 17 | 17 | 20 | 34 | 34 | 43 | 54 | 72 | 74 | 81 | 94 |  | 94 | 96 | 96 | 96 | 96 | 96 | 92 | 1296960
| Kanchan Purbachal Power Generation Ltd. | [26 empty] | 0
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 0 | [6 empty] | 17 | 54 | 17 | 17 | 17 | 17 | 17 |  | 90 | 108 | 108 | 54 | 54 | 17 | 17 | 518545
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 5 | 1 | 3 | 6 | 0 | [5 empty] | 37 | 50 | 46 | 49 | 46 | 42 | 42 | 28 |  | 28 | 25 | 20 | 2 | 16 | 5 | 7 | 432000
| Sonagazi 75 MW Solar Plant |  |  |  |  | 0 | 4 | 16 | 35 | 52 | 63 | 54 | 62 | 64 | 47 | 31 | 20 | 13 | 2 | [8 empty] | 428218
| Matarbari 2*600 MW (CPGCL) | 779 | 781 | 779 | 781 | 726 | 725 | 725 | 729 | 727 | 725 | 316 | 316 | 315 | 319 | 317 | 321 | 320 | 375 |  | 378 | 371 | 373 | 424 | 574 | 579 | 575 | 13076363
120 | Eastern Zone Total | 8258 | 8020 | 7798 | 7683 | 7299 | 6997 | 6763 | 6780 | 6929 | 7107 | 7234 | 7734 | 7989 | 7669 | 7901 | 7836 | 7702 | 7446 |  | 8716 | 9041 | 9060 | 9213 | 9063 | 8996 | 8632 | 189900903
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 20 | 0 | [16 empty] | 22 | 40 | 45 |  |  |  |  | 112320
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 66 | 73 | 73 | 73 | 73 | 73 | 35 | [10 empty] | 8 |  | 20 | 53 | 54 | 48 |  | 7 | 41 | 688800
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 19 | 38 | 65 | 81 | 91 | 94 | 92 | 80 | 70 | 45 | 16 | 3 | [8 empty] | 689040
131 | Rampal 1320 MW (BIFPCL) | 306 | 307 | 306 | 308 | 307 | 309 | 311 | 309 | 310 | 308 | 309 | 305 | 308 | 309 | 309 | 308 | 306 | 310 |  | 307 | 310 | 306 | 307 | 307 | 307 | 303 | 7381818
132 | United Payra Power Ltd. | [19 empty] | 6 | 17 | 17 |  |  |  |  | 37200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4827491
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 0 | [15 empty] | 32 | 40 | 48 | 16 | 16 | 32 | 48 | 234912
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 260 | 231 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 250 | 150 | 150 | 150 | 150 | 150 |  | 210 | 230 | 230 | 292 | 307 | 307 | 307 | 4669100
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 126 | 128 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 124 | 126 | 126 | 80 | 80 | 126 | 126 | 74 |  | 124 | 124 | 130 | 130 | 130 | 130 | 130 | 2515000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 9 | 8 | 6 | 8 | 8 | 8 | 8 | 9 | 9 | 10 | 9 | 9 | 1 |  | 1 | 1 | 1 | 1 | 3 | 6 | 6 | 170609
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 44 | 20 | 0 | [16 empty] | 15 | 36 | 49 |  |  |  |  | 143616
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 645 | 645 | 929 | 929 | 929 | 929 | 930 | 929 | 929 | 930 | 929 | 930 | 928 | 929 | 929 | 929 | 928 | 930 |  | 929 | 851 | 646 | 645 | 645 | 646 | 646 | 20418909
147 | Bheramara 410 MW CCPP | 340 | 340 | 340 | 345 | 345 | 345 | 345 | 355 | 345 | 345 | 370 | 350 | 345 | 362 | 380 | 360 | 345 | 345 |  | 345 | 345 | 355 | 345 | 360 | 380 | 340 | 8745696
148 | Payra 1320 MW | 1200 | 1100 | 980 | 980 | 980 | 900 | 780 | 700 | 700 | 700 | 720 | 860 | 990 | 900 | 900 | 900 | 900 | 760 |  | 760 | 790 | 800 | 920 | 1210 | 1244 | 1244 | 24264400
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 73 | 73 | 73 | 72 | 72 | 72 | 72 | 71 | 71 | 72 | 72 | 72 | 72 | 72 | 69 | 69 |  | 71 | 71 | 71 | 70 | 70 | 72 | 72 | 1686109
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5574000
153 | Baghabari 71 MW GTPP | 55 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 50 | 50 | 50 | 35 | 40 | 40 | 40 | 40 | 40 |  | 50 | 50 | 50 | 50 | 50 |  |  | 1060000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 38 | 38 | 40 | 40 | 40 | 40 | [20 empty] | 251475
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 35520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 65 | 0 | [24 empty] | 149800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 194 | 183 | 185 | 190 | 172 | 159 | 163 | 165 | 168 | 166 | 185 | 171 | 168 | 159 | 193 | 198 | 185 | 172 |  | 178 | 183 | 184 | 195 | 183 | 201 | 195 | 4530045
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 122 | 135 | 176 | 208 | 189 | 155 | 155 | 157 | 160 | 158 | 178 | 163 | 163 | 157 | 176 | 176 | 190 | 166 |  | 174 | 182 | 183 | 195 | 183 | 202 | 196 | 4352782
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 381 | 398 | 414 | 347 | 296 | 316 | 345 | 348 | 348 | 350 | 345 | 295 | 350 | 351 | 402 | 383 | 298 |  | 396 | 372 | 414 | 414 | 414 | 414 | 394 | 8857090
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 10 | 10 | 5 | 0 | [15 empty] | 5 | 5 | 20 | 16 | 16 | 14 | 14 | 94777
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244152
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | 16 | 16 | 16 | 0 | [15 empty] | 8 | 8 | 8 |  |  |  | 25 | 73990
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 0 | [15 empty] | 4 | 10 | 20 | 40 | 40 | 38 | 38 | 217580
168 | Santahar 50 MW Peaking PP | 23 | 23 | 0 | [16 empty] | 23 | 23 | 26 | 22 | 22 | 22 | 22 | 173270
169 | Natore 52 MW PP (Rajlanka) | [23 empty] | 8 | 8 | 0 | 16190
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 85 | 85 | 85 | 85 | 85 | 85 | 25 | 431536
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | [6 empty] | 3 | 35 | 35 | 35 |  |  |  | 18 | 109 | 113 | 56 | 35 | 35 | 76 | 769728
172 | Confidence Power Bogura Unit-1 113 MW | 18 | 18 | 18 | 18 | [15 empty] | 35 | 35 | 35 | 35 | 35 | 70 | 95 | 343488
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 39 | 34 | 34 | 34 | 35 | 35 | 35 | 34 | 41 | 58 | 59 | 59 | 56 | 61 | 53 | 80 | 84 | 84 |  | 88 | 92 | 85 | 85 | 85 | 85 | 34 | 1375526
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 4 | 5 | 6 | 7 | 7 | 7 | 4 | 3 | 2 | 0 | [8 empty] | 48538
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 30 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 75 | 115 | 115 | 115 | 115 | 75 | 54 | 1385856
| Intraco Solar 30 MW | [6 empty] | 6 | 13 | 21 | 27 | 30 | 32 | 30 | 27 | 21 | 14 | 6 | 1 | [8 empty] | 230215
| Adani Power Jharkhanda Ltd | 436 | 437 | 434 | 434 | 441 | 440 | 471 | 418 | 636 | 811 | 899 | 954 | 1113 | 1151 | 1171 | 1170 | 1169 | 1056 |  | 1135 | 1167 | 1161 | 1173 | 1151 | 1003 | 756 | 19925454
178 | Teesta Solar Limited | [5 empty] | 10 | 42 | 88 | 130 | 164 | 182 | 192 | 182 | 147 | 129 | 86 | 35 | 7 | [8 empty] | 1406810