## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-06 | Monday
|  | Date (day): | 2024-05-06 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14827.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16789 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-05 | 2024-05-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 100 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 77 | 77 | 75 | 80 | 28 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 400 | 402 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 16 | 96 | 90 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 301 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 25 | 95 | 80 | 80
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 4 | 40 | 40 | 40 | 15 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 15 | 60 |  | Engine problem.
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 110 |  | Titas gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 16 | 69 | 60 | 80
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 311 | 312 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 49 | 90 | 48 | 90 | 12 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 131 | 32 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 41 | 42 | 42 |  | 38 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 30 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 16 | 16 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 83 | 253 | 210 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 51 | 149 | 52 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 34 | 17 | 53 | 51 |  | Lube oil shortage.
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 120 | 162 | 90 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 460 | 350 | 500 | 500
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 350 | 300 | 360 | 450 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 3110 | 3722 | 3601 | 4308 | 652 | 798
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 77 | 118 | 118 | 62 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 1 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 19 | 31 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 210 | 210 | 210 | 210
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 17 | 34 | 71 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 40 | 57 | 40 | 64 | 34
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 51 | 50 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 49 | 62 | 36 | 60 | 40 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 0 | 5 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 19 | 51 | 20 | 90 | 18 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 16 | 16 | 16 | 284
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 19 | 54 | 17 | 54 |  |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 51 | 17 | 51 | 59 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 49 | 60 | 40 | 70 | 30 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 67 | 35 | 72 | 44 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 270 | 270 | 270 | 270 | 954 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 11 | 20 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 375 | 430 | 350 | 760 |  |  | Unit-2 on test
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 76 | 0 | 33 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1487 | 1755 | 1447 | 2227 | 1827 | 381
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 215 | 182 | 205 | 205 |  | 16 | Under maint
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 310 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 175 | 170 | 240 | 240 |  |  | ST Under maint.
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 335 | 320 | 350 | 350 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 34 | 34 | 34 | 11
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 48 | 20 | 50 | 50 | 5
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 90 | 90 | 105 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 6 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 8 | 23 | 36 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 130 | 100 | 136 | 64
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 126 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 28 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 40 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 14 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 97 | 70 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 84 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 34 | 17 | 42 |  | 12 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 62 | 96 | 54 | 95 |  | 20 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1602 | 1765 | 1863 | 2085 | 367 | 227
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 100 | 111 | 100 | 100 | 102 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 56 | 105 | 56 | 108 | 92 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 96 | 50 | 97 | 18 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 12 | 22
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 274 | 330 | 269.6 | 327 | 102 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 28 | 28 |  | 62 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 80 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 37 | 40 | 44 | 44
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 0 | 5 | 5 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 162 | 162 |  | 69 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 285 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 316 | 330 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 360 | 340 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1372 | 1392 | 1587 | 1607 | 0 | 539
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 920 | 940 | 655
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 5 | 0 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 44 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 370 | 400 | 410
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 9 | 17 | 90 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 93 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 310 | 306 | 375 | 375
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1677 | 1670 | 1949 | 1634 | 702 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 80 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 960 | 910 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 180 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 27 | 123 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 200 | 200 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1463 | 1396 | 1869 | 2048 | 123 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 33 | 0 | 33 | 19 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 25 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 42 | 42
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 189 | 149 | 170 | 200 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 181 | 153 | 180 | 200
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 315 | 346 | 414 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 28 | 22 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 0 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 92 | 94 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 35 | 95 | 18 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 758 | 753 | 748 | 748 |  |  | Engine problem
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1675 | 1816 | 1683 | 2041 | 274 | 76
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 73 | 70 | 70 | 75 | 10
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 67 | 92 | 56 | 92 | 21 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 90 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 10 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 72 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 547 | 507 | 559 | 512 | 71 | 129
| Total |  |  |  |  | 27054 | 25903 | 13207 | 14353 | 14827.6 | 16789 | 4118 | 2273
A. |  | 2024-05-05 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 14353 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 10874 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14400 | MW
3 | Day peak Generation : |  |  | 13207 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13886.85 | MW
4 | Evening peak Generation : |  |  | 14353 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 45 | MW
5 | Total Energy Generation : |  | 299.1216 | MKWHr | By Solar | 2.4172 | MKWHr
| By Gas : | 159.3815 | MKWHr |  | By Oil: | 35.1884 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 79.2864 | MKWHr |  | By Hydro: | 0.676 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.34224 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4118 | MW | Dhaka | 5524.65 | 5489.65 |  | 35 |  | 18:00 |  | 35
|  |  | For Plants S/D or M/C prob = |  |  | 2273 | MW | Chittagong | 1415.5 | 1415.5 |  | 0 |  | 19:00 |  | 45
|  |  | Total = |  |  | 6391 | MW | Khulna | 1815.6 | 1805.6 |  | 10 |  | 19:30 |  | 47
7 | Total Gas Supplied : |  |  | 1170.65 | MMCFD |  |  | Rajshahi | 1639.6 | 1639.6 |  | 0 |  | 20:00 |  | 39
8 | Fuel Cost : | i) Gas : | Taka | 446116330.574 | ii) Oil : | Taka | 645481195.72 | Comilla | 1281 | 1281 |  | 0 |  | 21:00 |  | 87
|  | iii) Coal : | Taka | 539387685.83 | Total | Taka | 1630985212.124 | Mymensingh | 849 | 849 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2166.45 | MKWHr. | Sylhet | 163 | 163 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 402 | MW (W to E) at | 19:00 | hrs | Barisal | 481.5 | 481.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | -360 | MW at | 23:00 | hrs | Rangpur | 717 | 717 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.7°C |  |  | Total | 13886.85 | 13841.85 |  | 45
B. |  | 2024-05-06 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 36.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16789 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
4 | Reserve(Generation end) |  |  |  | 2789 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 291.765 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9606 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.7178 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.112 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.53 |  | (b) Today: | 73.43 |  | (c) Rule Curve: |  | 81.05
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-05 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 100 | 0 | 81 | 0 | 404 | 0 |  | 0 | 450 | 308 | 24 | 80 | 15 | 326 | 0 | 0 | 37 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 19 | 0 | 32 | 8 | 0 | 0 | 30 | 100 | 0 | 8 | 210 | 0 | 0 | 0 |  | 12 | 41 | 51 | 0 | 20 | 6 | 10 | 25 | 0 | 0 | 0 | 135 | 235 | 211 | 26 | 0 | 31 | 48 | 0 | 26 | 0 | 8 | 25 | 0 | 0 | 32 | 14 | 122 | 71 | 0 | 0 | 0 | 30 | 0 | 53 | 36 | 112 | 0 | 57 | 0 | 0 | 100 | 0 | 0 | 0 | 310 | 8 | 0 | 0 | 87 | 0 | 0 | 5 | 0 | 17 | 0 | 49 | 141 | 2 | 379 | 2 | 17 | 17 | 0 | 16 | 17 | 17 | 70 | 38 | 60 | 340 | 16 | 0 | 90 | 35 | 0 | 4 | 0 | 54 | 0 | 335 | 17 | 0 | 269 | 2 | 773 | 506 | 440 | 0 |  | 641 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 20 | 39 | 0 | 130 | 10 | 80 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 25 | 21 | 8 | 25 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 199 | 0 | 414 | 55 | 0 | 90 | 0 | 34 | 0 | 0 | 95 | 1100 | 220 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 307 | 0 | 307 | 752 | 0 | 0 |  | 7965 | 5505 | 13470 | 4101 | 641 | 3065 | 0 | 1454 | 3807 | 30 | 0 | 248 | 122 | 0 | 2 | 315.15 | 73.55
2:00 | 0 | 0 | 0 | 100 | 0 | 81 | 0 | 410 | 0 |  | 0 | 450 | 263 | 24 | 80 | 9 | 320 | 0 | 0 | 32 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 19 | 15 | 32 | 8 | 0 | 0 | 30 | 100 | 0 | 8 | 210 | 0 | 0 | 0 |  | 12 | 41 | 51 | 0 | 20 | 6 | 10 | 25 | 0 | 0 | 0 | 207 | 235 | 205 | 8 | 0 | 35 | 50 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 32 | 14 | 118 | 38 | 0 | 0 | 0 | 30 | 0 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 280 | 14 | 5 | 0 | 15 | 0 | 0 | 16 | 0 | 17 | 0 | 49 | 101 | 5 | 365 | 8 | 17 | 17 | 0 | 16 | 0 | 17 | 70 | 38 | 48 | 340 | 16 | 0 | 90 | 35 | 0 | 17 | 0 | 46 | 0 | 325 | 17 | 0 | 268 | 7 | 776 | 450 | 350 | 0 |  | 642 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 25 | 21 | 8 | 25 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 180 | 0 | 304 | 55 | 0 | 113 | 0 | 34 | 0 | 0 | 95 | 1080 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 307 | 0 | 300 | 757 | 0 | 0 |  | 7675 | 5199 | 12874 | 4085 | 642 | 2747 | 0 | 1269 | 3787 | 30 | 0 | 189 | 118 | 0 | 7 | 215.83 | 73.55
3:00 | 0 | 0 | 0 | 100 | 0 | 80 | 0 | 414 | 0 |  | 0 | 350 | 294 | 0 | 12 | 25 | 327 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 5 | 41 | 51 | 0 | 18 | 6 | 10 | 35 | 0 | 0 | 0 | 340 | 190 | 208 | 8 | 0 | 35 | 49 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 32 | 14 | 112 | 55 | 0 | 0 | 0 | 30 | 0 | 53 | 37 | 112 | 0 | 61 | 0 | 0 | 100 | 0 | 0 | 0 | 260 | 14 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 49 | 88 | 6 | 365 | 9 | 0 | 0 | 0 | 16 | 0 | 0 | 70 | 38 | 48 | 340 | 16 | 0 | 90 | 35 | 0 | 0 | 0 | 18 | 0 | 0 | 17 | 0 | 268 | 9 | 730 | 400 | 300 | 0 |  | 743 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 180 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 700 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 308 | 0 | 150 | 634 | 0 | 0 |  | 6882 | 4253 | 11135 | 3770 | 743 | 2579 | 0 | 676 | 3089 | 30 | 0 | 127 | 112 | 0 | 9 | 85.95 | 73.54
4:00 | 0 | 0 | 0 | 100 | 0 | 78 | 0 | 419 | 0 |  | 0 | 350 | 287 | 0 | 0 | 25 | 335 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 17 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 7 | 41 | 51 | 0 | 19 | 6 | 10 | 35 | 0 | 0 | 0 | 355 | 180 | 196 | 8 | 0 | 35 | 49 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 30 | 0 | 53 | 40 | 112 | 0 | 61 | 0 | 0 | 100 | 0 | 0 | 0 | 270 | 14 | 5 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 49 | 85 | 5 | 365 | 9 | 0 | 0 | 0 | 16 | 0 | 0 | 70 | 38 | 48 | 340 | 16 | 0 | 17 | 35 | 0 | 0 | 0 | 18 | 0 | 250 | 0 | 0 | 269 | 10 | 728 | 400 | 300 | 0 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 180 | 0 | 313 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 660 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 150 | 563 | 0 | 0 |  | 6906 | 4289 | 11195 | 4008 | 926 | 2576 | 0 | 556 | 2979 | 30 | 0 | 110 | 0 | 0 | 10 | 0 | 73.54
5:00 | 0 | 0 | 0 | 100 | 0 | 78 | 0 | 418 | 0 |  | 0 | 350 | 313 | 0 | 0 | 25 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 17 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 7 | 41 | 51 | 0 | 19 | 6 | 10 | 30 | 0 | 0 | 0 | 356 | 180 | 194 | 8 | 0 | 35 | 51 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 32 | 0 | 14 | 82 | 0 | 0 | 0 | 30 | 0 | 53 | 40 | 112 | 0 | 61 | 0 | 0 | 100 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 49 | 85 | 6 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 38 | 48 | 340 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 0 | 245 | 0 | 0 | 270 | 12 | 726 | 400 | 300 | 0 |  | 926 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 184 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 150 | 559 | 0 | 0 |  | 6918 | 4294 | 11212 | 4053 | 926 | 2643 | 0 | 439 | 2995 | 30 | 0 | 100 | 14 | 0 | 12 | 0 | 73.53
6:00 | 0 | 0 | 0 | 100 | 0 | 78 | 0 | 419 | 0 |  | 0 | 350 | 295 | 0 | 0 | 25 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 17 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 41 | 51 | 0 | 19 | 6 | 7 | 30 | 0 | 0 | 0 | 280 | 180 | 224 | 8 | 0 | 35 | 51 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 31 | 0 | 20 | 102 | 0 | 0 | 0 | 30 | 0 | 53 | 40 | 112 | 0 | 61 | 0 | 0 | 100 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 2 | 49 | 85 | 6 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 39 | 48 | 340 | 0 | 3 | 0 | 35 | 0 | 0 | 1 | 17 | 0 | 260 | 0 | 0 | 269 | 12 | 727 | 400 | 300 | 1 |  | 767 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 180 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 309 | 0 | 150 | 560 | 3 | 0 |  | 6896 | 4096 | 10992 | 4034 | 767 | 2576 | 0 | 444 | 2996 | 30 | 0 | 100 | 20 | 13 | 12 | 0 | 73.53
7:00 | 0 | 0 | 0 | 100 | 0 | 79 | 0 | 417 | 0 |  | 0 | 350 | 296 | 0 | 0 | 25 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 17 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 41 | 51 | 0 | 19 | 6 | 7 | 25 | 0 | 0 | 0 | 280 | 180 | 224 | 8 | 0 | 36 | 52 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 32 | 0 | 34 | 102 | 0 | 0 | 0 | 30 | 0 | 53 | 40 | 112 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 49 | 85 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 32 | 48 | 340 | 0 | 8 | 0 | 0 | 0 | 0 | 6 | 18 | 0 | 260 | 0 | 0 | 268 | 7 | 725 | 400 | 300 | 12 |  | 768 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 180 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 220 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 308 | 4 | 150 | 558 | 21 | 0 |  | 6869 | 4150 | 11019 | 4036 | 768 | 2588 | 0 | 397 | 2988 | 30 | 0 | 100 | 34 | 71 | 7 | 0 | 73.52
8:00 | 0 | 0 | 0 | 100 | 0 | 76 | 0 | 416 | 0 |  | 0 | 350 | 302 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 0 | 22 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 41 | 51 | 0 | 19 | 0 | 7 | 2 | 0 | 0 | 0 | 280 | 180 | 222 | 8 | 0 | 37 | 49 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 24 | 0 | 48 | 102 | 0 | 0 | 0 | 30 | 0 | 50 | 40 | 112 | 0 | 61 | 0 | 0 | 100 | 0 | 0 | 0 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 10 | 25 | 85 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 38 | 25 | 340 | 0 | 14 | 0 | 0 | 0 | 0 | 11 | 17 | 0 | 260 | 0 | 0 | 270 | 12 | 728 | 330 | 250 | 34 |  | 768 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 180 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 660 | 220 | 0 | 0 | 1 | 22 | 0 | 0 | 0 | 310 | 10 | 150 | 560 | 18 | 0 |  | 6670 | 4204 | 10874 | 4045 | 768 | 2443 | 0 | 359 | 2977 | 0 | 0 | 100 | 48 | 122 | 12 | 0 | 73.51
9:00 | 0 | 0 | 0 | 100 | 0 | 76 | 0 | 406 | 0 |  | 0 | 420 | 308 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 0 | 25 | 0 | 2 | 0 | 0 | 0 | 100 | 0 | 0 | 214 | 0 | 0 | 0 |  | 13 | 32 | 51 | 0 | 19 | 0 | 7 | 0 | 0 | 0 | 0 | 315 | 180 | 219 | 8 | 0 | 35 | 52 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 24 | 0 | 62 | 101 | 0 | 0 | 0 | 30 | 0 | 50 | 40 | 112 | 0 | 59 | 0 | 0 | 100 | 0 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 1 | 14 | 40 | 85 | 0 | 397 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 26 | 50 | 358 | 0 | 14 | 0 | 0 | 0 | 16 | 16 | 17 | 0 | 300 | 0 | 0 | 270 | 6 | 761 | 325 | 250 | 52 |  | 916 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 203 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 690 | 220 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 312 | 8 | 150 | 577 | 76 | 0 |  | 7045 | 4571 | 11616 | 4259 | 916 | 2580 | 0 | 405 | 3060 | 0 | 0 | 107 | 62 | 221 | 6 | 0 | 73.51
10:00 | 0 | 0 | 0 | 100 | 0 | 76 | 0 | 404 | 0 |  | 0 | 450 | 304 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 7 | 0 | 16 | 8 | 0 | 0 | 30 | 100 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 51 | 0 | 19 | 0 | 10 | 0 | 0 | 0 | 0 | 305 | 195 | 214 | 0 | 0 | 35 | 51 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 24 | 0 | 88 | 100 | 0 | 0 | 2 | 30 | 0 | 50 | 37 | 112 | 0 | 61 | 0 | 0 | 100 | 18 | 0 | 0 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 18 | 62 | 85 | 3 | 374 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 34 | 26 | 75 | 358 | 2 | 22 | 0 | 0 | 0 | 17 | 22 | 17 | 0 | 285 | 0 | 0 | 268 | 23 | 782 | 355 | 250 | 65 |  | 916 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 194 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 760 | 220 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 309 | 9 | 150 | 741 | 59 | 0 |  | 7295 | 4762 | 12057 | 4194 | 916 | 2607 | 0 | 529 | 3311 | 30 | 0 | 107 | 88 | 252 | 23 | 0 | 73.51
11:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 400 | 0 |  | 0 | 450 | 300 | 1 | 0 | 0 | 311 | 0 | 0 | 5 | 49 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 22 | 9 | 0 | 0 | 8 | 0 | 0 | 30 | 107 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 32 | 51 | 0 | 19 | 0 | 10 | 2 | 0 | 0 | 0 | 335 | 215 | 200 | 0 | 0 | 35 | 47 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 24 | 0 | 98 | 100 | 0 | 0 | 2 | 30 | 0 | 50 | 37 | 112 | 0 | 60 | 0 | 0 | 100 | 20 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 32 | 0 | 17 | 20 | 49 | 85 | 6 | 419 | 10 | 35 | 0 | 0 | 16 | 1 | 17 | 52 | 30 | 75 | 380 | 16 | 37 | 54 | 15 | 0 | 29 | 23 | 23 | 0 | 275 | 24 | 0 | 270 | 10 | 372 | 460 | 350 | 73 |  | 918 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 203 | 0 | 406 | 0 | 0 | 2 | 0 | 22 | 0 | 4 | 30 | 920 | 220 | 0 | 0 | 0 | 59 | 30 | 0 | 0 | 307 | 12 | 150 | 749 | 51 | 0 |  | 7504 | 5073 | 12577 | 4267 | 918 | 2880 | 0 | 876 | 3070 | 30 | 0 | 147 | 98 | 281 | 10 | 0 | 73.5
12:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 400 | 0 |  | 0 | 450 | 304 | 16 | 25 | 4 | 311 | 0 | 0 | 16 | 49 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 22 | 20 | 25 | 0 | 8 | 0 | 0 | 30 | 100 | 0 | 1 | 210 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 19 | 0 | 10 | 2 | 0 | 0 | 0 | 290 | 175 | 215 | 0 | 0 | 26 | 48 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 32 | 0 | 102 | 100 | 0 | 0 | 2 | 30 | 0 | 50 | 37 | 112 | 0 | 61 | 0 | 0 | 100 | 18 | 0 | 0 | 285 | 8 | 5 | 0 | 83 | 0 | 0 | 56 | 0 | 51 | 20 | 49 | 85 | 6 | 316 | 47 | 35 | 34 | 0 | 16 | 19 | 34 | 70 | 37 | 49 | 350 | 17 | 51 | 120 | 17 | 0 | 35 | 30 | 62 | 0 | 335 | 54 | 0 | 270 | 11 | 375 | 460 | 350 | 76 |  | 920 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 181 | 0 | 315 | 9 | 0 | 92 | 0 | 67 | 0 | 5 | 95 | 960 | 220 | 0 | 0 | 4 | 93 | 90 | 0 | 0 | 310 | 10 | 150 | 758 | 72 | 0 |  | 7845 | 5362 | 13207 | 4108 | 920 | 2768 | 0 | 1594 | 3126 | 30 | 0 | 185 | 102 | 363 | 11 | 51 | 73.49
13:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 401 | 0 |  | 0 | 450 | 298 | 25 | 78 | 40 | 310 | 0 | 0 | 27 | 73 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 30 | 0 | 22 | 20 | 25 | 26 | 8 | 0 | 0 | 30 | 100 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 41 | 51 | 0 | 30 | 0 | 10 | 2 | 0 | 0 | 0 | 305 | 195 | 199 | 0 | 0 | 27 | 44 | 0 | 51 | 0 | 9 | 25 | 0 | 0 | 32 | 12 | 108 | 91 | 0 | 0 | 1 | 30 | 0 | 50 | 37 | 112 | 0 | 59 | 0 | 0 | 100 | 18 | 0 | 0 | 300 | 8 | 5 | 0 | 210 | 0 | 0 | 56 | 0 | 85 | 19 | 49 | 85 | 5 | 333 | 47 | 35 | 34 | 0 | 16 | 41 | 34 | 70 | 36 | 50 | 355 | 17 | 43 | 108 | 17 | 0 | 35 | 33 | 75 | 0 | 280 | 54 | 0 | 270 | 24 | 376 | 460 | 350 | 70 |  | 920 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 173 | 0 | 350 | 17 | 0 | 113 | 0 | 81 | 0 | 5 | 95 | 970 | 220 | 0 | 0 | 1 | 101 | 95 | 0 | 0 | 306 | 8 | 150 | 752 | 33 | 0 |  | 8203 | 5420 | 13623 | 4135 | 920 | 2809 | 0 | 1971 | 3125 | 30 | 0 | 187 | 108 | 314 | 24 | 54 | 73.48
14:00 | 0 | 0 | 0 | 100 | 0 | 73 | 0 | 402 | 0 |  | 0 | 450 | 302 | 60 | 78 | 40 | 309 | 0 | 0 | 64 | 73 | 31 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 22 | 0 | 25 | 30 | 8 | 0 | 0 | 30 | 70 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 41 | 51 | 0 | 32 | 0 | 10 | 2 | 0 | 0 | 0 | 280 | 170 | 212 | 0 | 0 | 30 | 25 | 0 | 51 | 0 | 22 | 25 | 0 | 0 | 32 | 13 | 120 | 92 | 0 | 0 | 2 | 30 | 0 | 50 | 39 | 112 | 0 | 60 | 0 | 0 | 100 | 18 | 0 | 0 | 290 | 8 | 5 | 0 | 210 | 0 | 0 | 56 | 0 | 120 | 17 | 49 | 85 | 6 | 366 | 49 | 17 | 34 | 4 | 16 | 54 | 34 | 70 | 37 | 50 | 345 | 17 | 21 | 106 | 22 | 0 | 35 | 28 | 75 | 0 | 335 | 17 | 0 | 270 | 30 | 368 | 460 | 350 | 57 |  | 921 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 170 | 0 | 336 | 17 | 0 | 113 | 0 | 85 | 0 | 5 | 95 | 1020 | 220 | 0 | 0 | 2 | 78 | 115 | 0 | 0 | 306 | 9 | 150 | 741 | 82 | 0 |  | 8240 | 5451 | 13691 | 4095 | 921 | 2769 | 0 | 2103 | 3156 | 30 | 0 | 162 | 120 | 305 | 30 | 37 | 73.5
15:00 | 0 | 0 | 0 | 100 | 0 | 74 | 0 | 401 | 0 |  | 0 | 450 | 293 | 81 | 78 | 40 | 307 | 0 | 0 | 68 | 73 | 31 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 22 | 0 | 25 | 30 | 8 | 0 | 0 | 30 | 75 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 31 | 0 | 10 | 0 | 0 | 0 | 0 | 325 | 170 | 202 | 0 | 0 | 30 | 20 | 0 | 51 | 0 | 21 | 25 | 0 | 0 | 32 | 13 | 120 | 93 | 0 | 0 | 1 | 28 | 10 | 50 | 0 | 112 | 0 | 56 | 0 | 0 | 100 | 18 | 0 | 0 | 295 | 8 | 0 | 0 | 210 | 0 | 0 | 55 | 0 | 133 | 13 | 49 | 85 | 5 | 415 | 49 | 17 | 17 | 3 | 16 | 54 | 34 | 70 | 37 | 50 | 375 | 17 | 34 | 108 | 35 | 0 | 33 | 11 | 72 | 0 | 360 | 17 | 0 | 270 | 32 | 374 | 460 | 350 | 42 |  | 920 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 8 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 175 | 0 | 377 | 17 | 0 | 94 | 0 | 85 | 0 | 5 | 95 | 1120 | 220 | 0 | 0 | 3 | 61 | 115 | 0 | 0 | 307 | 8 | 153 | 739 | 45 | 0 |  | 8341 | 5586 | 13927 | 4286 | 920 | 2760 | 0 | 2103 | 3263 | 30 | 0 | 187 | 120 | 226 | 32 | 70 | 73.46
16:00 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 397 | 0 |  | 0 | 450 | 302 | 82 | 65 | 40 | 302 | 0 | 0 | 68 | 73 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 22 | 0 | 25 | 31 | 8 | 0 | 0 | 30 | 75 | 0 | 8 | 210 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 33 | 0 | 10 | 0 | 0 | 0 | 0 | 285 | 170 | 208 | 0 | 0 | 32 | 20 | 0 | 51 | 0 | 21 | 40 | 0 | 0 | 32 | 12 | 118 | 96 | 0 | 0 | 1 | 30 | 10 | 50 | 27 | 112 | 0 | 58 | 0 | 0 | 100 | 18 | 0 | 0 | 310 | 8 | 0 | 0 | 200 | 0 | 0 | 58 | 0 | 149 | 10 | 49 | 85 | 6 | 365 | 49 | 17 | 17 | 2 | 16 | 54 | 34 | 70 | 37 | 50 | 350 | 25 | 21 | 108 | 35 | 0 | 32 | 14 | 72 | 0 | 360 | 17 | 0 | 270 | 41 | 372 | 460 | 350 | 26 |  | 920 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 11 | 4 | 17 | 0 | 16 | 30 | 0 | 20 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 189 | 0 | 397 | 17 | 0 | 76 | 0 | 92 | 0 | 4 | 95 | 1110 | 220 | 0 | 0 | 2 | 36 | 115 | 0 | 0 | 305 | 5 | 200 | 763 | 50 | 0 |  | 8296 | 5678 | 13974 | 4171 | 920 | 2827 | 0 | 2133 | 3320 | 30 | 0 | 243 | 118 | 171 | 41 | 73 | 73.45
17:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 401 | 0 |  | 0 | 450 | 304 | 86 | 65 | 40 | 304 | 0 | 0 | 68 | 76 | 30 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 22 | 0 | 25 | 30 | 8 | 0 | 0 | 30 | 72 | 0 | 9 | 210 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 44 | 0 | 10 | 2 | 0 | 0 | 0 | 280 | 170 | 212 | 0 | 0 | 32 | 20 | 0 | 51 | 0 | 21 | 40 | 0 | 0 | 32 | 12 | 108 | 97 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 112 | 0 | 60 | 0 | 0 | 100 | 18 | 0 | 0 | 285 | 8 | 0 | 0 | 223 | 0 | 0 | 58 | 0 | 146 | 10 | 49 | 85 | 6 | 364 | 49 | 17 | 34 | 1 | 16 | 54 | 34 | 85 | 42 | 50 | 350 | 33 | 10 | 108 | 35 | 0 | 32 | 6 | 81 | 0 | 375 | 17 | 0 | 270 | 41 | 380 | 460 | 300 | 8 |  | 920 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 29 | 4 | 16 | 0 | 25 | 30 | 0 | 25 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 184 | 0 | 370 | 17 | 0 | 76 | 0 | 92 | 0 | 3 | 95 | 1040 | 180 | 0 | 0 | 0 | 19 | 115 | 0 | 0 | 306 | 4 | 200 | 744 | 28 | 0 |  | 8323 | 5452 | 13775 | 4141 | 920 | 2708 | 0 | 2235 | 3240 | 30 | 0 | 263 | 108 | 89 | 41 | 72 | 73.44
18:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 353 | 0 |  | 0 | 340 | 300 | 96 | 85 | 40 | 250 | 0 | 0 | 73 | 90 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 22 | 19 | 25 | 30 | 16 | 0 | 0 | 30 | 73 | 0 | 17 | 210 | 0 | 0 | 0 |  | 18 | 42 | 51 | 0 | 44 | 6 | 10 | 3 | 0 | 0 | 0 | 280 | 170 | 181 | 0 | 0 | 32 | 20 | 0 | 51 | 0 | 22 | 40 | 0 | 0 | 28 | 12 | 116 | 97 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 265 | 8 | 0 | 0 | 230 | 0 | 0 | 67 | 0 | 149 | 3 | 62 | 87 | 8 | 318 | 49 | 17 | 51 | 0 | 16 | 54 | 51 | 97 | 81 | 60 | 345 | 33 | 0 | 108 | 36 | 0 | 32 | 1 | 96 | 0 | 320 | 17 | 0 | 270 | 22 | 373 | 302 | 250 | 1 |  | 921 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 29 | 4 | 25 | 0 | 34 | 30 | 0 | 28 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 140 | 0 | 270 | 17 | 0 | 76 | 0 | 100 | 0 | 0 | 95 | 880 | 180 | 0 | 0 | 0 | 3 | 115 | 0 | 0 | 307 | 1 | 200 | 750 | 3 | 0 |  | 7988 | 5025 | 13013 | 3752 | 921 | 2235 | 0 | 2470 | 3080 | 30 | 0 | 375 | 116 | 12 | 22 | 35 | 73.43
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 402 | 0 |  | 0 | 400 | 301 | 96 | 95 | 40 | 312 | 0 | 0 | 69 | 90 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 22 | 19 | 25 | 30 | 16 | 0 | 0 | 30 | 77 | 0 | 25 | 210 | 0 | 0 | 0 |  | 18 | 57 | 51 | 0 | 51 | 0 | 10 | 0 | 0 | 0 | 0 | 310 | 170 | 182 | 0 | 0 | 34 | 20 | 0 | 51 | 0 | 23 | 40 | 0 | 0 | 28 | 14 | 126 | 111 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 285 | 16 | 0 | 0 | 253 | 0 | 0 | 105 | 0 | 149 | 0 | 62 | 130 | 6 | 330 | 96 | 105 | 51 | 0 | 16 | 54 | 51 | 97 | 84 | 60 | 360 | 34 | 0 | 162 | 67 | 0 | 34 | 0 | 96 | 0 | 320 | 163 | 0 | 270 | 20 | 430 | 350 | 300 | 0 |  | 920 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 5 | 52 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 33 | 4 | 90 | 0 | 25 | 38 | 0 | 28 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 153 | 0 | 346 | 17 | 0 | 94 | 0 | 92 | 0 | 0 | 95 | 910 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 306 | 0 | 200 | 753 | 0 | 0 |  | 8964 | 5389 | 14353 | 4073 | 920 | 2490 | 0 | 2850 | 3169 | 30 | 0 | 675 | 126 | 0 | 20 | 45 | 73.43
19:30 | 0 | 0 | 0 | 100 | 0 | 76 | 0 | 404 | 0 |  | 0 | 400 | 303 | 9 | 17 | 40 | 313 | 0 | 0 | 20 | 90 | 126 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 19 | 25 | 30 | 16 | 0 | 0 | 30 | 75 | 0 | 25 | 210 | 0 | 0 | 0 |  | 18 | 56 | 51 | 0 | 60 | 11 | 10 | 2 | 0 | 0 | 0 | 300 | 170 | 184 | 0 | 0 | 34 | 20 | 0 | 51 | 0 | 23 | 40 | 0 | 0 | 32 | 14 | 122 | 128 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 310 | 16 | 0 | 0 | 195 | 0 | 0 | 105 | 0 | 149 | 0 | 62 | 136 | 6 | 339 | 96 | 88 | 51 | 0 | 16 | 54 | 51 | 97 | 84 | 60 | 345 | 39 | 0 | 162 | 72 | 0 | 0 | 0 | 100 | 0 | 320 | 163 | 0 | 270 | 11 | 423 | 396 | 300 | 0 |  | 919 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 29 | 57 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 33 | 4 | 90 | 0 | 8 | 38 | 0 | 28 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 169 | 0 | 346 | 17 | 0 | 94 | 0 | 92 | 0 | 0 | 95 | 1000 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 308 | 0 | 200 | 756 | 0 | 0 |  | 8757 | 5534 | 14291 | 4120 | 919 | 2564 | 0 | 2570 | 3257 | 30 | 0 | 698 | 122 | 0 | 11 | 47 | 0
20:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 405 | 0 |  | 0 | 400 | 303 | 32 | 30 | 40 | 316 | 0 | 0 | 18 | 90 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 20 | 25 | 30 | 16 | 0 | 0 | 30 | 80 | 0 | 25 | 210 | 0 | 0 | 0 |  | 11 | 49 | 51 | 0 | 71 | 18 | 10 | 7 | 0 | 0 | 0 | 285 | 170 | 183 | 0 | 0 | 35 | 20 | 0 | 51 | 0 | 23 | 40 | 0 | 0 | 32 | 17 | 122 | 126 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 305 | 16 | 0 | 0 | 95 | 0 | 0 | 64 | 0 | 142 | 0 | 62 | 138 | 6 | 363 | 64 | 88 | 51 | 0 | 16 | 17 | 51 | 97 | 84 | 60 | 345 | 48 | 0 | 162 | 72 | 0 | 0 | 0 | 102 | 0 | 320 | 163 | 0 | 270 | 6 | 492 | 450 | 350 | 0 |  | 634 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 168 | 0 | 347 | 20 | 0 | 76 | 0 | 48 | 0 | 0 | 35 | 1000 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 308 | 0 | 200 | 760 | 0 | 0 |  | 8718 | 4941 | 13659 | 4172 | 634 | 2710 | 0 | 2268 | 3330 | 30 | 0 | 387 | 122 | 0 | 6 | 39 | 73.43
21:00 | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 404 | 0 |  | 0 | 400 | 250 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 30 | 80 | 0 | 25 | 210 | 0 | 0 | 0 |  | 0 | 56 | 51 | 0 | 76 | 19 | 10 | 10 | 0 | 0 | 0 | 280 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 46 | 110 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 80 | 0 | 64 | 0 | 0 | 100 | 18 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 76 | 0 | 62 | 138 | 6 | 365 | 8 | 0 | 17 | 0 | 16 | 17 | 17 | 114 | 84 | 60 | 345 | 17 | 0 | 35 | 35 | 0 | 0 | 0 | 106 | 0 | 320 | 0 | 0 | 271 | 9 | 672 | 400 | 300 | 0 |  | 635 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 158 | 0 | 291 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 180 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 307 | 0 | 189 | 746 | 0 | 0 |  | 7153 | 4606 | 11759 | 3722 | 635 | 2419 | 0 | 1266 | 3525 | 30 | 0 | 107 | 46 | 0 | 9 | 87 | 73.43
22:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 297 | 0 |  | 0 | 300 | 205 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 8 | 210 | 0 | 0 | 0 |  | 0 | 56 | 68 | 0 | 76 | 19 | 10 | 19 | 0 | 0 | 0 | 285 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 16 | 0 | 80 | 110 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 265 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 68 | 0 | 317 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 64 | 38 | 60 | 310 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 0 | 270 | 0 | 0 | 270 | 6 | 778 | 300 | 250 | 0 |  | 635 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 158 | 0 | 220 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 150 | 720 | 0 | 0 |  | 5916 | 3919 | 9835 | 3351 | 635 | 1860 | 0 | 503 | 3246 | 30 | 0 | 124 | 80 | 0 | 6 | 0 | 73.43
23:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 282 | 0 |  | 0 | 300 | 203 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 30 | 102 | 0 | 8 | 210 | 0 | 0 | 0 |  | 0 | 24 | 46 | 0 | 66 | 19 | 10 | 20 | 0 | 0 | 0 | 295 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 94 | 115 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 100 | 18 | 0 | 0 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 60 | 340 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 0 | 240 | 0 | 0 | 268 | 6 | 775 | 250 | 250 | 0 |  | 582 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 160 | 0 | 220 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 140 | 635 | 0 | 0 |  | 5599 | 3569 | 9168 | 3311 | 582 | 1814 | 0 | 334 | 2927 | 30 | 0 | 70 | 94 | 0 | 6 | 0 | 73.43
24:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 300 | 0 |  | 0 | 350 | 224 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 24 | 34 | 0 | 31 | 6 | 10 | 18 | 0 | 0 | 0 | 270 | 140 | 0 | 0 | 0 | 37 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 100 | 136 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 320 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 49 | 360 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 17 | 0 | 240 | 0 | 0 | 272 | 7 | 638 | 300 | 250 | 0 |  | 634 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 186 | 0 | 414 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 140 | 631 | 0 | 0 |  | 5685 | 4147 | 9832 | 3699 | 634 | 2221 | 0 | 251 | 2832 | 30 | 0 | 58 | 100 | 0 | 7 | 0 | 73.43
KWH | 0 | 0 | 0 | 2425500 | 0 | 1605818 | 0 | 9446400 | 0 |  | 0 | 9327000 | 6929775 | 625920 | 719248 | 594015 | 7383421 | 0 | 0 | 523258 | 899568 | 602400 | 0 | 0 | 0 | 0 | 476640 | 538581 | 431695 | 0 | 440000 | 167040 | 329980 | 316200 | 142704 | 0 | 0 | 676000 | 2100000 | 0 | 179485 | 5018854 | 0 | 0 | 0 |  | 307680 | 974172 | 1216051 | 0 | 820800 | 129600 | 203424 | 192480 | 0 | 0 | 0 | 7237600 | 4548000 | 4334000 | 117090 | 0 | 711936 | 802560 | 0 | 1062802 | 0 | 261776 | 639691 | 0 | 0 | 607200 | 161470 | 2112000 | 2145140 | 0 | 0 | 11700 | 700000 | 161520 | 1096200 | 821088 | 2478354 | 0 | 1433280 | 0 | 0 | 2397660 | 272000 | 0 | 0 | 7057000 | 314448 | 65520 | 0 | 2022327 | 0 | 0 | 688800 | 0 | 1290816 | 127305 | 1236480 | 2232960 | 113745 | 8692000 | 588000 | 469421 | 383054 | 9481 | 293564 | 493571 | 480071 | 1624500 | 1036560 | 1288320 | 8357700 | 384960 | 260130 | 1442880 | 780327 | 0 | 382680 | 202736 | 1202880 | 0 | 7273700 | 541964 | 0 | 6501817 | 342240 | 14327272 | 9511363 | 7580455 | 493455 |  | 19717818 | 0 | 8388000 | 0 | 0 | 0 | 0 | 0 | 45120 | 140416 | 0 | 2495000 | 205094 | 165888 | 0 | 0 | 0 | 115662 | 55861 | 192560 | 0 | 219175 | 172582 | 37013 | 159426 | 0 | 0 | 184752 | 1625890 | 0 | 5591000 | 0 | 0 | 0 | 0 | 4591573 | 0 | 0 | 0 | 4535018 | 0 | 8164581 | 422400 | 0 | 1168032 | 0 | 951657 | 0 | 38454 | 1079136 | 22993200 | 4991523 | 0 | 28800 | 15300 | 596160 | 1173504 | 0 | 0 | 7374545 | 85354 | 4308200 | 16564494 | 577130 | 0 |  | 179951278 | 119170318 | 299121596 | 97438336 | 19717818 | 61943183 | 0 | 30710406 | 79286418 | 676000 | 0 | 4477990 | 2112000 | 2417205 | 342240 | 0
Fuel Cost | 0 | 0 | 0 | 10793475 | 0 | 6134224.76 | 0 | 27205632 | 0 |  | 0 | 29659860 | 23699830.5 | 12368179.2 | 13449937.6 | 10466544.3 | 22519434.05 | 0 | 0 | 10339578.08 | 16147245.6 | 11698608 | 0 | 0 | 0 | 0 | 8703446.4 | 8488036.56 | 7895701.55 | 0 | 330000 | 0 | 0 | 0 | 2555828.64 | 0 | 0 | 0 | 11466000 | 0 | 3399445.9 | 16010144.26 | 0 | 0 | 0 |  | 5412091.2 | 17155168.92 | 21779473.41 | 0 | 16063056 | 2133216 | 756737.28 | 0 | 0 | 0 | 0 | 20192904 | 13916880 | 14388880 | 392251.5 | 0 | 2399224.32 | 3515212.8 | 0 | 4261836.02 | 0 | 4688408.16 | 11552819.46 | 0 | 0 | 2258784 | 121102.5 | 13854720 | 6671385.4 | 0 | 0 | 0 | 2730000 | 602469.6 | 4987710 | 3735950.4 | 8475970.68 | 0 | 7954704 | 0 | 0 | 6689471.4 | 1789760 | 0 | 0 | 21806130 | 235836 | 49795.2 | 0 | 41255470.8 | 0 | 0 | 13231848 | 0 | 22731269.76 | 0 | 22021708.8 | 38741856 | 1885892.1 | 23033800 | 11207280 | 8806337.96 | 6871988.76 | 0 | 4799771.4 | 9595020.24 | 8612473.74 | 31044195 | 20119629.6 | 22944979.2 | 22231482 | 6571267.2 | 0 | 26390275.2 | 13093887.06 | 0 | 6838491.6 | 0 | 21675897.6 | 0 | 21602889 | 7630853.12 | 0 | 45317664.49 | 0 | 84530904.8 | 0 | 0 | 0 |  | 55407068.58 | 0 | 24744600 | 0 | 0 | 0 | 0 | 0 | 848707.2 | 2641224.96 | 0 | 7884200 | 972145.56 | 2859909.12 | 0 | 0 | 0 | 2071506.42 | 1025049.35 | 3236933.6 | 0 | 4179667.25 | 3090943.62 | 655130.1 | 2855319.66 | 0 | 0 | 139857.264 | 17933566.7 | 0 | 47188040 | 0 | 0 | 0 | 0 | 15289938.09 | 0 | 0 | 0 | 15101609.94 | 0 | 23840576.52 | 7214592 | 0 | 23150394.24 | 0 | 18957007.44 | 0 | 0 | 21410058.24 | 148995936 | 15523636.53 | 0 | 557280 | 0 | 0 | 20360294.4 | 0 | 0 | 53834178.5 | 0 | 32096090 | 109491305.34 | 0 | 0 |  | 1016690234.08 | 683556766.624 | 1700247000.704 | 299110995.304 | 55407068.58 | 147005335.27 | 0 | 566758999.3 | 539387685.83 | 0 | 0 | 78722196.42 | 13854720 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 400 | 0 |  | 0 | 450 | 304 | 16 | 25 | 4 | 311 | 0 | 0 | 16 | 49 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 22 | 20 | 25 | 0 | 8 | 0 | 0 | 30 | 100 | 0 | 1 | 210 | 0 | 0 | 0 |  | 18 | 40 | 51 | 0 | 19 | 0 | 10 | 2 | 0 | 0 | 0 | 290 | 175 | 215 | 0 | 0 | 26 | 48 | 0 | 51 | 0 | 8 | 25 | 0 | 0 | 32 | 0 | 102 | 100 | 0 | 0 | 2 | 30 | 0 | 50 | 37 | 112 | 0 | 61 | 0 | 0 | 100 | 18 | 0 | 0 | 285 | 8 | 5 | 0 | 83 | 0 | 0 | 56 | 0 | 51 | 20 | 49 | 85 | 6 | 316 | 47 | 35 | 34 | 0 | 16 | 19 | 34 | 70 | 37 | 49 | 350 | 17 | 51 | 120 | 17 | 0 | 35 | 30 | 62 | 0 | 335 | 54 | 0 | 270 | 11 | 375 | 460 | 350 | 76 |  | 920 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 181 | 0 | 315 | 9 | 0 | 92 | 0 | 67 | 0 | 5 | 95 | 960 | 220 | 0 | 0 | 4 | 93 | 90 | 0 | 0 | 310 | 10 | 150 | 758 | 72 | 0 |  | 13207 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 100 | 0 | 77 | 0 | 402 | 0 |  | 0 | 400 | 301 | 96 | 95 | 40 | 312 | 0 | 0 | 69 | 90 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 22 | 19 | 25 | 30 | 16 | 0 | 0 | 30 | 77 | 0 | 25 | 210 | 0 | 0 | 0 | 0 | 18 | 57 | 51 | 0 | 51 | 0 | 10 | 0 | 0 | 0 | 0 | 310 | 170 | 182 | 0 | 0 | 34 | 20 | 0 | 51 | 0 | 23 | 40 | 0 | 0 | 28 | 14 | 126 | 111 | 0 | 0 | 0 | 30 | 20 | 50 | 40 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 285 | 16 | 0 | 0 | 253 | 0 | 0 | 105 | 0 | 149 | 0 | 62 | 130 | 6 | 330 | 96 | 105 | 51 | 0 | 16 | 54 | 51 | 97 | 84 | 60 | 360 | 34 | 0 | 162 | 67 | 0 | 34 | 0 | 96 | 0 | 320 | 163 | 0 | 270 | 20 | 430 | 350 | 300 | 0 |  | 920 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 5 | 52 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 33 | 4 | 90 | 0 | 25 | 38 | 0 | 28 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 153 | 0 | 346 | 17 | 0 | 94 | 0 | 92 | 0 | 0 | 95 | 910 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 306 | 0 | 200 | 753 | 0 | 0 |  | 14353 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 400 | 0 |  | 0 | 450 | 310 | 100 | 80 | 40 | 335 | 0 | 0 | 80 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 20 | 25 | 32 | 16 | 0 | 0 | 30 | 118 | 0 | 25 | 210 | 0 | 0 | 0 |  | 22 | 64 | 51 | 0 | 90 | 19 | 10 | 20 | 0 | 0 | 0 | 300 | 240 | 205 | 90 | 0 | 34 | 50 | 0 | 51 | 0 | 41 | 52 | 0 | 0 | 33 | 20 | 151 | 100 | 0 | 0 | 0 | 43 | 28 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 162 | 18 | 0 | 0 | 300 | 25 | 5 | 0 | 300 | 0 | 0 | 108 | 0 | 149 | 0 | 60 | 136 | 6 | 400 | 97 | 105 | 34 | 0 | 16 | 54 | 51 | 114 | 75 | 70 | 360 | 53 | 0 | 162 | 72 | 0 | 42 | 0 | 95 | 0 | 350 | 163 | 0 | 270 | 40 | 760 | 500 | 450 |  |  | 655 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 33 | 25 | 90 | 0 | 34 | 42 | 8 | 28 | 0 | 0 | 11 | 75 | 0 | 230 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 414 | 90 | 0 | 113 | 0 | 92 | 0 | 0 | 95 | 1244 | 220 | 0 | 27 | 0 | 0 | 115 | 0 | 0 | 375 | 0 | 307 | 748 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 | 0 | 0 | 450 | 310 | 90 | 80 | 40 | 335 | 0 | 0 | 60 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 20 | 25 | 32 | 16 | 0 | 0 | 30 | 118 | 0 | 8 | 210 |  | 0 | 0 | 0 | 12 | 40 | 50 | 0 | 20 | 6 | 10 | 5 | 0 | 0 | 0 | 300 | 240 | 205 | 90 | 0 | 34 | 50 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 33 | 20 | 146 | 100 | 0 | 0 | 1.6 | 43 | 28 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 162 | 18 | 0 | 0 | 300 | 25 | 5 | 0 | 210 | 0 | 0 | 56 | 0 | 52 | 20 | 36 | 100 | 6 | 400 | 50 | 35 | 17 | 5 | 16 | 17 | 17 | 70 | 36 | 40 | 340 | 17 | 50 | 90 | 35 | 0 | 17 | 35 | 54 | 0 | 350 | 54 | 0 | 270 | 40 | 350 | 500 | 360 | 33 |  | 940 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 42 | 8 | 0 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 180 | 0 | 414 | 90 | 0 | 35 | 0 | 56 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 375 | 30 | 200 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 100 | 0 | 15 | 0 | 335 | 0 | 0 | 0 | 300 | 259 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 6 | 10 | 10 | 0 | 0 | 0 | 300 | 140 | 28 | 0 | 0 | 35 | 33 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 32 | 6 | 94 | 122 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 17 | 0 | 315 | 8 | 0 | 0 | 2 | 16 | 0 | 0 | 17 | 9 | 12 | 310 | 0 | 6 | 0 | 17 | 0 | 17 | 9 | 17 | 0 | 240 | 0 | 0 | 270 | 0 | 750 | 250 | 250 | 37 | 0 | 923 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 347 | 0 | 0 | 0 | 0 | 16 | 0 | 1 | 0 | 540 | 180 | 0 | 0 | 0 | 41 | 17 | 0 | 0 | 310 | 5 | 170 | 534 | 25 | 0 | 0 |  |  |  | 159381519 | 19717818 | 0 | 79286418 | 35188396 | 2112000 | 2417205 | 342240 | 676000 |  |  | 299121596
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 | [5 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 159.3815 | 19.7178 | 0 | 79.2864 | 35.1884 | 2.112 | 2.4172 | 0.34224 | 0.676
| Minimum Generation |  | 10874 | 8:00
| Highest Generation |  | 14353 | 19:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 299.1216
| Day Peak Generation |  | 13207 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 14353 | 19:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 926 | 4:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 920 | 19:00
| Load factor L.F |  | 86.83% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-06
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13207 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 9606
Evening Peak Generation : |  |  | 14353 | MW Hour : | 19:00 | Available Max Generation : |  | 16789
E.P. Demand (at gen end) : |  |  | 14400 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 14353 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2789
Total Gen. (MKWH) : |  |  | 299.1216 | System Load Factor : | 86.83% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -360 | MW at | 23:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-06
Actual : |  | 73.43 | Ft.(MSL) , | Rule curve : | 81.05 | Ft.( MSL )
Gas Consumed : |  | Total = | 1170.65 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 446116330.574
: |  |  | Coal : | 539387685.83 | Oil : | 645481195.72 | Total : | 1630985212.124
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 35 | 840:00 | 5342.4914 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | 0%
Khulna Area |  | 10 | 240:00 | 2064.3332 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1476.7776 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1099.0436 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 1004.2252 |  |  | 0 | 0%
Total |  | 45 |  | 15383.887 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:22 | Dohazari 132/33kV S/S Power Transformer -T-2 LT is restored.
| 08:45 | Hathazari-Kaptai 132kV Ckt-1 is restored.
08:56 | 11:05 | Baroaulia-Hathazari 132 kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end Due to Removing tin foil from
line.
| 08:58 | Sylhet 132/33kV S/S 20 MW PP is restored.
| 09:08 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt is restored.
09:15 | 17:32 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Project Work S/D Due to AR Modificaton
09:18 | 22:18 | Aminbazar-Meghnaghat 400kV Ckt-1 Project Work S/D from Meghnaghat 400/230kV end Due to Project Work S/D
| 09:25 | Hathazari-Kaptai 132kV Ckt-2 is restored.
10:02 | 02:01 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ghorashal 230kV end showing Distance Protection Relay relays.
10:05 | 10:45 | Pabna 132/33kV S/S T-1 HT Scheduled S/D |  |  |  |  | 40.0MW load interrup.
10:05 | 10:45 | Pabna 132/33kV S/S T-1 LT Scheduled S/D |  |  |  |  | 40.0MW load interrup.
10:06 | 10:46 | Pabna 132/33kV S/S T-2 HT Scheduled S/D |  |  |  |  | 20.0MW load interrup.
10:06 | 10:46 | Pabna 132/33kV S/S T-2 LT Scheduled S/D |  |  |  |  | 20.0MW load interrup.
10:37 | 17:15 | Bogura-Sirajganj 230 kV Ckt-2 Scheduled S/D from Sirajgonj 230 end Due to DS connnect to new transformer at Bogura
end. and from Bogura 230/132kV end Due to Busbar Stabllity Test &DS Connect With 230 kv Bus
11:00 | 11:06 | Sonargaon 132/33kV S/S Tr-2 LT Tripped showing DIR O/C & E/F relay O/C trip relays Due to Anondha Bazar 33 kv |  |  |  |  | 30.0MW load interrup.
feeder fault, Cable fault
11:59 | 19:23 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
12:00 |  | Day Peak Generation: 13207 MW.
12:18 | 21:12 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D
12:19 | 21:13 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D
14:05 |  | Fenchugonj CCPP Phase-2 Syncronized with remarks:- unit-3
14:59 | 15:09 | Fenchuganj-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance Relay relays Due to Triped by
fault
15:13 | 15:23 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance Protection 21/1: Z1,BN
relays Due to Unknown
16:28 |  | 132 kv bus section-1 & bus section 2 normalised at Rohonpur 400/132 KV S/S. 132 kv bus coupler 1 & bus coupler 2
shutdown at Rohonpur 400/132 KV S/S.
16:40 |  | Gulsan-Rampura 132kV Ckt-2 Project Work S/D from Rampura 230/132kV end Due to Due to Y phase cable fault checking.
| 17:07 | Chandraghona-Kaptai 132 kV Ckt-1 is restored.
| 17:15 | Chandraghona-Kaptai 132 kV Ckt-2 is restored.
17:33 | 18:18 | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing Distance protection relay relays. and
from Ghorashal 230kV end showing Distance Protection Relay, F21.2 relays.
18:15 | 18:34 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Tripped showing DIR O/C & E/F Relay relays Due to Manda 33 kv |  |  |  |  | 30.0MW load interrup.
feeder fault
| 18:45 | Bogura 230/132kV S/S 230KV Main 2 is restored.
18:56 | 19:40 | Kishoreganj-Mymensingh 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing Z1, y-phase Distance
Relay 4.4km relays Due to Z1, y-phase Distance Relay 4.4km and from Mymensingh 132/33kV end showing
Siprotec7SA87(Distance Relay) relays Due to Due to Dist. (B,C ),Z1 ,Line protection E/F(50N/51N), 47.8KM
19:00 |  | Evening Peak Gen. 14353 MW
19:27 |  | 132 kv bus coupler 1 syn Rohonpur 400/132 KV S/S.
19:28 |  | 132 kv bus coupler 2 syn Rohonpur 400/132 KV S/S.
19:35 | 20:29 | Ashuganj-Brahmanbaria 132kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing Distance relays.
20:31 |  | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing Distance relays. and from
Shahjibazar 132/33kV end showing Distance relays Due to stormy weather
20:51 | 21:08 | Bhaluka-Mymensingh 132 kV Ckt-2 Tripped from Bhaluka 132/33kV end showing O/C,E/F Relay relays Due to Thundering
20:51 | 21:08 | Bhaluka-Mymensingh 132 kV Ckt-1 Tripped from Bhaluka 132/33kV end showing O/C,E/F Relay. relays Due to
Thunderouing
20:51 |  | Ashuganj CCPP 225 MW Tripped with remarks:- GT
21:10 | 23:09 | Kabirpur -Kodda 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance Relay( Distance Start-T), SOTF, DTT-1
received, DTT-1 send. relays.
21:18 | 21:30 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Z1, BN relays Due to Heavy Thundering
& Rainfall at Narsindi end.
21:23 | 21:38 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance relay, Zone-1, B-phase.
relays.
21:23 | 22:12 | Kabirpur-Kaliakoir 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing Distance relay (Distance start-T).
relays.
21:32 | 22:48 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing Distance Relay, Y- Phase,
Distance -22.5 relays Due to Stormy weather. and from Kabirpur 132/33kV end showing Distance relay, Zone-1,
B-phase. relays.
21:45 | 01:34 | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing siemens 7sa87 sotf, 147.1 KM DFDR
108-132 Km relays. and from Ghorashal 230kV end showing Distance Protection Relay relays Due to None
22:02 | 02:02 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing siemens 7sa87 sotf, 127-132 Km
relays.
22:17 |  | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Scheduled S/D from Shahjibazar 132/33kV end Due to B-Baria end breaker is not
closing (Pole discrepancy)
22:35 | 23:58 | Keranigonj 230/132/33kV S/S Hasnabad Tripped showing SOTF trip, B-Phase pick-up(Distance: 3.90km), Trip relay
Operated. relays Due to Thundering
22:41 | 23:42 | Keranigonj 230/132/33kV S/S Lalbagh-3 Tripped showing SOTF trip, R-Y Phase Pick-up,86.1 trip relay operated relays Due
to Thundering
22:45 | 23:20 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Iniatation relays Due to Rain storm
22:45 | 23:24 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing lock out, OC/EF relays Due
to Baishaki Rain storm
22:45 | 23:09 | Matuail-Siddhirganj 132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing Lock Out,Distance relay trip zone :2 |  |  |  |  | 45.0MW load interrup.
Siddhirganj 132/33kV end
relays Due to Baisaki Storm, lightning erresror.
22:46 | 23:17 | Haripur-Siddirganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Z3, AN, DEF relays Due to Heavy
Thundering & Rainfall
22:51 | 23:58 | Aggreko-keraniganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing P-Phase pick-up,50/67N EF
trip,Trip Relay Operated. relays Due to Thundering
22:59 | 23:09 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing PH Y, Z1, Dist.Send relays Due to Heavy Thundering &
Rainfall
23:41 | 00:38 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Master trip relay relays Due to Unknown
23:43 | 23:52 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Over current protection relay relays Due to Due to 33kV Agla Feeder
fault
00:14 |  | Ashuganj CCPP 225 MW Syncronized with remarks:- GT
06:00 |  | Minimum generation 9606 MW
06:02 |  | Lalmonirhat-Rangpur 132 kV Ckt-2 Forced S/D from Rangpur 132/33kV end Due to Maintenance Work |  |  |  |  | 28.0MW load interrup.
Rangpur 132/33kV end
06:42 | 07:36 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to 33kv Datter Feeder Red hot. |  |  |  |  | 16.0MW load interrup.
06:42 | 07:36 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to 33kv Datterhat Feeder Red hot. |  |  |  |  | 16.0MW load interrup.
07:25 |  | Chapainawabganj-Rahanpur 132kV Ckt-1 Project Work S/D from Chapai 132/33kV end. and from Rahanpur 400/132kV end Due to
DFDR work
07:33 |  | Bogura 230/132kV S/S 132KV Main 2 Scheduled S/D Due to project work for transformer T04 commissioning.
21:12 |  | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Tripped showing
lockout relay relays Due to CT of 33kV was damage
06:02 |  | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D Due to
33 kV Bus coupler rearrange
06:03 |  | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D Due to
33 kV Bus coupler rearrange
07:00 |  | Minimum generation 12387 MW
07:02 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
33kV Underground Cable Replace
07:11 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
33kV Underground Cable Replace
07:17 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to
33kV Busbar Maintenance
07:18 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to
33kV Busbar Maintenance
07:40 |  | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to
Maintenance Work
07:40 |  | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to
Maintenance Work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 100 | 2425500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 77 | 1605818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 402 | 9446400
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9327000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 96 | 625920 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 301 | 6929775 | Meghna Bus section Over Load
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 95 | 719248
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 594015 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 69 | 523258
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 312 | 7383421
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 899568 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 476640
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 131 | 602400
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 538581
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 431695
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 607040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 329980 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 316200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 142704 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 253 | 2022327 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1290816 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 469421
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 34 | 384960 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1442880
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 202736
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 350 | 9511363 | low demand
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 300 | 7580455 | On test.
| Dhaka area Total |  |  |  | 5332 | 3722 | 66830121
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 77 | 2100000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 179485
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 127305
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 129600 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 676000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 210 | 5018854
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 383054 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 57 | 974172 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 1216051 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired from 17/04/2024
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 1236480 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 203424 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 192480
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 820800 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 9481
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 293564 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 493571
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 480071 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 1288320 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 67 | 780327 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 541964
60 | SS Power I |  | SS Power | 2*612 | 1224 | 270 | 6501817 | Madunaghat Transformer Over Load
| Cox's Bazar Wind |  | IPP | 66 | 60 | 20 | 342240 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 430 | 14327272
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 493455
| Chattogram area Total |  |  |  | 4404 | 1755 | 38809787
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4334000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7237600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 170 | 4548000 | ST under maint
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 320 | 7273700 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 711936 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 20 | 802560 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 117090 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1062802
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 113745 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 23 | 261776 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 130 | 2232960 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2112000
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 28 | 607200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 40 | 639691
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 14 | 161470 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1624500 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 84 | 1036560 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 34 | 382680
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 1202880 | Engine problem
| Cumilla Area Total |  |  |  | 2929 | 1765 | 36463150
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 111 | 2145140 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11700
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 105 | 688800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 588000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 260130
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 307680 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 330 | 4001450
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 700000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 161520 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 80 | 2478354 | ST under maint
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1096200
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 40 | 821088 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 65520 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1433280
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 2397660 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 272000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 314448
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7057000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 330 | 8692000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 360 | 8357700 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1392 | 33846770
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 19717818
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0 | Contract Expired
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 5 | 45120 | low demand
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 140416 | low demand
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8388000 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 422400 | low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 596160
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 306 | 7374545
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1670 | 36684459
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 165888 | low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 205094 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2495000 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 910 | 22993200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 4991523
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 28800 | reserve.
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 4308200
| Barisal Area Total |  |  |  | 2235 | 1396 | 35187705
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 33 | 115662 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 55861 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 25 | 219175 | low demand
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 172582 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 149 | 4591573
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 153 | 4535018 | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 346 | 8164581
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 159426
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 184752
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 37013
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 192560 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1168032 | Fuel shortage
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1079136 | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 15300
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 753 | 16564494
| Rajshahi Area Total |  |  |  | 3431 | 1816 | 37255165
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1625890
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5591000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 92 | 951657 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38454
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1173504
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 85354
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 577130
| Rangpur Area Total |  |  |  | 950 | 507 | 10042989
| Total |  |  |  | 25903 | 14353 | 299121596
| Eastern Grid Total |  |  |  | 15588 | 8964 | 179951278
| Western Grid Total |  |  |  | 10315 | 5389 | 119170318
| National Grid Total |  |  |  | 25903 | 14353 | 299121596
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-05
| (a) ENTIRE EASTERN GRID : |  | 9198.15 | MW | (b) ENTIRE WESTERN GRID : |  | 4643.7 | MW
| i) Dhaka area |  | 5489.65 | MW | i) Khulna area |  | 1805.6 | MW
| ii) Chittagong area |  | 1415.5 | MW | ii) Rajshahi area |  | 1639.6 | MW
| iii) Comilla area |  | 1281 | MW | iii) Barisal area |  | 481.5 | MW
| iv) Mymensingh area |  | 849 | MW | iv) Rangpur area |  | 717 | MW
| v) Sylhet area |  | 163 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13841.85 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 17 | 16:00 | Kalurghat | 38 | 14:00 | Narail | 64 | 00:00 | Shariatpur | 90 | 00:00
2 | AKSML | 98 | 06:00 | Chowmuhani | 253 | 21:00 | Kamrangirchar | 58.2 | 13:00 | Narinda | 82 | 13:00 | Sherpur | 130 | 19:00
3 | Aftabnagar | 60 | 16:00 | Chuadanga | 120 | 02:00 | Kaptai | N/A | N/A | Narshingdi | 164 | 19:00 | Shikalbaha | 27 | 19:00
4 | Agargaon | 120 | 13:00 | Coxsbazar | 136 | 19:00 | Kazla | 81 | 01:00 | Natore | 168 | 19:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 76 | 17:00 | Cumilla(N) | 178 | 02:00 | Keranigonj | 90 | 19:00 | Nawabganj | 66.8 | 21:00 | Shitalakhya | 110.9 | 16:00
6 | Amnura | 90 | 00:00 | Cumilla(S) | 166 | 00:00 | Khagrachori | 34 | 20:00 | Netrakona | 87 | 17:00 | Sholosohor | 46 | 23:00
7 | Ashuganj | 72 | 13:00 | Daudkandi | 132 | 19:00 | Khulna | 94 | 00:00 | New | 60 | 12:00 | Shyampur | 170 | 10:00
8 | BIPTC | N/A | N/A | Dhaka | 36 | 12:00 | Khulshi | 182 | 00:00 | Niamatpur | 104 | 00:00 | Siddhirganj | 114 | 18:30
9 | BSRM | 170 | 04:00 | Dhamrai | 130 | 16:00 | Kishoreganj | 125 | 15:00 | Noapara | 53 | 20:00 | Sirajganj | 128 | 19:30
10 | Bagerhat | 110 | 23:00 | Dhanmondi | 170.3 | 13:00 | Kodda | 285 | 19:00 | PHP | 9 | 18:30 | Sonargaon | 105 | 01:00
11 | Bakulia | 102 | 20:00 | Dohazari | 97 | 22:00 | Kulaura | 40 | 00:00 | Pabna | 138 | 20:00 | Sreemongol | 63 | 01:00
12 | Banani | 80.4 | 14:00 | Faridpur | 180 | 00:00 | Kurigram | 48 | 00:00 | Palashbari | 86 | 19:30 | Sreepur | 70 | 19:30
13 | Bangabhaban | 17 | 10:00 | Fatullah | 73 | 12:00 | Kushtia | 164 | 23:00 | Panchagarh | 49 | 19:00 | Srinagar | 51.2 | 21:00
14 | Barapukuria | 60 | 02:00 | Fenchuganj | 32 | 14:00 | Lalbag | 98 | 13:00 | Patuakhali | 102.1 | 00:00 | Sunamganj | 32 | 15:00
15 | Barguna | 24 | 00:00 | Feni | 122 | 19:00 | Lalmonirhat | 48 | 00:00 | Payra | 29 | 23:00 | Sylhet | 28 | 21:00
16 | Barishal | 123 | 23:00 | GPH | 94 | 06:00 | MI_Cement | 11.2 | 18:30 | Postogola | 64 | 00:00 | Sylhet-132 | 114 | 14:00
17 | Barishal-230 | 114 | 00:00 | Ghatail | 48 | 19:00 | Madanganj | 34 | 00:00 | Purbachal | 13 | 15:00 | TK | 33.5 | 20:00
18 | Baroaulia | 70 | 22:00 | Ghorashal | 72 | 16:00 | Madaripur | 123 | 22:00 | Purbasadipur | 134 | 00:00 | Tangail | 230 | 19:00
19 | Baroirhat | 63 | 21:00 | Goalpara | 42 | 23:00 | Madartek | 104.45 | 00:00 | Rahim | 20 | 11:00 | Thakurgaon | 94 | 19:30
20 | Bashundhara | 222 | 14:00 | Gollamari | 84 | 00:00 | Madunaghat | 53 | 19:00 | Rajbari | 90 | 22:00 | Tongi | 127 | 19:00
21 | BashundharaCement | 12 | 00:00 | Gopalganj | 117.2 | 01:00 | Magura | 72 | 23:00 | Rajendrapur | 108 | 19:00 | Ullahpara | 27 | 18:00
22 | Beanibazar | 37 | 12:00 | Gulshan | 82 | 00:00 | Mahasthangarh | 74 | 19:30 | Rajshahi | 180 | 00:00 | Ullon | 66 | 00:00
23 | Benapole | 80 | 14:00 | Halishahar | 94 | 16:00 | Manikganj | 146 | 19:30 | Rajshahi-230 | 54 | 00:00 | Uttara | 105 | 17:00
24 | Bhaluka | 122 | 18:30 | HaripurSBU | 186 | 00:00 | Maniknagar | 92 | 13:00 | Ramganj | 116 | 21:00 | UttaraNew | 43 | 19:30
25 | Bhandaria | 60 | 23:00 | Hasnabad | 102 | 00:00 | Matarbari | 48 | 21:00 | Rampur | 40 | 22:00 | Zigatola | 98 | 15:00
26 | Bhangura | 51 | 21:00 | Hathazari | 80 | 00:00 | Matuail | 78 | 15:00 | Rangamati | 16 | 19:00
27 | Bheramara(GK) | 75 | 21:00 | Ishurdi | 91 | 19:30 | Millgate | 127 | 12:00 | Rangpur | 123 | 13:00
28 | Bhulta | 238 | 20:00 | Jaldhaka | 68 | 00:00 | Mirpur | 164 | 16:00 | Ruppur | 5.6 | 12:00
29 | Bog-Sherpur | 64 | 19:00 | Jamalpur | 134 | 19:00 | Mirsorai | 6 | 00:00 | SSM | 15 | 00:00
30 | Bogura | 172 | 21:00 | Jashore | 155 | 21:00 | Mirzapur | 57 | 19:30 | Saidpur | 99 | 09:00
31 | Borhanuddin | 86 | 22:00 | Jhenaidah | 143 | 23:00 | Mithapukur | 50 | 01:00 | Satkhira | 141 | 02:00
32 | Brahmanbaria | 159 | 02:00 | Joydebpur | 199 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 129 | 19:00
33 | Cantonment | 172 | 17:00 | Joypurhat | 61 | 14:00 | Mogbazar | 154.5 | 15:00 | Savar | 220 | 16:00
34 | Chandpur | 81 | 21:00 | Juldah | 21 | 11:00 | Mongla | 41 | 14:00 | SevenRings | 17.97 | 16:00
35 | Chandraghona | 36 | 20:00 | KSRM | 52.5 | 08:00 | Motijheel | 61 | 13:00 | ShahCement | 19 | 00:00
36 | Chapai | 80 | 22:00 | Kabirpur | 272 | 11:00 | Munshiganj | 116 | 00:00 | Shahjadpur | 99 | 21:00
37 | Charsaidpur | 41 | 16:00 | Kachua | 85 | 19:00 | Mymensingh | 196 | 18:30 | Shahjibazar | 90 | 14:00
38 | Chauddagram | 76 | 20:00 | Kallyanpur | 129 | 00:00 | Naogaon | 148 | 00:00 | Shahmirpur | 54 | 17:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 401 | 22:00 | 383 | 15:00 | Kaliakoir | 382 | 03:00 | 358 | 11:00
| Ashuganj | 420 | 14:50 | 396 | 11:00 | Madunaghat_I | 400 | 18:00 | 392 | 01:00
| Bhulta | 411 | 03:00 | 387 | 11:00 | Meghnaghat | 240 | 23:00 | 226 | 15:00
| Bibiana | 405 | 22:00 | 390 | 15:00 | Payra | 411 | 06:00 | 404 | 00:00
| BIPTC | 408 | 21:00 | 394 | 15:00 | Rahanpur | 420 | 18:00 | 409 | 11:00
| Bogura | 419 | 18:30 | 402 | 11:00 | Rampal | 405 | 08:00 | 391 | 00:00
| Gopalganj | 404 | 23:00 | 391 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 239 | 23:00 | 217 | 11:00 | Hasnabad | 240 | 23:00 | 220 | 15:00
| AKSML | 227 | 21:00 | 218 | 03:00 | Hathazari | 225 | 18:00 | 219 | 01:00
| Aminbazar | 238 | 23:00 | 218 | 10:00 | Ishurdi | 236 | 06:00 | 224 | 15:00
| Ashuganj | 239 | 06:00 | 229 | 15:00 | Jhenaidah | 226 | 08:00 | 213 | 15:00
| Ashuganj-400 | 239 | 6:00 | 229 | 15:00 | Kaliakoir | 233 | 03:00 | 218 | 11:00
| Baghabari | 232 | 02:00 | 225 | 14:00 | Keranigonj | 239 | 23:00 | 217 | 11:00
| Barapukuria | 221 | 17:00 | 210 | 08:00 | Khulna(S) | 228 | 08:00 | 216 | 00:00
| Barapukuria-230 | 221 | 17:00 | 210 | 8:00 | Madunaghat_I | 227 | 18:00 | 222 | 09:00
| Barishal | 238 | 07:00 | 233 | 02:00 | Maniknagar | 238 | 23:00 | 221 | 11:00
| Bheramara | 235 | 03:00 | 222 | 15:00 | Meghnaghat | 244 | 23:00 | 230 | 10:00
| Bhulta | 238 | 23:00 | 222 | 11:00 | Meghnaghat-400 | 240 | 23:00 | 226 | 15:00
| Bibiana | 233 | 07:00 | 225 | 11:00 | Mirsorai | 231 | 20:00 | 218 | 16:00
| BIPTC | 236 | 06:00 | 223 | 03:00 | Rajshahi | 232 | 06:00 | 218 | 15:00
| Bogura | 228 | 18:00 | 216 | 11:00 | Rampal | 230 | 08:00 | 218 | 00:00
| Bogura-400 | 229 | 18:00 | 218 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 07:00 | 236 | 01:00 | Rampura | 238 | 23:00 | 219 | 11:00
| BSRM | 228 | 20:00 | 220 | 04:00 | Shikalbaha | 223 | 19:00 | 216 | 04:00
| Cumilla(N) | 235 | 22:00 | 220 | 20:00 | Shyampur | 239 | 23:00 | 220 | 11:00
| Fenchuganj | 238 | 21:00 | 231 | 09:00 | Siddhirganj | 263 | 21:00 | 224 | 11:00
| Ghorashal | 244 | 23:00 | 230 | 00:00 | Sirajgonj | 239 | 02:00 | 234 | 10:00
| Ghorashal-230 | 238 | 22:00 | 221 | 11:00 | Sreepur | 236 | 02:00 | 225 | 15:00
| GPH | 226 | 20:00 | 218 | 15:00 | Tongi | 238 | 22:00 | 213 | 11:00
| Haripur | 237 | 23:00 | 220 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 138 | 22:00 | 126 | 14:00 | Kushtia | 135 | 08:00 | 127 | 15:00
| Agargaon | 141 | 23:00 | 129 | 11:00 | Lalbag | 139 | 03:00 | 127 | 11:00
| Agrabad | 132 | 18:00 | 126 | 03:00 | Lalmonirhat | 131 | 15:00 | 120 | 08:00
| AKS | 130 | 18:00 | 125 | 00:00 | Madanganj | 138 | 23:00 | 125 | 11:00
| Aminbazar | 146 | 23:00 | 129 | 10:00 | Madaripur | 134 | 07:00 | 129 | 01:00
| Amnura | 135 | 18:30 | 125 | 14:00 | Madartek | 137 | 23:00 | 124 | 15:00
| Ashuganj | 142 | 04:00 | 135 | 15:00 | Madunaghat | 132 | 18:00 | 127 | 01:00
| Bagerhat | 132 | 08:00 | 120 | 22:00 | Magura | 135 | 07:00 | 126 | 15:00
| Bakulia | 134 | 08:00 | 128 | 16:00 | Mahasthangarh | 137 | 18:00 | 127 | 10:00
| Banani | 139 | 06:00 | 124 | 11:00 | Manikganj | 134 | 21:00 | 119 | 11:00
| Bangabhaban | 140 | 23:00 | 126 | 15:00 | Maniknagar | 141 | 23:00 | 127 | 11:00
| Barapukuria | 138 | 17:00 | 127 | 08:00 | Matarbari | 126 | 10:00 | 112 | 23:00
| Barguna | 134 | 12:00 | 124 | 00:00 | Matuail | 137 | 22:00 | 127 | 11:00
| Barishal | 135 | 07:00 | 119 | 00:00 | Millgate | 142 | 22:00 | 123 | 11:00
| Barishal-230 | 135 | 07:00 | 131 | 02:00 | Mirpur | 144 | 23:00 | 128 | 11:00
| Baroaulia | 132 | 07:00 | 127 | 01:00 | Mirzapur | 140 | 21:00 | 125 | 00:00
| Baroirhat | 133 | 22:00 | 122 | 16:00 | Mithapukur | 135 | 18:00 | 122 | 07:00
| Bashundhara | 142 | 22:00 | 123 | 11:00 | MI_Cement | 137 | 22:00 | 127 | 09:00
| BashundharaCement | 138 | 23:00 | 125 | 11:00 | Modern | 133 | 18:00 | 128 | 16:00
| Beanibazar | 137 | 00:00 | 128 | 13:00 | Mogbazar | 140 | 23:00 | 125 | 11:00
| Benapole | 132 | 08:00 | 120 | 15:00 | Mongla | 132 | 18:00 | 122 | 00:00
| Bhaluka | 135 | 02:00 | 122 | 16:00 | Motijheel | 140 | 23:00 | 126 | 15:00
| Bhandaria | 132 | 12:00 | 115 | 00:00 | Munshiganj | 139 | 23:00 | 127 | 10:00
| Bhangura | 135 | 02:00 | 131 | 00:00 | Mymensingh | 141 | 21:00 | 121 | 16:00
| Bheramara | 135 | 03:00 | 130 | 14:00 | Naogaon | 131 | 18:00 | 123 | 10:00
| Bheramara(GK) | 136 | 06:00 | 130 | 15:00 | Narail | 136 | 07:00 | 126 | 19:00
| Bhulta | 134 | 22:00 | 121 | 09:00 | Narinda | 141 | 23:00 | 127 | 11:00
| Bog-Sherpur | 135 | 02:00 | 128 | 10:00 | Narshingdi | 140 | 21:00 | 121 | 11:00
| Bogura | 138 | 18:00 | 117 | 13:00 | Natore | 130 | 06:00 | 121 | 15:00
| Bogura-230 | 138 | 18:00 | 128 | 11:00 | Nawabganj | 140 | 22:00 | 127 | 15:00
| Brahmanbaria | 140 | 21:00 | 127 | 15:00 | Netrakona | 137 | 02:00 | 120 | 15:00
| Cantonment | 141 | 23:00 | 128 | 11:00 | New | 142 | 22:00 | 126 | 15:00
| Chandpur | 138 | 22:00 | 121 | 03:00 | Niamatpur | 140 | 08:00 | 134 | 00:00
| Chandraghona | 132 | 07:00 | 127 | 01:00 | Noapara | 135 | 08:00 | 125 | 00:00
| Chapai | 137 | 18:00 | 131 | 00:00 | Pabna | 133 | 06:00 | 127 | 15:00
| Charsaidpur | 139 | 23:00 | 126 | 11:00 | Palashbari | 133 | 17:00 | 122 | 08:00
| Chauddagram | 135 | 22:00 | 125 | 01:00 | Panchagarh | 138 | 17:00 | 114 | 07:00
| Chhatak | 136 | 00:00 | 127 | 15:00 | Patuakhali | 132 | 08:00 | 127 | 00:00
| Chowmuhani | 130 | 22:00 | 118 | 16:00 | Payra | 135 | 07:00 | 131 | 00:00
| Chuadanga | 130 | 08:00 | 117 | 14:00 | PHP | 133 | 23:00 | 122 | 02:00
| Coxsbazar | 124 | 12:00 | 113 | 19:00 | Postogola | 140 | 23:00 | 128 | 10:00
| Cumilla(N) | 138 | 22:00 | 129 | 16:00 | Purbachal | 142 | 22:00 | 122 | 11:00
| Cumilla(S) | 138 | 04:00 | 126 | 16:00 | Purbasadipur | 134 | 17:00 | 111 | 07:00
| Daudkandi | 138 | 22:00 | 126 | 15:00 | Rahanpur | 142 | 18:00 | 136 | 11:00
| Dhaka | 137 | 05:00 | 125 | 11:00 | Rahim | 141 | 23:00 | 128 | 11:00
| Dhamrai | 145 | 23:00 | 123 | 11:00 | Rajbari | 132 | 06:00 | 123 | 19:00
| Dhanmondi | 140 | 23:00 | 127 | 11:00 | Rajendrapur | 139 | 03:00 | 124 | 11:00
| Dohazari | 131 | 09:00 | 126 | 16:00 | Rajshahi | 131 | 06:00 | 123 | 14:00
| Faridpur | 134 | 08:00 | 125 | 15:00 | Rajshahi-230 | 133 | 06:00 | 124 | 15:00
| Fatullah | 140 | 23:00 | 127 | 11:00 | Ramganj | 133 | 18:00 | 118 | 02:00
| Fenchuganj | 138 | 03:00 | 132 | 12:00 | Rampur | 132 | 08:00 | 127 | 01:00
| Feni | 131 | 22:00 | 122 | 03:00 | Rampura | 138 | 06:00 | 125 | 11:00
| Ghatail | 141 | 21:00 | 124 | 15:00 | Rangamati | 133 | 07:00 | 125 | 15:00
| Ghorashal | 148 | 22:00 | 132 | 14:00 | Rangpur | 134 | 17:00 | 119 | 08:00
| Goalpara | 138 | 08:00 | 127 | 15:00 | Ruppur | 136 | 06:00 | 129 | 15:00
| Gollamari | 137 | 18:30 | 130 | 00:00 | Saidpur | 134 | 17:00 | 116 | 07:00
| Gopalganj | 134 | 08:00 | 127 | 00:00 | Satkhira | 132 | 08:00 | 122 | 00:00
| Gopalganj-400 | 151 | 11:00 | 129 | 00:00 | Satmasjid | 140 | 23:00 | 129 | 11:00
| Gulshan | 137 | 03:00 | 124 | 15:00 | Savar | 141 | 22:00 | 127 | 10:00
| Halishahar | 132 | 07:00 | 127 | 16:00 | SevenRings | 149 | 22:00 | 131 | 11:00
| Haripur | 141 | 23:00 | 128 | 11:00 | ShahCement | 139 | 23:00 | 126 | 11:00
| HaripurSBU | 141 | 23:00 | 130 | 10:00 | Shahjadpur | 137 | 04:00 | 133 | 13:00
| Hasnabad | 140 | 23:00 | 128 | 11:00 | Shahjibazar | 138 | 21:00 | 127 | 13:00
| Hathazari | 134 | 18:00 | 128 | 00:00 | Shahmirpur | 134 | 18:00 | 129 | 16:00
| Ishurdi | 136 | 06:00 | 130 | 15:00 | Shariatpur | 133 | 08:00 | 126 | 00:00
| Jaldhaka | 133 | 17:00 | 114 | 07:00 | Sherpur | 143 | 00:00 | 121 | 15:00
| Jamalpur | 141 | 00:00 | 124 | 15:00 | Shikalbaha | 124 | 18:00 | 119 | 01:00
| Jashore | 133 | 08:00 | 123 | 15:00 | Shikalbaha-230 | 135 | 08:00 | 130 | 04:00
| Jhenaidah | 136 | 07:00 | 127 | 19:00 | Shitalakhya | 137 | 22:00 | 127 | 09:00
| Jhenaidah-230 | 137 | 08:00 | 128 | 15:00 | Sholosohor | 132 | 18:00 | 127 | 01:00
| Joydebpur | 145 | 03:00 | 127 | 11:00 | Shyampur | 137 | 23:00 | 126 | 10:00
| Joypurhat | 129 | 18:00 | 113 | 23:00 | Shyampur-230 | 139 | 23:00 | 126 | 11:00
| Juldah | 135 | 18:00 | 131 | 00:00 | Siddhirganj | 138 | 22:00 | 128 | 11:00
| Kabirpur | 141 | 22:00 | 120 | 11:00 | Sirajganj | 134 | 02:00 | 128 | 09:00
| Kachua | 138 | 22:00 | 122 | 02:00 | Sonargaon | 139 | 23:00 | 127 | 10:00
| Kaliakoir | 142 | 02:00 | 127 | 11:00 | Sreemongol | 136 | 21:00 | 127 | 12:00
| Kallyanpur | 134 | 23:00 | 123 | 15:00 | Sreepur | 136 | 02:00 | 127 | 15:00
| Kalurghat | 132 | 08:00 | 127 | 03:00 | Srinagar | 141 | 22:00 | 127 | 15:00
| Kamrangirchar | 141 | 23:00 | 121 | 15:00 | SSM | 136 | 06:00 | 130 | 08:00
| Kaptai | 135 | 1:00 | 130 | 3:00 | Sunamganj | 135 | 03:00 | 126 | 15:00
| Kazla | 139 | 23:00 | 126 | 11:00 | Sylhet | 135 | 00:00 | 129 | 15:00
| Keranigonj | 141 | 23:00 | 128 | 11:00 | Sylhet-132 | 136 | 00:00 | 129 | 13:00
| Khagrachori | 132 | 08:00 | 124 | 03:00 | Tangail | 139 | 21:00 | 124 | 11:00
| Khulna | 136 | 08:00 | 127 | 00:00 | Thakurgaon | 138 | 17:00 | 110 | 07:00
| Khulna(S) | 138 | 08:00 | 129 | 00:00 | TK | 132 | 07:00 | 127 | 16:00
| Khulshi | 131 | 18:00 | 126 | 16:00 | Tongi | 142 | 22:00 | 126 | 11:00
| Kishoreganj | 139 | 02:00 | 127 | 15:00 | Ullahpara | 135 | 18:00 | 130 | 13:00
| Kodda | 148 | 22:00 | 122 | 11:00 | Ullon | 139 | 22:00 | 125 | 11:00
| KSRM | 132 | 18:00 | 126 | 03:00 | Uttara | 144 | 23:00 | 126 | 15:00
| Kulaura | 137 | 05:00 | 131 | 13:00 | UttaraNew | 142 | 22:00 | 128 | 10:00
| Kurigram | 134 | 17:00 | 120 | 07:00 | Zigatola | 140 | 06:00 | 127 | 15:00

## L-Curve
Date | 2024-05-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 66 | 5685 | 4147 | 9832 |  |  |  | QF-LDC-11
0:30 | 149 | 6825 | 4826 | 11651 | Date: | 2024-05-05
1:00 | 232 | 7965 | 5505 | 13470
1:30 | 219 | 7820 | 5352 | 13172
2:00 | 206 | 7675 | 5199 | 12874
2:30 | 232 | 7278.5 | 4726 | 12004.5 | [5 empty] | Gen. at Eve. Peak | 14353 | 14353 MW (19:00 )
3:00 | 258 | 6882 | 4253 | 11135 | [6 empty] | 19:00
3:30 | 203 | 6894 | 4271 | 11165 | [5 empty] | Gen. at Day Peak | 13207 | 13207 MW (12:00 )
4:00 | 148 | 6906 | 4289 | 11195 | [6 empty] | 12:00
4:30 | 115 | 6912 | 4291.5 | 11203.5 | [5 empty] | Highest Generation | 14353
5:00 | 82 | 6918 | 4294 | 11212 | [6 empty] | 19:00
5:30 | 129 | 6907 | 4195 | 11102
6:00 | 176 | 6896 | 4096 | 10992
6:30 | 163 | 6882.5 | 4123 | 11005.5
7:00 | 150 | 6869 | 4150 | 11019
7:30 | 196 | 6769.5 | 4177 | 10946.5
8:00 | 242 | 6670 | 4204 | 10874
8:30 | 325 | 6857.5 | 4387.5 | 11245
9:00 | 408 | 7045 | 4571 | 11616
9:30 | 474 | 7170 | 4666.5 | 11836.5
10:00 | 540 | 7295 | 4762 | 12057
10:30 | 660 | 7399.5 | 4917.5 | 12317
11:00 | 780 | 7504 | 5073 | 12577
11:30 | 728 | 7674.5 | 5217.5 | 12892
12:00 | 676 | 7845 | 5362 | 13207
12:30 | 634 | 8024 | 5391 | 13415
13:00 | 592 | 8203 | 5420 | 13623
13:30 | 550 | 8221.5 | 5435.5 | 13657
14:00 | 508 | 8240 | 5451 | 13691
14:30 | 630 | 8290.5 | 5518.5 | 13809
15:00 | 752 | 8341 | 5586 | 13927
15:30 | 786 | 8318.5 | 5632 | 13950.5
16:00 | 820 | 8296 | 5678 | 13974
16:30 | 836 | 8309.5 | 5565 | 13874.5
17:00 | 852 | 8323 | 5452 | 13775
17:30 | 710.5 | 8155.5 | 5238.5 | 13394
18:00 | 569 | 7988 | 5025 | 13013
18:30 | 485.5 | 8476 | 5207 | 13683
19:00 | 402 | 8964 | 5389 | 14353
19:30 | 304 | 8757 | 5534 | 14291
20:00 | 210 | 8718 | 4941 | 13659 |  |  |  | Executive Engineer
20:30 | 238 | 7935.5 | 4773.5 | 12709 |  |  |  | Network Operation Division
21:00 | 266 | 7153 | 4606 | 11759
21:30 | 158.5 | 6534.5 | 4262.5 | 10797
22:00 | 51 | 5916 | 3919 | 9835 |  |  |  |  | Page 6 of 7
22:30 | 205.5 | 5757.5 | 3744 | 9501.5
23:00 | 360 | 5599 | 3569 | 9168
23:30 | 213 | 5642 | 3858 | 9500
24:00 | 66 | 5685 | 4147 | 9832
14353 MW (19:00 )
13207 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-05 |  | Energy |  | 299121596
[15 empty] | 2024-05-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3699 | 634 | 2221 | 0 | 251 | 2832 | 30 | 0 | 58 | 100 | 0 | 7 | 0
0:30 | 3900 | 637.5 | 2643 | 0 | 852.5 | 3319.5 | 30 | 0 | 153 | 111 | 0 | 4.5 | 157.575 |  |  | Date: | 43955
1:00 | 4101 | 641 | 3065 | 0 | 1454 | 3807 | 30 | 0 | 248 | 122 | 0 | 2 | 315.15
1:30 | 4093 | 641.5 | 2906 | 0 | 1361.5 | 3797 | 30 | 0 | 218.5 | 120 | 0 | 4.5 | 265.49 | [9 empty] | Total Energy | 299.1216 | 299.1216 | Total Energy Gen 299.122 MKWHr Energy Not Served 1.116 MKWHr Energy Requirement 300.238 MKWHr
2:00 | 4085 | 642 | 2747 | 0 | 1269 | 3787 | 30 | 0 | 189 | 118 | 0 | 7 | 215.83 | [9 empty] | Energy not Served | 1.1164 | 1.1164
2:30 | 3927.5 | 692.5 | 2663 | 0 | 972.5 | 3438 | 30 | 0 | 158 | 115 | 0 | 8 | 150.89 | [9 empty] | Energy Requirement | 300.238 | 300.238
3:00 | 3770 | 743 | 2579 | 0 | 676 | 3089 | 30 | 0 | 127 | 112 | 0 | 9 | 85.95
3:30 | 3889 | 834.5 | 2577.5 | 0 | 616 | 3034 | 30 | 0 | 118.5 | 56 | 0 | 9.5 | 42.975 | [8 empty] | Shortage
4:00 | 4008 | 926 | 2576 | 0 | 556 | 2979 | 30 | 0 | 110 | 0 | 0 | 10 | 0
4:30 | 4030.5 | 926 | 2609.5 | 0 | 497.5 | 2987 | 30 | 0 | 105 | 7 | 0 | 11 | 0
5:00 | 4053 | 926 | 2643 | 0 | 439 | 2995 | 30 | 0 | 100 | 14 | 0 | 12 | 0
5:30 | 4043.5 | 846.5 | 2609.5 | 0 | 441.5 | 2995.5 | 30 | 0 | 100 | 17 | 6.5 | 12 | 0
6:00 | 4034 | 767 | 2576 | 0 | 444 | 2996 | 30 | 0 | 100 | 20 | 13 | 12 | 0
6:30 | 4035 | 767.5 | 2582 | 0 | 420.5 | 2992 | 30 | 0 | 100 | 27 | 42 | 9.5 | 0 | [7 empty] | Coal
7:00 | 4036 | 768 | 2588 | 0 | 397 | 2988 | 30 | 0 | 100 | 34 | 71 | 7 | 0
7:30 | 4040.5 | 768 | 2515.5 | 0 | 378 | 2982.5 | 15 | 0 | 100 | 41 | 96.5 | 9.5 | 0 | [6 empty] | Oil
8:00 | 4045 | 768 | 2443 | 0 | 359 | 2977 | 0 | 0 | 100 | 48 | 122 | 12 | 0
8:30 | 4152 | 842 | 2511.5 | 0 | 382 | 3018.5 | 0 | 0 | 103.5 | 55 | 171.5 | 9 | 0
9:00 | 4259 | 916 | 2580 | 0 | 405 | 3060 | 0 | 0 | 107 | 62 | 221 | 6 | 0
9:30 | 4226.5 | 916 | 2593.5 | 0 | 467 | 3185.5 | 15 | 0 | 107 | 75 | 236.5 | 14.5 | 0
10:00 | 4194 | 916 | 2607 | 0 | 529 | 3311 | 30 | 0 | 107 | 88 | 252 | 23 | 0
10:30 | 4230.5 | 917 | 2743.5 | 0 | 702.5 | 3190.5 | 30 | 0 | 127 | 93 | 266.5 | 16.5 | 0
11:00 | 4267 | 918 | 2880 | 0 | 876 | 3070 | 30 | 0 | 147 | 98 | 281 | 10 | 0
11:30 | 4187.5 | 919 | 2824 | 0 | 1235 | 3098 | 30 | 0 | 166 | 100 | 322 | 10.5 | 25.5
12:00 | 4108 | 920 | 2768 | 0 | 1594 | 3126 | 30 | 0 | 185 | 102 | 363 | 11 | 51
12:30 | 4121.5 | 920 | 2788.5 | 0 | 1782.5 | 3125.5 | 30 | 0 | 186 | 105 | 338.5 | 17.5 | 44
13:00 | 4135 | 920 | 2809 | 0 | 1971 | 3125 | 30 | 0 | 187 | 108 | 314 | 24 | 37
13:30 | 4135 | 920 | 2809 | 0 | 1971 | 3125 | 30 | 0 | 187 | 108 | 314 | 24 | 37
14:00 | 4135 | 920 | 2809 | 0 | 1971 | 3125 | 30 | 0 | 187 | 108 | 314 | 24 | 37
14:30 | 4210.5 | 920 | 2784.5 | 0 | 2037 | 3194 | 30 | 0 | 187 | 114 | 270 | 28 | 53.5
15:00 | 4286 | 920 | 2760 | 0 | 2103 | 3263 | 30 | 0 | 187 | 120 | 226 | 32 | 70
15:30 | 4228.5 | 920 | 2793.5 | 0 | 2118 | 3291.5 | 30 | 0 | 215 | 119 | 198.5 | 36.5 | 71.5
16:00 | 4171 | 920 | 2827 | 0 | 2133 | 3320 | 30 | 0 | 243 | 118 | 171 | 41 | 73
16:30 | 4156 | 920 | 2767.5 | 0 | 2184 | 3280 | 30 | 0 | 253 | 113 | 130 | 41 | 72.5
17:00 | 4141 | 920 | 2708 | 0 | 2235 | 3240 | 30 | 0 | 263 | 108 | 89 | 41 | 72
17:30 | 3946.5 | 920.5 | 2471.5 | 0 | 2352.5 | 3160 | 30 | 0 | 319 | 112 | 50.5 | 31.5 | 53.5
18:00 | 3752 | 921 | 2235 | 0 | 2470 | 3080 | 30 | 0 | 375 | 116 | 12 | 22 | 35
18:30 | 3912.5 | 920.5 | 2362.5 | 0 | 2660 | 3124.5 | 30 | 0 | 525 | 121 | 6 | 21 | 40
19:00 | 4073 | 920 | 2490 | 0 | 2850 | 3169 | 30 | 0 | 675 | 126 | 0 | 20 | 45
19:30 | 4120 | 919 | 2564 | 0 | 2570 | 3257 | 30 | 0 | 698 | 122 | 0 | 11 | 42
20:00 | 4172 | 634 | 2710 | 0 | 2268 | 3330 | 30 | 0 | 387 | 122 | 0 | 6 | 39
20:30 | 3947 | 634.5 | 2564.5 | 0 | 1767 | 3427.5 | 30 | 0 | 247 | 84 | 0 | 7.5 | 63
21:00 | 3722 | 635 | 2419 | 0 | 1266 | 3525 | 30 | 0 | 107 | 46 | 0 | 9 | 87
21:30 | 3536.5 | 635 | 2139.5 | 0 | 884.5 | 3385.5 | 30 | 0 | 115.5 | 63 | 0 | 7.5 | 43.5
22:00 | 3351 | 635 | 1860 | 0 | 503 | 3246 | 30 | 0 | 124 | 80 | 0 | 6 | 0
22:30 | 3331 | 608.5 | 1837 | 0 | 418.5 | 3086.5 | 30 | 0 | 97 | 87 | 0 | 6 | 0
23:00 | 3311 | 582 | 1814 | 0 | 334 | 2927 | 30 | 0 | 70 | 94 | 0 | 6 | 0
23:30 | 3505 | 608 | 2017.5 | 0 | 292.5 | 2879.5 | 30 | 0 | 64 | 97 | 0 | 6.5 | 0 |  |  | Max Temp. in Dhaka |  | 36.7°C
24:00 | 3699 | 634 | 2221 | 0 | 251 | 2832 | 30 | 0 | 58 | 100 | 0 | 7 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 299.122 MKWHr Energy Not Served 1.116 MKWHr Energy Requirement 300.238 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 676000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 107 | 100 | 100 | 70 | 75 | 75 | 72 | 73 |  | 77 | 75 | 80 | 80 | 100 | 102 | 100 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | [9 empty] | 1 | 8 | 8 | 8 | 8 | 9 | 17 |  | 25 | 25 | 25 | 25 | 8 | 8 |  | 179485
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 0 | 10 | 14 | 18 | 20 | 20 | 19 | 17 | 13 | 10 | 10 | 3 | [8 empty] | 127305
6 | Sikalbaha 225MW CCPP (Gas) | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 214 | 211 | 211 | 210 | 211 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 5018854
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 68 | 46 | 34 | 1216051
12 | Hathazari 100 MW peaking PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 32 | 32 | 32 | 40 | 41 | 41 | 40 | 40 | 40 | 42 |  | 57 | 56 | 49 | 56 | 56 | 24 | 24 | 974172
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | [9 empty] | 34 | 34 | 34 | 17 | 17 | 34 | 51 |  | 51 | 51 | 51 | 17 |  |  |  | 383054
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 22 | 21 | 21 | 21 | 22 |  | 23 | 23 | 23 |  |  |  |  | 261776
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 326 | 320 | 327 | 335 | 333 | 335 | 333 | 305 | 323 | 318 | 311 | 311 | 310 | 309 | 307 | 302 | 304 | 250 |  | 312 | 313 | 316 | 270 | 250 | 240 | 250 | 7383421
18 | Kodda 300 MW PP Unit-2 (Summit) | 87 | 15 | [9 empty] | 83 | 210 | 210 | 210 | 200 | 223 | 230 |  | 253 | 195 | 95 |  |  |  |  | 2022327
19 | Ashuganj 195 MW PP (APSCL-United) | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [16 empty] | 117090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2425500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 269 | 268 | 268 | 269 | 270 | 269 | 268 | 270 | 270 | 268 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 271 | 270 | 268 | 272 | 6501817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 31 | 35 | 35 | 35 | 35 | 35 | 36 | 37 | 35 | 35 | 35 | 26 | 27 | 30 | 30 | 32 | 32 | 32 |  | 34 | 34 | 35 |  |  |  | 37 | 711936
33 | Ashuganj 225 MW CCPP | 211 | 205 | 208 | 196 | 194 | 224 | 224 | 222 | 219 | 214 | 200 | 215 | 199 | 212 | 202 | 208 | 212 | 181 |  | 182 | 184 | 183 | 0 |  |  | 0 | 4334000
34 | Ashuganj 450 MW CCPP(South) | 235 | 235 | 190 | 180 | 180 | 180 | 180 | 180 | 180 | 195 | 215 | 175 | 195 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 140 | 140 | 4548000
| Ashuganj 450 MW CCPP(North) | 135 | 207 | 340 | 355 | 356 | 280 | 280 | 280 | 315 | 305 | 335 | 290 | 305 | 280 | 325 | 285 | 280 | 280 |  | 310 | 300 | 285 | 280 | 285 | 295 | 270 | 7237600
| Ashuganj 420 MW CCPP(East) | 335 | 325 |  | 250 | 245 | 260 | 260 | 260 | 300 | 285 | 275 | 335 | 280 | 335 | 360 | 360 | 375 | 320 |  | 320 | 320 | 320 | 320 | 270 | 240 | 240 | 7273700
35 | Ashuganj 55 MW PP (Precision) | 48 | 50 | 49 | 49 | 51 | 51 | 52 | 49 | 52 | 51 | 47 | 48 | 44 | 25 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 |  |  |  | 10 | 802560
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 410 | 414 | 419 | 418 | 419 | 417 | 416 | 406 | 404 | 400 | 400 | 401 | 402 | 401 | 397 | 401 | 353 |  | 402 | 404 | 405 | 404 | 297 | 282 | 300 | 9446400
| Meghnaghat Unique power | 506 | 450 | 400 | 400 | 400 | 400 | 400 | 330 | 325 | 355 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 302 |  | 350 | 396 | 450 | 400 | 300 | 250 | 300 | 9511363
| Summit Meghanghat-2 589 MW(Gas) | 440 | 350 | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 250 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 250 |  | 300 | 300 | 350 | 300 | 250 | 250 | 250 | 7580455
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 350 | 350 | 350 | 350 | 350 | 350 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 340 |  | 400 | 400 | 400 | 400 | 300 | 300 | 350 | 9327000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 71 | 38 | 55 | 70 | 82 | 102 | 102 | 102 | 101 | 100 | 100 | 100 | 91 | 92 | 93 | 96 | 97 | 97 |  | 111 | 128 | 126 | 110 | 110 | 115 | 136 | 2145140
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 8 | 14 | 14 | 22 | 37 | 51 | 43 | 21 | 34 | 21 | 10 | 0 | [8 empty] | 260130
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 700000
45 | Fenchugonj CCPP Phase-2 | [14 empty] | 10 | 10 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 161520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 60 | 61 | 61 | 61 | 61 | 60 | 61 | 59 | 61 | 60 | 61 | 59 | 60 | 56 | 58 | 60 | 63 |  | 63 | 63 | 63 | 64 | 63 | 40 | 62 | 1433280
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2397660
51 | Sylhet 20 MW GTPP | [9 empty] | 18 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 272000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | [11 empty] | 65520
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 1096200
56 | Shahjahanulla 25 MW PP | 8 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 314448
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 280 | 260 | 270 | 290 | 280 | 280 | 265 | 310 | 295 | 310 | 285 | 300 | 290 | 295 | 310 | 285 | 265 |  | 285 | 310 | 305 | 280 | 265 | 270 | 320 | 7057000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 358 | 358 | 380 | 350 | 355 | 345 | 375 | 350 | 350 | 345 |  | 360 | 345 | 345 | 345 | 310 | 340 | 360 | 8357700
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 5 | 17 | 17 | 35 | 35 | 30 | 35 | 35 | 35 | 35 | 35 |  | 35 | 55 | 55 | 17 |  |  |  | 431695
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 5 | 7 | 7 | 12 | 12 | 12 | 13 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 11 |  |  |  |  | 307680
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 7 | 7 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 203424
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 122 | 118 | 112 | 0 | 14 | 20 | 34 | 48 | 62 | 88 | 98 | 102 | 108 | 120 | 120 | 118 | 108 | 116 |  | 126 | 122 | 122 | 46 | 80 | 94 | 100 | 2112000
64 | Malancha, Ctg. EPZ (United) | 25 | 25 | 35 | 35 | 30 | 30 | 25 | 2 | 0 | 0 | 2 | 2 | 2 | 2 | 0 | 0 | 2 | 3 |  | 0 | 2 | 7 | 10 | 19 | 20 | 18 | 192480
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 |  | 32 | 31 | 32 | 24 | 24 | 24 | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 28 |  | 28 | 32 | 32 |  | 16 | 16 | 16 | 607200
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | [9 empty] | 12 | 13 | 13 | 12 | 12 | 12 |  | 14 | 14 | 17 |  |  |  | 8 | 161470
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 0 |  |  |  | 440000
70 | Summit Madhabdi | 19 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 20 | 20 | 0 | 0 | 0 | 0 | 19 |  | 19 | 19 | 20 | 10 | 0 | 0 | 5 | 167040
71 | Maona 33 MW PP(Summit) | 0 | 15 | 8 | 17 | 17 | 17 | 17 | 17 | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 0 | 0 | 8 | 0 | 329980
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 0 | 0 | 0 | 0 | 0 |  | 0 | 16 | 0 | 0 | 26 | 30 | 30 | 31 | 30 | 30 |  | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 316200
73 | Ghorashal 108 MW PP (Regent) | 81 | 81 | 80 | 78 | 78 | 78 | 79 | 76 | 76 | 76 | 77 | 77 | 77 | 73 | 74 | 70 | 77 | 77 |  | 77 | 76 | 77 | 77 |  |  |  | 1605818
| Feni Lanka Power | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 65 | 34 | 34 | 52 | 70 | 70 | 70 | 70 | 70 | 85 | 97 |  | 97 | 97 | 97 | 114 | 64 |  |  | 1624500
| Chowmuhani 113 MW | 38 | 38 | 38 | 38 | 38 | 39 | 32 | 38 | 26 | 26 | 30 | 37 | 36 | 37 | 37 | 37 | 42 | 81 |  | 84 | 84 | 84 | 84 | 38 |  |  | 1036560
| Manikgonj 162MW PP(MPGL) | 90 | 90 | 90 | 17 | [6 empty] | 54 | 120 | 108 | 106 | 108 | 108 | 108 | 108 |  | 162 | 162 | 162 | 35 |  |  |  | 1442880
77 | Siddhirganj 100 PP(Dutch Bangla) | 37 | 32 | [8 empty] | 5 | 16 | 27 | 64 | 68 | 68 | 68 | 73 |  | 69 | 20 | 18 |  |  |  |  | 523258
78 | Gazipur 52 MW PP | 8 | 8 | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 8 |  |  |  | 142704
79 | Kodda 150 MW PP | 16 | 16 | [6 empty] | 16 | 16 | 32 | 32 | 32 | 31 | 31 | 32 | 30 | 115 |  | 131 | 126 | 64 |  |  |  |  | 602400
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 8 |  |  | 639691
| Gazipur 100 MW PP | 17 | 17 | [6 empty] | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 105 | 88 | 88 |  |  |  |  | 469421
| Kaptai 7 MW Solar PP | [13 empty] | 4 | 3 | 2 | 1 | 0 | [8 empty] | 9481
| Jodiac Power | 17 | [9 empty] | 1 | 19 | 41 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 17 | 17 |  |  |  | 493571
| Karnaphuli Power Ltd. | 17 | 17 | [8 empty] | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 51 |  | 51 | 51 | 51 | 17 |  |  |  | 480071
82 | Madanganj 102 PP(Summit) | 80 | 80 | 12 | [8 empty] | 25 | 78 | 78 | 78 | 65 | 65 | 85 |  | 95 | 17 | 30 |  |  |  |  | 719248
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 308 | 263 | 294 | 287 | 313 | 295 | 296 | 302 | 308 | 304 | 300 | 304 | 298 | 302 | 293 | 302 | 304 | 300 |  | 301 | 303 | 303 | 250 | 205 | 203 | 224 | 6929775
87 | Meghnaghat 100 MW(IEL) | 24 | 24 | [8 empty] | 1 | 16 | 25 | 60 | 81 | 82 | 86 | 96 |  | 96 | 9 | 32 |  |  |  |  | 625920
| Meghnaghat 104 MW PP (OPCL) | 16 | 16 | 16 | 16 | [5 empty] | 2 | 16 | 17 | 17 | 17 | 17 | 25 | 33 | 33 |  | 34 | 39 | 48 | 17 |  |  |  | 384960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 36 | 40 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 37 | 37 | 37 | 39 | 0 | 27 | 40 | 40 |  | 40 | 40 | 40 | 40 | 10 | 10 | 10 | 821088
93 | Ashuganj 51 MW PP (Midland) | 26 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 1062802
94 | Gagnagar 102 MW PP (Digital Power) | 25 | 25 | 25 | 25 | [5 empty] | 28 | 49 | 49 | 73 | 73 | 73 | 73 | 76 | 90 |  | 90 | 90 | 90 | 8 |  |  |  | 899568
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | [9 empty] | 6 |  |  | 11 | 18 | 19 | 19 | 19 | 6 | 129600
96 | Chattogram 108 MW PP (ECPV) | 20 | 20 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 30 | 32 | 31 | 33 | 44 | 44 |  | 51 | 60 | 71 | 76 | 76 | 66 | 31 | 820800
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 9 | 25 | 25 | 25 | 25 | 25 | 0 |  |  |  | 4 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 15 |  |  | 594015
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 |  |  |  | 538581
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2478354
102 | Sarishabari 3 MW Solar Plant | [8 empty] | 0 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 11700
103 | Kamalaghat 54 MW PP(Banco Energy) | [10 empty] | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 17 |  |  |  | 476640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 5 | 16 | 8 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 32 | 56 | 56 | 56 | 55 | 58 | 58 | 67 |  | 105 | 105 | 64 | 45 |  |  |  | 688800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | [6 empty] | 1 | 15 | 17 | 51 | 85 | 120 | 133 | 149 | 146 | 149 |  | 149 | 149 | 142 | 76 |  |  |  | 1290816
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 25 | 40 | 62 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1236480
116 | Chandpur 200 MW (Desh energy) | 141 | 101 | 88 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 87 |  | 130 | 136 | 138 | 138 | 68 | 17 |  | 2232960
117 | Ashuganj 150 MW PP (Midland) | 2 | 5 | 6 | 5 | 6 | 6 |  |  |  | 3 | 6 | 6 | 5 | 6 | 5 | 6 | 6 | 8 |  | 6 | 6 | 6 | 6 |  |  |  | 113745
118 | Bibiyana-III 400 MW CCPP | 379 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 397 | 374 | 419 | 316 | 333 | 366 | 415 | 365 | 364 | 318 |  | 330 | 339 | 363 | 365 | 317 | 330 | 353 | 8692000
| Jamalpur 115 MW PP (United) | 2 | 8 | 9 | 9 | [6 empty] | 10 | 47 | 47 | 49 | 49 | 49 | 49 | 49 |  | 96 | 96 | 64 | 8 |  |  |  | 588000
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | [6 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 293564
| Juldah unit-2 (Acorn) | 60 | 48 | 48 | 48 | 48 | 48 | 48 | 25 | 50 | 75 | 75 | 49 | 50 | 50 | 50 | 50 | 50 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 49 | 1288320
| Anlima Energy Ltd. | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  |  | 15 | 17 | 17 | 22 | 35 | 35 | 35 | 36 |  | 67 | 72 | 72 | 35 | 35 | 35 | 35 | 780327
| Bhairob 54.5 MW | 4 | 17 | [5 empty] | 0 | 16 | 17 | 29 | 35 | 35 | 35 | 33 | 32 | 32 | 32 |  | 34 | 0 | [5 empty] | 382680
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 11 | 16 | 22 | 23 | 30 | 33 | 28 | 11 | 14 | 6 | 1 | [8 empty] | 202736
| Chandpur 115(Doreen) | 54 | 46 | 18 | 18 | 18 | 17 | 18 | 17 | 17 | 17 | 23 | 62 | 75 | 75 | 72 | 72 | 81 | 96 |  | 96 | 100 | 102 | 106 | 17 | 17 | 17 | 1202880
| Kanchan Purbachal Power Generation Ltd. | [26 empty] | 0
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | [7 empty] | 24 | 54 | 54 | 17 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 |  |  |  |  | 541964
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 2 | 7 | 9 | 10 | 12 | 12 | 7 | 12 | 6 | 23 | 10 | 11 | 24 | 30 | 32 | 41 | 41 | 22 |  | 20 | 11 | 6 | 9 | 6 | 6 | 7 | 342240
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 12 | 34 | 52 | 65 | 73 | 76 | 70 | 57 | 42 | 26 | 8 | 1 | [8 empty] | 493455
| Matarbari 2*600 MW (CPGCL) | 773 | 776 | 730 | 728 | 726 | 727 | 725 | 728 | 761 | 782 | 372 | 375 | 376 | 368 | 374 | 372 | 380 | 373 |  | 430 | 423 | 492 | 672 | 778 | 775 | 638 | 14327272
120 | Eastern Zone Total | 7965 | 7675 | 6882 | 6906 | 6918 | 6896 | 6869 | 6670 | 7045 | 7295 | 7504 | 7845 | 8203 | 8240 | 8341 | 8296 | 8323 | 7988 |  | 8964 | 8757 | 8718 | 7153 | 5916 | 5599 | 5685 | 179951278
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | [18 empty] | 5 | 29 | 3 |  |  |  |  | 45120
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 55 | 55 | [9 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 20 | 53 | 17 | 26 | 35 | 422400
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 20 | 22 | 39 | 51 | 59 | 93 | 101 | 78 | 61 | 36 | 19 | 3 | [8 empty] | 596160
131 | Rampal 1320 MW (BIFPCL) | 307 | 307 | 308 | 308 | 309 | 309 | 308 | 310 | 312 | 309 | 307 | 310 | 306 | 306 | 307 | 305 | 306 | 307 |  | 306 | 308 | 308 | 307 | 308 | 308 | 308 | 7374545
132 | United Payra Power Ltd. | 17 | [25 empty] | 28800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 |  | 180 | 180 | 220 | 180 | 180 | 180 | 220 | 4991523
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 80 | 16 | [17 empty] | 16 | 16 | [5 empty] | 165888
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 300 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 153 | 200 | 200 | 200 |  | 200 | 200 | 200 | 189 | 150 | 140 | 140 | 4308200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 80 | 80 | 80 | 80 | 80 | 80 | 126 | 126 | 125 | 126 | 124 | 128 | 128 | 126 | 80 | 80 |  | 80 | 80 | 126 | 126 | 80 | 80 | 128 | 2495000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 8 | 8 | 8 | 8 | 7 | 8 | 9 | 8 | 8 | 7 | 7 |  | 10 | 10 | 10 | 10 | 10 | 10 | 4 | 205094
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | 39 | [16 empty] | 12 |  | 52 | 57 | [5 empty] | 140416
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 641 | 642 | 743 | 926 | 926 | 767 | 768 | 768 | 916 | 916 | 918 | 920 | 920 | 921 | 920 | 920 | 920 | 921 |  | 920 | 919 | 634 | 635 | 635 | 582 | 634 | 19717818
147 | Bheramara 410 MW CCPP | 360 | 340 | 340 | 345 | 345 | 345 | 345 | 365 | 375 | 360 | 345 | 345 | 375 | 340 | 385 | 360 | 350 | 250 |  | 370 | 370 | 355 | 345 | 250 | 250 | 410 | 8388000
148 | Payra 1320 MW | 1100 | 1080 | 700 | 660 | 680 | 680 | 680 | 660 | 690 | 760 | 920 | 960 | 970 | 1020 | 1120 | 1110 | 1040 | 880 |  | 910 | 1000 | 1000 | 1040 | 720 | 500 | 540 | 22993200
149
150 | Barapukuria TPP Unit-1 | 69 | 69 | 69 | 71 | 71 | 71 | 69 | 69 | 70 | 71 | 72 | 73 | 71 | 71 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 71 | 73 | 1625890
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5591000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 11 | 29 | 29 |  | 33 | 33 | [5 empty] | 115662
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 0 | 0 | 0 | 4 | 1 | 2 | 3 | 2 | 0 | 0 | [8 empty] | 15300
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 203 | 184 | 182 | 181 | 185 | 182 | 187 | 213 | 211 | 206 | 202 | 189 | 181 | 175 | 175 | 182 | 185 | 160 |  | 149 | 172 | 171 | 160 | 160 | 161 | 186 | 4591573
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 199 | 180 | 180 | 180 | 184 | 180 | 180 | 180 | 203 | 194 | 203 | 181 | 173 | 170 | 175 | 189 | 184 | 140 |  | 153 | 169 | 168 | 158 | 158 | 160 | 186 | 4535018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 304 | 320 | 313 | 337 | 298 | 313 | 330 | 350 | 348 | 406 | 315 | 350 | 336 | 377 | 397 | 370 | 270 |  | 346 | 346 | 347 | 291 | 220 | 220 | 414 | 8164581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 10 | 10 | 10 | 10 | [10 empty] | 4 | 4 | 4 | 4 |  | 4 | 4 | [5 empty] | 55861
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 8 | 8 | 184752
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | 25 | 25 | [9 empty] | 25 | 25 | 25 | 16 | 16 | 25 | 34 |  | 25 | 8 | [5 empty] | 219175
167 | Katakhali 50 MW Peaking PP | 21 | 21 | [12 empty] | 15 | 30 | 30 | 30 |  | 38 | 38 | [5 empty] | 172582
168 | Santahar 50 MW Peaking PP | 25 | 25 | [13 empty] | 20 | 25 | 28 |  | 28 | 28 | [5 empty] | 159426
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | [9 empty] | 8 | 8 | 0 | [10 empty] | 8 | 0 | 37013
170 | Chapainawabganj 100 MW Peaking PP | [14 empty] | 8 | 17 | 16 | 25 |  | 90 | 90 | 34 |  |  |  |  | 192560
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 90 | 113 | [8 empty] | 2 | 92 | 113 | 113 | 94 | 76 | 76 | 76 |  | 94 | 94 | 76 |  |  |  |  | 1168032
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | [8 empty] | 30 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 35 |  |  |  |  | 1079136
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | [6 empty] | 22 | 67 | 81 | 85 | 85 | 92 | 92 | 100 |  | 92 | 92 | 48 |  |  |  |  | 951657
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 2 | 4 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 0 | [8 empty] | 38454
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 36 | 35 | [7 empty] | 30 | 90 | 95 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 55 |  |  |  | 1173504
| Intraco Solar 30 MW | [5 empty] | 0 | 4 | 10 | 8 | 9 | 12 | 10 | 8 | 9 | 8 | 5 | 4 | 1 | [8 empty] | 85354
| Adani Power Jharkhanda Ltd | 752 | 757 | 634 | 563 | 559 | 560 | 558 | 560 | 577 | 741 | 749 | 758 | 752 | 741 | 739 | 763 | 744 | 750 |  | 753 | 756 | 760 | 746 | 720 | 635 | 631 | 16564494
178 | Teesta Solar Limited | [5 empty] | 3 | 21 | 18 | 76 | 59 | 51 | 72 | 33 | 82 | 45 | 50 | 28 | 3 | [8 empty] | 577130