## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-07 | Tuesday
|  | Date (day): | 2024-05-07 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14312.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16421 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-06 | 2024-05-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 160 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 66 | 12 | 75 | 75 | 33 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 365 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 350 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 90 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 290 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 0 | 0 | 80 | 80
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 28 | 40 | 40 | 40 | 15 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 29 | 0 | 0 | 15 | 60 |  | Engine problem.
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 0 | 0 | 60 | 80
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 270 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 16 | 48 | 90 | 12 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 48 | 32 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 20 | 15 | 42 | 42 |  | 38 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 16 | 16 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 210 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 43 | 55 | 52 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 35 | 105
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 17 | 53 | 51 |  | Lube oil shortage.
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 90 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 302 | 250 | 500 | 500
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 300 | 250 | 250 | 450 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 2521 | 2264 | 3491 | 4303 | 757 | 798
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 0 | 118 | 118 | 62 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 1 | 0 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 0 | 6 | 19 | 31 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 211 | 185 | 210 | 210
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 17 | 34 | 71 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 20 | 8 | 40 | 64 | 34
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 0 | 50 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 0 | 36 | 60 | 40 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 0 | 10 | 10 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 0 | 5 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 31 | 0 | 20 | 90 | 18 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 16 | 0 | 16 | 16 | 284
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 54 |  |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 17 | 51 | 59 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 60 | 0 | 40 | 70 | 30 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 31 | 0 | 35 | 72 | 44 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 272 | 270 | 270 | 270 | 954 |  | Coal Shortage.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 44 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 338 | 316 | 350 | 760 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 52 | 0 | 33 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1289 | 853 | 1447 | 2227 | 1827 | 381
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 137 | 203 | 210 | 210 |  | 11 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 305 | 340 | 340 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 180 | 140 | 0 | 0 |  |  | under maint
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 285 | 275 | 350 | 350 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 38 | 38 | 38 | 7
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 50 | 6 | 50 | 50 | 5
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 5 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 8 | 8 | 36 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 2 | 100 | 136 | 64
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 96 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 28 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 0 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 4 | 8 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 70 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 9 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 17 | 42 |  | 12 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 35 | 0 | 54 | 95 |  | 20 | Engine problem
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1331 | 1158 | 1582 | 1804 | 453 | 222
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 136 | 120 | 140 | 62 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 65 | 56 | 108 | 92 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 24 | 50 | 97 | 18 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 25 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 12 | 22
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 162 | 243 | 289.6 | 367 | 62 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 20 | 20 | 20 |  | 70 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 80 | 80 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 5 | 30 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 5 | 30 | 44
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  |  | Contract Expired
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 40 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 102 | 70 | 70 |  | 161 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 300 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 317 | 376 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 350 | 340 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1258 | 1347 | 1440 | 1494 | 0 | 652
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 922 | 923 | 940 | 650
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 44 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 405 | 260 | 400 | 400
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 90 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 55 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 308 | 0 | 375 | 375
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1690 | 1183 | 1949 | 1619 | 702 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 8 | 0 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 80 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 780 | 550 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 170 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 170 | 140 | 200 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1264 | 940 | 1869 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 33 | 19 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 161 | 170 | 200 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 161 | 180 | 200 |  |  | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 348 | 414 | 414 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 28 | 22 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 0 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 3 | 18 | 35 | 95 | 18 |  | Fuel shortage
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 625 | 436 | 748 | 748 |  |  | Engine problem
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1274 | 1195 | 1683 | 2041 | 274 | 84
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 70 | 73 | 73 | 12
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 200 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 38 | 56 | 92 | 21 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 31 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 61 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 448 | 339 | 562 | 510 | 73 | 129
| Total |  |  |  |  | 27054 | 25903 | 11237 | 9522 | 14312.6 | 16421 | 4263 | 2389
A. |  | 2024-05-06 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 11237 | MW at | 12:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 9606 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9522 | MW
3 | Day peak Generation : |  |  | 11237 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9197.45 | MW
4 | Evening peak Generation : |  |  | 9522 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 241.463 | MKWHr | By Solar | 1.7262 | MKWHr
| By Gas : | 145.169 | MKWHr |  | By Oil: | 8.9593 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 62.7877 | MKWHr |  | By Hydro: | 0.696 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.35472 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4263 | MW | Dhaka | 4235.25 | 4235.25 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2389 | MW | Chittagong | 403 | 403 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 6652 | MW | Khulna | 554.4 | 554.4 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1016.28 | MMCFD |  |  | Rajshahi | 1233.6 | 1233.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 408969974.516 | ii) Oil : | Taka | 162041164.14 | Comilla | 670 | 670 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 431559398.76 | Total | Taka | 1002570537.416 | Mymensingh | 901 | 901 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2699.4 | MKWHr. | Sylhet | 364 | 364 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 526 | MW (W to E) at | 19:00 | hrs | Barisal | 111.2 | 111.2 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 10 | MW at | 1:00 | hrs | Rangpur | 725 | 725 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.8°C |  |  | Total | 9197.45 | 9197.45 |  | 0
B. |  | 2024-05-07 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 29.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16421 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
4 | Reserve(Generation end) |  |  |  | 2421 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 300.8349 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7282 | MW at | 3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.7847 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9853 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 17:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.43 |  | (b) Today: | 73.51 |  | (c) Rule Curve: |  | 80.86
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-06 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 305 | 0 |  | 0 | 350 | 258 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 24 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 24 | 17 | 0 | 31 | 0 | 10 | 0 | 0 | 0 | 0 | 270 | 140 | 28 | 0 | 0 | 34 | 10 | 0 | 10 | 0 | 0 | 3 | 0 | 0 | 22 | 0 | 100 | 134 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 49 | 28 | 0 | 419 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 7 | 49 | 388 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 22 | 0 | 240 | 0 | 0 | 274 | 12 | 632 | 350 | 250 | 0 |  | 636 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 0 | 230 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 188 | 0 | 414 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 170 | 632 | 0 | 0 |  | 5937 | 4339 | 10276 | 3879 | 636 | 2282 | 0 | 296 | 3000 | 30 | 0 | 41 | 100 | 0 | 12 | 0 | 73.43
2:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 305 | 0 |  | 0 | 350 | 320 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 33 | 0 | 0 | 0 | 30 | 104 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 24 | 0 | 0 | 31 | 0 | 10 | 7 | 0 | 0 | 0 | 300 | 140 | 44 | 0 | 0 | 36 | 10 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 32 | 0 | 92 | 133 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 305 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 49 | 51 | 0 | 363 | 9 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 26 | 49 | 340 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 34 | 0 | 280 | 0 | 0 | 275 | 8 | 628 | 400 | 250 | 0 |  | 636 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 214 | 0 | 414 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 170 | 626 | 0 | 0 |  | 6105 | 4394 | 10499 | 3928 | 636 | 2396 | 0 | 376 | 3009 | 30 | 0 | 24 | 92 | 0 | 8 | 0 | 73.43
3:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 305 | 0 |  | 0 | 350 | 310 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 32 | 0 | 0 | 0 | 30 | 102 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 24 | 0 | 0 | 31 | 6 | 10 | 23 | 0 | 0 | 0 | 300 | 140 | 48 | 0 | 0 | 36 | 10 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 32 | 0 | 92 | 140 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 49 | 51 | 0 | 328 | 8 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 9 | 49 | 315 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 34 | 0 | 280 | 0 | 0 | 275 | 0 | 609 | 400 | 250 | 0 |  | 685 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 220 | 0 | 414 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 170 | 631 | 0 | 0 |  | 6006 | 4318 | 10324 | 3893 | 685 | 2378 | 0 | 365 | 2857 | 30 | 0 | 24 | 92 | 0 | 0 | 0 | 73.43
4:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 305 | 0 |  | 0 | 350 | 320 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 24 | 0 | 0 | 31 | 6 | 10 | 24 | 0 | 0 | 0 | 300 | 140 | 48 | 0 | 0 | 36 | 10 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 32 | 16 | 88 | 140 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 275 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 49 | 51 | 0 | 306 | 8 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 9 | 49 | 310 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 17 | 0 | 280 | 0 | 0 | 271 | 0 | 604 | 400 | 250 | 0 |  | 685 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 219 | 0 | 400 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 170 | 633 | 0 | 0 |  | 5985 | 4286 | 10271 | 3888 | 685 | 2369 | 0 | 356 | 2831 | 30 | 0 | 24 | 88 | 0 | 0 | 0 | 73.43
5:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 305 | 0 |  | 0 | 350 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 96 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 31 | 6 | 10 | 25 | 0 | 0 | 0 | 300 | 140 | 48 | 0 | 0 | 36 | 10 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 32 | 16 | 92 | 154 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 51 | 0 | 306 | 8 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 9 | 12 | 310 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 17 | 0 | 280 | 0 | 0 | 270 | 0 | 608 | 400 | 250 | 0 |  | 845 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 190 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 170 | 561 | 0 | 0 |  | 5872 | 4189 | 10061 | 3843 | 845 | 2261 | 0 | 229 | 2761 | 30 | 0 | 0 | 92 | 0 | 0 | 0 | 73.43
6:00 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 305 | 0 |  | 0 | 300 | 252 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 31 | 6 | 10 | 25 | 0 | 0 | 0 | 300 | 140 | 48 | 0 | 0 | 37 | 10 | 0 | 10 | 0 | 0 | 8 | 0 | 0 | 32 | 16 | 76 | 143 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 285 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 330 | 8 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 9 | 12 | 325 | 0 | 2 | 0 | 17 | 0 | 17 | 1 | 17 | 0 | 240 | 0 | 0 | 272 | 0 | 607 | 300 | 250 | 4 |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 310 | 0 | 170 | 534 | 1 | 0 |  | 5630 | 3976 | 9606 | 3528 | 922 | 2108 | 0 | 195 | 2736 | 30 | 0 | 0 | 76 | 11 | 0 | 0 | 73.43
7:00 | 0 | 0 | 0 | 100 | 0 | 12 | 0 | 330 | 0 |  | 0 | 300 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 31 | 6 | 10 | 20 | 0 | 0 | 0 | 300 | 250 | 100 | 0 | 0 | 37 | 12 | 0 | 17 | 0 | 0 | 8 | 0 | 0 | 32 | 10 | 70 | 142 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 112 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 17 | 0 | 315 | 8 | 0 | 0 | 0 | 16 | 0 | 0 | 17 | 9 | 12 | 310 | 0 | 4 | 0 | 17 | 0 | 17 | 3 | 17 | 0 | 240 | 0 | 0 | 272 | 0 | 605 | 300 | 250 | 16 |  | 921 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 220 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 310 | 1 | 170 | 533 | 9 | 0 |  | 5860 | 3995 | 9855 | 3677 | 921 | 2145 | 0 | 207 | 2753 | 30 | 0 | 0 | 70 | 52 | 0 | 0 | 73.43
8:00 | 0 | 0 | 0 | 100 | 0 | 15 | 0 | 335 | 0 |  | 0 | 300 | 259 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 31 | 6 | 10 | 10 | 0 | 0 | 0 | 300 | 140 | 28 | 0 | 0 | 35 | 33 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 32 | 6 | 94 | 122 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 17 | 0 | 315 | 8 | 0 | 0 | 2 | 16 | 0 | 0 | 17 | 9 | 12 | 310 | 0 | 6 | 0 | 17 | 0 | 17 | 9 | 17 | 0 | 240 | 0 | 0 | 270 | 0 | 750 | 250 | 250 | 37 |  | 923 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 347 | 0 | 0 | 0 | 0 | 16 | 0 | 1 | 0 | 540 | 180 | 0 | 0 | 0 | 41 | 17 | 0 | 0 | 310 | 5 | 170 | 534 | 25 | 0 |  | 5794 | 4037 | 9831 | 3474 | 923 | 2075 | 0 | 232 | 2877 | 30 | 0 | 0 | 94 | 126 | 0 | 0 | 73.44
9:00 | 0 | 0 | 0 | 100 | 0 | 24 | 0 | 357 | 0 |  | 0 | 370 | 300 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 0 | 0 | 0 | 30 | 100 | 0 | 0 | 210 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 31 | 6 | 10 | 2 | 0 | 0 | 0 | 300 | 140 | 43 | 0 | 0 | 32 | 50 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 32 | 6 | 102 | 122 | 0 | 0 | 0 | 30 | 20 | 11 | 10 | 112 | 0 | 62 | 0 | 0 | 100 | 18 | 0 | 0 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 12 | 12 | 17 | 0 | 315 | 8 | 0 | 0 | 4 | 16 | 0 | 0 | 17 | 11 | 12 | 325 | 0 | 28 | 0 | 17 | 0 | 17 | 9 | 17 | 0 | 240 | 0 | 0 | 270 | 0 | 754 | 250 | 250 | 47 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 344 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 0 | 560 | 180 | 0 | 0 | 1 | 43 | 35 | 0 | 0 | 308 | 7 | 170 | 538 | 73 | 0 |  | 6176 | 4201 | 10377 | 3613 | 923 | 2247 | 0 | 317 | 2902 | 30 | 0 | 16 | 102 | 227 | 0 | 0 | 73.44
10:00 | 0 | 0 | 0 | 100 | 0 | 38 | 0 | 401 | 0 |  | 0 | 370 | 312 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 8 | 0 | 0 | 30 | 105 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 31 | 6 | 12 | 2 | 0 | 0 | 0 | 290 | 140 | 56 | 8 | 0 | 33 | 50 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 24 | 6 | 102 | 118 | 0 | 0 | 1 | 30 | 20 | 11 | 10 | 112 | 0 | 63 | 0 | 0 | 100 | 18 | 0 | 0 | 305 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 40 | 17 | 12 | 29 | 0 | 315 | 8 | 17 | 0 | 4 | 16 | 0 | 0 | 34 | 26 | 25 | 320 | 0 | 18 | 0 | 17 | 0 | 17 | 7 | 27 | 0 | 310 | 0 | 0 | 270 | 0 | 753 | 250 | 250 | 20 |  | 922 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 347 | 0 | 0 | 0 | 0 | 39 | 0 | 2 | 0 | 560 | 180 | 0 | 0 | 1 | 47 | 35 | 0 | 0 | 309 | 4 | 170 | 535 | 53 | 0 |  | 6460 | 4182 | 10642 | 3749 | 922 | 2295 | 0 | 454 | 2900 | 30 | 0 | 16 | 102 | 174 | 0 | 0 | 73.44
11:00 | 0 | 0 | 0 | 100 | 0 | 62 | 0 | 401 | 0 |  | 0 | 450 | 315 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 24 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 25 | 8 | 0 | 0 | 30 | 105 | 0 | 0 | 210 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 31 | 6 | 12 | 2 | 0 | 0 | 0 | 290 | 180 | 107 | 8 | 0 | 35 | 52 | 0 | 43 | 0 | 3 | 25 | 0 | 0 | 24 | 16 | 116 | 118 | 0 | 0 | 1 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 102 | 18 | 0 | 0 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 53 | 19 | 12 | 51 | 0 | 316 | 8 | 35 | 0 | 5 | 16 | 0 | 0 | 34 | 28 | 60 | 320 | 0 | 29 | 0 | 17 | 0 | 19 | 25 | 35 | 0 | 285 | 0 | 0 | 270 | 0 | 354 | 325 | 300 | 66 |  | 922 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 140 | 0 | 311 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 670 | 180 | 0 | 0 | 0 | 66 | 35 | 0 | 0 | 310 | 10 | 170 | 624 | 51 | 0 |  | 6563 | 4507 | 11070 | 3969 | 922 | 2445 | 0 | 596 | 2701 | 30 | 0 | 19 | 116 | 272 | 0 | 0 | 73.45
12:00 | 0 | 0 | 0 | 100 | 0 | 66 | 0 | 401 | 0 |  | 0 | 450 | 300 | 0 | 0 | 28 | 317 | 0 | 0 | 0 | 32 | 16 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 25 | 8 | 0 | 0 | 30 | 105 | 0 | 1 | 211 | 0 | 0 | 0 |  | 18 | 20 | 17 | 0 | 31 | 6 | 12 | 2 | 0 | 0 | 0 | 285 | 180 | 137 | 8 | 0 | 35 | 50 | 0 | 51 | 0 | 8 | 16 | 0 | 0 | 24 | 4 | 82 | 109 | 0 | 0 | 2 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 102 | 18 | 0 | 0 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 43 | 19 | 62 | 51 | 0 | 317 | 0 | 35 | 0 | 4 | 16 | 0 | 0 | 17 | 28 | 60 | 320 | 0 | 25 | 0 | 31 | 0 | 35 | 24 | 35 | 0 | 285 | 0 | 0 | 272 | 0 | 338 | 302 | 300 | 52 |  | 922 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 348 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 3 | 780 | 180 | 0 | 0 | 3 | 55 | 35 | 0 | 0 | 308 | 12 | 170 | 625 | 61 | 0 |  | 6561 | 4676 | 11237 | 3988 | 922 | 2436 | 0 | 663 | 2795 | 30 | 0 | 61 | 82 | 260 | 0 | 0 | 73.45
13:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 387 | 0 |  | 0 | 450 | 300 | 0 | 0 | 40 | 314 | 0 | 0 | 0 | 50 | 0 | 29 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 8 | 0 | 0 | 30 | 100 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 23 | 17 | 0 | 35 | 6 | 12 | 5 | 0 | 0 | 0 | 280 | 180 | 226 | 8 | 0 | 38 | 52 | 0 | 51 | 0 | 8 | 8 | 0 | 0 | 24 | 16 | 66 | 108 | 0 | 0 | 2 | 30 | 20 | 11 | 10 | 80 | 0 | 63 | 0 | 0 | 102 | 18 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 32 | 19 | 62 | 34 | 0 | 315 | 0 | 35 | 0 | 3 | 16 | 0 | 0 | 17 | 26 | 50 | 320 | 0 | 37 | 0 | 35 | 0 | 35 | 25 | 30 | 0 | 285 | 0 | 0 | 270 | 14 | 337 | 300 | 250 | 1 |  | 923 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 140 | 0 | 305 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 5 | 700 | 180 | 0 | 0 | 1 | 41 | 35 | 0 | 0 | 309 | 6 | 150 | 571 | 41 | 0 |  | 6641 | 4459 | 11100 | 4173 | 923 | 2354 | 0 | 673 | 2639 | 30 | 0 | 48 | 66 | 180 | 14 | 0 | 73.45
14:00 | 0 | 0 | 0 | 160 | 0 | 66 | 0 | 347 | 0 |  | 0 | 300 | 290 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 32 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 32 | 8 | 0 | 0 | 30 | 110 | 0 | 8 | 213 | 0 | 0 | 0 |  | 12 | 30 | 17 | 0 | 24 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 140 | 224 | 8 | 0 | 38 | 53 | 0 | 51 | 0 | 8 | 0 | 0 | 0 | 28 | 12 | 76 | 108 | 0 | 0 | 1 | 30 | 20 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 8 | 25 | 34 | 0 | 318 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 60 | 320 | 0 | 34 | 0 | 35 | 0 | 34 | 8 | 10 | 0 | 285 | 0 | 0 | 270 | 25 | 339 | 288 | 250 | 0 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 140 | 0 | 316 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 8 | 540 | 180 | 0 | 0 | 1 | 85 | 35 | 0 | 0 | 311 | 6 | 150 | 481 | 72 | 0 |  | 6102 | 4150 | 10252 | 3848 | 923 | 2183 | 0 | 501 | 2393 | 30 | 0 | 55 | 76 | 218 | 25 | 0 | 73.45
15:00 | 0 | 0 | 0 | 160 | 0 | 66 | 0 | 324 | 0 |  | 0 | 350 | 310 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 32 | 0 | 29 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 33 | 32 | 8 | 0 | 0 | 30 | 100 | 0 | 8 | 210 | 0 | 0 | 0 |  | 13 | 30 | 17 | 0 | 24 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 140 | 194 | 8 | 0 | 38 | 52 | 0 | 51 | 0 | 8 | 0 | 0 | 0 | 28 | 2 | 68 | 108 | 0 | 0 | 1 | 30 | 20 | 11 | 10 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 8 | 40 | 17 | 0 | 364 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 60 | 342 | 0 | 9 | 0 | 17 | 0 | 35 | 2 | 0 | 0 | 330 | 0 | 0 | 272 | 22 | 340 | 300 | 200 | 0 |  | 923 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 75 | 0 | 230 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 10 | 520 | 180 | 0 | 0 | 0 | 32 | 35 | 0 | 0 | 309 | 4 | 150 | 450 | 35 | 0 |  | 6150 | 4139 | 10289 | 3922 | 923 | 2344 | 0 | 486 | 2346 | 30 | 0 | 55 | 68 | 93 | 22 | 0 | 73.46
16:00 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 324 | 0 |  | 0 | 300 | 292 | 0 | 0 | 40 | 230 | 0 | 0 | 0 | 32 | 0 | 22 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 25 | 32 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 184 | 0 | 0 | 0 |  | 12 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 223 | 8 | 0 | 38 | 41 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 32 | 2 | 96 | 122 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 6 | 12 | 0 | 0 | 364 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 12 | 342 | 0 | 2 | 0 | 0 | 0 | 34 | 3 | 0 | 0 | 230 | 0 | 0 | 266 | 14 | 340 | 250 | 230 | 0 |  | 923 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 164 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 500 | 170 | 0 | 0 | 0 | 34 | 35 | 0 | 0 | 309 | 5 | 140 | 437 | 20 | 0 |  | 5517 | 3814 | 9331 | 3607 | 923 | 2009 | 0 | 287 | 2262 | 30 | 0 | 33 | 96 | 70 | 14 | 0 | 73.46
17:00 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 324 | 0 |  | 0 | 300 | 280 | 0 | 0 | 40 | 231 | 0 | 0 | 0 | 16 | 0 | 23 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 25 | 32 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 6 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 140 | 191 | 0 | 0 | 36 | 35 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 32 | 8 | 80 | 124 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 2 | 0 | 0 | 0 | 330 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 310 | 0 | 9 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 268 | 0 | 315 | 250 | 230 | 0 |  | 924 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 200 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 155 | 0 | 298 | 8 | 0 | 0 | 0 | 0 | 0 | 1 | 15 | 500 | 170 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 310 | 1 | 140 | 436 | 19 | 0 |  | 5289 | 3708 | 8997 | 3486 | 924 | 1940 | 0 | 219 | 2238 | 30 | 0 | 33 | 80 | 47 | 0 | 0 | 73.47
18:00 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 364 | 0 |  | 0 | 300 | 278 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 27 | 15 | 25 | 33 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 7 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 140 | 203 | 0 | 0 | 38 | 11 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 32 | 8 | 92 | 123 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 20 | 0 | 0 | 102 | 18 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 17 | 0 | 0 | 0 | 0 | 325 | 2 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 310 | 0 | 2 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 230 | 0 | 0 | 275 | 50 | 317 | 250 | 230 | 0 |  | 923 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 156 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 500 | 170 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 140 | 440 | 3 | 0 |  | 5460 | 3423 | 8883 | 3621 | 923 | 1952 | 0 | 203 | 1942 | 30 | 0 | 63 | 92 | 7 | 50 | 0 | 73.47
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 365 | 0 |  | 0 | 350 | 290 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 25 | 33 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 140 | 203 | 0 | 0 | 38 | 6 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 28 | 8 | 96 | 136 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 55 | 0 | 0 | 2 | 0 | 376 | 24 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 275 | 0 | 0 | 270 | 44 | 316 | 250 | 250 | 0 |  | 923 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 18 | 550 | 170 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 140 | 436 | 0 | 0 |  | 5865 | 3657 | 9522 | 3810 | 923 | 2137 | 0 | 436 | 1982 | 30 | 0 | 64 | 96 | 0 | 44 | 0 | 73.48
19:30 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 365 | 0 |  | 0 | 350 | 290 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 20 | 33 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 35 | 191 | 0 | 0 | 38 | 20 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 28 | 8 | 82 | 135 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 75 | 0 | 0 | 17 | 0 | 364 | 24 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 285 | 0 | 0 | 270 | 41 | 318 | 250 | 250 | 0 |  | 923 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 159 | 0 | 417 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 18 | 530 | 170 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 140 | 436 | 0 | 0 |  | 5769 | 3640 | 9409 | 3676 | 923 | 2154 | 0 | 475 | 1964 | 30 | 0 | 64 | 82 | 0 | 41 | 0 | 0
20:00 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 364 | 0 |  | 0 | 350 | 290 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 0 | 20 | 0 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 310 | 5 | 191 | 0 | 0 | 38 | 20 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 28 | 8 | 92 | 136 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 70 | 0 | 0 | 17 | 0 | 364 | 24 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 285 | 0 | 0 | 270 | 29 | 316 | 250 | 250 | 0 |  | 639 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 159 | 0 | 405 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 560 | 170 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 140 | 435 | 0 | 0 |  | 5672 | 3355 | 9027 | 3618 | 639 | 2145 | 0 | 435 | 1991 | 30 | 0 | 48 | 92 | 0 | 29 | 0 | 73.48
21:00 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 375 | 0 |  | 0 | 350 | 292 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 25 | 8 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 199 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 320 | 0 | 197 | 0 | 0 | 38 | 21 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 138 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 34 | 0 | 0 | 0 | 0 | 364 | 8 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 335 | 0 | 0 | 269 | 26 | 316 | 251 | 250 | 0 |  | 639 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 171 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 463 | 0 | 0 |  | 5522 | 3461 | 8983 | 3851 | 639 | 2168 | 0 | 173 | 2018 | 30 | 0 | 24 | 54 | 0 | 26 | 0 | 73.48
22:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 391 | 0 |  | 0 | 350 | 285 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 32 | 16 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 310 | 0 | 191 | 0 | 0 | 38 | 42 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 40 | 138 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 340 | 0 | 0 | 270 | 43 | 309 | 230 | 200 | 0 |  | 639 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 185 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 457 | 0 | 0 |  | 5339 | 3309 | 8648 | 3860 | 639 | 1997 | 0 | 85 | 1946 | 30 | 0 | 8 | 40 | 0 | 43 | 0 | 73.48
23:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 338 | 0 |  | 0 | 300 | 266 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 310 | 0 | 190 | 0 | 0 | 35 | 40 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 62 | 138 | 0 | 0 | 0 | 30 | 20 | 0 | 0 | 80 | 0 | 40 | 0 | 0 | 103 | 0 | 0 | 0 | 265 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 275 | 34 | 316 | 220 | 200 | 0 |  | 635 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 180 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 180 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 140 | 440 | 0 | 0 |  | 4902 | 3280 | 8182 | 3471 | 635 | 1859 | 0 | 0 | 2113 | 0 | 0 | 8 | 62 | 0 | 34 | 0 | 73.49
24:00 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 305 | 0 |  | 0 | 300 | 287 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 280 | 0 | 190 | 0 | 0 | 35 | 13 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 109 | 0 | 0 | 0 | 30 | 20 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 70 | 0 | 0 | 0 | 260 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 277 | 18 | 310 | 220 | 200 | 0 |  | 637 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71 | 0 | 180 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 140 | 448 | 0 | 0 |  | 4516 | 3302 | 7818 | 3148 | 637 | 1716 | 0 | 0 | 2237 | 0 | 0 | 8 | 54 | 0 | 18 | 0 | 73.49
KWH | 0 | 0 | 0 | 3244500 | 0 | 484045 | 0 | 8312400 | 0 |  | 0 | 8462500 | 6823389 | 0 | 0 | 383486 | 6452339 | 0 | 0 | 0 | 259344 | 189120 | 185359 | 0 | 0 | 0 | 9720 | 106125 | 0 | 0 | 480000 | 375120 | 596700 | 609400 | 155040 | 0 | 0 | 696000 | 1500000 | 0 | 25673 | 4804624 | 0 | 0 | 0 |  | 216720 | 243936 | 146623 | 0 | 463680 | 76800 | 136752 | 253440 | 0 | 0 | 0 | 7516800 | 3003000 | 3181000 | 50182 | 0 | 865440 | 688800 | 0 | 550325 | 0 | 97568 | 170093 | 0 | 0 | 578700 | 113790 | 1985280 | 2964480 | 0 | 0 | 8250 | 715000 | 465480 | 207000 | 297216 | 2118927 | 0 | 1263744 | 0 | 0 | 2415120 | 380000 | 0 | 0 | 7005000 | 361776 | 63024 | 0 | 0 | 0 | 0 | 422400 | 0 | 497088 | 98820 | 499200 | 584640 | 0 | 8159000 | 178800 | 334080 | 0 | 23281 | 250909 | 0 | 0 | 250800 | 304920 | 591360 | 7899100 | 0 | 201720 | 0 | 414000 | 0 | 538200 | 118356 | 370560 | 0 | 6767500 | 0 | 0 | 6534544 | 354720 | 11432727 | 6980454 | 5870909 | 253209 |  | 19784727 | 0 | 7767648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2310000 | 120304 | 0 | 0 | 0 | 0 | 5447 | 0 | 0 | 0 | 0 | 0 | 1747 | 0 | 0 | 0 | 160308 | 1676072 | 0 | 5295000 | 0 | 0 | 0 | 0 | 4295318 | 0 | 0 | 0 | 4228191 | 0 | 8586109 | 171360 | 0 | 0 | 0 | 354115 | 0 | 23288 | 93120 | 15608200 | 4684159 | 0 | 0 | 14100 | 493200 | 367296 | 0 | 0 | 5854545 | 58748 | 3796400 | 12590192 | 433250 | 0 |  | 142690127 | 98772844 | 241462971 | 91986254 | 19784727 | 53182759 | 0 | 8276635 | 62787680 | 696000 | 0 | 682694 | 1985280 | 1726222 | 354720 | 0
Fuel Cost | 0 | 0 | 0 | 14438025 | 0 | 1849051.9 | 0 | 23939712 | 0 |  | 0 | 26910750 | 23335990.38 | 0 | 0 | 6757023.32 | 19679633.95 | 0 | 0 | 0 | 4655224.8 | 3672710.4 | 3456945.35 | 0 | 0 | 0 | 177487.2 | 1672530 | 0 | 0 | 360000 | 0 | 0 | 0 | 2776766.4 | 0 | 0 | 0 | 8190000 | 0 | 486246.62 | 15326750.56 | 0 | 0 | 0 |  | 3812104.8 | 4295712.96 | 2626017.93 | 0 | 9074217.6 | 1264128 | 508717.44 | 0 | 0 | 0 | 0 | 20971872 | 9189180 | 10560920 | 168109.7 | 0 | 2916532.8 | 3016944 | 0 | 2206803.25 | 0 | 1747442.88 | 3071879.58 | 0 | 0 | 2152764 | 85342.5 | 13023436.8 | 9219532.8 | 0 | 0 | 0 | 2788500 | 1736240.4 | 941850 | 1352332.8 | 7246730.34 | 0 | 7013779.2 | 0 | 0 | 6738184.8 | 2500400 | 0 | 0 | 21645450 | 271332 | 47898.24 | 0 | 0 | 0 | 0 | 8114304 | 0 | 8753719.68 | 0 | 8890752 | 10143504 | 0 | 21621350 | 3407928 | 6267340.8 | 0 | 0 | 4102362.15 | 0 | 0 | 4792788 | 5918497.2 | 10532121.6 | 21011606 | 0 | 0 | 0 | 6946920 | 0 | 9617634 | 0 | 6677491.2 | 0 | 20099475 | 0 | 0 | 45545771.68 | 0 | 67453089.3 | 0 | 0 | 0 |  | 55595082.87 | 0 | 22914561.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7299600 | 570240.96 | 0 | 0 | 0 | 0 | 97555.77 | 0 | 0 | 0 | 0 | 0 | 30921.9 | 0 | 0 | 0 | 121353.156 | 18487074.16 | 0 | 44689800 | 0 | 0 | 0 | 0 | 14303408.94 | 0 | 0 | 0 | 14079876.03 | 0 | 25071438.28 | 2926828.8 | 0 | 0 | 0 | 7053970.8 | 0 | 0 | 1847500.8 | 101141136 | 14567734.49 | 0 | 0 | 0 | 0 | 6372585.6 | 0 | 0 | 42738178.5 | 0 | 28283180 | 83221169.12 | 0 | 0 |  | 579775859.31 | 491413197.776 | 1071189057.086 | 280086548.416 | 55595082.87 | 128883426.1 | 0 | 149601724.2 | 431559398.76 | 0 | 0 | 12439439.94 | 13023436.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 100 | 0 | 66 | 0 | 401 | 0 |  | 0 | 450 | 300 | 0 | 0 | 28 | 317 | 0 | 0 | 0 | 32 | 16 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 25 | 25 | 8 | 0 | 0 | 30 | 105 | 0 | 1 | 211 | 0 | 0 | 0 |  | 18 | 20 | 17 | 0 | 31 | 6 | 12 | 2 | 0 | 0 | 0 | 285 | 180 | 137 | 8 | 0 | 35 | 50 | 0 | 51 | 0 | 8 | 16 | 0 | 0 | 24 | 4 | 82 | 109 | 0 | 0 | 2 | 30 | 20 | 11 | 10 | 80 | 0 | 62 | 0 | 0 | 102 | 18 | 0 | 0 | 270 | 16 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 43 | 19 | 62 | 51 | 0 | 317 | 0 | 35 | 0 | 4 | 16 | 0 | 0 | 17 | 28 | 60 | 320 | 0 | 25 | 0 | 31 | 0 | 35 | 24 | 35 | 0 | 285 | 0 | 0 | 272 | 0 | 338 | 302 | 300 | 52 |  | 922 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72 | 0 | 230 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 140 | 0 | 348 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 3 | 780 | 180 | 0 | 0 | 3 | 55 | 35 | 0 | 0 | 308 | 12 | 170 | 625 | 61 | 0 |  | 11237 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 365 | 0 |  | 0 | 350 | 290 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 15 | 25 | 33 | 16 | 0 | 0 | 30 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 140 | 203 | 0 | 0 | 38 | 6 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 28 | 8 | 96 | 136 | 0 | 0 | 0 | 30 | 20 | 5 | 5 | 80 | 0 | 40 | 0 | 0 | 102 | 18 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 55 | 0 | 0 | 2 | 0 | 376 | 24 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 275 | 0 | 0 | 270 | 44 | 316 | 250 | 250 | 0 |  | 923 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 18 | 550 | 170 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 140 | 436 | 0 | 0 |  | 9522 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 |  | 0 | 450 | 310 | 100 | 80 | 40 | 335 | 0 | 0 | 80 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 22 | 20 | 25 | 32 | 16 | 0 | 0 | 30 | 118 | 0 | 25 | 210 | 0 | 0 | 0 |  | 22 | 64 | 51 | 0 | 90 | 19 | 10 | 20 | 0 | 0 | 0 | 340 | 0 | 210 | 0 | 0 | 38 | 50 | 0 | 51 | 0 | 41 | 52 | 0 | 0 | 33 | 20 | 151 | 140 | 0 | 0 | 0 | 30 | 20 | 50 | 44 | 112 | 0 | 60 | 0 | 0 | 70 | 18 | 0 | 0 | 300 | 25 | 5 | 0 | 300 | 0 | 0 | 108 | 0 | 149 | 0 | 60 | 136 | 6 | 400 | 97 | 105 | 34 | 0 | 16 | 54 | 51 | 114 | 75 | 70 | 360 | 53 | 0 | 162 | 72 | 0 | 42 | 0 | 95 | 0 | 350 | 163 | 0 | 270 | 40 | 760 | 500 | 450 |  |  | 650 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 33 | 25 | 90 | 0 | 34 | 42 | 8 | 28 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 414 | 90 | 0 | 113 | 0 | 92 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 375 | 0 | 307 | 748 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 | 0 | 0 | 450 | 310 | 90 | 80 | 40 | 335 | 0 | 0 | 60 | 48 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 22 | 20 | 25 | 32 | 16 | 0 | 0 | 30 | 118 | 0 | 8 | 210 |  | 0 | 0 | 0 | 12 | 40 | 50 | 0 | 20 | 6 | 10 | 5 | 0 | 0 | 0 | 340 | 0 | 210 | 0 | 0 | 38 | 50 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 33 | 20 | 146 | 120 | 0 | 0 | 1.6 | 30 | 20 | 30 | 30 | 112 | 0 | 60 | 0 | 0 | 70 | 18 | 0 | 0 | 300 | 25 | 5 | 0 | 210 | 0 | 0 | 56 | 0 | 52 | 20 | 36 | 100 | 6 | 400 | 50 | 35 | 17 | 5 | 16 | 17 | 17 | 70 | 36 | 40 | 340 | 17 | 50 | 90 | 35 | 0 | 17 | 35 | 54 | 0 | 350 | 54 | 0 | 270 | 40 | 350 | 500 | 250 | 33 |  | 940 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 42 | 8 | 0 | 0 | 0 | 11 | 73 | 0 | 230 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 180 | 0 | 414 | 90 | 0 | 35 | 0 | 56 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 375 | 30 | 200 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 320 | 233 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 25 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 208 | 0 | 0 | 35 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 160 | 0 | 0 | 1 | 30 | 20 | 0 | 0 | 80 | 0 | 40 | 0 | 0 | 60 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 17 | 8 | 0 | 0 | 0 | 325 | 18 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 10 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 355 | 0 | 0 | 278 | 26 | 322 | 250 | 250 | 25 | 0 | 589 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73 | 0 | 170 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 520 | 170 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 313 | 8 | 140 | 445 | 35 | 0 | 0 |  |  |  | 145169013 | 19784727 | 0 | 62787680 | 8959329 | 1985280 | 1726222 | 354720 | 696000 |  |  | 241462971
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 | [6 empty] | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 | [5 empty] | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 145.169 | 19.7847 | 0 | 62.7877 | 8.9593 | 1.9853 | 1.7262 | 0.35472 | 0.696
| Minimum Generation |  | 9606 | 6:00
| Highest Generation |  | 11237 | 12:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 241.463
| Day Peak Generation |  | 11237 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 9522 | 19:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 924 | 17:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 923 | 19:00
| Load factor L.F |  | 89.53% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-07
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11237 | MW Hour : | 12:00 | Min. Gen. at | 3:00 | 7282
Evening Peak Generation : |  |  | 9522 | MW Hour : | 19:00 | Available Max Generation : |  | 16421
E.P. Demand (at gen end) : |  |  | 9522 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 11237 | MW Hour : | 12:00 | Reserve(Generation end) |  | 2421
Total Gen. (MKWH) : |  |  | 241.463 | System Load Factor : | 89.53% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 10 | MW at | 1:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-07
Actual : |  | 73.51 | Ft.(MSL) , | Rule curve : | 80.86 | Ft.( MSL )
Gas Consumed : |  | Total = | 1016.28 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 408969974.516
: |  |  | Coal : | 431559398.76 | Oil : | 162041164.14 | Total : | 1002570537.416
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5342.4914 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1476.7776 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1099.0436 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 1004.2252 |  |  | 0 | 0%
Total |  | 0 |  | 15383.887 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:57 | 16:56 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Scheduled S/D from Gopalganj 400/132kV end.
09:06 | 19:31 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D.
09:07 | 19:30 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D.
09:17 | 17:08 | Aminbazar-Meghnaghat 400kV Ckt-2 Project Work S/D from Meghnaghat 400/230kV end.
| 09:20 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
| 09:20 | Lalmonirhat-Rangpur 132 kV Ckt-2 is restored.
09:28 | 11:17 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Forced S/D from Daudkandi 132/33kV end Due to Remove Kite of the Conductor.
| 09:30 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 is restored.
09:41 | 13:35 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Project Work S/D Due to AR Modification.
10:35 |  | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to Project work.
| 10:38 | Ashuganj CCPP 225 MW ST Syncronized.
10:48 | 11:22 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Tripped showing E/F & O/C Trip relays Due to E/F & O/C Trip by 33 Kv Kotiadi Fault.
11:10 | 19:10 | Madanganj 132/33kV S/S Madanganj -Haripur 132 kv Ckt-2 Scheduled S/D.
11:12 | 19:09 | Haripur 230/132kV S/S Madanganj-2 Scheduled S/D Due to Busbar Protection work.
12:20 | 12:28 | Chauddagram-Feni 132 kV Ckt-2 Tripped from Feni 132/33kV end showing Quadramho Relay-21 relays Due to Due to Heavy
Rainfall and Stormy Weather Cause the Tripping.
12:21 | 12:32 | Feni 132/33kV S/S T-1(405T) LT Forced S/D Due to At Time of Chauddragram Ckt-02 Tripping Period NLDC Given Order
Reduce the Sub-station Load, To Prevent Overload at Chauddragram Ckt-01. That Why T-01 open Secondary.
12:30 | 14:27 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to PBS work. | [5 empty] | 100 MW load interrup.
12:31 | 14:27 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to PBS work.
12:32 | 14:29 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to PBS work.
12:32 | 14:28 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to PBS work.
13:00 | 18:25 | Chauddagram-Feni 132 kV Ckt-1 Tripped from Feni 132/33 kV end showing Relay-21 (Quadramho) relays Due to SF6 Gas
Reclosing Lockout, Compressor Trouble, Distance RT Zone-01 Trip, Distance RY SOTF Trip and from Chauddagram
132/33kV end showing Zone-1 Line-1 SOTF Trip AR operate relays Due to Heavy rainfall with hailstones & stormy weather.
13:01 | 17:10 | Feni 132/33kV S/S Feni-Lanka HFO PS Tripped showing SEL relays Due to Line Differential Protection
Operated, Distance Protection Operated No M Volt on line.
13:10 | 14:35 | Feni 132/33kV S/S T-1(405T) LT Tripped showing Siemens relays Due to Due to REB Ckt-01 SKY Wire Broke and Fall on
line at 33KV Bus End. Definite Earth Current.
13:11 | 23:47 | BSRM-Cumilla(N) 230 kV Ckt-2 Tripped from BSRM 230/33kV end showing Distance relays Due to None and from Cumilla(N)
230/132/33kV end showing Secondary distance protection B- phase E/F protection operated Yellow LED Sotf relays.
13:18 | 15:12 | New Tongi S/S T2(413T) LT Forced S/D Due to Excessive heat in 33 kV side R phase.
13:19 | 15:10 | New Tongi S/S T2(413T) HT Forced S/D Due to Excessive heat in 33 kV side R phase.
13:21 | 15:01 | BSRM 230/33kV S/S 230/33 kV Transformer-1 (125/140 MVA) LT Tripped showing Dir. Oc & E/F Relay relays.
13:35 | 16:11 | Baroirhat-Hathazari 132 kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing distance relay relays Due to thundering.
13:35 | 16:08 | Baroirhat-Feni 132 kV Ckt-2 Tripped from Baroirhat 132/33 kV end showing Trip Relay k35,K36 relays Due to Stormy rain | [5 empty] | 6 MW load interrup in
|  | and from Feni 132/33kV end showing Relay-21(Quadramho) relays Due to Distance RY Zone-01 Trip, | [5 empty] | Baroirhat 132/33 kV end.
Distance RY Zone-02 Trip, A/R Lockout.
13:35 | 15:46 | Feni-PHP 132kV Ckt-1 Tripped from Feni 132/33kV end showing Relay-21(Quadramho) relays Due to Distance RY
Zone-01 Trip,A/R Lockout.
13:35 | 13:47 | Chauddagram-Feni 132 kV Ckt-2 Tripped from Chauddagram 132/33kV end showing Distance, relays Due to Heavy rainfall
with hailstones & stormy weather.
13:35 | 16:11 | Baroirhat-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing distance relay relays Due to
thundering and from Baroirhat 132/33kV end showing Trip relay k35,k36 relays Due to Stormy rain.
13:47 | 15:05 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Forced S/D.
13:47 | 16:27 | BSRM-Mirsharai 230 kV Ckt-2 Tripped from BSRM 230/33kV end showing Distance relays.
14:38 | 15:40 | Feni 132/33kV S/S T-1(405T) LT Tripped showing Siemens relays Due to Due to REB Ckt-01 Breaker Broke Out,
Transformer Secondary Trip Definite Over Current.
14:48 | 17:17 | Rahanpur 400/132kV S/S Rahanpur-Chapainawabganj 132 KV Line Ckt-02 Scheduled S/D.
| 14:48 | Chapainawabganj-Rahanpur 132kV Ckt-1 is restored.
14:50 | 17:23 | Chapai 132/33kV S/S Chapai Rahanpur ckt 2 Project Work S/D
15:06 | 16:21 | Bakulia-Khulshi 132 kV Ckt-1 Tripped from Bakulia 132/33kV end showing Distance Relay relays Due to Thunder & Storm.
15:06 | 20:49 | Bakulia-MSML 132 kV Ckt-2 Tripped from Bakulia 132/33kV end showing Distance Relay relays Due to Thunder & Storm.
15:07 | 16:56 | Chandpur 132/33kV S/S 402T HT Tripped showing Lockout Relay Operate relays Due to OLTC Buchhol TZ Trip. | [5 empty] | 10 MW load interrup.
15:07 | 16:57 | Chandpur 132/33kV S/S 402T LT Tripped showing No relay operate in 33 kV TR-1 panel relays.
15:10 |  | Chattogram TPP-1 Tripped with remarks:- ST
15:10 |  | Kalurghat 132/33kV S/S TRFO-01(506T) LT Tripped showing REF615 relays Due to PDB feeder y phase out from busbur due to flashing. | [5 empty] | 18 MW load interrup.
15:10 | 16:35 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Tripped showing RET615 relays Due to PDB Feeder y phase disconnected from 33 kV busbar.
15:11 | 16:07 | Baroaulia-Hathazari 132 kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing distance relay relays Due to thundering.
15:12 |  | Chattogram TPP-1 Tripped with remarks:- u-1.
15:12 |  | Chattogram TPP-1 Tripped with remarks:- ST.
15:50 | 16:57 | Chandpur 132/33kV S/S 402T LT Scheduled S/D.
15:50 | 16:56 | Chandpur 132/33kV S/S 402T HT Scheduled S/D Due to After OLTC Buchhol TZ trip, Shutdown taken by AE Chandpur Grid.
16:07 | 16:39 | Barishal 230/132kV S/S T-4 LT Tripped showing O/C relays Due to Due to 33KV Babuganj Feeder Fault. | [5 empty] | 3 MW load interrup.
16:07 |  | Barishal 230/132kV S/S Gopalgonj CKT-2 Tripped showing 7SL87 relays Due to Over Voltage.
16:07 |  | Barishal 230/132kV S/S Gopalgonj CKT-1 Tripped showing 7SL87 relays Due to Over voltage.
16:07 | 16:39 | Barishal 230/132kV S/S T-5 LT Tripped showing O/C relays Due to Due to 33KV Babuganj Feeder Fault.
16:25 | 20:47 | Bakulia-Khulshi 132 kV Ckt-1 Tripped from Bakulia 132/33 kV end showing Distance relay relays Due to Thundering.
16:30 | 20:47 | Bakulia-Khulshi 132 kV Ckt-1 Forced S/D from Bakulia 132/33kV end Due to Line Maintenance Work.
17:51 |  | Rampal 1320 MW (BIFPCL) Tripped.
18:22 | 20:17 | Khulna(C )-Noapara 132kV Ckt-1 Tripped from Noapara 132/33kV end showing Distance Relay relays Due to Distance Relay Trip.
18:28 | 20:18 | Khulna (C) S/S TR-1 425T LT Forced S/D Due to for over voltage.
18:28 | 20:17 | Khulna (C) S/S TR-1 425T HT Forced S/D Due to for over voltage.
18:47 | 20:17 | Bagerhat-Goalpara 132 kV Ckt-1 Tripped from Goalpara 132/33kV end showing Distance Relay relays Due to A Phase
To Earth, Distance Trip(Zone-1), Three Phase Trip.
18:47 | 20:17 | Bagerhat-Goalpara 132 kV Ckt-1 Tripped from Goalpara 132/33kV end showing Distance Relay relays Due to A Phase
To Earth, Distance Trip(Zone-1), Three Phase Trip.
18:56 | 20:13 | Kabirpur -Tongi 132kV Ckt-2 Forced S/D from Tongi 230/132/33kV end Due to temperature rise.
19:56 | 20:14 | Bhulta-Haripur 132 kV Ckt-1 Tripped from Haripur 230/132kV end showing Optimho: Z2, Delay, BCN. Relays. | [5 empty] | 20 MW load interrup in
Haripur 230/132 kV end.
19:59 | 20:30 | Khulna (S)-Satkhira 132kV Ckt-2 Forced S/D from Satkhira 230/132kV end Due to According to ALDC instruction.
20:09 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
20:19 | 21:22 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Tripped showing Due to 33KV Shankarpur PDB feeder commissioning. | [5 empty] | 76 MW load interrup.
20:19 | 21:22 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Tripped showing Over current relays Due to 33KV Shankarpur PDB feeder commissioning.
20:19 | 21:06 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Tripped showing 33KV Shankarpur PDB feeder commissioning.
20:20 |  | At Bhola P/S, (230/33)KV transformer is S/D due to LT side Transformer Bushing red Hot Maintenance work.
20:30 | 20:49 | Bakulia-MSML 132 kV Ckt-2 Forced S/D from Bakulia 132/33kV end Due to Line Maintenance Work.
20:57 | 21:38 | Barishal(N)-Madaripur 132 kV Ckt-1 Tripped from Barishal 230/132kV end showing Distance,general relays Due to
distance 34.089km, loop L1N 1976amp.
21:03 | 21:17 | Patuakhali 132/33kV S/S 405T (T-1) HT Tripped showing EF relays Due to Khepupara 33kV fault. | [5 empty] | 2 MW load interrup.
21:03 | 21:27 | Patuakhali 132/33kV S/S 415T (T-2) HT Tripped showing EF relays Due to Khepupara 33kV fault.
21:03 | 21:28 | Patuakhali 132/33kV S/S 415T (T-2) LT Tripped showing EF relays Due to Khepupara 33kV fault.
21:03 | 21:17 | Patuakhali 132/33kV S/S 405T (T-1) LT Tripped showing E/F relays Due to 33kV Khepupara Feeder.
21:07 | 21:22 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Tripped from Faridpur 132/33kV end showing Distance relays.
21:12 | 21:55 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Tr-04 33 Kv Pdb Emergency bus Shutdown for red hot | [5 empty] | 30 MW load interrup.
Maintenece work.
21:13 | 21:57 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Tr-04 33 kv Pdb old feeder emergency bus shutdown for red
hot maintenece work.
| 21:47 | At Bhola P/S, (230/33)KV transformer is restored
22:30 | 22:49 | Cox'sbazar-Dohazari 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing QUADRAMHO SHPM101 relays Due to stormy weather.
| 22:32 | Rampal 1320 MW (BIFPCL) Syncronized with remarks:- U1
22:32 | 00:04 | Baroirhat 132/33kV S/S TR-1, 406T HT Forced S/D Due to Post Insulator change in 33 kv feeder.
22:32 | 00:05 | Baroirhat 132/33kV S/S TR-1, 406T LT Forced S/D Due to Post Insulator change in 33 kv feeder.
22:48 | 22:53 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing E/F relay. | [5 empty] | 32 MW load interrup.
23:00 | 23:09 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH Y, Z 1, Dist Send. relays. | [5 empty] | 12 MW load interrup.
23:15 | 23:28 | Keranigonj 230/132/33kV S/S Hasnabad Tripped showing 86.1
23:17 |  | Kushiara 163 MW CCPP (KP) Shutdown
23:24 | 01:38 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH Y, Z 1, Dist Send. relays Due to Rainy and Stormy Weather. | [5 empty] | 5 MW load interrup.
01:40 | 01:50 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance Protection 21/1 Z1 BN trip. Relays.
01:45 |  | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH Y, Z 1, Dist Send. relays.
07:08 |  | Gopalganj 132/33kV S/S T1 LT Forced S/D Due to High temperature maintenance of loop joint at y phase breaker side of bus D/S.
|  | temperature maintenance of loop joint at y phase breaker |  |  |  |  | load
|  | side of bus D/S |  |  |  |  | interrup.
MiCOM P441: PH Y, Z 1, Dist Send. relays.
01:45 |  | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing
|  | MiCOM P441: PH Y, Z 1, Dist Send. relays. |  |  |  |  | 5.0MW
|  | MiCOM P441: PH Y, Z 1, Dist Send. relays Due to Rainy and |  |  |  |  | load
|  | Stormy Weather. |  |  |  |  | interrup.
23:15 | 23:28 | Keranigonj 230/132/33kV S/S Hasnabad Tripped showing 86.1
relays Due to SOTF, 21 distance fault 3.7 km, Zone-01 trip
23:17 |  | Kushiara 163 MW CCPP (KP) Shutdown
|  | fault. |  |  |  |  | interrup.
23:00 | 23:09 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing |  |  |  |  | 12.0MW
|  | MiCOM P441: PH Y, Z 1, Dist Send. relays. |  |  |  |  | load
interrup.
21:03 | 21:27 | Patuakhali 132/33kV S/S 415T (T-2) HT Tripped showing EF
relays Due to Khepupara 33kV fault
21:03 | 21:28 | Patuakhali 132/33kV S/S 415T (T-2) LT Tripped showing EF
relays Due to Khepupara 33kV fault
21:03 | 21:17 | Patuakhali 132/33kV S/S 405T (T-1) LT Tripped showing E/F
relays Due to 33kV Khepupara Feeder

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 160 | 3244500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 484045 | Bad weather
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 365 | 8312400 | Bad weather
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8462500 | Bad weather
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 0 | 0 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 290 | 6823389 | Bad weather
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 0 | 0 | Reserve.
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 383486 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 185359 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas line problem.
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 0 | 0 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6452339 | Bad weather
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 259344 | Bad weather
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 9720 | Reserve.
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 189120 | Bad weather
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 106125 | Bad weather
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 15 | 855120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 596700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 609400
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 16 | 155040 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve.
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 55 | 497088 | Bad weather
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 334080 | Bad weather
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve.
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve.
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 118356
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Under maint.
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 250 | 6980454 | Bad weather
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 250 | 5870909 | On test.
| Dhaka area Total |  |  |  | 5332 | 2264 | 50929474
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 1500000 | Tripped at 15:12.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 25673 | Reserve.
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 98820
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 76800 | Reserve.
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 696000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 185 | 4804624 | Bad weather
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 8 | 243936 | Bad weather
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 146623 | Reserve.
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 499200 | Reserve.
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 136752 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 253440
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 463680 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23281
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 250909 | Reserve.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 591360 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 414000 | Reserve.
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve.
60 | SS Power I |  | SS Power | 2*612 | 1224 | 270 | 6534544 | Bad weather
| Cox's Bazar Wind |  | IPP | 66 | 60 | 44 | 354720 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 316 | 11432727 | Bad weather
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 253209
| Chattogram area Total |  |  |  | 4404 | 853 | 28800298
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 3181000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7516800 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 140 | 3003000 | ST under maint
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 275 | 6767500 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 38 | 865440 | Bad weather
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 6 | 688800 | Bad weather
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 50182 | Bad weather
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 550325 | Bad weather
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 8 | 97568 | Bad weather
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 2 | 584640 | Bad weather
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 96 | 1985280
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 28 | 578700 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 170093 | Reserve.
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 8 | 113790 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 250800 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 304920 | Bad weather
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 538200
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 370560 | Bad weather
| Cumilla Area Total |  |  |  | 2929 | 1158 | 27617598
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 136 | 2964480 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8250
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 422400 | Bad weather
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 24 | 178800 | Bad weather
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 201720
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 216720 | Engine problem
| Mymensingh Area Total |  |  |  | 592 | 243 | 3992370
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 465480 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 80 | 2118927 | ST under maint
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 5 | 207000 | Bad weather
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 5 | 297216 | Bad weather
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 63024 | Bad weather
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1263744 | Bad weather
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2415120 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 380000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 361776 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7005000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 376 | 8159000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 7899100 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1347 | 31350387
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 19784727
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7767648 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 0 | 0 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 171360 | Reserve.
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 493200
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 0 | 5854545 | Tripped at 17:51.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1183 | 34071480
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 0 | 120304 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2310000 | Bad weather
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 15608200 | Bad weather
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 170 | 4684159 | Bad weather
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3796400 | Bad weather
| Barisal Area Total |  |  |  | 2235 | 940 | 26519063
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 5447 | Reserve.
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 161 | 4295318
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 161 | 4228191 | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8586109 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 160308 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 1747 | Reserve.
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve.
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 18 | 93120 | Bad weather
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 14100
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 436 | 12590192 | Bad weather
| Rajshahi Area Total |  |  |  | 3431 | 1195 | 29974532
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1676072
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 5295000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 38 | 354115 | Bad weather
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23288
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 31 | 367296 | Bad weather
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 58748
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 433250
| Rangpur Area Total |  |  |  | 950 | 339 | 8207769
| Total |  |  |  | 25903 | 9522 | 241462971
| Eastern Grid Total |  |  |  | 15588 | 5865 | 142690127
| Western Grid Total |  |  |  | 10315 | 3657 | 98772844
| National Grid Total |  |  |  | 25903 | 9522 | 241462971
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-06
| (a) ENTIRE EASTERN GRID : |  | 6573.25 | MW | (b) ENTIRE WESTERN GRID : |  | 2624.2 | MW
| i) Dhaka area |  | 4235.25 | MW | i) Khulna area |  | 554.4 | MW
| ii) Chittagong area |  | 403 | MW | ii) Rajshahi area |  | 1233.6 | MW
| iii) Comilla area |  | 670 | MW | iii) Barisal area |  | 111.2 | MW
| iv) Mymensingh area |  | 901 | MW | iv) Rangpur area |  | 725 | MW
| v) Sylhet area |  | 364 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9197.45 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 22:00 | Kalurghat | 38 | 11:00 | Narail | 62 | 01:00 | Shariatpur | 70 | 01:00
2 | AKSML | 109.5 | 06:00 | Chowmuhani | 178 | 01:00 | Kamrangirchar | 52.4 | 13:00 | Narinda | 68 | 13:00 | Sherpur | 110 | 19:00
3 | Aftabnagar | 48 | 12:00 | Chuadanga | 122 | 02:00 | Kaptai | N/A | N/A | Narshingdi | 131 | 19:00 | Shikalbaha | 31 | 15:00
4 | Agargaon | 96 | 10:00 | Coxsbazar | 133 | 00:00 | Kazla | 90 | 13:00 | Natore | 155 | 00:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 68 | 13:00 | Cumilla(N) | 108 | 17:00 | Keranigonj | 66 | 18:00 | Nawabganj | 47.8 | 04:00 | Shitalakhya | 98 | 12:00
6 | Amnura | 82 | 00:00 | Cumilla(S) | 145 | 11:00 | Khagrachori | 22 | 11:00 | Netrakona | 96 | 19:00 | Sholosohor | 44 | 14:00
7 | Ashuganj | 69 | 19:30 | Daudkandi | 114 | 18:30 | Khulna | 95 | 13:00 | New | 53.3 | 11:00 | Shyampur | 124 | 03:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 13:00 | Khulshi | 169 | 13:00 | Niamatpur | 84 | 00:00 | Siddhirganj | 106 | 11:00
9 | BSRM | 177 | 04:00 | Dhamrai | 112 | 10:00 | Kishoreganj | 100 | 19:30 | Noapara | 52 | 12:00 | Sirajganj | 96 | 19:30
10 | Bagerhat | 103 | 02:00 | Dhanmondi | 132 | 13:00 | Kodda | 257 | 18:30 | PHP | 10 | 18:00 | Sonargaon | 91 | 11:00
11 | Bakulia | 97 | 13:00 | Dohazari | 68 | 00:00 | Kulaura | 28 | 19:30 | Pabna | 118 | 00:00 | Sreemongol | 42 | 19:00
12 | Banani | 62.2 | 13:00 | Faridpur | 160 | 00:00 | Kurigram | 45 | 18:30 | Palashbari | 81 | 19:30 | Sreepur | 65 | 17:00
13 | Bangabhaban | 15 | 10:00 | Fatullah | 63 | 12:00 | Kushtia | 162 | 00:00 | Panchagarh | 47 | 19:00 | Srinagar | 34.8 | 03:00
14 | Barapukuria | 53 | 19:30 | Fenchuganj | 27 | 19:30 | Lalbag | 92 | 13:00 | Patuakhali | 98.5 | 00:00 | Sunamganj | 35 | 19:00
15 | Barguna | 24 | 01:00 | Feni | 85 | 11:00 | Lalmonirhat | 42 | 19:00 | Payra | 28.8 | 00:00 | Sylhet | 24 | 00:00
16 | Barishal | 113 | 13:00 | GPH | 16 | 07:00 | MI_Cement | 11 | 09:00 | Postogola | 49 | 14:00 | Sylhet-132 | 89 | 19:30
17 | Barishal-230 | 96 | 00:00 | Ghatail | 38 | 19:00 | Madanganj | 20 | 12:00 | Purbachal | 12 | 19:00 | TK | 20 | 15:00
18 | Baroaulia | 69 | 13:00 | Ghorashal | 67 | 19:00 | Madaripur | 104 | 00:00 | Purbasadipur | 107 | 19:30 | Tangail | 164 | 18:30
19 | Baroirhat | 47 | 12:00 | Goalpara | 42 | 00:00 | Madartek | 68.52 | 22:00 | Rahim | 38 | 16:00 | Thakurgaon | 78 | 19:30
20 | Bashundhara | 168 | 13:00 | Gollamari | 82 | 00:00 | Madunaghat | 45 | 12:00 | Rajbari | 84 | 00:00 | Tongi | 130 | 15:00
21 | BashundharaCement | 12 | 03:00 | Gopalganj | 108.4 | 00:00 | Magura | 70 | 00:00 | Rajendrapur | 90 | 18:30 | Ullahpara | 27 | 13:00
22 | Beanibazar | 37 | 19:00 | Gulshan | 64 | 11:00 | Mahasthangarh | 62 | 19:30 | Rajshahi | 168 | 00:00 | Ullon | 45 | 00:00
23 | Benapole | 76 | 01:00 | Halishahar | 90 | 15:00 | Manikganj | 111 | 01:00 | Rajshahi-230 | 58 | 23:00 | Uttara | 79 | 12:00
24 | Bhaluka | 126 | 15:00 | HaripurSBU | 175 | 15:00 | Maniknagar | 74 | 13:00 | Ramganj | 96 | 02:00 | UttaraNew | 31 | 10:00
25 | Bhandaria | 59 | 00:00 | Hasnabad | 67 | 14:00 | Matarbari | 45 | 00:00 | Rampur | 40 | 00:00 | Zigatola | 81 | 15:00
26 | Bhangura | 42 | 00:00 | Hathazari | 62 | 13:00 | Matuail | 72 | 09:00 | Rangamati | 15 | 13:00
27 | Bheramara(GK) | 72 | 00:00 | Ishurdi | 75 | 00:00 | Millgate | 111 | 15:00 | Rangpur | 110 | 18:30
28 | Bhulta | 220 | 10:00 | Jaldhaka | 61 | 08:00 | Mirpur | 126 | 12:00 | Ruppur | 6.6 | 15:00
29 | Bog-Sherpur | 56 | 02:00 | Jamalpur | 98 | 20:00 | Mirsorai | 5 | 01:00 | SSM | 16 | 00:00
30 | Bogura | 143 | 00:00 | Jashore | 151 | 01:00 | Mirzapur | 42 | 18:30 | Saidpur | 85 | 08:00
31 | Borhanuddin | 85 | 00:00 | Jhenaidah | 137 | 00:00 | Mithapukur | 44 | 19:00 | Satkhira | 140 | 00:00
32 | Brahmanbaria | 118 | 19:00 | Joydebpur | 159 | 18:30 | Modern | 0 | 00:00 | Satmasjid | 96 | 13:00
33 | Cantonment | 134 | 13:00 | Joypurhat | 54 | 00:00 | Mogbazar | 116.9 | 13:00 | Savar | 178 | 15:00
34 | Chandpur | 52 | 12:00 | Juldah | 20 | 12:00 | Mongla | 43 | 11:00 | SevenRings | 17.87 | 17:00
35 | Chandraghona | 27 | 12:00 | KSRM | 43 | 14:00 | Motijheel | 45 | 11:00 | ShahCement | 27 | 11:00
36 | Chapai | 73 | 00:00 | Kabirpur | 209 | 12:00 | Munshiganj | 66 | 16:00 | Shahjadpur | 77 | 00:00
37 | Charsaidpur | 36 | 16:00 | Kachua | 59 | 00:00 | Mymensingh | 162 | 18:30 | Shahjibazar | 83 | 19:00
38 | Chauddagram | 53 | 01:00 | Kallyanpur | 96 | 18:30 | Naogaon | 130 | 00:00 | Shahmirpur | 63 | 15:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 406 | 22:00 | 393 | 10:00 | Kaliakoir | 385 | 19:30 | 374 | 09:00
| Ashuganj | 415 | 13:00 | 390 | 10:00 | Madunaghat_I | 398 | 02:00 | 394 | 11:00
| Bhulta | 410 | 20:00 | 395 | 16:00 | Meghnaghat | 400 | 23:00 | 386 | 12:00
| Bibiana | 405 | 05:00 | 396 | 11:00 | Payra | 418 | 23:00 | 409 | 01:00
| BIPTC | 407 | 03:00 | 394 | 15:00 | Rahanpur | 420 | 09:00 | 411 | 00:00
| Bogura | 417 | 14:00 | 407 | 00:00 | Rampal | 416 | 23:00 | 397 | 01:00
| Gopalganj | 415 | 23:00 | 399 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 237 | 23:00 | 225 | 10:00 | Hasnabad | 239 | 23:00 | 226 | 10:00
| AKSML | 236 | 16:00 | 221 | 10:00 | Hathazari | 236 | 16:00 | 219 | 11:00
| Aminbazar | 238 | 22:00 | 225 | 10:00 | Ishurdi | 237 | 16:00 | 229 | 00:00
| Ashuganj | 239 | 14:00 | 235 | 19:30 | Jhenaidah | 235 | 20:00 | 217 | 01:00
| Ashuganj-400 | 240 | 23:00 | 224 | 14:00 | Kaliakoir | 235 | 22:00 | 226 | 09:00
| Baghabari | 234 | 16:00 | 227 | 00:00 | Keranigonj | 237 | 23:00 | 224 | 10:00
| Barapukuria | 219 | 16:00 | 213 | 07:00 | Khulna(S) | 240 | 22:00 | 219 | 00:00
| Barapukuria-230 | 21 | 16:00 | 213 | 7:00 | Madunaghat_I | 227 | 02:00 | 221 | 10:00
| Barishal | 244 | 23:00 | 234 | 00:00 | Maniknagar | 238 | 23:00 | 226 | 10:00
| Bheramara | 237 | 04:00 | 229 | 00:00 | Meghnaghat | 242 | 20:00 | 234 | 10:00
| Bhulta | 237 | 23:00 | 227 | 10:00 | Meghnaghat-400 | 238 | 22:00 | 224 | 14:00
| Bibiana | 232 | 02:00 | 228 | 09:00 | Mirsorai | 234 | 16:00 | 220 | 11:00
| BIPTC | 237 | 16:00 | 226 | 00:00 | Rajshahi | 233 | 16:00 | 223 | 00:00
| Bogura | 227 | 14:00 | 222 | 00:00 | Rampal | 239 | 23:00 | 221 | 01:00
| Bogura-400 | 227 | 16:00 | 222 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 246 | 23:00 | 238 | 00:00 | Rampura | 236 | 23:00 | 224 | 09:00
| BSRM | 233 | 16:00 | 221 | 09:00 | Shikalbaha | 231 | 16:00 | 217 | 00:00
| Cumilla(N) | 236 | 20:00 | 226 | 09:00 | Shyampur | 238 | 23:00 | 226 | 10:00
| Fenchuganj | 237 | 00:00 | 232 | 10:00 | Siddhirganj | 239 | 23:00 | 229 | 09:00
| Ghorashal | 240 | 00:00 | 240 | 00:00 | Sirajgonj | 238 | 05:00 | 234 | 06:00
| Ghorashal-230 | 235 | 23:00 | 226 | 10:00 | Sreepur | 234 | 03:00 | 228 | 15:00
| GPH | 235 | 16:00 | 220 | 07:00 | Tongi | 234 | 00:00 | 223 | 11:00
| Haripur | 237 | 23:00 | 226 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 23:00 | 129 | 09:00 | Kushtia | 139 | 18:30 | 128 | 00:00
| Agargaon | 141 | 23:00 | 131 | 10:00 | Lalbag | 139 | 23:00 | 128 | 10:00
| Agrabad | 142 | 16:00 | 127 | 11:00 | Lalmonirhat | 128 | 03:00 | 122 | 21:00
| AKS | 138 | 16:00 | 125 | 10:00 | Madanganj | 137 | 00:00 | 128 | 10:00
| Aminbazar | 138 | 00:00 | 128 | 12:00 | Madaripur | 138 | 19:30 | 131 | 00:00
| Amnura | 136 | 18:00 | 127 | 00:00 | Madartek | 136 | 23:00 | 128 | 10:00
| Ashuganj | 140 | 03:00 | 137 | 16:00 | Madunaghat | 140 | 16:00 | 128 | 09:00
| Bagerhat | 143 | 18:30 | 123 | 00:00 | Magura | 144 | 18:00 | 128 | 00:00
| Bakulia | 142 | 16:00 | 129 | 11:00 | Mahasthangarh | 133 | 04:00 | 129 | 00:00
| Banani | 138 | 23:00 | 128 | 10:00 | Manikganj | 133 | 23:00 | 120 | 09:00
| Bangabhaban | 139 | 23:00 | 130 | 10:00 | Maniknagar | 138 | 00:00 | 130 | 13:00
| Barapukuria | 135 | 16:00 | 129 | 07:00 | Matarbari | 137 | 18:30 | 112 | 00:00
| Barguna | 138 | 00:00 | 124 | 01:00 | Matuail | 139.5 | 23:00 | 129.5 | 10:00
| Barishal | 140 | 16:00 | 119 | 01:00 | Millgate | 138 | 23:00 | 129 | 12:00
| Barishal-230 | 140 | 18:30 | 132 | 00:00 | Mirpur | 137 | 23:00 | 126 | 12:00
| Baroaulia | 141 | 16:00 | 127 | 10:00 | Mirzapur | 131 | 03:00 | 123 | 18:00
| Baroirhat | 135 | 17:00 | 120 | 00:00 | Mithapukur | 132 | 09:00 | 126 | 21:00
| Bashundhara | 137 | 23:00 | 128 | 10:00 | MI_Cement | 139 | 23:00 | 129 | 10:00
| BashundharaCement | 137 | 00:00 | 128 | 10:00 | Modern | 138 | 18:00 | 128 | 09:00
| Beanibazar | 135 | 09:00 | 129 | 19:00 | Mogbazar | 139 | 23:00 | 130 | 10:00
| Benapole | 143 | 18:30 | 123 | 00:00 | Mongla | 143 | 19:30 | 121 | 01:00
| Bhaluka | 132 | 22:00 | 126 | 10:00 | Motijheel | 139 | 23:00 | 130 | 10:00
| Bhandaria | 140 | 19:00 | 116 | 00:00 | Munshiganj | 138 | 00:00 | 129 | 10:00
| Bhangura | 137 | 16:00 | 132 | 00:00 | Mymensingh | 135 | 03:00 | 123 | 16:00
| Bheramara | 137 | 16:00 | 132 | 00:00 | Naogaon | 130 | 05:00 | 125 | 00:00
| Bheramara(GK) | 137 | 16:00 | 131 | 00:00 | Narail | 144 | 18:30 | 128 | 00:00
| Bhulta | 135 | 23:00 | 123 | 10:00 | Narinda | 138 | 00:00 | 130 | 13:00
| Bog-Sherpur | 133 | 04:00 | 130 | 00:00 | Narshingdi | 136 | 00:00 | 127 | 16:00
| Bogura | 135 | 04:00 | 119 | 00:00 | Natore | 133 | 16:00 | 124 | 00:00
| Bogura-230 | 135 | 14:00 | 131 | 00:00 | Nawabganj | 140 | 23:00 | 129 | 10:00
| Brahmanbaria | 137 | 00:00 | 129 | 18:00 | Netrakona | 131 | 23:00 | 122 | 15:00
| Cantonment | 140 | 23:00 | 130 | 10:00 | New | 138 | 23:00 | 130 | 12:00
| Chandpur | 140 | 14:00 | 117 | 00:00 | Niamatpur | 140 | 16:00 | 135 | 00:00
| Chandraghona | 141 | 16:00 | 128 | 10:00 | Noapara | 142 | 18:00 | 127 | 00:00
| Chapai | 138 | 18:00 | 132 | 00:00 | Pabna | 136 | 16:00 | 129 | 00:00
| Charsaidpur | 139 | 23:00 | 129 | 10:00 | Palashbari | 131 | 09:00 | 125 | 07:00
| Chauddagram | 139 | 14:00 | 123 | 00:00 | Panchagarh | 133 | 10:00 | 119 | 07:00
| Chhatak | 135 | 08:00 | 129 | 18:30 | Patuakhali | 137 | 19:30 | 127 | 00:00
| Chowmuhani | 139 | 14:00 | 114 | 00:00 | Payra | 138 | 23:00 | 133 | 00:00
| Chuadanga | 142 | 18:30 | 118 | 00:00 | PHP | 136 | 17:00 | 122 | 00:00
| Coxsbazar | 136 | 18:30 | 114 | 00:00 | Postogola | 140 | 23:00 | 131 | 10:00
| Cumilla(N) | 138 | 20:00 | 130 | 09:00 | Purbachal | 138 | 23:00 | 129 | 10:00
| Cumilla(S) | 138 | 23:00 | 127 | 11:00 | Purbasadipur | 128 | 16:00 | 118 | 07:00
| Daudkandi | 138 | 23:00 | 125 | 10:00 | Rahanpur | 141 | 09:00 | 138 | 00:00
| Dhaka | 137 | 23:00 | 129 | 10:00 | Rahim | 140 | 23:00 | 131 | 10:00
| Dhamrai | 141 | 00:00 | 131 | 09:00 | Rajbari | 138 | 23:00 | 127 | 00:00
| Dhanmondi | 140 | 23:00 | 130 | 10:00 | Rajendrapur | 139 | 00:00 | 118 | 18:00
| Dohazari | 139 | 16:00 | 126 | 00:00 | Rajshahi | 133 | 16:00 | 124 | 00:00
| Faridpur | 138 | 22:00 | 130 | 00:00 | Rajshahi-230 | 135 | 16:00 | 126 | 15:00
| Fatullah | 139 | 23:00 | 130 | 10:00 | Ramganj | 138 | 14:00 | 115 | 00:00
| Fenchuganj | 136 | 08:00 | 133 | 07:00 | Rampur | 140 | 16:00 | 127 | 10:00
| Feni | 140 | 14:00 | 120 | 00:00 | Rampura | 137 | 23:00 | 129 | 10:00
| Ghatail | 133 | 20:00 | 125 | 18:00 | Rangamati | 140 | 16:00 | 127 | 11:00
| Ghorashal | 140 | 00:00 | 136 | 10:00 | Rangpur | 130 | 09:00 | 123 | 21:00
| Goalpara | 144 | 18:30 | 130 | 00:00 | Ruppur | 138 | 18:00 | 132 | 00:00
| Gollamari | 142 | 19:30 | 132 | 00:00 | Saidpur | 129 | 05:00 | 121 | 07:00
| Gopalganj | 140 | 18:30 | 127 | 12:00 | Satkhira | 143 | 20:00 | 122 | 00:00
| Gopalganj-400 | 139 | 23:00 | 132 | 00:00 | Satmasjid | 142 | 23:00 | 132 | 10:00
| Gulshan | 137 | 23:00 | 129 | 10:00 | Savar | 137 | 00:00 | 125 | 11:00
| Halishahar | 142 | 16:00 | 127 | 11:00 | SevenRings | 141 | 04:00 | 135 | 16:00
| Haripur | 140 | 23:00 | 131 | 10:00 | ShahCement | 139 | 23:00 | 129 | 10:00
| HaripurSBU | 140 | 23:00 | 131 | 10:00 | Shahjadpur | 140 | 23:00 | 135 | 00:00
| Hasnabad | 139 | 00:00 | 130 | 10:00 | Shahjibazar | 133 | 00:00 | 129 | 18:30
| Hathazari | 142 | 17:00 | 130 | 12:00 | Shahmirpur | 143 | 16:00 | 130 | 10:00
| Ishurdi | 138 | 16:00 | 132 | 00:00 | Shariatpur | 140 | 23:00 | 129 | 00:00
| Jaldhaka | 128 | 04:00 | 118 | 07:00 | Sherpur | 133 | 04:00 | 118 | 23:00
| Jamalpur | 133 | 02:00 | 122 | 17:00 | Shikalbaha | 127 | 16:00 | 119 | 10:00
| Jashore | 143 | 18:30 | 125 | 00:00 | Shikalbaha-230 | 140 | 16:00 | 131 | 00:00
| Jhenaidah | 144 | 18:00 | 130 | 00:00 | Shitalakhya | 139 | 23:00 | 129 | 10:00
| Jhenaidah-230 | 144 | 18:00 | 130 | 01:00 | Sholosohor | 141 | 16:00 | 127 | 10:00
| Joydebpur | 138 | 00:00 | 130 | 16:00 | Shyampur | 136 | 00:00 | 131 | 11:00
| Joypurhat | 129 | 15:00 | 122 | 00:00 | Shyampur-230 | 139 | 20:00 | 130 | 10:00
| Juldah | 143 | 16:00 | 130 | 10:00 | Siddhirganj | 140 | 23:00 | 130 | 10:00
| Kabirpur | 135 | 22:00 | 123 | 18:00 | Sirajganj | 134 | 23:00 | 130 | 00:00
| Kachua | 139 | 14:00 | 121 | 00:00 | Sonargaon | 139 | 23:00 | 129 | 12:00
| Kaliakoir | 140 | 02:00 | 127 | 17:00 | Sreemongol | 133 | 00:00 | 130 | 16:00
| Kallyanpur | 134 | 23:00 | 128 | 09:00 | Sreepur | 133 | 03:00 | 128 | 15:00
| Kalurghat | 140 | 16:00 | 126 | 11:00 | Srinagar | 140 | 23:00 | 129 | 10:00
| Kamrangirchar | 139 | 23:00 | 126 | 11:00 | SSM | 144 | 19:00 | 130 | 10:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 134 | 08:00 | 128 | 18:30
| Kazla | 139 | 00:00 | 130 | 11:00 | Sylhet | 134 | 09:00 | 130 | 19:00
| Keranigonj | 139 | 23:00 | 129 | 10:00 | Sylhet-132 | 134 | 09:00 | 130 | 23:00
| Khagrachori | 141 | 16:00 | 126 | 11:00 | Tangail | 130 | 12:00 | 122 | 18:00
| Khulna | 143 | 19:30 | 129 | 00:00 | Thakurgaon | 130 | 10:00 | 116 | 07:00
| Khulna(S) | 143 | 18:30 | 130 | 00:00 | TK | 139 | 17:00 | 127 | 09:00
| Khulshi | 137 | 16:00 | 126 | 11:00 | Tongi | 139 | 23:00 | 132 | 09:00
| Kishoreganj | 135 | 03:00 | 129 | 15:00 | Ullahpara | 136 | 16:00 | 132 | 00:00
| Kodda | 137 | 19:30 | 120 | 18:00 | Ullon | 136 | 03:00 | 128 | 09:00
| KSRM | 141 | 16:00 | 127 | 10:00 | Uttara | 137 | 00:00 | 126 | 12:00
| Kulaura | 135 | 10:00 | 132 | 07:00 | UttaraNew | 137 | 23:00 | 127 | 10:00
| Kurigram | 130 | 09:00 | 122 | 19:00 | Zigatola | 140 | 23:00 | 130 | 10:00

## L-Curve
Date | 2024-05-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 314 | 4516 | 3302 | 7818 |  |  |  | QF-LDC-11
0:30 | 162 | 5226.5 | 3820.5 | 9047 | Date: | 2024-05-06
1:00 | 10 | 5937 | 4339 | 10276
1:30 | 114 | 6021 | 4366.5 | 10387.5
2:00 | 218 | 6105 | 4394 | 10499
2:30 | 228 | 6055.5 | 4356 | 10411.5 | [5 empty] | Gen. at Eve. Peak | 9522 | 9522 MW (19:00 )
3:00 | 238 | 6006 | 4318 | 10324 | [6 empty] | 19:00
3:30 | 253 | 5995.5 | 4302 | 10297.5 | [5 empty] | Gen. at Day Peak | 11237 | 11237 MW (12:00 )
4:00 | 268 | 5985 | 4286 | 10271 | [6 empty] | 12:00
4:30 | 225 | 5928.5 | 4237.5 | 10166 | [5 empty] | Highest Generation | 11237
5:00 | 182 | 5872 | 4189 | 10061 | [6 empty] | 12:00
5:30 | 172 | 5751 | 4082.5 | 9833.5
6:00 | 162 | 5630 | 3976 | 9606
6:30 | 147 | 5745 | 3985.5 | 9730.5
7:00 | 132 | 5860 | 3995 | 9855
7:30 | 249 | 5827 | 4016 | 9843
8:00 | 366 | 5794 | 4037 | 9831
8:30 | 467 | 5985 | 4119 | 10104
9:00 | 568 | 6176 | 4201 | 10377
9:30 | 555 | 6318 | 4191.5 | 10509.5
10:00 | 542 | 6460 | 4182 | 10642
10:30 | 584 | 6511.5 | 4344.5 | 10856
11:00 | 626 | 6563 | 4507 | 11070
11:30 | 595 | 6562 | 4591.5 | 11153.5
12:00 | 564 | 6561 | 4676 | 11237
12:30 | 448 | 6601 | 4567.5 | 11168.5
13:00 | 332 | 6641 | 4459 | 11100
13:30 | 298 | 6371.5 | 4304.5 | 10676
14:00 | 264 | 6102 | 4150 | 10252
14:30 | 374 | 6126 | 4144.5 | 10270.5
15:00 | 484 | 6150 | 4139 | 10289
15:30 | 554 | 5833.5 | 3976.5 | 9810
16:00 | 624 | 5517 | 3814 | 9331
16:30 | 667 | 5403 | 3761 | 9164
17:00 | 710 | 5289 | 3708 | 8997
17:30 | 736 | 5374.5 | 3565.5 | 8940
18:00 | 762 | 5460 | 3423 | 8883
18:30 | 644 | 5662.5 | 3540 | 9202.5
19:00 | 526 | 5865 | 3657 | 9522
19:30 | 446 | 5769 | 3640 | 9409
20:00 | 254 | 5672 | 3355 | 9027 |  |  |  | Executive Engineer
20:30 | 345 | 5597 | 3408 | 9005 |  |  |  | Network Operation Division
21:00 | 436 | 5522 | 3461 | 8983
21:30 | 368 | 5430.5 | 3385 | 8815.5
22:00 | 300 | 5339 | 3309 | 8648 |  |  |  |  | Page 6 of 7
22:30 | 254 | 5120.5 | 3294.5 | 8415
23:00 | 208 | 4902 | 3280 | 8182
23:30 | 261 | 4709 | 3291 | 8000
24:00 | 314 | 4516 | 3302 | 7818
9522 MW (19:00 )
11237 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-06 |  | Energy |  | 241462971
[15 empty] | 2024-05-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3148 | 637 | 1716 | 0 | 0 | 2237 | 0 | 0 | 8 | 54 | 0 | 18 | 0
0:30 | 3513.5 | 636.5 | 1999 | 0 | 148 | 2618.5 | 15 | 0 | 24.5 | 77 | 0 | 15 | 0 |  |  | Date: | 43956
1:00 | 3879 | 636 | 2282 | 0 | 296 | 3000 | 30 | 0 | 41 | 100 | 0 | 12 | 0
1:30 | 3903.5 | 636 | 2339 | 0 | 336 | 3004.5 | 30 | 0 | 32.5 | 96 | 0 | 10 | 0 | [9 empty] | Total Energy | 241.463 | 241.463 | Total Energy Gen 241.463 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 241.463 MKWHr
2:00 | 3928 | 636 | 2396 | 0 | 376 | 3009 | 30 | 0 | 24 | 92 | 0 | 8 | 0 | [9 empty] | Energy not Served | 0 | 0
2:30 | 3910.5 | 660.5 | 2387 | 0 | 370.5 | 2933 | 30 | 0 | 24 | 92 | 0 | 4 | 0 | [9 empty] | Energy Requirement | 241.463 | 241.463
3:00 | 3893 | 685 | 2378 | 0 | 365 | 2857 | 30 | 0 | 24 | 92 | 0 | 0 | 0
3:30 | 3890.5 | 685 | 2373.5 | 0 | 360.5 | 2844 | 30 | 0 | 24 | 90 | 0 | 0 | 0 | [8 empty] | Shortage
4:00 | 3888 | 685 | 2369 | 0 | 356 | 2831 | 30 | 0 | 24 | 88 | 0 | 0 | 0
4:30 | 3865.5 | 765 | 2315 | 0 | 292.5 | 2796 | 30 | 0 | 12 | 90 | 0 | 0 | 0
5:00 | 3843 | 845 | 2261 | 0 | 229 | 2761 | 30 | 0 | 0 | 92 | 0 | 0 | 0
5:30 | 3685.5 | 883.5 | 2184.5 | 0 | 212 | 2748.5 | 30 | 0 | 0 | 84 | 5.5 | 0 | 0
6:00 | 3528 | 922 | 2108 | 0 | 195 | 2736 | 30 | 0 | 0 | 76 | 11 | 0 | 0
6:30 | 3602.5 | 921.5 | 2126.5 | 0 | 201 | 2744.5 | 30 | 0 | 0 | 73 | 31.5 | 0 | 0 | [7 empty] | Coal
7:00 | 3677 | 921 | 2145 | 0 | 207 | 2753 | 30 | 0 | 0 | 70 | 52 | 0 | 0
7:30 | 3575.5 | 922 | 2110 | 0 | 219.5 | 2815 | 30 | 0 | 0 | 82 | 89 | 0 | 0 | [6 empty] | Oil
8:00 | 3474 | 923 | 2075 | 0 | 232 | 2877 | 30 | 0 | 0 | 94 | 126 | 0 | 0
8:30 | 3543.5 | 923 | 2161 | 0 | 274.5 | 2889.5 | 30 | 0 | 8 | 98 | 176.5 | 0 | 0
9:00 | 3613 | 923 | 2247 | 0 | 317 | 2902 | 30 | 0 | 16 | 102 | 227 | 0 | 0
9:30 | 3681 | 922.5 | 2271 | 0 | 385.5 | 2901 | 30 | 0 | 16 | 102 | 200.5 | 0 | 0
10:00 | 3749 | 922 | 2295 | 0 | 454 | 2900 | 30 | 0 | 16 | 102 | 174 | 0 | 0
10:30 | 3859 | 922 | 2370 | 0 | 525 | 2800.5 | 30 | 0 | 17.5 | 109 | 223 | 0 | 0
11:00 | 3969 | 922 | 2445 | 0 | 596 | 2701 | 30 | 0 | 19 | 116 | 272 | 0 | 0
11:30 | 3978.5 | 922 | 2440.5 | 0 | 629.5 | 2748 | 30 | 0 | 40 | 99 | 266 | 0 | 0
12:00 | 3988 | 922 | 2436 | 0 | 663 | 2795 | 30 | 0 | 61 | 82 | 260 | 0 | 0
12:30 | 4080.5 | 922.5 | 2395 | 0 | 668 | 2717 | 30 | 0 | 54.5 | 74 | 220 | 7 | 0
13:00 | 4173 | 923 | 2354 | 0 | 673 | 2639 | 30 | 0 | 48 | 66 | 180 | 14 | 0
13:30 | 4173 | 923 | 2354 | 0 | 673 | 2639 | 30 | 0 | 48 | 66 | 180 | 14 | 0
14:00 | 4173 | 923 | 2354 | 0 | 673 | 2639 | 30 | 0 | 48 | 66 | 180 | 14 | 0
14:30 | 4047.5 | 923 | 2349 | 0 | 579.5 | 2492.5 | 30 | 0 | 51.5 | 67 | 136.5 | 18 | 0
15:00 | 3922 | 923 | 2344 | 0 | 486 | 2346 | 30 | 0 | 55 | 68 | 93 | 22 | 0
15:30 | 3764.5 | 923 | 2176.5 | 0 | 386.5 | 2304 | 30 | 0 | 44 | 82 | 81.5 | 18 | 0
16:00 | 3607 | 923 | 2009 | 0 | 287 | 2262 | 30 | 0 | 33 | 96 | 70 | 14 | 0
16:30 | 3546.5 | 923.5 | 1974.5 | 0 | 253 | 2250 | 30 | 0 | 33 | 88 | 58.5 | 7 | 0
17:00 | 3486 | 924 | 1940 | 0 | 219 | 2238 | 30 | 0 | 33 | 80 | 47 | 0 | 0
17:30 | 3553.5 | 923.5 | 1946 | 0 | 211 | 2090 | 30 | 0 | 48 | 86 | 27 | 25 | 0
18:00 | 3621 | 923 | 1952 | 0 | 203 | 1942 | 30 | 0 | 63 | 92 | 7 | 50 | 0
18:30 | 3715.5 | 923 | 2044.5 | 0 | 319.5 | 1962 | 30 | 0 | 63.5 | 94 | 3.5 | 47 | 0
19:00 | 3810 | 923 | 2137 | 0 | 436 | 1982 | 30 | 0 | 64 | 96 | 0 | 44 | 0
19:30 | 3676 | 923 | 2154 | 0 | 475 | 1964 | 30 | 0 | 64 | 82 | 0 | 41 | 0
20:00 | 3618 | 639 | 2145 | 0 | 435 | 1991 | 30 | 0 | 48 | 92 | 0 | 29 | 0
20:30 | 3734.5 | 639 | 2156.5 | 0 | 304 | 2004.5 | 30 | 0 | 36 | 73 | 0 | 27.5 | 0
21:00 | 3851 | 639 | 2168 | 0 | 173 | 2018 | 30 | 0 | 24 | 54 | 0 | 26 | 0
21:30 | 3855.5 | 639 | 2082.5 | 0 | 129 | 1982 | 30 | 0 | 16 | 47 | 0 | 34.5 | 0
22:00 | 3860 | 639 | 1997 | 0 | 85 | 1946 | 30 | 0 | 8 | 40 | 0 | 43 | 0
22:30 | 3665.5 | 637 | 1928 | 0 | 42.5 | 2029.5 | 15 | 0 | 8 | 51 | 0 | 38.5 | 0
23:00 | 3471 | 635 | 1859 | 0 | 0 | 2113 | 0 | 0 | 8 | 62 | 0 | 34 | 0
23:30 | 3309.5 | 636 | 1787.5 | 0 | 0 | 2175 | 0 | 0 | 8 | 58 | 0 | 26 | 0 |  |  | Max Temp. in Dhaka |  | 29.8°C
24:00 | 3148 | 637 | 1716 | 0 | 0 | 2237 | 0 | 0 | 8 | 54 | 0 | 18 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 241.463 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 241.463 MKWHr
Note on W13: Author:

## Generation
2024-05-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 696000
3 | Chattogram TPP-1 | 100 | 104 | 102 | 100 | 96 | 100 | 100 | 100 | 100 | 105 | 105 | 105 | 100 | 110 | 100 | 0 | [9 empty] | 0 | 1500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 1 | 8 | 8 | 8 | 0 | [9 empty] | 0 | 25673
| Teknaf 20MW PP (Solartech) | [8 empty] | 12 | 17 | 19 | 19 | 19 | 8 | 8 | 6 | 2 | [8 empty] | 0 | 98820
6 | Sikalbaha 225MW CCPP (Gas) | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 211 | 211 | 213 | 210 | 184 | 185 | 185 |  | 185 | 185 | 185 | 199 | 211 | 211 | 202 | 4804624
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [7 empty] | 0 | 146623
12 | Hathazari 100 MW peaking PP | 24 | 24 | 24 | 24 | [7 empty] | 20 | 23 | 30 | 30 | 8 | 8 | 8 |  | 8 | 8 | 8 | 0 |  |  |  | 243936
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [10 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 97568
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 290 | 317 | 317 | 317 | 314 | 250 | 250 | 230 | 231 | 270 |  | 270 | 270 | 270 | 293 | 270 | 270 | 250 | 6452339
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [9 empty] | 0 | 50182
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 180 | 160 | 160 | 160 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 3244500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 274 | 275 | 275 | 271 | 270 | 272 | 272 | 270 | 270 | 270 | 270 | 272 | 270 | 270 | 272 | 266 | 268 | 275 |  | 270 | 270 | 270 | 269 | 270 | 275 | 277 | 6534544
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 34 | 36 | 36 | 36 | 36 | 37 | 37 | 35 | 32 | 33 | 35 | 35 | 38 | 38 | 38 | 38 | 36 | 38 |  | 38 | 38 | 38 | 38 | 38 | 35 | 35 | 865440
33 | Ashuganj 225 MW CCPP | 28 | 44 | 48 | 48 | 48 | 48 | 100 | 28 | 43 | 56 | 107 | 137 | 226 | 224 | 194 | 223 | 191 | 203 |  | 203 | 191 | 191 | 197 | 191 | 190 | 190 | 3181000
34 | Ashuganj 450 MW CCPP(South) | 140 | 140 | 140 | 140 | 140 | 140 | 250 | 140 | 140 | 140 | 180 | 180 | 180 | 140 | 140 | 140 | 140 | 140 |  | 140 | 35 | 5 | 0 |  |  | 0 | 3003000
| Ashuganj 450 MW CCPP(North) | 270 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 290 | 290 | 285 | 280 | 280 | 280 | 280 | 280 | 305 |  | 305 | 310 | 310 | 320 | 310 | 310 | 280 | 7516800
| Ashuganj 420 MW CCPP(East) | 240 | 280 | 280 | 280 | 280 | 240 | 240 | 240 | 240 | 310 | 285 | 285 | 285 | 285 | 330 | 230 | 230 | 230 |  | 275 | 285 | 285 | 335 | 340 | 285 | 250 | 6767500
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 33 | 50 | 50 | 52 | 50 | 52 | 53 | 52 | 41 | 35 | 11 |  | 6 | 20 | 20 | 21 | 42 | 40 | 13 | 688800
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 305 | 305 | 305 | 305 | 305 | 305 | 330 | 335 | 357 | 401 | 401 | 401 | 387 | 347 | 324 | 324 | 324 | 364 |  | 365 | 365 | 364 | 375 | 391 | 338 | 305 | 8312400
| Meghnaghat Unique power | 350 | 400 | 400 | 400 | 400 | 300 | 300 | 250 | 250 | 250 | 325 | 302 | 300 | 288 | 300 | 250 | 250 | 250 |  | 250 | 250 | 250 | 251 | 230 | 220 | 220 | 6980454
| Summit Meghanghat-2 589 MW(Gas) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 300 | 300 | 250 | 250 | 200 | 230 | 230 | 230 |  | 250 | 250 | 250 | 250 | 200 | 200 | 200 | 5870909
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 370 | 370 | 450 | 450 | 450 | 300 | 350 | 300 | 300 | 300 |  | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 8462500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 134 | 133 | 140 | 140 | 154 | 143 | 142 | 122 | 122 | 118 | 118 | 109 | 108 | 108 | 108 | 122 | 124 | 123 |  | 136 | 135 | 136 | 138 | 138 | 138 | 109 | 2964480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 4 | 6 | 28 | 18 | 29 | 25 | 37 | 34 | 9 | 2 | 9 | 2 |  | 0 | [6 empty] | 201720
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 465480
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 63 | 63 | 63 | 63 | 62 | 62 | 62 | 63 | 63 | 62 | 63 | 40 | 40 | 40 | 40 | 20 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1263744
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 103 | 70 | 2415120
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 |  | 0 | 380000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | [11 empty] | 2 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 63024
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 |  | 0 | 207000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 |  |  | 361776
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 305 | 280 | 275 | 280 | 285 | 300 | 280 | 295 | 305 | 290 | 270 | 280 | 270 | 310 | 290 | 275 | 270 |  | 300 | 300 | 300 | 295 | 270 | 265 | 260 | 7005000
| Bibiyana South 400 MW | 388 | 340 | 315 | 310 | 310 | 325 | 310 | 310 | 325 | 320 | 320 | 320 | 320 | 320 | 342 | 342 | 310 | 310 |  | 350 | 340 | 340 | 340 | 340 | 310 | 310 | 7899100
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Tangail Palli Power Gen 22 MW | [8 empty] | 12 | 18 | 18 | 18 | 18 | 12 | 13 | 12 | 6 | 7 |  | 18 | 18 | 18 | 18 | 18 |  | 0 | 216720
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 0 | [10 empty] | 0 | 136752
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 100 | 92 | 92 | 88 | 92 | 76 | 70 | 94 | 102 | 102 | 116 | 82 | 66 | 76 | 68 | 96 | 80 | 92 |  | 96 | 82 | 92 | 54 | 40 | 62 | 54 | 1985280
64 | Malancha, Ctg. EPZ (United) | 0 | 7 | 23 | 24 | 25 | 25 | 20 | 10 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 0 | 0 | 0 |  | 0 | 0 | 3 | 16 | 27 | 26 | 16 | 253440
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 28 | 28 | 32 | 32 | 32 |  | 28 | 28 | 28 | 0 |  | 8 | 0 | 578700
68 | Cumilla 25 MW PP (Summit) |  |  |  | 16 | 16 | 16 | 10 | 6 | 6 | 6 | 16 | 4 | 16 | 12 | 2 | 2 | 8 | 8 |  | 8 | 8 | 8 | 0 |  |  | 0 | 113790
69 | Summit Ashulia | [17 empty] | 27 |  |  |  | 20 | 20 | 20 | 20 | 20 | 480000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 |  | 15 | 15 | 0 | 5 | 7 | 0 | 0 | 375120
71 | Maona 33 MW PP(Summit) | 8 | 8 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 25 | 25 | 25 |  | 25 | 20 | 20 | 25 | 32 | 33 | 33 | 596700
72 | Rupganj 33 MW PP(Summit) | 24 | 33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 32 | 32 | 32 | 32 | 32 | 33 |  | 33 | 33 | 0 | 8 | 16 | 0 | 0 | 609400
73 | Ghorashal 108 MW PP (Regent) | [6 empty] | 12 | 15 | 24 | 38 | 62 | 66 | 66 | 66 | 66 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 |  |  | 0 | 484045
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 17 | 17 | [12 empty] | 0 | 250800
| Chowmuhani 113 MW | 7 | 26 | 9 | 9 | 9 | 9 | 9 | 9 | 11 | 26 | 28 | 28 | 26 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 0 |  |  | 0 | 304920
| Manikgonj 162MW PP(MPGL) | [25 empty] | 0 | 0
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 155040
79 | Kodda 150 MW PP | [8 empty] | 16 | 16 | 16 | 16 | [5 empty] | 30 |  | 48 | 48 | 32 | 16 | 0 |  | 0 | 189120
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 3 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 16 | 8 | [13 empty] | 170093
| Gazipur 100 MW PP | [9 empty] | 17 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 52 | 52 | 35 | 17 | 0 |  | 0 | 334080
| Kaptai 7 MW Solar PP | [7 empty] | 2 | 4 | 4 | 5 | 4 | 3 | 0 | [12 empty] | 23281
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [6 empty] | 12 |  |  |  | 22 | 29 | 29 | 29 | 29 | 22 | 23 | [8 empty] | 0 | 185359
86 | Meghnaghat CCPP ( Summit) | 258 | 320 | 310 | 320 | 300 | 252 | 250 | 259 | 300 | 312 | 315 | 300 | 300 | 290 | 310 | 292 | 280 | 278 |  | 290 | 290 | 290 | 292 | 285 | 266 | 287 | 6823389
87 | Meghnaghat 100 MW(IEL) | [25 empty] | 0 | 0
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 |  | 0 | 297216
93 | Ashuganj 51 MW PP (Midland) | 10 | 10 | 10 | 10 | 10 | 10 | 17 | 43 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 0 |  | 0 |  | 5 | 5 | 5 | 5 | 0 |  | 0 | 550325
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 24 | 32 | 50 | 32 | 32 | 32 | 16 | 16 |  | 16 | 16 | 16 | 0 |  |  | 0 | 259344
95 | Patenga 50MW PP (Baraka) |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [11 empty] | 0 | 76800
96 | Chattogram 108 MW PP (ECPV) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 35 | 24 | 24 | 0 |  |  |  |  | 0 |  |  |  |  | 0 | 463680
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 28 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 0 |  |  | 0 | 383486
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 0 |  |  | 0 | 106125
101 | Kushiara 163 MW CCPP (KP) | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 80 | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 0 | 2118927
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 8250
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | [12 empty] | 0 | 9720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 65 | 65 | 65 | 45 | 8 |  | 0 | 422400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 17 | 40 | 53 | 43 | 32 | 17 | 17 | 17 | 17 | 17 |  | 55 | 75 | 70 | 34 | 17 |  | 0 | 497088
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 62 | 62 | 25 | 40 | 12 | [9 empty] | 0 | 499200
116 | Chandpur 200 MW (Desh energy) | 28 | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 29 | 51 | 51 | 34 | 34 | 17 | 0 |  |  |  | 2 | 17 | 17 | 0 |  |  | 0 | 584640
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 419 | 363 | 328 | 306 | 306 | 330 | 315 | 315 | 315 | 315 | 316 | 317 | 315 | 318 | 364 | 364 | 330 | 325 |  | 376 | 364 | 364 | 364 | 365 | 304 | 244 | 8159000
| Jamalpur 115 MW PP (United) | 2 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 2 |  | 24 | 24 | 24 | 8 | 0 |  | 0 | 178800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | [9 empty] | 0 | 250909
| Juldah unit-2 (Acorn) | 49 | 49 | 49 | 49 | 12 | 12 | 12 | 12 | 12 | 25 | 60 | 60 | 50 | 60 | 60 | 12 | [9 empty] | 0 | 591360
| Anlima Energy Ltd. | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 31 | 35 | 35 | 17 | 0 | [9 empty] | 0 | 414000
| Bhairob 54.5 MW |  |  | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 35 | 35 | 34 | 35 | 34 | 35 | 35 |  | 35 | 35 | 35 | 35 | 26 |  | 0 | 538200
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 9 | 9 | 7 | 25 | 24 | 25 | 8 | 2 | 3 | 0 | [9 empty] | 118356
| Chandpur 115(Doreen) | 22 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 35 | 35 | 30 | 10 | [11 empty] | 0 | 370560
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | [20 empty] | 0 |  |  |  |  | 0 | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 12 | 8 | [10 empty] | 14 | 25 | 22 | 14 | 0 | 50 |  | 44 | 41 | 29 | 26 | 43 | 34 | 18 | 354720
| Sonagazi 75 MW Solar Plant | [5 empty] | 4 | 16 | 37 | 47 | 20 | 66 | 52 | 1 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 253209
| Matarbari 2*600 MW (CPGCL) | 632 | 628 | 609 | 604 | 608 | 607 | 605 | 750 | 754 | 753 | 354 | 338 | 337 | 339 | 340 | 340 | 315 | 317 |  | 316 | 318 | 316 | 316 | 309 | 316 | 310 | 11432727
120 | Eastern Zone Total | 5937 | 6105 | 6006 | 5985 | 5872 | 5630 | 5860 | 5794 | 6176 | 6460 | 6563 | 6561 | 6641 | 6102 | 6150 | 5517 | 5289 | 5460 |  | 5865 | 5769 | 5672 | 5522 | 5339 | 4902 | 4516 | 142690127
121
122
123 | Khulna 60MW
124 | manik
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 | [12 empty] | 8 | [8 empty] | 0 | 171360
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 19 | 41 | 43 | 47 | 66 | 55 | 41 | 85 | 32 | 34 | 15 | 2 | [8 empty] | 493200
131 | Rampal 1320 MW (BIFPCL) | 308 | 307 | 309 | 310 | 309 | 310 | 310 | 310 | 308 | 309 | 310 | 308 | 309 | 311 | 309 | 309 | 310 | [7 empty] | 189 | 311 | 5854545
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4684159
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 150 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3796400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 126 | 128 | 80 | 80 | 80 | 80 | 80 | 126 | 126 | 126 | 80 | 76 | 76 | 72 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2310000
140 | Bhola 33 MW PP (Venture) | 9 | 9 | 10 | 9 | 10 | 7 | 7 | 7 | 6 | 7 | 6 | 8 | 6 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 2 | 2 |  |  | 120304
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 636 | 636 | 685 | 685 | 845 | 922 | 921 | 923 | 923 | 922 | 922 | 922 | 923 | 923 | 923 | 923 | 924 | 923 |  | 923 | 923 | 639 | 639 | 639 | 635 | 637 | 19784727
147 | Bheramara 410 MW CCPP | 400 | 405 | 405 | 410 | 410 | 250 | 250 | 250 | 300 | 300 | 400 | 405 | 405 | 300 | 345 | 220 | 220 | 220 |  | 260 | 260 | 260 | 375 | 345 | 220 | 220 | 7767648
148 | Payra 1320 MW | 680 | 700 | 560 | 540 | 540 | 540 | 560 | 540 | 560 | 560 | 670 | 780 | 700 | 540 | 520 | 500 | 500 | 500 |  | 550 | 530 | 560 | 560 | 500 | 500 | 500 | 15608200
149
150 | Barapukuria TPP Unit-1 | 74 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 73 | 73 | 72 | 72 | 72 | 75 | 70 | 69 | 70 |  | 70 | 70 | 70 | 70 | 70 | 73 | 71 | 1676072
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 180 | 180 | 5295000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 5447
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 1 | 0 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 14100
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 205 | 217 | 218 | 218 | 190 | 140 | 140 | 140 | 140 | 140 | 140 | 150 | 170 | 170 | 159 | 168 | 155 | 156 |  | 161 | 159 | 159 | 172 | 185 | 176 | 150 | 4295318
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 214 | 220 | 219 | 190 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 151 | 164 | 155 | 156 |  | 161 | 159 | 159 | 171 | 185 | 180 | 140 | 4228191
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 400 | 305 | 348 | 324 | 347 | 344 | 347 | 311 | 348 | 305 | 316 | 414 | 326 | 298 | 341 |  | 414 | 417 | 405 | 414 | 331 | 292 | 250 | 8586109
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 0 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 160308
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [25 empty] | 0 | 0
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 1747
170 | Chapainawabganj 100 MW Peaking PP
171 | Baghabari 200 MW PP (Paramount)
Bagura 113 MW PP (Confidence)-2
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 3 | 5 | 8 | 10 | 12 | 15 | 17 |  | 18 | 18 | 0 |  |  |  | 0 | 93120
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [7 empty] | 16 | 40 | 39 | 35 | 35 | 34 | 34 | 34 | 0 |  |  |  | 38 | 38 | 38 | 0 |  |  | 0 | 354115
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 3 | 2 |  | 3 | 4 | 3 | 2 | 0 | 1 | 0 | [8 empty] | 23288
178 | Energypac Power Venture Thakurgaon Ltd. | [7 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 31 | 35 | 35 | 0 |  |  | 0 | 367296
| Intraco Solar 30 MW | [5 empty] | 0 | 1 | 5 | 7 | 4 | 10 | 12 | 6 | 6 | 4 | 5 | 1 | 0 | [8 empty] | 58748
| Adani Power Jharkhanda Ltd | 632 | 626 | 631 | 633 | 561 | 534 | 533 | 534 | 538 | 535 | 624 | 625 | 571 | 481 | 450 | 437 | 436 | 440 |  | 436 | 436 | 435 | 463 | 457 | 440 | 448 | 12590192
178 | Teesta Solar Limited | [5 empty] | 1 | 9 | 25 | 73 | 53 | 51 | 61 | 41 | 72 | 35 | 20 | 19 | 3 | [8 empty] | 433250