## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-15 | Wednesday
|  | Date (day): | 2024-05-15 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 16382.6 | MW |  |  | (b) At Evening Peak Hour : |  | 17130 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-14 | 2024-05-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 79 | 76 | 75 | 75 | 33 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 413 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 72 | 91 | 90 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 303 | 275 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 80 | 68 | 96 | 96
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 43 | 43 | 12 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 15 | 60 |  | Engine problem.
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 65 | 40 | 60 | 85
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 316 | 310 | 300 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 90 | 90 | 90 | 90 | 12 |  | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 32 | 33 | 40 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 17 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 31 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 245 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 71 | 134 | 135 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 17 | 100
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 70 | 70 | 72 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 35 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 270 | 500 | 400 | 500 |  |  | Meghnaghat Bus section Limitation
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 300 | 63 | 450 | 450 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 3202 | 3581 | 4007 | 4349 | 735 | 799
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 102 | 103 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 2 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 5 | 19 | 6 | 18 | 32 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 213 | 213 | 210 | 210
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 51 | 100 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 48 | 70 | 80 | 80 | 18
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 85 | 51 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 36 | 48 | 40 | 45 | 55 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 49 | 62 | 49 | 62 | 38 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 15 | 16 | 16 |  |  | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 14 | 5 | 25
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 5 | 95 | 20 | 95 | 13 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 17 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 13 | 51 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 62 | 48 | 62 | 38 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 53 | 17 | 17 | 99 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 53 | 125 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 486 | 486 | 490 | 490 |  | 734 | Madanaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 675 | 504 | 530 | 530
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 55 | 0 | 33 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1976 | 2217 | 2131 | 2409 | 821 | 1081
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 216 | 220 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 280 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 260 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 300 | 300 | 300 | 300 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 36 | 38 | 38 | 7
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 48 | 42 | 50 | 50
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 58 | 125 | 150 | 150 | 0
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 31 | 36 | 42 |  | 10 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 50 | 50 |  | 113 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 126 | 108 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 33 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 52 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 8 | 16 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 97 | 97 | 98 | 98
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 104 | 57 | 104 | 9 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 50 | 50 | 50 |  | 4 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 67 | 54 | 115 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1720 | 1940 | 2091 | 2149 | 386 | 132
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 68 | 95 | 100 | 120 | 82 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 105 | 56 | 108 | 92 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 98 | 50 | 100 | 15 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 28 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 24
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 222 | 322 | 279.6 | 352 | 82 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 38 | 43 | 43 |  | 27 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 52 | 52
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 39 | 41 | 42 | 42
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 59 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 130 | 126 | 150 | 150 |  | 81 | machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 25 | 25
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 260 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 367 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 340 | 340 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1491 | 1458 | 1562 | 1582 | 0 | 569
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 857 | 935 | 625
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 16 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 0 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 38 | 44 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 345 | 400 | 400
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 24 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 90 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 409 | 459 | 500 | 500
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1792 | 1786 | 2069 | 1719 | 702 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 48 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 124 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 700 | 1080 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 110 | 110
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 50 | 17 | 50 | 100 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 170 | 270 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1116 | 1660 | 1866 | 1961 | 100 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 41 | 0 | 33 | 19 |  | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 35 | 0 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 34 | 34 |  | 16 | Engine problem
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 42 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 184 | 200 | 200 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 189 | 185 | 200 | 200 |  |  | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 315 | 400 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 28 | 22 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 763 | 764 | 748 | 748 |  |  | Unit-1 Reserve
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1564 | 1966 | 1797 | 2094 | 466 | 84
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 70 | 70 | 70 | 70 | 15
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 90 | 42 | 100 | 13 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 74 | 115 | 70 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 178 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 618 | 505 | 580 | 515 | 68 | 129
| Total |  |  |  |  | 27054 | 25903 | 13701 | 15435 | 16382.6 | 17130 | 3360 | 2917
A. |  | 2024-05-14 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 15435 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 12270 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15700 | MW
3 | Day peak Generation : |  |  | 13701 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15042.71 | MW
4 | Evening peak Generation : |  |  | 15435 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 253 | MW
5 | Total Energy Generation : |  | 333.7339 | MKWHr | By Solar | 3.3988 | MKWHr
| By Gas : | 166.2267 | MKWHr |  | By Oil: | 51.9803 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 88.8185 | MKWHr |  | By Hydro: | 0.7197 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.04992 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3360 | MW | Dhaka | 5371.11 | 5321.11 |  | 50 |  | 18:00 |  | 125
|  |  | For Plants S/D or M/C prob = |  |  | 2917 | MW | Chittagong | 1489.5 | 1489.5 |  | 0 |  | 19:00 |  | 166
|  |  | Total = |  |  | 6277 | MW | Khulna | 1837 | 1837 |  | 0 |  | 19:30 |  | 253
7 | Total Gas Supplied : |  |  | 1247.88 | MMCFD |  |  | Rajshahi | 1595.6 | 1595.6 |  | 0 |  | 20:00 |  | 301
8 | Fuel Cost : | i) Gas : | Taka | 473358964.04 | ii) Oil : | Taka | 953614015.22 | Comilla | 1414 | 1414 |  | 0 |  | 21:00 |  | 294
|  | iii) Coal : | Taka | 607449537.41 | Total | Taka | 2034422516.67 | Mymensingh | 1247 | 1119 |  | 128 |  | 22:00 |  | 331.385
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3535.95 | MKWHr. | Sylhet | 640 | 630 |  | 10 |  | 23:00 |  | 361.945
| ii) During Peak Demand : |  |  | 148 | MW (W to E) at | 19:30 | hrs | Barisal | 460.5 | 460.5 |  | 0 |  | 24:00 |  | 585.415
| iii) Maximum : |  |  | 148 | MW at | 19:30 | hrs | Rangpur | 988 | 923 |  | 65
10 | Maximum Temperature in Dhaka was |  |  |  | 35.3°C |  |  | Total | 15042.71 | 14789.71 |  | 253
B. |  | 2024-05-15 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 35.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 17130 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14000 | MW
4 | Reserve(Generation end) |  |  |  | 1130 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 345.9502 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12482 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.9796 | MKWHr. | ii) HVDC Flow at Peak Time |  | 857 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5603 | MKWHr. | iii) Maximum HVDC Flow : |  | 908 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.58 |  | (b) Today: | 73.43 |  | (c) Rule Curve: |  | 79.34
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-14 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 407 | 0 |  | 0 | 450 | 315 | 99 | 80 | 15 | 330 | 0 | 0 | 90 | 90 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 23 | 20 | 33 | 16 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 213 | 0 | 0 | 0 |  | 18 | 58 | 85 | 0 | 70 | 6 | 13 | 38 | 0 | 0 | 0 | 310 | 240 | 217 | 8 | 0 | 35 | 51 | 0 | 51 | 0 | 23 | 43 | 0 | 0 | 32 | 14 | 118 | 107 | 0 | 0 | 0 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 132 | 0 | 0 | 0 | 310 | 24 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 95 | 0 | 49 | 17 | 0 | 366 | 70 | 17 | 17 | 0 | 52 | 54 | 17 | 98 | 54 | 62 | 340 | 53 | 0 | 162 | 17 | 0 | 35 | 0 | 75 | 0 | 240 | 17 | 0 | 492 | 0 | 575 | 145 | 450 | 0 |  | 628 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 5 | 0 | 28 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 198 | 0 | 417 | 35 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 1100 | 110 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 510 | 0 | 260 | 748 | 0 | 0 |  | 8744 | 5237 | 13981 | 4406 | 628 | 2636 | 0 | 1937 | 3984 | 30 | 0 | 242 | 118 | 0 | 0 | 305 | 73.6
2:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 409 | 0 |  | 0 | 450 | 317 | 99 | 80 | 15 | 331 | 0 | 0 | 88 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 23 | 20 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 211 | 0 | 0 | 0 |  | 18 | 58 | 34 | 0 | 33 | 6 | 13 | 38 | 0 | 0 | 0 | 310 | 240 | 219 | 8 | 40 | 34 | 52 | 0 | 51 | 0 | 23 | 34 | 0 | 0 | 32 | 14 | 110 | 106 | 0 | 0 | 0 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 134 | 0 | 49 | 17 | 0 | 365 | 69 | 17 | 17 | 0 | 52 | 17 | 17 | 98 | 37 | 62 | 340 | 53 | 0 | 54 | 17 | 0 | 35 | 0 | 80 | 0 | 240 | 17 | 0 | 490 | 0 | 577 | 150 | 500 | 0 |  | 622 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 190 | 0 | 400 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1100 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 508 | 0 | 260 | 745 | 0 | 0 |  | 8569 | 5000 | 13569 | 4451 | 622 | 2667 | 0 | 1561 | 3980 | 30 | 0 | 148 | 110 | 0 | 0 | 287 | 73.6
3:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 411 | 0 |  | 0 | 450 | 318 | 99 | 80 | 15 | 333 | 0 | 0 | 88 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 23 | 19 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 213 | 0 | 0 | 0 |  | 18 | 58 | 34 | 0 | 0 | 4 | 13 | 38 | 0 | 0 | 0 | 310 | 240 | 220 | 8 | 75 | 35 | 49 | 0 | 51 | 0 | 23 | 25 | 0 | 0 | 32 | 14 | 104 | 108 | 0 | 0 | 0 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 134 | 0 | 0 | 0 | 280 | 23 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 133 | 0 | 49 | 17 | 0 | 365 | 69 | 17 | 17 | 0 | 52 | 0 | 17 | 98 | 37 | 48 | 340 | 53 | 0 | 0 | 17 | 0 | 35 | 0 | 75 | 0 | 240 | 0 | 0 | 455 | 0 | 575 | 150 | 400 | 0 |  | 841 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 186 | 0 | 396 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1040 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 483 | 0 | 260 | 720 | 0 | 0 |  | 8238 | 5081 | 13319 | 4471 | 841 | 2541 | 0 | 1368 | 3833 | 30 | 0 | 131 | 104 | 0 | 0 | 268 | 73.59
4:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 415 | 0 |  | 0 | 450 | 275 | 75 | 80 | 15 | 331 | 0 | 0 | 74 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 24 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 58 | 34 | 0 | 0 | 0 | 13 | 32 | 0 | 0 | 0 | 310 | 240 | 222 | 8 | 75 | 35 | 52 | 0 | 51 | 0 | 23 | 25 | 0 | 0 | 32 | 14 | 106 | 108 | 0 | 0 | 0 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 134 | 0 | 0 | 0 | 270 | 23 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 136 | 0 | 49 | 17 | 0 | 366 | 69 | 17 | 0 | 0 | 52 | 0 | 0 | 98 | 38 | 48 | 340 | 68 | 0 | 0 | 0 | 0 | 35 | 0 | 75 | 0 | 240 | 0 | 0 | 450 | 0 | 575 | 250 | 400 | 0 |  | 907 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 185 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 462 | 0 | 260 | 677 | 0 | 0 |  | 8168 | 4975 | 13143 | 4470 | 907 | 2553 | 0 | 1222 | 3724 | 30 | 0 | 131 | 106 | 0 | 0 | 179 | 73.59
5:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 413 | 0 |  | 0 | 450 | 319 | 50 | 51 | 15 | 332 | 0 | 0 | 50 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 24 | 20 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 58 | 34 | 0 | 0 | 0 | 13 | 38 | 0 | 0 | 0 | 310 | 240 | 221 | 8 | 50 | 35 | 51 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 32 | 14 | 100 | 108 | 0 | 0 | 0 | 40 | 20 | 52 | 36 | 112 | 0 | 57 | 0 | 0 | 134 | 0 | 0 | 0 | 275 | 23 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 133 | 0 | 49 | 17 | 0 | 306 | 69 | 17 | 0 | 0 | 52 | 0 | 0 | 73 | 38 | 48 | 310 | 70 | 0 | 0 | 0 | 0 | 35 | 0 | 75 | 0 | 240 | 0 | 0 | 450 | 0 | 577 | 250 | 350 | 0 |  | 908 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 185 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 463 | 0 | 260 | 680 | 0 | 0 |  | 7856 | 4910 | 12766 | 4358 | 908 | 2504 | 0 | 1048 | 3710 | 30 | 0 | 108 | 100 | 0 | 0 | 128 | 73.58
6:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 408 | 0 |  | 0 | 450 | 318 | 0 | 15 | 15 | 333 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 21 | 20 | 33 | 32 | 8 | 0 | 30 | 0 | 105 | 0 | 0 | 213 | 0 | 0 | 0 |  | 18 | 58 | 0 | 0 | 0 | 0 | 13 | 38 | 0 | 0 | 0 | 310 | 240 | 221 | 8 | 50 | 35 | 52 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 32 | 14 | 82 | 108 | 0 | 0 | 0 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 134 | 0 | 0 | 0 | 285 | 23 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 133 | 1 | 49 | 17 | 0 | 307 | 59 | 17 | 0 | 0 | 52 | 0 | 0 | 17 | 38 | 48 | 310 | 70 | 3 | 0 | 0 | 0 | 0 | 2 | 75 | 0 | 240 | 0 | 0 | 450 | 0 | 574 | 250 | 300 | 4 |  | 906 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 185 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 110 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 416 | 2 | 226 | 680 | 9 | 0 |  | 7537 | 4733 | 12270 | 4358 | 906 | 2472 | 0 | 776 | 3546 | 30 | 0 | 74 | 82 | 26 | 0 | 0 | 73.58
7:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 410 | 0 |  | 0 | 450 | 315 | 0 | 0 | 15 | 330 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 24 | 0 | 19 | 20 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 213 | 0 | 0 | 0 |  | 18 | 58 | 0 | 0 | 0 | 0 | 13 | 10 | 0 | 0 | 0 | 295 | 340 | 199 | 8 | 51 | 35 | 50 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 86 | 108 | 0 | 0 | 0 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 101 | 5 | 12 | 17 | 0 | 339 | 49 | 17 | 0 | 1 | 52 | 0 | 0 | 17 | 38 | 48 | 340 | 70 | 12 | 57 | 0 | 0 | 15 | 8 | 75 | 0 | 240 | 0 | 0 | 450 | 1 | 537 | 250 | 300 | 19 |  | 907 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 191 | 0 | 347 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 800 | 110 | 0 | 0 | 1 | 25 | 17 | 0 | 0 | 408 | 7 | 170 | 680 | 20 | 0 |  | 7620 | 4676 | 12296 | 4493 | 907 | 2480 | 0 | 781 | 3345 | 30 | 0 | 74 | 86 | 99 | 1 | 0 | 73.57
8:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 406 | 0 |  | 0 | 450 | 313 | 0 | 0 | 15 | 325 | 0 | 0 | 0 | 50 | 16 | 0 | 0 | 0 | 0 | 13 | 55 | 55 | 0 | 18 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 58 | 0 | 0 | 0 | 0 | 13 | 2 | 0 | 0 | 0 | 290 | 240 | 211 | 8 | 50 | 35 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 98 | 96 | 0 | 0 | 1 | 40 | 20 | 52 | 39 | 112 | 0 | 56 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 23 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 72 | 10 | 12 | 17 | 0 | 351 | 49 | 17 | 0 | 3 | 52 | 0 | 0 | 17 | 38 | 48 | 340 | 68 | 21 | 108 | 0 | 0 | 35 | 16 | 75 | 0 | 240 | 0 | 0 | 448 | 4 | 538 | 250 | 300 | 37 |  | 907 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 189 | 0 | 330 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 700 | 110 | 0 | 0 | 2 | 51 | 74 | 0 | 0 | 411 | 14 | 170 | 678 | 70 | 0 |  | 7683 | 4713 | 12396 | 4361 | 907 | 2453 | 0 | 996 | 3245 | 30 | 0 | 74 | 98 | 228 | 4 | 52 | 73.57
9:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 403 | 0 |  | 0 | 450 | 309 | 1 | 0 | 15 | 325 | 0 | 0 | 14 | 64 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 18 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 50 | 0 | 0 | 0 | 0 | 14 | 2 | 0 | 0 | 0 | 305 | 240 | 217 | 8 | 50 | 34 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 102 | 95 | 0 | 0 | 2 | 42 | 20 | 52 | 39 | 112 | 0 | 58 | 0 | 0 | 132 | 0 | 0 | 0 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 72 | 0 | 37 | 17 | 0 | 378 | 49 | 17 | 0 | 2 | 52 | 0 | 0 | 17 | 38 | 48 | 345 | 65 | 35 | 108 | 1 | 0 | 0 | 13 | 75 | 0 | 240 | 0 | 0 | 448 | 7 | 501 | 250 | 300 | 39 |  | 908 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 195 | 0 | 348 | 0 | 0 | 0 | 0 | 42 | 0 | 5 | 0 | 700 | 110 | 0 | 0 | 3 | 70 | 74 | 0 | 0 | 407 | 22 | 170 | 754 | 98 | 0 |  | 7697 | 4905 | 12602 | 4448 | 908 | 2467 | 0 | 1005 | 3280 | 30 | 0 | 66 | 102 | 289 | 7 | 189 | 73.56
10:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 402 | 0 |  | 0 | 450 | 302 | 32 | 34 | 15 | 320 | 0 | 0 | 28 | 64 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 105 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 50 | 0 | 0 | 0 | 0 | 14 | 2 | 0 | 0 | 0 | 305 | 240 | 215 | 8 | 51 | 34 | 50 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 114 | 90 | 0 | 0 | 1 | 40 | 20 | 52 | 39 | 112 | 0 | 57 | 0 | 0 | 130 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 71 | 0 | 49 | 17 | 0 | 380 | 49 | 17 | 0 | 5 | 51 | 0 | 0 | 17 | 38 | 45 | 365 | 68 | 32 | 108 | 17 | 0 | 0 | 28 | 75 | 0 | 240 | 5 | 0 | 451 | 3 | 594 | 250 | 300 | 62 |  | 907 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 700 | 110 | 0 | 0 | 2 | 90 | 74 | 0 | 0 | 407 | 28 | 170 | 759 | 166 | 0 |  | 7988 | 5060 | 13048 | 4450 | 907 | 2533 | 0 | 1123 | 3381 | 30 | 0 | 87 | 114 | 420 | 3 | 126.06 | 73.56
11:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 401 | 0 |  | 0 | 450 | 305 | 48 | 72 | 15 | 317 | 0 | 0 | 46 | 90 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 17 | 15 | 33 | 24 | 8 | 0 | 30 | 0 | 100 | 0 | 0 | 212 | 0 | 0 | 0 |  | 18 | 50 | 0 | 10 | 0 | 0 | 14 | 2 | 0 | 0 | 0 | 290 | 260 | 212 | 8 | 50 | 31 | 49 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 116 | 66 | 0 | 0 | 2 | 40 | 30 | 50 | 39 | 112 | 0 | 58 | 0 | 0 | 130 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 71 | 18 | 49 | 17 | 26 | 366 | 49 | 17 | 0 | 5 | 51 | 0 | 0 | 23 | 38 | 48 | 350 | 68 | 36 | 108 | 17 | 0 | 6 | 32 | 75 | 0 | 270 | 53 | 0 | 483 | 2 | 735 | 254 | 300 | 27 |  | 907 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 200 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 195 | 0 | 414 | 1 | 0 | 0 | 0 | 35 | 0 | 7 | 0 | 700 | 110 | 0 | 0 | 5 | 97 | 74 | 0 | 0 | 407 | 21 | 170 | 756 | 45 | 0 |  | 8313 | 4891 | 13204 | 4396 | 907 | 2529 | 0 | 1273 | 3521 | 30 | 0 | 135 | 116 | 295 | 2 | 139.43 | 73.55
12:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 401 | 0 |  | 0 | 450 | 303 | 72 | 80 | 15 | 316 | 0 | 0 | 65 | 90 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 17 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 102 | 0 | 2 | 213 | 0 | 0 | 0 |  | 18 | 48 | 51 | 36 | 5 | 5 | 14 | 0 | 0 | 0 | 0 | 290 | 280 | 190 | 8 | 50 | 35 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 126 | 68 | 0 | 0 | 1 | 40 | 30 | 50 | 39 | 112 | 0 | 56 | 0 | 0 | 130 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 71 | 18 | 49 | 17 | 58 | 375 | 49 | 17 | 0 | 5 | 51 | 0 | 13 | 97 | 38 | 48 | 350 | 70 | 28 | 108 | 17 | 0 | 17 | 35 | 67 | 0 | 300 | 53 | 0 | 486 | 0 | 675 | 270 | 300 | 55 |  | 907 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 189 | 0 | 414 | 17 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 700 | 110 | 0 | 0 | 4 | 99 | 74 | 0 | 0 | 409 | 25 | 170 | 763 | 178 | 0 |  | 8611 | 5090 | 13701 | 4454 | 907 | 2525 | 0 | 1501 | 3503 | 30 | 0 | 200 | 126 | 455 | 0 | 142.295 | 73.54
13:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 401 | 0 |  | 0 | 450 | 303 | 91 | 80 | 30 | 312 | 0 | 0 | 75 | 90 | 115 | 0 | 0 | 0 | 0 | 43 | 55 | 55 | 0 | 17 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 213 | 0 | 0 | 0 |  | 18 | 48 | 51 | 36 | 35 | 6 | 14 | 3 | 0 | 0 | 0 | 295 | 280 | 184 | 8 | 50 | 34 | 47 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 24 | 14 | 126 | 67 | 0 | 0 | 2 | 39 | 30 | 53 | 38 | 112 | 0 | 54 | 0 | 0 | 130 | 0 | 0 | 0 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 57 | 0 | 71 | 17 | 49 | 17 | 75 | 375 | 49 | 17 | 25 | 5 | 51 | 6 | 26 | 97 | 47 | 48 | 350 | 70 | 46 | 162 | 17 | 0 | 17 | 32 | 38 | 0 | 270 | 53 | 0 | 486 | 8 | 562 | 450 | 350 | 57 |  | 908 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 5 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 195 | 0 | 0 | 17 | 0 | 10 | 0 | 65 | 0 | 7 | 70 | 740 | 110 | 0 | 17 | 3 | 96 | 94 | 0 | 0 | 410 | 32 | 170 | 759 | 160 | 0 |  | 9017 | 4898 | 13915 | 4429 | 908 | 2366 | 0 | 1891 | 3426 | 30 | 0 | 274 | 126 | 457 | 8 | 177 | 73.54
14:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 402 | 0 |  | 0 | 450 | 304 | 90 | 80 | 30 | 315 | 0 | 0 | 80 | 90 | 146 | 5 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 102 | 0 | 8 | 213 | 0 | 0 | 0 |  | 18 | 48 | 51 | 36 | 40 | 6 | 14 | 3 | 0 | 0 | 0 | 280 | 260 | 211 | 8 | 80 | 34 | 45 | 0 | 51 | 0 | 0 | 34 | 0 | 0 | 32 | 14 | 120 | 69 | 0 | 0 | 2 | 39 | 30 | 52 | 38 | 112 | 0 | 54 | 0 | 0 | 130 | 0 | 0 | 0 | 305 | 24 | 8 | 0 | 65 | 0 | 0 | 57 | 0 | 43 | 17 | 49 | 17 | 78 | 368 | 48 | 17 | 34 | 4 | 51 | 51 | 51 | 97 | 56 | 48 | 350 | 70 | 8 | 162 | 17 | 0 | 17 | 28 | 36 | 0 | 250 | 53 | 0 | 486 | 5 | 502 | 450 | 350 | 59 |  | 907 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 5 | 42 | 0 | 16 | 14 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 195 | 0 | 0 | 17 | 0 | 84 | 0 | 66 | 0 | 7 | 108 | 800 | 110 | 0 | 17 | 4 | 86 | 108 | 0 | 0 | 410 | 30 | 170 | 760 | 105 | 0 |  | 9095 | 5047 | 14142 | 4422 | 907 | 2364 | 0 | 2157 | 3428 | 30 | 0 | 359 | 120 | 350 | 5 | 151 | 73.55
15:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 401 | 0 |  | 0 | 450 | 299 | 91 | 80 | 30 | 311 | 0 | 0 | 85 | 90 | 145 | 20 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 17 | 15 | 33 | 31 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 213 | 0 | 0 | 0 |  | 18 | 48 | 67 | 36 | 48 | 6 | 14 | 0 | 0 | 0 | 0 | 295 | 260 | 211 | 8 | 75 | 34 | 45 | 0 | 51 | 0 | 2 | 29 | 0 | 0 | 32 | 14 | 120 | 70 | 0 | 0 | 2 | 39 | 30 | 51 | 38 | 112 | 0 | 54 | 0 | 0 | 128 | 0 | 0 | 0 | 300 | 24 | 8 | 0 | 255 | 0 | 0 | 57 | 0 | 35 | 13 | 49 | 17 | 88 | 385 | 48 | 17 | 34 | 3 | 51 | 54 | 51 | 97 | 57 | 48 | 360 | 52 | 27 | 162 | 17 | 0 | 17 | 23 | 37 | 0 | 250 | 17 | 0 | 486 | 5 | 590 | 400 | 300 | 45 |  | 906 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 126 | 7 | 0 | 0 | 0 | 0 | 13 | 5 | 42 | 0 | 25 | 30 | 0 | 0 | 0 | 0 | 5 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 192 | 0 | 0 | 17 | 0 | 113 | 0 | 80 | 0 | 6 | 113 | 740 | 110 | 0 | 14 | 3 | 69 | 114 | 0 | 0 | 409 | 23 | 170 | 765 | 24 | 0 |  | 9241 | 5027 | 14268 | 4489 | 906 | 2250 | 0 | 2401 | 3460 | 30 | 0 | 369 | 120 | 238 | 5 | 174 | 73.53
16:00 | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 403 | 0 |  | 0 | 450 | 303 | 90 | 80 | 15 | 319 | 0 | 0 | 85 | 90 | 144 | 25 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 17 | 15 | 33 | 31 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 212 | 0 | 0 | 0 |  | 18 | 48 | 68 | 36 | 61 | 6 | 12 | 0 | 0 | 0 | 0 | 280 | 260 | 212 | 8 | 76 | 31 | 42 | 0 | 51 | 0 | 27 | 34 | 0 | 0 | 32 | 14 | 122 | 70 | 0 | 0 | 1 | 39 | 30 | 52 | 38 | 112 | 0 | 54 | 0 | 0 | 128 | 0 | 0 | 0 | 300 | 24 | 8 | 0 | 260 | 0 | 0 | 57 | 0 | 35 | 9 | 49 | 20 | 93 | 367 | 48 | 17 | 34 | 3 | 51 | 54 | 51 | 97 | 56 | 48 | 350 | 52 | 21 | 162 | 17 | 0 | 17 | 14 | 53 | 0 | 250 | 17 | 0 | 485 | 6 | 736 | 450 | 0 | 30 |  | 906 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 126 | 8 | 0 | 0 | 0 | 0 | 40 | 12 | 42 | 0 | 25 | 30 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 193 | 0 | 0 | 17 | 0 | 113 | 0 | 82 | 0 | 3 | 113 | 660 | 110 | 0 | 14 | 2 | 48 | 114 | 0 | 0 | 357 | 15 | 200 | 769 | 83 | 0 |  | 9146 | 4944 | 14090 | 4412 | 906 | 2003 | 0 | 2447 | 3507 | 30 | 0 | 428 | 122 | 229 | 6 | 201 | 73.53
17:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 405 | 0 |  | 0 | 450 | 280 | 90 | 80 | 30 | 315 | 0 | 0 | 85 | 90 | 144 | 14 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 17 | 15 | 33 | 31 | 8 | 0 | 30 | 0 | 105 | 0 | 8 | 212 | 0 | 0 | 0 |  | 18 | 64 | 85 | 36 | 75 | 9 | 15 | 2 | 0 | 0 | 0 | 280 | 260 | 213 | 8 | 76 | 35 | 42 | 0 | 51 | 0 | 31 | 34 | 0 | 0 | 32 | 14 | 114 | 75 | 0 | 0 | 0 | 39 | 30 | 52 | 38 | 112 | 0 | 54 | 0 | 0 | 130 | 0 | 0 | 0 | 280 | 24 | 8 | 0 | 275 | 0 | 0 | 57 | 0 | 35 | 0 | 49 | 17 | 90 | 330 | 48 | 17 | 51 | 1 | 52 | 54 | 51 | 97 | 63 | 48 | 350 | 52 | 9 | 162 | 17 | 0 | 17 | 7 | 54 | 0 | 270 | 17 | 0 | 485 | 2 | 594 | 451 | 0 | 12 |  | 906 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 122 | 7 | 0 | 0 | 0 | 0 | 40 | 11 | 42 | 10 | 34 | 30 | 0 | 30 | 0 | 0 | 8 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 185 | 0 | 0 | 17 | 0 | 113 | 0 | 90 | 0 | 2 | 113 | 690 | 110 | 0 | 17 | 1 | 23 | 114 | 0 | 0 | 360 | 7 | 250 | 769 | 40 | 0 |  | 8994 | 4981 | 13975 | 4388 | 906 | 1959 | 0 | 2533 | 3447 | 30 | 0 | 494 | 114 | 102 | 2 | 167 | 73.52
18:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 330 | 0 |  | 0 | 380 | 300 | 83 | 80 | 30 | 250 | 0 | 0 | 80 | 90 | 148 | 14 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 15 | 0 | 31 | 8 | 0 | 30 | 0 | 110 | 0 | 17 | 211 | 0 | 0 | 0 |  | 18 | 64 | 85 | 12 | 75 | 19 | 15 | 2 | 0 | 0 | 0 | 280 | 260 | 214 | 8 | 70 | 35 | 42 | 0 | 51 | 0 | 31 | 37 | 0 | 0 | 32 | 0 | 100 | 101 | 0 | 0 | 0 | 39 | 30 | 52 | 41 | 80 | 0 | 60 | 0 | 0 | 130 | 0 | 0 | 0 | 260 | 24 | 8 | 0 | 195 | 0 | 0 | 57 | 0 | 37 | 0 | 49 | 17 | 95 | 306 | 58 | 17 | 51 | 0 | 52 | 54 | 51 | 97 | 84 | 62 | 310 | 52 | 1 | 162 | 18 | 0 | 46 | 1 | 53 | 0 | 270 | 17 | 0 | 486 | 1 | 505 | 310 | 62 | 2 |  | 905 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 130 | 7 | 0 | 0 | 0 | 0 | 40 | 11 | 42 | 21 | 34 | 33 | 0 | 32 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 185 | 0 | 96 | 17 | 0 | 35 | 0 | 86 | 0 | 1 | 35 | 640 | 110 | 0 | 17 | 0 | 4 | 115 | 0 | 0 | 365 | 1 | 200 | 768 | 11 | 0 |  | 8474 | 4795 | 13269 | 4173 | 905 | 1874 | 0 | 2398 | 3264 | 30 | 0 | 503 | 100 | 21 | 1 | 125 | 73.52
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 404 | 0 |  | 0 | 450 | 306 | 43 | 68 | 45 | 314 | 0 | 0 | 34 | 90 | 146 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 17 | 31 | 8 | 0 | 30 | 0 | 102 | 0 | 25 | 211 | 0 | 0 | 0 |  | 24 | 72 | 85 | 30 | 85 | 19 | 15 | 20 | 0 | 0 | 0 | 280 | 260 | 213 | 8 | 70 | 36 | 42 | 0 | 51 | 0 | 31 | 42 | 0 | 0 | 32 | 14 | 98 | 95 | 0 | 0 | 0 | 38 | 30 | 53 | 41 | 112 | 0 | 55 | 0 | 0 | 130 | 0 | 0 | 0 | 290 | 24 | 8 | 0 | 195 | 0 | 0 | 105 | 0 | 103 | 0 | 62 | 17 | 112 | 366 | 97 | 70 | 51 | 0 | 52 | 54 | 51 | 97 | 101 | 62 | 340 | 69 | 0 | 161 | 50 | 0 | 50 | 0 | 58 | 0 | 300 | 108 | 0 | 486 | 0 | 508 | 500 | 62 | 0 |  | 906 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 28 | 20 | 24 | 124 | 10 | 0 | 0 | 0 | 0 | 41 | 11 | 90 | 35 | 34 | 35 | 8 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 191 | 0 | 192 | 17 | 0 | 51 | 0 | 92 | 0 | 0 | 90 | 860 | 110 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 421 | 0 | 304 | 763 | 0 | 0 |  | 9477 | 5489 | 14966 | 4430 | 906 | 2320 | 0 | 2843 | 3642 | 30 | 0 | 697 | 98 | 0 | 0 | 166 | 73.5
19:30 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 413 | 0 |  | 0 | 450 | 275 | 91 | 68 | 55 | 310 | 0 | 0 | 40 | 90 | 150 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 17 | 31 | 8 | 0 | 30 | 0 | 103 | 0 | 25 | 213 | 0 | 0 | 0 |  | 24 | 70 | 85 | 48 | 95 | 19 | 15 | 14 | 0 | 0 | 0 | 280 | 260 | 216 | 8 | 70 | 36 | 42 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 108 | 95 | 0 | 0 | 0 | 38 | 30 | 53 | 41 | 112 | 0 | 59 | 0 | 0 | 126 | 0 | 0 | 0 | 260 | 24 | 8 | 0 | 245 | 0 | 0 | 105 | 0 | 134 | 0 | 62 | 17 | 125 | 367 | 98 | 70 | 51 | 0 | 52 | 54 | 51 | 97 | 104 | 62 | 340 | 70 | 0 | 35 | 53 | 0 | 50 | 0 | 54 | 0 | 300 | 125 | 0 | 486 | 0 | 504 | 500 | 63 | 0 |  | 857 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 30 | 38 | 24 | 124 | 10 | 16 | 0 | 0 | 0 | 41 | 11 | 90 | 35 | 34 | 35 | 8 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 185 | 0 | 315 | 17 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 1080 | 110 | 0 | 50 | 0 | 0 | 115 | 0 | 0 | 459 | 0 | 270 | 764 | 0 | 0 |  | 9518 | 5917 | 15435 | 4458 | 857 | 2380 | 0 | 3003 | 3863 | 30 | 0 | 736 | 108 | 0 | 0 | 253 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 407 | 0 |  | 0 | 450 | 294 | 74 | 68 | 55 | 312 | 0 | 0 | 58 | 90 | 150 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 0 | 31 | 8 | 0 | 30 | 0 | 111 | 0 | 25 | 212 | 0 | 0 | 0 |  | 24 | 70 | 85 | 48 | 95 | 19 | 15 | 20 | 0 | 0 | 0 | 285 | 260 | 217 | 8 | 50 | 36 | 43 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 110 | 95 | 0 | 0 | 0 | 40 | 30 | 53 | 41 | 80 | 0 | 59 | 0 | 0 | 126 | 0 | 0 | 0 | 265 | 24 | 8 | 0 | 260 | 0 | 0 | 107 | 0 | 133 | 0 | 62 | 17 | 122 | 371 | 98 | 70 | 51 | 0 | 52 | 54 | 51 | 97 | 104 | 62 | 340 | 70 | 0 | 35 | 53 | 0 | 49 | 0 | 53 | 0 | 300 | 163 | 0 | 486 | 0 | 506 | 500 | 160 | 0 |  | 620 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 90 | 35 | 8 | 40 | 0 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 185 | 0 | 320 | 17 | 0 | 113 | 0 | 92 | 0 | 0 | 113 | 1000 | 110 | 0 | 50 | 0 | 0 | 114 | 0 | 0 | 456 | 0 | 297 | 763 | 0 | 0 |  | 9646 | 5439 | 15085 | 4434 | 620 | 2481 | 0 | 2926 | 3808 | 30 | 0 | 676 | 110 | 0 | 0 | 301 | 73.51
21:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 402 | 0 |  | 0 | 450 | 302 | 63 | 80 | 55 | 314 | 0 | 0 | 48 | 90 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 21 | 15 | 33 | 31 | 8 | 0 | 30 | 0 | 108 | 0 | 25 | 212 | 0 | 0 | 0 |  | 24 | 70 | 85 | 48 | 85 | 20 | 15 | 31 | 0 | 0 | 0 | 315 | 260 | 212 | 8 | 52 | 36 | 44 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 106 | 103 | 0 | 0 | 0 | 40 | 30 | 53 | 42 | 80 | 0 | 58 | 0 | 0 | 126 | 0 | 0 | 0 | 305 | 24 | 8 | 0 | 195 | 0 | 0 | 107 | 0 | 149 | 0 | 62 | 17 | 127 | 370 | 99 | 70 | 51 | 0 | 52 | 54 | 51 | 97 | 95 | 62 | 355 | 72 | 0 | 35 | 53 | 0 | 50 | 0 | 39 | 0 | 280 | 163 | 0 | 486 | 0 | 506 | 500 | 300 | 0 |  | 620 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 90 | 35 | 8 | 38 | 0 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 198 | 0 | 320 | 17 | 0 | 113 | 0 | 92 | 0 | 0 | 113 | 990 | 110 | 0 | 97 | 0 | 0 | 114 | 0 | 0 | 462 | 0 | 270 | 769 | 0 | 0 |  | 9770 | 5522 | 15292 | 4556 | 620 | 2682 | 0 | 2842 | 3783 | 30 | 0 | 673 | 106 | 0 | 0 | 294 | 73.5
22:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 401 | 0 |  | 0 | 450 | 303 | 50 | 80 | 30 | 318 | 0 | 0 | 40 | 90 | 150 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 18 | 20 | 33 | 31 | 8 | 0 | 30 | 0 | 100 | 0 | 25 | 212 | 0 | 0 | 0 |  | 24 | 70 | 85 | 48 | 95 | 20 | 15 | 33 | 0 | 0 | 0 | 305 | 260 | 201 | 8 | 72 | 37 | 47 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 92 | 102 | 0 | 0 | 0 | 39 | 30 | 53 | 42 | 112 | 0 | 56 | 0 | 0 | 125 | 0 | 0 | 0 | 310 | 24 | 8 | 0 | 195 | 0 | 0 | 107 | 0 | 86 | 0 | 62 | 17 | 128 | 402 | 99 | 70 | 51 | 0 | 52 | 54 | 51 | 97 | 94 | 62 | 360 | 72 | 0 | 35 | 53 | 0 | 50 | 0 | 36 | 0 | 270 | 17 | 0 | 486 | 0 | 509 | 500 | 350 | 0 |  | 625 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 90 | 35 | 8 | 35 | 0 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 203 | 0 | 414 | 17 | 0 | 113 | 0 | 92 | 0 | 0 | 113 | 990 | 110 | 0 | 94 | 0 | 0 | 114 | 0 | 0 | 460 | 0 | 270 | 765 | 0 | 0 |  | 9566 | 5617 | 15183 | 4588 | 625 | 2869 | 0 | 2680 | 3780 | 30 | 0 | 519 | 92 | 0 | 0 | 331.385 | 73.5
23:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 400 | 0 |  | 0 | 450 | 300 | 49 | 80 | 30 | 318 | 0 | 0 | 40 | 90 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 33 | 16 | 8 | 0 | 30 | 0 | 100 | 0 | 17 | 213 | 0 | 0 | 0 |  | 24 | 70 | 85 | 35 | 91 | 20 | 15 | 35 | 0 | 0 | 0 | 335 | 280 | 206 | 0 | 70 | 37 | 50 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 90 | 102 | 0 | 0 | 0 | 39 | 30 | 53 | 42 | 112 | 0 | 55 | 0 | 0 | 125 | 0 | 0 | 0 | 315 | 24 | 8 | 0 | 195 | 0 | 0 | 107 | 0 | 35 | 0 | 62 | 17 | 128 | 398 | 99 | 17 | 51 | 0 | 52 | 54 | 51 | 97 | 95 | 61 | 365 | 72 | 0 | 35 | 53 | 0 | 50 | 0 | 19 | 0 | 250 | 17 | 0 | 489 | 0 | 509 | 500 | 350 | 0 |  | 627 | 0 | 390 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 89 | 35 | 8 | 35 | 0 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 205 | 0 | 414 | 17 | 0 | 113 | 0 | 92 | 0 | 0 | 113 | 1000 | 110 | 0 | 77 | 0 | 0 | 115 | 0 | 0 | 457 | 0 | 276 | 771 | 0 | 0 |  | 9249 | 5642 | 14891 | 4622 | 627 | 2868 | 0 | 2452 | 3802 | 30 | 0 | 400 | 90 | 0 | 0 | 361.945 | 73.49
24:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 403 | 0 |  | 0 | 450 | 299 | 70 | 80 | 30 | 323 | 0 | 0 | 50 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 20 | 33 | 31 | 0 | 0 | 30 | 0 | 100 | 0 | 8 | 212 | 0 | 0 | 0 |  | 24 | 70 | 85 | 35 | 87 | 6 | 15 | 30 | 0 | 0 | 0 | 285 | 260 | 209 | 0 | 50 | 34 | 50 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 112 | 99 | 0 | 0 | 0 | 39 | 30 | 53 | 42 | 112 | 0 | 56 | 0 | 0 | 127 | 0 | 0 | 0 | 310 | 24 | 5 | 0 | 220 | 0 | 0 | 108 | 0 | 36 | 0 | 49 | 17 | 122 | 367 | 99 | 17 | 17 | 0 | 52 | 54 | 51 | 97 | 78 | 61 | 340 | 58 | 0 | 35 | 17 | 0 | 49 | 0 | 18 | 0 | 260 | 17 | 0 | 492 | 0 | 507 | 450 | 350 | 0 |  | 627 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 11 | 59 | 35 | 34 | 35 | 0 | 30 | 0 | 0 | 8 | 71 | 0 | 230 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 196 | 0 | 396 | 17 | 0 | 113 | 0 | 92 | 0 | 0 | 113 | 1100 | 110 | 0 | 36 | 0 | 0 | 115 | 0 | 0 | 490 | 0 | 305 | 765 | 0 | 0 |  | 8978 | 5679 | 14657 | 4437 | 627 | 2788 | 0 | 2349 | 3960 | 30 | 0 | 354 | 112 | 0 | 0 | 585.415 | 73.49
KWH | 0 | 0 | 0 | 4284000 | 0 | 1845227 | 0 | 9756000 | 0 |  | 0 | 10215000 | 7313833 | 1463040 | 1414545 | 636293 | 7646667 | 0 | 0 | 1205990 | 1732896 | 1748640 | 93973 | 0 | 0 | 0 | 654120 | 1115720 | 912846 | 0 | 452000 | 392400 | 727400 | 726100 | 192960 | 0 | 719700 | 0 | 2300000 | 0 | 191716 | 5023759 | 0 | 0 | 0 |  | 482640 | 1382688 | 1116449 | 424800 | 993600 | 173760 | 312144 | 432480 | 0 | 0 | 0 | 7674000 | 6251000 | 5106000 | 200727 | 1287560 | 824616 | 1139520 | 0 | 1156827 | 0 | 377088 | 683237 | 0 | 0 | 764400 | 312220 | 2560320 | 2160000 | 0 | 0 | 12700 | 935000 | 621120 | 1247400 | 947376 | 2453891 | 0 | 1360032 | 0 | 0 | 3130840 | 0 | 0 | 0 | 7202000 | 522168 | 189408 | 0 | 2401199 | 0 | 0 | 1776000 | 0 | 2040192 | 116505 | 1145280 | 432000 | 1348218 | 8751000 | 1580400 | 606720 | 579599 | 36438 | 1252036 | 745396 | 681630 | 1855920 | 1419600 | 1273920 | 8283800 | 1497600 | 292500 | 2253600 | 516873 | 0 | 735840 | 241530 | 1406400 | 0 | 6410300 | 761090 | 0 | 11427271 | 49920 | 13760000 | 7937727 | 6886364 | 474218 |  | 19979636 | 0 | 8758944 | 0 | 36480 | 0 | 0 | 0 | 30720 | 31360 | 101250 | 3070000 | 197016 | 10560 | 0 | 0 | 0 | 195547 | 115359 | 702784 | 217340 | 221432 | 331580 | 9917 | 249430 | 0 | 0 | 186120 | 1595781 | 0 | 5578000 | 0 | 0 | 0 | 0 | 4751682 | 0 | 0 | 0 | 4895473 | 0 | 6654109 | 331200 | 0 | 1133088 | 0 | 1345728 | 0 | 54765 | 1148736 | 22848900 | 2531045 | 0 | 475200 | 35220 | 773280 | 1986048 | 0 | 0 | 10378180 | 220361 | 5432700 | 17797651 | 1141310 | 0 |  | 208179922 | 125553932 | 333733854 | 107866153 | 19979636 | 58360542 | 0 | 44937538 | 88818483 | 719700 | 0 | 7042735 | 2560320 | 3398827 | 49920 | 0
Fuel Cost | 0 | 0 | 0 | 19063800 | 0 | 7048767.14 | 0 | 28097280 | 0 |  | 0 | 32483700 | 25013308.86 | 28909670.4 | 26451991.5 | 11211482.66 | 23322334.35 | 0 | 0 | 23830362.4 | 31105483.2 | 33958588.8 | 1752596.45 | 0 | 0 | 0 | 11944231.2 | 17583747.2 | 16695953.34 | 0 | 339000 | 0 | 0 | 0 | 3455913.6 | 0 | 0 | 0 | 12558000 | 0 | 3631101.04 | 16025791.21 | 0 | 0 | 0 |  | 8489637.6 | 24349135.68 | 19995601.59 | 8096688 | 19444752 | 2860089.6 | 1161175.68 | 0 | 0 | 0 | 0 | 21410460 | 19128060 | 16951920 | 672435.45 | 4158818.8 | 2778955.92 | 4991097.6 | 0 | 4638876.27 | 0 | 6753646.08 | 12339260.22 | 0 | 0 | 2843568 | 234165 | 16795699.2 | 6717600 | 0 | 0 | 0 | 3646500 | 2316777.6 | 5675670 | 4310560.8 | 8392307.22 | 0 | 7548177.6 | 0 | 0 | 8735043.6 | 0 | 0 | 0 | 22254180 | 391626 | 143950.08 | 0 | 48984459.6 | 0 | 0 | 34116960 | 0 | 35927781.12 | 0 | 20397436.8 | 7495200 | 22353454.44 | 23190150 | 30122424 | 11382067.2 | 10398006.06 | 0 | 20470788.6 | 14490498.24 | 12228442.2 | 35466631.2 | 27554436 | 22688515.2 | 22034908 | 25564032 | 0 | 41218344 | 8673128.94 | 0 | 13149460.8 | 0 | 25343328 | 0 | 19038591 | 10716147.2 | 0 | 79648078.87 | 0 | 81184000 | 0 | 0 | 0 |  | 56142777.16 | 0 | 25838884.8 | 0 | 632928 | 0 | 0 | 0 | 577843.2 | 589881.6 | 1802250 | 9701200 | 933855.84 | 182054.4 | 0 | 0 | 0 | 3502246.77 | 2116837.65 | 11813799.04 | 4624995.2 | 4222708.24 | 5938597.8 | 175530.9 | 4467291.3 | 0 | 0 | 140892.84 | 17601464.43 | 0 | 47078320 | 0 | 0 | 0 | 0 | 15823101.06 | 0 | 0 | 0 | 16301925.09 | 0 | 19429998.28 | 5656896 | 0 | 22457804.16 | 0 | 26806901.76 | 0 | 0 | 22790922.24 | 148060872 | 7871549.95 | 0 | 9195120 | 0 | 0 | 34457932.8 | 0 | 0 | 75760714 | 0 | 40473615 | 117642473.11 | 0 | 0 |  | 1346546808.41 | 760814184.62 | 2107360993.03 | 329642656.63 | 56142777.16 | 143716307.41 | 0 | 828834398.51 | 607449537.41 | 0 | 0 | 124779616.71 | 16795699.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 79 | 0 | 401 | 0 |  | 0 | 450 | 303 | 72 | 80 | 15 | 316 | 0 | 0 | 65 | 90 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 17 | 15 | 33 | 32 | 8 | 0 | 30 | 0 | 102 | 0 | 2 | 213 | 0 | 0 | 0 |  | 18 | 48 | 51 | 36 | 5 | 5 | 14 | 0 | 0 | 0 | 0 | 290 | 280 | 190 | 8 | 50 | 35 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 32 | 8 | 126 | 68 | 0 | 0 | 1 | 40 | 30 | 50 | 39 | 112 | 0 | 56 | 0 | 0 | 130 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 58 | 0 | 71 | 18 | 49 | 17 | 58 | 375 | 49 | 17 | 0 | 5 | 51 | 0 | 13 | 97 | 38 | 48 | 350 | 70 | 28 | 108 | 17 | 0 | 17 | 35 | 67 | 0 | 300 | 53 | 0 | 486 | 0 | 675 | 270 | 300 | 55 |  | 907 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 189 | 0 | 414 | 17 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 700 | 110 | 0 | 0 | 4 | 99 | 74 | 0 | 0 | 409 | 25 | 170 | 763 | 178 | 0 |  | 13701 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 413 | 0 |  | 0 | 450 | 275 | 91 | 68 | 55 | 310 | 0 | 0 | 40 | 90 | 150 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 15 | 17 | 31 | 8 | 0 | 30 | 0 | 103 | 0 | 25 | 213 | 0 | 0 | 0 | 0 | 24 | 70 | 85 | 48 | 95 | 19 | 15 | 14 | 0 | 0 | 0 | 280 | 260 | 216 | 8 | 70 | 36 | 42 | 0 | 51 | 0 | 31 | 43 | 0 | 0 | 32 | 16 | 108 | 95 | 0 | 0 | 0 | 38 | 30 | 53 | 41 | 112 | 0 | 59 | 0 | 0 | 126 | 0 | 0 | 0 | 260 | 24 | 8 | 0 | 245 | 0 | 0 | 105 | 0 | 134 | 0 | 62 | 17 | 125 | 367 | 98 | 70 | 51 | 0 | 52 | 54 | 51 | 97 | 104 | 62 | 340 | 70 | 0 | 35 | 53 | 0 | 50 | 0 | 54 | 0 | 300 | 125 | 0 | 486 | 0 | 504 | 500 | 63 | 0 |  | 857 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 30 | 38 | 24 | 124 | 10 | 16 | 0 | 0 | 0 | 41 | 11 | 90 | 35 | 34 | 35 | 8 | 30 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 185 | 0 | 315 | 17 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 1080 | 110 | 0 | 50 | 0 | 0 | 115 | 0 | 0 | 459 | 0 | 270 | 764 | 0 | 0 |  | 15435 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 |  | 0 | 450 | 310 | 100 | 96 | 43 | 335 | 0 | 0 | 85 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 21 | 20 | 33 | 33 | 16 | 0 | 30 | 0 | 100 | 0 | 25 | 210 | 0 | 0 | 0 |  | 24 | 80 | 85 | 45 | 95 | 18 | 16 | 25 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 50 | 38 | 50 | 0 | 51 | 0 | 42 | 52 | 0 | 0 | 33 | 20 | 151 | 120 | 0 | 0 | 0 | 43 | 30 | 52 | 42 | 112 | 0 | 60 | 0 | 0 | 150 | 0 | 0 | 0 | 300 | 25 | 8 | 0 | 300 | 0 | 0 | 108 | 0 | 149 | 0 | 62 | 17 | 150 | 400 | 100 | 100 | 100 | 0 | 52 | 54 | 110 | 98 | 104 | 62 | 360 | 72 | 0 | 162 | 17 | 0 | 50 | 0 | 115 | 0 | 300 | 163 | 0 | 490 | 40 | 530 | 500 | 450 |  |  | 625 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 33 | 25 | 90 | 35 | 34 | 42 | 8 | 28 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 414 | 90 | 0 | 113 | 0 | 100 | 0 | 0 | 113 | 1244 | 110 | 0 | 50 | 0 | 0 | 115 | 0 | 0 | 500 | 0 | 307 | 748 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 400 | 0 | 0 | 0 | 450 | 310 | 90 | 96 | 43 | 300 | 0 | 0 | 60 | 90 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 20 | 33 | 33 | 8 | 0 | 30 | 0 | 100 | 0 | 8 | 210 |  | 0 | 0 | 0 | 22 | 80 | 51 | 40 | 20 | 6 | 16 | 5 | 0 | 0 | 0 | 300 | 300 | 220 | 8 | 50 | 38 | 50 | 0 | 51 | 0 | 36 | 52 | 0 | 0 | 33 | 20 | 146 | 100 | 0 | 0 | 1.6 | 43 | 30 | 52 | 42 | 112 | 0 | 60 | 0 | 0 | 150 | 0 | 0 | 0 | 300 | 25 | 8 | 0 | 300 | 0 | 0 | 56 | 0 | 135 | 20 | 49 | 17 | 150 | 400 | 50 | 17 | 100 | 5 | 52 | 17 | 110 | 98 | 57 | 48 | 340 | 72 | 50 | 162 | 17 | 0 | 50 | 35 | 115 | 0 | 300 | 54 | 0 | 490 | 40 | 530 | 400 | 450 | 33 |  | 935 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 130 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 42 | 8 | 0 | 0 | 0 | 11 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 200 | 0 | 400 | 90 | 0 | 35 | 0 | 42 | 0 | 8 | 113 | 1244 | 110 |  | 17 | 6 | 100 | 70 | 0 | 0 | 500 | 30 | 307 | 748 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 408 | 0 | 0 | 0 | 450 | 295 | 0 | 0 | 15 | 324 | 0 | 0 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 20 | 33 | 33 | 8 | 0 | 30 | 0 | 102 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 18 | 56 | 51 | 0 | 0 | 0 | 16 | 5 | 0 | 0 | 0 | 285 | 240 | 220 | 0 | 67 | 35 | 53 | 0 | 51 | 0 | 31 | 8 | 0 | 0 | 24 | 16 | 94 | 65 | 0 | 0 | 1 | 39 | 30 | 53 | 42 | 80 | 0 | 59 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 7 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 108 | 11 | 37 | 18 | 12 | 305 | 49 | 17 | 0 | 3 | 52 | 0 | 0 | 70 | 38 | 48 | 310 | 53 | 16 | 0 | 17 | 0 | 50 | 16 | 57 | 0 | 230 | 0 | 0 | 450 | 0 | 492 | 365 | 250 | 37 | 0 | 914 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 172 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 840 | 110 | 0 | 0 | 1 | 50 | 74 | 0 | 0 | 381 | 13 | 307 | 764 | 90 | 0 | 0 |  |  |  | 166226695 | 19979636 | 0 | 88818483 | 51980273 | 2560320 | 3398827 | 49920 | 719700 |  |  | 333733854
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 166.2267 | 19.9796 | 0 | 88.8185 | 51.9803 | 2.5603 | 3.3988 | 0.04992 | 0.7197
| Minimum Generation |  | 12270 | 6:00
| Highest Generation |  | 15435 | 19:30 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 333.7339
| Day Peak Generation |  | 13701 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15435 | 19:30 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 908 | 5:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 857 | 19:30
| Load factor L.F |  | 90.09% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-15
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13701 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 12482
Evening Peak Generation : |  |  | 15435 | MW Hour : | 19:30 | Available Max Generation : |  | 17130
E.P. Demand (at gen end) : |  |  | 15700 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 16000
Maximum Generation : |  |  | 15435 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1130
Total Gen. (MKWH) : |  |  | 333.7339 | System Load Factor : | 90.09% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 148 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-15
Actual : |  | 73.43 | Ft.(MSL) , | Rule curve : | 79.34 | Ft.( MSL )
Gas Consumed : |  | Total = | 1247.88 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 473358964.04
: |  |  | Coal : | 607449537.41 | Oil : | 953614015.22 | Total : | 2034422516.67
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 50 | 1200:00 | 4631.2738 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1272.9296 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1783.2374 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1550.0593 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1275.3707 |  |  | 0 | 0%
Mymensingh Area |  | 128 | 3072:00 | 948.6126 |  |  | 0 | 0%
Sylhet Area |  | 10 | 240:00 | 531.6643 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 443.1356 |  |  | 0 | 0%
Rangpur Area |  | 65 | 1560:00 | 866.6942 |  |  | 0 | 0%
Total |  | 253 |  | 13302.9775 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:25 | 17:15 | Sherpur 132/33kV S/S Transformer- 03 LT Project Work S/D
08:25 | 21:43 | Bogura-Rahanpur 400kV Ckt-1 Forced S/D from Bogura 400/230kV end Due to As per instruction by NLDC. and from
Rahanpur 400/132kV end Due to Sas witness
08:26 | 17:13 | Sherpur 132/33kV S/S Transformer- 03 HT Project Work S/D
| 08:27 | Bogura 132/33kV S/S Transformer-3 HT is restored.
| 08:27 | Bogura 132/33kV S/S Transformer-3 LT is restored.
| 08:38 | Gulsan-Rampura 132kV Ckt-2 is restored.
08:40 |  | Chapai 132/33kV S/S T-4 (435T) LT Scheduled S/D Due to Oil centrifuge
08:41 |  | Chapai 132/33kV S/S T-4 (435T) HT Scheduled S/D Due to Oil centrifuge
| 08:47 | Aminbazar 400/230/132kV S/S ATR-03 HT is restored.
| 08:50 | Aminbazar 400/230/132kV S/S ATR-03 LT is restored.
| 08:56 | Kodda 132/33kV S/S Tr-1 (406T) HT is restored.
| 08:57 | Kodda 132/33kV S/S Tr-1 (406T) LT is restored.
| 09:09 | Feni 132/33kV S/S T-2(415T) HT is restored.
09:15 |  | Rampur 230/132/33 S/S 132kV BUS-02 Forced S/D Due to 903 B Bus cupler singled CB Trip circuit Fail. All are shifted to
Bus-1 Bus cupler Open/ (S/D). (230kV energise by 132kV)
09:19 | 16:30 | Ashuganj-Sreepur 230 kV Ckt-2 Scheduled S/D from Ashuganj 230/132/33kV end Due to NLDC Instruction.
09:32 | 21:30 | Haripur-Siddirganj 230kV Ckt-2 Forced S/D from Siddhirganj 132/33kV end Due to Maintenance work in Haripur end.
09:34 |  | Haripur-Siddirganj 132kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to For Bus bar Protection Work by ERA
Construction.
09:43 | 16:32 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Project Work S/D Due to Project work
10:20 | 19:57 | Gopalganj 400/132kV S/S ATR-02 LT Scheduled S/D
10:21 | 19:57 | Gopalganj 400/132kV S/S ATR-02 HT Scheduled S/D
10:42 | 13:42 | Fenchuganj -Sylhet 132kV Ckt-1 Project Work S/D from Sylhet 132/33kV end Due to South Surma Grid SCDA test by
NLDC
11:20 |  | Ruppur 132/11kV S/S TR-02 HT Project Work S/D Due to CB replacing 11 kv side
11:24 |  | Ruppur 132/11kV S/S TR-02 LT Project Work S/D Due to CB replacing
12:00 |  | Day Peak Gen. 13701 MW
12:21 |  | Sirajgonj 400 MW CCPP Unit-4 Tripped with remarks:- GBC trip
12:21 |  | Sirajgonj 400 MW CCPP Unit-4 Tripped with remarks:- GBC trip
14:28 | 14:34 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing Over current relays Due to 33kv Zinzira-1 fault |  |  |  |  | 17.0MW load interrup.
15:43 |  | Meghnaghat CCPP(Summit)-2 Tripped
17:19 |  | Sirajgonj 400 MW CCPP Unit-4 Syncronized with remarks:- GT
17:35 |  | Meghnaghat CCPP(Summit)-2 Syncronized
| 17:57 | Kallyanpur-Lalbag 132kV Ckt-1 is restored.
18:32 |  | Sirajgonj 400 MW CCPP Unit-4 Syncronized with remarks:- ST
19:30 |  | Evening Peak Generation = 15,435MW
19:43 |  | Meghnaghat CCPP(Summit)-2 Syncronized with remarks:- ST
06:14 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kv bus DS high temperature maintenance. |  |  |  |  | 70.0MW load interrup.
06:14 |  | Kabirpur 132/33kV S/S XFR, T-2 LT Scheduled S/D Due to 33 kv bus DS high temperature maintenance. |  |  |  |  | 70.0MW load interrup.
06:57 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 132 kv CT & 33 kv CT terminal clamp connector Hot-spot Maintenance
06:57 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to 132 kv CT & 33 kv CT terminal clamp connector Hot-spot Maintenance
07:00 |  | Minimum genaration 12482 MW.
07:09 |  | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Loop replacement
because red hot
07:28 |  | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to PBS-2 Tetultola maintenance
07:30 |  | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33 kv Tetultola maintenance
07:51 |  | Kallyanpur-Lalbag 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to For maintenance work.
interrup.
07:25 |  | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to |  |  |  |  | 20.0MW
|  | Pbs work |  |  |  |  | load
interrup.
07:26 |  | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to |  |  |  |  | 20.0MW
|  | Pbs work |  |  |  |  | load
interrup.
09:27 |  | Mymensingh 200 MW PP (United) Syncronized
09:35 |  | Jamalpur 115 MW PP (United) Syncronized
09:37 |  | Mymensingh 200 MW PP (United) Syncronized
09:39 |  | Kodda 150 MW PP B-R Syncronized
07:28 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Dead line checking due Thunderstorm.
07:29 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Deadline checking due to heavy Thunderstorm
07:29 |  | Aminbazar-Mirpur 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Deadline checking due to heavy Thunderstorm
07:53 |  | Keranigonj 230/132/33kV S/S Hasnabad Tripped showing 86.1 relays Due to Thundering

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 76 | 1845227 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 413 | 9756000
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10215000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 91 | 1463040
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 7313833 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 68 | 1414545 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 636293
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 93973
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 40 | 1205990 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 7646667
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 1732896 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 654120
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1748640
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1115720
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 912846
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 844400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 727400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 726100
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 192960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 2401199 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 134 | 2040192 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 606720 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1497600 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 2253600 | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 241530
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Under maint.
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 500 | 7937727
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 63 | 6886364 | tripped at 15:43
| Dhaka area Total |  |  |  | 5332 | 3581 | 78394582
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 103 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 191716
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 116505
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 173760 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 719700 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 213 | 5023759
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 579599 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 70 | 1382688 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1116449 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 48 | 424800 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 1145280 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 312144 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 432480
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 993600 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36438
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1252036 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 745396
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 681630 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 62 | 1273920 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 516873 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 125 | 761090 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 486 | 11427271
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 49920 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 504 | 13760000 | Megnghat bus section limitation.
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 474218
| Chattogram area Total |  |  |  | 4404 | 2217 | 45891272
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 5106000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7674000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6251000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 6410300 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 824616 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 42 | 1139520 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1156827
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 125 | 1348218 | Transformer overload.
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 31 | 377088 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1287560
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 432000 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 108 | 2560320
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 764400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 683237 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 16 | 312220 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1855920 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 1419600 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 50 | 735840
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 1406400 | Fuel shortage
| Cumilla Area Total |  |  |  | 2929 | 1940 | 41945793
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 95 | 2160000 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12700
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 105 | 1776000 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1580400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 292500
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 482640
| Mymensingh Area Total |  |  |  | 592 | 322 | 6304240
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 935000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 621120 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2453891 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1247400
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 41 | 947376 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 189408 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1360032
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 126 | 3130840 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 522168
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7202000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8751000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8283800 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1458 | 35644035
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 857 | 19979636
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 16 | 36480
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 30720 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 38 | 31360 | Fuel shortage
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 345 | 8758944 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 24 | 101250 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 331200 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 773280
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 459 | 10378180
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1786 | 40421050
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 10560 | Megnghat bus section limitation.
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 197016 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 124 | 3070000 | Engine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 22848900 | Megnghat bus section limitation.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2531045
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 50 | 475200 | FGMO Test.
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 270 | 5432700
| Barisal Area Total |  |  |  | 2235 | 1660 | 34565421
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 41 | 195547 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 115359 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 217340
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 221432
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 331580 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4751682
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4895473 | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 315 | 6654109 | Gas shortage
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 249430 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 186120 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 9917 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 702784 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1133088
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1148736
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35220
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 764 | 17797651 | Unit-1 Reserve
| Rajshahi Area Total |  |  |  | 3431 | 1966 | 38645468
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1595781
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5578000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 1345728 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 54765
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1986048
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 220361
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1141310
| Rangpur Area Total |  |  |  | 950 | 505 | 11921993
| Total |  |  |  | 25903 | 15435 | 333733854
| Eastern Grid Total |  |  |  | 15588 | 9518 | 208179922
| Western Grid Total |  |  |  | 10315 | 5917 | 125553932
| National Grid Total |  |  |  | 25903 | 15435 | 333733854
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-14
| (a) ENTIRE EASTERN GRID : |  | 9973.61 | MW | (b) ENTIRE WESTERN GRID : |  | 4816.1 | MW
| i) Dhaka area |  | 5321.11 | MW | i) Khulna area |  | 1837 | MW
| ii) Chittagong area |  | 1489.5 | MW | ii) Rajshahi area |  | 1595.6 | MW
| iii) Comilla area |  | 1414 | MW | iii) Barisal area |  | 460.5 | MW
| iv) Mymensingh area |  | 1119 | MW | iv) Rangpur area |  | 923 | MW
| v) Sylhet area |  | 630 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14789.71 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 10 | 14:00 | Chhatak | 36 | 23:00 | Kalurghat | 40 | 11:00 | Narail | 62 | 19:30 | Shariatpur | 88 | 22:00
2 | AKSML | 105 | 12:00 | Chowmuhani | 236 | 23:00 | Kamrangirchar | 56.8 | 12:00 | Narinda | 51 | 13:00 | Sherpur | 140 | 19:30
3 | Aftabnagar | 50 | 09:00 | Chuadanga | 119 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 168 | 07:00 | Shikalbaha | 35 | 21:00
4 | Agargaon | 115 | 13:00 | Coxsbazar | 131 | 22:00 | Kazla | 109 | 14:00 | Natore | 164 | 19:30 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 80 | 15:00 | Cumilla(N) | 210 | 19:30 | Keranigonj | 81 | 19:30 | Nawabganj | 62.8 | 22:00 | Shitalakhya | 108.6 | 16:00
6 | Amnura | 72 | 22:00 | Cumilla(S) | 164 | 01:00 | Khagrachori | 30 | 22:00 | Netrakona | 142 | 22:00 | Sholosohor | 48 | 16:00
7 | Ashuganj | 88 | 19:00 | Daudkandi | 161 | 21:00 | Khulna | 97 | 19:30 | New | 62.4 | 14:00 | Shyampur | 174 | 10:00
8 | BIPTC | N/A | N/A | Dhaka | 54 | 13:00 | Khulshi | 192 | 16:00 | Niamatpur | 82 | 22:00 | Siddhirganj | 116 | 15:00
9 | BSRM | 183 | 15:00 | Dhamrai | 130 | 20:00 | Kishoreganj | 122 | 02:00 | Noapara | 50 | 22:00 | Sirajganj | 128 | 21:00
10 | Bagerhat | 94 | 23:00 | Dhanmondi | 149 | 13:00 | Kodda | 289 | 21:00 | PHP | 9 | 02:00 | Sonargaon | 129 | 16:00
11 | Bakulia | 104 | 19:30 | Dohazari | 107 | 19:30 | Kulaura | 56 | 22:00 | Pabna | 138 | 20:00 | Sreemongol | 74 | 19:30
12 | Banani | 63.2 | 14:00 | Faridpur | 172 | 21:00 | Kurigram | 68 | 19:00 | Palashbari | 124 | 22:00 | Sreepur | 68 | 18:00
13 | Bangabhaban | 15 | 10:00 | Fatullah | 72 | 11:00 | Kushtia | 154 | 19:30 | Panchagarh | 59 | 19:00 | Srinagar | 49 | 22:00
14 | Barapukuria | 68 | 23:00 | Fenchuganj | 46 | 19:00 | Lalbag | 93 | 12:00 | Patuakhali | 80 | 23:00 | Sunamganj | 60 | 19:00
15 | Barguna | 22 | 22:00 | Feni | 118 | 19:00 | Lalmonirhat | 58 | 22:00 | Payra | 36 | 22:00 | Sylhet | 42 | 19:00
16 | Barishal | 113 | 19:00 | GPH | 19 | 19:30 | MI_Cement | 11.6 | 11:00 | Postogola | 59 | 15:00 | Sylhet-132 | 135 | 19:00
17 | Barishal-230 | 102 | 19:30 | Ghatail | 60 | 19:30 | Madanganj | 37 | 15:00 | Purbachal | 14 | 19:30 | TK | 34.5 | 19:00
18 | Baroaulia | 84 | 15:00 | Ghorashal | 71 | 15:00 | Madaripur | 119 | 22:00 | Purbasadipur | 142 | 22:00 | Tangail | 212 | 19:00
19 | Baroirhat | 69 | 19:30 | Goalpara | 32 | 19:30 | Madartek | 80.69 | 23:00 | Rahim | 30 | 19:00 | Thakurgaon | 103 | 22:00
20 | Bashundhara | 184 | 19:00 | Gollamari | 72 | 00:00 | Madunaghat | 68 | 19:30 | Rajbari | 80 | 19:30 | Tongi | 144 | 18:30
21 | BashundharaCement | 12 | 13:00 | Gopalganj | 110 | 19:30 | Magura | 68 | 21:00 | Rajendrapur | 110 | 16:00 | Ullahpara | 26 | 19:30
22 | Beanibazar | 80 | 19:00 | Gulshan | 128 | 16:00 | Mahasthangarh | 80 | 00:00 | Rajshahi | 163 | 21:00 | Ullon | 56 | 19:00
23 | Benapole | 68 | 19:30 | Halishahar | 84 | 15:00 | Manikganj | 138 | 19:00 | Rajshahi-230 | 61 | 00:00 | Uttara | 96 | 16:00
24 | Bhaluka | 110 | 08:00 | HaripurSBU | 161 | 00:00 | Maniknagar | 76 | 12:00 | Ramganj | 116 | 21:00 | UttaraNew | 42 | 17:00
25 | Bhandaria | 55 | 22:00 | Hasnabad | 97 | 00:00 | Matarbari | 51 | 02:00 | Rampur | 42 | 00:00 | Zigatola | 86 | 15:00
26 | Bhangura | 47 | 19:30 | Hathazari | 61 | 00:00 | Matuail | 80 | 12:00 | Rangamati | 18 | 19:30
27 | Bheramara(GK) | 66 | 00:00 | Ishurdi | 83 | 19:00 | Millgate | 126 | 15:00 | Rangpur | 148 | 19:00
28 | Bhulta | 222 | 06:00 | Jaldhaka | 87 | 22:00 | Mirpur | 148 | 19:00 | Ruppur | 6.6 | 11:00
29 | Bog-Sherpur | 62 | 19:30 | Jamalpur | 138 | 19:30 | Mirsorai | 6 | 00:00 | SSM | 12 | 01:00
30 | Bogura | 177 | 22:00 | Jashore | 148 | 19:30 | Mirzapur | 40 | 18:30 | Saidpur | 117 | 19:00
31 | Borhanuddin | 81 | 00:00 | Jhenaidah | 139 | 19:30 | Mithapukur | 64 | 19:00 | Satkhira | 136 | 23:00
32 | Brahmanbaria | 170 | 22:00 | Joydebpur | 197 | 21:00 | Modern | 0 | 00:00 | Satmasjid | 111 | 19:00
33 | Cantonment | 146 | 12:00 | Joypurhat | 69 | 00:00 | Mogbazar | 122.5 | 14:00 | Savar | 213 | 16:00
34 | Chandpur | 72 | 21:00 | Juldah | 23 | 13:00 | Mongla | 39 | 17:00 | SevenRings | 17.3 | 00:00
35 | Chandraghona | 39 | 19:00 | KSRM | 33 | 15:00 | Motijheel | 48 | 11:00 | ShahCement | 27 | 18:00
36 | Chapai | 69 | 00:00 | Kabirpur | 276 | 19:00 | Munshiganj | 110 | 00:00 | Shahjadpur | 93 | 19:30
37 | Charsaidpur | 47 | 01:00 | Kachua | 78 | 19:00 | Mymensingh | 224 | 17:00 | Shahjibazar | 132 | 00:00
38 | Chauddagram | 70 | 22:00 | Kallyanpur | 117 | 19:00 | Naogaon | 140 | 21:00 | Shahmirpur | 53 | 17:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 397 | 07:00 | 384 | 16:00 | Kaliakoir | 380 | 04:00 | 364 | 12:00
| Ashuganj | 411 | 6:00 | 388 | 14:00 | Madunaghat_I | 409 | 7:00 | 390 | 14:00
| Bhulta | 405 | 05:00 | 391 | 10:00 | Meghnaghat | 395 | 05:00 | 380 | 16:00
| Bibiana | 401 | 20:00 | 390 | 12:00 | Payra | 411 | 07:00 | 404 | 19:00
| BIPTC | 405 | 02:00 | 389 | 15:00 | Rahanpur | 401 | 05:00 | 381 | 12:00
| Bogura | 395 | 08:00 | 379 | 12:00 | Rampal | 406 | 08:00 | 390 | 21:00
| Gopalganj | 403 | 07:00 | 389 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 229 | 03:00 | 220 | 12:00 | Hasnabad | 229 | 04:00 | 222 | 11:00
| AKSML | 228 | 21:00 | 216 | 10:00 | Hathazari | 226 | 20:00 | 219 | 09:00
| Aminbazar | 230 | 00:00 | 220 | 10:00 | Ishurdi | 236 | 18:00 | 227 | 13:00
| Ashuganj | 235 | 18:00 | 229 | 10:00 | Jhenaidah | 229 | 08:00 | 217 | 19:00
| Ashuganj-400 | 234 | 07;00 | 219 | 14:00 | Kaliakoir | 229 | 02:00 | 219 | 12:00
| Baghabari | 230 | 05:00 | 222 | 13:00 | Keranigonj | 229 | 04:00 | 220 | 12:00
| Barapukuria | 215 | 16:00 | 205 | 19:00 | Khulna(S) | 232 | 08:00 | 216 | 23:00
| Barapukuria-230 | 215 | 16:00 | 205 | 19:00 | Madunaghat_I | 225 | 7:00 | 210 | 20:00
| Barishal | 237 | 06:00 | 226 | 23:00 | Maniknagar | 231 | 05:00 | 222 | 12:00
| Bheramara | 235 | 01:00 | 225 | 13:00 | Meghnaghat | 238 | 03:00 | 232 | 11:00
| Bhulta | 232 | 04:00 | 222 | 12:00 | Meghnaghat-400 | 234 | 02:00 | 227 | 10:00
| Bibiana | 231 | 06:00 | 224 | 10:00 | Mirsorai | 228 | 20:00 | 217 | 10:00
| BIPTC | 236 | 06:00 | 225 | 13:00 | Rajshahi | 234 | 17:00 | 222 | 13:00
| Bogura | 219 | 17:00 | 211 | 11:00 | Rampal | 232 | 08:00 | 218 | 23:00
| Bogura-400 | 217 | 08:00 | 210 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 08:00 | 232 | 21:00 | Rampura | 231 | 03:00 | 221 | 12:00
| BSRM | 228 | 20:00 | 216 | 10:00 | Shikalbaha | 226 | 18:30 | 216 | 11:00
| Cumilla(N) | 228 | 07:00 | 221 | 10:00 | Shyampur | 236 | 01:00 | 223 | 11:00
| Fenchuganj | 233 | 05:00 | 228 | 19:00 | Siddhirganj | 232 | 01:00 | 225 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 235 | 05:00 | 228 | 13:00
| Ghorashal-230 | 231 | 04:00 | 222 | 10:00 | Sreepur | 229 | 20:00 | 222 | 10:00
| GPH | 226 | 18:00 | 216 | 10:00 | Tongi | 227 | 04:00 | 215 | 12:00
| Haripur | 229 | 00:00 | 223 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 01:00 | 126 | 13:00 | Kushtia | 135 | 08:00 | 128 | 13:00
| Agargaon | 135 | 02:00 | 127 | 12:00 | Lalbag | 133 | 03:00 | 127 | 11:00
| Agrabad | 131 | 17:00 | 123 | 10:00 | Lalmonirhat | 126 | 16:00 | 116 | 22:00
| AKS | 128 | 00:00 | 122 | 10:00 | Madanganj | 134 | 03:00 | 128 | 09:00
| Aminbazar | 134 | 02:00 | 125 | 13:00 | Madaripur | 132 | 09:00 | 125 | 19:00
| Amnura | 138 | 19:30 | 122 | 12:00 | Madartek | 134 | 04:00 | 126 | 12:00
| Ashuganj | 140 | 05:00 | 136 | 10:00 | Madunaghat | 132 | 18:00 | 124 | 10:00
| Bagerhat | 131 | 18:30 | 118 | 23:00 | Magura | 136 | 18:00 | 125 | 19:00
| Bakulia | 132 | 18:00 | 123 | 10:00 | Mahasthangarh | 131 | 17:00 | 123 | 12:00
| Banani | 133 | 03:00 | 125 | 13:00 | Manikganj | 128 | 02:00 | 117 | 11:00
| Bangabhaban | 134 | 02:00 | 127 | 11:00 | Maniknagar | 134 | 01:00 | 127 | 12:00
| Barapukuria | 134 | 16:00 | 124 | 19:00 | Matarbari | 120 | 17:00 | 111 | 11:00
| Barguna | 132 | 18:00 | 123 | 00:00 | Matuail | 134 | 03:00 | 128.5 | 12:00
| Barishal | 135 | 06:00 | 118 | 00:00 | Millgate | 133 | 02:00 | 124 | 10:00
| Barishal-230 | 135 | 07:00 | 126 | 23:00 | Mirpur | 132 | 01:00 | 125 | 12:00
| Baroaulia | 131 | 17:00 | 124 | 10:00 | Mirzapur | 128 | 05:00 | 119 | 12:00
| Baroirhat | 129 | 18:00 | 120 | 10:00 | Mithapukur | 129 | 15:00 | 119 | 19:00
| Bashundhara | 134 | 02:00 | 123 | 12:00 | MI_Cement | 135 | 01:00 | 129 | 10:00
| BashundharaCement | 134 | 04:00 | 128 | 09:00 | Modern | 132 | 18:00 | 124 | 10:00
| Beanibazar | 126 | 06:00 | 117 | 19:00 | Mogbazar | 135 | 01:00 | 127 | 11:00
| Benapole | 133 | 18:00 | 120 | 23:00 | Mongla | 129 | 08:00 | 119 | 21:00
| Bhaluka | 124 | 07:00 | 119 | 10:00 | Motijheel | 134 | 02:00 | 127 | 11:00
| Bhandaria | 128 | 18:00 | 116 | 00:00 | Munshiganj | 136 | 18:00 | 129 | 09:00
| Bhangura | 133 | 04:00 | 129 | 12:00 | Mymensingh | 132 | 00:00 | 113 | 12:00
| Bheramara | 135 | 06:00 | 131 | 13:00 | Naogaon | 129 | 17:00 | 119 | 11:00
| Bheramara(GK) | 135 | 04:00 | 131 | 22:00 | Narail | 137 | 18:30 | 125 | 23:00
| Bhulta | 126 | 04:00 | 121 | 09:00 | Narinda | 134 | 01:00 | 127 | 12:00
| Bog-Sherpur | 132 | 17:00 | 125 | 11:00 | Narshingdi | 125 | 01:00 | 120 | 09:00
| Bogura | 134 | 17:00 | 115 | 13:00 | Natore | 130 | 18:00 | 123 | 22:00
| Bogura-230 | 133 | 17:00 | 126 | 11:00 | Nawabganj | 133 | 04:00 | 126 | 12:00
| Brahmanbaria | 129 | 07:00 | 124 | 00:00 | Netrakona | 130 | 00:00 | 117 | 13:00
| Cantonment | 135 | 02:00 | 127 | 12:00 | New | 133 | 03:00 | 124 | 12:00
| Chandpur | 127 | 18:00 | 115 | 23:00 | Niamatpur | 134 | 04:00 | 126 | 10:00
| Chandraghona | 131 | 18:00 | 124 | 10:00 | Noapara | 134 | 18:00 | 123 | 21:00
| Chapai | 132 | 08:00 | 124 | 21:00 | Pabna | 133 | 06:00 | 128 | 13:00
| Charsaidpur | 135 | 18:00 | 129 | 09:00 | Palashbari | 127 | 16:00 | 116 | 19:00
| Chauddagram | 136 | 00:00 | 121 | 22:00 | Panchagarh | 134 | 15:00 | 116 | 19:00
| Chhatak | 128 | 06:00 | 118 | 22:00 | Patuakhali | 133 | 18:00 | 126 | 00:00
| Chowmuhani | 125 | 18:00 | 113 | 22:00 | Payra | 135 | 18:00 | 131 | 00:00
| Chuadanga | 130 | 08:00 | 116 | 19:00 | PHP | 128 | 18:00 | 120 | 10:00
| Coxsbazar | 123 | 17:00 | 113 | 12:00 | Postogola | 134 | 00:00 | 129 | 12:00
| Cumilla(N) | 132 | 18:00 | 126 | 23:00 | Purbachal | 134 | 02:00 | 123 | 12:00
| Cumilla(S) | 132 | 06:00 | 124 | 23:00 | Purbasadipur | 129 | 16:00 | 112 | 19:00
| Daudkandi | 130 | 18:00 | 124 | 14:00 | Rahanpur | 136 | 08:00 | 129 | 10:00
| Dhaka | 134 | 02:00 | 126 | 12:00 | Rahim | 139 | 02:00 | 130 | 09:00
| Dhamrai | 126 | 04:00 | 119 | 11:00 | Rajbari | 133 | 06:00 | 125 | 22:00
| Dhanmondi | 134.2 | 20:00 | 128 | 12:00 | Rajendrapur | 130 | 20:00 | 119 | 11:00
| Dohazari | 128 | 01:00 | 120 | 11:00 | Rajshahi | 133 | 18:00 | 125 | 12:00
| Faridpur | 133 | 06:00 | 125 | 23:00 | Rajshahi-230 | 134 | 17:00 | 119 | 21:00
| Fatullah | 134 | 02:00 | 129 | 10:00 | Ramganj | 125 | 18:00 | 111 | 23:00
| Fenchuganj | 133 | 08:00 | 127 | 14:00 | Rampur | 130 | 00:00 | 122 | 10:00
| Feni | 128 | 18:00 | 120 | 00:00 | Rampura | 134 | 04:00 | 126 | 12:00
| Ghatail | 127 | 00:00 | 116 | 15:00 | Rangamati | 131 | 18:30 | 121 | 10:00
| Ghorashal | 136 | 00:00 | 132 | 10:00 | Rangpur | 129 | 16:00 | 117 | 19:00
| Goalpara | 136 | 18:00 | 124 | 23:00 | Ruppur | 136 | 06:00 | 131 | 12:00
| Gollamari | 135 | 18:30 | 127 | 00:00 | Saidpur | 129 | 16:00 | 116 | 19:00
| Gopalganj | 132 | 08:00 | 125 | 20:00 | Satkhira | 131 | 18:00 | 119 | 00:00
| Gopalganj-400 | 134 | 07:00 | 128 | 19:00 | Satmasjid | 135 | 06:00 | 127 | 12:00
| Gulshan | 133 | 03:00 | 126 | 12:00 | Savar | 134 | 07:00 | 125 | 23:00
| Halishahar | 132 | 17:00 | 123 | 10:00 | SevenRings | 138 | 05:00 | 131 | 12:00
| Haripur | 134 | 00:00 | 130 | 09:00 | ShahCement | 135 | 18:00 | 129 | 09:00
| HaripurSBU | 134 | 00:00 | 130 | 09:00 | Shahjadpur | 138 | 05:00 | 132 | 13:00
| Hasnabad | 134 | 00:00 | 129 | 11:00 | Shahjibazar | 127 | 08:00 | 122 | 23:00
| Hathazari | 132 | 18:00 | 128 | 12:00 | Shahmirpur | 133 | 17:00 | 125 | 11:00
| Ishurdi | 137 | 18:00 | 132 | 13:00 | Shariatpur | 134 | 11:00 | 124 | 19:00
| Jaldhaka | 128 | 16:00 | 114 | 19:00 | Sherpur | 132 | 00:00 | 114 | 13:00
| Jamalpur | 134 | 00:00 | 118 | 13:00 | Shikalbaha | 122 | 17:00 | 115 | 08:00
| Jashore | 134 | 18:00 | 122 | 23:00 | Shikalbaha-230 | 133 | 18:00 | 125 | 11:00
| Jhenaidah | 136 | 05:00 | 127 | 19:00 | Shitalakhya | 135 | 01:00 | 129 | 10:00
| Jhenaidah-230 | 137 | 08:00 | 128 | 19:00 | Sholosohor | 131 | 18:00 | 122 | 10:00
| Joydebpur | 134 | 20:00 | 124 | 10:00 | Shyampur | 133 | 01:00 | 127 | 10:00
| Joypurhat | 130 | 14:00 | 116 | 11:00 | Shyampur-230 | 133 | 00:00 | 128 | 11:00
| Juldah | 133 | 18:00 | 126 | 10:00 | Siddhirganj | 134 | 00:00 | 130 | 10:00
| Kabirpur | 131 | 05:00 | 121 | 11:00 | Sirajganj | 130 | 17:00 | 125 | 21:00
| Kachua | 128 | 07:00 | 116 | 23:00 | Sonargaon | 135 | 02:00 | 128 | 10:00
| Kaliakoir | 132 | 19:30 | 122 | 12:00 | Sreemongol | 128 | 06:00 | 122 | 19:00
| Kallyanpur | 128 | 03:00 | 123 | 16:00 | Sreepur | 128 | 06:00 | 118 | 22:00
| Kalurghat | 130 | 00:00 | 124 | 10:00 | Srinagar | 133 | 05:00 | 127 | 12:00
| Kamrangirchar | 135 | 06:00 | 121 | 12:00 | SSM | 134 | 00:00 | 130 | 01:00
| Kaptai | 133 | 11:00 | 125 | 20:00 | Sunamganj | 127 | 06:00 | 116 | 23:00
| Kazla | 134 | 02:00 | 127 | 11:00 | Sylhet | 129 | 06:00 | 121 | 22:00
| Keranigonj | 134 | 04:00 | 128 | 11:00 | Sylhet-132 | 129 | 07:00 | 122 | 22:00
| Khagrachori | 130 | 18:00 | 122 | 10:00 | Tangail | 127 | 20:00 | 116 | 12:00
| Khulna | 134 | 18:00 | 124 | 20:00 | Thakurgaon | 133 | 16:00 | 115 | 07:00
| Khulna(S) | 135 | 18:00 | 127 | 19:00 | TK | 131 | 18:00 | 123 | 10:00
| Khulshi | 131 | 18:00 | 122 | 10:00 | Tongi | 135 | 04:00 | 127 | 12:00
| Kishoreganj | 124 | 19:30 | 119 | 12:00 | Ullahpara | 133 | 17:00 | 128 | 12:00
| Kodda | 133 | 20:00 | 120 | 10:00 | Ullon | 136 | 02:00 | 126 | 12:00
| KSRM | 132 | 17:00 | 124 | 10:00 | Uttara | 132 | 01:00 | 125 | 12:00
| Kulaura | 131 | 05:00 | 125 | 22:00 | UttaraNew | 132 | 01:00 | 125 | 12:00
| Kurigram | 127 | 16:00 | 114 | 19:00 | Zigatola | 134 | 05:00 | 128 | 11:00

## L-Curve
Date | 2024-05-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 308 | 8978 | 5679 | 14657 |  |  |  | QF-LDC-11
0:30 | 276 | 8861 | 5458 | 14319 | Date: | 2024-05-14
1:00 | 244 | 8744 | 5237 | 13981
1:30 | 266 | 8656.5 | 5118.5 | 13775
2:00 | 288 | 8569 | 5000 | 13569
2:30 | 336 | 8403.5 | 5040.5 | 13444 | [5 empty] | Gen. at Eve. Peak | 15435 | 15435 MW (19:30 )
3:00 | 384 | 8238 | 5081 | 13319 | [6 empty] | 19:30
3:30 | 372 | 8203 | 5028 | 13231 | [5 empty] | Gen. at Day Peak | 13701 | 13701 MW (12:00 )
4:00 | 360 | 8168 | 4975 | 13143 | [6 empty] | 12:00
4:30 | 440 | 8012 | 4942.5 | 12954.5 | [5 empty] | Highest Generation | 15435
5:00 | 520 | 7856 | 4910 | 12766 | [6 empty] | 19:30
5:30 | 514 | 7696.5 | 4821.5 | 12518
6:00 | 508 | 7537 | 4733 | 12270
6:30 | 475 | 7578.5 | 4704.5 | 12283
7:00 | 442 | 7620 | 4676 | 12296
7:30 | 533 | 7651.5 | 4694.5 | 12346
8:00 | 624 | 7683 | 4713 | 12396
8:30 | 711 | 7690 | 4809 | 12499
9:00 | 798 | 7697 | 4905 | 12602
9:30 | 815 | 7842.5 | 4982.5 | 12825
10:00 | 832 | 7988 | 5060 | 13048
10:30 | 865 | 8150.5 | 4975.5 | 13126
11:00 | 898 | 8313 | 4891 | 13204
11:30 | 871 | 8462 | 4990.5 | 13452.5
12:00 | 844 | 8611 | 5090 | 13701
12:30 | 686 | 8814 | 4994 | 13808
13:00 | 528 | 9017 | 4898 | 13915
13:30 | 518 | 9056 | 4972.5 | 14028.5
14:00 | 508 | 9095 | 5047 | 14142
14:30 | 541 | 9168 | 5037 | 14205
15:00 | 574 | 9241 | 5027 | 14268
15:30 | 557 | 9193.5 | 4985.5 | 14179
16:00 | 540 | 9146 | 4944 | 14090
16:30 | 595 | 9070 | 4962.5 | 14032.5
17:00 | 650 | 8994 | 4981 | 13975
17:30 | 667 | 8734 | 4888 | 13622
18:00 | 684 | 8474 | 4795 | 13269
18:30 | 495 | 8975.5 | 5142 | 14117.5
19:00 | 306 | 9477 | 5489 | 14966
19:30 | 148 | 9518 | 5917 | 15435
20:00 | 260 | 9646 | 5439 | 15085 |  |  |  | Executive Engineer
20:30 | 274 | 9708 | 5480.5 | 15188.5 |  |  |  | Network Operation Division
21:00 | 288 | 9770 | 5522 | 15292
21:30 | 283 | 9668 | 5569.5 | 15237.5
22:00 | 278 | 9566 | 5617 | 15183 |  |  |  |  | Page 6 of 7
22:30 | 286 | 9407.5 | 5629.5 | 15037
23:00 | 294 | 9249 | 5642 | 14891
23:30 | 301 | 9113.5 | 5660.5 | 14774
24:00 | 308 | 8978 | 5679 | 14657
15435 MW (19:30 )
13701 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-14 |  | Energy |  | 333733854
[15 empty] | 2024-05-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4437 | 627 | 2788 | 0 | 2349 | 3960 | 30 | 0 | 354 | 112 | 0 | 0 | 585.415
0:30 | 4421.5 | 627.5 | 2712 | 0 | 2143 | 3972 | 30 | 0 | 298 | 115 | 0 | 0 | 445.2075 |  |  | Date: | 43964
1:00 | 4406 | 628 | 2636 | 0 | 1937 | 3984 | 30 | 0 | 242 | 118 | 0 | 0 | 305
1:30 | 4428.5 | 625 | 2651.5 | 0 | 1749 | 3982 | 30 | 0 | 195 | 114 | 0 | 0 | 296 | [9 empty] | Total Energy | 333.7339 | 333.7339 | Total Energy Gen 333.734 MKWHr Energy Not Served 4.913 MKWHr Energy Requirement 338.646 MKWHr
2:00 | 4451 | 622 | 2667 | 0 | 1561 | 3980 | 30 | 0 | 148 | 110 | 0 | 0 | 287 | [9 empty] | Energy not Served | 4.9125 | 4.9125
2:30 | 4461 | 731.5 | 2604 | 0 | 1464.5 | 3906.5 | 30 | 0 | 139.5 | 107 | 0 | 0 | 277.5 | [9 empty] | Energy Requirement | 338.6464 | 338.6464
3:00 | 4471 | 841 | 2541 | 0 | 1368 | 3833 | 30 | 0 | 131 | 104 | 0 | 0 | 268
3:30 | 4470.5 | 874 | 2547 | 0 | 1295 | 3778.5 | 30 | 0 | 131 | 105 | 0 | 0 | 223.5 | [8 empty] | Shortage
4:00 | 4470 | 907 | 2553 | 0 | 1222 | 3724 | 30 | 0 | 131 | 106 | 0 | 0 | 179
4:30 | 4414 | 907.5 | 2528.5 | 0 | 1135 | 3717 | 30 | 0 | 119.5 | 103 | 0 | 0 | 153.5
5:00 | 4358 | 908 | 2504 | 0 | 1048 | 3710 | 30 | 0 | 108 | 100 | 0 | 0 | 128
5:30 | 4358 | 907 | 2488 | 0 | 912 | 3628 | 30 | 0 | 91 | 91 | 13 | 0 | 64
6:00 | 4358 | 906 | 2472 | 0 | 776 | 3546 | 30 | 0 | 74 | 82 | 26 | 0 | 0
6:30 | 4425.5 | 906.5 | 2476 | 0 | 778.5 | 3445.5 | 30 | 0 | 74 | 84 | 62.5 | 0.5 | 0 | [7 empty] | Coal
7:00 | 4493 | 907 | 2480 | 0 | 781 | 3345 | 30 | 0 | 74 | 86 | 99 | 1 | 0
7:30 | 4427 | 907 | 2466.5 | 0 | 888.5 | 3295 | 30 | 0 | 74 | 92 | 163.5 | 2.5 | 26 | [6 empty] | Oil
8:00 | 4361 | 907 | 2453 | 0 | 996 | 3245 | 30 | 0 | 74 | 98 | 228 | 4 | 52
8:30 | 4404.5 | 907.5 | 2460 | 0 | 1000.5 | 3262.5 | 30 | 0 | 70 | 100 | 258.5 | 5.5 | 120.5
9:00 | 4448 | 908 | 2467 | 0 | 1005 | 3280 | 30 | 0 | 66 | 102 | 289 | 7 | 189
9:30 | 4449 | 907.5 | 2500 | 0 | 1064 | 3330.5 | 30 | 0 | 76.5 | 108 | 354.5 | 5 | 157.53
10:00 | 4450 | 907 | 2533 | 0 | 1123 | 3381 | 30 | 0 | 87 | 114 | 420 | 3 | 126.06
10:30 | 4423 | 907 | 2531 | 0 | 1198 | 3451 | 30 | 0 | 111 | 115 | 357.5 | 2.5 | 132.745
11:00 | 4396 | 907 | 2529 | 0 | 1273 | 3521 | 30 | 0 | 135 | 116 | 295 | 2 | 139.43
11:30 | 4425 | 907 | 2527 | 0 | 1387 | 3512 | 30 | 0 | 167.5 | 121 | 375 | 1 | 140.8625
12:00 | 4454 | 907 | 2525 | 0 | 1501 | 3503 | 30 | 0 | 200 | 126 | 455 | 0 | 142.295
12:30 | 4441.5 | 907.5 | 2445.5 | 0 | 1696 | 3464.5 | 30 | 0 | 237 | 126 | 456 | 4 | 146.6475
13:00 | 4429 | 908 | 2366 | 0 | 1891 | 3426 | 30 | 0 | 274 | 126 | 457 | 8 | 151
13:30 | 4429 | 908 | 2366 | 0 | 1891 | 3426 | 30 | 0 | 274 | 126 | 457 | 8 | 151
14:00 | 4429 | 908 | 2366 | 0 | 1891 | 3426 | 30 | 0 | 274 | 126 | 457 | 8 | 151
14:30 | 4459 | 907 | 2308 | 0 | 2146 | 3443 | 30 | 0 | 321.5 | 123 | 347.5 | 6.5 | 162.5
15:00 | 4489 | 906 | 2250 | 0 | 2401 | 3460 | 30 | 0 | 369 | 120 | 238 | 5 | 174
15:30 | 4450.5 | 906 | 2126.5 | 0 | 2424 | 3483.5 | 30 | 0 | 398.5 | 121 | 233.5 | 5.5 | 187.5
16:00 | 4412 | 906 | 2003 | 0 | 2447 | 3507 | 30 | 0 | 428 | 122 | 229 | 6 | 201
16:30 | 4400 | 906 | 1981 | 0 | 2490 | 3477 | 30 | 0 | 461 | 118 | 165.5 | 4 | 184
17:00 | 4388 | 906 | 1959 | 0 | 2533 | 3447 | 30 | 0 | 494 | 114 | 102 | 2 | 167
17:30 | 4280.5 | 905.5 | 1916.5 | 0 | 2465.5 | 3355.5 | 30 | 0 | 498.5 | 107 | 61.5 | 1.5 | 146
18:00 | 4173 | 905 | 1874 | 0 | 2398 | 3264 | 30 | 0 | 503 | 100 | 21 | 1 | 125
18:30 | 4301.5 | 905.5 | 2097 | 0 | 2620.5 | 3453 | 30 | 0 | 600 | 99 | 10.5 | 0.5 | 145.5
19:00 | 4430 | 906 | 2320 | 0 | 2843 | 3642 | 30 | 0 | 697 | 98 | 0 | 0 | 166
19:30 | 4458 | 857 | 2380 | 0 | 3003 | 3863 | 30 | 0 | 736 | 108 | 0 | 0 | 233.5
20:00 | 4434 | 620 | 2481 | 0 | 2926 | 3808 | 30 | 0 | 676 | 110 | 0 | 0 | 301
20:30 | 4495 | 620 | 2581.5 | 0 | 2884 | 3795.5 | 30 | 0 | 674.5 | 108 | 0 | 0 | 297.5
21:00 | 4556 | 620 | 2682 | 0 | 2842 | 3783 | 30 | 0 | 673 | 106 | 0 | 0 | 294
21:30 | 4572 | 622.5 | 2775.5 | 0 | 2761 | 3781.5 | 30 | 0 | 596 | 99 | 0 | 0 | 312.6925
22:00 | 4588 | 625 | 2869 | 0 | 2680 | 3780 | 30 | 0 | 519 | 92 | 0 | 0 | 331.385
22:30 | 4605 | 626 | 2868.5 | 0 | 2566 | 3791 | 30 | 0 | 459.5 | 91 | 0 | 0 | 346.665
23:00 | 4622 | 627 | 2868 | 0 | 2452 | 3802 | 30 | 0 | 400 | 90 | 0 | 0 | 361.945
23:30 | 4529.5 | 627 | 2828 | 0 | 2400.5 | 3881 | 30 | 0 | 377 | 101 | 0 | 0 | 473.68 |  |  | Max Temp. in Dhaka |  | 35.3°C
24:00 | 4437 | 627 | 2788 | 0 | 2349 | 3960 | 30 | 0 | 354 | 112 | 0 | 0 | 585.415
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 333.734 MKWHr Energy Not Served 4.913 MKWHr Energy Requirement 338.646 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 719700
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 105 | 100 | 100 | 100 | 105 | 100 | 102 | 100 | 102 | 100 | 100 | 105 | 110 |  | 102 | 103 | 111 | 108 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | [9 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 17 |  | 25 | 25 | 25 | 25 | 25 | 17 | 8 | 191716
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 |  |  | 18 | 18 | 17 | 17 | 13 | 9 |  | 0 | [8 empty] | 116505
6 | Sikalbaha 225MW CCPP (Gas) | 213 | 211 | 213 | 212 | 212 | 213 | 213 | 212 | 212 | 212 | 212 | 213 | 213 | 213 | 213 | 212 | 212 | 211 |  | 211 | 213 | 212 | 212 | 212 | 213 | 212 | 5023759
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 34 | 34 | 34 | 34 | [6 empty] | 51 | 51 | 51 | 67 | 68 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1116449
12 | Hathazari 100 MW peaking PP | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 50 | 50 | 50 | 48 | 48 | 48 | 48 | 48 | 64 | 64 |  | 72 | 70 | 70 | 70 | 70 | 70 | 70 | 1382688
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | [9 empty] | 25 | 34 | 34 | 34 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 579599
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 23 | 23 | 23 | 23 | [10 empty] | 2 | 27 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 377088
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 330 | 331 | 333 | 331 | 332 | 333 | 330 | 325 | 325 | 320 | 317 | 316 | 312 | 315 | 311 | 319 | 315 | 250 |  | 314 | 310 | 312 | 314 | 318 | 318 | 323 | 7646667
18 | Kodda 300 MW PP Unit-2 (Summit) | [13 empty] | 65 | 255 | 260 | 275 | 195 |  | 195 | 245 | 260 | 195 | 195 | 195 | 220 | 2401199
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 492 | 490 | 455 | 450 | 450 | 450 | 450 | 448 | 448 | 451 | 483 | 486 | 486 | 486 | 486 | 485 | 485 | 486 |  | 486 | 486 | 486 | 486 | 486 | 489 | 492 | 11427271
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 34 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 31 | 35 | 34 | 34 | 34 | 31 | 35 | 35 |  | 36 | 36 | 36 | 36 | 37 | 37 | 34 | 824616
33 | Ashuganj 225 MW CCPP | 217 | 219 | 220 | 222 | 221 | 221 | 199 | 211 | 217 | 215 | 212 | 190 | 184 | 211 | 211 | 212 | 213 | 214 |  | 213 | 216 | 217 | 212 | 201 | 206 | 209 | 5106000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 340 | 240 | 240 | 240 | 260 | 280 | 280 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 280 | 260 | 6251000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 295 | 290 | 305 | 305 | 290 | 290 | 295 | 280 | 295 | 280 | 280 | 280 |  | 280 | 280 | 285 | 315 | 305 | 335 | 285 | 7674000
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 270 | 300 | 270 | 250 | 250 | 250 | 270 | 270 |  | 300 | 300 | 300 | 280 | 270 | 250 | 260 | 6410300
35 | Ashuganj 55 MW PP (Precision) | 51 | 52 | 49 | 52 | 51 | 52 | 50 | 51 | 51 | 50 | 49 | 48 | 47 | 45 | 45 | 42 | 42 | 42 |  | 42 | 42 | 43 | 44 | 47 | 50 | 50 | 1139520
36 | Chandpur 150 MW CCPP |  | 40 | 75 | 75 | 50 | 50 | 51 | 50 | 50 | 51 | 50 | 50 | 50 | 80 | 75 | 76 | 76 | 70 |  | 70 | 70 | 50 | 52 | 72 | 70 | 50 | 1287560
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 407 | 409 | 411 | 415 | 413 | 408 | 410 | 406 | 403 | 402 | 401 | 401 | 401 | 402 | 401 | 403 | 405 | 330 |  | 404 | 413 | 407 | 402 | 401 | 400 | 403 | 9756000
| Meghnaghat Unique power | 145 | 150 | 150 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 254 | 270 | 450 | 450 | 400 | 450 | 451 | 310 |  | 500 | 500 | 500 | 500 | 500 | 500 | 450 | 7937727
| Summit Meghanghat-2 589 MW(Gas) | 450 | 500 | 400 | 400 | 350 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 350 | 300 |  |  | 62 |  | 62 | 63 | 160 | 300 | 350 | 350 | 350 | 6886364
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10215000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 107 | 106 | 108 | 108 | 108 | 108 | 108 | 96 | 95 | 90 | 66 | 68 | 67 | 69 | 70 | 70 | 75 | 101 |  | 95 | 95 | 95 | 103 | 102 | 102 | 99 | 2160000
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 12 | 21 | 35 | 32 | 36 | 28 | 46 | 8 | 27 | 21 | 9 | 1 | [8 empty] | 292500
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 |  | 38 | 38 | 40 | 40 | 39 | 39 | 39 | 935000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 621120
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 58 | 57 | 58 | 56 | 54 | 54 | 54 | 54 | 54 | 60 |  | 55 | 59 | 59 | 58 | 56 | 55 | 56 | 1360032
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 132 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 132 | 130 | 130 | 130 | 130 | 130 | 128 | 128 | 130 | 130 |  | 130 | 126 | 126 | 126 | 125 | 125 | 127 | 3130840
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 189408
55 | Fenchugonj 51 MW PP (Barakatullah) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 53 | 52 | 51 | 52 | 52 | 52 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1247400
56 | Shahjahanulla 25 MW PP | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 522168
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 280 | 270 | 275 | 285 | 300 | 300 | 300 | 310 | 300 | 285 | 305 | 305 | 300 | 300 | 280 | 260 |  | 290 | 260 | 265 | 305 | 310 | 315 | 310 | 7202000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 310 | 310 | 340 | 340 | 345 | 365 | 350 | 350 | 350 | 350 | 360 | 350 | 350 | 310 |  | 340 | 340 | 340 | 355 | 360 | 365 | 340 | 8283800
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 17 | 17 | 24 | 55 | 35 | 55 | 55 | 55 | 55 | 35 |  | 17 | 17 | 35 |  | 55 | 55 | 55 | 55 | 35 | 0 | 0 | 912846
59 | Tangail Palli Power Gen 22 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 482640
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 12 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 312144
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 118 | 110 | 104 | 106 | 100 | 82 | 86 | 98 | 102 | 114 | 116 | 126 | 126 | 120 | 120 | 122 | 114 | 100 |  | 98 | 108 | 110 | 106 | 92 | 90 | 112 | 2560320
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 32 | 38 | 38 | 10 | 2 | 2 | 2 | 2 | 0 | 3 | 3 | 0 | 0 | 2 | 2 |  | 20 | 14 | 20 | 31 | 33 | 35 | 30 | 432480
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 764400
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 14 | 14 | 14 | 14 |  |  | 14 | 16 | 16 | 16 | 16 | 16 | 16 | 312220
69 | Summit Ashulia | 23 | 23 | 23 | 24 | 24 | 21 | 19 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 21 | 18 | 18 | 18 | 452000
70 | Summit Madhabdi | 20 | 20 | 19 | 15 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 20 | 20 | 20 | 392400
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 17 | 17 | 0 | 33 | 33 | 33 | 33 | 727400
72 | Rupganj 33 MW PP(Summit) | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 32 | 32 | 32 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 16 | 31 | 726100
73 | Ghorashal 108 MW PP (Regent) | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 76 | 73 |  | 73 | 76 | 76 | 76 | 76 | 76 | 75 | 1845227
| Feni Lanka Power | 98 | 98 | 98 | 98 | 73 | 17 | 17 | 17 | 17 | 17 | 23 | 97 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1855920
| Chowmuhani 113 MW | 54 | 37 | 37 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 47 | 56 | 57 | 56 | 63 | 84 |  | 101 | 104 | 104 | 95 | 94 | 95 | 78 | 1419600
| Manikgonj 162MW PP(MPGL) | 162 | 54 |  |  |  |  | 57 | 108 | 108 | 108 | 108 | 108 | 162 | 162 | 162 | 162 | 162 | 162 |  | 161 | 35 | 35 | 35 | 35 | 35 | 35 | 2253600
77 | Siddhirganj 100 PP(Dutch Bangla) | 90 | 88 | 88 | 74 | 50 |  |  |  | 14 | 28 | 46 | 65 | 75 | 80 | 85 | 85 | 85 | 80 |  | 34 | 40 | 58 | 48 | 40 | 40 | 50 | 1205990
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 192960
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 48 | 115 | 146 | 145 | 144 | 144 | 148 |  | 146 | 150 | 150 | 150 | 150 | 32 | 16 | 1748640
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 34 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 34 | 29 | 34 | 34 | 37 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 683237
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 70 | 70 | 70 | 70 | 70 | 17 | 17 | 606720
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 2 | 5 | 5 | 5 | 5 | 4 | 3 | 3 | 1 | [9 empty] | 36438
| Jodiac Power | 54 | 17 | [10 empty] | 6 | 51 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 745396
| Karnaphuli Power Ltd. | 17 | 17 | 17 | [8 empty] | 13 | 26 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 681630
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 51 | 15 |  |  |  | 34 | 72 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 68 | 68 | 68 | 80 | 80 | 80 | 80 | 1414545
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [13 empty] | 5 | 20 | 25 | 14 | 14 |  | 13 | 13 | 13 |  |  |  | 0 | 93973
86 | Meghnaghat CCPP ( Summit) | 315 | 317 | 318 | 275 | 319 | 318 | 315 | 313 | 309 | 302 | 305 | 303 | 303 | 304 | 299 | 303 | 280 | 300 |  | 306 | 275 | 294 | 302 | 303 | 300 | 299 | 7313833
87 | Meghnaghat 100 MW(IEL) | 99 | 99 | 99 | 75 | 50 |  |  |  | 1 | 32 | 48 | 72 | 91 | 90 | 91 | 90 | 90 | 83 |  | 43 | 91 | 74 | 63 | 50 | 49 | 70 | 1463040
| Meghnaghat 104 MW PP (OPCL) | 53 | 53 | 53 | 68 | 70 | 70 | 70 | 68 | 65 | 68 | 68 | 70 | 70 | 70 | 52 | 52 | 52 | 52 |  | 69 | 70 | 70 | 72 | 72 | 72 | 58 | 1497600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [10 empty] | 10 | 36 | 36 | 36 | 36 | 36 | 36 | 12 |  | 30 | 48 | 48 | 48 | 48 | 35 | 35 | 424800
92 | Fenchuganj 44 MW (Energyprima) | 39 | 39 | 39 | 39 | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 38 | 38 | 38 | 38 | 41 |  | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 947376
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1156827
94 | Gagnagar 102 MW PP (Digital Power) | 90 | 90 | 40 | 40 | 8 | 8 | 8 | 50 | 64 | 64 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1732896
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 4 | [8 empty] | 5 | 6 | 6 | 6 | 6 | 9 | 19 |  | 19 | 19 | 19 | 20 | 20 | 20 | 6 | 173760
96 | Chattogram 108 MW PP (ECPV) | 70 | 33 | [9 empty] | 5 | 35 | 40 | 48 | 61 | 75 | 75 |  | 85 | 95 | 95 | 85 | 95 | 91 | 87 | 993600
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 15 | 30 | 30 |  | 45 | 55 | 55 | 55 | 30 | 30 | 30 | 636293
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 | 0 | 0 | 1115720
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 |  | 112 | 112 | 80 | 80 | 112 | 112 | 112 | 2453891
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 12700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | [6 empty] | 13 | 17 | 17 | 17 | 17 | 43 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 17 | 0 |  | 0 | 654120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 78 | 78 | 78 | 78 | 78 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 57 | 57 | 57 | 57 | 57 |  | 105 | 105 | 107 | 107 | 107 | 107 | 108 | 1776000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 95 | 134 | 133 | 136 | 133 | 133 | 101 | 72 | 72 | 71 | 71 | 71 | 71 | 43 | 35 | 35 | 35 | 37 |  | 103 | 134 | 133 | 149 | 86 | 35 | 36 | 2040192
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 49 | 49 | 12 | 12 | 37 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 62 | 62 | 62 | 62 | 62 | 62 | 49 | 1145280
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432000
117 | Ashuganj 150 MW PP (Midland) | [10 empty] | 26 | 58 | 75 | 78 | 88 | 93 | 90 | 95 |  | 112 | 125 | 122 | 127 | 128 | 128 | 122 | 1348218
118 | Bibiyana-III 400 MW CCPP | 366 | 365 | 365 | 366 | 306 | 307 | 339 | 351 | 378 | 380 | 366 | 375 | 375 | 368 | 385 | 367 | 330 | 306 |  | 366 | 367 | 371 | 370 | 402 | 398 | 367 | 8751000
| Jamalpur 115 MW PP (United) | 70 | 69 | 69 | 69 | 69 | 59 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 58 |  | 97 | 98 | 98 | 99 | 99 | 99 | 99 | 1580400
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1252036
| Juldah unit-2 (Acorn) | 62 | 62 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 45 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 62 |  | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 1273920
| Anlima Energy Ltd. | 17 | 17 | 17 | [5 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 50 | 53 | 53 | 53 | 53 | 53 | 17 | 516873
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 |  | 15 | 35 |  |  | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 46 |  | 50 | 50 | 49 | 50 | 50 | 50 | 49 | 735840
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 8 | 16 | 13 | 28 | 32 | 35 | 32 | 28 | 23 | 14 | 7 | 1 | [8 empty] | 241530
| Chandpur 115(Doreen) | 75 | 80 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 67 | 38 | 36 | 37 | 53 | 54 | 53 |  | 58 | 54 | 53 | 39 | 36 | 19 | 18 | 1406400
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | 17 | 17 | [7 empty] | 5 | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 17 |  | 108 | 125 | 163 | 163 | 17 | 17 | 17 | 761090
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 7 | 3 | 2 | 0 | 8 | 5 | 5 | 6 | 2 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49920
| Sonagazi 75 MW Solar Plant | [5 empty] | 4 | 19 | 37 | 39 | 62 | 27 | 55 | 57 | 59 | 45 | 30 | 12 | 2 | [8 empty] | 474218
| Matarbari 2*600 MW (CPGCL) | 575 | 577 | 575 | 575 | 577 | 574 | 537 | 538 | 501 | 594 | 735 | 675 | 562 | 502 | 590 | 736 | 594 | 505 |  | 508 | 504 | 506 | 506 | 509 | 509 | 507 | 13760000
120 | Eastern Zone Total | 8744 | 8569 | 8238 | 8168 | 7856 | 7537 | 7620 | 7683 | 7697 | 7988 | 8313 | 8611 | 9017 | 9095 | 9241 | 9146 | 8994 | 8474 |  | 9477 | 9518 | 9646 | 9770 | 9566 | 9249 | 8978 | 208179922
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 16 |  |  |  | 5 | 16 | 36480
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 28 | 30 | [5 empty] | 30720
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | [9 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 331200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 5 | 25 | 51 | 70 | 90 | 97 | 99 | 96 | 86 | 69 | 48 | 23 | 4 | [8 empty] | 773280
131 | Rampal 1320 MW (BIFPCL) | 510 | 508 | 483 | 462 | 463 | 416 | 408 | 411 | 407 | 407 | 407 | 409 | 410 | 410 | 409 | 357 | 360 | 365 |  | 421 | 459 | 456 | 462 | 460 | 457 | 490 | 10378180
132 | United Payra Power Ltd. | [12 empty] | 17 | 17 | 14 | 14 | 17 | 17 |  | 54 | 50 | 50 | 97 | 94 | 77 | 36 | 475200
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2531045
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [20 empty] | 16 |  |  |  |  | 0 | 10560
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 260 | 260 | 260 | 260 | 260 | 226 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 200 | 250 | 200 |  | 304 | 270 | 297 | 270 | 270 | 276 | 305 | 5432700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 126 | 126 | 122 | 130 |  | 124 | 124 | 122 | 130 | 128 | 130 | 130 | 3070000
140 | Bhola 33 MW PP (Venture) | 9 | 9 | 9 | 10 | 9 | 8 | 7 | 6 | 6 | 4 | 6 | 6 | 7 | 7 | 7 | 8 | 7 | 7 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 197016
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [13 empty] | 8 | 24 | 16 | 16 | 24 |  | 24 | 24 |  |  |  |  | 0 | 101250
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 20 | 38 | [5 empty] | 31360
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 628 | 622 | 841 | 907 | 908 | 906 | 907 | 907 | 908 | 907 | 907 | 907 | 908 | 907 | 906 | 906 | 906 | 905 |  | 906 | 857 | 620 | 620 | 625 | 627 | 627 | 19979636
147 | Bheramara 410 MW CCPP | 355 | 360 | 345 | 345 | 345 | 345 | 355 | 345 | 370 | 365 | 340 | 360 | 365 | 340 | 390 | 345 | 340 | 345 |  | 345 | 345 | 345 | 375 | 380 | 390 | 340 | 8758944
148 | Payra 1320 MW | 1100 | 1100 | 1040 | 1000 | 980 | 900 | 800 | 700 | 700 | 700 | 700 | 700 | 740 | 800 | 740 | 660 | 690 | 640 |  | 860 | 1080 | 1000 | 990 | 990 | 1000 | 1100 | 22848900
149
150 | Barapukuria TPP Unit-1 | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 69 | 70 | 70 | 70 | 69 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 71 | 1595781
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 200 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5578000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 13 | 40 | 40 | 40 |  | 41 | 41 | [5 empty] | 195547
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 2 | 5 | 4 | 3 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 35220
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 198 | 189 | 184 | 183 | 183 | 183 | 190 | 184 | 185 | 186 | 193 | 186 | 197 | 196 | 192 | 193 | 185 | 177 |  | 164 | 184 | 184 | 197 | 202 | 204 | 195 | 4751682
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 198 | 190 | 186 | 185 | 185 | 185 | 191 | 189 | 195 | 199 | 195 | 189 | 195 | 195 | 192 | 193 | 185 | 185 |  | 191 | 185 | 185 | 198 | 203 | 205 | 196 | 4895473
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 417 | 400 | 396 | 363 | 314 | 320 | 347 | 330 | 348 | 414 | 414 | 414 | [5 empty] | 96 |  | 192 | 315 | 320 | 320 | 414 | 414 | 396 | 6654109
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 10 | [12 empty] | 5 | 5 | 12 | 11 | 11 |  | 11 | 11 | 17 | 16 | 11 | 11 | 11 | 115359
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 186120
165 | Amnura 50 MW PP(Sinha) | [16 empty] | 10 | 21 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 217340
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 25 | 16 | 25 | 25 | 34 | 34 |  | 34 | 34 | 8 | 8 | 8 | 8 | 34 | 221432
167 | Katakhali 50 MW Peaking PP | 5 | [12 empty] | 14 | 30 | 30 | 30 | 33 |  | 35 | 35 | 40 | 38 | 35 | 35 | 35 | 331580
168 | Santahar 50 MW Peaking PP | 28 | [15 empty] | 30 | 32 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 249430
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 |  |  |  |  | 0 | 9917
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 7 | 42 | 42 | 42 | 42 | 42 |  | 90 | 90 | 90 | 90 | 90 | 89 | 59 | 702784
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [12 empty] | 10 | 84 | 113 | 113 | 113 | 35 |  | 51 | 113 | 113 | 113 | 113 | 113 | 113 | 1133088
172 | Confidence Power Bogura Unit-1 113 MW | [12 empty] | 70 | 108 | 113 | 113 | 113 | 35 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 1148736
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 74 | 34 | 34 |  |  |  | 2 | 34 | 42 | 35 | 35 | 34 | 65 | 66 | 80 | 82 | 90 | 86 |  | 92 | 90 | 92 | 92 | 92 | 92 | 92 | 1345728
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 6 | 7 | 7 | 7 | 7 | 6 | 3 | 2 | 1 | [8 empty] | 54765
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 35 | 35 | 35 | 35 |  | 17 | 74 | 74 | 74 | 74 | 74 | 94 | 108 | 114 | 114 | 114 | 115 |  | 115 | 115 | 114 | 114 | 114 | 115 | 115 | 1986048
| Intraco Solar 30 MW | [5 empty] | 2 | 7 | 14 | 22 | 28 | 21 | 25 | 32 | 30 | 23 | 15 | 7 | 1 | [8 empty] | 220361
| Adani Power Jharkhanda Ltd | 748 | 745 | 720 | 677 | 680 | 680 | 680 | 678 | 754 | 759 | 756 | 763 | 759 | 760 | 765 | 769 | 769 | 768 |  | 763 | 764 | 763 | 769 | 765 | 771 | 765 | 17797651
178 | Teesta Solar Limited | [5 empty] | 9 | 20 | 70 | 98 | 166 | 45 | 178 | 160 | 105 | 24 | 83 | 40 | 11 | [8 empty] | 1141310