## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-03-01 |  | 2024-02-01 |  | 2023-03-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13898 | 2024-03-31 | 11433 | 2024-02-20 | 12921 | 2023-03-13 | 15648 | 2023-04-19
|  |  | 21:00 |  | 19:00 |  | 19:00 |  | 21:00
2 | Minimum Generation (MW) | 7249 | 2024-03-22 | 6491 | 2024-02-26 | 6507 | 2023-03-20 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13898 | 2024-03-31 | 11433 | 2024-02-20 | 12921 | 2023-03-13 | 15648 | 2023-04-19
|  |  | 21:00 |  | 19:00 |  | 19:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11821 | 2024-03-27 | 11433 | 2024-02-20 | 11515 | 2023-03-14 | 13415 | 2023-04-19
|  |  | 12:00 |  | 19:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14050 | 2024-03-30 | 11600 | 2024-02-29 | 13046 | 2023-03-31 | 16096 | 2023-04-19
|  |  | 21:00 |  | 19:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11984.9032 |  | 10621.7586 |  | 11615.6452 |  | - | -
7 | Average Generation (MW) at Day Peak | 10819.7097 |  | 9975.931 |  | 10322.4194 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 964 | 2024-03-28 | 927 | 2024-02-29 | 920 | 2023-03-02 | 964 | 2024-03-28
|  |  | 13:30 |  | 22:30 |  | 23:00 |  | 13:30
9 | Maximum Power Import from Tripura, India (MW) | 165 | 2024-03-31 | 134 | 2024-02-14 | 170 | 2023-03-13 | 194 | 12/06/19
|  |  | 21:00 |  | 14:00 |  | 14:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 666 | 2024-03-30 | 166 | 2024-02-19 | 236 | 2023-03-05 | 4395 | 04/10/2022
|  |  | 21:00 |  | 19:00 |  | 19:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13353 | 2024-03-30 | 11426 | 2024-02-19 | 12052 | 44990 | 13200 | 04/10/2022
|  | - | 21:00 | - | 19:00 | - | 0.79167 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-03-26 | 0 | 2024-02-21 | 40 | 44988 | - | -
|  |  | 21:00 |  | 19:00 |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12107 | 2024-03-26 | 9940 | 2024-02-21 | 10693 | 2023-03-03 | - | -
|  |  | 21:00 |  | 19:00 |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 513 | 2024-03-14 | 448 | 2024-02-06 | 356 | 44991 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 11763 | 2024-03-14 | 9431 | 2024-02-06 | 10869 | 44991 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-03-26 | 0 | 2024-02-21 | 0 | 44993 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 9801 | 2024-03-26 | 9810 | 2024-02-21 | 9421 | 44993 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 23 |  | 19 |  | 18 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 23 |  | 20 |  | 12 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 2159.2989 |  | 1547.5883 |  | 1561.2501 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 33.0767 |  | 26.3507 |  | 46.9674 |  | - | -
22 | Net Generation of BPDB (MKWH) | 2126.2221 |  | 1521.2375 |  | 1514.2827 |  | - | -
23 | Net Generation of IPP (MKWH) | 4044.7402 |  | 3361.366 |  | 4695.4667 |  | - | -
24 | Net Generation of REB (MKWH) | 99.727 |  | 89.9855 |  | 121.5861 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 104.0822 |  | 118.5854 |  | 299.4051 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6374.7716 |  | 5091.1744 |  | 6630.7407 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 3706.1266 |  | 3054.7436 |  | 4237.6738 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 23.3688 |  | 16.4698 |  | 214.1302 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 599.397 |  | 508.5277 |  | 1443.6516 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 23.5131 |  | 28.5971 |  | 17.7881 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 57.0855 |  | 38.0423 |  | 146.7623 |  | 57.09 | March-24
31 | Energy Generation by Coal (MKWH) | 932.5694 |  | 846.7537 |  | 617.702 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 724.0301 |  | 586.2757 |  | 535.4411 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 73.5217 |  | 70.7431 |  | 84.1419 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/3 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13898 | 2024-03-31 | 21:00
Generation Period
| Dhaka | MW | 4880.51
| Chattogram | MW | 1335
| Cumilla | MW | 1193
| Mymensingh | MW | 1058
| Sylhet | MW | 468
a) | Total supply in East zone | MW | 8934.51
| Khulna | MW | 1710.2
| Barisal | MW | 453
| Rajshahi | MW | 1503.8
| Rangpur | MW | 807
b) | Total supply in West zone | MW | 4474
c) | Total supply in both zone ( a+b) | MW | 13408.51
Ref: | 27.21.0000.603.16.087.20.793 | Date: 23/04/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 600 | 2024-03-08 | 8:00
| b) Ishurdi end | MW
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS
| b) Ishurdi end | MW | 64 | 2024-03-05 | 7:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.11377
| b) Ishurdi end | MKWH | 116.3064
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 112.8172
| b) Ishurdi end | MKWH | 0.11046
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 170 | 2024-03-05 | 7:00
| b)Serajganj end | MW | 640 | 2024-03-13 | 14:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 340 | 2024-03-13 | 12:00
| b)Sirajganj end | MW | -106 | 2024-03-05 | 7:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.0725
| b)Sirajganj end | MKWH | 286.8
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 278.4277
| b)Sirajganj end | MKWH | 0.072
30 | Transmission loss of EWI /NO-2 | % | 2.938'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2130 | 2024-03-03 | 21:00
|  | MW | 1462
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2108 | 2024-03-03 | 19:30
|  | MW | 1446
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 30186 | 2024-03-03 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 30162 | 2024-03-03
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 602318
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 602270.002
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.0079689
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2024-03-31 07:07 | 2024-03-31 07:56 | 0:49 | T | Over Voltage | 66 | 53.9 | Power interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) HT | 2024-03-31 07:07 | 2024-03-31 08:10 | 1:03 | T | Over Voltage | 66 | 69.3 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2024-03-18 13:37 | 2024-03-18 14:10 | 0:33 | E/O | General Trip,Winding Temp,R,Y,B Phase Relay Panel General Trip ,Lockout | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-03-21 09:11 | 2024-03-21 09:29 | 0:18 | T | 33kv gaffargaon feeder trip for C.T. burst. | 50 | 15 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-03-21 09:11 | 2024-03-21 09:29 | 0:18 | T | 33kv gaffargaon feeder trip for C.T. burst. | 50 | 15 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-03-01 10:09 | 2024-03-01 12:13 | 2:04 | E/O | Shutdown taken by DPBS-1 due to Red Hot maintenance of T-1&T-2 33 kV bus section DS. | 100 | 206.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-03-24 23:02 | 2024-03-25 00:15 | 1:13 | E/O | Shutdown taken by DPBS-1 due to hot maintenance. | 60 | 73 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-03-01 10:09 | 2024-03-01 11:39 | 1:30 | E/O | Shutdown taken by DPBS-1 due to Red Hot maintenance of T-1&T-2 33 kV bus section DS. | 100 | 150 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-03-22 10:51 | 2024-03-22 12:14 | 1:23 | E/O | Shutdown taken by DPBS-1 due to red hot maintenance work of 33 kV Kabirpur feeder. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-03-31 07:26 | 2024-03-31 09:21 | 1:55 | T | Trip | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | 400kV Bus 1 | 2024-03-31 10:49 | 2024-03-31 14:52 | 4:03 | E/O | due to bibiyana ckt-01 ds works | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-03-28 07:15 | 2024-03-28 07:25 | 0:10 | T | 33 kv Mithamoin and Pakundia feeder Relay O/C ,E/F Because our T-02 Transformer 33kv incoming CB Trip ,O/C | 30 | 5 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-03-07 10:42 | 2024-03-07 10:51 | 0:09 | T | PBS 33 kV Korni feeder fault (Earth fall over current). | 5 | 0.75 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-03-10 16:08 | 2024-03-10 16:23 | 0:15 | T | PBS 3 feeder (Gorai, Square & Vatgram) trip at a time. | 40 | 10 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-03-31 06:32 | 2024-03-31 10:59 | 4:27 | T | 33kv outgoing Feeder fault E/F,Â O/C | 15 | 66.75 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) HT | 2024-03-07 10:11 | 2024-03-07 14:30 | 4:19 | T | Non directional over current. | 32 | 138.1333 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-03-07 09:40 | 2024-03-07 09:54 | 0:14 | T | Non directional over current. | 40 | 9.3333 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-03-10 16:08 | 2024-03-10 16:24 | 0:16 | T | PBS 3 feeder trip at a time. | 40 | 10.6667 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-03-31 06:32 | 2024-03-31 10:00 | 3:28 | T | 33kv outgoing Feeder fault E/F,Â O/C | 15 | 52 | Power interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2024-03-31 07:03 | 2024-03-31 08:30 | 1:27 | T | IDMT-2 Trip | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-03-31 07:03 | 2024-03-31 08:30 | 1:27 | T | IDMT-2 Trip | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-03-17 07:45 | 2024-03-17 07:49 | 0:04 | T | Diff. Pro.-1 Trip | 25 | 1.6667 | Power interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-03-18 19:27 | 2024-03-18 20:10 | 0:43 | E/O | Bird nest remove of 33 Kv granty structure | 52 | 37.2667 | Power interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-03-31 08:20 | 2024-03-31 08:30 | 0:10 | E/O | aspar direction of NLDC | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-03-12 12:40 | 2024-03-12 12:49 | 0:09 | T | Over Current | 60 | 9 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-03-28 11:27 | 2024-03-28 12:32 | 1:05 | T | Over Current | 60 | 65 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-03-31 06:54 | 2024-03-31 07:04 | 0:10 | T | Under Frequency | 31 | 5.1667 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-03-01 16:10 | 2024-03-01 17:50 | 1:40 | E/O | 33 kv bus red hot | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2024-03-01 16:08 | 2024-03-02 16:48 | 24:40 | E/O | 33 kv bus red hot | 0 | 0 | No interruption
|  |  | Total : | 60:02 |  | Unserved Energy: |  | 993.6
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | Auto TR-3 HT | 2024-03-10 12:23 | 2024-03-10 12:50 | 0:27 | E/O | OLTC oil filling. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-03-22 09:35 | 2024-03-22 10:02 | 0:27 | T | T-2 33 kv incoming CB tripped due to 33 kv ckts Zinzira ckt-1 & ckt-2 triped by line fault | 16 | 7.2 | Power interruption
Hasnabad 132/33kV Grid Substation | 33kv Main Bus | 2024-03-31 11:55 | 2024-03-31 12:11 | 0:16 | T | Nobabganj-2 fault | 40 | 10.6667 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-03-15 02:07 | 2024-03-15 02:42 | 0:35 | T | None | 0 | 0 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-03-16 05:02 | 2024-03-16 05:53 | 0:51 | T | 33kv Kalatiya and Konakhola feeder underground cable blust and firing. | 23 | 19.55 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-03-19 20:40 | 2024-03-19 21:15 | 0:35 | T | Konakhola feeder Cable Fault | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-03-24 07:08 | 2024-03-24 07:39 | 0:31 | T | 33kV kalatiya feeder fault. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2024-03-25 17:37 | 2024-03-25 23:35 | 5:58 | E/O | Maintenence work at 33kv Bus section -02 by PBS for kolatiya feeder(H-13) cable fault. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2024-03-15 02:07 | 2024-03-15 02:43 | 0:36 | T | Trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2024-03-16 05:02 | 2024-03-16 05:25 | 0:23 | T | 33kv Kalatiya and Konakhola feeder underground cable blust and firing. | 23 | 8.8167 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2024-03-16 05:51 | 2024-03-16 14:49 | 8:58 | E/O | 33 kv kolatiya (H-13) Feeder Bus D/S insulator over flashing. PBS Maintenance work purpose. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2024-03-19 20:40 | 2024-03-19 20:56 | 0:16 | T | Konakhula feeder Cable Fault | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2024-03-24 07:08 | 2024-03-24 07:39 | 0:31 | T | 33kV kalatiya feeder fault. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Main Bus | 2024-03-23 12:35 | 2024-03-23 16:55 | 4:20 | E/O | red hot maintenance of Munshiganj-2 main bus ds | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-03-31 06:57 | 2024-03-31 07:51 | 0:54 | T | Due to thundering Strom. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-03-14 14:31 | 2024-03-14 14:51 | 0:20 | T | For 33 kv Agla and Sholla feeder | 0 | 0 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-03-14 18:11 | 2024-03-14 18:22 | 0:11 | T | For sholla feeder | 0 | 0 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-03-19 18:26 | 2024-03-19 18:35 | 0:09 | T | 33kV Feeder trip (Feeeder-05 Nikra) | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2024-03-14 12:42 | 2024-03-14 19:45 | 7:03 | T | TA-1 33Kv Cable Fault | 51 | 359.55 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 LT | 2024-03-27 08:59 | 2024-03-27 09:19 | 0:20 | T | DPDC 33 KV EPZ FEEDER 1,2 TRIPED | 40 | 13.3333 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 HT | 2024-03-14 12:42 | 2024-03-14 13:04 | 0:22 | T | TA-1 33Kv Cable Fault | 51 | 18.7 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 LT | 2024-03-27 08:59 | 2024-03-27 09:19 | 0:20 | T | DPDC EPZ FEEDER 1,2 TRIPED | 40 | 13.3333 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-03-21 19:51 | 2024-03-21 20:04 | 0:13 | E/O | Due to Haripur-2 circuit trip(NLDC instruction). | 55 | 11.9167 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-03-31 07:07 | 2024-03-31 08:21 | 1:14 | T | PBS 33kv kabilganj feeder fault. | 45 | 55.5 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-03-11 05:25 | 2024-03-11 05:55 | 0:30 | T | PBS 33kv Salam steel feeder B-phase underground cable fault. | 40 | 20 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-03-31 07:07 | 2024-03-31 08:21 | 1:14 | T | PBS 33kv Salam steel feeder fault. Y-phase loop out from 33kv Busbar. | 35 | 43.1667 | Power interruption
Ullon 132/33kV Grid Sub-Station | GT-3 HT | 2024-03-05 09:46 | 2024-03-05 13:49 | 4:03 | E/O | Oil Leakage | 0 | 0 | No interruption
|  |  | Total : | 41:37 |  | Unserved Energy: |  | 581.7333
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | Bus-A | 2024-03-24 08:10 | 2024-03-24 09:09 | 0:59 | T | Tripped showing Trip relay K31, K32 relays. | 20 | 19.6667 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T HT | 2024-03-24 08:10 | 2024-03-24 09:12 | 1:02 | T | Tripped showing Trip relay K31, K32 relays. | 20 | 20.6667 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2024-03-02 08:28 | 2024-03-02 11:27 | 2:59 | E/O | Red hot | 11 | 32.8167 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2024-03-30 08:17 | 2024-03-30 21:22 | 13:05 | E/O | U-clamp change work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | TR-2, 416T HT | 2024-03-24 08:10 | 2024-03-24 09:13 | 1:03 | T | Trip | 20 | 21 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2024-03-15 20:40 | 2024-03-15 21:05 | 0:25 | T | Over current | 85 | 35.4167 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2024-03-02 10:45 | 2024-03-02 11:13 | 0:28 | E/O | Due To Emergency Red Hot Maintenance Work By BPDB. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2024-03-16 10:45 | 2024-03-16 15:29 | 4:44 | E/O | Due to BPDB incomer R phase cable red hot work, no L/S occurred, New moring load shifted to Agrabad S/S | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-03-21 02:00 | 2024-03-21 02:59 | 0:59 | T | Due to BPDB 33 kv outgoing feeder incommer-3 Y-phase loop out & breaker blust. | 11 | 10.8167 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-03-21 02:00 | 2024-03-21 19:24 | 17:24 | T | 33 KV incoming feeder T-1 &T-2 trip due to PDB 33 KV outgoing feeder incoming-3, Y-phase loop out & breaker blust. | 22 | 382.8 | Power interruption
Khagrachori 132/33kV Grid Sub-Station | TR-2 LT | 2024-03-03 14:22 | 2024-03-03 15:22 | 1:00 | E/O | Red hot at secondary CT of TR-01. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2024-03-25 19:31 | 2024-03-25 19:40 | 0:09 | E/O | Suggested by NLDC | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-03-31 07:34 | 2024-03-31 10:26 | 2:52 | T | Trip | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 230kV BUS-01 | 2024-03-03 19:30 | 2024-03-03 23:01 | 3:31 | T | Bus Coupler Tripped which is not added. kulsi-1 tripped and 230kV bus coupler tripped. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-03-13 11:21 | 2024-03-13 15:52 | 4:31 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-03-13 11:24 | 2024-03-13 15:50 | 4:26 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 59:37 |  | Unserved Energy: |  | 523.1833
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2024-03-05 22:35 | 2024-03-05 23:45 | 1:10 | E/O | Kasba feeder 33KV Bus B-Phase Red Hot maintenance | 40 | 46.6667 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-03-23 23:10 | 2024-03-23 23:20 | 0:10 | T | 33 kv Nabinogor feeder fault. | 15 | 2.5 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2024-03-18 14:46 | 2024-03-18 18:03 | 3:17 | E/O | Shutdown by AE Chandpur grid | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2024-03-18 09:11 | 2024-03-18 11:57 | 2:46 | E/O | Ten Delta Test | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2024-03-08 20:42 | 2024-03-08 21:50 | 1:08 | E/O | TR-2 33kv bus incoming DS R phase red hot maintenance. | 30 | 34 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 2024-03-15 10:36 | 2024-03-15 10:48 | 0:12 | T | Non dir. O/C Trip | 16 | 3.2 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2024-03-15 10:36 | 2024-03-15 10:48 | 0:12 | T | Non Dir. O/C Trip | 16 | 3.2 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2024-03-19 07:42 | 2024-03-19 08:01 | 0:19 | T | PDB-Moulovibazar & PBS-Maijgaon Distribution Feeder fault. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-03-22 15:30 | 2024-03-22 16:15 | 0:45 | T | Doreen 11 MW & 33KV Reb Ckt -4 3phase with neutral fault. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) LT | 2024-03-22 15:30 | 2024-03-22 16:15 | 0:45 | T | Doreen 11 MW & 33KV Reb Ckt -4 3phase with neutral fault. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 LT | 2024-03-31 21:20 | 2024-03-31 21:20 | 0:00 | E/O | 33kv CT Point Redhot Maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-03-10 16:39 | 2024-03-10 16:52 | 0:13 | E/O | RTU works | 30 | 6.5 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 LT | 2024-03-17 11:42 | 2024-03-17 16:06 | 4:24 | E/O | Tr-1 B-Phase 33 kv under ground cable fault | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 HT | 2024-03-01 12:56 | 2024-03-01 13:06 | 0:10 | T | PROJECT WORK | 21 | 3.5 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-03-31 22:24 | 2024-03-31 22:34 | 0:10 | T | Thundering, Lighting & Heavy Rain | 36 | 6 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2024-03-31 22:24 | 2024-03-31 22:48 | 0:24 | T | Thundering, Lighting & Heavy Rain | 20 | 8 | Power interruption
|  |  | Total : | 16:05 |  | Unserved Energy: |  | 113.5667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-03-13 17:17 | 2024-03-13 17:20 | 0:03 | T | 33 kv morrelgonj feeder fault | 14 | 0.7 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-03-14 19:50 | 2024-03-14 20:01 | 0:11 | T | Incomer Tripped due to 33kV Morrelgonj Feeder fault. | 15 | 2.75 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-03-13 17:17 | 2024-03-13 17:21 | 0:04 | T | 33 kv morrelgonj feeder fault | 14 | 0.93333 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-03-14 19:50 | 2024-03-14 20:02 | 0:12 | T | Incomer Tripped due to 33kV Morrelgonj Feeder fault. | 15 | 3 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-03-12 22:14 | 2024-03-12 22:50 | 0:36 | T | Due to 33KV Feeder fault. | 24 | 14.4 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-03-12 22:14 | 2024-03-12 22:50 | 0:36 | T | Due to 33kv wazirpur feeder fault | 24 | 14.4 | Power interruption
Borhanuddin 230/33kV Grid Sub-Station | Tr-Load HT | 2024-03-06 14:12 | 2024-03-06 18:10 | 3:58 | E/O | Incomer DS Maintenance. | 32 | 126.9333 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-03-03 11:15 | 2024-03-03 12:05 | 0:50 | E/O | Due to 33kv switch years side fire hazardous secuatioon. | 17 | 14.1667 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T HT | 2024-03-03 11:15 | 2024-03-03 11:52 | 0:37 | E/O | Due to 33kv switch years side fire hazardous secuatioon. | 17 | 10.4833 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T HT | 2024-03-31 05:57 | 2024-03-31 07:50 | 1:53 | T | 33kv khalishpur feeder CB burn | 27 | 50.85 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2024-03-03 11:15 | 2024-03-03 11:50 | 0:35 | E/O | Due to 33kv switch years side fire hazardous secuatioon. | 24 | 14 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2024-03-31 05:57 | 2024-03-31 07:46 | 1:49 | T | 33 kv khalishpur feeder CB burn | 27 | 49.05 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 HT | 2024-03-25 07:20 | 2024-03-25 12:01 | 4:41 | T | None | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T HT | 2024-03-22 07:58 | 2024-03-22 12:10 | 4:12 | T | None | 4 | 16.8 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2024-03-05 05:20 | 2024-03-05 05:46 | 0:26 | T | BICL 33 kV feeder fault | 13 | 5.6333 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2024-03-27 18:03 | 2024-03-27 18:19 | 0:16 | T | REB 1 feeder earth fault | 8 | 2.1333 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) LT | 2024-03-04 03:58 | 2024-03-04 04:22 | 0:24 | T | Due to bird fall on 33 kV bus . | 37 | 14.8 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) LT | 2024-03-04 03:58 | 2024-03-04 04:36 | 0:38 | T | Due to bird fall on 33 kV bus . | 37 | 23.4333 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-03-06 12:37 | 2024-03-06 17:17 | 4:40 | E/O | Hot spot maintenance | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-03-16 10:24 | 2024-03-16 14:40 | 4:16 | E/O | 33kv incoming side C.T Y Phase oil leakage. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-03-04 03:58 | 2024-03-04 04:35 | 0:37 | T | Due to bird fall on 33 kV bus . | 37 | 22.8167 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2024-03-31 03:11 | 2024-03-31 03:27 | 0:16 | T | 33 kv feeder fault. | 60 | 16 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2024-03-31 08:47 | 2024-03-31 10:59 | 2:12 | E/O | Due to emergency mait.work | 30 | 66 | Power interruption
|  |  | Total : | 34:02 |  | Unserved Energy: |  | 469.2833
HVDC Grid Circle :
Bhangura 132/33kV Grid Sub-Station | Tr-1(403T) LT | 2024-03-28 09:42 | 2024-03-28 10:35 | 0:53 | E/O | Due to emergency mait.work | 10 | 8.8333 | Power interruption
Bhangura 132/33kV Grid Sub-Station | Tr-2(413T) LT | 2024-03-28 08:31 | 2024-03-28 09:34 | 1:03 | E/O | Due to emergency mait.work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-03-31 06:47 | 2024-03-31 07:44 | 0:57 | T | Trip | 20 | 19 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2024-03-10 14:47 | 2024-03-10 18:00 | 3:13 | E/O | Over Temperature Maintanance | 12 | 38.6 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2024-03-19 13:54 | 2024-03-19 14:07 | 0:13 | T | WZPDCL KALIGONG FEEDER FAULT | 28 | 6.0667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-03-31 05:10 | 2024-03-31 05:40 | 0:30 | T | EF DMT | 20 | 10 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-03-19 11:48 | 2024-03-19 13:15 | 1:27 | E/O | 132 KV T-1 35/50 MVA x-former HT Bushing tan delta point oil leakage. | 0 | 0 | No interruption
|  |  | Total : | 8:16 |  | Unserved Energy: |  | 82.5
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | Bus-33KV | 2024-03-24 13:29 | 2024-03-24 15:25 | 1:56 | E/O | gomastrapur 33 KV feeder bus DS insulator replace | 7 | 13.5333 | Power interruption
Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2024-03-24 13:25 | 2024-03-24 15:25 | 2:00 | E/O | gomastrapur 33 KV feeder bus DS insulator replace | 7 | 14 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-3, 404T LT | 2024-03-26 16:41 | 2024-03-26 17:54 | 1:13 | E/O | Red hot maintenance at 33KV NESCO Substation. | 12 | 14.6 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T HT | 2024-03-27 12:23 | 2024-03-27 13:45 | 1:22 | E/O | Alarm Resetting. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2024-03-20 11:45 | 2024-03-20 11:59 | 0:14 | E/O | Emergency maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T HT | 2024-03-18 13:19 | 2024-03-18 13:26 | 0:07 | T | Trip | 170 | 19.8333 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T HT | 2024-03-18 13:19 | 2024-03-18 13:37 | 0:18 | T | Trip | 230 | 69 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2024-03-20 13:38 | 2024-03-21 12:10 | 22:32 | E/O | Smoke visible T1-132 Kv CB control pannel announciator . | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-03-20 04:18 | 2024-03-20 07:42 | 3:24 | T | Tripped showing Micon P-142 relays at 33kV Bus | 12 | 40.8 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-03-20 04:18 | 2024-03-20 07:42 | 3:24 | T | Tripped showing Micon P-142 relays at 33kV Bus | 12 | 40.8 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 HT | 2024-03-18 09:56 | 2024-03-18 13:05 | 3:09 | E/O | Red hot | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 407T LT | 2024-03-20 10:17 | 2024-03-20 10:24 | 0:07 | T | Feeder fault | 12 | 1.4 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-03-22 10:54 | 2024-03-22 11:22 | 0:28 | E/O | polarity change of ct | 30 | 14 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-03-25 09:40 | 2024-03-25 10:05 | 0:25 | T | CCCE project work | 33 | 13.75 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-03-21 07:30 | 2024-03-21 08:25 | 0:55 | E/O | T-2 33kv BUS S/D by PBS Niamatpur. No operation from Grid Side. | 15 | 13.75 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2024-03-18 12:10 | 2024-03-18 17:48 | 5:38 | E/O | underground cable fault | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2024-03-16 22:17 | 2024-03-16 23:10 | 0:53 | T | Tripped showing MCGG relays. | 40 | 35.3333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2024-03-21 16:55 | 2024-03-21 17:20 | 0:25 | T | Tripped showing MCGG relays. | 40 | 16.6667 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) HT | 2024-03-21 16:55 | 2024-03-21 17:29 | 0:34 | T | 33kv Balubari Feeder Fault | 21 | 11.9 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) LT | 2024-03-16 22:17 | 2024-03-16 22:17 | 0:00 | T | Tripped showing MCGG relays. | 24 | 0 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-03-10 19:40 | 2024-03-11 16:15 | 20:35 | E/O | Current is not flowing through metering of CTs of Tr-1 33 kv side | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2024-03-31 05:20 | 2024-03-31 05:24 | 0:04 | T | Airport Are Faulty | 10 | 0.66667 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) HT | 2024-03-20 19:02 | 2024-03-21 01:57 | 6:55 | T | Tripped showing Lock out relay only relays. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) LT | 2024-03-09 15:12 | 2024-03-09 15:30 | 0:18 | T | Economic zone 33kV Feeder B-Phase CT Blast | 8 | 2.4 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-03-09 15:12 | 2024-03-09 15:50 | 0:38 | T | Economic zone 33kV Feeder B-Phase CT Blast | 8 | 5.0667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-03-27 16:10 | 2024-03-27 16:17 | 0:07 | E/O | After complete testing of Faulty Economic zone 33kV feeder pbs-2 has given clearance to closed CB of Economic zone 33kV feede. for this reason XEN - GMD Bogura order to conduct separet operation of T3 & T4 , all operation has been conducted by the instruction XEN NLDC, | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-03-20 03:46 | 2024-03-20 04:53 | 1:07 | T | Thundering | 0 | 0 | No interruption
|  |  | Total : | 78:48 |  | Unserved Energy: |  | 327.5
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 298:27 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Cantonment Ckt-1 | 2024-03-31 07:07 | 2024-03-31 08:02 | 0:55 | T | Over Voltage | 22 | 20.1667 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Cantonment Ckt-2 | 2024-03-31 07:07 | 2024-03-31 08:10 | 1:03 | T | Over Voltage | 22 | 23.1 | Power interruption
Agargaon 230/132kV Grid Sub-Station | Satmosjid Ckt-2 | 2024-03-31 07:07 | 2024-03-31 08:05 | 0:58 | T | Over Voltage | 22 | 21.2667 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Mirpur-01 | 2024-03-24 02:20 | 2024-03-24 08:49 | 6:29 | T | Storm | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-03-09 09:57 | 2024-03-09 17:31 | 7:34 | E/O | shutdown by NLDC | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2024-03-13 11:33 | 2024-03-13 12:52 | 1:19 | E/O | Red hot maintenance of CT clamp | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2024-03-31 07:05 | 2024-03-31 09:01 | 1:56 | T | Trip | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-2 | 2024-03-27 18:02 | 2024-03-27 18:22 | 0:20 | T | Trip | 72 | 24 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-03-14 06:10 | 2024-03-14 15:18 | 9:08 | T | Trip | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-03-31 09:25 | 2024-03-31 15:45 | 6:20 | E/O | Due to Line DS Problem | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Kabirpur-1 | 2024-03-28 18:42 | 2024-03-28 18:56 | 0:14 | T | Due to Kodda End Source Power Failed. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2024-03-08 16:15 | 2024-03-08 16:51 | 0:36 | T | Tripped showing REL 650 relays. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-1 | 2024-03-31 06:26 | 2024-03-31 16:37 | 10:11 | T | Trip | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tangail-2 | 2024-03-08 16:15 | 2024-03-08 16:39 | 0:24 | T | Trip | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-03-20 07:09 | 2024-03-20 13:01 | 5:52 | T | None | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-03-31 06:52 | 2024-03-31 06:52 | 0:00 | T | Bad weather. After line checking found opg wire disconnect of lalbag line at the lalbag end. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-03-31 12:08 | 2024-03-31 14:51 | 2:43 | E/O | DPDC has taken shutdown. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-03-19 14:56 | 2024-03-19 19:52 | 4:56 | T | Bad weather. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-03-31 11:59 | 2024-03-31 14:51 | 2:52 | E/O | DPDC has taken shutdown. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-03-20 13:23 | 2024-03-20 14:20 | 0:57 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-03-28 11:08 | 2024-03-28 11:23 | 0:15 | E/O | for cutting tree emergency | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-03-24 01:27 | 2024-03-24 01:38 | 0:11 | T | DIST: Z1,R,Y,B | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakair-ckt-2A(E08) | 2024-03-31 06:53 | 2024-03-31 08:09 | 1:16 | T | None | 60 | 76 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakoir ckt-2B(E-09) | 2024-03-31 06:53 | 2024-03-31 08:09 | 1:16 | T | None | 60 | 76 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2A(E04) | 2024-03-31 06:53 | 2024-03-31 08:12 | 1:19 | T | None | 44 | 57.9333 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Tangail-ckt-2B(E03) | 2024-03-31 06:53 | 2024-03-31 08:12 | 1:19 | T | None | 44 | 57.9333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2024-03-23 21:00 | 2024-03-23 21:25 | 0:25 | T | Tripped showing Distance relays. | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 2024-03-28 18:42 | 2024-03-28 19:04 | 0:22 | T | Kodda End Source Power Failed. | 36 | 13.2 | Power interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-2 | 2024-03-28 18:42 | 2024-03-28 19:04 | 0:22 | T | Kodda End Power Source Failed. | 36 | 13.2 | Power interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-03-31 08:20 | 2024-03-31 08:29 | 0:09 | E/O | aspar direction of NLDC | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-03-31 08:20 | 2024-03-31 08:29 | 0:09 | E/O | aspar direction of NLDC | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-03-31 06:25 | 2024-03-31 16:37 | 10:12 | T | Y-phase connected with 33kv H pole due to storm.. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-03-14 14:42 | 2024-03-14 14:48 | 0:06 | T | Tripped showing Distance relays. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-03-14 14:51 | 2024-03-14 14:51 | 0:00 | T | Tripped showing Distance relays. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-03-14 14:55 | 2024-03-14 17:32 | 2:37 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-03-31 06:57 | 2024-03-31 07:40 | 0:43 | T | Heavy storm | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2024-03-21 18:45 | 2024-03-21 19:10 | 0:25 | T | Heavy Storm | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2024-03-19 16:21 | 2024-03-19 16:31 | 0:10 | T | Tripped showing Z1,B-Phase relays. | 60 | 10 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2024-03-27 18:03 | 2024-03-27 18:17 | 0:14 | T | Tripped showing Distance relays. | 100 | 23.3333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-03-19 16:21 | 2024-03-19 16:31 | 0:10 | T | Tripped showing Distance relays. | 60 | 10 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2024-03-11 14:24 | 2024-03-11 14:42 | 0:18 | T | None | 0 | 0 | No interruption
|  |  | Total : | 86:45 |  | Unserved Energy: |  | 426.1333
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-03-13 08:56 | 2024-03-13 10:14 | 1:18 | T | Tripped showing Distance relays. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-03-24 02:45 | 2024-03-24 03:27 | 0:42 | T | Tripped showing Distance relays. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-2 | 2024-03-17 00:23 | 2024-03-17 09:10 | 8:47 | T | Tripped showing Distance relays. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-03-31 07:58 | 2024-03-31 08:21 | 0:23 | T | Rain and Storm. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-03-31 07:58 | 2024-03-31 08:16 | 0:18 | T | Rain and Storm. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Sonargaon 2 | 2024-03-21 19:50 | 2024-03-22 10:56 | 15:06 | T | Rain and Thundaring. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-15 02:10 | 2024-03-15 02:56 | 0:46 | T | Tripped showing Micom P441 (PH Y, Zone 2) relays. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-17 00:17 | 2024-03-17 04:01 | 3:44 | T | Tripped showing Micom P441 (PH Y, Zone 2) relays. | 11 | 41.0667 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-21 19:35 | 2024-03-21 22:17 | 2:42 | T | Rain and thundaring. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-24 02:42 | 2024-03-24 03:06 | 0:24 | T | Heavy Rainfall & Thundering | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-24 17:22 | 2024-03-24 17:41 | 0:19 | T | Raining & Thundering | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-31 06:54 | 2024-03-31 07:42 | 0:48 | T | Rain and storm. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-03-13 08:56 | 2024-03-13 10:12 | 1:16 | T | Unknown | 10 | 12.6667 | Power interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-03-24 02:46 | 2024-03-24 03:34 | 0:48 | T | Unknown | 10 | 8 | Power interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2024-03-24 02:40 | 2024-03-24 09:02 | 6:22 | T | Thundering | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Lalbagh-3 | 2024-03-19 14:57 | 2024-03-19 15:23 | 0:26 | T | Tripped showing 86.1 Trip Relay operated relays. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-03-21 09:38 | 2024-03-21 16:19 | 6:41 | E/O | Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-03-08 12:45 | 2024-03-08 13:46 | 1:01 | E/O | to control overload of 132 KV Haripur-2 ckt | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-03-14 12:34 | 2024-03-14 15:11 | 2:37 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-03-29 12:14 | 2024-03-29 12:16 | 0:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -2 | 2024-03-31 06:56 | 2024-03-31 12:15 | 5:19 | T | Tripped showing 1. B-Phase Trip 2. Zone-1 Trip relays. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-03-26 23:29 | 2024-03-27 03:15 | 3:46 | T | 33Kv Bongshal (DPDC) feeder fault . | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132 kV Maniknagar | 2024-03-19 15:41 | 2024-03-19 19:42 | 4:01 | T | STROM WEATHER | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132 kV Siddhirgonj | 2024-03-21 15:53 | 2024-03-21 22:45 | 6:52 | T | Tripping at Siddhirgonj end | 66 | 453.2 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | Haripur | 2024-03-24 02:45 | 2024-03-24 03:18 | 0:33 | T | By CB Trip from Haripur end | 74 | 40.7 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-03-02 16:04 | 2024-03-02 19:57 | 3:53 | T | N/A | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-03-19 15:10 | 2024-03-19 15:25 | 0:15 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-03-31 06:57 | 2024-03-31 07:44 | 0:47 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-03-31 06:57 | 2024-03-31 07:18 | 0:21 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-04 | 2024-03-31 06:59 | 2024-03-31 09:21 | 2:22 | T | storm | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2024-03-31 06:55 | 2024-03-31 09:17 | 2:22 | T | Storm | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-03-14 12:34 | 2024-03-14 15:10 | 2:36 | E/O | Over current relay change | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-03-07 15:13 | 2024-03-07 16:40 | 1:27 | E/O | Oil Leakage Checking EGCB end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-03-21 15:53 | 2024-03-21 16:36 | 0:43 | T | Matuail line trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-03-24 02:45 | 2024-03-24 05:10 | 2:25 | T | Rain & Thundering and Ullon-1 trip during fault | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-03-21 15:53 | 2024-03-21 16:36 | 0:43 | T | Matuail line trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-03-21 15:52 | 2024-03-21 15:52 | 0:00 | T | Conductor loop break off in pot head B- phase. | 72 | 0 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2024-03-24 02:45 | 2024-03-24 03:03 | 0:18 | T | Heavy rain & thunder during fault time | 15 | 4.5 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2024-03-31 07:00 | 2024-03-31 07:53 | 0:53 | T | Heavy Rain | 8 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-03-31 07:20 | 2024-03-31 08:48 | 1:28 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2024-03-16 05:44 | 2024-03-16 06:00 | 0:16 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2024-03-18 06:29 | 2024-03-18 08:31 | 2:02 | E/O | Shutdown taken from Daudkandi grid S/S. | 34 | 69.1333 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2024-03-18 06:29 | 2024-03-18 08:32 | 2:03 | E/O | Shutdown taken from Daudkandi Grid S/S. | 34 | 69.7 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-03-16 05:44 | 2024-03-16 05:53 | 0:09 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-03-31 07:19 | 2024-03-31 09:01 | 1:42 | T | Trip | 0 | 0 | No interruption
|  |  | Total : | 101:46 |  | Unserved Energy: |  | 698.9667
Chattogram Grid Circle :
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-03-03 21:29 | 2024-03-03 21:45 | 0:16 | T | Tripped showing Distabnce & O/C relay | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-03-03 21:29 | 2024-03-03 22:03 | 0:34 | T | Tripped showing Distabnce & O/C relay | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-03-12 21:41 | 2024-03-12 23:03 | 1:22 | T | Tripped showing Relay Trip-01, 02,03 | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2024-03-28 18:09 | 2024-03-28 18:47 | 0:38 | T | Tripped showing Zone-1(B) relays. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2024-03-24 08:10 | 2024-03-24 09:15 | 1:05 | T | Tripped showing Trip relay K34, K35, K36 & K34X relays. | 20 | 21.6667 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-03-24 08:10 | 2024-03-24 09:09 | 0:59 | T | Tripped showing Trip relay K34, K35, K36 & K34X relays. | 20 | 19.6667 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-03-28 13:58 | 2024-03-28 18:50 | 4:52 | T | Distance trip | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-03-24 08:10 | 2024-03-24 09:11 | 1:01 | T | Tripped showing Trip relay K34, K35, K36 & K34X | 20 | 20.3333 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | PHP | 2024-03-24 08:10 | 2024-03-24 09:16 | 1:06 | T | Tripped showing Trip relay K34, K35, K36 & K34X | 20 | 22 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2024-03-02 10:35 | 2024-03-02 12:32 | 1:57 | E/O | Testing Relay | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2024-03-26 07:13 | 2024-03-26 07:54 | 0:41 | T | Transient fault | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-03-03 21:29 | 2024-03-03 22:18 | 0:49 | T | B-ph O/C & E/F trip. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-03-24 08:02 | 2024-03-24 08:45 | 0:43 | T | Distance trip | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-03-11 22:52 | 2024-03-11 23:43 | 0:51 | T | Distance trip | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2024-03-26 16:27 | 2024-03-26 16:38 | 0:11 | T | Distance trip | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Madunaghat GIS-01 | 2024-03-16 11:22 | 2024-03-16 14:33 | 3:11 | T | Over current. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2024-03-28 18:09 | 2024-03-28 18:48 | 0:39 | T | Heavy storm, rain and thundering. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-1(Rampur) | 2024-03-03 19:30 | 2024-03-05 15:31 | 44:01 | T | Tripped showing QUADRAMHO C- Phase Trip Aided Trip CDD | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-MSML Line | 2024-03-12 21:40 | 2024-03-12 22:48 | 1:08 | T | Earth Fault | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-1 | 2024-03-25 19:26 | 2024-03-25 19:39 | 0:13 | T | General trip,(R,Y,B) Phase fault , Z-com trip | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2024-03-16 11:21 | 2024-03-16 14:21 | 3:00 | T | Tripped showing Quardmo relays Due to b phase, E/F, Distance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2024-03-03 19:30 | 2024-03-03 19:30 | 0:00 | T | General Trip, Distance Trip, B-phs, at sas panel- Main Prot Trip, Last Fault Distance 0.48 km. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2024-03-03 21:28 | 2024-03-03 22:50 | 1:22 | T | kulsi-1 trail from kulsi grid and tripped kulsi-2. | 0 | 0 | No interruption
|  |  | Total : | 70:39 |  | Unserved Energy: |  | 83.6667
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-03-31 09:28 | 2024-03-31 14:49 | 5:21 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibiyana-South | 2024-03-17 09:26 | 2024-03-17 14:00 | 4:34 | E/O | Maintenance | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-03-24 08:53 | 2024-03-24 13:15 | 4:22 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2024-03-23 20:04 | 2024-03-23 20:27 | 0:23 | T | Trip | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-03-14 13:31 | 2024-03-14 13:35 | 0:04 | T | Line Fault | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-03-24 04:33 | 2024-03-24 05:03 | 0:30 | T | DISTANCE RELAY A B C, 3Phase, Zone-2 Fault. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-03-27 20:13 | 2024-03-27 20:30 | 0:17 | T | Distance Relay A.B.C, Zone-01 Boishakhi Storme Started. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-03-03 11:06 | 2024-03-03 22:13 | 11:07 | E/O | maintenance work of cumilla end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-03-04 06:10 | 2024-03-04 18:30 | 12:20 | E/O | maintenance work of cumilla ss end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-03-07 14:48 | 2024-03-07 21:34 | 6:46 | E/O | order by NLDC | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-03-03 11:09 | 2024-03-03 22:14 | 11:05 | E/O | maintenance work of cumilla end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-03-04 06:11 | 2024-03-04 18:30 | 12:19 | E/O | maintenance work of cumilla ss end | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-03-07 12:46 | 2024-03-07 21:35 | 8:49 | E/O | order by NLDC | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-03-31 08:08 | 2024-03-31 08:57 | 0:49 | T | Thunder & bad weather | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-03-23 20:17 | 2024-03-23 20:40 | 0:23 | T | Stormy Wether | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-03-31 08:08 | 2024-03-31 08:57 | 0:49 | T | Trip | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-03-31 08:08 | 2024-03-31 08:57 | 0:49 | T | None | 0 | 0 | No interruption
|  |  | Total : | 80:47 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Mongla 1 | 2024-03-06 12:50 | 2024-03-06 13:50 | 1:00 | E/O | Emergency open for near to sub station side factory and under transmission line fire broke out | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-2 | 2024-03-11 17:09 | 2024-03-12 20:23 | 27:14 | E/O | Gopalganj 400 kv R phase PT problem | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North- West Ckt-2 | 2024-03-10 09:07 | 2024-03-10 11:31 | 2:24 | E/O | Due to Interim transformer à¦¸à§à¦¥à¦¾à¦ªà¦¨ à¦•à¦°à¦¾à¦° à¦œà¦¨à§à¦¯ à¦¸à¦¾à¦Ÿ à¦¡à¦¾à¦‰à¦¨ à¦¨à§‡à¦“à§Ÿà¦¾ à¦¹à§Ÿ | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North- West Ckt-2 | 2024-03-10 18:22 | 2024-03-10 18:43 | 0:21 | E/O | For installing interim Tr-1 | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North-WestCkt-1 | 2024-03-10 09:07 | 2024-03-10 11:31 | 2:24 | E/O | Due to Interim transformer à¦¸à§à¦¥à¦¾à¦ªà¦¨ à¦•à¦°à¦¾à¦° à¦œà¦¨à§à¦¯ à¦¸à¦¾à¦Ÿ à¦¡à¦¾à¦‰à¦¨ à¦¨à§‡à¦“à§Ÿà¦¾ à¦¹à§Ÿà¥¤ | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-1 | 2024-03-11 23:36 | 2024-03-12 16:22 | 16:46 | E/O | Distant relay Fault | 0 | 0 | No interruption
|  |  | Total : | 50:09 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-03-18 12:05 | 2024-03-18 16:39 | 4:34 | E/O | PT maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2024-03-10 16:05 | 2024-03-10 16:46 | 0:41 | E/O | TRTUD work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2024-03-31 06:49 | 2024-03-31 09:49 | 3:00 | T | Trip | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | BEN-1 | 2024-03-16 22:10 | 2024-03-17 04:54 | 6:44 | T | Tripped Due to Thunder storm | 0 | 0 | No interruption
|  |  | Total : | 14:59 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura 230/132kV Grid Sub-Station | Serajganj Line-1 | 2024-03-04 15:04 | 2024-03-04 15:12 | 0:08 | E/O | Emergency Maintenance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2024-03-04 18:41 | 2024-03-04 18:57 | 0:16 | T | Thandaring | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2024-03-15 10:25 | 2024-03-15 10:40 | 0:15 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-01 | 2024-03-22 08:20 | 2024-03-22 12:07 | 3:47 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-1 | 2024-03-15 09:47 | 2024-03-15 10:27 | 0:40 | E/O | Gas Filling | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-03-18 11:12 | 2024-03-18 11:52 | 0:40 | T | under voltage | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2024-03-23 15:07 | 2024-03-23 15:18 | 0:11 | T | Thandaring & Rain | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Panchagar CKT-1 | 2024-03-18 00:08 | 2024-03-18 12:26 | 12:18 | T | O/C | 31 | 381.3 | Power interruption
|  |  | Total : | 18:15 |  | Unserved Energy: |  | 381.3
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 423:20 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 2024-03-02 07:49 | 2024-03-02 20:31 | 12:42 | S/O | Annual Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-03-30 15:56 | 2024-03-30 16:27 | 0:31 | S/O | Schedule shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-03-03 09:09 | 2024-03-03 20:15 | 11:06 | S/O | ATR-01 DS Maintenance Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-03-04 08:28 | 2024-03-04 17:42 | 9:14 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-03-05 08:30 | 2024-03-05 20:40 | 12:10 | S/O | ATR-1 Jack Bus conductor changing work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2024-03-11 07:35 | 2024-03-11 18:47 | 11:12 | S/O | Replace for bus PT 7:35 913B Open | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2024-03-11 07:45 | 2024-03-11 14:10 | 6:25 | S/O | 7:45 725B open 7:50 726S open 8"36 727G close Replace for bus PT | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2024-03-25 10:05 | 2024-03-25 12:17 | 2:12 | S/O | Hotspot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2024-03-12 14:51 | 2024-03-12 15:21 | 0:30 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2024-03-25 11:50 | 2024-03-25 12:59 | 1:09 | S/O | Hotspot removing | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer LT | 2024-03-02 15:59 | 2024-03-02 16:49 | 0:50 | S/O | fall kite on bay conductor | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer LT | 2024-03-30 14:50 | 2024-03-30 16:49 | 1:59 | S/O | Schedule shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2024-03-01 06:33 | 2024-03-01 20:33 | 14:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132 kv Busbar-2 | 2024-03-20 06:28 | 2024-03-20 17:37 | 11:09 | S/O | 132 KV bus jumper temperature high | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan LT | 2024-03-02 08:28 | 2024-03-02 12:18 | 3:50 | D/W | bus upgradation. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2024-03-02 08:23 | 2024-03-02 16:38 | 8:15 | D/W | Project work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Bus B | 2024-03-10 07:52 | 2024-03-10 17:34 | 9:42 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-03-20 07:04 | 2024-03-20 09:34 | 2:30 | S/O | Red-hot maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-03-15 06:24 | 2024-03-15 12:33 | 6:09 | D/W | Project work | 40 | 246 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-03-15 06:24 | 2024-03-15 12:33 | 6:09 | D/W | Project work | 40 | 246 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-03-22 06:23 | 2024-03-22 08:50 | 2:27 | S/O | 33 KV capacitor bank 3 disconnector switch maintenance work | 8 | 19.6 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 LT | 2024-03-16 22:47 | 2024-03-17 00:06 | 1:19 | S/O | 33kv bus coupler red hot maintenance work | 15 | 19.75 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-03-13 06:03 | 2024-03-13 06:36 | 0:33 | S/O | Cleaning work of Auxiliary Transformer. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-03-22 07:15 | 2024-03-22 10:06 | 2:51 | S/O | Red hot maintenance purpose. | 50 | 142.5 | Power interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2024-03-05 08:39 | 2024-03-05 11:27 | 2:48 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2024-03-05 11:34 | 2024-03-05 17:55 | 6:21 | S/O | X-former Oil Leakage and RDS 316 Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2024-03-06 11:50 | 2024-03-06 16:14 | 4:24 | S/O | Bushing Oil Leakage Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Reserve bus | 2024-03-05 08:36 | 2024-03-05 17:31 | 8:55 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | Reserve bus | 2024-03-09 08:44 | 2024-03-09 13:26 | 4:42 | S/O | Aminbazar-1 RDS-306 Maintenance work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | 33 kV T3 Bus | 2024-03-23 09:48 | 2024-03-23 12:36 | 2:48 | S/O | 33 kv Bus-section-03 side maintenance work | 40 | 112 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2024-03-05 06:45 | 2024-03-05 09:07 | 2:22 | S/O | Red hot at bus ds | 30 | 71 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-03-28 05:46 | 2024-03-28 08:26 | 2:40 | S/O | T-5 redhot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2024-03-14 14:42 | 2024-03-14 16:06 | 1:24 | S/O | 33kV BUS to GT-3 incomer DS Y Phase Red hot removal. | 10 | 14 | Power interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-03-09 08:15 | 2024-03-09 17:57 | 9:42 | S/O | 132KV Main Bus Shift to Reserve Bus Work . | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-03-13 09:22 | 2024-03-13 17:08 | 7:46 | S/O | AM Work(Missing Schedule), 132KV Aminbazar ckt-1 with main bus bay. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Main Bus | 2024-03-14 08:57 | 2024-03-14 16:52 | 7:55 | S/O | Annual Maintenance work on Main Bus of Aminbazar ckt-2 | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-03-02 09:05 | 2024-03-02 18:16 | 9:11 | S/O | Amin Bazar ckt-1 with Reserve Bus Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2024-03-03 09:29 | 2024-03-03 11:28 | 1:59 | S/O | AM Work (Relay Test) by SPMD, Dhaka-2. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T2 LT | 2024-03-03 11:41 | 2024-03-03 12:25 | 0:44 | S/O | AM Work (Relay Test) by SPMD, Dhaka-2. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) HT | 2024-03-07 14:46 | 2024-03-07 15:39 | 0:53 | S/O | 400 kV GND project. | 50 | 44.1667 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-03-07 09:46 | 2024-03-07 10:38 | 0:52 | S/O | Shutdown taken by 400 kV GNDP project. | 40 | 34.6667 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-03-13 10:46 | 2024-03-13 15:55 | 5:09 | S/O | Oil centrifugeing | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2024-03-14 09:15 | 2024-03-14 15:50 | 6:35 | S/O | OLTC oil change | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-03-02 07:49 | 2024-03-02 13:33 | 5:44 | S/O | 33kV Bus-A DS maintenance work by DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-03-02 07:49 | 2024-03-02 13:25 | 5:36 | S/O | 33kV Bus-B DS maintenance work by DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-03-19 14:20 | 2024-03-19 17:14 | 2:54 | S/O | remove the nest | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-03-09 10:00 | 2024-03-09 14:11 | 4:11 | S/O | hot spot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-03-23 10:57 | 2024-03-24 20:08 | 33:11 | S/O | replacement work of 132kV Main Bus-I DS (902M) and ES (905G) of 132kV Buscoupler | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2024-03-19 16:35 | 2024-03-19 17:03 | 0:28 | S/O | Birds nest remove | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-03-02 07:46 | 2024-03-02 13:20 | 5:34 | S/O | 33kV Bus-B DS maintenance work by DPBS-3 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-03-17 07:50 | 2024-03-17 10:16 | 2:26 | S/O | For removing fallen foliage by birds. | 7 | 17.0333 | Power interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-03-19 14:20 | 2024-03-19 16:23 | 2:03 | S/O | remove the nest | 35 | 71.75 | Power interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-03-04 09:50 | 2024-03-05 18:50 | 33:00 | S/O | 132 KV Bus Coupler Main Bus-2 Bus DS 901 M replacment work. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 HT | 2024-03-13 09:50 | 2024-03-13 15:44 | 5:54 | D/W | project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 LT | 2024-03-12 08:56 | 2024-03-12 12:14 | 3:18 | D/W | Internal Testing & SAS Integration | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-03-02 09:41 | 2024-03-02 16:30 | 6:49 | D/W | due to SAS Integration | 10 | 68.1667 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-03-03 09:39 | 2024-03-03 13:47 | 4:08 | D/W | SAS integration | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-03-04 09:06 | 2024-03-04 16:21 | 7:15 | D/W | SAS integration | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2024-03-30 11:07 | 2024-03-30 12:42 | 1:35 | D/W | 33 kV Bay Extension work of PDB. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-02 LT | 2024-03-08 07:30 | 2024-03-08 11:47 | 4:17 | S/O | Annual maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2024-03-08 11:54 | 2024-03-08 14:33 | 2:39 | S/O | Annual maintenance | 0 | 0 | No interruption
|  |  | Total : | 357:06 |  | Unserved Energy: |  | 1106.6333
Dhaka (South) Grid Circle :
Gulshan 132/33kV Grid Sub-Station | MT-2 LT | 2024-03-03 07:42 | 2024-03-03 08:21 | 0:39 | S/O | Relay Testing | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Bus Coupler | 2024-03-22 09:41 | 2024-03-22 14:20 | 4:39 | S/O | Loop Changing Work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-1 | 2024-03-22 09:41 | 2024-03-22 14:20 | 4:39 | S/O | Loop Changing Work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-2 | 2024-03-22 09:41 | 2024-03-22 14:20 | 4:39 | S/O | Loop Changing Work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2024-03-07 15:29 | 2024-03-09 16:01 | 48:32 | S/O | Transformer Oil Centrifuging. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2024-03-21 14:13 | 2024-03-22 16:32 | 26:19 | S/O | Oil Centifusing Work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 LT | 2024-03-25 09:33 | 2024-03-25 12:46 | 3:13 | S/O | Red hot Maintanance. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 LT | 2024-03-05 07:26 | 2024-03-13 13:18 | 197:52 | S/O | MK Boxes changing Work. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-1 | 2024-03-19 07:45 | 2024-03-19 14:27 | 6:42 | S/O | More safety due to crane incoming of cvt replacement work | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-1 | 2024-03-20 07:46 | 2024-03-20 14:52 | 7:06 | S/O | Shyampur Hasnabad ckt-1 line CVT replacement work. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-1 | 2024-03-29 09:11 | 2024-03-29 15:35 | 6:24 | S/O | Maintenance Work | 0 | 0 | No interruption
Kazla 132/33kV Grid Sub-Station | GT-1 HT | 2024-03-03 11:40 | 2024-03-03 14:15 | 2:35 | D/W | For gas density meter installation from CCCE project. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2024-03-20 12:12 | 2024-03-20 16:30 | 4:18 | S/O | Maintenance work at 33kv feeder at Bus section -02 by PBS. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-03-09 06:48 | 2024-03-09 07:08 | 0:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132kV Bus-1 | 2024-03-03 09:55 | 2024-03-03 09:55 | 0:00 | S/O | For Anti-corrosive painting work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-03-03 15:40 | 2024-03-03 15:45 | 0:05 | D/W | Project work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 2024-03-02 18:18 | 2024-03-02 18:41 | 0:23 | D/W | Project work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo LT | 2024-03-02 09:26 | 2024-03-02 14:05 | 4:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-03-19 10:19 | 2024-03-19 15:20 | 5:01 | S/O | Anti corrosive painting | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2024-03-24 09:20 | 2024-03-25 00:09 | 14:49 | S/O | Relay change | 0 | 0 | No interruption
|  |  | Total : | 342:54 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | TR-2, 416T LT | 2024-03-09 08:02 | 2024-03-09 12:59 | 4:57 | S/O | 33 KV bus Maintenance | 18 | 89.1 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2024-03-06 06:41 | 2024-03-06 09:35 | 2:54 | S/O | PBS work. 33 kv feeder RED HOT maintenance. | 18 | 52.2 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-02(416T) HT | 2024-03-31 11:25 | 2024-03-31 12:30 | 1:05 | S/O | None | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2024-03-01 07:20 | 2024-03-01 12:25 | 5:05 | S/O | Annual Maintenance T1 | 40 | 203.3333 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2024-03-15 06:07 | 2024-03-15 13:01 | 6:54 | S/O | Cable capacity increase (33kV side) | 60 | 414 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-03-01 05:17 | 2024-03-01 09:06 | 3:49 | S/O | G2G project work. | 35 | 133.5833 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2024-03-22 06:30 | 2024-03-22 08:21 | 1:51 | D/W | G2G capacity upgradation work | 26 | 48.1 | Power interruption
KSRM 132/33kV Grid Sub-Station | Transformer-03 HT | 2024-03-04 12:46 | 2024-03-04 16:21 | 3:35 | S/O | Electrical Maintenance. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2024-03-10 09:40 | 2024-03-10 15:26 | 5:46 | S/O | Annual maintenance | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-03-12 12:47 | 2024-03-12 14:47 | 2:00 | S/O | Red hot maintenance by BPDB. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2024-03-11 09:22 | 2024-03-11 14:28 | 5:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2024-03-16 10:07 | 2024-03-16 12:05 | 1:58 | S/O | For GD meter replacement | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-03-12 10:05 | 2024-03-12 16:01 | 5:56 | D/W | Emergency shutdown needed to check functional test of NIPES of tr-2 | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2024-03-16 10:06 | 2024-03-16 12:01 | 1:55 | S/O | For GD meter replacement. | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 HT | 2024-03-30 09:33 | 2024-03-30 10:41 | 1:08 | S/O | Nest removing | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 HT | 2024-03-30 11:11 | 2024-03-30 11:39 | 0:28 | S/O | Nest removing | 0 | 0 | No interruption
|  |  | Total : | 54:27 |  |  |  | 940.3167
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2024-03-04 10:06 | 2024-03-11 23:39 | 181:33 | S/O | Transfer 33kv incommer 2 from 33kv bus section 2 to 3. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-03-20 11:02 | 2024-03-20 12:33 | 1:31 | D/W | OLTC maintenance work. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 200KVA Aux. T-2 HT | 2024-03-15 06:10 | 2024-03-15 09:00 | 2:50 | S/O | 33 Kv Bus T2 & T5 Bus Shutdown | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-13 13:10 | 2024-03-13 17:58 | 4:48 | S/O | For fire | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-13 19:29 | 2024-03-13 21:08 | 1:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-19 12:03 | 2024-03-19 12:36 | 0:33 | S/O | Shutdown taken by AE | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-19 14:35 | 2024-03-19 16:03 | 1:28 | S/O | Shutdown taken by AE | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-20 10:11 | 2024-03-20 13:40 | 3:29 | S/O | Under ground Cable Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-23 09:45 | 2024-03-23 16:43 | 6:58 | S/O | Underground Cable Maintenance. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-03-24 09:30 | 2024-03-24 15:46 | 6:16 | S/O | Shutdown taken by AE Chandpur grid | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2024-03-14 11:30 | 2024-03-16 22:09 | 58:39 | S/O | Maintenance work | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 HT | 2024-03-19 12:58 | 2024-03-19 14:21 | 1:23 | S/O | Due to 33 kv REB Lalbag & Payerkhola feeder red hot maintenance. | 30 | 41.5 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2024-03-02 09:03 | 2024-03-02 14:05 | 5:02 | S/O | 33kv BUS Maintenance By BPDB | 1 | 5.0333 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2024-03-16 07:34 | 2024-03-16 11:44 | 4:10 | S/O | Shutdown for TANDELTA testing | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-3 LT | 2024-03-16 12:45 | 2024-03-16 15:32 | 2:47 | S/O | For TAN DELTA Testing Purpose | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV TRANSFARBUS | 2024-03-23 15:17 | 2024-03-23 16:44 | 1:27 | D/W | 230/132 KV T-03 project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-03-23 10:06 | 2024-03-23 13:29 | 3:23 | S/O | G2G project works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2024-03-22 10:18 | 2024-03-22 11:26 | 1:08 | S/O | G2G Project Works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 230 KV Bus-2 | 2024-03-05 10:38 | 2024-03-05 17:12 | 6:34 | S/O | PT Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 230 KV Bus-2 | 2024-03-25 09:42 | 2024-03-25 13:23 | 3:41 | S/O | BUS PT TEST WORK. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-03-23 09:46 | 2024-03-23 13:41 | 3:55 | S/O | G2G Project works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2024-03-11 10:07 | 2024-03-11 16:39 | 6:32 | D/W | G2G Project works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2024-03-18 08:33 | 2024-03-18 17:15 | 8:42 | D/W | Bay equipment Erection work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-03-22 09:53 | 2024-03-22 11:33 | 1:40 | S/O | G2G project works | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-03-28 06:20 | 2024-03-28 08:34 | 2:14 | S/O | Reb maintenance work at 33KV bus #1 & #2 | 25 | 55.8333 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-03-22 06:26 | 2024-03-22 09:04 | 2:38 | S/O | For 33KV Isolator Maintenance | 6 | 15.8 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-03-27 08:05 | 2024-03-27 09:24 | 1:19 | S/O | PDB taken S/D for Redhot maintenance at 33KV Bus-02. | 10 | 13.1667 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-03-28 06:18 | 2024-03-28 10:04 | 3:46 | S/O | Reb maintenance work at 33KV bus #1 & #2 | 25 | 94.1667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2024-03-18 07:11 | 2024-03-18 11:18 | 4:07 | S/O | Maintenance of oil leakage. | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2024-03-09 09:00 | 2024-03-09 11:14 | 2:14 | S/O | Due to annual maintenance of 33kv PBS | 25 | 55.8333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Tr-1 LT | 2024-03-19 14:56 | 2024-03-19 16:52 | 1:56 | S/O | Tr-1 B-Phase 33KV underground cable fault Maintenace works | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Bus Bar 132 KV -2 | 2024-03-02 10:46 | 2024-03-02 18:08 | 7:22 | D/W | Purpose of Bus coupler SAS Witness | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 HT | 2024-03-01 10:45 | 2024-03-01 20:39 | 9:54 | D/W | SAS Integration | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-03-02 07:05 | 2024-03-02 10:28 | 3:23 | S/O | 123Kv Bus Section-1 Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 HT | 2024-03-21 09:19 | 2024-03-21 12:59 | 3:40 | S/O | Ten Delta Test Purpose. | 0 | 0 | No interruption
|  |  | Total : | 362:41 |  | Unserved Energy: |  | 281.3333
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-03-27 06:31 | 2024-03-27 08:34 | 2:03 | S/O | Due to maint.work | 16 | 32.8 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-03-27 06:31 | 2024-03-27 08:33 | 2:02 | S/O | 33 kv bus coupler D/S maintenance work | 16 | 32.5333 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2024-03-01 07:15 | 2024-03-01 09:12 | 1:57 | S/O | 33 kv side CB clamp overheat maintenance | 18 | 35.1 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2024-03-09 13:39 | 2024-03-09 18:13 | 4:34 | S/O | Repair Maintenance Work of 33 kv bus by PBS | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-03-09 07:10 | 2024-03-09 15:21 | 8:11 | S/O | Annual Maintenance of 33 kV Bus by PBS | 12 | 98.2 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Main Bus Bar | 2024-03-22 06:21 | 2024-03-22 09:41 | 3:20 | D/W | G2G project work | 10 | 33.3333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-03-09 16:28 | 2024-03-09 18:42 | 2:14 | D/W | EEGBPSP project work. | 22 | 49.1333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-03-09 06:13 | 2024-03-09 08:27 | 2:14 | D/W | Energy pack project work | 22 | 49.1333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-03-10 13:49 | 2024-03-10 18:36 | 4:47 | D/W | 33 kv bus changing work. | 20 | 95.6667 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-03-22 06:19 | 2024-03-22 09:42 | 3:23 | D/W | G2G project Work | 10 | 33.8333 | Power interruption
Faridpur 132/33kV Grid Sub-Station | 33 KV Bus | 2024-03-21 07:20 | 2024-03-21 09:38 | 2:18 | D/W | 33kv Feeder Connection of WZPDCLO | 15 | 34.5 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-03-01 07:30 | 2024-03-03 02:15 | 42:45 | S/O | For 132 kv Breaker Change. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-03-09 07:19 | 2024-03-09 08:36 | 1:17 | S/O | 33kV Bus Section-2&3 Maintenance | 39 | 50.05 | Power interruption
Gollamari 132/33kV Grid Sub-Station | 132kV Bus-1 | 2024-03-31 10:31 | 2024-03-31 13:32 | 3:01 | D/W | Project Work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-01 | 2024-03-16 07:16 | 2024-03-16 17:46 | 10:30 | D/W | None | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Bus-02 | 2024-03-18 07:01 | 2024-03-19 14:02 | 31:01 | D/W | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 HT | 2024-03-19 09:55 | 2024-03-19 14:05 | 4:10 | D/W | Due to maint.work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Main Bus Section-1 | 2024-03-09 10:11 | 2024-03-09 13:29 | 3:18 | S/O | South ckt-2 Bus isolater maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-03-04 10:05 | 2024-03-04 10:05 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2024-03-04 10:04 | 2024-03-04 10:04 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2024-03-04 08:13 | 2024-03-04 15:16 | 7:03 | S/O | Alarm Annunciator Replacement | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-03-30 07:46 | 2024-03-30 13:28 | 5:42 | S/O | 33 kv bus extension | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 HT | 2024-03-11 17:57 | 2024-03-11 19:16 | 1:19 | S/O | Oil leakage maintenance of T1 transformer 33KV CT. | 14 | 18.4333 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2024-03-25 08:50 | 2024-03-25 11:53 | 3:03 | S/O | Buchholz relay oil leakage maintenance | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-1 HT | 2024-03-14 09:43 | 2024-03-14 09:43 | 0:00 | D/W | 33 KV Upgradation under G to G Project | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-03-14 09:42 | 2024-03-14 09:42 | 0:00 | D/W | 33 KV Upgradation under G to G Project | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-03-27 08:13 | 2024-03-27 13:55 | 5:42 | S/O | Emergency maintenance | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 LT | 2024-03-19 08:27 | 2024-03-31 16:58 | 296:31 | D/W | Disk insulator changes | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-03-16 07:03 | 2024-03-16 09:28 | 2:25 | S/O | Due to red-hot maintenance | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T HT | 2024-03-31 08:12 | 2024-03-31 09:24 | 1:12 | S/O | PBS Maintenance. | 10 | 12 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2024-03-31 08:12 | 2024-03-31 09:25 | 1:13 | S/O | PBS Maintenance. | 10 | 12.1667 | Power interruption
|  |  | Total : | 457:15 |  | Unserved Energy : |  | 586.8833
HVDC Grid Circle
Bheramara(GK) 132/33kV Grid Sub-Station | TR-1 LT | 2024-03-14 12:33 | 2024-03-14 13:03 | 0:30 | S/O | TRTUD project work. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2024-03-14 13:07 | 2024-03-14 13:33 | 0:26 | S/O | TRTUD project work. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-3 LT | 2024-03-14 11:49 | 2024-03-14 12:19 | 0:30 | S/O | TRTUD project work. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2024-03-04 08:16 | 2024-03-04 10:09 | 1:53 | S/O | 33 kv busbar maintenance | 17 | 32.0167 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-03-04 08:12 | 2024-03-04 10:37 | 2:25 | S/O | 33 kv busbar maintenance | 18 | 43.5 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 HT | 2024-03-01 09:20 | 2024-03-01 11:01 | 1:41 | S/O | Over Temp Maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 HT | 2024-03-22 06:37 | 2024-03-22 16:57 | 10:20 | D/W | 33kv busber upgadation | 35 | 361.6667 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2024-03-23 06:59 | 2024-03-23 16:30 | 9:31 | S/O | 33 kv Busbar upgradation | 10 | 95.1667 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 HT | 2024-03-16 06:33 | 2024-03-16 16:54 | 10:21 | D/W | 33 kv Busbar Upgradation | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-2 HT | 2024-03-29 07:08 | 2024-03-29 16:42 | 9:34 | D/W | 33 kv busbar upgradation | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-03-01 07:21 | 2024-03-01 09:07 | 1:46 | S/O | 33kv T2A side DS &CT Over temp maintenance | 38 | 67.1333 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-03-09 06:52 | 2024-03-09 18:12 | 11:20 | D/W | 33 kV Busbar Upgradation | 60 | 680 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-03-15 06:44 | 2024-03-15 16:52 | 10:08 | D/W | 33 kv Busbar upgradation | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-03-22 06:36 | 2024-03-22 16:59 | 10:23 | D/W | 33 kv busber upgradation | 35 | 363.4167 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | 230 kV Bus | 2024-03-06 07:53 | 2024-03-06 15:11 | 7:18 | S/O | Busbar 1 | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-03-08 07:08 | 2024-03-08 11:12 | 4:04 | S/O | Tr-1 Oil leakage minimise. | 0 | 0 | No interruption
|  |  | Total : | 92:10 |  | Unserved Energy : |  | 1642.9
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T LT | 2024-03-18 11:34 | 2024-03-18 14:41 | 3:07 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-03-09 08:09 | 2024-03-09 11:03 | 2:54 | S/O | T-1 & T-2 33KV Busbar maintenance work by PBS-1 | 50 | 145 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-03-09 08:10 | 2024-03-09 10:21 | 2:11 | S/O | T-1 & T-2 33KV Busbar maintenance work by PBS-1 | 50 | 109.1667 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-03-23 07:03 | 2024-03-23 09:10 | 2:07 | S/O | 33 kvbus section d/s insulator maintenance | 5 | 10.5833 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-03-23 07:03 | 2024-03-23 09:03 | 2:00 | S/O | 33 kv bus insulator maintenance | 5 | 10 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 132KVMain bus 2 | 2024-03-22 08:36 | 2024-03-22 11:56 | 3:20 | S/O | Polashbari ckt 1 Bus DS Red hot | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Main Bus | 2024-03-08 05:59 | 2024-03-08 10:34 | 4:35 | D/W | 132 kV Main Bus à¦à¦° à¦¸à¦¾à¦¥à§‡ conductor connection à¦à¦¬à¦‚ à¦¹à¦¾à¦‡ à¦­à§‹à¦²à§à¦Ÿà§‡à¦œ à¦ªà¦¾à¦°à§à¦¶à§à¦¬à§‡ à¦•à¦¿à¦›à§ à¦•à¦¾à¦œà§‡à¦° (Jack bus à¦¸à§à¦¥à¦¾à¦ªà¦¨) à¦•à¦°à¦¾à¦° à¦œà¦¨à§à¦¯à¥¤ | 80 | 366.6667 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | 33kV Bus | 2024-03-04 06:35 | 2024-03-04 07:42 | 1:07 | S/O | Project work | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-1(407T) LT | 2024-03-04 06:29 | 2024-03-04 07:46 | 1:17 | S/O | Project work | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-2(417T) LT | 2024-03-10 16:29 | 2024-03-14 15:00 | 94:31 | S/O | Oil centrifuging work. | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2024-03-27 09:28 | 2024-03-27 16:27 | 6:59 | S/O | T-3(B) PRD Oil Leakage Maintenance Work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) HT | 2024-03-20 11:02 | 2024-03-20 16:20 | 5:18 | S/O |  | 10 | 53 | Power interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 LT | 2024-03-27 08:11 | 2024-03-27 17:39 | 9:28 | S/O | SAS Testing | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 LT | 2024-03-30 09:32 | 2024-03-30 15:26 | 5:54 | S/O | SAS WITNESS | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-03-28 08:45 | 2024-03-28 16:05 | 7:20 | S/O | SAS witness test | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-03-29 10:45 | 2024-03-29 17:34 | 6:49 | S/O |  | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2024-03-03 10:07 | 2024-03-03 20:12 | 10:05 | D/W | Nesco 33kV Project Work. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) LT | 2024-03-23 06:06 | 2024-03-23 10:20 | 4:14 | S/O | 33 KV RPC-01 DS | 20 | 84.6667 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) HT | 2024-03-30 07:05 | 2024-03-30 13:52 | 6:47 | S/O | 33 kv capacitor bank bus DS replacement work. | 2 | 13.5667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-03-13 15:10 | 2024-03-13 16:18 | 1:08 | S/O | For connecting y phase source loop to t4 33kV busbar of economic zone feeder | 15 | 17 | Power interruption
|  |  | Total : | 181:11 |  | Unserved Energy : |  | 809.65
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1847:44 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-02 | 2024-03-02 07:41 | 2024-03-02 15:36 | 7:55 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-03-02 06:44 | 2024-03-02 17:46 | 11:02 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-03-09 09:19 | 2024-03-09 14:07 | 4:48 | D/W | Project work | 110 | 528 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2024-03-02 06:44 | 2024-03-02 17:46 | 11:02 | S/O | Due to maint.work | 70 | 772.3333 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2024-03-09 09:19 | 2024-03-09 14:07 | 4:48 | D/W | Project work | 110 | 528 | Power interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-01 | 2024-03-03 08:41 | 2024-03-03 19:32 | 10:51 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-03-05 07:24 | 2024-03-05 14:56 | 7:32 | S/O | NLDC instruction | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2024-03-14 04:29 | 2024-03-14 16:20 | 11:51 | S/O | Line Insulator Disc Cheek | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-03-20 13:03 | 2024-03-20 17:07 | 4:04 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-03-10 10:18 | 2024-03-10 14:58 | 4:40 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Shahajibazar 132 kV Ckt-3 | 2024-03-07 08:22 | 2024-03-07 16:49 | 8:27 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-03-06 09:27 | 2024-03-06 17:19 | 7:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-03-10 09:27 | 2024-03-10 17:18 | 7:51 | S/O | Due to maint.work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 01 | 2024-03-10 07:37 | 2024-03-10 10:03 | 2:26 | S/O | Annual maintenance | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 02 | 2024-03-10 15:18 | 2024-03-10 17:38 | 2:20 | S/O | Annual maintenance | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-01 | 2024-03-15 06:26 | 2024-03-15 12:31 | 6:05 | D/W | Project work | 40 | 243.3333 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | 132 KV Kaliakoir-Dhamrai CKT-02 | 2024-03-15 06:26 | 2024-03-15 12:31 | 6:05 | D/W | Project work | 40 | 243.3333 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-1 | 2024-03-08 07:36 | 2024-03-08 11:58 | 4:22 | S/O | Due to LILO work of 132 kV four ckt Line to Pubile Grid Substation by EEGBPSP. | 15 | 65.5 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-03-08 12:02 | 2024-03-08 16:38 | 4:36 | D/W | LILO of Joydebpur Ghorasal 132kV four ckt line to Pubail 132kV Grid SS | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2024-03-20 07:18 | 2024-03-20 07:18 | 0:00 | S/O | Conductor armaring, rope and bird nest removing. | 90 | 0 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-03-14 11:13 | 2024-03-14 15:29 | 4:16 | S/O | Relay testing by SPMD-2. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-2 | 2024-03-14 03:32 | 2024-03-14 17:14 | 13:42 | S/O | Due to relay test work of spmd-2 | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-03-11 14:24 | 2024-03-11 17:45 | 3:21 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-03-12 08:32 | 2024-03-12 17:15 | 8:43 | S/O | Annual Maintenance and Dead line checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-03-13 07:38 | 2024-03-13 15:59 | 8:21 | S/O | Dead line checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2024-03-10 08:43 | 2024-03-10 17:56 | 9:13 | S/O | Dead Line Checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-03-08 08:41 | 2024-03-08 19:41 | 11:00 | S/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tongi-2 | 2024-03-12 08:37 | 2024-03-12 17:13 | 8:36 | S/O | Annual Maintenance and Dead line checking. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tongi-2 | 2024-03-13 07:42 | 2024-03-13 16:04 | 8:22 | S/O | Dead line checking. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-03-09 08:55 | 2024-03-09 10:37 | 1:42 | S/O | Aminbazar-1 RDS-306 Maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-03-23 09:14 | 2024-03-23 17:35 | 8:21 | S/O | Cross Arm Painting Work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2024-03-30 14:17 | 2024-03-30 16:19 | 2:02 | S/O | Due to disconnected of Suspension insulator disc (Jumper) at angle tower no 05 of aminbazar Ckt-1, Ph-R. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-02 | 2024-03-11 15:20 | 2024-03-11 16:27 | 1:07 | S/O | breaker maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-03-02 09:29 | 2024-03-02 14:01 | 4:32 | S/O | Annual Maintenance | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-03-20 13:16 | 2024-03-20 14:28 | 1:12 | S/O | None | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-03-11 08:56 | 2024-03-11 17:41 | 8:45 | S/O | OPGW Maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-03-08 07:50 | 2024-03-08 14:51 | 7:01 | D/W | Ruppur project work. | 20 | 140.3333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-03-08 08:51 | 2024-03-08 14:50 | 5:59 | D/W | Ruppur project | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-03-02 08:27 | 2024-03-02 18:21 | 9:54 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-03-03 10:38 | 2024-03-03 11:43 | 1:05 | S/O | AM Work (Relay Test) by SPMD, Dhaka-2. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-03-13 08:47 | 2024-03-13 17:25 | 8:38 | S/O | AM work(Missing schedule). | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-03-24 02:23 | 2024-03-24 08:48 | 6:25 | S/O | Dead line checking after storm | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2024-03-14 08:36 | 2024-03-14 16:54 | 8:18 | S/O | Annual Maintenance work on Main Bus of Aminbazar ckt-2 | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-03-21 08:13 | 2024-03-21 16:25 | 8:12 | S/O | B phase CT replacement work on Mirpur-Uttara Sector-18 Ckt | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2024-03-23 08:30 | 2024-03-23 17:58 | 9:28 | S/O | 3nos 132KV LA replacement works. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2024-03-10 07:22 | 2024-03-10 10:05 | 2:43 | S/O | Sreepur-bhaluka line S/D | 30 | 81.5 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2024-03-10 07:22 | 2024-03-10 10:05 | 2:43 | S/O | Sreepur-bhaluka line S/D | 30 | 81.5 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2024-03-07 13:10 | 2024-03-07 14:51 | 1:41 | S/O | Emergency bamboo cutting | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-03-09 10:00 | 2024-03-09 14:55 | 4:55 | S/O | hot sopot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-03-09 09:45 | 2024-03-09 14:11 | 4:26 | S/O | hot spot Maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-03-06 10:06 | 2024-03-06 17:18 | 7:12 | D/W | Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-03-09 09:55 | 2024-03-09 17:30 | 7:35 | S/O | Auto Recloser logic & wiring of SAS panel. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-03-10 09:32 | 2024-03-10 17:17 | 7:45 | S/O | Spare BO BI & MFM (project work) | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-03-11 09:44 | 2024-03-11 17:10 | 7:26 | S/O | project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-03-10 07:39 | 2024-03-10 10:01 | 2:22 | S/O | From Bhaluka Side. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-03-10 15:18 | 2024-03-10 17:38 | 2:20 | S/O | from bhaluka side. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-03-15 16:17 | 2024-03-15 16:45 | 0:28 | S/O | Annual maintenance works | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-03-03 09:52 | 2024-03-03 17:23 | 7:31 | D/W | Project Work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2024-03-02 09:47 | 2024-03-02 19:45 | 9:58 | D/W | Annual maintenance works | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kaliakoir Ckt | 2024-03-11 09:19 | 2024-03-11 18:09 | 8:50 | S/O | Annual maintenance works | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2024-03-05 09:15 | 2024-03-05 16:58 | 7:43 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2024-03-07 06:45 | 2024-03-07 16:35 | 9:50 | S/O | Annual Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2024-03-09 08:58 | 2024-03-09 15:42 | 6:44 | S/O | Annual maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-03-16 11:59 | 2024-03-16 15:12 | 3:13 | S/O | Annual maintenance works | 0 | 0 | No interruption
|  |  | Total : | 402:17 |  | Unserved Energy: |  | 2683.8333
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-03-09 08:54 | 2024-03-09 11:50 | 2:56 | S/O | Due to maintenance works at Ashuganj SS end. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-03-02 09:51 | 2024-03-02 17:01 | 7:10 | S/O | Earth Wire Connection on 230kV Bhulta-Ghorasal-1 Transmission line (Shutdown Taken by Rampura 230/132 kV Grid Substation). | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-03-27 11:47 | 2024-03-27 14:06 | 2:19 | S/O | Due to air leakage of Circuit Breaker at Ghorasal SS end. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-03-27 14:48 | 2024-03-31 16:32 | 97:44 | S/O | Due to maintenance of Air Leakage of Circuit Breaker. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-03-14 09:35 | 2024-03-14 15:21 | 5:46 | S/O | CB open: 09:35 Line Isolator Open: 09:47 Earth Switch close: 09:50 | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-03-12 08:23 | 2024-03-12 14:38 | 6:15 | S/O | CB Open: 08:23, Line Isolator Open: 08:30, Earth Switch Close: 08:35 | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-03-08 07:05 | 2024-03-08 18:49 | 11:44 | S/O | Disc cleaning by Dhamrai end and IDRNPP project work. | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi circuit-1 | 2024-03-08 07:45 | 2024-03-08 18:48 | 11:03 | D/W | IDRNPP Project work | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2024-03-22 09:11 | 2024-03-22 10:15 | 1:04 | S/O | energy meter replacement | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2024-03-09 08:35 | 2024-03-09 16:35 | 8:00 | S/O | Work on other end. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2024-03-10 08:37 | 2024-03-10 15:51 | 7:14 | S/O | Another side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2024-03-21 09:39 | 2024-03-21 16:18 | 6:39 | S/O | Work of Madanganj Substation. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-03-10 07:10 | 2024-03-10 11:52 | 4:42 | S/O | Work on Far end | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-16 10:34 | 2024-03-16 15:08 | 4:34 | S/O | Another side side by NLDC. ( Work at another side) | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-03-17 19:33 | 2024-03-17 23:14 | 3:41 | S/O | Emergency Work of Ullon Substation. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-03-14 09:41 | 2024-03-14 15:22 | 5:41 | S/O | Madanganj grid substation shutdown taken by dead line checking. | 22 | 125.0333 | Power interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2024-03-13 09:03 | 2024-03-13 15:37 | 6:34 | S/O | Dead line checking by Madanganj grid ss | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-03-19 07:42 | 2024-03-19 14:24 | 6:42 | S/O | CVT change | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-03-27 07:19 | 2024-03-29 15:35 | 56:16 | S/O | OPGW installation work. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-Hasnabad Ckt-1 | 2024-03-20 07:43 | 2024-03-20 15:58 | 8:15 | S/O | Line CVT replacement work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-03-01 07:52 | 2024-03-01 15:07 | 7:15 | S/O | Disk cleaning work at Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-03-11 07:21 | 2024-03-11 13:49 | 6:28 | D/W | Project work at Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2024-03-11 07:22 | 2024-03-11 13:49 | 6:27 | D/W | Project work at Aminbazar end. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-03-07 09:06 | 2024-03-07 16:35 | 7:29 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-03-08 08:35 | 2024-03-08 15:50 | 7:15 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-03-09 08:34 | 2024-03-09 16:35 | 8:01 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-03-10 08:36 | 2024-03-10 15:50 | 7:14 | S/O | dead line checking | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-2 | 2024-03-01 06:51 | 2024-03-01 19:24 | 12:33 | S/O | RHD Dept Works under Transmission Tower | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-03-11 08:34 | 2024-03-11 15:57 | 7:23 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-03-12 08:20 | 2024-03-12 14:38 | 6:18 | S/O | Due to maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2024-03-16 10:51 | 2024-03-16 14:38 | 3:47 | S/O | Operation done according to instruction of Mr. Mizanur Rahman, NLDC. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2024-03-31 12:56 | 2024-03-31 13:08 | 0:12 | S/O | Relay testing work by DPDC. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-01 | 2024-03-01 08:25 | 2024-03-01 17:27 | 9:02 | S/O | For dead line checking | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-02 | 2024-03-06 08:17 | 2024-03-06 16:23 | 8:06 | S/O | Dead line checking. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Haripur-01 | 2024-03-09 07:20 | 2024-03-09 11:59 | 4:39 | S/O | For Preventive maintenance work shutdown. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Start Up(MPL) | 2024-03-09 12:10 | 2024-03-09 14:12 | 2:02 | S/O | For Preventive maintenance work shutdown. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | Keraniganj-2 | 2024-03-21 08:47 | 2024-03-21 11:47 | 3:00 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-03-11 06:33 | 2024-03-11 09:16 | 2:43 | S/O | Maintenance work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-03-09 09:59 | 2024-03-09 16:16 | 6:17 | S/O | S/D Taken By Gulshan SS Authority for armouring | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV APR (D04) | 2024-03-27 07:18 | 2024-03-28 21:08 | 37:50 | S/O | Maintenance at Hasnabad end | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2024-03-24 09:22 | 2024-03-25 00:10 | 14:48 | S/O | Corrective maintenance of 230kV end. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2024-03-01 14:55 | 2024-03-01 17:03 | 2:08 | S/O | EGCB End | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-03-01 09:02 | 2024-03-01 12:50 | 3:48 | S/O | EGCB End | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 2 | 2024-03-11 07:09 | 2024-03-21 17:12 | 250:03 | S/O | Due to maint.work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-2 | 2024-03-21 19:59 | 2024-03-22 10:54 | 14:55 | S/O | Line checking purpose. | 0 | 0 | No interruption
|  |  | Total : | 704:02 |  | Unserved Energy: |  | 125.0333
Chattogram Grid Circle :
Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2024-03-09 08:24 | 2024-03-09 16:21 | 7:57 | S/O | Maintenance work at 158,158A,159 tower. | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2024-03-15 06:36 | 2024-03-15 17:29 | 10:53 | S/O | Work at tower no: 158,158A,159 | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2024-03-16 07:25 | 2024-03-16 14:30 | 7:05 | S/O | Work at tower no. 158,158A,159 | 20 | 141.6667 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-03-09 09:05 | 2024-03-09 16:21 | 7:16 | S/O | Maintenance work at 158,158A, 159 tower. | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-03-15 06:36 | 2024-03-15 17:29 | 10:53 | S/O | Work at tower no: 158,158A,159 | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-03-16 07:25 | 2024-03-16 14:30 | 7:05 | S/O | Work at tower no. 158,158A,159 | 20 | 141.6667 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-03-15 07:07 | 2024-03-15 11:36 | 4:29 | D/W | Project work | 12 | 53.8 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-03-15 07:08 | 2024-03-15 11:38 | 4:30 | D/W | Project work | 12 | 54 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2024-03-08 06:42 | 2024-03-08 17:22 | 10:40 | D/W | Project work | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2024-03-22 08:47 | 2024-03-22 11:04 | 2:17 | S/O | Due to maint.work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-03-11 14:57 | 2024-03-11 18:25 | 3:28 | D/W | Tower erection work on Ananda bazar ss | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroaulia-01 | 2024-03-10 07:14 | 2024-03-10 19:33 | 12:19 | S/O | Due to maint.work | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroaulia-02 | 2024-03-10 07:14 | 2024-03-10 19:33 | 12:19 | S/O | Due to maint.work | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2024-03-05 09:21 | 2024-03-06 16:35 | 31:14 | S/O | dead line checking | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2024-03-10 08:26 | 2024-03-10 15:32 | 7:06 | S/O | Disk Change on tower#40 and R/W Clearing | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-1 | 2024-03-05 08:30 | 2024-03-05 16:34 | 8:04 | S/O | Annual Deadline Checking | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-2 | 2024-03-01 08:20 | 2024-03-01 17:38 | 9:18 | S/O | Annual Maintenance of Transmission Line(Ckt-02). | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-2 | 2024-03-02 08:13 | 2024-03-02 17:02 | 8:49 | S/O | Annual maintenance | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-2 | 2024-03-03 08:08 | 2024-03-03 16:45 | 8:37 | S/O | Deadline Check of Rangamati- Khagrachari Ckt-02 | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | RANGAMATI-2 | 2024-03-04 08:15 | 2024-03-04 16:43 | 8:28 | S/O | Deadline Checking. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-1(Rampur) | 2024-03-11 06:39 | 2024-03-11 14:35 | 7:56 | S/O | due to Line by-pass work(35-37 tower span) by ESPNCR. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-03-05 07:27 | 2024-03-05 15:31 | 8:04 | S/O | EMERGENCY MAINTENANCE | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-03-11 06:36 | 2024-03-11 14:23 | 7:47 | D/W | kulsi-1 T connected to halisharhar-1. which one only energies before. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-03-23 07:30 | 2024-03-23 12:55 | 5:25 | S/O | Opening T Connection. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-03-11 14:54 | 2024-03-11 18:25 | 3:31 | D/W | ESPNER project | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2024-03-23 07:45 | 2024-03-23 12:34 | 4:49 | S/O | Opening T Connection. | 0 | 0 | No interruption
Rangamati 132/33kV Grid Sub-Station | Khagrachari Ckt-01 | 2024-03-06 08:15 | 2024-03-06 16:26 | 8:11 | S/O | Annual deadline maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2024-03-01 04:58 | 2024-03-01 05:11 | 0:13 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2024-03-09 06:47 | 2024-03-09 16:09 | 9:22 | D/W | Project Work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2024-03-01 05:19 | 2024-03-01 09:04 | 3:45 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 241:50 |  | Unserved Energy: |  | 391.1333
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-03-08 08:43 | 2024-03-08 19:42 | 10:59 | S/O | Due to maint.work | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Shahzi Ckt-I | 2024-03-06 09:02 | 2024-03-06 18:07 | 9:05 | S/O | Due to maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-03-16 09:10 | 2024-03-16 11:45 | 2:35 | S/O | S/D taken by NLDC | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-03-20 06:20 | 2024-03-20 12:42 | 6:22 | S/O | NLDC SDE. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2024-03-01 08:36 | 2024-03-01 16:13 | 7:37 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2024-03-23 15:14 | 2024-03-23 16:46 | 1:32 | D/W | 230/132 KV T-03 Project work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2024-03-23 15:15 | 2024-03-23 16:46 | 1:31 | D/W | 230/132 KV T-03 Project work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-03-08 07:25 | 2024-03-08 18:42 | 11:17 | D/W | Conductor Stringing of new 132KV Kachua to Laksham line. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-03-09 06:45 | 2024-03-09 16:53 | 10:08 | D/W | Project Work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2024-03-11 08:07 | 2024-03-11 13:15 | 5:08 | S/O | Dead Line Checking By Meghnaghat SS | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2024-03-05 08:24 | 2024-03-05 17:31 | 9:07 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Kachua | 2024-03-01 09:22 | 2024-03-01 17:42 | 8:20 | D/W | Gas leakage maintenance for Bus-01 by PW | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-1 | 2024-03-01 07:12 | 2024-03-01 18:38 | 11:26 | D/W | gas leakage maintenance for Bus-01 | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-2 | 2024-03-01 07:13 | 2024-03-01 18:39 | 11:26 | D/W | same | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-03-05 06:16 | 2024-03-06 20:13 | 37:57 | D/W | Project Work | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-2 | 2024-03-05 06:16 | 2024-03-06 20:13 | 37:57 | D/W | Project Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-03-04 09:49 | 2024-03-04 16:07 | 6:18 | S/O | Sylhet South SS End Project Work | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-03-08 07:24 | 2024-03-08 18:41 | 11:17 | D/W | Project Work | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-03-09 06:40 | 2024-03-09 16:55 | 10:15 | D/W | Project Work | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla South CKT | 2024-03-08 07:21 | 2024-03-08 18:42 | 11:21 | D/W | Project Work | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla South CKT | 2024-03-09 06:41 | 2024-03-09 16:55 | 10:14 | D/W | Project Work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | SPCL 86 MW | 2024-03-18 10:06 | 2024-03-18 15:24 | 5:18 | S/O | Shutdown taken by 86MW Plant. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-03-02 09:09 | 2024-03-02 14:42 | 5:33 | S/O | Annual Maintainance. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-03-06 08:26 | 2024-03-06 17:56 | 9:30 | S/O | Annual maintenece | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-03-06 18:33 | 2024-03-06 22:12 | 3:39 | S/O | Ashuganj end breaker fault. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-03-27 07:24 | 2024-03-27 14:56 | 7:32 | S/O | Sky wire maintenance. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-03-21 09:08 | 2024-03-21 12:51 | 3:43 | S/O | Annual maintenece | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Biyanibazar 132KV Ckt-1 | 2024-03-05 10:25 | 2024-03-05 18:16 | 7:51 | D/W | SAS witness works. | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Biyanibazar 132KV Ckt-1 | 2024-03-06 11:02 | 2024-03-06 14:37 | 3:35 | D/W | SAS integration witness works | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Biyanibazar 132KV Ckt-2 | 2024-03-06 11:05 | 2024-03-06 14:36 | 3:31 | D/W | SAS integration witness works | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Biyanibazar 132KV Ckt-2 | 2024-03-07 10:16 | 2024-03-07 16:54 | 6:38 | D/W | SAS Witness work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-03-04 10:00 | 2024-03-04 20:30 | 10:30 | D/W | SAS Integration for Fenchugonj 1 witness by GNDP Project. | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-03-09 10:33 | 2024-03-09 18:05 | 7:32 | D/W | Project Work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-03-04 10:00 | 2024-03-04 20:30 | 10:30 | D/W | SAS Integration for Fenchugonj 2 witness by GNDP Project. | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-03-09 10:33 | 2024-03-09 18:06 | 7:33 | D/W | Project Work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 75 MW ST PS | 2024-03-28 13:25 | 2024-03-28 15:50 | 2:25 | D/W | Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-03-02 07:20 | 2024-03-02 10:13 | 2:53 | S/O | 123Kv Bus Section-1 Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-03-11 10:35 | 2024-03-11 17:59 | 7:24 | S/O | Work by South Surma GIS Grid | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-03-12 11:07 | 2024-03-12 16:08 | 5:01 | S/O | Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-03-13 11:37 | 2024-03-13 16:41 | 5:04 | S/O | SAS testing Purpose. | 0 | 0 | No interruption
|  |  | Total : | 347:34 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-03-09 06:17 | 2024-03-09 08:25 | 2:08 | S/O | Due to maint.work | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-03-22 06:24 | 2024-03-22 10:10 | 3:46 | D/W | Ordered by ALDC, Khulna. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-03-30 06:33 | 2024-03-30 06:33 | 0:00 | S/O | Ordered by ALDC KHULNA. | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Bagerhat (L3) | 2024-03-30 06:34 | 2024-03-30 06:34 | 0:00 | D/W | Project Work | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-03-09 06:15 | 2024-03-09 18:40 | 12:25 | D/W | For 132 kv Main Bus S/D (Project work) | 22 | 273.1667 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-03-22 06:21 | 2024-03-22 09:41 | 3:20 | D/W | G2G Project Work | 10 | 33.3333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-03-27 06:05 | 2024-03-28 16:23 | 34:18 | D/W | EEGBPSP Project work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2024-03-08 10:10 | 2024-03-08 19:01 | 8:51 | S/O | Power station inner side maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2024-03-08 07:40 | 2024-03-11 18:10 | 82:30 | S/O | 132kv breaker change | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-2 | 2024-03-10 07:23 | 2024-03-10 18:26 | 11:03 | S/O | PT change | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-1 | 2024-03-16 10:49 | 2024-03-16 17:10 | 6:21 | S/O | 230 kV pre commissioning work | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- South -1 | 2024-03-09 09:45 | 2024-03-09 13:41 | 3:56 | S/O | South ckt-2 Bus isolated maintenancr | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- South -2 | 2024-03-08 09:23 | 2024-03-08 10:19 | 0:56 | S/O | Hotspot maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2024-03-09 09:40 | 2024-03-09 13:43 | 4:03 | S/O | South ckt-2 bus isolater maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North- West Ckt-2 | 2024-03-09 09:52 | 2024-03-09 13:42 | 3:50 | S/O | South ckt-2 bus isolater maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | North-WestCkt-1 | 2024-03-09 09:52 | 2024-03-09 13:42 | 3:50 | S/O | South ckt-2 bus isolated maintenance | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Jhenaidah Ckt-1 | 2024-03-06 07:57 | 2024-03-06 14:44 | 6:47 | S/O | Project Work at Jhenaidah S/S End. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-03-08 09:46 | 2024-03-12 17:18 | 103:32 | D/W | Project Work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2024-03-27 10:16 | 2024-03-28 12:46 | 26:30 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur -1 | 2024-03-08 07:40 | 2024-03-11 18:11 | 82:31 | S/O | CB change of Faridpur grid SS. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-1 | 2024-03-16 10:48 | 2024-03-16 17:10 | 6:22 | S/O | For Gopalgonj side maintenance purpose | 0 | 0 | No interruption
|  |  | Total : | 406:59 |  | Unserved Energy: |  | 306.5
HVDC Grid Circle :
Bheramara(GK) 132/33kV Grid Sub-Station | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-1 | 2024-03-14 10:44 | 2024-03-14 10:56 | 0:12 | S/O | TRTUD project work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-03-19 05:03 | 2024-03-19 15:51 | 10:48 | S/O | PT maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-2 | 2024-03-14 09:44 | 2024-03-14 17:45 | 8:01 | S/O | development work | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-2 | 2024-03-08 08:26 | 2024-03-08 11:28 | 3:02 | S/O | Insulator disk cleaning | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2024-03-23 08:44 | 2024-03-23 15:08 | 6:24 | S/O | Gas leakage maintenance work in BKR | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-2 | 2024-03-14 09:45 | 2024-03-14 17:45 | 8:00 | D/W | Solar panel installation work at ishwardi End | 0 | 0 | No interruption
|  |  | Total : | 36:27 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Amnura 132/33kV Grid Sub-Station | Amnura - 100MW PPP | 2024-03-28 15:31 | 2024-03-28 16:10 | 0:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - Rajshahi | 2024-03-11 08:40 | 2024-03-11 15:10 | 6:30 | S/O | Clearance from ALDC, Bogura. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2024-03-25 09:10 | 2024-03-25 16:14 | 7:04 | D/W | Project Work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2024-03-24 08:47 | 2024-03-24 16:49 | 8:02 | S/O | SCADA connection | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2024-03-11 08:29 | 2024-03-11 14:47 | 6:18 | S/O | OPGW WIRE MAINTENANCE | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | Mahasthangarh-Bogura 1 | 2024-03-20 11:03 | 2024-03-20 14:10 | 3:07 | S/O | Due to maint.work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-03-08 05:55 | 2024-03-08 14:20 | 8:25 | S/O | Maintanence work of Niamotpur s/s. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-03-08 05:59 | 2024-03-08 10:35 | 4:36 | D/W | Due to maint.work | 40 | 184 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-03-18 08:35 | 2024-03-18 17:57 | 9:22 | S/O | Rahanpur 400/132 kV Grid Sub-station SAS test. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-03-08 05:59 | 2024-03-08 10:34 | 4:35 | D/W | Due to maint.work | 40 | 183.3333 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-03-19 09:00 | 2024-03-19 12:20 | 3:20 | S/O | Rahanpur 400/132 kV Grid Sub-station SAS test. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2024-03-15 09:10 | 2024-03-15 12:48 | 3:38 | S/O | Due to maint.work | 15 | 54.5 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2024-03-01 11:08 | 2024-03-01 13:11 | 2:03 | S/O | Due to maint.work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2024-03-24 08:50 | 2024-03-24 16:30 | 7:40 | S/O | Sas witnessing work for project work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2024-03-22 08:25 | 2024-03-22 12:42 | 4:17 | S/O | OPGW Maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2024-03-22 08:26 | 2024-03-22 12:44 | 4:18 | S/O | OPGW Maintenance work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-02 | 2024-03-22 08:26 | 2024-03-22 12:43 | 4:17 | S/O | OPGW Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-1 | 2024-03-28 19:24 | 2024-03-29 03:02 | 7:38 | S/O | Equipments Test | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-1 | 2024-03-30 19:40 | 2024-03-31 02:19 | 6:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2024-03-28 19:26 | 2024-03-29 03:20 | 7:54 | S/O | Equipments Test | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-2 | 2024-03-31 19:40 | 2024-03-31 19:40 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Purbosadipur CKT-01 | 2024-03-01 08:44 | 2024-03-01 11:03 | 2:19 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 112:41 |  | Unserved Energy: |  | 421.8333
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2251:50 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March 2024
| Area | Previous Month (February' 2023) |  |  |  | Current Month (March '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 25 | 16 | 171 | 213 | 50 | 20 | 125 | 195
2 | Dhaka (South) Grid Circle. | 69 | 33 | 125 | 227 | 58 | 14 | 65 | 137
3 | Chattogram Grid Circle. | 6 | 16 | 108 | 130 | 30 | 9 | 46 | 85
4 | Cumilla Grid Circle. | 8 | 9 | 123 | 140 | 18 | 16 | 75 | 109
5 | Khulna Grid Circle. | 8 | 10 | 86 | 104 | 16 | 13 | 52 | 81
6 | HVDC Grid Circle | 6 | 8 | 75 | 89 | 5 | 6 | 22 | 33
7 | Bogura Grid Circle. | 7 | 9 | 67 | 83 | 19 | 16 | 42 | 77
8 | Others | bar: Total number of T; Total number of Total
9 | Total | 130 | 101 | 755 | 987 | 196 | 94 | 427 | 717
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March 2024
| Area | Previous Month (February' 2024) |  |  |  | Current Month (March '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 374.21 | 95.83 | 4627.41 | 5097.45 | 952.8 | 466.94 | 3790.47 | 5210.21
2 | Dhaka (South) Grid Circle. | 773.94 | 35 | 1591.66 | 2400.6 | 1129.95 | 150.75 | 125.03 | 1405.73
3 | Chattogram Grid Circle. | 106.62 | 149.2 | 4266.54 | 4522.36 | 574.04 | 32.82 | 1331.45 | 1938.31
4 | Cumilla Grid Circle. | 22.6 | 1.17 | 271.53 | 295.3 | 73.07 | 40.5 | 281.33 | 394.9
5 | Khulna Grid Circle. | 39.68 | 287.75 | 2948.1 | 3275.53 | 237.7 | 231.58 | 893.38 | 1362.66
6 | HVDC Grid Circle |  | 438 | 4552.58 | 4990.58 | 35.07 | 47.43 | 1642.9 | 1725.4
7 | Bogura Grid Circle. | 32.66 | 6.67 | 1582.85 | 1622.18 | 638.92 | 69.88 | 1231.48 | 1940.28
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1349.71 | 1013.62 | 19840.67 | 22204 | 3641.55 | 1039.9 | 9296.04 | 13977.49
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 20 | 13 | 33 | 10 | 4 | 19 | 2100.23
2 | Dhaka (South) | 5031.6 | 12 | - | 12 | 8 | 1 | 3 | 581.73
3 | Chattogram | 2042 | 7 | 6 | 13 | 1 | 2 | 10 | 1463.5
4 | Khulna | 2434 | 20 | 14 | 34 | 10 | 7 | 17 | 1056.16
5 | HVDC | 5954.3 | 5 | 7 | 12 | 2 | 2 | 8 | 1725.4
6 | Bogura | 3145.6 | 17 | 9 | 26 | 8 | 4 | 14 | 1137.15
7 | Cumilla | 2981 | 9 | 7 | 18 | 8 | - | 8 | 394.9
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 8459.07
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.96%
3 | Chattogram | 99.8%
4 | Khulna | 99.93%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.99% | [6 empty] | Information Management Division
7 | Cumilla | 99.98% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 13 | 9 | 22 | 7 | 2 | 13 | 3109.96
2 | Dhaka (South) | 990.29 | - | 8 | 1 | 9 | 1 | 2 | 6 | 824.03
3 | Chattogram | 917 | - | 4 | 4 | 8 | 1 |  | 7 | 474.8
4 | Khulna | 1238.4 | - | - | 2 | 2 | - | - | 2 | 306.5
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | 3 | 4 |  |  | 4 | 803.13
7 | Cumilla | 1648.16 | - | - | - | - | - | - | - | -
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 5518.42
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 100%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-03-01 | 26 | - | 7 | 13hr53 min | 2 | 4hr05 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Agargaon 230/132kV Grid Sub-Station | 2 | 1:52 | 123.2
Bhaluka 132/33kV Grid Sub-Station | 2 | 0:36 | 30
Kabirpur 132/33kV Grid Sub-Station | 3 | 4:47 | 429.67
Kishoreganj 132/33kV Grid Sub-Station | 1 | 0:10 | 5
Mirzapur 132/33kV GIS Grid Sub-Station | 7 | 13:08 | 287.63
Savar 132/33kV Grid Sub-Station | 2 | 0:47 | 38.93
Sreepur 230/132/33kV Grid Sub-Station | 3 | 1:24 | 79.17
Agargaon 230/132kV Grid Sub-Station | 3 | 2:56 | 64.53
Kabirpur 132/33kV Grid Sub-Station | 1 | 0:20 | 24
Mirzapur 132/33kV GIS Grid Sub-Station | 4 | 5:10 | 267.87
Rajendrapur 132/33kV Grid Sub-Station | 2 | 0:44 | 26.4
Tongi 230/132/33kV Grid Sub-Station | 3 | 0:34 | 43.33
Dhamrai 132/33kV Grid Sub-Station | 2 | 12:18 | 492
Jamalpur 132/33kV Grid Sub-Station | 2 | 3:46 | 39.35
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:51 | 142.5
Kishoreganj 132/33kV Grid Sub-Station | 1 | 2:48 | 112
Kodda 132/33kV Grid Sub-Station | 1 | 2:22 | 71
Manikganj 132/33kV Grid Sub-Station | 1 | 1:24 | 14
Mirzapur 132/33kV GIS Grid Sub-Station | 2 | 1:45 | 78.83
Savar 132/33kV Grid Sub-Station | 2 | 4:29 | 88.78
Sreepur 230/132/33kV Grid Sub-Station | 2 | 6:49 | 68.1667
Aminbazar 400/230/132kV Grid Sub-Station | 3 | 20:38 | 1828.33
Dhamrai 132/33kV Grid Sub-Station | 2 | 12:10 | 486.67
Joydebpur 132/33kV Grid Sub-Station | 1 | 4:22 | 65.5
Manikganj 132/33kV Grid Sub-Station | 1 | 7:01 | 140.3333
Mymensingh 132/33kV Grid Sub-Station | 2 | 5:26 | 163
Hasnabad 132/33kV Grid Substation | 2 | 0:43 | 17.87
Keranigonj 230/132/33kV Grid Sub-Station | 2 | 1:14 | 28.37
Siddhirganj 132/33kV Grid Sub-Station | 4 | 8:05 | 404.92
Sonargaon 132/33kV Grid Sub-Station | 4 | 3:11 | 130.58
Haripur 230/132kV Grid Sub-Station | 1 | 3:44 | 41.0667
Hasnabad 132/33kV Grid Substation | 2 | 2:04 | 20.67
Matuail 132/33kV Grid Sub-Station | 1 | 6:52 | 453.2
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:33 | 40.7
Siddhirganj 132/33kV Grid Sub-Station | 1 | 0:18 | 4.5
Sonargaon 132/33kV Grid Sub-Station | 2 | 4:05 | 138.83
Hasnabad 132/33kV Grid Substation | 1 | 5:41 | 125.0333
Baroirhat 132/33kV Grid Sub-Station | 4 | 6:03 | 94.15
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:25 | 35.4167
Kalurghat 132/33kV Grid Sub-Station | 2 | 18:23 | 393.62
Baroirhat 132/33kV Grid Sub-Station | 5 | 9:08 | 172.77
Chandraghona 132/33kV Grid Sub-Station | 1 | 2:54 | 52.2
Coxsbazar 132/33kV Grid Sub-Station | 2 | 11:59 | 617.33
Dohazari 132/33kV Grid Sub-Station | 2 | 5:40 | 181.68
Baroaulia 132/33kV Grid Sub-Station | 2 | 14:10 | 283.33
Baroirhat 132/33kV Grid Sub-Station | 2 | 8:59 | 107.8
Brahmanbaria 132/33kV Grid Sub-Station | 2 | 1:20 | 49.47
Chowmuhani 132/33kV Grid Sub-Station | 1 | 1:08 | 34
Cumilla(S) 132/33kV Grid Sub-Station | 2 | 0:24 | 6.4
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:13 | 6.5
Sylhet (South) 132/33kV GIS Grid Sub-Station | 1 | 0:10 | 3.5
Sylhet 132/33kV Grid Sub-Station | 2 | 0:34 | 14
Chauddagram 132/33kV Grid Sub-Station | 1 | 1:23 | 41.5
Chhatak 132/33kV Grid Sub-Station | 1 | 5:02 | 5.0333
Feni 132/33kV Grid Sub-Station | 4 | 9:57 | 178.97
Ramganj 132/33kV Grid Sub-Station | 1 | 2:14 | 55.8333
Bagerhat 132/33kV Grid Sub-Station | 4 | 0:30 | 7.38
Barishal 230/132kV Grid Sub-Station | 2 | 1:12 | 28.8
Borhanuddin 230/33kV Grid Sub-Station | 1 | 3:58 | 126.9333
Khulna (C) 132/33kV Grid Sub-Station | 5 | 5:44 | 138.55
Madaripur 132/33kV Grid Sub-Station | 1 | 4:12 | 16.8
Mongla 132/33kV Grid Sub-Station | 2 | 0:58 | 7.77
Patuakhali 132/33kV Grid Sub-Station | 3 | 1:39 | 61.05
Satkhira 132/33kV Grid Sub-Station | 2 | 2:28 | 82
Bagerhat 132/33kV Grid Sub-Station | 3 | 6:02 | 100.43
Barishal 230/132kV Grid Sub-Station | 1 | 8:11 | 98.2
Bhandaria 132/33kV Grid Sub-Station | 5 | 373:55 | 261.1
Faridpur 132/33kV Grid Sub-Station | 2 | 3:35 | 84.55
Mongla 132/33kV Grid Sub-Station | 1 | 1:19 | 18.4333
Shariatpur 132/33kV Grid Sub-Station | 2 | 2:25 | 24.17
Bhandaria 132/33kV Grid Sub-Station | 2 | 15:45 | 306.5
Bhangura 132/33kV Grid Sub-Station | 1 | 0:53 | 8.8333
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:57 | 19
Jashore 132/33kV Grid Sub-Station | 1 | 3:13 | 38.6
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:13 | 6.0667
Kushtia 132/33kV Grid Sub-Station | 1 | 0:30 | 10
Ishurdi 132/33kV Grid Sub-Station | 2 | 6:43 | 75.52
Jashore 132/33kV Grid Sub-Station | 5 | 43:20 | 1567.38
Amnura 132/33kV Grid Sub-Station | 2 | 3:56 | 27.53
Barapukuria 230/132/33kV Grid Sub-Station | 3 | 1:38 | 103.43
Jaldhaka 132/33kV Grid Sub-Station | 2 | 6:48 | 81.6
Niamatpur 132/33kV Grid Sub-Station | 4 | 1:55 | 42.9
Purbasadipur 132/33kV Grid Sub-Station | 3 | 1:52 | 63.9
Rajshahi 132/33kV Grid Sub-Station | 1 | 0:04 | 0.66667
Sirajganj 132/33kV Grid Sub-Station | 2 | 0:56 | 7.47
Thakurgaon 132/33kV Grid Sub-Station | 1 | 12:18 | 381.3
Bogura 132/33kV Grid Sub-Station | 2 | 5:05 | 254.17
Chapai 132/33kV Grid Sub-Station | 2 | 4:07 | 20.58
Niamatpur 132/33kV Grid Sub-Station | 1 | 4:35 | 366.6667
Purbasadipur 132/33kV Grid Sub-Station | 1 | 5:18 | 53
Rangpur 132/33kV Grid Sub-Station | 1 | 4:14 | 84.6667
Saidpur 132/33kV Grid Sub-Station | 1 | 6:47 | 13.5667
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:08 | 17
Niamatpur 132/33kV Grid Sub-Station | 1 | 9:11 | 367.33
Purbasadipur 132/33kV Grid Sub-Station | 1 | 3:38 | 54.5
Total Unserved energy : | 191 | 818:25 | 13977.7767
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March 2024
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2024-03-31 19:00 | 34
2 | Agargaon 230/132kV Grid Sub-Station | 2024-03-19 14:00 | 82
3 | Banani 132/33kV Grid Sub-Station | 2024-03-29 07:00 | 101.2
4 | Bangabhaban 132/33kV Grid Sub-Station | 2024-03-18 10:00 | 16
5 | Bashundhara 132/33kV Grid Sub-Station | 2024-03-14 14:00 | 187
6 | BashundharaCement 132/33kV Sub-Station | 2024-03-07 09:00 | 11
7 | Bhulta 132/33kV Grid Sub-Station | 2024-03-17 19:30 | 255
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2024-03-19 15:00 | 130
9 | Charsaidpur 132/33kV Sub-Station | 2024-03-27 01:00 | 50
10 | Dhaka University 132/33kV Grid Sub-Station | 2024-03-13 12:00 | 32
11 | Dhamrai 132/33kV Grid Sub-Station | 2024-03-02 11:00 | 132
12 | Dhanmondi 132/33kV Grid Sub-Station | 2024-03-31 13:00 | 142
13 | Fatullah 132/33kV Grid Sub-Station | 2024-03-30 12:00 | 67
14 | Ghorashal 230/132/33kV Sub-Station | 2024-03-17 22:00 | 84
15 | Gulshan 132/33kV Grid Sub-Station | 2024-03-18 13:00 | 106
16 | HaripurSBU 132/33kV Sub-Station | 2024-03-10 12:00 | 178
17 | Hasnabad 132/33kV Grid Substation | 2024-03-16 12:00 | 103
18 | Joydebpur 132/33kV Grid Sub-Station | 2024-03-30 20:00 | 195
19 | Kabirpur 132/33kV Grid Sub-Station | 2024-03-10 15:00 | 266
20 | Kallyanpur 132/33kV Grid Sub-Station | 2024-03-30 20:00 | 105
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2024-03-14 13:00 | 58.8
22 | Kazla 132/33kV Grid Sub-Station | 2024-03-05 12:00 | 100
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2024-03-17 13:00 | 88
24 | Kodda 132/33kV Grid Sub-Station | 2024-03-25 14:00 | 300
25 | Lalbag 132/33kV Grid Sub-Station | 2024-03-14 13:00 | 93
26 | Madanganj 132/33kV Grid Sub-Station | 2024-03-14 19:30 | 43
27 | Madartek 132/33kV Grid Sub-Station | 2024-03-31 22:00 | 79.13
28 | Manikganj 132/33kV Grid Sub-Station | 2024-03-31 20:00 | 124
29 | Maniknagar 132/33kV Grid Sub-Station | 2024-03-14 13:00 | 70
30 | Matuail 132/33kV Grid Sub-Station | 2024-03-16 12:00 | 72
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2024-03-30 16:00 | 113
32 | Mirpur 132/33kV Grid Sub-Station | 2024-03-30 16:00 | 145
33 | MI_Cement 132/33kV Grid Sub-Station | 2024-03-13 03:00 | 12.8
34 | Mogbazar 132/33kV Grid Sub-Station | 2024-03-18 15:00 | 120.2
35 | Motijheel 132/33kV Grid Sub-Station | 2024-03-14 13:00 | 42
36 | Munshiganj 132/33kV Grid Sub-Station | 2024-03-30 21:00 | 109
37 | Narinda 132/33kV Grid Sub-Station | 2024-03-30 11:00 | 74
38 | Narshingdi 132/33kV Grid Sub-Station | 2024-03-29 20:00 | 173
39 | Nawabganj 132/33kV Grid Sub-Station | 2024-03-30 21:00 | 48.2
40 | New Tongi 132/33kV Grid Sub-Station | 2024-03-30 10:00 | 28.6
41 | Postogola 132/33kV Grid Sub-Station | 2024-03-30 19:00 | 53
42 | Purbachal 132/33kV Grid Sub-Station | 2024-03-03 19:00 | 19
43 | Rahim Steel 132/33kV Sub-Station | 2024-03-12 13:00 | 56
44 | Rajendrapur 132/33kV Grid Sub-Station | 2024-03-30 22:00 | 94
45 | Satmasjid 132/33kV Grid Sub-Station | 2024-03-30 19:30 | 109
46 | Savar 132/33kV Grid Sub-Station | 2024-03-29 12:00 | 184
47 | SevenRings 132/11kV Sub-Station | 2024-03-10 03:00 | 21.67
48 | ShahCement 132/33kV Grid Sub-Station | 2024-03-08 15:00 | 32
49 | Shitalakhya 132/33kV Grid Sub-Station | 2024-03-30 16:00 | 99.6
50 | Shyampur 132/33kV Grid Sub-Station | 2024-03-27 13:00 | 188
51 | Siddhirganj 132/33kV Grid Sub-Station | 2024-03-27 15:00 | 124
52 | Sonargaon 132/33kV Grid Sub-Station | 2024-03-16 11:00 | 117
53 | Sreepur 230/132/33kV Grid Sub-Station | 2024-03-28 19:00 | 66
54 | Srinagar 132/33kV Grid Sub-Station | 2024-03-30 21:00 | 47.27
55 | Tongi 230/132/33kV Grid Sub-Station | 2024-03-31 15:00 | 166
56 | Ullon 132/33kV Grid Sub-Station | 2024-03-30 20:00 | 55
57 | Uttara 132/33kV Grid Sub-Station | 2024-03-27 15:00 | 75
58 | UttaraNew 132/33kV Grid Sub-Station | 2024-03-31 18:30 | 42
59 | Zigatola 132/33kV Grid Sub-Station | 2024-03-30 19:00 | 72
60 | Agrabad 132/33kV Grid Sub-Station | 2024-03-07 13:00 | 88
61 | AKS 132/33kV Grid Sub-Station | 2024-03-03 17:00 | 21
62 | AKSML 230/33kV Grid Sub-Station | 2024-03-30 10:00 | 169
63 | Bakulia 132/33kV Grid Sub-Station | 2024-03-31 19:30 | 97
64 | Baroaulia 132/33kV Grid Sub-Station | 2024-03-14 14:00 | 79
65 | Baroirhat 132/33kV Grid Sub-Station | 2024-03-27 21:00 | 56
66 | BSRM 230/33kV Grid Sub-Station | 2024-03-30 19:00 | 141
67 | Chandraghona 132/33kV Grid Sub-Station | 2024-03-30 18:00 | 31
68 | Coxsbazar 132/33kV Grid Sub-Station | 2024-03-31 22:00 | 131
69 | Dohazari 132/33kV Grid Sub-Station | 2024-03-27 20:00 | 94
70 | GPH 230/33kV Grid Sub-Station | 2024-03-01 02:00 | 99
71 | Halishahar 132/33kV Grid Sub-Station | 2024-03-28 16:00 | 93
72 | Hathazari 230/132/33kV Grid Sub-Station | 2024-03-16 19:00 | 90
73 | Juldah 132/33kV Grid Sub-Station | 2024-03-18 12:00 | 26
74 | Kalurghat 132/33kV Grid Sub-Station | 2024-03-02 12:00 | 36
75 | Khagrachori 132/33kV Grid Sub-Station | 2024-03-17 19:00 | 32
76 | Khulshi 132/33kV Grid Sub-Station | 2024-03-19 13:00 | 178
77 | KSRM 132/33kV Grid Sub-Station | 2024-03-11 06:00 | 62
78 | Madunaghat 132/33kV Grid Sub-Station | 2024-03-27 22:00 | 48
79 | Matarbari 132/33kV Sub-Station | 2024-03-14 21:00 | 48
80 | Mirsorai 230/33kV Grid Sub-Station | 2024-03-30 21:00 | 8
81 | Modern Steel 132/11kV Grid Sub-Station | 2024-03-01 | 0
82 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2024-03-27 19:00 | 37
83 | Rangamati 132/33kV Grid Sub-Station | 2024-03-23 03:00 | 35
84 | Shahmirpur 132/33kV Grid Sub-Station | 2024-03-26 03:00 | 54
85 | Shikalbaha 132/33kV Sub-Station | 2024-03-25 19:00 | 35
86 | Sholosohor 132/33kV Grid Sub-Station | 2024-03-31 10:00 | 48
87 | SSM 132/33kV Grid Sub-Station | 2024-03-21 01:00 | 16
88 | TK chemical 132kV Grid Sub-Station | 2024-03-30 19:00 | 29.4
89 | Ashuganj 230/132/33kV Sub-Station | 2024-03-19 19:00 | 74
90 | Brahmanbaria 132/33kV Grid Sub-Station | 2024-03-29 21:00 | 164
91 | Chandpur 132/33kV Grid Sub-Station | 2024-03-25 18:30 | 62
92 | Chauddagram 132/33kV Grid Sub-Station | 2024-03-27 19:30 | 76
93 | Chowmuhani 132/33kV Grid Sub-Station | 2024-03-17 20:00 | 198
94 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2024-03-30 22:00 | 171
95 | Cumilla(S) 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 165
96 | Daudkandi 132/33kV Grid Sub-Station | 2024-03-30 21:00 | 154
97 | Feni 132/33kV Grid Sub-Station | 2024-03-27 20:00 | 113
98 | Kachua 132/33kV Grid Sub-Station | 2024-03-16 18:30 | 85
99 | PHP 132/33kV Sub-Station | 2024-03-12 19:00 | 11
100 | Ramganj 132/33kV Grid Sub-Station | 2024-03-27 18:30 | 110
101 | Bhaluka 132/33kV Grid Sub-Station | 2024-03-16 10:00 | 142
102 | Jamalpur 132/33kV Grid Sub-Station | 2024-03-29 19:00 | 170
103 | Kishoreganj 132/33kV Grid Sub-Station | 2024-03-13 21:00 | 144
104 | Mirzapur 132/33kV GIS Grid Sub-Station | 2024-03-05 07:00 | 56
105 | Mymensingh 132/33kV Grid Sub-Station | 2024-03-28 18:00 | 229
106 | Netrakona 132/33kV Grid Sub-Station | 2024-03-09 18:30 | 128
107 | Sherpur 132/33kV Grid Sub-Station | 2024-03-30 19:30 | 144
108 | Tangail 132/33kV Grid Sub-Station | 2024-03-30 21:00 | 240
109 | Beanibazar 132/33kV Grid Sub-Station | 2024-03-28 18:30 | 58
110 | Chhatak 132/33kV Grid Sub-Station | 2024-03-29 21:00 | 31
111 | Fenchuganj 230/132/33kV Grid Sub-Station | 2024-03-29 21:00 | 37
112 | Kulaura 132/33kV Grid Sub-Station | 2024-03-18 18:00 | 38
113 | Shahjibazar 132/33kV Grid Sub-Station | 2024-03-29 22:00 | 116
114 | Sreemongol 132/33kV Grid Sub-Station | 2024-03-29 21:00 | 60
115 | Sunamganj 132/33kV Grid Sub-Station | 2024-03-30 20:00 | 49
116 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2024-03-17 18:00 | 32
117 | Sylhet 132/33kV Grid Sub-Station | 2024-03-14 14:00 | 109
118 | Bagerhat 132/33kV Grid Sub-Station | 2024-03-28 19:00 | 92
119 | Benapole 132/33kV Grid Sub-Station | 2024-03-15 18:30 | 80
120 | Bheramara(GK) 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 63
121 | Chuadanga 132/33kV Grid Sub-Station | 2024-03-30 19:00 | 115
122 | Faridpur 132/33kV Grid Sub-Station | 2024-03-30 19:00 | 152
123 | Goalpara 132/33kV Grid Sub-Station | 2024-03-30 14:00 | 38
124 | Gollamari 132/33kV Grid Sub-Station | 2024-03-27 19:00 | 81
125 | Gopalganj 132/33kV Grid Sub-Station | 2024-03-30 19:00 | 109.2
126 | Jashore 132/33kV Grid Sub-Station | 2024-03-31 18:30 | 152
127 | Jhenaidah 132/33kV Grid Sub-Station | 2024-03-30 22:00 | 136
128 | Khulna (C) 132/33kV Grid Sub-Station | 2024-03-31 16:00 | 80
129 | Kushtia 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 132
130 | Madaripur 132/33kV Grid Sub-Station | 2024-03-30 23:00 | 101
131 | Magura 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 65
132 | Mongla 132/33kV Grid Sub-Station | 2024-03-28 16:00 | 40
133 | Narail 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 59
134 | Noapara 132/33kV Grid Sub-Station | 2024-03-10 19:00 | 60
135 | Rajbari 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 74
136 | Satkhira 132/33kV Grid Sub-Station | 2024-03-29 21:00 | 133
137 | Shariatpur 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 79
138 | Barguna 132/33kV Grid Sub-Station | 2024-03-13 21:00 | 20
139 | Barishal 132/33kV Grid Sub-Station | 2024-03-30 21:00 | 114
140 | Barishal 230/132kV Grid Sub-Station | 2024-03-30 19:00 | 94
141 | Bhandaria 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 51
142 | Borhanuddin 230/33kV Grid Sub-Station | 2024-03-31 21:00 | 79
143 | Patuakhali 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 84
144 | Payra 400/132/33kV Grid Sub-Station | 2024-03-27 21:00 | 24
145 | Amnura 132/33kV Grid Sub-Station | 2024-03-08 08:00 | 73
146 | Bhangura 132/33kV Grid Sub-Station | 2024-03-28 13:00 | 37
147 | Bog-Sherpur 132/33kV Grid Sub-Station | 2024-03-27 19:00 | 72
148 | Bogura 132/33kV Grid Sub-Station | 2024-03-03 10:00 | 179
149 | Chapai 132/33kV Grid Sub-Station | 2024-03-30 03:00 | 71
150 | Ishurdi 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 75
151 | Joypurhat 132/33kV Grid Sub-Station | 2024-03-07 11:00 | 66
152 | Mahasthangarh 132/33kV Grid Sub-Station | 2024-03-18 13:00 | 112
153 | Naogaon 132/33kV Grid Sub-Station | 2024-03-31 22:00 | 130
154 | Natore 132/33kV Grid Sub-Station | 2024-03-31 22:00 | 158
155 | Niamatpur 132/33kV Grid Sub-Station | 2024-03-18 21:00 | 102
156 | Pabna 132/33kV Grid Sub-Station | 2024-03-31 19:00 | 120
157 | Rajshahi 132/33kV Grid Sub-Station | 2024-03-31 21:00 | 157
158 | Rajshahi 230/132/33kV Grid Sub-Station | 2024-03-31 22:00 | 37
159 | Ruppur 132/11kV Grid Sub-Station | 2024-03-24 10:00 | 6
160 | Shahjadpur 132/33kV Grid Sub-Station | 2024-03-31 20:00 | 93
161 | Sirajganj 132/33kV Grid Sub-Station | 2024-03-31 22:00 | 110
162 | Ullahpara 132/33kV Grid Sub-Station | 2024-03-24 21:00 | 49
163 | Barapukuria 230/132/33kV Grid Sub-Station | 2024-03-11 10:00 | 62
164 | Jaldhaka 132/33kV Grid Sub-Station | 2024-03-06 19:00 | 80
165 | Kurigram 132/33kV Grid Sub-Station | 2024-03-19 18:00 | 71
166 | Lalmonirhat 132/33kV Grid Sub-Station | 2024-03-06 03:00 | 55
167 | Mithapukur 132/33kV Grid Sub-Station | 2024-03-10 13:00 | 56
168 | Palashbari 132/33kV Grid Sub-Station | 2024-03-11 08:00 | 112
169 | Panchagarh 132/33kV Grid Sub-Station | 2024-03-19 18:00 | 53
170 | Purbasadipur 132/33kV Grid Sub-Station | 2024-03-19 18:00 | 125
171 | Rangpur 132/33kV Grid Sub-Station | 2024-03-19 18:00 | 143
172 | Saidpur 132/33kV Grid Sub-Station | 2024-03-19 17:00 | 111
172 | Thakurgaon 132/33kV Grid Sub-Station | 2024-03-11 19:30 | 89
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 4802.26 | 2024-03-27 | 12:00
Chattogram | 1368.9 | 2024-03-27 | 23:00
Cumilla | 1206 | 2024-03-16 | 21:00
Mymensingh | 1119 | 2024-03-29 | 21:00
Sylhet | 515 | 2024-03-29 | 21:00
Khulna | 1656 | 2024-03-29 | 21:00
Barishal | 421.4 | 2024-03-29 | 21:00
Rajshahi | 1405.6 | 2024-03-18 | 20:00
Rangpur | 913 | 2024-03-19 | 18:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:March 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 416 | 2024-03-31 08:00 | 358 | 2024-03-20 12:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 416 | 2024-03-31 08:00 | 369 | 2024-03-12 14:00
3 | Bibiana 400/230kV Sub-Station | 400 | 418 | 2024-03-01 17:00 | 395 | 2024-03-27 12:00
4 | BIPTC | 400 | 409 | 2024-03-16 21:00 | 387 | 2024-03-07 13:00
5 | Bogura 400/230kV Grid Sub-Station | 400 | 410 | 2024-03-02 03:00 | 368 | 2024-03-13 12:00
6 | Gopalganj 400/132kV Grid Sub-Station | 400 | 418 | 2024-03-31 08:00 | 384 | 2024-03-30 23:00
7 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 398 | 2024-03-09 05:00 | 351 | 2024-03-31 15:00
8 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 421 | 2024-03-06 19:00 | 361 | 2024-03-21
9 | Payra 400kV Sub-Station | 400 | 420 | 2024-03-02 04:00 | 402 | 2024-03-30 23:00
10 | Rahanpur 400/132kV Grid Sub-Station | 400 | 418 | 2024-03-02 05:00 | 386 | 2024-03-13 12:00
11 | Rampal 400/230kV Grid Sub-Station | 400 | 416 | 2024-03-22 02:00 | 385 | 2024-03-16 12:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 250 | 2024-03-24 12:00 | 210 | 2024-03-28 11:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 236 | 2024-03-09 09:00 | 206 | 2024-03-30 08:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 238 | 2024-03-09 04:00 | 220 | 2024-03-13 11:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 228 | 2024-03-20 06:00 | 205 | 2024-03-11 08:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 247 | 2024-03-31 07:00 | 231 | 2024-03-16 14:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 241 | 2024-03-31 07:00 | 221 | 2024-03-08 11:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 234 | 2024-03-05 04:00 | 211 | 2024-03-13 12:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 239 | 2024-03-09 19:30 | 212 | 2024-03-30 07:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 238 | 2024-03-27 18:30 | 217 | 2024-03-18 15:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-03-01 07:00 | 228 | 2024-03-31 15:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 250 | 2024-03-31 08:00 | 220 | 2024-03-02 12:00
12 | Ghorashal 230kV Switching Sub-Station | 230 | 244 | 2024-03-31 07:00 | 216 | 2024-03-27 10:00
13 | GPH 230/33kV Grid Sub-Station | 230 | 236 | 2024-03-09 10:00 | 209 | 2024-03-20 15:00
14 | Haripur 230/132kV Grid Sub-Station | 230 | 244 | 2024-03-31 08:00 | 213 | 2024-03-27 10:00
15 | Hasnabad 230/132kV Grid Sub-Station | 230 | 239 | 2024-03-31 07:00 | 212 | 2024-03-31 15:00
16 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 236 | 2024-03-09 10:00 | 210 | 2024-03-20 15:00
17 | Ishurdi 230/132kV Grid Sub-Station | 230 | 241 | 2024-03-07 04:00 | 223 | 2024-03-11 07:00
18 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 241 | 2024-03-31 07:00 | 213 | 2024-03-31 20:00
19 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-03-31 08:00 | 210 | 2024-03-28 11:00
20 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 243 | 2024-03-02 04:00 | 216 | 2024-03-29 21:00
21 | Maniknagar 230/132kV Grid Sub-Station | 230 | 243 | 2024-03-31 08:00 | 214 | 2024-03-13 15:00
22 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 246 | 2024-03-31 08:00 | 220 | 2024-03-14 12:00
23 | Mirsorai 230/33kV Grid Sub-Station | 230 | 240 | 2024-03-09 19:30 | 210 | 2024-03-28
24 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 242 | 2024-03-07 05:00 | 222 | 2024-03-13 12:00
25 | Rampura 230/132kV Grid Sub-Station | 230 | 242 | 2024-03-31 07:00 | 213 | 2024-03-27 10:00
26 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 233 | 2024-03-06 19:30 | 207 | 2024-03-30 18:30
27 | Shyampur 230/132kV Grid Sub-Station | 230 | 244 | 2024-03-31 08:00 | 214 | 2024-03-31 15:00
28 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 246 | 2024-03-31 08:00 | 216 | 2024-03-27 09:00
29 | Sirajgonj 230 kV Switching Station | 230 | 243 | 2024-03-22 06:00 | 227 | 2024-03-13 12:00
30 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 240 | 2024-03-31 08:00 | 219 | 2024-03-11 12:00
31 | Tongi 230/132/33kV Grid Sub-Station | 230 | 245 | 2024-03-31 07:00 | 205 | 2024-03-14 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 |  | 132 | 139 | 2024-02-10 03:00 | 119 | 2024-02-19 11:00
2 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 08:00 | 120 | 2024-03-12 14:00
3 | Agrabad 132/33kV Grid Sub-Station | 132 | 135 | 2024-03-01 08:00 | 118 | 2024-03-20 15:00
4 | AKS 132/33kV Grid Sub-Station | 132 | 134 | 2024-03-01 09:00 | 116 | 2024-03-20 15:00
5 | Amnura 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-18 21:00 | 121 | 2024-03-13 17:00
6 | Ashuganj 230/132/33kV Sub-Station | 132 | 145 | 2024-03-31 08:00 | 133 | 2024-03-03 11:00
7 | Bagerhat 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 113 | 2024-03-31 19:30
8 | Bakulia 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-09 09:00 | 119 | 2024-03-20 12:00
9 | Banani 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-22 05:00 | 121 | 2024-03-30 12:00
10 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 08:00 | 119 | 2024-03-13 14:00
11 | Barguna 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-21 20:00 | 120 | 2024-03-30 22:00
12 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 05:00 | 116 | 2024-03-30 23:00
13 | Baroaulia 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-12 18:00 | 120 | 2024-03-20 14:00
14 | Baroirhat 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-14 15:00 | 116 | 2024-03-20 15:00
15 | Bashundhara 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 120 | 2024-03-14 12:00
16 | BashundharaCement 132/33kV Sub-Station | 132 | 143 | 2024-03-31 08:00 | 120 | 2024-03-12
17 | Beanibazar 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-20 07:00 | 123 | 2024-03-30 12:00
18 | Benapole 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 114 | 2024-03-31 20:00
19 | Bhaluka 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-31 08:00 | 119 | 2024-03-12 11:00
20 | Bhandaria 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-21 19:30 | 113 | 2024-03-31
21 | Bhangura 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-07 04:00 | 124 | 2024-03-13 10:00
22 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-02 04:00 | 126 | 2024-03-31 21:00
23 | Bhulta 132/33kV Grid Sub-Station | 132 | 130 | 2024-03-24 18:30 | 113 | 2024-03-13 12:00
24 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-02 03:00 | 121 | 2024-03-13 12:00
25 | Bogura 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-20 06:00 | 122 | 2024-03-13 12:00
26 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 08:00 | 114 | 2024-03-03 10:00
27 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 143 | 2024-03-31 07:00 | 119 | 2024-03-31 15:00
28 | Chandpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-14 14:00 | 113 | 2024-03-31 04:00
29 | Chandraghona 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-13 07:00 | 120 | 2024-03-20 15:00
30 | Chapai 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-06 05:00 | 124 | 2024-03-10 08:00
31 | Charsaidpur 132/33kV Sub-Station | 132 | 142 | 2024-03-31 07:00 | 121 | 2024-03-25 12:00
32 | Chauddagram 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-06 19:00 | 116 | 2024-03-31 02:00
33 | Chhatak 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-01 04:00 | 123 | 2024-03-30 12:00
34 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-14 14:00 | 113 | 2024-03-25 10:00
35 | Chuadanga 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 113 | 2024-03-31 03:00
36 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 130 | 2024-03-13 09:00 | 113 | 2024-03-15 05:00
37 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-06 19:00 | 122 | 2024-03-31 21:00
38 | Daudkandi 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-24 18:30 | 113 | 2024-03-27 10:00
39 | Dhaka University 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 08:00 | 122 | 2024-03-13 12:00
40 | Dhamrai 132/33kV Grid Sub-Station | 132 | 146 | 2024-03-31 07:00 | 122 | 2024-03-31 15:00
41 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 122.5 | 2024-03-25 12:00
42 | Dohazari 132/33kV Grid Sub-Station | 132 | 134 | 2024-03-13 09:00 | 114 | 2024-03-20
43 | Faridpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 126 | 2024-03-27 13:00
44 | Fatullah 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 121 | 2024-03-31 15:00
45 | Feni 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-12 18:30 | 114 | 2024-03-31 02:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 07:00 | 120 | 2024-03-31 20:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 07:00 | 121 | 2024-03-31 20:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 07:00 | 123 | 2024-03-31 23:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-31 08:00 | 121 | 2024-03-31 15:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-09 09:00 | 117 | 2024-03-20 15:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 143 | 2024-03-31 07:00 | 123 | 2024-03-25 12:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 143 | 2024-03-31 07:00 | 123 | 2024-03-25 12:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-07 04:00 | 130 | 2024-03-13 12:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-20 06:00 | 113 | 2024-03-06 07:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-19 17:00 | 113 | 2024-03-06 23:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-22 09:00 | 116 | 2024-03-31 20:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-22 05:00 | 121 | 2024-03-31 20:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 147 | 2024-03-31 07:00 | 124 | 2024-03-19 10:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 134 | 2024-03-20 06:00 | 113 | 2024-03-10 13:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-02 03:00 | 119 | 2024-03-20 15:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 07:00 | 116 | 2024-03-25 12:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-06 19:00 | 113 | 2024-03-31 02:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-09 06:00 | 121 | 2024-03-30 12:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-01 04:00 | 120 | 2024-03-20 13:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 146 | 2024-03-31 07:00 | 119 | 2024-03-27 13:00
66 | Kazla 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 08:00 | 119 | 2024-03-13 13:00
67 | Khagrachori 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-09 09:00 | 117 | 2024-03-20 13:00
68 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 06:00 | 118 | 2024-03-31 20:00
69 | Khulshi 132/33kV Grid Sub-Station | 132 | 135 | 2024-03-01 07:00 | 116 | 2024-03-20 15:00
70 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 08:00 | 122 | 2024-03-11 09:00
71 | Kodda 132/33kV Grid Sub-Station | 132 | 147 | 2024-03-31 08:00 | 119 | 2024-03-31 12:00
72 | KSRM 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-01 09:00 | 120 | 2024-03-16 13:00
73 | Kulaura 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-02 05:00 | 128 | 2024-03-27 14:00
74 | Kurigram 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-20 06:00 | 114 | 2024-03-11 08:00
75 | Kushtia 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 07:00 | 123 | 2024-03-31 20:00
76 | Lalbag 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 08:00 | 120 | 2024-03-13 14:00
77 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-20 06:00 | 113 | 2024-03-16 16:00
78 | Madanganj 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 08:00 | 120 | 2024-03-31 15:00
79 | Madaripur 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-31 07:00 | 127 | 2024-03-31 20:00
80 | Madartek 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-31 08:00 | 120 | 2024-03-12 14:00
81 | Madunaghat 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-01 13:00 | 118 | 2024-03-20 15:00
82 | Magura 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-09 03:00 | 119 | 2024-03-31 23:00
83 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-02 04:00 | 118 | 2024-03-13 12:00
84 | Manikganj 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 07:00 | 119 | 2024-03-19 10:00
85 | Maniknagar 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 120 | 2024-03-02 12:00
86 | Matarbari 132/33kV Sub-Station | 132 | 131 | 2024-03-19 05:00 | 113 | 2024-03-15
87 | Matuail 132/33kV Grid Sub-Station | 132 | 143.7 | 2024-03-31 08:00 | 121 | 2024-03-25 12:00
88 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 08:00 | 120 | 2024-03-14 14:00
89 | Mirpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 07:00 | 120 | 2024-03-18 13:00
90 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 139 | 2024-03-19 18:30 | 120 | 2024-03-14 09:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-20 06:00 | 115 | 2024-03-11 08:00
92 | MI_Cement 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 121 | 2024-03-31 15:00
93 | Modern Steel 132/11kV Grid Sub-Station | 132 | 137 | 2024-03-24 08:00 | 117 | 2024-03-20 15:00
94 | Mogbazar 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 07:00 | 120 | 2024-03-31 14:00
95 | Mongla 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 07:00 | 113 | 2024-03-31 20:00
96 | Motijheel 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 08:00 | 119 | 2024-03-14 12:00
97 | Munshiganj 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 07:00 | 121 | 2024-03-27 10:00
98 | Mymensingh 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-23 18:00 | 114 | 2024-03-12 12:00
99 | Naogaon 132/33kV Grid Sub-Station | 132 | 135 | 2024-03-22 06:00 | 115 | 2024-03-13 12:00
100 | Narail 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 07:00 | 118 | 2024-03-31 23:00
101 | Narshingdi 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-11 03:00 | 113 | 2024-03-03 10:00
102 | Natore 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-07 04:00 | 123 | 2024-03-13 12:00
103 | Nawabganj 132/33kV Grid Sub-Station | 132 | 146 | 2024-03-31 07:00 | 121 | 2024-03-12 14:00
104 | Netrakona 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-31 07:00 | 113 | 2024-03-12 10:00
105 | New Tongi 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-29 18:00 | 121 | 2024-03-31 15:00
106 | Niamatpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-09 21:00 | 124 | 2024-03-13 12:00
107 | Noapara 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 118 | 2024-03-31 20:00
108 | Pabna 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 123 | 2024-03-29 23:00
109 | Palashbari 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-20 06:00 | 114 | 2024-03-07 07:00
110 | Panchagarh 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-19 22:00 | 113 | 2024-03-07 09:00
111 | Patuakhali 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-12 18:30 | 123 | 2024-03-30 22:00
112 | PHP 132/33kV Sub-Station | 132 | 138 | 2024-03-12 18:30 | 113 | 2024-03-31 03:00
113 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 08:00 | 122 | 2024-03-31 15:00
114 | Purbachal 132/33kV Grid Sub-Station | 132 | 146 | 2024-03-31 07:00 | 120 | 2024-03-03 11:00
115 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-26 06:00 | 113 | 2024-03-12 12:00
116 | Rahim Steel 132/33kV Sub-Station | 132 | 143 | 2024-03-31 07:00 | 123 | 2024-03-25 12:00
117 | Rajbari 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-31 07:00 | 123 | 2024-03-31 21:00
118 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 08:00 | 119 | 2024-03-28 19:30
119 | Rajshahi 132/33kV Grid Sub-Station | 132 | 135 | 2024-03-31 07:00 | 123 | 2024-03-13 11:00
120 | Ramganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-14 14:00 | 113 | 2024-03-13 14:00
121 | Rangamati 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-12 18:00 | 118 | 2024-03-20 15:00
122 | Rangpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-20 04:00 | 115 | 2024-03-07 08:00
123 | Ruppur 132/11kV Grid Sub-Station | 132 | 143 | 2024-03-31 07:00 | 129 | 2024-03-13 12:00
124 | Saidpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-26 06:00 | 113 | 2024-03-07 08:00
125 | Satkhira 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 113 | 2024-03-31 19:30
126 | Satmasjid 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 07:00 | 119 | 2024-03-31 15:00
127 | Savar 132/33kV Grid Sub-Station | 132 | 143 | 2024-03-31 07:00 | 119 | 2024-03-25 11:00
128 | SevenRings 132/11kV Sub-Station | 132 | 143 | 2024-03-08 19:00 | 129 | 2024-03-14 13:00
129 | ShahCement 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 07:00 | 121 | 2024-03-25 12:00
130 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 06:00 | 130 | 2024-03-13 12:00
131 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-31 09:00 | 118 | 2024-03-03 10:00
132 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-01 09:00 | 119 | 2024-03-20 15:00
133 | Shariatpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-22 06:00 | 126 | 2024-03-31 21:00
134 | Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-03-19 17:00 | 113 | 2024-03-04 18:30
135 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 121 | 2024-03-31 15:00
136 | Sholosohor 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-24 17:00 | 118 | 2024-03-20 15:00
137 | Shyampur 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-31 08:00 | 121 | 2024-03-27 12:00
138 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 144 | 2024-03-31 08:00 | 122 | 2024-03-25 12:00
139 | Sirajganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-03-20 06:00 | 121 | 2024-03-13 12:00
140 | Sonargaon 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 08:00 | 118 | 2024-03-25 12:00
141 | Sreemongol 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-07 13:00 | 124 | 2024-03-14 14:00
142 | Srinagar 132/33kV Grid Sub-Station | 132 | 137 | 2024-03-22 18:30 | 120 | 2024-03-14 12:00
143 | SSM 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-01 23:00 | 120 | 2024-03-20 18:30
144 | Sunamganj 132/33kV Grid Sub-Station | 132 | 135 | 2024-03-09 04:00 | 122 | 2024-03-29 23:00
145 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 136 | 2024-03-09 04:00 | 125 | 2024-03-30 12:00
146 | Sylhet 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-09 03:00 | 126 | 2024-03-30 12:00
147 | Tangail 132/33kV Grid Sub-Station | 132 | 136 | 2024-03-21 18:30 | 116 | 2024-03-14 07:00
148 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-25 23:00 | 113 | 2024-03-05 07:00
149 | TK chemical 132kV Grid Sub-Station | 132 | 137 | 2024-03-09 10:00 | 118 | 2024-03-20 15:00
150 | Ullahpara 132/33kV Grid Sub-Station | 132 | 139 | 2024-03-04 01:00 | 125 | 2024-03-13 11:00
151 | Ullon 132/33kV Grid Sub-Station | 132 | 141 | 2024-03-31 07:00 | 120 | 2024-03-10 17:00
152 | Uttara 132/33kV Grid Sub-Station | 132 | 146 | 2024-03-31 08:00 | 121 | 2024-03-18 14:00
153 | UttaraNew 132/33kV Grid Sub-Station | 132 | 145 | 2024-03-31 07:00 | 120 | 2024-03-18 14:00
154 | Zigatola 132/33kV Grid Sub-Station | 132 | 142 | 2024-03-31 08:00 | 121 | 2024-03-13 14:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:March 2024
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 440 | 445.2235 | 2024-03-18 23:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 440 | 445.2235 | 2024-03-18 23:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -169 | 198.4364 | 2024-03-13 11:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -169 | 198.4364 | 2024-03-13 11:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -230 | 230.7033 | 2024-03-31 13:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -227 | 227.8794 | 2024-03-31 13:00
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 530 | 533.3854 | 2024-03-09 18:30
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 503 | 506.5659 | 2024-03-09 18:30
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 260 | 528.3938 | 2024-03-29 13:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 276 | 295.2982 | 2024-03-30 07:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 276 | 295.2982 | 2024-03-30 07:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 513 | 604.623 | 2024-03-24 15:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -171.38 | 1358.8507 | 2024-03-10 07:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -297.2 | 304.7955 | 2024-03-31 21:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 236 | 240.0667 | 2024-03-01 19:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -158 | 159.9656 | 2024-03-25 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -158 | 159.9656 | 2024-03-25 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -158 | 159.9656 | 2024-03-25 19:30
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 304 | 312.642 | 2024-03-25 03:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 269 | 411.9527 | 2024-03-03 18:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -92 | 95.3362 | 2024-03-28 01:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -147 | 163.2483 | 2024-03-30 22:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 212 | 225.8938 | 2024-03-29 12:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 213 | 225.8185 | 2024-03-30 13:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 185 | 187.5793 | 2024-03-20 09:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 154 | 162.2252 | 2024-03-30 19:30
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 185 | 195.1128 | 2024-03-18 14:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 185 | 195.1128 | 2024-03-18 14:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 185 | 187.9202 | 2024-03-16 11:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 190 | 248.3948 | 2024-03-15 18:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 164 | 169.7999 | 2024-03-01 13:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 145 | 158.4961 | 2024-03-27 19:30
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 111 | 121.3342 | 2024-03-27 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 189 | 193.6104 | 2024-03-11 19:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 183 | 216.6679 | 2024-03-18 13:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 243 | 267.9888 | 2024-03-18 13:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 171 | 172.1656 | 2024-03-15 15:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 171 | 172.1656 | 2024-03-15 15:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -94 | 106.0047 | 2024-03-23 22:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -94 | 106.0047 | 2024-03-23 22:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 182 | 198.0101 | 2024-03-13 22:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 182 | 198.0101 | 2024-03-13 22:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 259 | 265.198 | 2024-03-10 08:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 225 | 240.5203 | 2024-03-31 07:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 223 | 238.296 | 2024-03-31 07:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 231 | 243.181 | 2024-03-29 19:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 100 | 100 | 2024-03-02 14:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 80 | 113.1371 | 2024-03-01 13:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 133 | 169.4521 | 2024-03-25 10:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 132 | 177.7217 | 2024-03-08
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 138 | 179.6357 | 2024-03-25 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 94 | 104.6518 | 2024-03-13 09:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 94 | 104.6518 | 2024-03-13 09:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 78 | 90.5539 | 2024-03-11 23:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 118 | 123.3694 | 2024-03-13 21:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 118 | 123.3694 | 2024-03-13 21:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 118 | 123.3694 | 2024-03-13 21:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 118 | 123.3694 | 2024-03-13 21:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 103 | 142.1724 | 2024-03-31 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 103 | 142.1724 | 2024-03-31 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 102 | 142.1443 | 2024-03-31 21:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -199 | 216.0023 | 2024-03-31 21:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -199 | 216.0023 | 2024-03-31 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 112 | 150.1466 | 2024-03-16 17:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 150 | 158.7577 | 2024-03-23 13:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2024-03-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 150 | 158.7577 | 2024-03-23 13:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -140 | 148.6607 | 2024-03-30 18:30
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -140 | 148.6607 | 2024-03-30 18:30
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -166 | 221.0701 | 2024-03-26 19:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 144 | 156 | 2024-03-19 12:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 144 | 156 | 2024-03-19 12:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -70 | 70.7107 | 2024-03-17 04:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -563 | 563.0888 | 2024-03-25 01:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 129 | 129.0039 | 2024-03-12 07:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 9 | 9 | 2024-03-13 05:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 52 | 219.2556 | 2024-03-06 02:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 273 | 273.5928 | 2024-03-02 18:30
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 243 | 248.5015 | 2024-03-31 15:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 237 | 247.9879 | 2024-03-16 14:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 237 | 247.9879 | 2024-03-16 14:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 149 | 157.1655 | 2024-03-13 10:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 117 | 174.1551 | 2024-03-19
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 156 | 156.6269 | 2024-03-24 10:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 152 | 154.7417 | 2024-03-25 11:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 286 | 297.2491 | 2024-03-03 12:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 285 | 300.7341 | 2024-03-12 11:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 212 | 214.8697 | 2024-03-14 09:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 212 | 214.8697 | 2024-03-14 09:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 212 | 214.8697 | 2024-03-14 09:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: March 2024 | [5 empty] | (For Evening Peak) | [8 empty] | Month: March 2024 |  |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-03-01 | 10151 | 10170 | 18 | 19:00 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | - | 2024-03-01 | 9834 | 9859 | 24 | 12:00 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | -
2024-03-02 | 11397 | 11470 | 70 | 19:00 | 15 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | - | 2024-03-02 | 9950 | 9859 | 60 | 12:00 | 10 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | -
2024-03-03 | 11834 | 11930 | 92 | 19:00 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | - | 2024-03-03 | 10943 | 11040 | 93 | 12:00 | 10 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | -
2024-03-04 | 11603 | 11629 | 25 | 19:00 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | - | 2024-03-04 | 10649 | 10701 | 50 | 12:00 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-05 | 11921 | 12040 | 114 | 19:00 | 15 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | - | 2024-03-05 | 11147 | 11220 | 70 | 12:00 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | -
2024-03-06 | 11749 | 11800 | 49 | 19:00 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | - | 2024-03-06 | 11027 | 11060 | 32 | 12:00 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | -
2024-03-07 | 11663 | 11750 | 83 | 19:00 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | - | 2024-03-07 | 11037 | 11140 | 107 | 11:00 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | -
2024-03-08 | 10494 | 10535 | 39 | 19:00 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | - | 2024-03-08 | 9803 | 9803 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-09 | 11724 | 11825 | 96 | 19:00 | 20 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | - | 2024-03-09 | 9964 | 10000 | 34 | 12:00 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | -
2024-03-10 | 11961 | 12045 | 80 | 19:00 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | - | 2024-03-10 | 11183 | 11300 | 112 | 12:00 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | -
2024-03-11 | 12244 | 12400 | 149 | 19:00 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | - | 2024-03-11 | 11155 | 11300 | 138 | 12:00 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | -
2024-03-12 | 12206 | 12300 | 90 | 19:00 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | 2024-03-12 | 11355 | 11415 | 57 | 12:00 | 13 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | -
2024-03-13 | 12621 | 12780 | 152 | 19:30 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | - | 2024-03-13 | 11515 | 11900 | 368 | 12:00 | 230 | 0 | 0 | 0 | 15 | 123 | 0 | 0 | 0 | -
2024-03-14 | 12482 | 12576 | 90 | 19:30 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | 2024-03-14 | 11763 | 12300 | 513 | 12:00 | 268 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 45 | -
2024-03-15 | 12216 | 12300 | 80 | 21:00 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | - | 2024-03-15 | 10657 | 10750 | 89 | 12:00 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 10 | -
2024-03-16 | 12774 | 12800 | 25 | 21:00 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | - | 2024-03-16 | 11257 | 11450 | 184 | 12:00 | 25 | 84 | 0 | 0 | 0 | 65 | 0 | 0 | 10 | -
2024-03-17 | 12925 | 13000 | 72 | 21:00 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | - | 2024-03-17 | 11100 | 11210 | 105 | 12:00 | 30 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | -
2024-03-18 | 13327 | 13450 | 117 | 21:00 | 10 | 0 | 0 | 0 | 17 | 90 | 0 | 0 | 0 | - | 2024-03-18 | 11439 | 11900 | 440 | 12:00 | 195 | 0 | 0 | 0 | 45 | 150 | 50 | 0 | 0 | -
2024-03-19 | 12411 | 12411 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-19 | 11492 | 11900 | 390 | 12:00 | 180 | 0 | 0 | 45 | 0 | 135 | 0 | 0 | 30 | -
2024-03-20 | 10668 | 10668 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-20 | 9947 | 9980 | 32 | 12:00 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-21 | 10246 | 10246 | 0 | 18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-21 | 10124 | 10124 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-22 | 10354 | 10354 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-22 | 9066 | 9066 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-23 | 11281 | 11281 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-23 | 10399 | 10399 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-24 | 11263 | 11263 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-24 | 10526 | 10526 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-25 | 12883 | 12925 | 40 | 21:00 | 0 | 0 | 0 | 0 | 10 | 20 | 10 | 0 | 0 | - | 2024-03-25 | 11228 | 11228 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-26 | 12107 | 12107 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-26 | 9801 | 9801 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-03-27 | 11935 | 11935 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-03-27 | 11821 | 11900 | 75 | 12:00 | 15 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | -
2024-03-28 | 12652 | 12695 | 41 | 21:00 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | - | 2024-03-28 | 11585 | 11700 | 110 | 11:00 | 20 | 0 | 0 | 0 | 60 | 30 | 0 | 0 | 0 | -
2024-03-29 | 13189 | 13250 | 58 | 21:00 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 |  | 2024-03-29 | 11214 | 11250 | 34 | 12:00 | 19 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0
2024-03-30 | 13353 | 14050 | 666 | 21:00 | 65 | 80 | 150 | 125 | 100 | 66 | 0 | 0 | 80 |  | 2024-03-30 | 11576 | 12100 | 500 | 12:00 | 181 | 94 | 0 | 72 | 70 | 40 | 0 | 0 | 43
2024-03-31 | 13898 | 13950 | 50 | 21:00 | 10 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 |  | 2024-03-31 | 10854 | 10854 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13898 | 2024-03-31 | 21:00
2 | Maximum Day Peak Genaration | MW | 11821 | 2024-03-27 | 12:00
3 | Maximum Evening Peak Demand | MW | 14050 | 2024-03-30 | 21:00
4 | Minimum Generation | MW | 7249 | 2024-03-22 | 6:00
5 | Average of the daily evening peak Genaration | MW | 11984.9032 | - | -
6 | Average of the daily day peak Genaration | MW | 10819.7097 | - | -
7 | Maximum load shed | MW | 666 | 2024-03-30 | 21:00
8 | Minimum load shed | MW | 0 | 2024-03-26 | 21:00
9 | Total nos. of load shed days | Day | 23 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 74.8667 | - | -
11 | Total Generation | MkWh | 7883.8722 | - | -
12 | Total Generation by BPDB | MkWh | 2159.2989 | % of total Gen. | 27.39%
13 | Total Generation by IPP | MkWh | 1866.367 | '' | 23.67%
14 | A) Total Generation by Generation Companies | MkWh | 2178.3732 | '' | 27.63%
| B) Total Generation by REB | MkWh | 99.727 | " | 1.265%
| C) Total Generation by RENTAL | MkWh | 104.0822 | " | 1.32%
| D) Total Imported from India (BIPTC) | MkWh | 639.36 | " | 8.11%
| E) Total Imported from Tripura, India (A.C) | MkWh | 836.6639 | " | 10.61%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3706.1266 | % of total Gen. | 47.01%
| B) Oil | MkWh | 621.48 | '' | 7.883%
| C) Hydro | MkWh | 23.5131 | '' | 0.2982%
| D) Solar | MkWh | 91.681 | '' | 1.163%
| E) Coal | MkWh | 2708.9996 | '' | 34.36%
| F) BIPTC (Import from India) | MkWh | 639.36 | '' | 8.11%
| G) A.C (Import from Tripura, India) | MkWh | 84.6701 | '' | 1.074%
| H) Wind | MkWh | 8.0323 | '' | 0.1019%
16 | Maximun of the daily total Generation . | MkWh | 277.9771 | 2024-03-19
17 | Monthly Load factor | % | 73.5217 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 40398.846 | - | -
| A) Gas | M.Taka | 11154.3959 | - | -
| B) Liquid fuel | M.Taka | 9607.7387 | - | -
| C) Coal | M.Taka | 16218.1566 | - | -
| D) BIPTC (Import from India) | M.Taka | 2685.3119 | - | -
| E) Tripura(Import from India) | M.Taka | 733.2429 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1582.703 | 2024-03-24
| A) Gas | M.Taka | 397.6261 | 2024-03-23
| B) Liquid fuel | M.Taka | 572.9953 | 2024-03-24
| C) Coal | M.Taka | 639.5417 | 2024-03-23
| D) BIPTC (Import from India) | M.Taka | 92.1129 | 2024-03-04
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.1242
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.2056
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.84 | 31/03/2024 | 06:00
b) | Actual | FT (MSL) | 79.9 | 31/03/2024 | 6:00
22 | Peak Genaration of March 2023 | MW | 12921 | 2023-03-13 | 19:00
23 | Peak Demand of March 2023 | MW | 13046 | 2023-03-31 | 21:00
24 | Maximum peak Generation recorded upto 31/03/2024 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/03/2024 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 31/03/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:March 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 | √ | √ | √ | √ | √ | √ | √ | [15 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335
10 | Ashuganj 225 MW CCPP | APSCL | 221 | [22 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | [20 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | [20 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [7 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD