## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-24 | Friday
|  | Date (day): | 2024-05-24 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14966.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16376 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-23 | 2024-05-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 398 | 401 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 64 | 98 | 90 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 315 | 319 | 320 | 320
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 80 | 80 | 80 | 80 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 40 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 14 | 0 | 15 | 60 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 70 | 83 | 85 | 90 |  |  | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 306 | 304 | 310 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 82 | 90 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 149 | 48 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 41 | 43 | 43 |  | 37 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 28 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 100 | 290 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 149 | 149 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 105 | 17 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 70 | 70 | 53 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 350 | 500 | 400 | 500
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 300 | 500 | 400 | 500 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 3483 | 4320 | 3919 | 4328 | 780 | 829
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 103 | 110 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 30 | 6 | 20 | 30 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 85 | 34 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 45 | 62 | 55 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 60 | 51 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 58 | 40 | 70 | 70 | 30 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 49 | 86 | 49 | 62 | 38 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 18 | 20 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 44 | 58 | 45 | 60 |  | 8 | Engine problem
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 50 | 50 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 99 | 110 | 51 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 94 | 48 | 60 | 40 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 63 | 35 | 53 | 63 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 460 | 487 | 490 | 490 |  | 734 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 1 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 232 | 233 | 235 | 235
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 45 | 0 | 33 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1450 | 1835 | 1576 | 1835 | 826 | 1336
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 193 | 210 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 310 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 270 | 270 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 250 | 260 | 250 | 280 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 35 | 35 | 36 | 9
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 43 | 43 | 50 | 50
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 12 | 53 | 12 | 50 | 100 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 44 | 39 | 40
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 104 | 138 | 100 | 200 | 0
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 84 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 24 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 50 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 52 | 52 | 114 | 0
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 83 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 50 | 50
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 88 | 111 | 115 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1708 | 1938 | 1785 | 2108 | 342 | 176
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 60 | 70 | 45 | 80 | 122 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 58 | 106 | 58 | 105 | 95 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 98 | 57 | 100 | 15 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 228 | 286 | 223.6 | 297 | 122 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 37 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 48 | 48 | 60 | 60 |  | 30 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 49 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 41 | 42 | 42 | 42 |  | 8 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 55 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 200 | 202 | 204 | 204 |  | 27 | Engine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 367 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 345 | 345 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1606 | 1591 | 1644 | 1659 | 0 | 500
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 925 | 640 | 944 | 655
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 0 | 0 | 20
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 0 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 44 | 62 |  | 47 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 385 | 340 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 40 | 0 | 0
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 53 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 100
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 378 | 560 | 400 | 540
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1788 | 1719 | 1541 | 1509 | 1007 | 59
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 16 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 122 | 130 | 90 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 700 | 1130 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 17 | 133 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 307 | 250 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1409 | 1813 | 1941 | 2038 | 133 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 40 | 50 | 50 | 21 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 37 | 39 | 40 | 42 |  | 10 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 35 | 0 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 14 | 39 | 42 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Machine problem
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 191 | 194 | 180 | 190 |  |  | FGMO
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 194 | 180 | 190 |  |  | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 414 | 350 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 0 | 81 |  | 23 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 73 | 113 | 50 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 50 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 762 | 766 | 760 | 760 |  |  | unit-1 under maint
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1795 | 2064 | 1719 | 2089 | 193 | 297
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 65 | 65 | 65
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 215 | 220 | 220 |  | 54 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 50 | 106 | 50 | 113
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 201 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 699 | 501 | 618 | 513 | 40 | 139
| Total |  |  |  |  | 27054 | 25903 | 14166 | 16067 | 14966.6 | 16376 | 3443 | 3400
A. |  | 2024-05-23 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 16067 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12609 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 16400 | MW
3 | Day peak Generation : |  |  | 14166 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15532.81 | MW
4 | Evening peak Generation : |  |  | 16067 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 318 | MW
5 | Total Energy Generation : |  | 343.4637 | MKWHr | By Solar | 3.8691 | MKWHr
| By Gas : | 169.4985 | MKWHr |  | By Oil: | 64.4911 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 82.5781 | MKWHr |  | By Hydro: | 0.5892 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0672 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3443 | MW | Dhaka | 5552.11 | 5452.11 |  | 100 |  | 18:00 |  | 456
|  |  | For Plants S/D or M/C prob = |  |  | 3400 | MW | Chittagong | 1522.5 | 1522.5 |  | 0 |  | 19:00 |  | 425.93
|  |  | Total = |  |  | 6843 | MW | Khulna | 1897.4 | 1897.4 |  | 0 |  | 19:30 |  | 308.465
7 | Total Gas Supplied : |  |  | 1242.27 | MMCFD |  |  | Rajshahi | 1621.6 | 1621.6 |  | 0 |  | 20:00 |  | 327.565
8 | Fuel Cost : | i) Gas : | Taka | 471889295.144 | ii) Oil : | Taka | 1181738852.32 | Comilla | 1518 | 1483 |  | 35 |  | 21:00 |  | 318
|  | iii) Coal : | Taka | 572029146.78 | Total | Taka | 2225657294.244 | Mymensingh | 1267 | 1117 |  | 150 |  | 22:00 |  | 303
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 6421.8 | MKWHr. | Sylhet | 667 | 667 |  | 0 |  | 23:00 |  | 534
| ii) During Peak Demand : |  |  | 258 | MW (W to E) at | 21:00 | hrs | Barisal | 470.2 | 470.2 |  | 0 |  | 24:00 |  | 471
| iii) Maximum : |  |  | 238 | MW at | 23:00 | hrs | Rangpur | 1017 | 984 |  | 33
10 | Maximum Temperature in Dhaka was |  |  |  | 38.0°C |  |  | Total | 15532.81 | 15214.81 |  | 318
B. |  | 2024-05-24 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 38.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16376 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13500 | MW
4 | Reserve(Generation end) |  |  |  | 876 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 331.3429 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11969 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.344 | MKWHr. | ii) HVDC Flow at Peak Time |  | 640 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0266 | MKWHr. | iii) Maximum HVDC Flow : |  | 925 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.16 |  | (b) Today: | 71.99 |  | (c) Rule Curve: |  | 77.6
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-23 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 405 | 0 |  | 0 | 450 | 322 | 91 | 80 | 30 | 303 | 0 | 0 | 82 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 33 | 31 | 0 | 0 | 25 | 0 | 110 | 0 | 0 | 121 | 0 | 0 | 0 |  | 9 | 47 | 17 | 68 | 58 | 6 | 0 | 37 | 0 | 0 | 0 | 285 | 260 | 217 | 0 | 86 | 37 | 40 | 0 | 43 | 0 | 39 | 52 | 0 | 0 | 31 | 17 | 86 | 82 | 0 | 0 | 0 | 40 | 48 | 46 | 42 | 112 | 0 | 31 | 0 | 0 | 204 | 0 | 0 | 0 | 295 | 24 | 5 | 0 | 280 | 0 | 0 | 78 | 0 | 50 | 0 | 49 | 17 | 21 | 365 | 69 | 17 | 17 | 0 | 52 | 35 | 110 | 52 | 44 | 48 | 340 | 70 | 0 | 162 | 53 | 0 | 14 | 0 | 115 | 17 | 240 | 17 | 0 | 490 | 0 | 233 | 450 | 450 | 0 |  | 641 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 50 | 41 | 0 | 58 | 0 | 0 | 30 | 0 | 30 | 0 | 0 | 5 | 69 | 0 | 230 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 193 | 0 | 402 | 90 | 0 | 113 | 15 | 113 | 0 | 0 | 113 | 1000 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 482 | 0 | 307 | 765 | 0 | 0 |  | 8930 | 5765 | 14695 | 4442 | 641 | 2931 | 0 | 2667 | 3576 | 25 | 0 | 327 | 86 | 0 | 0 | 482.275 | 72.21
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 408 | 0 |  | 0 | 450 | 323 | 91 | 80 | 30 | 294 | 0 | 0 | 82 | 74 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 25 | 31 | 0 | 0 | 25 | 0 | 110 | 0 | 0 | 121 | 0 | 0 | 0 |  | 12 | 47 | 17 | 68 | 47 | 6 | 0 | 37 | 0 | 0 | 0 | 285 | 260 | 216 | 0 | 86 | 37 | 40 | 0 | 43 | 0 | 39 | 52 | 0 | 0 | 31 | 17 | 80 | 82 | 0 | 0 | 0 | 40 | 48 | 47 | 42 | 112 | 0 | 31 | 0 | 0 | 205 | 0 | 0 | 0 | 280 | 24 | 5 | 0 | 295 | 0 | 0 | 77 | 0 | 35 | 0 | 49 | 17 | 13 | 365 | 69 | 17 | 17 | 0 | 52 | 35 | 110 | 52 | 38 | 48 | 340 | 70 | 0 | 162 | 21 | 0 | 17 | 0 | 115 | 17 | 240 | 17 | 0 | 490 | 5 | 234 | 400 | 450 | 0 |  | 640 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 16 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 68 | 0 | 230 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 186 | 0 | 397 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 980 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 430 | 0 | 307 | 762 | 0 | 0 |  | 8777 | 5493 | 14270 | 4415 | 640 | 2862 | 0 | 2519 | 3501 | 25 | 0 | 223 | 80 | 0 | 5 | 315.15 | 72.2
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 407 | 0 |  | 0 | 450 | 323 | 85 | 75 | 30 | 300 | 0 | 0 | 75 | 82 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 25 | 31 | 0 | 0 | 25 | 0 | 110 | 0 | 0 | 121 | 0 | 0 | 0 |  | 12 | 47 | 17 | 12 | 45 | 6 | 0 | 37 | 0 | 0 | 0 | 285 | 260 | 217 | 0 | 85 | 37 | 40 | 0 | 43 | 0 | 39 | 52 | 0 | 0 | 31 | 17 | 82 | 83 | 0 | 0 | 0 | 40 | 48 | 47 | 42 | 112 | 0 | 32 | 0 | 0 | 206 | 0 | 0 | 0 | 285 | 24 | 5 | 0 | 250 | 0 | 0 | 77 | 0 | 35 | 0 | 49 | 17 | 11 | 365 | 69 | 17 | 17 | 0 | 52 | 35 | 110 | 52 | 39 | 48 | 340 | 70 | 0 | 162 | 17 | 0 | 17 | 0 | 115 | 17 | 240 | 17 | 0 | 490 | 3 | 233 | 400 | 400 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 70 | 0 | 230 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 188 | 0 | 387 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 930 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 381 | 0 | 250 | 767 | 0 | 0 |  | 8621 | 5351 | 13972 | 4429 | 925 | 2808 | 0 | 2126 | 3351 | 25 | 0 | 223 | 82 | 0 | 3 | 313.24 | 72.19
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 407 | 0 |  | 0 | 450 | 320 | 20 | 37 | 30 | 270 | 0 | 0 | 24 | 82 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 25 | 31 | 0 | 0 | 25 | 0 | 110 | 0 | 0 | 122 | 0 | 0 | 0 |  | 12 | 47 | 17 | 12 | 46 | 6 | 0 | 37 | 0 | 0 | 0 | 295 | 260 | 214 | 0 | 85 | 37 | 40 | 0 | 43 | 0 | 39 | 52 | 0 | 0 | 31 | 17 | 76 | 83 | 0 | 0 | 0 | 40 | 48 | 47 | 42 | 112 | 0 | 32 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 24 | 5 | 0 | 95 | 0 | 0 | 77 | 0 | 35 | 0 | 49 | 17 | 13 | 368 | 69 | 17 | 17 | 0 | 52 | 17 | 110 | 52 | 39 | 48 | 340 | 70 | 0 | 162 | 17 | 0 | 17 | 0 | 115 | 17 | 240 | 17 | 0 | 490 | 1 | 234 | 400 | 400 | 0 |  | 925 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 230 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 186 | 0 | 349 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 380 | 0 | 250 | 764 | 0 | 0 |  | 8274 | 5134 | 13408 | 4414 | 925 | 2772 | 0 | 1658 | 3344 | 25 | 0 | 193 | 76 | 0 | 1 | 278.86 | 72.18
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 408 | 0 |  | 0 | 450 | 324 | 17 | 34 | 30 | 256 | 0 | 0 | 17 | 82 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 25 | 31 | 0 | 0 | 25 | 0 | 111 | 0 | 0 | 122 | 0 | 0 | 0 |  | 12 | 47 | 17 | 12 | 45 | 6 | 0 | 34 | 0 | 0 | 0 | 285 | 260 | 218 | 0 | 85 | 37 | 40 | 0 | 43 | 0 | 39 | 52 | 0 | 0 | 31 | 17 | 78 | 86 | 0 | 0 | 0 | 40 | 48 | 47 | 42 | 112 | 0 | 32 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 24 | 5 | 0 | 95 | 0 | 0 | 77 | 0 | 35 | 0 | 49 | 17 | 13 | 366 | 70 | 17 | 17 | 0 | 52 | 17 | 110 | 52 | 39 | 48 | 340 | 70 | 0 | 162 | 17 | 0 | 17 | 0 | 115 | 17 | 240 | 17 | 0 | 482 | 0 | 232 | 400 | 400 | 0 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 170 | 0 | 307 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 380 | 0 | 250 | 768 | 0 | 0 |  | 8236 | 5065 | 13301 | 4355 | 925 | 2731 | 0 | 1645 | 3349 | 25 | 0 | 193 | 78 | 0 | 0 | 237.795 | 72.17
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 358 | 0 |  | 0 | 450 | 324 | 0 | 16 | 30 | 257 | 0 | 0 | 0 | 82 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 25 | 31 | 0 | 0 | 25 | 0 | 107 | 0 | 0 | 122 | 0 | 0 | 0 |  | 12 | 47 | 17 | 0 | 28 | 0 | 0 | 34 | 0 | 0 | 0 | 285 | 260 | 215 | 0 | 85 | 37 | 43 | 0 | 10 | 0 | 39 | 51 | 0 | 0 | 31 | 17 | 60 | 87 | 0 | 0 | 0 | 40 | 48 | 47 | 42 | 112 | 0 | 31 | 0 | 0 | 207 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 77 | 0 | 34 | 1 | 49 | 17 | 13 | 307 | 70 | 17 | 17 | 0 | 52 | 0 | 85 | 52 | 38 | 48 | 310 | 70 | 2 | 126 | 17 | 0 | 17 | 2 | 115 | 17 | 400 | 17 | 0 | 480 | 0 | 234 | 400 | 400 | 5 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 16 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 161 | 0 | 306 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 180 | 0 | 0 | 0 | 9 | 35 | 0 | 0 | 381 | 3 | 250 | 724 | 12 | 0 |  | 7932 | 4823 | 12755 | 4300 | 925 | 2650 | 0 | 1382 | 3186 | 25 | 0 | 193 | 60 | 34 | 0 | 186.225 | 72.16
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 352 | 0 |  | 0 | 450 | 318 | 0 | 0 | 30 | 270 | 0 | 0 | 0 | 74 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 0 | 25 | 6 | 3 | 0 | 25 | 0 | 109 | 0 | 0 | 122 | 0 | 0 | 0 |  | 12 | 47 | 17 | 0 | 12 | 0 | 0 | 24 | 0 | 0 | 0 | 300 | 285 | 196 | 0 | 85 | 37 | 49 | 0 | 10 | 0 | 39 | 16 | 0 | 0 | 31 | 17 | 70 | 71 | 0 | 0 | 0 | 40 | 48 | 47 | 42 | 112 | 0 | 31 | 0 | 0 | 206 | 0 | 0 | 0 | 290 | 24 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 35 | 5 | 49 | 60 | 11 | 308 | 49 | 17 | 17 | 2 | 52 | 0 | 68 | 52 | 32 | 48 | 310 | 70 | 14 | 126 | 17 | 0 | 17 | 8 | 115 | 17 | 270 | 17 | 0 | 470 | 0 | 234 | 400 | 400 | 18 |  | 925 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 230 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 166 | 0 | 347 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 800 | 180 | 0 | 0 | 0 | 24 | 35 | 0 | 0 | 383 | 9 | 250 | 724 | 48 | 0 |  | 7683 | 4926 | 12609 | 4168 | 925 | 2690 | 0 | 1252 | 3157 | 25 | 0 | 193 | 70 | 129 | 0 | 182.405 | 72.15
8:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 352 | 0 |  | 0 | 450 | 321 | 0 | 0 | 30 | 287 | 0 | 0 | 0 | 82 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 0 | 25 | 32 | 8 | 0 | 25 | 0 | 105 | 0 | 0 | 122 | 0 | 0 | 0 |  | 12 | 47 | 17 | 0 | 12 | 0 | 0 | 9 | 0 | 0 | 0 | 285 | 265 | 198 | 0 | 85 | 36 | 49 | 0 | 10 | 0 | 39 | 16 | 0 | 0 | 31 | 17 | 80 | 67 | 0 | 0 | 1 | 42 | 48 | 47 | 42 | 112 | 0 | 30 | 0 | 0 | 205 | 0 | 0 | 0 | 280 | 24 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 36 | 10 | 49 | 68 | 13 | 306 | 49 | 17 | 17 | 3 | 50 | 0 | 68 | 52 | 38 | 48 | 310 | 70 | 25 | 126 | 17 | 0 | 17 | 15 | 109 | 17 | 270 | 17 | 0 | 460 | 0 | 236 | 400 | 400 | 36 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 110 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66 | 0 | 230 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 163 | 0 | 298 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 780 | 180 | 0 | 0 | 2 | 53 | 35 | 0 | 0 | 381 | 15 | 250 | 727 | 95 | 0 |  | 7726 | 5014 | 12740 | 4145 | 925 | 2617 | 0 | 1368 | 3130 | 25 | 0 | 193 | 80 | 257 | 0 | 219.65 | 72.14
9:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 353 | 0 |  | 0 | 450 | 315 | 0 | 0 | 30 | 299 | 0 | 0 | 0 | 82 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 10 | 0 | 0 | 32 | 8 | 0 | 25 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 47 | 17 | 0 | 12 | 0 | 0 | 3 | 0 | 0 | 0 | 335 | 250 | 195 | 0 | 86 | 36 | 47 | 0 | 10 | 0 | 38 | 16 | 0 | 0 | 31 | 17 | 86 | 62 | 0 | 0 | 2 | 39 | 48 | 47 | 42 | 80 | 0 | 54 | 0 | 0 | 202 | 0 | 0 | 0 | 305 | 24 | 5 | 0 | 0 | 0 | 0 | 58 | 0 | 36 | 14 | 49 | 68 | 13 | 340 | 49 | 17 | 17 | 4 | 50 | 0 | 74 | 52 | 38 | 48 | 369 | 70 | 28 | 126 | 17 | 0 | 17 | 21 | 104 | 17 | 250 | 17 | 0 | 460 | 0 | 233 | 350 | 350 | 51 |  | 925 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 110 | 0 | 0 | 50 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 176 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 780 | 220 | 0 | 0 | 3 | 76 | 40 | 0 | 0 | 381 | 22 | 250 | 726 | 137 | 0 |  | 7615 | 5307 | 12922 | 4248 | 925 | 2600 | 0 | 1357 | 3127 | 25 | 0 | 192 | 86 | 362 | 0 | 217.74 | 72.13
10:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 392 | 0 |  | 0 | 450 | 318 | 3 | 10 | 30 | 304 | 0 | 0 | 8 | 82 | 32 | 0 | 0 | 0 | 0 | 22 | 55 | 35 | 0 | 17 | 23 | 25 | 30 | 8 | 0 | 25 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 47 | 17 | 25 | 19 | 0 | 0 | 2 | 0 | 0 | 0 | 290 | 250 | 217 | 0 | 85 | 32 | 45 | 0 | 15 | 0 | 38 | 16 | 0 | 0 | 30 | 17 | 86 | 60 | 0 | 0 | 2 | 36 | 48 | 44 | 42 | 112 | 0 | 55 | 0 | 0 | 201 | 0 | 0 | 0 | 310 | 24 | 5 | 0 | 2 | 0 | 0 | 58 | 0 | 60 | 17 | 49 | 68 | 13 | 395 | 48 | 17 | 34 | 4 | 51 | 15 | 101 | 52 | 37 | 48 | 345 | 70 | 44 | 162 | 17 | 0 | 17 | 28 | 91 | 17 | 250 | 54 | 0 | 460 | 0 | 234 | 300 | 300 | 63 |  | 925 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 110 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 192 | 0 | 384 | 0 | 0 | 7 | 0 | 29 | 0 | 7 | 50 | 700 | 220 | 0 | 0 | 4 | 91 | 72 | 0 | 0 | 383 | 28 | 250 | 755 | 175 | 0 |  | 7874 | 5450 | 13324 | 4337 | 925 | 2561 | 0 | 1620 | 3079 | 25 | 0 | 228 | 86 | 463 | 0 | 263.58 | 72.12
11:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 315 | 27 | 70 | 30 | 307 | 0 | 0 | 38 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 23 | 25 | 29 | 8 | 0 | 25 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 48 | 17 | 56 | 40 | 6 | 0 | 2 | 0 | 0 | 0 | 295 | 250 | 211 | 0 | 85 | 30 | 45 | 0 | 43 | 0 | 44 | 16 | 0 | 0 | 30 | 17 | 88 | 60 | 0 | 0 | 2 | 36 | 48 | 44 | 41 | 80 | 0 | 40 | 0 | 0 | 201 | 0 | 0 | 0 | 285 | 24 | 5 | 0 | 90 | 0 | 0 | 58 | 0 | 139 | 18 | 49 | 74 | 11 | 404 | 48 | 17 | 34 | 5 | 51 | 35 | 92 | 52 | 36 | 56 | 345 | 70 | 49 | 162 | 17 | 0 | 17 | 29 | 90 | 17 | 250 | 54 | 0 | 460 | 0 | 235 | 300 | 300 | 54 |  | 925 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 110 | 0 | 0 | 50 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 184 | 0 | 414 | 0 | 0 | 70 | 0 | 50 | 0 | 7 | 70 | 680 | 220 | 0 | 0 | 4 | 98 | 110 | 0 | 0 | 379 | 33 | 250 | 758 | 189 | 0 |  | 8252 | 5617 | 13869 | 4323 | 925 | 2558 | 0 | 2154 | 3059 | 25 | 0 | 249 | 88 | 488 | 0 | 201.505 | 72.11
12:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 398 | 0 |  | 0 | 450 | 315 | 64 | 80 | 30 | 306 | 0 | 0 | 70 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 23 | 33 | 29 | 8 | 0 | 25 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 45 | 17 | 58 | 44 | 6 | 0 | 5 | 0 | 0 | 0 | 300 | 250 | 211 | 0 | 85 | 30 | 43 | 0 | 43 | 0 | 37 | 16 | 0 | 0 | 24 | 17 | 92 | 60 | 0 | 0 | 2 | 38 | 48 | 44 | 41 | 112 | 0 | 54 | 0 | 0 | 200 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 100 | 0 | 0 | 58 | 0 | 149 | 19 | 49 | 104 | 12 | 380 | 48 | 17 | 34 | 5 | 50 | 35 | 99 | 52 | 37 | 48 | 360 | 70 | 48 | 162 | 17 | 0 | 17 | 29 | 88 | 17 | 250 | 54 | 0 | 460 | 0 | 232 | 350 | 300 | 45 |  | 925 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 7 | 110 | 0 | 0 | 50 | 37 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 192 | 0 | 397 | 0 | 0 | 73 | 0 | 50 | 0 | 7 | 70 | 700 | 220 | 0 | 0 | 4 | 100 | 115 | 0 | 0 | 378 | 29 | 250 | 762 | 201 | 0 |  | 8475 | 5691 | 14166 | 4370 | 925 | 2639 | 0 | 2295 | 3079 | 25 | 0 | 252 | 92 | 489 | 0 | 223.47 | 72.11
13:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 398 | 0 |  | 0 | 450 | 315 | 71 | 80 | 30 | 309 | 0 | 0 | 75 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 0 | 33 | 29 | 8 | 0 | 25 | 0 | 105 | 0 | 1 | 0 | 0 | 0 | 0 |  | 12 | 38 | 17 | 58 | 44 | 6 | 0 | 10 | 0 | 0 | 0 | 285 | 250 | 210 | 8 | 85 | 31 | 42 | 0 | 43 | 0 | 41 | 16 | 0 | 0 | 24 | 17 | 90 | 60 | 0 | 0 | 2 | 36 | 48 | 43 | 40 | 112 | 0 | 54 | 0 | 0 | 200 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 115 | 0 | 0 | 65 | 0 | 145 | 18 | 49 | 103 | 12 | 405 | 48 | 17 | 34 | 4 | 51 | 35 | 110 | 52 | 38 | 48 | 345 | 70 | 27 | 162 | 23 | 0 | 17 | 28 | 77 | 17 | 270 | 54 | 0 | 460 | 8 | 233 | 350 | 300 | 68 |  | 924 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 8 | 110 | 0 | 0 | 50 | 37 | 0 | 40 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 195 | 0 | 414 | 0 | 0 | 113 | 0 | 100 | 0 | 7 | 113 | 700 | 220 | 0 | 0 | 4 | 98 | 115 | 0 | 0 | 379 | 30 | 250 | 760 | 169 | 0 |  | 8521 | 5838 | 14359 | 4327 | 924 | 2667 | 0 | 2474 | 3079 | 25 | 0 | 310 | 90 | 455 | 8 | 612 | 72.1
14:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 399 | 0 |  | 0 | 450 | 310 | 74 | 80 | 30 | 306 | 0 | 0 | 75 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 23 | 33 | 29 | 8 | 0 | 25 | 0 | 105 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 45 | 17 | 46 | 43 | 6 | 0 | 6 | 0 | 0 | 0 | 290 | 250 | 209 | 8 | 85 | 31 | 39 | 0 | 43 | 0 | 42 | 16 | 0 | 0 | 24 | 17 | 94 | 60 | 0 | 0 | 2 | 36 | 48 | 43 | 40 | 112 | 0 | 54 | 0 | 0 | 199 | 0 | 0 | 0 | 295 | 16 | 5 | 0 | 180 | 0 | 0 | 57 | 0 | 87 | 16 | 49 | 103 | 12 | 398 | 47 | 17 | 34 | 4 | 51 | 35 | 110 | 51 | 42 | 48 | 345 | 70 | 21 | 162 | 22 | 0 | 17 | 25 | 67 | 17 | 270 | 54 | 0 | 480 | 11 | 233 | 350 | 350 | 62 |  | 925 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 110 | 0 | 0 | 50 | 37 | 0 | 30 | 28 | 0 | 37 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 190 | 0 | 414 | 0 | 0 | 113 | 0 | 95 | 0 | 7 | 113 | 700 | 220 | 0 | 0 | 1 | 89 | 115 | 0 | 0 | 380 | 28 | 250 | 756 | 168 | 0 |  | 8576 | 5818 | 14394 | 4325 | 925 | 2701 | 0 | 2484 | 3096 | 25 | 0 | 310 | 94 | 423 | 11 | 674.23 | 72.11
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 394 | 0 |  | 0 | 450 | 305 | 74 | 80 | 30 | 300 | 0 | 0 | 75 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 23 | 33 | 29 | 8 | 0 | 25 | 0 | 105 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 45 | 17 | 44 | 43 | 6 | 0 | 2 | 0 | 0 | 0 | 315 | 250 | 201 | 8 | 85 | 31 | 38 | 0 | 43 | 0 | 42 | 16 | 0 | 0 | 23 | 17 | 96 | 60 | 0 | 0 | 2 | 38 | 47 | 44 | 36 | 112 | 0 | 52 | 0 | 0 | 194 | 0 | 0 | 0 | 315 | 16 | 5 | 0 | 220 | 0 | 0 | 57 | 0 | 67 | 13 | 49 | 103 | 10 | 369 | 47 | 17 | 34 | 3 | 52 | 35 | 110 | 51 | 36 | 48 | 349 | 70 | 31 | 162 | 17 | 0 | 17 | 19 | 68 | 17 | 270 | 17 | 0 | 490 | 9 | 232 | 390 | 370 | 49 |  | 923 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 128 | 9 | 110 | 0 | 0 | 50 | 38 | 0 | 32 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 198 | 0 | 414 | 0 | 0 | 113 | 0 | 94 | 0 | 6 | 113 | 730 | 220 | 0 | 0 | 1 | 80 | 112 | 0 | 0 | 377 | 22 | 250 | 769 | 141 | 0 |  | 8583 | 5865 | 14448 | 4351 | 923 | 2768 | 0 | 2502 | 3133 | 25 | 0 | 274 | 96 | 367 | 9 | 765.91 | 72.09
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 395 | 0 |  | 0 | 450 | 310 | 78 | 80 | 30 | 300 | 0 | 0 | 75 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 16 | 23 | 33 | 24 | 8 | 0 | 0 | 0 | 105 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 45 | 34 | 44 | 23 | 6 | 0 | 2 | 0 | 0 | 0 | 285 | 250 | 185 | 8 | 86 | 31 | 35 | 0 | 43 | 0 | 42 | 16 | 0 | 0 | 23 | 17 | 94 | 60 | 0 | 0 | 1 | 38 | 47 | 43 | 40 | 112 | 0 | 53 | 0 | 0 | 197 | 0 | 0 | 0 | 290 | 24 | 5 | 0 | 225 | 0 | 0 | 57 | 0 | 67 | 8 | 49 | 103 | 12 | 368 | 47 | 17 | 68 | 2 | 51 | 35 | 110 | 51 | 36 | 48 | 345 | 70 | 22 | 162 | 17 | 0 | 17 | 13 | 68 | 17 | 270 | 17 | 0 | 485 | 7 | 233 | 360 | 370 | 21 |  | 923 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 128 | 9 | 16 | 0 | 0 | 45 | 38 | 0 | 40 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 189 | 0 | 382 | 0 | 0 | 113 | 0 | 95 | 0 | 4 | 113 | 920 | 220 | 0 | 0 | 1 | 40 | 115 | 0 | 0 | 434 | 15 | 270 | 768 | 95 | 0 |  | 8448 | 5872 | 14320 | 4256 | 923 | 2686 | 0 | 2444 | 3394 | 0 | 0 | 294 | 94 | 222 | 7 | 802.2 | 72.09
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 312 | 84 | 80 | 44 | 300 | 0 | 0 | 78 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 23 | 30 | 28 | 8 | 0 | 25 | 0 | 105 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 38 | 34 | 44 | 45 | 6 | 0 | 2 | 0 | 0 | 0 | 285 | 250 | 185 | 8 | 85 | 32 | 36 | 0 | 43 | 0 | 42 | 18 | 0 | 0 | 23 | 17 | 90 | 67 | 0 | 0 | 0 | 36 | 48 | 46 | 40 | 112 | 0 | 54 | 0 | 0 | 198 | 0 | 0 | 0 | 275 | 24 | 5 | 0 | 204 | 0 | 0 | 57 | 0 | 69 | 4 | 62 | 103 | 10 | 368 | 47 | 17 | 68 | 1 | 51 | 35 | 110 | 51 | 38 | 48 | 345 | 54 | 9 | 162 | 17 | 0 | 17 | 6 | 68 | 17 | 270 | 17 | 0 | 485 | 4 | 232 | 360 | 340 | 13 |  | 923 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 7 | 16 | 0 | 0 | 45 | 38 | 0 | 40 | 35 | 0 | 28 | 0 | 10 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 185 | 0 | 374 | 0 | 0 | 113 | 0 | 101 | 0 | 3 | 113 | 960 | 220 | 0 | 0 | 0 | 11 | 115 | 0 | 0 | 435 | 7 | 270 | 764 | 47 | 0 |  | 8444 | 5820 | 14264 | 4264 | 923 | 2637 | 0 | 2495 | 3430 | 25 | 0 | 295 | 90 | 101 | 4 | 702.88 | 72.08
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 388 | 0 |  | 0 | 450 | 310 | 90 | 80 | 55 | 301 | 0 | 0 | 83 | 90 | 145 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 17 | 23 | 30 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 9 | 0 | 0 | 0 | 0 |  | 12 | 54 | 34 | 12 | 46 | 18 | 0 | 2 | 0 | 0 | 0 | 290 | 250 | 207 | 8 | 85 | 32 | 36 | 0 | 43 | 0 | 42 | 33 | 0 | 0 | 23 | 17 | 88 | 67 | 0 | 0 | 0 | 38 | 48 | 49 | 40 | 112 | 0 | 54 | 0 | 0 | 198 | 0 | 0 | 0 | 270 | 24 | 5 | 0 | 230 | 0 | 0 | 57 | 0 | 69 | 0 | 62 | 103 | 17 | 368 | 47 | 17 | 68 | 0 | 51 | 35 | 110 | 52 | 72 | 48 | 345 | 58 | 2 | 162 | 17 | 0 | 27 | 1 | 81 | 17 | 270 | 17 | 0 | 485 | 8 | 233 | 320 | 260 | 2 |  | 923 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 16 | 0 | 0 | 45 | 31 | 0 | 40 | 14 | 0 | 28 | 0 | 20 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 185 | 0 | 348 | 0 | 0 | 35 | 0 | 102 | 0 | 1 | 35 | 860 | 220 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 398 | 1 | 208 | 678 | 10 | 0 |  | 8499 | 5223 | 13722 | 4278 | 923 | 2487 | 0 | 2339 | 3146 | 25 | 0 | 411 | 88 | 17 | 8 | 456 | 72.08
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 398 | 0 |  | 0 | 450 | 310 | 97 | 80 | 55 | 305 | 0 | 0 | 83 | 90 | 150 | 8 | 0 | 0 | 0 | 20 | 55 | 55 | 0 | 17 | 23 | 30 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 62 | 17 | 30 | 56 | 19 | 0 | 2 | 0 | 0 | 0 | 290 | 260 | 209 | 8 | 85 | 32 | 37 | 0 | 43 | 0 | 42 | 50 | 0 | 0 | 23 | 17 | 100 | 66 | 0 | 0 | 0 | 38 | 48 | 49 | 41 | 112 | 0 | 55 | 0 | 0 | 201 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 250 | 0 | 0 | 104 | 0 | 90 | 0 | 62 | 133 | 43 | 368 | 96 | 50 | 68 | 0 | 51 | 35 | 110 | 52 | 73 | 60 | 345 | 70 | 0 | 162 | 47 | 0 | 35 | 0 | 101 | 17 | 320 | 163 | 0 | 486 | 0 | 232 | 440 | 450 | 0 |  | 923 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 32 | 22 | 0 | 130 | 10 | 16 | 0 | 0 | 40 | 41 | 0 | 88 | 18 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 41 | 0 | 102 | 0 | 0 | 75 | 870 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 458 | 0 | 244 | 762 | 0 | 0 |  | 9450 | 5704 | 15154 | 4411 | 923 | 2898 | 0 | 2794 | 3336 | 25 | 0 | 667 | 100 | 0 | 0 | 425.93 | 72.06
19:30 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 317 | 98 | 80 | 55 | 305 | 0 | 0 | 83 | 90 | 149 | 14 | 0 | 0 | 0 | 27 | 55 | 55 | 0 | 17 | 23 | 30 | 28 | 8 | 0 | 25 | 0 | 106 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 62 | 17 | 36 | 56 | 19 | 0 | 2 | 0 | 0 | 0 | 310 | 270 | 211 | 8 | 85 | 30 | 37 | 0 | 43 | 0 | 42 | 50 | 0 | 0 | 23 | 17 | 84 | 66 | 0 | 0 | 0 | 36 | 48 | 49 | 41 | 112 | 0 | 55 | 0 | 0 | 201 | 0 | 0 | 0 | 280 | 24 | 5 | 0 | 260 | 0 | 0 | 105 | 0 | 135 | 0 | 62 | 136 | 55 | 367 | 97 | 50 | 68 | 0 | 51 | 35 | 110 | 52 | 73 | 60 | 345 | 71 | 0 | 162 | 53 | 0 | 35 | 0 | 109 | 17 | 330 | 163 | 0 | 485 | 0 | 233 | 500 | 500 | 0 |  | 922 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 41 | 43 | 0 | 130 | 10 | 16 | 0 | 0 | 40 | 38 | 0 | 88 | 35 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 187 | 0 | 414 | 20 | 0 | 95 | 0 | 98 | 0 | 0 | 113 | 1020 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 540 | 0 | 280 | 763 | 0 | 0 |  | 9684 | 6093 | 15777 | 4402 | 922 | 2995 | 0 | 3051 | 3605 | 25 | 0 | 693 | 84 | 0 | 0 | 308.465 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 316 | 96 | 80 | 55 | 302 | 0 | 0 | 83 | 90 | 149 | 14 | 0 | 0 | 0 | 47 | 55 | 55 | 0 | 18 | 23 | 30 | 28 | 8 | 0 | 25 | 0 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 62 | 34 | 38 | 58 | 19 | 0 | 12 | 0 | 0 | 0 | 310 | 270 | 211 | 8 | 85 | 30 | 38 | 0 | 43 | 0 | 43 | 50 | 0 | 0 | 24 | 17 | 84 | 66 | 0 | 0 | 0 | 37 | 48 | 49 | 41 | 112 | 0 | 55 | 0 | 0 | 201 | 0 | 0 | 0 | 275 | 24 | 5 | 0 | 264 | 0 | 0 | 106 | 0 | 131 | 0 | 62 | 138 | 53 | 367 | 99 | 50 | 68 | 0 | 51 | 35 | 110 | 52 | 73 | 60 | 345 | 70 | 0 | 162 | 53 | 0 | 35 | 0 | 107 | 23 | 310 | 163 | 0 | 485 | 0 | 234 | 500 | 500 | 0 |  | 640 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 31 | 70 | 40 | 130 | 10 | 16 | 0 | 0 | 40 | 41 | 0 | 88 | 35 | 0 | 46 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 185 | 0 | 414 | 53 | 0 | 105 | 0 | 105 | 0 | 0 | 113 | 1040 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 516 | 0 | 280 | 769 | 0 | 0 |  | 9719 | 5938 | 15657 | 4382 | 640 | 3000 | 0 | 3169 | 3608 | 25 | 0 | 749 | 84 | 0 | 0 | 327.565 | 72.07
21:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 319 | 98 | 80 | 55 | 304 | 0 | 0 | 83 | 90 | 149 | 14 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 33 | 28 | 8 | 0 | 25 | 0 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 62 | 60 | 40 | 58 | 30 | 0 | 18 | 0 | 0 | 0 | 310 | 270 | 193 | 8 | 85 | 35 | 43 | 0 | 43 | 0 | 44 | 50 | 0 | 0 | 24 | 17 | 84 | 70 | 0 | 0 | 0 | 37 | 48 | 49 | 42 | 112 | 0 | 55 | 0 | 0 | 202 | 0 | 0 | 0 | 305 | 24 | 5 | 0 | 290 | 0 | 0 | 106 | 0 | 149 | 0 | 86 | 138 | 53 | 367 | 98 | 105 | 85 | 0 | 50 | 35 | 110 | 52 | 83 | 94 | 345 | 70 | 0 | 162 | 63 | 0 | 35 | 0 | 111 | 35 | 260 | 163 | 0 | 487 | 1 | 233 | 500 | 500 | 0 |  | 640 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 31 | 55 | 40 | 130 | 10 | 16 | 0 | 0 | 40 | 39 | 0 | 90 | 35 | 0 | 39 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 215 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 194 | 0 | 414 | 53 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1130 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 560 | 0 | 307 | 766 | 0 | 0 |  | 9970 | 6097 | 16067 | 4347 | 640 | 3045 | 0 | 3408 | 3763 | 25 | 0 | 754 | 84 | 0 | 1 | 318 | 72.06
22:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 361 | 0 |  | 0 | 450 | 316 | 95 | 80 | 55 | 305 | 0 | 0 | 83 | 90 | 149 | 14 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 25 | 28 | 8 | 0 | 25 | 0 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 62 | 51 | 42 | 63 | 22 | 0 | 19 | 0 | 0 | 0 | 340 | 300 | 186 | 8 | 85 | 35 | 45 | 0 | 43 | 0 | 44 | 50 | 0 | 0 | 24 | 17 | 88 | 70 | 0 | 0 | 0 | 40 | 48 | 49 | 42 | 112 | 0 | 55 | 0 | 0 | 202 | 0 | 0 | 0 | 285 | 24 | 5 | 0 | 300 | 0 | 0 | 106 | 0 | 149 | 0 | 86 | 138 | 55 | 390 | 98 | 105 | 85 | 0 | 50 | 35 | 110 | 52 | 83 | 96 | 369 | 70 | 0 | 162 | 87 | 0 | 35 | 0 | 113 | 17 | 230 | 17 | 0 | 487 | 0 | 234 | 500 | 400 | 0 |  | 639 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 31 | 40 | 40 | 130 | 10 | 16 | 0 | 0 | 50 | 39 | 0 | 90 | 35 | 0 | 35 | 0 | 22 | 0 | 0 | 0 | 65 | 0 | 200 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 191 | 0 | 414 | 53 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 565 | 0 | 307 | 765 | 0 | 0 |  | 9733 | 5990 | 15723 | 4172 | 639 | 2925 | 0 | 3427 | 3867 | 25 | 0 | 580 | 88 | 0 | 0 | 303 | 0
23:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 400 | 0 |  | 0 | 450 | 320 | 90 | 80 | 55 | 302 | 0 | 0 | 83 | 90 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 25 | 30 | 0 | 0 | 25 | 0 | 105 | 0 | 10 | 0 | 0 | 0 | 0 |  | 12 | 70 | 51 | 44 | 63 | 19 | 0 | 12 | 0 | 0 | 0 | 300 | 270 | 194 | 8 | 85 | 35 | 46 | 0 | 43 | 0 | 45 | 50 | 0 | 0 | 24 | 17 | 90 | 71 | 0 | 0 | 0 | 38 | 48 | 49 | 42 | 112 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 290 | 24 | 3 | 0 | 273 | 0 | 0 | 106 | 0 | 107 | 0 | 49 | 138 | 56 | 367 | 98 | 52 | 85 | 0 | 50 | 35 | 110 | 52 | 84 | 71 | 345 | 70 | 0 | 162 | 55 | 0 | 35 | 0 | 114 | 17 | 230 | 17 | 0 | 490 | 10 | 234 | 500 | 450 | 0 |  | 639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 44 | 40 | 130 | 10 | 48 | 0 | 0 | 50 | 39 | 0 | 90 | 35 | 0 | 35 | 0 | 22 | 0 | 0 | 0 | 66 | 0 | 200 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 193 | 0 | 325 | 84 | 0 | 113 | 32 | 107 | 0 | 0 | 113 | 1200 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 602 | 0 | 307 | 771 | 0 | 0 |  | 9438 | 5853 | 15291 | 3960 | 639 | 2889 | 0 | 3266 | 3870 | 25 | 0 | 542 | 90 | 0 | 10 | 534 | 0
24:00 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 402 | 0 |  | 0 | 450 | 318 | 98 | 80 | 55 | 300 | 0 | 0 | 83 | 90 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 25 | 30 | 0 | 0 | 25 | 0 | 110 | 0 | 8 | 0 | 0 | 0 | 0 |  | 12 | 70 | 51 | 56 | 64 | 6 | 0 | 27 | 0 | 0 | 0 | 300 | 270 | 195 | 8 | 85 | 35 | 46 | 0 | 43 | 0 | 45 | 43 | 0 | 0 | 24 | 17 | 74 | 70 | 0 | 0 | 0 | 40 | 48 | 49 | 42 | 112 | 0 | 56 | 0 | 0 | 201 | 0 | 0 | 0 | 285 | 24 | 3 | 0 | 253 | 0 | 0 | 106 | 0 | 73 | 0 | 49 | 138 | 51 | 380 | 98 | 17 | 34 | 0 | 52 | 35 | 110 | 52 | 84 | 48 | 371 | 70 | 0 | 162 | 53 | 0 | 35 | 0 | 114 | 17 | 230 | 17 | 0 | 490 | 9 | 233 | 500 | 450 | 0 |  | 639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 50 | 40 | 130 | 10 | 48 | 0 | 0 | 50 | 39 | 0 | 77 | 35 | 0 | 35 | 0 | 22 | 0 | 0 | 0 | 66 | 0 | 230 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 185 | 0 | 347 | 91 | 0 | 113 | 32 | 107 | 0 | 0 | 113 | 1160 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 759 | 0 | 0 |  | 9300 | 5857 | 15157 | 3986 | 639 | 2918 | 0 | 3104 | 3867 | 25 | 0 | 535 | 74 | 0 | 9 | 471 | 0
KWH | 0 | 0 | 0 | 4299750 | 0 | 282272 | 0 | 9439200 | 0 |  | 0 | 10321000 | 7411520 | 1441920 | 1356191 | 939976 | 7113276 | 0 | 0 | 1263360 | 2034432 | 1565280 | 42000 | 0 | 0 | 0 | 1116360 | 1321934 | 1196303 | 0 | 42300 | 452880 | 624000 | 670500 | 132960 | 0 | 589200 | 0 | 2400000 | 0 | 158061 | 1146036 | 0 | 0 | 0 |  | 293520 | 1204992 | 576801 | 776640 | 1021440 | 197760 | 0 | 366720 | 0 | 0 | 0 | 7537600 | 6420000 | 4968000 | 100364 | 2018200 | 809064 | 1000800 | 0 | 814179 | 0 | 981584 | 819403 | 0 | 0 | 657800 | 410960 | 2026560 | 1604160 | 0 | 0 | 15150 | 913000 | 1153200 | 1117200 | 981000 | 2472709 | 0 | 1084704 | 0 | 0 | 5078240 | 0 | 0 | 0 | 7159000 | 524016 | 116928 | 0 | 4215273 | 0 | 0 | 1780800 | 0 | 1888128 | 142290 | 1300800 | 2002080 | 546981 | 8835000 | 1560000 | 663360 | 980218 | 36117 | 1252036 | 716851 | 2543371 | 1275660 | 1204560 | 1283520 | 8191800 | 1620480 | 358780 | 3784320 | 727636 | 0 | 534240 | 218609 | 2382720 | 464760 | 6463500 | 981890 | 0 | 11498180 | 67200 | 5672727 | 9633636 | 9085909 | 498263 |  | 20344000 | 0 | 7953984 | 0 | 0 | 0 | 0 | 0 | 160320 | 242944 | 216375 | 2880000 | 215789 | 1203840 | 0 | 0 | 1150000 | 927923 | 0 | 795872 | 324620 | 0 | 393904 | 0 | 236097 | 0 | 0 | 88812 | 1485381 | 0 | 5483000 | 0 | 0 | 0 | 0 | 4581818 | 0 | 0 | 0 | 4703664 | 0 | 9077890 | 536160 | 0 | 1732608 | 60192 | 1606828 | 0 | 58095 | 1717632 | 23566800 | 5126073 | 0 | 0 | 30540 | 796320 | 2185152 | 0 | 0 | 10392730 | 241265 | 6392700 | 18086545 | 1473690 | 0 |  | 206994100 | 136469563 | 343463663 | 104332392 | 20344000 | 65166061 | 0 | 56423461 | 82578063 | 589200 | 0 | 8067607 | 2026560 | 3869119 | 67200 | 0
Fuel Cost | 0 | 0 | 0 | 19133887.5 | 0 | 1078279.04 | 0 | 27184896 | 0 |  | 0 | 32820780 | 25347398.4 | 28492339.2 | 25360771.7 | 16562377.12 | 21695491.8 | 0 | 0 | 24963993.6 | 36518054.4 | 30397737.6 | 783300 | 0 | 0 | 0 | 20384733.6 | 20833679.84 | 21880381.87 | 0 | 31725 | 0 | 0 | 0 | 2381313.6 | 0 | 0 | 0 | 13104000 | 0 | 2993675.34 | 3655854.84 | 0 | 0 | 0 |  | 5163016.8 | 21219909.12 | 10330505.91 | 14802758.4 | 19989580.8 | 3255129.6 | 0 | 0 | 0 | 0 | 0 | 21029904 | 19645200 | 16493760 | 336219.4 | 6518786 | 2726545.68 | 4383504 | 0 | 3264857.79 | 0 | 17580169.44 | 14798418.18 | 0 | 0 | 2447016 | 308220 | 13294233.6 | 4988937.6 | 0 | 0 | 0 | 3560700 | 4301436 | 5083260 | 4463550 | 8456664.78 | 0 | 6020107.2 | 0 | 0 | 14168289.6 | 0 | 0 | 0 | 22121310 | 393012 | 88865.28 | 0 | 85991569.2 | 0 | 0 | 34209168 | 0 | 33249934.08 | 0 | 23167248 | 34736088 | 9068944.98 | 23412750 | 29733600 | 12444633.6 | 17585110.92 | 0 | 20470788.6 | 13935583.44 | 45628075.74 | 24377862.6 | 23380509.6 | 22859491.2 | 21790188 | 27661593.6 | 0 | 69215212.8 | 12209732.08 | 0 | 9546868.8 | 0 | 42936614.4 | 7873034.4 | 19196595 | 13825011.2 | 0 | 80142314.6 | 0 | 33469089.3 | 0 | 0 | 0 |  | 57166640 | 0 | 23464252.8 | 0 | 0 | 0 | 0 | 0 | 3015619.2 | 4569776.64 | 3851475 | 9100800 | 1022839.86 | 20754201.6 | 0 | 0 | 5612000 | 16619100.93 | 0 | 13378608.32 | 6907913.6 | 0 | 7054820.64 | 0 | 4228497.27 | 0 | 0 | 67230.684 | 16383752.43 | 0 | 46276520 | 0 | 0 | 0 | 0 | 15257453.94 | 0 | 0 | 0 | 15663201.12 | 0 | 26507438.8 | 9157612.8 | 0 | 34340290.56 | 1064194.56 | 32008013.76 | 0 | 0 | 34077818.88 | 152712864 | 15942087.03 | 0 | 0 | 0 | 0 | 37912387.2 | 0 | 0 | 75866929 | 0 | 47625615 | 119552062.45 | 0 | 0 |  | 1438956149.77 | 857162018.074 | 2296118167.844 | 321061106.044 | 57166640 | 150828189.1 | 0 | 1039519096.05 | 572029146.78 | 0 | 0 | 142219756.27 | 13294233.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 398 | 0 |  | 0 | 450 | 315 | 64 | 80 | 30 | 306 | 0 | 0 | 70 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 17 | 23 | 33 | 29 | 8 | 0 | 25 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 45 | 17 | 58 | 44 | 6 | 0 | 5 | 0 | 0 | 0 | 300 | 250 | 211 | 0 | 85 | 30 | 43 | 0 | 43 | 0 | 37 | 16 | 0 | 0 | 24 | 17 | 92 | 60 | 0 | 0 | 2 | 38 | 48 | 44 | 41 | 112 | 0 | 54 | 0 | 0 | 200 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 100 | 0 | 0 | 58 | 0 | 149 | 19 | 49 | 104 | 12 | 380 | 48 | 17 | 34 | 5 | 50 | 35 | 99 | 52 | 37 | 48 | 360 | 70 | 48 | 162 | 17 | 0 | 17 | 29 | 88 | 17 | 250 | 54 | 0 | 460 | 0 | 232 | 350 | 300 | 45 |  | 925 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 7 | 110 | 0 | 0 | 50 | 37 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 230 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 192 | 0 | 397 | 0 | 0 | 73 | 0 | 50 | 0 | 7 | 70 | 700 | 220 | 0 | 0 | 4 | 100 | 115 | 0 | 0 | 378 | 29 | 250 | 762 | 201 | 0 |  | 14166 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 319 | 98 | 80 | 55 | 304 | 0 | 0 | 83 | 90 | 149 | 14 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 33 | 28 | 8 | 0 | 25 | 0 | 110 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 62 | 60 | 40 | 58 | 30 | 0 | 18 | 0 | 0 | 0 | 310 | 270 | 193 | 8 | 85 | 35 | 43 | 0 | 43 | 0 | 44 | 50 | 0 | 0 | 24 | 17 | 84 | 70 | 0 | 0 | 0 | 37 | 48 | 49 | 42 | 112 | 0 | 55 | 0 | 0 | 202 | 0 | 0 | 0 | 305 | 24 | 5 | 0 | 290 | 0 | 0 | 106 | 0 | 149 | 0 | 86 | 138 | 53 | 367 | 98 | 105 | 85 | 0 | 50 | 35 | 110 | 52 | 83 | 94 | 345 | 70 | 0 | 162 | 63 | 0 | 35 | 0 | 111 | 35 | 260 | 163 | 0 | 487 | 1 | 233 | 500 | 500 | 0 |  | 640 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 31 | 55 | 40 | 130 | 10 | 16 | 0 | 0 | 40 | 39 | 0 | 90 | 35 | 0 | 39 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 215 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 194 | 0 | 414 | 53 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1130 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 560 | 0 | 307 | 766 | 0 | 0 |  | 16067 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 400 | 0 |  | 0 | 450 | 320 | 100 | 80 | 55 | 335 | 0 | 0 | 90 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 23 | 33 | 33 | 8 | 0 | 0 | 30 | 110 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 64 | 85 | 70 | 60 | 20 | 0 | 20 | 0 | 0 | 0 | 300 | 280 | 220 | 0 | 0 | 36 | 50 | 0 | 43 | 0 | 40 | 52 | 0 | 0 | 32 | 20 | 151 | 80 | 0 | 0 | 0 | 42 | 60 | 50 | 42 | 112 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 105 | 0 | 149 | 0 | 62 | 200 | 50 | 400 | 100 | 52 | 51 | 0 | 52 | 35 | 110 | 114 | 75 | 60 | 360 | 72 | 0 | 162 | 53 | 0 | 50 | 0 | 115 | 35 | 280 | 163 | 0 | 490 | 40 | 235 | 500 | 500 |  |  | 655 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 42 | 62 | 0 | 130 | 10 | 110 | 0 | 0 | 50 | 42 | 25 | 81 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 11 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 190 | 0 | 414 | 90 | 0 | 113 | 100 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 540 | 0 | 307 | 760 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 400 | 0 | 0 | 0 | 450 | 320 | 90 | 80 | 40 | 310 | 0 | 0 | 85 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 23 | 33 | 33 | 8 | 0 | 0 | 30 | 110 | 0 | 8 | 0 |  | 0 | 0 | 0 | 12 | 55 | 51 | 70 | 45 | 6 | 0 | 20 | 0 | 0 | 0 | 300 | 270 | 210 | 0 | 0 | 35 | 50 | 0 | 43 | 0 | 39 | 25 | 0 | 0 | 32 | 20 | 146 | 45 | 0 | 0 | 1.6 | 42 | 60 | 50 | 42 | 112 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 58 | 0 | 149 | 20 | 49 | 100 | 12 | 400 | 57 | 17 | 34 | 5 | 52 | 35 | 51 | 52 | 36 | 48 | 345 | 53 | 50 | 162 | 35 | 0 | 50 | 35 | 115 | 17 | 250 | 54 | 0 | 490 | 40 | 235 | 400 | 400 | 33 |  | 944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 90 | 10 | 110 | 0 | 0 | 50 | 40 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 11 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 180 | 0 | 350 | 53 | 0 | 50 | 0 | 50 | 0 | 8 | 50 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 400 | 30 | 250 | 760 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 395 | 0 | 0 | 0 | 340 | 321 | 17 | 17 | 40 | 290 | 0 | 0 | 18 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 16 | 23 | 25 | 32 | 8 | 0 | 0 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 24 | 17 | 12 | 12 | 6 | 0 | 25 | 0 | 0 | 0 | 290 | 250 | 210 | 0 | 0 | 34 | 50 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 24 | 0 | 72 | 46 | 0 | 0 | 1 | 42 | 48 | 49 | 42 | 80 | 0 | 61 | 0 | 0 | 203 | 0 | 0 | 0 | 260 | 24 | 5 | 0 | 45 | 0 | 0 | 57 | 0 | 34 | 10 | 24 | 68 | 12 | 366 | 49 | 17 | 34 | 0 | 51 | 0 | 51 | 52 | 38 | 36 | 345 | 53 | 24 | 72 | 20 | 0 | 17 | 15 | 55 | 17 | 230 | 17 | 0 | 449 | 0 | 234 | 350 | 350 | 37 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 220 | 0 | 0 | 82 | 0 | 175 | 0 | 0 | 0 | 150 | 0 | 320 | 17 | 0 | 35 | 0 | 35 | 0 | 3 | 0 | 700 | 180 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 380 | 15 | 200 | 831 | 98 | 0 | 0 |  |  |  | 169498453 | 20344000 | 0 | 82578063 | 64491068 | 2026560 | 3869119 | 67200 | 589200 |  |  | 343463663
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 169.4985 | 20.344 | 0 | 82.5781 | 64.4911 | 2.0266 | 3.8691 | 0.0672 | 0.5892
| Minimum Generation |  | 12609 | 7:00
| Highest Generation |  | 16067 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 343.4637
| Day Peak Generation |  | 14166 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 16067 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 925 | 3:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 640 | 21:00
| Load factor L.F |  | 89.07% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-24
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 14166 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11969
Evening Peak Generation : |  |  | 16067 | MW Hour : | 21:00 | Available Max Generation : |  | 16376
E.P. Demand (at gen end) : |  |  | 16400 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15500
Maximum Generation : |  |  | 16067 | MW Hour : | 21:00 | Reserve(Generation end) |  | 876
Total Gen. (MKWH) : |  |  | 343.4637 | System Load Factor : | 89.07% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 238 | MW at | 23:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-24
Actual : |  | 71.99 | Ft.(MSL) , | Rule curve : | 77.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1242.27 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 471889295.144
: |  |  | Coal : | 572029146.78 | Oil : | 1181738852.32 | Total : | 2225657294.244
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 100 | 2400:00 | 5342.4914 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | 0%
Cumilla Area |  | 35 | 840:00 | 1476.7776 |  |  | 0 | 0%
Mymensingh Area |  | 150 | 3600:00 | 1099.0436 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | 0%
Rangpur Area |  | 33 | 792:00 | 1004.2252 |  |  | 0 | 0%
Total |  | 318 |  | 15383.887 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:16 |  | Aminbazar 400/230/132kV S/S 132 kv Bus 01 Scheduled S/D
| 08:37 | Ramganj 132/33kV S/S Transformer -02 HT is restored.
| 08:37 | Ramganj 132/33kV S/S Transformer -02 LT is restored.
08:45 |  | Sikalbaha 225MW CCPP Tripped.
09:15 | 20:08 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Maintenance work by EGCB .
09:29 | 17:25 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-2 Scheduled S/D Due to Project Work.
10:55 | 22:07 | Khulna(S) 230/132kV S/S 230 KV Main Bus 1 Project Work S/D .
11:08 | 12:20 | Mithapukur 132/33kV S/S BUS SECTION-1 (33KV) Forced S/D Due to Maintenance work.
11:10 | 12:54 | Haripur-Sonargaon 132kV Ckt-1 Scheduled S/D from Sonargaon 132/33kV end Due to Corrective maintenance of R
phase CT and from Haripur 230/132kV end Due to Another side by NLDC.
11:10 | 12:25 | Mithapukur 132/33kV S/S TR-1(404T) LT Forced S/D Due to Maintenance work.
11:13 | 12:24 | Mithapukur 132/33kV S/S TR-1(404T) HT Forced S/D Due to Maintenance work.
| 12:41 | Bhaluka 132/33kV S/S BR Powergen Ckt- 02 is restored.
14:55 | 16:23 | Gopalganj 400/132kV S/S ATR-01 HT Project Work S/D
14:55 | 16:23 | Gopalganj 400/132kV S/S ATR-01 LT Project Work S/D
16:20 |  | Kurigram 132/33kV S/S Capacitor Bank Tripped showing Unbalance Current Relay(SPAJ-160C), Trip Relay(MVAJ-2). Relays.
16:26 | 16:59 | Gopalganj 400/132kV S/S ATR-02 HT Project Work S/D
16:26 | 16:59 | Gopalganj 400/132kV S/S ATR-02 LT Project Work S/D
17:16 | 17:35 | Gopalganj 400/132kV S/S ATR-03 LT Project Work S/D
17:16 | 17:35 | Gopalganj 400/132kV S/S ATR-03 HT Project Work S/D
| 17:57 | Ishurdi 132/33kV S/S 132 kV Baghabari Line is restored.
| 18:04 | Fatullah-Madanganj 132 kV Ckt-2 is restored.
| 18:04 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt is restored.
22:21 | 23:38 | Chauddagram 132/33kV S/S 132 kv T-1 LT Forced S/D Due to Red hot in 33 Kv incomer breaker DS. | [5 empty] | 40 MW load interrup.
| 22:25 | Sirajgonj Unit-1 GT was sync.
22:29 |  | Bheramara 410 MW ST was shutdown.
22:29 |  | Bheramara 410 MW CCPP Shutdown with remarks:- ST
22:32 |  | Bheramara 410 MW GT was shutdown.
22:32 |  | Bheramara 410 MW CCPP Shutdown with remarks:- GT
22:33 | 23:38 | Chauddagram 132/33kV S/S 132 kv T-1 HT Forced S/D Due to 33 kV DS Red Hot.
23:06 |  | Khulna South S/S - Rupsha P/S (NWPGCL-800 MW) 230 kv ckt-1 charge From Khulna South S/S.
23:34 | 00:28 | Sirajganj 132/33kV S/S Sherpur-2 Tripped showing Distance Relay C phase, CB1 A/R Fail. relays.
| 23:37 | Adani Power Jharkhand Ltd. Unit-1 was sync.
23:45 | 00:27 | Sirajganj 132/33kV S/S Sherpur-1 Tripped showing Distance Relay C phase, AIDED Trip, CB1 A/R lockout relays.
02:38 | 07:34 | Rampura 230/132kV S/S Auto Transformer - 04 HT Tripped showing ATR4-1+R panel : SIPROTEC 7UT86 - a) General Trip ,
b) Phase- A,B,C Trip, c) 87T Diff>Trip, d) 33kV protection : TV-50/51 relays Due to Due to Auxillary transformer fault.
02:38 | 07:35 | Rampura 230/132kV S/S Auto Transformer - 04 LT Tripped showing No relays Due to Due to auxillary transformer fault.
05:29 |  | Rampur 230/132/33 S/S Khulshi-1 Scheduled S/D Due to Khulshi grid busbar maintenance work.
05:29 |  | Rampur 230/132/33 S/S Khulshi-2 Scheduled S/D Due to Khulshi grid busbar maintenance work.
05:34 |  | AKSML-Khulshi 132kV Ckt-1 Project Work S/D from AKS 132/33kV end Due to project works for Khulshi S/S demand.
05:43 |  | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Scheduled S/D Due to Due to bus shutdown at khulshi s/s end .
05:54 |  | Sirajganj 132/33kV S/S Main Bus Project Work S/D Due to 68 MW Soler new 132kv bus is connected 132 KV main bus. | [5 empty] | 100 MW load interrup.
05:57 | 06:15 | AKSML-Baroaulia 132kV Ckt-1 Tripped from AKS 132/33kV end showing no relay operates relays Due to CB Tripped by | [5 empty] | 1 MW load interrup in
|  | Baroawlia end. AKSPL End no tripping. | [5 empty] | AKS 132/33 kV end.
05:58 |  | Bakulia-Khulshi 132 kV Ckt-1 Project Work S/D from Bakulia 132/33kV end Due to 132kV Bus Shutdown at Khulshi Grid SS.
06:24 |  | Juldah-Shahmirpur 132kV Ckt-2 Project Work S/D from Juldah 132/33kV end Due to shahmirpur bud S/D.
06:25 |  | Juldah-Shahmirpur 132kV Ckt-1 Project Work S/D from Juldah 132/33kV end Due to shahmirpur bus S/D.
06:28 |  | Shahmirpur-Sikalbaha 132kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end.
06:48 |  | Shahmirpur 132/33kV S/S Bus-1 Project Work S/D Due to Breaker change of Sikalbaha Ckt-1 by GTG project work. | [5 empty] | 45 MW load interrup.
06:49 |  | Baghabari-Sirajganj 230 kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to RNPP project work.
07:01 |  | Baghabari-Sirajganj 230 kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to RNPP project work.
07:05 |  | Bogura(New)-Naogaon 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end. and from Naogaon 132/33kV end Due to Project
work.
07:41 |  | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D Due to new tower erection.
06:41 |  | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from
Shikalbaha 230/132kV end Due to Bus-Shut down at Shahmirpur
End.
06:47 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from
Kaliakoir 400/230/132kV end Due to BY NLDC
06:48 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from
Kaliakoir 400/230/132kV end Due to By NLDC
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4299750
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 282272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 401 | 9439200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10321000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 98 | 1441920
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 319 | 7411520
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 80 | 1356191 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 939976
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 14 | 42000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 83 | 1263360 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 304 | 7113276 | DP high
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 2034432 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1116360
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1565280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1321934
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1196303
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 495180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 624000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 670500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 132960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 290 | 4215273
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1888128
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 663360
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1620480 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3784320
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 218609
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 464760 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 500 | 9633636
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 500 | 9085909
| Dhaka area Total |  |  |  | 5332 | 4320 | 84641889
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 110 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 158061
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 142290
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 197760 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 589200 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 1146036
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 980218 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 62 | 1204992 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 60 | 576801 | Fuel consevation
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 40 | 776640 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 86 | 1300800 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 366720
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 58 | 1021440 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36117
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 1252036 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 716851 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2543371
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 94 | 1283520 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 63 | 727636 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 981890
60 | SS Power I |  | SS Power | 2*612 | 1224 | 487 | 11498180
| Cox's Bazar Wind |  | IPP | 66 | 60 | 1 | 67200 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 233 | 5672727
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 498263
| Chattogram area Total |  |  |  | 4404 | 1835 | 36138749
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 193 | 4968000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7537600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6420000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 260 | 6463500 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 809064 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 43 | 1000800 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 100364 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 814179 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 53 | 546981 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 44 | 981584 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2018200 | ST Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 138 | 2002080 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 84 | 2026560
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 24 | 657800 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 50 | 819403
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 410960 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1275660 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 83 | 1204560 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 534240 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 111 | 2382720
| Cumilla Area Total |  |  |  | 2929 | 1938 | 42974255
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 70 | 1604160 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15150
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 106 | 1780800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 98 | 1560000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 358780
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293520 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 286 | 5612410
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 37 | 913000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 48 | 1153200 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2472709 | ST Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1117200
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 981000 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 116928 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1084704
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 202 | 5078240 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 524016
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7159000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8835000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8191800 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1591 | 37626797
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 640 | 20344000
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 0 | 0
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 160320 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 55 | 242944 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 7953984 | FGMO
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 40 | 216375 | Contract Expired
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 536160 | Megnghat bus section limitation.
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 60192 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 796320
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 560 | 10392730
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1719 | 40703025
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 1203840 | Megnghat bus section limitation.
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 215789
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2880000 | Engine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1130 | 23566800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5126073
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Megnghat bus section limitation.
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6392700
| Barisal Area Total |  |  |  | 2235 | 1813 | 39385202
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 40 | 1150000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 39 | 927923 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 324620
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 393904 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 194 | 4581818
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 194 | 4703664 | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9077890
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 236097 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 88812 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 795872 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1732608
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1717632
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30540
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 766 | 18086545
| Rajshahi Area Total |  |  |  | 3431 | 2064 | 43847925
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 65 | 1485381
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 215 | 5483000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1606828 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 58095
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2185152
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 241265
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1473690
| Rangpur Area Total |  |  |  | 950 | 501 | 12533411
| Total |  |  |  | 25903 | 16067 | 343463663
| Eastern Grid Total |  |  |  | 15588 | 9970 | 206994100
| Western Grid Total |  |  |  | 10315 | 6097 | 136469563
| National Grid Total |  |  |  | 25903 | 16067 | 343463663
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-23
| (a) ENTIRE EASTERN GRID : |  | 10241.61 | MW | (b) ENTIRE WESTERN GRID : |  | 4973.2 | MW
| i) Dhaka area |  | 5452.11 | MW | i) Khulna area |  | 1897.4 | MW
| ii) Chittagong area |  | 1522.5 | MW | ii) Rajshahi area |  | 1621.6 | MW
| iii) Comilla area |  | 1483 | MW | iii) Barisal area |  | 470.2 | MW
| iv) Mymensingh area |  | 1117 | MW | iv) Rangpur area |  | 984 | MW
| v) Sylhet area |  | 667 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 15214.81 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 8 | 06:00 | Chhatak | 39 | 22:00 | Kalurghat | 40 | 12:00 | Narail | 62 | 23:00 | Shariatpur | 96 | 23:00
2 | AKSML | 119 | 15:00 | Chowmuhani | 242 | 22:00 | Kamrangirchar | 59.4 | 19:00 | Narinda | 50 | 13:00 | Sherpur | 140 | 19:00
3 | Aftabnagar | 44 | 13:00 | Chuadanga | 112 | 19:00 | Kaptai | N/A | N/A | Narshingdi | 175 | 03:00 | Shikalbaha | 30 | 19:00
4 | Agargaon | 121 | 13:00 | Coxsbazar | 137 | 20:00 | Kazla | 116 | 19:30 | Natore | 168 | 21:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 84 | 16:00 | Cumilla(N) | 205 | 20:00 | Keranigonj | 86 | 16:00 | Nawabganj | 52 | 19:00 | Shitalakhya | 114.5 | 16:00
6 | Amnura | 69 | 22:00 | Cumilla(S) | 182 | 15:00 | Khagrachori | 38 | 19:00 | Netrakona | 122 | 19:30 | Sholosohor | 48 | 23:00
7 | Ashuganj | 94 | 22:00 | Daudkandi | 175 | 21:00 | Khulna | 101 | 20:00 | New | 60 | 12:00 | Shyampur | 186 | 11:00
8 | BIPTC | N/A | N/A | Dhaka | 54 | 13:00 | Khulshi | 187 | 11:00 | Niamatpur | 81 | 23:00 | Siddhirganj | 114 | 00:00
9 | BSRM | 174 | 02:00 | Dhamrai | 134 | 20:00 | Kishoreganj | 142 | 01:00 | Noapara | 53 | 20:00 | Sirajganj | 122 | 23:00
10 | Bagerhat | 99 | 00:00 | Dhanmondi | 174 | 13:00 | Kodda | 272 | 19:00 | PHP | 3 | 09:00 | Sonargaon | 108 | 12:00
11 | Bakulia | 115 | 21:00 | Dohazari | 104 | 19:00 | Kulaura | 58 | 23:00 | Pabna | 134 | 20:00 | Sreemongol | 83 | 21:00
12 | Banani | 55.4 | 12:00 | Faridpur | 174 | 22:00 | Kurigram | 64 | 19:30 | Palashbari | 122 | 19:00 | Sreepur | 65 | 14:00
13 | Bangabhaban | 17 | 10:00 | Fatullah | 67 | 23:00 | Kushtia | 160 | 19:30 | Panchagarh | 54 | 22:00 | Srinagar | 53.9 | 23:00
14 | Barapukuria | 69 | 21:00 | Fenchuganj | 47 | 22:00 | Lalbag | 105 | 13:00 | Patuakhali | 91 | 01:00 | Sunamganj | 62 | 01:00
15 | Barguna | 22 | 00:00 | Feni | 125 | 22:00 | Lalmonirhat | 58 | 19:00 | Payra | 36 | 21:00 | Sylhet | 48 | 15:00
16 | Barishal | 119 | 20:00 | GPH | 87 | 00:00 | MI_Cement | 11.1 | 13:00 | Postogola | 64 | 19:00 | Sylhet-132 | 141 | 17:00
17 | Barishal-230 | 112 | 23:00 | Ghatail | 42 | 19:00 | Madanganj | 46 | 23:00 | Purbachal | 25 | 15:00 | TK | 35.5 | 21:00
18 | Baroaulia | 72 | 13:00 | Ghorashal | 72 | 20:00 | Madaripur | 126 | 22:00 | Purbasadipur | 143 | 21:00 | Tangail | 214 | 21:00
19 | Baroirhat | 68 | 02:00 | Goalpara | 28 | 01:00 | Madartek | 96.97 | 00:00 | Rahim | 46 | 12:00 | Thakurgaon | 103 | 22:00
20 | Bashundhara | 230 | 16:00 | Gollamari | 86 | 00:00 | Madunaghat | 66 | 21:00 | Rajbari | 80 | 20:00 | Tongi | 139 | 12:00
21 | BashundharaCement | 1 | 01:00 | Gopalganj | 121.6 | 23:00 | Magura | 70 | 21:00 | Rajendrapur | 124 | 22:00 | Ullahpara | 33 | 23:00
22 | Beanibazar | 82 | 19:00 | Gulshan | 134 | 15:00 | Mahasthangarh | 84 | 19:30 | Rajshahi | 161 | 21:00 | Ullon | 64 | 21:00
23 | Benapole | 64 | 20:00 | Halishahar | 88.5 | 12:00 | Manikganj | 143 | 19:00 | Rajshahi-230 | 61 | 23:00 | Uttara | 82 | 13:00
24 | Bhaluka | 124 | 22:00 | HaripurSBU | 187 | 15:00 | Maniknagar | 88 | 12:00 | Ramganj | 120 | 20:00 | UttaraNew | 37 | 23:00
25 | Bhandaria | 56 | 23:00 | Hasnabad | 117 | 23:00 | Matarbari | 52 | 23:00 | Rampur | 46 | 23:00 | Zigatola | 98 | 15:00
26 | Bhangura | 45 | 20:00 | Hathazari | 93 | 21:00 | Matuail | 85 | 00:00 | Rangamati | 20 | 19:00
27 | Bheramara(GK) | 72 | 21:00 | Ishurdi | 89 | 21:00 | Millgate | 131 | 16:00 | Rangpur | 142 | 21:00
28 | Bhulta | 249 | 14:00 | Jaldhaka | 82 | 21:00 | Mirpur | 162 | 16:00 | Ruppur | 7 | 11:00
29 | Bog-Sherpur | 68 | 21:00 | Jamalpur | 121 | 22:00 | Mirsorai | 5 | 00:00 | SSM | 16 | 00:00
30 | Bogura | 176 | 20:00 | Jashore | 153 | 14:00 | Mirzapur | 42 | 22:00 | Saidpur | 118 | 21:00
31 | Borhanuddin | 87 | 21:00 | Jhenaidah | 140 | 19:30 | Mithapukur | 60 | 19:00 | Satkhira | 143 | 00:00
32 | Brahmanbaria | 175 | 03:00 | Joydebpur | 188 | 21:00 | Modern | 0 | 00:00 | Satmasjid | 137 | 13:00
33 | Cantonment | 174 | 13:00 | Joypurhat | 68 | 21:00 | Mogbazar | 149.1 | 15:00 | Savar | 213 | 10:00
34 | Chandpur | 80 | 20:00 | Juldah | 21 | 14:00 | Mongla | 33 | 10:00 | SevenRings | 20.89 | 19:00
35 | Chandraghona | 40 | 19:30 | KSRM | 30 | 13:00 | Motijheel | 53 | 13:00 | ShahCement | 19 | 00:00
36 | Chapai | 73 | 21:00 | Kabirpur | 286 | 11:00 | Munshiganj | 124 | 00:00 | Shahjadpur | 83 | 23:00
37 | Charsaidpur | 40 | 11:00 | Kachua | 89 | 21:00 | Mymensingh | 243 | 23:00 | Shahjibazar | 152 | 23:00
38 | Chauddagram | 82 | 19:00 | Kallyanpur | 126 | 00:00 | Naogaon | 145 | 21:00 | Shahmirpur | 61 | 03:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 397 | 06:00 | 380 | 15:00 | Kaliakoir | 379 | 18:00 | 364 | 09:00
| Ashuganj | 410 | 8:00 | 394 | 16:00 | Madunaghat_I | 412 | 23:00 | 379 | 15:00
| Bhulta | 402 | 05:00 | 383 | 12:00 | Meghnaghat | 393 | 03:00 | 382 | 13:00
| Bibiana | 400 | 05:00 | 390 | 17:00 | Payra | 410 | 06:00 | 402 | 22:00
| BIPTC | 405 | 01:00 | 392 | 15:00 | Rahanpur | 402 | 02:00 | 390 | 21:00
| Bogura | 400 | 02:00 | 387 | 19:30 | Rampal | 403 | 08:00 | 0.4 | 05:00
| Gopalganj | 402 | 05:00 | 390 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 02:00 | 218 | 11:00 | Hasnabad | 230 | 23:00 | 220 | 11:00
| AKSML | 235 | 21:00 | 216 | 09:00 | Hathazari | 238 | 23:00 | 217 | 09:00
| Aminbazar | 227 | 01:00 | 218 | 09:00 | Ishurdi | 235 | 02:00 | 225 | 13:00
| Ashuganj | 235 | 23:00 | 225 | 12:00 | Jhenaidah | 226 | 08:00 | 213 | 19:30
| Ashuganj-400 | 232 | 2:00 | 210 | 13:00 | Kaliakoir | 230 | 01:00 | 219 | 09:00
| Baghabari | 230 | 00:00 | 224 | 12:00 | Keranigonj | 228 | 06:00 | 218 | 11:00
| Barapukuria | 218 | 14:00 | 206 | 21:00 | Khulna(S) | 229 | 08:00 | 217 | 19:00
| Barapukuria-230 | 218 | 9:00 | 210 | 22:00 | Madunaghat_I | 240 | 23:00 | 218 | 15:00
| Barishal | 242 | 08:00 | 229 | 19:00 | Maniknagar | 229 | 02:00 | 219 | 12:00
| Bheramara | 234 | 01:00 | 223 | 13:00 | Meghnaghat | 239 | 03:00 | 230 | 09:00
| Bhulta | 231 | 02:00 | 219 | 12:00 | Meghnaghat-400 | 234 | 23:00 | 213 | 02:00
| Bibiana | 230 | 06:00 | 222 | 15:00 | Mirsorai | 234 | 21:00 | 214 | 16:00
| BIPTC | 235 | 01:00 | 223 | 13:00 | Rajshahi | 232 | 01:00 | 222 | 15:00
| Bogura | 220 | 01:00 | 213 | 19:30 | Rampal | 230 | 08:00 | 217 | 19:30
| Bogura-400 | 221 | 02:00 | 212 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 09:00 | 236 | 00:00 | Rampura | 229 | 04:00 | 216 | 12:00
| BSRM | 239 | 23:00 | 218 | 09:00 | Shikalbaha | 238 | 21:00 | 218 | 16:00
| Cumilla(N) | 234 | 23:00 | 221 | 09:00 | Shyampur | 230 | 02:00 | 220 | 11:00
| Fenchuganj | 234 | 07:00 | 228 | 12:00 | Siddhirganj | 232 | 03:00 | 220 | 09:00
| Ghorashal | 235 | 01:00 | 230 | 11:00 | Sirajgonj | 236 | 01:00 | 231 | 12:00
| Ghorashal-230 | 230 | 02:00 | 217 | 12:00 | Sreepur | 229 | 06:00 | 220 | 12:00
| GPH | 240 | 23:00 | 217 | 09:00 | Tongi | 228 | 04:00 | 214 | 11:00
| Haripur | 230 | 07:00 | 219 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 06:00 | 124 | 11:00 | Kushtia | 133 | 06:00 | 125 | 23:00
| Agargaon | 138 | 06:00 | 129 | 11:00 | Lalbag | 132 | 02:00 | 125 | 11:00
| Agrabad | 137 | 23:00 | 123 | 16:00 | Lalmonirhat | 129 | 10:00 | 117 | 21:00
| AKS | 136 | 23:00 | 123 | 09:00 | Madanganj | 134 | 21:00 | 127 | 09:00
| Aminbazar | 131 | 04:00 | 124 | 11:00 | Madaripur | 130 | 05:00 | 126 | 16:00
| Amnura | 138 | 20:00 | 124 | 22:00 | Madartek | 133 | 02:00 | 123 | 11:00
| Ashuganj | 139 | 18:30 | 135 | 10:00 | Madunaghat | 138 | 23:00 | 123 | 15:00
| Bagerhat | 130 | 06:00 | 115 | 19:00 | Magura | 133 | 05:00 | 124 | 19:00
| Bakulia | 140 | 23:00 | 125 | 09:00 | Mahasthangarh | 131 | 02:00 | 124 | 21:00
| Banani | 133 | 05:00 | 123 | 12:00 | Manikganj | 132 | 20:00 | 121 | 09:00
| Bangabhaban | 133 | 01:00 | 124 | 15:00 | Maniknagar | 134 | 02:00 | 125 | 11:00
| Barapukuria | 136 | 14:00 | 124 | 21:00 | Matarbari | 134 | 04:00 | 112 | 09:00
| Barguna | 133 | 09:00 | 125 | 00:00 | Matuail | 133 | 23:00 | 126.8 | 12:00
| Barishal | 138 | 08:00 | 121 | 00:00 | Millgate | 134 | 01:00 | 122 | 11:00
| Barishal-230 | 138 | 08:00 | 128 | 19:00 | Mirpur | 130 | 05:00 | 121 | 12:00
| Baroaulia | 137 | 23:00 | 124 | 15:00 | Mirzapur | 131 | 23:00 | 123 | 09:00
| Baroirhat | 137 | 23:00 | 120 | 15:00 | Mithapukur | 131 | 13:00 | 120 | 22:00
| Bashundhara | 134 | 02:00 | 122 | 12:00 | MI_Cement | 135 | 23:00 | 128 | 09:00
| BashundharaCement | 134 | 00:00 | 127 | 09:00 | Modern | 135 | 23:00 | 125 | 11:00
| Beanibazar | 126 | 08:00 | 121 | 00:00 | Mogbazar | 134 | 02:00 | 124 | 12:00
| Benapole | 132 | 05:00 | 119 | 13:00 | Mongla | 128 | 06:00 | 117 | 19:00
| Bhaluka | 126 | 23:00 | 118 | 12:00 | Motijheel | 133 | 01:00 | 124 | 15:00
| Bhandaria | 130 | 09:00 | 115 | 00:00 | Munshiganj | 134 | 21:00 | 127 | 09:00
| Bhangura | 134 | 05:00 | 130 | 19:00 | Mymensingh | 134 | 23:00 | 115 | 13:00
| Bheramara | 135 | 01:00 | 127 | 23:00 | Naogaon | 128 | 13:00 | 121 | 19:30
| Bheramara(GK) | 135 | 03:00 | 127 | 23:00 | Narail | 134 | 08:00 | 122 | 19:30
| Bhulta | 126 | 07:00 | 119 | 12:00 | Narinda | 134 | 2:00 | 125 | 11:00
| Bog-Sherpur | 132 | 01:00 | 127 | 07:00 | Narshingdi | 127 | 08:00 | 117 | 10:00
| Bogura | 134 | 14:00 | 128 | 04:00 | Natore | 132 | 01:00 | 126 | 19:30
| Bogura-230 | 133 | 01:00 | 128 | 19:30 | Nawabganj | 133 | 06:00 | 126 | 10:00
| Brahmanbaria | 127 | 06:00 | 123 | 11:00 | Netrakona | 132 | 23:00 | 122 | 20:00
| Cantonment | 137 | 02:00 | 128 | 11:00 | New | 136 | 17:00 | 123 | 11:00
| Chandpur | 138 | 23:00 | 123 | 03:00 | Niamatpur | 134 | 02:00 | 129 | 21:00
| Chandraghona | 136 | 21:00 | 124 | 09:00 | Noapara | 133 | 08:00 | 122 | 19:30
| Chapai | 132 | 06:00 | 126 | 21:00 | Pabna | 134 | 02:00 | 128 | 19:30
| Charsaidpur | 134 | 00:00 | 127 | 12:00 | Palashbari | 129 | 13:00 | 118 | 19:00
| Chauddagram | 135 | 23:00 | 121 | 11:00 | Panchagarh | 136 | 10:00 | 110 | 19:00
| Chhatak | 128 | 05:00 | 123 | 00:00 | Patuakhali | 133 | 18:00 | 126 | 22:00
| Chowmuhani | 133 | 23:00 | 117 | 01:00 | Payra | 134 | 06:00 | 131 | 21:00
| Chuadanga | 128 | 08:00 | 114 | 19:00 | PHP | 136 | 23:00 | 119 | 16:00
| Coxsbazar | 120 | 21:00 | 112 | 14:00 | Postogola | 135 | 23:00 | 127 | 09:00
| Cumilla(N) | 138 | 23:00 | 127 | 15:00 | Purbachal | 133 | 01:00 | 122 | 11:00
| Cumilla(S) | 138 | 23:00 | 125 | 12:00 | Purbasadipur | 132 | 13:00 | 115 | 21:00
| Daudkandi | 128 | 23:00 | 119 | 10:00 | Rahanpur | 136 | 02:00 | 131 | 22:00
| Dhaka | 134 | 05:00 | 124 | 11:00 | Rahim | 134 | 04:00 | 127 | 12:00
| Dhamrai | 132 | 23:00 | 124 | 09:00 | Rajbari | 130 | 06:00 | 123 | 23:00
| Dhanmondi | 133.5 | 04:00 | 125 | 12:00 | Rajendrapur | 132 | 18:30 | 123 | 09:00
| Dohazari | 132 | 21:00 | 121 | 08:00 | Rajshahi | 132 | 01:00 | 127 | 19:00
| Faridpur | 130 | 05:00 | 125 | 13:00 | Rajshahi-230 | 133 | 01:00 | 121 | 21:00
| Fatullah | 134 | 21:00 | 127 | 11:00 | Ramganj | 134 | 23:00 | 117 | 02:00
| Fenchuganj | 132 | 07:00 | 129 | 01:00 | Rampur | 136 | 23:00 | 123 | 09:00
| Feni | 135 | 23:00 | 120 | 01:00 | Rampura | 133 | 04:00 | 123 | 12:00
| Ghatail | 132 | 23:00 | 124 | 08:00 | Rangamati | 138 | 23:00 | 123 | 09:00
| Ghorashal | 137 | 01:00 | 130 | 10:00 | Rangpur | 132 | 13:00 | 118 | 21:00
| Goalpara | 135 | 08:00 | 125 | 13:00 | Ruppur | 135 | 03:00 | 130 | 19:00
| Gollamari | 134 | 07:00 | 126 | 19:30 | Saidpur | 132 | 14:00 | 116 | 21:00
| Gopalganj | 131 | 08:00 | 124 | 19:00 | Satkhira | 130 | 08:00 | 118 | 19:30
| Gopalganj-400 | 131 | 05:00 | 126 | 15:00 | Satmasjid | 137 | 05:00 | 128 | 12:00
| Gulshan | 133 | 05:00 | 123 | 12:00 | Savar | 132 | 04:00 | 123 | 11:00
| Halishahar | 138 | 23:00 | 124 | 09:00 | SevenRings | 137 | 02:00 | 129 | 12:00
| Haripur | 134 | 03:00 | 127 | 12:00 | ShahCement | 134 | 00:00 | 127 | 12:00
| HaripurSBU | 134 | 04:00 | 127 | 12:00 | Shahjadpur | 137 | 00:00 | 135 | 03:00
| Hasnabad | 134 | 21:00 | 128 | 10:00 | Shahjibazar | 128 | 06:00 | 122 | 00:00
| Hathazari | 140 | 23:00 | 127 | 09:00 | Shahmirpur | 138 | 21:00 | 127 | 09:00
| Ishurdi | 137 | 01:00 | 131 | 15:00 | Shariatpur | 130 | 06:00 | 122 | 22:00
| Jaldhaka | 131 | 13:00 | 113 | 22:00 | Sherpur | 133 | 23:00 | 120 | 07:00
| Jamalpur | 135 | 23:00 | 123 | 07:00 | Shikalbaha | 127 | 23:00 | 115 | 09:00
| Jashore | 131 | 06:00 | 120 | 19:00 | Shikalbaha-230 | 139 | 23:00 | 126 | 17:00
| Jhenaidah | 134 | 08:00 | 125 | 19:30 | Shitalakhya | 135 | 23:00 | 128 | 09:00
| Jhenaidah-230 | 135 | 08:00 | 125 | 19:30 | Sholosohor | 137 | 23:00 | 124 | 09:00
| Joydebpur | 135 | 01:00 | 124 | 15:00 | Shyampur | 133 | 20:00 | 125 | 10:00
| Joypurhat | 127 | 01:00 | 118 | 21:00 | Shyampur-230 | 133 | 02:00 | 126 | 11:00
| Juldah | 138 | 21:00 | 126 | 09:00 | Siddhirganj | 134 | 21:00 | 127 | 10:00
| Kabirpur | 134 | 23:00 | 119 | 11:00 | Sirajganj | 132 | 01:00 | 127 | 22:00
| Kachua | 137 | 23:00 | 123 | 01:00 | Sonargaon | 132 | 00:00 | 124 | 12:00
| Kaliakoir | 135 | 18:00 | 127 | 09:00 | Sreemongol | 126 | 07:00 | 123 | 00:00
| Kallyanpur | 130 | 03:00 | 123 | 15:00 | Sreepur | 129 | 06:00 | 123 | 12:00
| Kalurghat | 136 | 22:00 | 125 | 09:00 | Srinagar | 132 | 02:00 | 125 | 15:00
| Kamrangirchar | 133 | 03:00 | 122 | 15:00 | SSM | 138 | 23:00 | 130 | 04:00
| Kaptai | 132 | 4:00 | 125 | 14:00 | Sunamganj | 127 | 07:00 | 121 | 00:00
| Kazla | 133 | 03:00 | 124 | 13:00 | Sylhet | 129 | 07:00 | 126 | 00:00
| Keranigonj | 133 | 03:00 | 126 | 11:00 | Sylhet-132 | 130 | 06:00 | 127 | 00:00
| Khagrachori | 138 | 23:00 | 123 | 09:00 | Tangail | 130 | 23:00 | 122 | 19:30
| Khulna | 133 | 08:00 | 122 | 19:00 | Thakurgaon | 136 | 10:00 | 115 | 21:00
| Khulna(S) | 135 | 08:00 | 126 | 19:00 | TK | 135 | 23:00 | 124 | 15:00
| Khulshi | 136 | 23:00 | 122 | 16:00 | Tongi | 134 | 04:00 | 125 | 11:00
| Kishoreganj | 129 | 19:00 | 122 | 12:00 | Ullahpara | 135 | 02:00 | 130 | 09:00
| Kodda | 136 | 19:00 | 121 | 14:00 | Ullon | 133 | 02:00 | 124 | 11:00
| KSRM | 140 | 23:00 | 122 | 13:00 | Uttara | 131 | 06:00 | 122 | 11:00
| Kulaura | 130 | 03:00 | 128 | 12:00 | UttaraNew | 131 | 05:00 | 122 | 12:00
| Kurigram | 130 | 13:00 | 107 | 19:00 | Zigatola | 133 | 03:00 | 126 | 11:00

## L-Curve
Date | 2024-05-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 244 | 9300 | 5857 | 15157 |  |  |  | QF-LDC-11
0:30 | 402 | 9115 | 5811 | 14926 | Date: | 2024-05-23
1:00 | 560 | 8930 | 5765 | 14695
1:30 | 569 | 8853.5 | 5629 | 14482.5
2:00 | 578 | 8777 | 5493 | 14270
2:30 | 644 | 8699 | 5422 | 14121 | [5 empty] | Gen. at Eve. Peak | 16067 | 16067 MW (21:00 )
3:00 | 710 | 8621 | 5351 | 13972 | [6 empty] | 21:00
3:30 | 702 | 8447.5 | 5242.5 | 13690 | [5 empty] | Gen. at Day Peak | 14166 | 14166 MW (12:00 )
4:00 | 694 | 8274 | 5134 | 13408 | [6 empty] | 12:00
4:30 | 686 | 8255 | 5099.5 | 13354.5 | [5 empty] | Highest Generation | 16067
5:00 | 678 | 8236 | 5065 | 13301 | [6 empty] | 21:00
5:30 | 668 | 8084 | 4944 | 13028
6:00 | 658 | 7932 | 4823 | 12755
6:30 | 696 | 7807.5 | 4874.5 | 12682
7:00 | 734 | 7683 | 4926 | 12609
7:30 | 771 | 7704.5 | 4970 | 12674.5
8:00 | 808 | 7726 | 5014 | 12740
8:30 | 980 | 7670.5 | 5160.5 | 12831
9:00 | 1152 | 7615 | 5307 | 12922
9:30 | 1255 | 7744.5 | 5378.5 | 13123
10:00 | 1358 | 7874 | 5450 | 13324
10:30 | 1369 | 8063 | 5533.5 | 13596.5
11:00 | 1380 | 8252 | 5617 | 13869
11:30 | 1370 | 8363.5 | 5654 | 14017.5
12:00 | 1360 | 8475 | 5691 | 14166
12:30 | 1377 | 8498 | 5764.5 | 14262.5
13:00 | 1394 | 8521 | 5838 | 14359
13:30 | 1363 | 8548.5 | 5828 | 14376.5
14:00 | 1332 | 8576 | 5818 | 14394
14:30 | 1367 | 8579.5 | 5841.5 | 14421
15:00 | 1402 | 8583 | 5865 | 14448
15:30 | 1345 | 8515.5 | 5868.5 | 14384
16:00 | 1288 | 8448 | 5872 | 14320
16:30 | 1266 | 8446 | 5846 | 14292
17:00 | 1244 | 8444 | 5820 | 14264
17:30 | 1044 | 8471.5 | 5521.5 | 13993
18:00 | 844 | 8499 | 5223 | 13722
18:30 | 769 | 8974.5 | 5463.5 | 14438
19:00 | 694 | 9450 | 5704 | 15154
19:30 | 496 | 9684 | 6093 | 15777
20:00 | 350 | 9719 | 5938 | 15657 |  |  |  | Executive Engineer
20:30 | 304 | 9844.5 | 6017.5 | 15862 |  |  |  | Network Operation Division
21:00 | 258 | 9970 | 6097 | 16067
21:30 | 269 | 9851.5 | 6043.5 | 15895
22:00 | 280 | 9733 | 5990 | 15723 |  |  |  |  | Page 6 of 7
22:30 | 259 | 9585.5 | 5921.5 | 15507
23:00 | 238 | 9438 | 5853 | 15291
23:30 | 241 | 9369 | 5855 | 15224
24:00 | 244 | 9300 | 5857 | 15157
16067 MW (21:00 )
14166 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-23 |  | Energy |  | 343463663
[15 empty] | 2024-05-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3986 | 639 | 2918 | 0 | 3104 | 3867 | 25 | 0 | 535 | 74 | 0 | 9 | 471
0:30 | 4214 | 640 | 2924.5 | 0 | 2885.5 | 3721.5 | 25 | 0 | 431 | 80 | 0 | 4.5 | 476.6375 |  |  | Date: | 43973
1:00 | 4442 | 641 | 2931 | 0 | 2667 | 3576 | 25 | 0 | 327 | 86 | 0 | 0 | 482.275
1:30 | 4428.5 | 640.5 | 2896.5 | 0 | 2593 | 3538.5 | 25 | 0 | 275 | 83 | 0 | 2.5 | 398.7125 | [9 empty] | Total Energy | 343.4637 | 343.4637 | Total Energy Gen 343.464 MKWHr Energy Not Served 9.420 MKWHr Energy Requirement 352.884 MKWHr
2:00 | 4415 | 640 | 2862 | 0 | 2519 | 3501 | 25 | 0 | 223 | 80 | 0 | 5 | 315.15 | [9 empty] | Energy not Served | 9.4198 | 9.4198
2:30 | 4422 | 782.5 | 2835 | 0 | 2322.5 | 3426 | 25 | 0 | 223 | 81 | 0 | 4 | 314.195 | [9 empty] | Energy Requirement | 352.8835 | 352.8835
3:00 | 4429 | 925 | 2808 | 0 | 2126 | 3351 | 25 | 0 | 223 | 82 | 0 | 3 | 313.24
3:30 | 4421.5 | 925 | 2790 | 0 | 1892 | 3347.5 | 25 | 0 | 208 | 79 | 0 | 2 | 296.05 | [8 empty] | Shortage
4:00 | 4414 | 925 | 2772 | 0 | 1658 | 3344 | 25 | 0 | 193 | 76 | 0 | 1 | 278.86
4:30 | 4384.5 | 925 | 2751.5 | 0 | 1651.5 | 3346.5 | 25 | 0 | 193 | 77 | 0 | 0.5 | 258.3275
5:00 | 4355 | 925 | 2731 | 0 | 1645 | 3349 | 25 | 0 | 193 | 78 | 0 | 0 | 237.795
5:30 | 4327.5 | 925 | 2690.5 | 0 | 1513.5 | 3267.5 | 25 | 0 | 193 | 69 | 17 | 0 | 212.01
6:00 | 4300 | 925 | 2650 | 0 | 1382 | 3186 | 25 | 0 | 193 | 60 | 34 | 0 | 186.225
6:30 | 4234 | 925 | 2670 | 0 | 1317 | 3171.5 | 25 | 0 | 193 | 65 | 81.5 | 0 | 184.315 | [7 empty] | Coal
7:00 | 4168 | 925 | 2690 | 0 | 1252 | 3157 | 25 | 0 | 193 | 70 | 129 | 0 | 182.405
7:30 | 4156.5 | 925 | 2653.5 | 0 | 1310 | 3143.5 | 25 | 0 | 193 | 75 | 193 | 0 | 201.0275 | [6 empty] | Oil
8:00 | 4145 | 925 | 2617 | 0 | 1368 | 3130 | 25 | 0 | 193 | 80 | 257 | 0 | 219.65
8:30 | 4196.5 | 925 | 2608.5 | 0 | 1362.5 | 3128.5 | 25 | 0 | 192.5 | 83 | 309.5 | 0 | 218.695
9:00 | 4248 | 925 | 2600 | 0 | 1357 | 3127 | 25 | 0 | 192 | 86 | 362 | 0 | 217.74
9:30 | 4292.5 | 925 | 2580.5 | 0 | 1488.5 | 3103 | 25 | 0 | 210 | 86 | 412.5 | 0 | 240.66
10:00 | 4337 | 925 | 2561 | 0 | 1620 | 3079 | 25 | 0 | 228 | 86 | 463 | 0 | 263.58
10:30 | 4330 | 925 | 2559.5 | 0 | 1887 | 3069 | 25 | 0 | 238.5 | 87 | 475.5 | 0 | 232.5425
11:00 | 4323 | 925 | 2558 | 0 | 2154 | 3059 | 25 | 0 | 249 | 88 | 488 | 0 | 201.505
11:30 | 4346.5 | 925 | 2598.5 | 0 | 2224.5 | 3069 | 25 | 0 | 250.5 | 90 | 488.5 | 0 | 212.4875
12:00 | 4370 | 925 | 2639 | 0 | 2295 | 3079 | 25 | 0 | 252 | 92 | 489 | 0 | 223.47
12:30 | 4348.5 | 924.5 | 2653 | 0 | 2384.5 | 3079 | 25 | 0 | 281 | 91 | 472 | 4 | 448.85
13:00 | 4327 | 924 | 2667 | 0 | 2474 | 3079 | 25 | 0 | 310 | 90 | 455 | 8 | 674.23
13:30 | 4327 | 924 | 2667 | 0 | 2474 | 3079 | 25 | 0 | 310 | 90 | 455 | 8 | 674.23
14:00 | 4327 | 924 | 2667 | 0 | 2474 | 3079 | 25 | 0 | 310 | 90 | 455 | 8 | 674.23
14:30 | 4339 | 923.5 | 2717.5 | 0 | 2488 | 3106 | 25 | 0 | 292 | 93 | 411 | 8.5 | 720.07
15:00 | 4351 | 923 | 2768 | 0 | 2502 | 3133 | 25 | 0 | 274 | 96 | 367 | 9 | 765.91
15:30 | 4303.5 | 923 | 2727 | 0 | 2473 | 3263.5 | 12.5 | 0 | 284 | 95 | 294.5 | 8 | 784.055
16:00 | 4256 | 923 | 2686 | 0 | 2444 | 3394 | 0 | 0 | 294 | 94 | 222 | 7 | 802.2
16:30 | 4260 | 923 | 2661.5 | 0 | 2469.5 | 3412 | 12.5 | 0 | 294.5 | 92 | 161.5 | 5.5 | 752.54
17:00 | 4264 | 923 | 2637 | 0 | 2495 | 3430 | 25 | 0 | 295 | 90 | 101 | 4 | 702.88
17:30 | 4271 | 923 | 2562 | 0 | 2417 | 3288 | 25 | 0 | 353 | 89 | 59 | 6 | 579.44
18:00 | 4278 | 923 | 2487 | 0 | 2339 | 3146 | 25 | 0 | 411 | 88 | 17 | 8 | 456
18:30 | 4344.5 | 923 | 2692.5 | 0 | 2566.5 | 3241 | 25 | 0 | 539 | 94 | 8.5 | 4 | 440.965
19:00 | 4411 | 923 | 2898 | 0 | 2794 | 3336 | 25 | 0 | 667 | 100 | 0 | 0 | 425.93
19:30 | 4402 | 922 | 2995 | 0 | 3051 | 3605 | 25 | 0 | 693 | 84 | 0 | 0 | 376.7475
20:00 | 4382 | 640 | 3000 | 0 | 3169 | 3608 | 25 | 0 | 749 | 84 | 0 | 0 | 327.565
20:30 | 4364.5 | 640 | 3022.5 | 0 | 3288.5 | 3685.5 | 25 | 0 | 751.5 | 84 | 0 | 0.5 | 322.7825
21:00 | 4347 | 640 | 3045 | 0 | 3408 | 3763 | 25 | 0 | 754 | 84 | 0 | 1 | 318
21:30 | 4259.5 | 639.5 | 2985 | 0 | 3417.5 | 3815 | 25 | 0 | 667 | 86 | 0 | 0.5 | 310.5
22:00 | 4172 | 639 | 2925 | 0 | 3427 | 3867 | 25 | 0 | 580 | 88 | 0 | 0 | 303
22:30 | 4066 | 639 | 2907 | 0 | 3346.5 | 3868.5 | 25 | 0 | 561 | 89 | 0 | 5 | 418.5
23:00 | 3960 | 639 | 2889 | 0 | 3266 | 3870 | 25 | 0 | 542 | 90 | 0 | 10 | 534
23:30 | 3973 | 639 | 2903.5 | 0 | 3185 | 3868.5 | 25 | 0 | 538.5 | 82 | 0 | 9.5 | 502.5 |  |  | Max Temp. in Dhaka |  | 38.0°C
24:00 | 3986 | 639 | 2918 | 0 | 3104 | 3867 | 25 | 0 | 535 | 74 | 0 | 9 | 471
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 343.464 MKWHr Energy Not Served 9.420 MKWHr Energy Requirement 352.884 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 589200
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 111 | 107 | 109 | 105 | 105 | 110 | 102 | 103 | 105 | 105 | 105 | 105 | 105 | 100 |  | 100 | 106 | 110 | 110 | 100 | 105 | 110 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [12 empty] | 1 | 8 | 8 | 8 | 8 | 9 |  | 25 | 25 | 25 | 25 | 25 | 10 | 8 | 158061
| Teknaf 20MW PP (Solartech) |  |  |  |  | 0 | 1 | 5 | 10 | 14 | 17 | 18 | 19 | 18 | 16 | 13 | 8 | 4 | 0 | [8 empty] | 142290
6 | Sikalbaha 225MW CCPP (Gas) | 121 | 121 | 121 | 122 | 122 | 122 | 122 | 122 | [18 empty] | 1146036
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 |  | 17 | 17 | 34 | 60 | 51 | 51 | 51 | 576801
12 | Hathazari 100 MW peaking PP | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 45 | 38 | 45 | 45 | 45 | 38 | 54 |  | 62 | 62 | 62 | 62 | 62 | 70 | 70 | 1204992
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 68 | 68 | 68 |  | 68 | 68 | 68 | 85 | 85 | 85 | 34 | 980218
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 38 | 44 | 37 | 41 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 43 | 44 | 44 | 45 | 45 | 981584
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 303 | 294 | 300 | 270 | 256 | 257 | 270 | 287 | 299 | 304 | 307 | 306 | 309 | 306 | 300 | 300 | 300 | 301 |  | 305 | 305 | 302 | 304 | 305 | 302 | 300 | 7113276
18 | Kodda 300 MW PP Unit-2 (Summit) | 280 | 295 | 250 | 95 | 95 | 0 |  |  |  | 2 | 90 | 100 | 115 | 180 | 220 | 225 | 204 | 230 |  | 250 | 260 | 264 | 290 | 300 | 273 | 253 | 4215273
19 | Ashuganj 195 MW PP (APSCL-United) | [12 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 100364
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4299750
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 490 | 490 | 490 | 482 | 480 | 470 | 460 | 460 | 460 | 460 | 460 | 460 | 480 | 490 | 485 | 485 | 485 |  | 486 | 485 | 485 | 487 | 487 | 490 | 490 | 11498180
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 32 | 30 | 30 | 31 | 31 | 31 | 31 | 32 | 32 |  | 32 | 30 | 30 | 35 | 35 | 35 | 35 | 809064
33 | Ashuganj 225 MW CCPP | 217 | 216 | 217 | 214 | 218 | 215 | 196 | 198 | 195 | 217 | 211 | 211 | 210 | 209 | 201 | 185 | 185 | 207 |  | 209 | 211 | 211 | 193 | 186 | 194 | 195 | 4968000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 285 | 265 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 260 | 270 | 270 | 270 | 300 | 270 | 270 | 6420000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 295 | 285 | 285 | 300 | 285 | 335 | 290 | 295 | 300 | 285 | 290 | 315 | 285 | 285 | 290 |  | 290 | 310 | 310 | 310 | 340 | 300 | 300 | 7537600
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 400 | 270 | 270 | 250 | 250 | 250 | 250 | 270 | 270 | 270 | 270 | 270 | 270 |  | 320 | 330 | 310 | 260 | 230 | 230 | 230 | 6463500
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 43 | 49 | 49 | 47 | 45 | 45 | 43 | 42 | 39 | 38 | 35 | 36 | 36 |  | 37 | 37 | 38 | 43 | 45 | 46 | 46 | 1000800
36 | Chandpur 150 MW CCPP | 86 | 86 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 2018200
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 408 | 407 | 407 | 408 | 358 | 352 | 352 | 353 | 392 | 401 | 398 | 398 | 399 | 394 | 395 | 401 | 388 |  | 398 | 402 | 401 | 401 | 361 | 400 | 402 | 9439200
| Meghnaghat Unique power | 450 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 350 | 300 | 300 | 350 | 350 | 350 | 390 | 360 | 360 | 320 |  | 440 | 500 | 500 | 500 | 500 | 500 | 500 | 9633636
| Summit Meghanghat-2 589 MW(Gas) | 450 | 450 | 400 | 400 | 400 | 400 | 400 | 400 | 350 | 300 | 300 | 300 | 300 | 350 | 370 | 370 | 340 | 260 |  | 450 | 500 | 500 | 500 | 400 | 450 | 450 | 9085909
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10321000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 82 | 82 | 83 | 83 | 86 | 87 | 71 | 67 | 62 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 67 | 67 |  | 66 | 66 | 66 | 70 | 70 | 71 | 70 | 1604160
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 2 | 14 | 25 | 28 | 44 | 49 | 48 | 27 | 21 | 31 | 22 | 9 | 2 | [8 empty] | 358780
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 39 | 36 | 36 | 38 | 36 | 36 | 38 | 38 | 36 | 38 |  | 38 | 36 | 37 | 37 | 40 | 38 | 40 | 913000
45 | Fenchugonj CCPP Phase-2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1153200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 31 | 31 | 32 | 32 | 32 | 31 | 31 | 30 | 54 | 55 | 40 | 54 | 54 | 54 | 52 | 53 | 54 | 54 |  | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 1084704
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 205 | 206 | 207 | 207 | 207 | 206 | 205 | 202 | 201 | 201 | 200 | 200 | 199 | 194 | 197 | 198 | 198 |  | 201 | 201 | 201 | 202 | 202 | 204 | 201 | 5078240
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 3 | 3 | 116928
55 | Fenchugonj 51 MW PP (Barakatullah) | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 43 | 43 | 44 | 43 | 46 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1117200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 524016
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 285 | 290 | 290 | 280 | 290 | 280 | 305 | 310 | 285 | 300 | 300 | 295 | 315 | 290 | 275 | 270 |  | 300 | 280 | 275 | 305 | 285 | 290 | 285 | 7159000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 340 | 310 | 310 | 310 | 369 | 345 | 345 | 360 | 345 | 345 | 349 | 345 | 345 | 345 |  | 345 | 345 | 345 | 345 | 369 | 345 | 371 | 8191800
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1196303
59 | Tangail Palli Power Gen 22 MW | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 293520
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 86 | 80 | 82 | 76 | 78 | 60 | 70 | 80 | 86 | 86 | 88 | 92 | 90 | 94 | 96 | 94 | 90 | 88 |  | 100 | 84 | 84 | 84 | 88 | 90 | 74 | 2026560
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 34 | 34 | 24 | 9 | 3 | 2 | 2 | 5 | 10 | 6 | 2 | 2 | 2 | 2 |  | 2 | 2 | 12 | 18 | 19 | 12 | 27 | 366720
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 24 | 24 | 24 | 23 | 23 | 23 | 23 |  | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 657800
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 410960
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 15 | 17 |  | 17 | 17 | 18 | 18 | 18 | 19 | 18 | 42300
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 0 | 0 | 23 | 23 | 23 | 0 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 452880
71 | Maona 33 MW PP(Summit) | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 30 | 30 |  | 30 | 30 | 30 | 33 | 25 | 25 | 25 | 624000
72 | Rupganj 33 MW PP(Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 6 | 32 | 32 | 30 | 29 | 29 | 29 | 29 | 29 | 24 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 30 | 30 | 670500
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 282272
| Feni Lanka Power | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 51 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1275660
| Chowmuhani 113 MW | 44 | 38 | 39 | 39 | 39 | 38 | 32 | 38 | 38 | 37 | 36 | 37 | 38 | 42 | 36 | 36 | 38 | 72 |  | 73 | 73 | 73 | 83 | 83 | 84 | 84 | 1204560
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 126 | 126 | 126 | 126 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3784320
77 | Siddhirganj 100 PP(Dutch Bangla) | 82 | 82 | 75 | 24 | 17 | 0 |  |  |  | 8 | 38 | 70 | 75 | 75 | 75 | 75 | 78 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1263360
78 | Gazipur 52 MW PP | [6 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 132960
79 | Kodda 150 MW PP | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 145 |  | 150 | 149 | 149 | 149 | 149 | 98 | 98 | 1565280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 51 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 33 |  | 50 | 50 | 50 | 50 | 50 | 50 | 43 | 819403
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 50 | 50 | 50 | 105 | 105 | 52 | 17 | 663360
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 36117
| Jodiac Power | 35 | 35 | 35 | 17 | 17 | 0 |  |  |  | 15 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 716851
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 85 | 68 | 68 | 74 | 101 | 92 | 99 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2543371
82 | Madanganj 102 PP(Summit) | 80 | 80 | 75 | 37 | 34 | 16 |  |  |  | 10 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1356191
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 8 | 14 | 14 | 14 | 14 |  |  | 42000
86 | Meghnaghat CCPP ( Summit) | 322 | 323 | 323 | 320 | 324 | 324 | 318 | 321 | 315 | 318 | 315 | 315 | 315 | 310 | 305 | 310 | 312 | 310 |  | 310 | 317 | 316 | 319 | 316 | 320 | 318 | 7411520
87 | Meghnaghat 100 MW(IEL) | 91 | 91 | 85 | 20 | 17 | 0 |  |  |  | 3 | 27 | 64 | 71 | 74 | 74 | 78 | 84 | 90 |  | 97 | 98 | 96 | 98 | 95 | 90 | 98 | 1441920
| Meghnaghat 104 MW PP (OPCL) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 54 | 58 |  | 70 | 71 | 70 | 70 | 70 | 70 | 70 | 1620480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 68 | 68 | 12 | 12 | 12 | 0 |  |  |  | 25 | 56 | 58 | 58 | 46 | 44 | 44 | 44 | 12 |  | 30 | 36 | 38 | 40 | 42 | 44 | 56 | 776640
92 | Fenchuganj 44 MW (Energyprima) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 40 | 40 | 36 | 40 | 40 | 40 |  | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 981000
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 15 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 814179
94 | Gagnagar 102 MW PP (Digital Power) | 82 | 74 | 82 | 82 | 82 | 82 | 74 | 82 | 82 | 82 | 82 | 82 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2034432
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 0 |  |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 18 |  | 19 | 19 | 19 | 30 | 22 | 19 | 6 | 197760
96 | Chattogram 108 MW PP (ECPV) | 58 | 47 | 45 | 46 | 45 | 28 | 12 | 12 | 12 | 19 | 40 | 44 | 44 | 43 | 43 | 23 | 45 | 46 |  | 56 | 56 | 58 | 58 | 63 | 63 | 64 | 1021440
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 44 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 939976
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1321934
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 112 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2472709
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 15150
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 22 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 |  | 20 | 27 | 47 | 54 | 54 | 54 | 54 | 1116360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 77 | 77 | 77 | 77 | 77 | 58 | 58 | 58 | 58 | 58 | 58 | 65 | 57 | 57 | 57 | 57 | 57 |  | 104 | 105 | 106 | 106 | 106 | 106 | 106 | 1780800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 50 | 35 | 35 | 35 | 35 | 34 | 35 | 36 | 36 | 60 | 139 | 149 | 145 | 87 | 67 | 67 | 69 | 69 |  | 90 | 135 | 131 | 149 | 149 | 107 | 73 | 1888128
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 62 | 62 |  | 62 | 62 | 62 | 86 | 86 | 49 | 49 | 1300800
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 60 | 68 | 68 | 68 | 74 | 104 | 103 | 103 | 103 | 103 | 103 | 103 |  | 133 | 136 | 138 | 138 | 138 | 138 | 138 | 2002080
117 | Ashuganj 150 MW PP (Midland) | 21 | 13 | 11 | 13 | 13 | 13 | 11 | 13 | 13 | 13 | 11 | 12 | 12 | 12 | 10 | 12 | 10 | 17 |  | 43 | 55 | 53 | 53 | 55 | 56 | 51 | 546981
118 | Bibiyana-III 400 MW CCPP | 365 | 365 | 365 | 368 | 366 | 307 | 308 | 306 | 340 | 395 | 404 | 380 | 405 | 398 | 369 | 368 | 368 | 368 |  | 368 | 367 | 367 | 367 | 390 | 367 | 380 | 8835000
| Jamalpur 115 MW PP (United) | 69 | 69 | 69 | 69 | 70 | 70 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 |  | 96 | 97 | 99 | 98 | 98 | 98 | 98 | 1560000
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 50 | 51 | 51 | 50 | 51 | 51 | 52 | 51 | 51 | 51 |  | 51 | 51 | 51 | 50 | 50 | 50 | 52 | 1252036
| Juldah unit-2 (Acorn) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 56 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 60 | 60 | 60 | 94 | 96 | 71 | 48 | 1283520
| Anlima Energy Ltd. | 53 | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 22 | 17 | 17 | 17 | 17 |  | 47 | 53 | 53 | 63 | 87 | 55 | 53 | 727636
| Bhairob 54.5 MW | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 534240
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 8 | 15 | 21 | 28 | 29 | 29 | 28 | 25 | 19 | 13 | 6 | 1 | [8 empty] | 218609
| Chandpur 115(Doreen) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 109 | 104 | 91 | 90 | 88 | 77 | 67 | 68 | 68 | 68 | 81 |  | 101 | 109 | 107 | 111 | 113 | 114 | 114 | 2382720
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 23 | 35 | 17 | 17 | 17 | 464760
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 | 163 | 17 | 17 | 17 | 981890
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 5 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 9 | 7 | 4 | 8 |  | 0 | 0 | 0 | 1 | 0 | 10 | 9 | 67200
| Sonagazi 75 MW Solar Plant | [5 empty] | 5 | 18 | 36 | 51 | 63 | 54 | 45 | 68 | 62 | 49 | 21 | 13 | 2 | [8 empty] | 498263
| Matarbari 2*600 MW (CPGCL) | 233 | 234 | 233 | 234 | 232 | 234 | 234 | 236 | 233 | 234 | 235 | 232 | 233 | 233 | 232 | 233 | 232 | 233 |  | 232 | 233 | 234 | 233 | 234 | 234 | 233 | 5672727
120 | Eastern Zone Total | 8930 | 8777 | 8621 | 8274 | 8236 | 7932 | 7683 | 7726 | 7615 | 7874 | 8252 | 8475 | 8521 | 8576 | 8583 | 8448 | 8444 | 8499 |  | 9450 | 9684 | 9719 | 9970 | 9733 | 9438 | 9300 | 206994100
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 32 | 41 | 31 | 31 | 31 | 31 | 31 | 160320
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [12 empty] | 20 | 53 | 53 | 53 | 84 | 91 | 536160
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 9 | 24 | 53 | 76 | 91 | 98 | 100 | 98 | 89 | 80 | 40 | 11 | [9 empty] | 796320
131 | Rampal 1320 MW (BIFPCL) | 482 | 430 | 381 | 380 | 380 | 381 | 383 | 381 | 381 | 383 | 379 | 378 | 379 | 380 | 377 | 434 | 435 | 398 |  | 458 | 540 | 516 | 560 | 565 | 602 | 622 | 10392730
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5126073
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 1203840
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 270 | 270 | 208 |  | 244 | 280 | 280 | 307 | 307 | 307 | 307 | 6392700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 130 | 130 | 130 | 122 | 124 | 124 | 128 | 128 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2880000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 10 | 10 | 10 | 10 | 9 | 7 | 7 | 7 | 7 | 7 | 8 | 9 | 9 | 9 | 7 | 7 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 215789
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [14 empty] | 8 | 16 | 16 |  |  |  |  | 40 | 40 | 40 | 40 | 40 | 216375
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 22 | 43 | 70 | 55 | 40 | 44 | 50 | 242944
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 0 | [22 empty] | 32 | 32 | 60192
146 | Bheramara HVDC | 641 | 640 | 925 | 925 | 925 | 925 | 925 | 925 | 925 | 925 | 925 | 925 | 924 | 925 | 923 | 923 | 923 | 923 |  | 923 | 922 | 640 | 640 | 639 | 639 | 639 | 20344000
147 | Bheramara 410 MW CCPP | 345 | 345 | 345 | 355 | 345 | 345 | 360 | 345 | 395 | 345 | 355 | 385 | 345 | 340 | 370 | 340 | 340 | 340 |  | 385 | 340 | 340 | 340 | 150 |  |  | 7953984
148 | Payra 1320 MW | 1000 | 980 | 930 | 930 | 940 | 820 | 800 | 780 | 780 | 700 | 680 | 700 | 700 | 700 | 730 | 920 | 960 | 860 |  | 870 | 1020 | 1040 | 1130 | 1244 | 1200 | 1160 | 23566800
149
150 | Barapukuria TPP Unit-1 | 69 | 68 | 70 | 66 | 67 | 67 | 66 | 66 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 64 | 64 | 64 |  | 64 | 64 | 64 | 65 | 65 | 66 | 66 | 1485381
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 215 | 200 | 200 | 230 | 5483000
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 45 | 45 |  | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 1150000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 38 | 37 | 37 | 37 | 38 | 38 | 38 | 31 |  | 41 | 38 | 41 | 39 | 39 | 39 | 39 | 927923
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 30540
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 182 | 176 | 180 | 175 | 159 | 156 | 160 | 157 | 170 | 194 | 184 | 191 | 196 | 187 | 197 | 189 | 185 | 185 |  | 192 | 186 | 185 | 194 | 191 | 192 | 184 | 4581818
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 193 | 186 | 188 | 186 | 170 | 161 | 166 | 163 | 176 | 192 | 184 | 192 | 195 | 190 | 198 | 189 | 185 | 185 |  | 192 | 187 | 185 | 194 | 191 | 193 | 185 | 4703664
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 402 | 397 | 387 | 349 | 307 | 306 | 347 | 298 | 362 | 384 | 414 | 397 | 414 | 414 | 414 | 382 | 374 | 348 |  | 414 | 414 | 414 | 414 | 414 | 325 | 347 | 9077890
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 |  |  |  | 88812
165 | Amnura 50 MW PP(Sinha) | [13 empty] | 28 | 35 | 35 | 35 | 14 |  | 18 | 35 | 35 | 35 | 35 | 35 | 35 | 324620
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 30 | 0 | [9 empty] | 14 | 35 | 37 | 35 | 30 | 28 | 28 |  | 28 | 28 | 46 | 39 | 35 | 35 | 35 | 393904
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | 0 | [12 empty] | 10 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 236097
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 58 | 0 | [10 empty] | 40 | 30 | 32 | 40 | 40 | 40 |  | 88 | 88 | 88 | 90 | 90 | 90 | 77 | 795872
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 35 | 0 | [5 empty] | 7 | 70 | 73 | 113 | 113 | 113 | 113 | 113 | 35 |  | 41 | 95 | 105 | 113 | 113 | 113 | 113 | 1732608
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 35 | 0 | [5 empty] | 50 | 70 | 70 | 113 | 113 | 113 | 113 | 113 | 35 |  | 75 | 113 | 113 | 113 | 113 | 113 | 113 | 1717632
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 34 | 0 | [5 empty] | 29 | 50 | 50 | 100 | 95 | 94 | 95 | 101 | 102 |  | 102 | 98 | 105 | 106 | 107 | 107 | 107 | 1606828
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 7 | 7 | 7 | 7 | 7 | 6 | 4 | 3 | 1 | [8 empty] | 58095
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 75 | 35 | 35 | 35 | 35 | 35 | 40 | 72 | 110 | 115 | 115 | 115 | 112 | 115 | 115 | 74 |  | 90 | 115 | 115 | 115 | 115 | 115 | 115 | 2185152
| Intraco Solar 30 MW |  |  |  |  | 0 | 3 | 9 | 15 | 22 | 28 | 33 | 29 | 30 | 28 | 22 | 15 | 7 | 1 |  | 0 | [6 empty] | 241265
| Adani Power Jharkhanda Ltd | 765 | 762 | 767 | 764 | 768 | 724 | 724 | 727 | 726 | 755 | 758 | 762 | 760 | 756 | 769 | 768 | 764 | 678 |  | 762 | 763 | 769 | 766 | 765 | 771 | 759 | 18086545
178 | Teesta Solar Limited |  |  |  |  | 0 | 12 | 48 | 95 | 137 | 175 | 189 | 201 | 169 | 168 | 141 | 95 | 47 | 10 | [8 empty] | 1473690