## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-05-26 | Sunday
|  | Date (day): | 2024-05-26 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14799.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15838 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-05-25 | 2024-05-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 396 | 396 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 4 | 93 | 90 | 90 |  |  | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 300 | 310 | 310 |  |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 2 | 80 | 80 | 80 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 25 | 40 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 10 | 0 | 15 | 60 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 10 | 70 | 85 | 90 |  |  | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 286 | 286 | 150 | 300
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 90 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 21 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 149 | 48 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 40 | 43 | 43 |  | 37 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 29 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 26 | 14 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 195 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 99 | 115 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 52 | 17 | 50 | 55 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 70 | 70 | 53 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 0 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 2755 | 2927 | 2918 | 3259 | 794 | 829
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 25 | 8 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 20 | 30 |  | Fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 137 | 150 | 150 |  | 75 | Under maint
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 34 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 53 | 72 | 55 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 17 | 85 | 51 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 58 | 69 | 70 | 70 | 30 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 48 | 62 | 49 | 62 | 38 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 12 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 44 | 45 | 45 | 60 |  | 8 | Engine problem
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 76 | 110 | 51 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 60 | 48 | 60 | 40 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 50 | 35 | 53 | 63 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 35 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 410 | 488 | 490 | 490 |  | 734 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 8 | 47 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 506 | 526 | 575 | 575
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 72 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1753 | 2138 | 1983 | 2215 | 936 | 1186
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 214 | 210 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 50 | 0 | 0 | 0 |  | 360 | Under maint
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 265 | 270 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 260 | 280 | 250 | 280 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 35 | 36 | 9
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 43 | 41 | 50 | 50
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  | 51 | Gas shortage due to LND S/D.
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 35 | 12 | 50 | 100 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 43 | 39 | 40
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 75 | 70 | 50 | 50 |  | 113 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 136 | 100 | 155 | 45
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 78 | 82 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 31 | 31 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 20 | 46 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 10 | 20 | 20 |  | 5 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 97 | 52 | 114 | 0 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 45 | 73 | 36 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 50 | 50
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 54 | 83 | 115 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1399 | 1547 | 1492 | 1770 | 387 | 529
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 66 | 58 | 45 | 80 | 122 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 57 | 107 | 58 | 105 | 95 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 47 | 97 | 57 | 100 | 15 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 233 | 274 | 223.6 | 297 | 122 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 40 | 42 | 42 |  | 28 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 56 | 60 | 60 |  | 30 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Gas shortage, ST Under maint.
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 49 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 38 | 38 | 42 | 42 |  | 8 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 0 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 60 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 197 | 200 | 204 | 204 |  | 27 | Engine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 19 | 16 | 24 | 24
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 270 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 352 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 385 | 345 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1478 | 1466 | 1532 | 1547 | 0 | 612
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 920 | 944 | 655
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 85 | 20 | 85
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 30 | 33 | 30 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 40 | 45 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 40 | 32 | 32
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 73 | 90 | 53 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 85 | 15 | 100
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 52 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 580 | 600 | 620 | 620
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1710 | 1898 | 1864 | 1684 | 1007 | 61
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 80 | 48 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 8 | 2 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1140 | 870 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 17 | 17 | 17 | 133 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 307 | 276 | 250 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1902 | 1563 | 1981 | 2038 | 133 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 32 | 40 | 40 | 40 |  | 12 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 35 | 14 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 21 | 35 | 42 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Machine problem
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 157 | 180 | 190 |  |  | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 370 | 350 | 414 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 0 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 50 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 50 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1259 | 1319 | 1425 | 1425 |  |  | unit-1 under maint
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1923 | 2317 | 2168 | 2521 | 243 | 290
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 64 | 65 | 65
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 210 | 220 | 220 |  | 54 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 8 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 104 | 70 | 107
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 41 | 115 | 115 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 203 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 573 | 493 | 638 | 507 | 40 | 139
| Total |  |  |  |  | 27054 | 25903 | 13726 | 14623 | 14799.6 | 15838 | 3662 | 3710
A. |  | 2024-05-25 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 14707 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 12749 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14900 | MW
3 | Day peak Generation : |  |  | 13726 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14471.44 | MW
4 | Evening peak Generation : |  |  | 14623 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 265 | MW
5 | Total Energy Generation : |  | 337.8796 | MKWHr | By Solar | 3.8485 | MKWHr
| By Gas : | 125.9662 | MKWHr |  | By Oil: | 73.0218 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 111.6802 | MKWHr |  | By Hydro: | 0.7233 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.52656 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3662 | MW | Dhaka | 5944.44 | 5869.44 |  | 75 |  | 18:00 |  | 492
|  |  | For Plants S/D or M/C prob = |  |  | 3710 | MW | Chittagong | 1422.5 | 1422.5 |  | 0 |  | 19:00 |  | 265
|  |  | Total = |  |  | 7372 | MW | Khulna | 1862.2 | 1862.2 |  | 0 |  | 19:30 |  | 338
7 | Total Gas Supplied : |  |  | 915.18 | MMCFD |  |  | Rajshahi | 1440.8 | 1440.8 |  | 0 |  | 20:00 |  | 268
8 | Fuel Cost : | i) Gas : | Taka | 383488310.808 | ii) Oil : | Taka | 1338948456.76 | Comilla | 1116 | 1116 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 761279198.46 | Total | Taka | 2483715966.028 | Mymensingh | 1252 | 1062 |  | 190 |  | 22:00 |  | 35
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5205.75 | MKWHr. | Sylhet | 284 | 284 |  | 0 |  | 23:00 |  | 971
| ii) During Peak Demand : |  |  | 796 | MW (W to E) at | 19:00 | hrs | Barisal | 193.5 | 193.5 |  | 0 |  | 24:00 |  | 1168
| iii) Maximum : |  |  | 244 | MW at | 20:00 | hrs | Rangpur | 956 | 956 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 38.8°C |  |  | Total | 14471.44 | 14206.44 |  | 265
B. |  | 2024-05-26 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 38.9°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15838 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13500 | MW
4 | Reserve(Generation end) |  |  |  | 838 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 344.611 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12391 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.288 | MKWHr. | ii) HVDC Flow at Peak Time |  | 920 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.825 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 71.78 |  | (b) Today: | 71.68 |  | (c) Rule Curve: |  | 77.2
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-05-25 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 405 | 0 |  | 0 | 450 | 295 | 73 | 80 | 25 | 260 | 0 | 0 | 83 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 25 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 153 | 0 | 0 | 0 |  | 12 | 74 | 17 | 68 | 44 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 270 | 206 | 0 | 20 | 35 | 50 | 0 | 0 | 0 | 44 | 34 | 0 | 0 | 31 | 13 | 64 | 113 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 198 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 195 | 0 | 0 | 78 | 0 | 53 | 0 | 49 | 90 | 18 | 366 | 69 | 17 | 17 | 0 | 52 | 35 | 68 | 52 | 46 | 48 | 345 | 72 | 0 | 144 | 53 | 0 | 35 | 0 | 111 | 17 | 230 | 17 | 0 | 490 | 26 | 550 | 255 | 0 | 0 |  | 641 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 5 | 14 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 46 | 35 | 0 | 21 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 190 | 0 | 314 | 72 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 1363 | 0 | 0 |  | 8204 | 6503 | 14707 | 3842 | 641 | 2029 | 0 | 2886 | 4849 | 30 | 0 | 340 | 64 | 0 | 26 | 996.065 | 71.83
2:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 406 | 0 |  | 0 | 450 | 300 | 73 | 80 | 25 | 261 | 0 | 0 | 83 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 23 | 25 | 30 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 56 | 17 | 58 | 44 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 270 | 201 | 0 | 31 | 35 | 52 | 0 | 0 | 0 | 45 | 34 | 0 | 0 | 31 | 17 | 60 | 111 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 201 | 0 | 0 | 0 | 290 | 24 | 0 | 0 | 195 | 0 | 0 | 78 | 0 | 53 | 0 | 49 | 68 | 12 | 364 | 70 | 17 | 17 | 0 | 52 | 35 | 68 | 52 | 46 | 48 | 345 | 60 | 0 | 162 | 53 | 0 | 35 | 0 | 112 | 17 | 230 | 17 | 0 | 493 | 31 | 550 | 230 | 0 | 0 |  | 641 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 30 | 42 | 32 | 80 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 0 | 35 | 0 | 14 | 0 | 22 | 0 | 0 | 8 | 63 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 354 | 73 | 0 | 113 | 105 | 100 | 0 | 0 | 113 | 1244 | 180 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 1368 | 0 | 0 |  | 8160 | 6289 | 14449 | 3670 | 641 | 2011 | 0 | 2843 | 4856 | 30 | 0 | 307 | 60 | 0 | 31 | 908.205 | 71.82
3:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 404 | 0 |  | 0 | 450 | 297 | 74 | 80 | 25 | 266 | 0 | 0 | 83 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 24 | 23 | 25 | 31 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 56 | 17 | 58 | 46 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 260 | 191 | 0 | 40 | 35 | 53 | 0 | 0 | 0 | 45 | 34 | 0 | 0 | 31 | 17 | 62 | 110 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 203 | 0 | 0 | 0 | 285 | 24 | 0 | 0 | 195 | 0 | 0 | 78 | 0 | 53 | 0 | 49 | 68 | 13 | 365 | 68 | 17 | 17 | 0 | 52 | 35 | 68 | 52 | 38 | 48 | 345 | 70 | 0 | 162 | 53 | 0 | 19 | 0 | 112 | 17 | 230 | 17 | 0 | 491 | 19 | 550 | 230 | 0 | 0 |  | 926 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 30 | 50 | 32 | 80 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 0 | 35 | 0 | 21 | 0 | 22 | 0 | 0 | 8 | 63 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 322 | 73 | 0 | 113 | 105 | 100 | 0 | 0 | 113 | 1222 | 180 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 623 | 0 | 307 | 1236 | 0 | 0 |  | 8123 | 6404 | 14527 | 3663 | 926 | 1972 | 0 | 2831 | 4702 | 30 | 0 | 322 | 62 | 0 | 19 | 308.465 | 71.81
4:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 404 | 0 |  | 0 | 450 | 305 | 74 | 80 | 25 | 260 | 0 | 0 | 83 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 24 | 23 | 25 | 31 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 56 | 17 | 58 | 45 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 51 | 35 | 43 | 0 | 0 | 0 | 45 | 34 | 0 | 0 | 31 | 17 | 62 | 111 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 24 | 0 | 0 | 198 | 0 | 0 | 78 | 0 | 53 | 0 | 49 | 68 | 12 | 368 | 68 | 17 | 17 | 0 | 52 | 35 | 68 | 52 | 38 | 48 | 345 | 70 | 0 | 162 | 37 | 0 | 17 | 0 | 112 | 17 | 230 | 17 | 0 | 490 | 7 | 410 | 230 | 0 | 0 |  | 926 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 50 | 32 | 80 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 0 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 353 | 73 | 0 | 113 | 105 | 100 | 0 | 0 | 113 | 1182 | 180 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1234 | 0 | 0 |  | 7980 | 6378 | 14358 | 3683 | 926 | 2016 | 0 | 2815 | 4519 | 30 | 0 | 300 | 62 | 0 | 7 | 231.11 | 71.8
5:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 300 | 72 | 80 | 25 | 245 | 0 | 0 | 83 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 24 | 23 | 25 | 31 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 152 | 0 | 0 | 0 |  | 12 | 56 | 17 | 58 | 46 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 219 | 0 | 50 | 35 | 40 | 0 | 0 | 0 | 46 | 34 | 0 | 0 | 31 | 17 | 60 | 115 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 203 | 0 | 0 | 0 | 295 | 24 | 0 | 0 | 210 | 0 | 0 | 78 | 0 | 51 | 0 | 49 | 68 | 13 | 366 | 69 | 17 | 17 | 0 | 52 | 35 | 68 | 52 | 38 | 48 | 345 | 70 | 0 | 162 | 35 | 0 | 17 | 0 | 112 | 17 | 230 | 17 | 0 | 490 | 10 | 418 | 230 | 0 | 0 |  | 926 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 50 | 32 | 80 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 0 | 35 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 307 | 73 | 0 | 113 | 105 | 100 | 0 | 0 | 113 | 1182 | 180 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 307 | 1229 | 0 | 0 |  | 7974 | 6328 | 14302 | 3669 | 926 | 1957 | 0 | 2824 | 4525 | 30 | 0 | 301 | 60 | 0 | 10 | 212.965 | 71.79
6:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 401 | 0 |  | 0 | 450 | 304 | 73 | 72 | 25 | 245 | 0 | 0 | 83 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 25 | 23 | 25 | 31 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 56 | 17 | 12 | 45 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 218 | 0 | 51 | 35 | 43 | 0 | 0 | 0 | 46 | 34 | 0 | 0 | 31 | 17 | 56 | 115 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 270 | 24 | 0 | 0 | 213 | 0 | 0 | 78 | 0 | 53 | 2 | 49 | 68 | 12 | 365 | 69 | 17 | 17 | 0 | 52 | 27 | 34 | 52 | 38 | 48 | 345 | 71 | 3 | 90 | 35 | 0 | 17 | 2 | 60 | 17 | 230 | 17 | 0 | 490 | 2 | 466 | 0 | 0 | 5 |  | 925 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 30 | 50 | 32 | 80 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 0 | 14 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 351 | 73 | 0 | 35 | 15 | 35 | 0 | 0 | 35 | 1120 | 180 | 0 | 35 | 0 | 5 | 74 | 0 | 0 | 622 | 2 | 250 | 1222 | 13 | 0 |  | 7471 | 5885 | 13356 | 3664 | 925 | 1753 | 0 | 2149 | 4444 | 30 | 0 | 301 | 56 | 32 | 2 | 185.27 | 71.78
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 402 | 0 |  | 0 | 450 | 315 | 48 | 34 | 25 | 245 | 0 | 0 | 43 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 20 | 23 | 25 | 31 | 2 | 0 | 0 | 30 | 0 | 0 | 0 | 151 | 0 | 0 | 0 |  | 12 | 56 | 17 | 12 | 46 | 6 | 0 | 39 | 0 | 0 | 0 | 280 | 240 | 202 | 0 | 51 | 35 | 45 | 0 | 0 | 0 | 46 | 34 | 0 | 0 | 32 | 17 | 56 | 82 | 0 | 0 | 1 | 39 | 58 | 49 | 42 | 0 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 305 | 24 | 0 | 0 | 296 | 0 | 0 | 57 | 0 | 53 | 4 | 37 | 68 | 13 | 365 | 49 | 17 | 17 | 2 | 52 | 17 | 34 | 52 | 38 | 48 | 345 | 71 | 13 | 54 | 35 | 0 | 17 | 7 | 17 | 17 | 250 | 17 | 0 | 490 | 0 | 470 | 0 | 0 | 20 |  | 925 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 30 | 50 | 0 | 80 | 10 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 14 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 352 | 73 | 0 | 35 | 15 | 35 | 0 | 1 | 35 | 1110 | 180 | 0 | 35 | 0 | 27 | 74 | 0 | 0 | 623 | 7 | 250 | 1231 | 48 | 0 |  | 7363 | 5863 | 13226 | 3637 | 925 | 1799 | 0 | 1900 | 4448 | 30 | 0 | 301 | 56 | 130 | 0 | 213.92 | 71.77
8:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 355 | 0 |  | 0 | 400 | 290 | 24 | 34 | 25 | 254 | 0 | 0 | 25 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 20 | 23 | 25 | 31 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 150 | 0 | 0 | 0 |  | 12 | 56 | 17 | 12 | 45 | 6 | 0 | 8 | 0 | 0 | 0 | 280 | 240 | 194 | 0 | 50 | 35 | 45 | 0 | 0 | 0 | 45 | 25 | 0 | 0 | 32 | 17 | 66 | 89 | 0 | 0 | 0 | 39 | 58 | 49 | 42 | 0 | 0 | 61 | 0 | 0 | 204 | 0 | 0 | 0 | 270 | 24 | 0 | 0 | 300 | 0 | 0 | 57 | 0 | 51 | 0 | 37 | 68 | 12 | 316 | 49 | 17 | 17 | 2 | 52 | 17 | 34 | 17 | 38 | 48 | 310 | 72 | 26 | 54 | 35 | 0 | 17 | 14 | 17 | 17 | 240 | 17 | 0 | 491 | 0 | 574 | 0 | 0 | 39 |  | 926 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 30 | 50 | 0 | 80 | 7 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 14 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 311 | 73 | 0 | 35 | 15 | 35 | 0 | 3 | 35 | 1020 | 180 | 0 | 35 | 2 | 50 | 74 | 0 | 0 | 624 | 15 | 250 | 1219 | 98 | 0 |  | 7161 | 5794 | 12955 | 3498 | 926 | 1614 | 0 | 1821 | 4451 | 30 | 0 | 300 | 66 | 249 | 0 | 186.225 | 71.76
9:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 321 | 0 |  | 0 | 350 | 295 | 25 | 34 | 25 | 285 | 0 | 0 | 25 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 20 | 23 | 25 | 29 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 148 | 0 | 0 | 0 |  | 12 | 56 | 17 | 0 | 45 | 6 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 194 | 0 | 50 | 31 | 45 | 0 | 0 | 0 | 43 | 25 | 0 | 0 | 31 | 17 | 70 | 89 | 0 | 0 | 0 | 39 | 58 | 49 | 10 | 0 | 0 | 40 | 0 | 0 | 205 | 0 | 0 | 0 | 260 | 24 | 2 | 0 | 300 | 0 | 0 | 57 | 0 | 108 | 7 | 37 | 68 | 12 | 318 | 48 | 17 | 25 | 4 | 52 | 0 | 34 | 17 | 38 | 48 | 310 | 72 | 38 | 108 | 35 | 0 | 17 | 23 | 17 | 17 | 230 | 17 | 0 | 473 | 2 | 539 | 0 | 0 | 54 |  | 926 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 30 | 50 | 0 | 80 | 7 | 80 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 8 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 304 | 73 | 0 | 0 | 15 | 35 | 0 | 5 | 0 | 980 | 180 | 0 | 35 | 3 | 75 | 35 | 0 | 0 | 557 | 22 | 250 | 1219 | 144 | 0 |  | 7116 | 5633 | 12749 | 3453 | 926 | 1514 | 0 | 1788 | 4301 | 30 | 0 | 290 | 70 | 375 | 2 | 77.355 | 71.75
10:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 322 | 0 |  | 0 | 350 | 300 | 0 | 7 | 25 | 287 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 20 | 23 | 25 | 29 | 8 | 0 | 20 | 30 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 12 | 56 | 17 | 0 | 44 | 6 | 0 | 2 | 0 | 0 | 0 | 155 | 285 | 209 | 8 | 70 | 32 | 45 | 0 | 0 | 0 | 36 | 8 | 0 | 0 | 31 | 17 | 70 | 87 | 0 | 0 | 0 | 39 | 58 | 46 | 10 | 0 | 0 | 40 | 0 | 0 | 200 | 0 | 0 | 0 | 295 | 24 | 2 | 0 | 300 | 0 | 0 | 57 | 0 | 149 | 13 | 49 | 68 | 12 | 350 | 48 | 17 | 34 | 3 | 52 | 0 | 34 | 17 | 37 | 48 | 330 | 72 | 47 | 162 | 35 | 0 | 17 | 28 | 17 | 17 | 230 | 17 | 0 | 403 | 2 | 503 | 0 | 0 | 65 |  | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 0 | 130 | 8 | 80 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 351 | 73 | 0 | 0 | 15 | 10 | 0 | 7 | 0 | 1010 | 180 | 0 | 24 | 4 | 74 | 35 | 0 | 0 | 557 | 28 | 250 | 1222 | 176 | 0 |  | 7117 | 5730 | 12847 | 3481 | 926 | 1607 | 0 | 1756 | 4228 | 50 | 0 | 282 | 70 | 445 | 2 | 146.115 | 71.75
11:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 391 | 0 |  | 0 | 450 | 309 | 0 | 0 | 25 | 286 | 0 | 0 | 0 | 40 | 32 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 20 | 23 | 25 | 29 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 145 | 0 | 0 | 0 |  | 12 | 47 | 17 | 12 | 44 | 6 | 0 | 2 | 0 | 0 | 0 | 75 | 305 | 196 | 8 | 72 | 30 | 44 | 0 | 0 | 0 | 36 | 8 | 0 | 0 | 24 | 11 | 74 | 76 | 0 | 0 | 0 | 38 | 58 | 45 | 26 | 0 | 0 | 54 | 0 | 0 | 199 | 0 | 0 | 0 | 305 | 24 | 2 | 0 | 300 | 0 | 0 | 57 | 0 | 146 | 14 | 48 | 71 | 12 | 366 | 48 | 50 | 36 | 0 | 52 | 0 | 35 | 17 | 39 | 48 | 330 | 70 | 50 | 162 | 35 | 0 | 17 | 32 | 17 | 17 | 270 | 17 | 0 | 400 | 4 | 500 | 0 | 0 | 71 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 50 | 0 | 130 | 8 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 414 | 73 | 0 | 0 | 15 | 0 | 0 | 7 | 0 | 1030 | 220 | 0 | 17 | 5 | 53 | 35 | 0 | 0 | 559 | 33 | 307 | 1219 | 194 | 0 |  | 7313 | 5913 | 13226 | 3537 | 920 | 1843 | 0 | 1779 | 4298 | 30 | 0 | 282 | 74 | 459 | 4 | 185.27 | 71.74
12:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 396 | 0 |  | 0 | 450 | 306 | 4 | 2 | 25 | 286 | 0 | 0 | 10 | 40 | 32 | 0 | 0 | 0 | 0 | 21 | 55 | 55 | 0 | 20 | 23 | 25 | 26 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 12 | 53 | 17 | 58 | 44 | 6 | 0 | 2 | 0 | 0 | 0 | 50 | 270 | 200 | 8 | 75 | 33 | 43 | 0 | 0 | 0 | 36 | 20 | 0 | 0 | 31 | 17 | 78 | 66 | 0 | 0 | 0 | 38 | 58 | 44 | 38 | 0 | 0 | 54 | 0 | 0 | 197 | 0 | 0 | 0 | 300 | 19 | 2 | 0 | 300 | 0 | 0 | 57 | 0 | 149 | 20 | 48 | 100 | 10 | 368 | 47 | 50 | 51 | 4 | 52 | 35 | 76 | 52 | 45 | 48 | 360 | 70 | 51 | 162 | 35 | 0 | 17 | 31 | 54 | 17 | 260 | 35 | 0 | 410 | 8 | 506 | 0 | 0 | 72 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 130 | 8 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 220 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 73 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 1140 | 220 | 0 | 17 | 5 | 52 | 41 | 0 | 0 | 580 | 31 | 307 | 1259 | 203 | 0 |  | 7618 | 6108 | 13726 | 3519 | 920 | 1845 | 0 | 2061 | 4484 | 30 | 8 | 296 | 78 | 477 | 8 | 213.92 | 71.74
13:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 399 | 0 |  | 0 | 450 | 300 | 34 | 38 | 25 | 286 | 0 | 0 | 55 | 90 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 25 | 26 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 135 | 0 | 0 | 0 |  | 12 | 52 | 27 | 58 | 44 | 6 | 0 | 3 | 0 | 0 | 0 | 0 | 310 | 206 | 8 | 80 | 29 | 42 | 0 | 0 | 0 | 41 | 34 | 0 | 0 | 31 | 17 | 78 | 56 | 0 | 0 | 0 | 33 | 57 | 45 | 40 | 0 | 0 | 51 | 0 | 0 | 197 | 0 | 0 | 0 | 280 | 16 | 2 | 0 | 300 | 0 | 0 | 56 | 0 | 145 | 18 | 48 | 104 | 12 | 394 | 46 | 50 | 51 | 0 | 52 | 35 | 110 | 52 | 45 | 48 | 350 | 70 | 49 | 162 | 35 | 0 | 17 | 29 | 91 | 17 | 315 | 54 | 0 | 456 | 14 | 453 | 0 | 0 | 69 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 0 | 80 | 7 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 351 | 90 | 0 | 0 | 32 | 0 | 0 | 4 | 0 | 1160 | 180 | 0 | 17 | 5 | 101 | 70 | 0 | 0 | 620 | 33 | 270 | 1308 | 194 | 0 |  | 7964 | 6102 | 14066 | 3489 | 920 | 1718 | 0 | 2403 | 4549 | 30 | 0 | 363 | 78 | 502 | 14 | 271 | 71.73
14:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 394 | 0 |  | 0 | 450 | 310 | 41 | 50 | 24 | 285 | 0 | 0 | 70 | 90 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 18 | 0 | 25 | 26 | 8 | 0 | 0 | 30 | 0 | 0 | 6 | 130 | 0 | 0 | 0 |  | 12 | 45 | 34 | 58 | 43 | 6 | 0 | 3 | 0 | 0 | 0 | 0 | 305 | 209 | 8 | 90 | 29 | 40 | 0 | 0 | 0 | 43 | 34 | 0 | 0 | 31 | 17 | 96 | 67 | 0 | 0 | 0 | 33 | 57 | 45 | 39 | 0 | 0 | 54 | 0 | 0 | 196 | 0 | 0 | 0 | 290 | 16 | 2 | 0 | 300 | 0 | 0 | 56 | 0 | 142 | 14 | 49 | 103 | 10 | 368 | 45 | 17 | 51 | 0 | 52 | 35 | 110 | 52 | 45 | 48 | 345 | 70 | 45 | 162 | 35 | 0 | 17 | 24 | 103 | 17 | 320 | 54 | 0 | 477 | 28 | 454 | 0 | 0 | 61 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 36 | 0 | 130 | 7 | 80 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 36 | 0 | 10 | 0 | 0 | 0 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 352 | 90 | 0 | 14 | 32 | 11 | 0 | 7 | 35 | 1160 | 220 | 0 | 17 | 4 | 79 | 85 | 0 | 0 | 626 | 29 | 270 | 1357 | 174 | 0 |  | 7986 | 6314 | 14300 | 3513 | 920 | 1776 | 0 | 2469 | 4627 | 30 | 0 | 404 | 96 | 437 | 28 | 239 | 71.74
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 390 | 0 |  | 0 | 450 | 307 | 41 | 70 | 26 | 290 | 0 | 0 | 75 | 90 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 0 | 0 | 0 | 26 | 8 | 0 | 0 | 30 | 0 | 0 | 8 | 133 | 0 | 0 | 0 |  | 12 | 47 | 34 | 58 | 43 | 6 | 0 | 3 | 0 | 0 | 0 | 0 | 305 | 207 | 8 | 85 | 29 | 38 | 0 | 0 | 0 | 43 | 33 | 0 | 0 | 0 | 16 | 92 | 57 | 0 | 0 | 2 | 33 | 60 | 47 | 39 | 0 | 0 | 42 | 0 | 0 | 195 | 0 | 0 | 0 | 295 | 19 | 2 | 0 | 293 | 0 | 0 | 54 | 0 | 113 | 0 | 49 | 102 | 12 | 369 | 45 | 17 | 51 | 0 | 52 | 35 | 110 | 52 | 45 | 48 | 358 | 70 | 37 | 162 | 35 | 0 | 17 | 19 | 84 | 17 | 350 | 17 | 0 | 492 | 7 | 567 | 0 | 0 | 28 |  | 920 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 26 | 36 | 32 | 130 | 9 | 80 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 33 | 0 | 16 | 0 | 0 | 0 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 392 | 90 | 0 | 35 | 45 | 34 | 0 | 6 | 60 | 1170 | 220 | 0 | 17 | 3 | 76 | 112 | 0 | 0 | 624 | 18 | 307 | 1323 | 136 | 0 |  | 7939 | 6473 | 14412 | 3468 | 920 | 1820 | 0 | 2610 | 4766 | 30 | 0 | 374 | 92 | 325 | 7 | 371 | 71.72
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 397 | 0 |  | 0 | 450 | 305 | 57 | 80 | 40 | 290 | 0 | 0 | 79 | 90 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 23 | 29 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 8 | 130 | 0 | 0 | 0 |  | 12 | 47 | 51 | 58 | 38 | 6 | 0 | 2 | 0 | 0 | 0 | 0 | 305 | 205 | 8 | 80 | 30 | 38 | 0 | 0 | 0 | 43 | 34 | 0 | 0 | 0 | 16 | 96 | 60 | 0 | 0 | 1 | 33 | 56 | 47 | 39 | 0 | 0 | 50 | 0 | 0 | 198 | 0 | 0 | 0 | 275 | 19 | 2 | 0 | 215 | 0 | 0 | 54 | 0 | 66 | 9 | 49 | 103 | 12 | 369 | 45 | 17 | 51 | 0 | 52 | 35 | 110 | 52 | 44 | 48 | 354 | 70 | 25 | 162 | 35 | 0 | 17 | 0 | 82 | 17 | 355 | 17 | 0 | 490 | 51 | 571 | 0 | 0 | 32 |  | 919 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 27 | 36 | 32 | 130 | 8 | 32 | 0 | 0 | 0 | 40 | 0 | 0 | 21 | 0 | 33 | 0 | 16 | 0 | 0 | 0 | 63 | 0 | 220 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 380 | 90 | 0 | 102 | 85 | 65 | 0 | 4 | 95 | 1120 | 220 | 0 | 17 | 2 | 44 | 113 | 0 | 0 | 552 | 16 | 250 | 1307 | 99 | 0 |  | 7942 | 6375 | 14317 | 3526 | 919 | 1784 | 0 | 2702 | 4573 | 30 | 12 | 392 | 96 | 232 | 51 | 605 | 71.72
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 396 | 0 |  | 0 | 450 | 306 | 63 | 80 | 40 | 291 | 0 | 0 | 80 | 90 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 23 | 29 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 12 | 131 | 0 | 0 | 0 |  | 12 | 64 | 51 | 69 | 44 | 6 | 0 | 5 | 0 | 0 | 0 | 0 | 320 | 203 | 8 | 80 | 31 | 37 | 0 | 0 | 0 | 43 | 31 | 0 | 0 | 0 | 16 | 92 | 59 | 0 | 0 | 1 | 33 | 56 | 47 | 39 | 0 | 0 | 49 | 0 | 0 | 194 | 0 | 0 | 0 | 300 | 19 | 2 | 0 | 193 | 0 | 0 | 58 | 0 | 70 | 4 | 49 | 103 | 12 | 377 | 46 | 17 | 51 | 0 | 52 | 35 | 110 | 52 | 44 | 48 | 352 | 70 | 12 | 162 | 35 | 0 | 18 | 7 | 84 | 0 | 355 | 17 | 0 | 485 | 28 | 575 | 0 | 0 | 12 |  | 919 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 32 | 36 | 32 | 80 | 8 | 32 | 0 | 0 | 0 | 39 | 15 | 0 | 35 | 0 | 30 | 0 | 30 | 0 | 0 | 0 | 62 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 350 | 90 | 0 | 112 | 32 | 92 | 0 | 3 | 113 | 1020 | 180 | 0 | 17 | 1 | 14 | 114 | 0 | 0 | 558 | 7 | 250 | 1310 | 32 | 0 |  | 7941 | 6107 | 14048 | 3496 | 919 | 1742 | 0 | 2739 | 4470 | 30 | 0 | 439 | 92 | 93 | 28 | 623 | 71.71
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 403 | 0 |  | 0 | 380 | 250 | 72 | 80 | 40 | 290 | 0 | 0 | 75 | 90 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 23 | 29 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 19 | 136 | 0 | 0 | 0 |  | 12 | 72 | 73 | 69 | 44 | 16 | 0 | 9 | 0 | 0 | 0 | 0 | 270 | 209 | 8 | 74 | 29 | 37 | 0 | 0 | 0 | 41 | 31 | 0 | 0 | 31 | 16 | 82 | 59 | 0 | 0 | 0 | 39 | 56 | 47 | 37 | 0 | 0 | 58 | 0 | 0 | 196 | 0 | 0 | 0 | 285 | 19 | 2 | 0 | 195 | 0 | 0 | 61 | 0 | 66 | 0 | 62 | 105 | 21 | 330 | 46 | 17 | 51 | 0 | 52 | 35 | 110 | 55 | 47 | 60 | 310 | 70 | 2 | 162 | 35 | 0 | 34 | 1 | 83 | 0 | 320 | 17 | 0 | 485 | 37 | 504 | 0 | 0 | 1 |  | 920 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 33 | 36 | 32 | 80 | 8 | 32 | 0 | 0 | 0 | 39 | 20 | 0 | 35 | 0 | 33 | 0 | 30 | 0 | 0 | 0 | 63 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 307 | 90 | 0 | 112 | 49 | 94 | 0 | 1 | 113 | 940 | 180 | 0 | 17 | 0 | 4 | 114 | 0 | 0 | 558 | 2 | 250 | 1316 | 15 | 0 |  | 7702 | 5983 | 13685 | 3361 | 920 | 1560 | 0 | 2851 | 4326 | 30 | 0 | 492 | 82 | 26 | 37 | 492 | 71.71
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 396 | 0 |  | 0 | 400 | 300 | 93 | 80 | 40 | 286 | 0 | 0 | 70 | 90 | 149 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 23 | 29 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 137 | 0 | 0 | 0 |  | 12 | 72 | 85 | 69 | 45 | 19 | 0 | 12 | 0 | 0 | 0 | 0 | 265 | 214 | 8 | 70 | 33 | 41 | 0 | 0 | 0 | 43 | 46 | 0 | 0 | 31 | 10 | 82 | 58 | 0 | 0 | 0 | 40 | 56 | 49 | 38 | 0 | 0 | 60 | 0 | 0 | 200 | 0 | 0 | 0 | 270 | 16 | 0 | 0 | 195 | 0 | 0 | 107 | 0 | 99 | 0 | 62 | 136 | 35 | 352 | 97 | 52 | 51 | 0 | 52 | 35 | 110 | 97 | 73 | 60 | 385 | 70 | 0 | 162 | 50 | 0 | 0 | 0 | 83 | 0 | 280 | 163 | 0 | 488 | 47 | 526 | 0 | 0 | 0 |  | 920 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 33 | 45 | 40 | 130 | 2 | 48 | 0 | 0 | 0 | 40 | 20 | 85 | 35 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 370 | 90 | 0 | 113 | 85 | 104 | 0 | 0 | 113 | 870 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 276 | 1319 | 0 | 0 |  | 8352 | 6271 | 14623 | 3439 | 920 | 1710 | 0 | 3242 | 4353 | 30 | 0 | 800 | 82 | 0 | 47 | 265 | 71.69
19:30 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 372 | 0 |  | 0 | 330 | 250 | 96 | 80 | 55 | 290 | 0 | 0 | 75 | 90 | 149 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 30 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 136 | 0 | 0 | 0 |  | 12 | 72 | 85 | 69 | 45 | 19 | 0 | 12 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 70 | 0 | 0 | 0 | 0 | 0 | 44 | 51 | 0 | 0 | 32 | 5 | 90 | 55 | 0 | 0 | 0 | 40 | 58 | 49 | 38 | 0 | 0 | 60 | 0 | 0 | 203 | 0 | 0 | 0 | 290 | 16 | 0 | 0 | 195 | 0 | 0 | 111 | 0 | 149 | 0 | 62 | 155 | 60 | 385 | 98 | 52 | 51 | 0 | 52 | 35 | 110 | 97 | 75 | 60 | 350 | 70 | 0 | 162 | 53 | 0 | 0 | 0 | 100 | 0 | 300 | 163 | 0 | 489 | 48 | 574 | 0 | 0 | 0 |  | 919 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 33 | 48 | 40 | 130 | 2 | 48 | 0 | 0 | 0 | 39 | 20 | 85 | 35 | 0 | 39 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 245 | 90 | 0 | 113 | 85 | 105 | 0 | 0 | 113 | 960 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 307 | 1313 | 0 | 0 |  | 8176 | 6270 | 14446 | 3179 | 919 | 1444 | 0 | 3396 | 4541 | 30 | 0 | 799 | 90 | 0 | 48 | 338 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 381 | 0 |  | 0 | 400 | 305 | 96 | 80 | 55 | 285 | 0 | 0 | 75 | 90 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 0 | 30 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 136 | 0 | 0 | 0 |  | 12 | 72 | 85 | 25 | 44 | 19 | 0 | 14 | 0 | 0 | 0 | 0 | 270 | 0 | 8 | 70 | 0 | 0 | 0 | 0 | 0 | 44 | 51 | 0 | 0 | 32 | 5 | 84 | 50 | 0 | 0 | 0 | 40 | 58 | 49 | 42 | 0 | 0 | 61 | 0 | 0 | 202 | 0 | 0 | 0 | 280 | 23 | 0 | 0 | 130 | 0 | 0 | 115 | 0 | 146 | 0 | 62 | 145 | 58 | 365 | 99 | 52 | 51 | 0 | 52 | 17 | 110 | 97 | 75 | 60 | 340 | 70 | 0 | 162 | 53 | 0 | 0 | 0 | 96 | 0 | 300 | 163 | 0 | 490 | 45 | 573 | 0 | 0 | 0 |  | 629 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 42 | 60 | 40 | 130 | 8 | 64 | 0 | 0 | 0 | 40 | 30 | 85 | 35 | 0 | 47 | 0 | 22 | 0 | 0 | 8 | 65 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 305 | 90 | 0 | 113 | 105 | 105 | 0 | 0 | 113 | 970 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 626 | 0 | 307 | 1307 | 0 | 0 |  | 8085 | 6134 | 14219 | 3119 | 629 | 1631 | 0 | 3294 | 4548 | 30 | 0 | 839 | 84 | 0 | 45 | 268 | 71.7
21:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 315 | 96 | 80 | 55 | 220 | 0 | 0 | 75 | 90 | 149 | 13 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 17 | 23 | 0 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 136 | 0 | 0 | 0 |  | 10 | 72 | 85 | 16 | 45 | 19 | 0 | 20 | 0 | 0 | 0 | 0 | 335 | 28 | 20 | 70 | 29 | 1 | 0 | 0 | 0 | 44 | 51 | 0 | 0 | 32 | 17 | 90 | 54 | 0 | 0 | 0 | 40 | 58 | 49 | 42 | 0 | 0 | 60 | 0 | 0 | 198 | 0 | 0 | 0 | 310 | 24 | 0 | 0 | 95 | 0 | 0 | 112 | 0 | 149 | 0 | 62 | 155 | 60 | 395 | 98 | 52 | 51 | 0 | 52 | 23 | 110 | 97 | 76 | 60 | 352 | 70 | 0 | 126 | 53 | 0 | 0 | 0 | 108 | 20 | 385 | 108 | 0 | 490 | 23 | 577 | 0 | 0 | 0 |  | 629 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 34 | 55 | 8 | 130 | 8 | 32 | 0 | 0 | 0 | 40 | 30 | 79 | 35 | 0 | 44 | 0 | 22 | 0 | 0 | 8 | 65 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 414 | 90 | 0 | 113 | 50 | 106 | 0 | 0 | 113 | 1070 | 22 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 307 | 1311 | 0 | 0 |  | 8236 | 6056 | 14292 | 3376 | 629 | 1601 | 0 | 3127 | 4654 | 30 | 0 | 762 | 90 | 0 | 23 | 0 | 71.69
22:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 310 | 94 | 80 | 55 | 220 | 0 | 0 | 68 | 90 | 149 | 13 | 0 | 0 | 0 | 38 | 55 | 55 | 0 | 0 | 23 | 0 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 136 | 0 | 0 | 0 |  | 5 | 72 | 85 | 68 | 44 | 19 | 0 | 27 | 0 | 0 | 0 | 0 | 330 | 46 | 8 | 50 | 31 | 24 | 0 | 0 | 0 | 44 | 51 | 0 | 0 | 32 | 17 | 90 | 70 | 0 | 0 | 0 | 43 | 58 | 49 | 42 | 0 | 0 | 54 | 0 | 0 | 198 | 0 | 0 | 0 | 315 | 24 | 2 | 0 | 95 | 0 | 0 | 116 | 0 | 149 | 0 | 62 | 155 | 58 | 402 | 99 | 52 | 51 | 0 | 51 | 35 | 110 | 97 | 78 | 60 | 370 | 70 | 0 | 144 | 53 | 0 | 14 | 0 | 111 | 25 | 305 | 17 | 0 | 490 | 44 | 575 | 0 | 0 | 0 |  | 629 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 34 | 51 | 32 | 130 | 8 | 32 | 0 | 0 | 0 | 40 | 30 | 79 | 35 | 0 | 42 | 0 | 22 | 0 | 0 | 8 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 414 | 90 | 0 | 113 | 95 | 106 | 0 | 0 | 113 | 1244 | 48 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1313 | 0 | 0 |  | 8230 | 6333 | 14563 | 3342 | 629 | 1645 | 0 | 3293 | 4825 | 30 | 0 | 665 | 90 | 0 | 44 | 35 | 71.69
23:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 393 | 0 |  | 0 | 400 | 315 | 99 | 80 | 30 | 220 | 0 | 0 | 60 | 82 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 15 | 25 | 14 | 0 | 0 | 0 | 30 | 0 | 0 | 11 | 136 | 0 | 0 | 0 |  | 12 | 72 | 85 | 68 | 44 | 19 | 0 | 16 | 0 | 0 | 0 | 0 | 270 | 56 | 0 | 50 | 31 | 30 | 0 | 0 | 0 | 46 | 51 | 0 | 0 | 32 | 17 | 90 | 70 | 0 | 0 | 0 | 40 | 58 | 49 | 42 | 0 | 0 | 59 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 24 | 2 | 0 | 95 | 0 | 0 | 107 | 0 | 111 | 0 | 62 | 155 | 55 | 390 | 99 | 52 | 51 | 0 | 51 | 35 | 110 | 97 | 85 | 48 | 385 | 70 | 0 | 162 | 53 | 0 | 35 | 0 | 111 | 17 | 215 | 17 | 0 | 490 | 35 | 576 | 0 | 0 | 0 |  | 621 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 34 | 52 | 40 | 130 | 10 | 64 | 0 | 0 | 0 | 40 | 30 | 77 | 35 | 0 | 42 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 414 | 90 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 1244 | 121 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 307 | 1326 | 0 | 0 |  | 7961 | 6472 | 14433 | 3237 | 621 | 1697 | 0 | 3271 | 4853 | 30 | 0 | 599 | 90 | 0 | 35 | 971 | 71.68
24:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 368 | 0 |  | 0 | 400 | 312 | 98 | 80 | 30 | 220 | 0 | 0 | 62 | 82 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 23 | 33 | 14 | 0 | 0 | 0 | 30 | 0 | 0 | 8 | 136 | 0 | 0 | 0 |  | 12 | 72 | 68 | 68 | 44 | 6 | 0 | 30 | 0 | 0 | 0 | 0 | 240 | 68 | 0 | 70 | 31 | 30 | 0 | 0 | 0 | 46 | 50 | 0 | 0 | 31 | 17 | 90 | 64 | 0 | 0 | 0 | 40 | 30 | 49 | 42 | 0 | 0 | 55 | 0 | 0 | 205 | 0 | 0 | 0 | 310 | 24 | 2 | 0 | 95 | 0 | 0 | 107 | 0 | 52 | 0 | 49 | 155 | 53 | 406 | 99 | 17 | 34 | 0 | 52 | 35 | 99 | 52 | 86 | 48 | 382 | 70 | 0 | 162 | 53 | 0 | 35 | 0 | 111 | 17 | 215 | 17 | 0 | 490 | 40 | 575 | 0 | 0 | 0 |  | 621 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 33 | 52 | 40 | 130 | 1 | 64 | 0 | 0 | 0 | 40 | 20 | 79 | 35 | 0 | 42 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 411 | 90 | 0 | 113 | 105 | 107 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 307 | 1306 | 0 | 0 |  | 7741 | 6536 | 14277 | 3212 | 621 | 1805 | 0 | 3075 | 4831 | 30 | 0 | 573 | 90 | 0 | 40 | 1168 | 71.68
KWH | 0 | 0 | 0 | 4221000 | 0 | 224772 | 0 | 9342000 | 0 |  | 0 | 9772000 | 7137193 | 1423680 | 1360544 | 780776 | 6394421 | 0 | 0 | 1371840 | 1819440 | 1660320 | 44411 | 0 | 0 | 0 | 1056960 | 1322032 | 1301931 | 0 | 421800 | 454320 | 509760 | 552800 | 117120 | 0 | 3300 | 720000 | 100000 | 0 | 186561 | 3354051 | 0 | 0 | 0 |  | 285600 | 1428864 | 946902 | 1044240 | 1064640 | 223200 | 0 | 467040 | 0 | 0 | 0 | 3131500 | 6826000 | 4108000 | 117091 | 1380330 | 719568 | 900480 | 0 | 0 | 0 | 1023984 | 827006 | 0 | 0 | 671300 | 332440 | 1824960 | 1780800 | 0 | 0 | 3200 | 896000 | 1407360 | 1142400 | 914112 | 0 | 0 | 1283424 | 0 | 0 | 4044320 | 0 | 0 | 0 | 7133500 | 475056 | 33072 | 0 | 5339345 | 0 | 0 | 1802400 | 0 | 2298384 | 93690 | 1202880 | 2422560 | 546981 | 8857000 | 1550400 | 683520 | 913309 | 17836 | 1259564 | 748943 | 2042391 | 1347480 | 1232280 | 1208640 | 8324200 | 1672320 | 399280 | 3476160 | 1028727 | 0 | 485640 | 214911 | 1972800 | 390600 | 6664500 | 812945 | 0 | 11470908 | 526560 | 12560000 | 1397272 | 0 | 539245 |  | 20288000 | 0 | 0 | 0 | 997440 | 0 | 0 | 0 | 648480 | 1019264 | 464250 | 2462000 | 183351 | 1799136 | 0 | 0 | 0 | 808215 | 144516 | 485152 | 493050 | 0 | 607910 | 0 | 286497 | 0 | 0 | 113364 | 1465309 | 0 | 5148000 | 0 | 10000 | 0 | 0 | 195609 | 0 | 0 | 0 | 4652300 | 0 | 8494109 | 1939680 | 0 | 1794720 | 1502928 | 1599984 | 0 | 58953 | 1764096 | 28825000 | 4374600 | 0 | 614400 | 38160 | 685440 | 2313792 | 0 | 0 | 14509090 | 249615 | 6785500 | 30916363 | 1548190 | 0 |  | 187593092 | 150286463 | 337879555 | 83708295 | 20288000 | 42257920 | 0 | 63138781 | 111680170 | 723300 | 10000 | 9873049 | 1824960 | 3848520 | 526560 | 0
Fuel Cost | 0 | 0 | 0 | 18783450 | 0 | 858629.04 | 0 | 26904960 | 0 |  | 0 | 31074960 | 24409200.06 | 28131916.8 | 25442172.8 | 13757273.12 | 19502984.05 | 0 | 0 | 27107558.4 | 32658948 | 32243414.4 | 828265.15 | 0 | 0 | 0 | 19300089.6 | 20835224.32 | 23812317.99 | 0 | 316350 | 0 | 0 | 0 | 2097619.2 | 0 | 0 | 0 | 546000 | 0 | 3533465.34 | 10699422.69 | 0 | 0 | 0 |  | 5023704 | 25162295.04 | 16959014.82 | 19903214.4 | 20835004.8 | 3673872 | 0 | 0 | 0 | 0 | 0 | 8736885 | 20887560 | 13638560 | 392254.85 | 4458465.9 | 2424944.16 | 3944102.4 | 0 | 0 | 0 | 18339553.44 | 14935728.36 | 0 | 0 | 2497236 | 249330 | 11971737.6 | 5538288 | 0 | 0 | 0 | 3494400 | 5249452.8 | 5197920 | 4159209.6 | 0 | 0 | 7123003.2 | 0 | 0 | 11283652.8 | 0 | 0 | 0 | 22042515 | 356292 | 25134.72 | 0 | 108922638 | 0 | 0 | 34624104 | 0 | 40474542.24 | 0 | 21423292.8 | 42031416 | 9068944.98 | 23471050 | 29550624 | 12822835.2 | 16384763.46 | 0 | 20593871.4 | 14559451.92 | 36640494.54 | 25750342.8 | 23918554.8 | 21525878.4 | 22142372 | 28546502.4 | 0 | 63578966.4 | 17262039.06 | 0 | 8678386.8 | 0 | 35549856 | 6616764 | 19793565 | 11446265.6 | 0 | 79952228.76 | 0 | 74104000 | 0 | 0 | 0 |  | 57009280 | 0 | 0 | 0 | 17305584 | 0 | 0 | 0 | 12197908.8 | 19172355.84 | 8263650 | 7779920 | 869083.74 | 31017104.64 | 0 | 0 | 0 | 14475130.65 | 2651868.6 | 8155405.12 | 10492104 | 0 | 10887668.1 | 0 | 5131161.27 | 0 | 0 | 85816.548 | 16162358.27 | 0 | 43449120 | 0 | 470200 | 0 | 0 | 651377.97 | 0 | 0 | 0 | 15492159 | 0 | 24802798.28 | 33129734.4 | 0 | 35571350.4 | 26571767.04 | 31871681.28 | 0 | 0 | 34999664.64 | 186786000 | 13605006 | 0 | 11888640 | 0 | 0 | 40144291.2 | 0 | 0 | 105916357 | 0 | 50551975 | 204357159.43 | 0 | 0 |  | 1470781302.41 | 1081915681.218 | 2552696983.628 | 252132631.838 | 57009280 | 131355678.97 | 0 | 1161656215.08 | 761279198.46 | 0 | 470200 | 176822041.68 | 11971737.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 396 | 0 |  | 0 | 450 | 306 | 4 | 2 | 25 | 286 | 0 | 0 | 10 | 40 | 32 | 0 | 0 | 0 | 0 | 21 | 55 | 55 | 0 | 20 | 23 | 25 | 26 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 143 | 0 | 0 | 0 |  | 12 | 53 | 17 | 58 | 44 | 6 | 0 | 2 | 0 | 0 | 0 | 50 | 270 | 200 | 8 | 75 | 33 | 43 | 0 | 0 | 0 | 36 | 20 | 0 | 0 | 31 | 17 | 78 | 66 | 0 | 0 | 0 | 38 | 58 | 44 | 38 | 0 | 0 | 54 | 0 | 0 | 197 | 0 | 0 | 0 | 300 | 19 | 2 | 0 | 300 | 0 | 0 | 57 | 0 | 149 | 20 | 48 | 100 | 10 | 368 | 47 | 50 | 51 | 4 | 52 | 35 | 76 | 52 | 45 | 48 | 360 | 70 | 51 | 162 | 35 | 0 | 17 | 31 | 54 | 17 | 260 | 35 | 0 | 410 | 8 | 506 | 0 | 0 | 72 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 40 | 0 | 130 | 8 | 80 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 220 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 73 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 1140 | 220 | 0 | 17 | 5 | 52 | 41 | 0 | 0 | 580 | 31 | 307 | 1259 | 203 | 0 |  | 13726 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 396 | 0 |  | 0 | 400 | 300 | 93 | 80 | 40 | 286 | 0 | 0 | 70 | 90 | 149 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 23 | 29 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 137 | 0 | 0 | 0 | 0 | 12 | 72 | 85 | 69 | 45 | 19 | 0 | 12 | 0 | 0 | 0 | 0 | 265 | 214 | 8 | 70 | 33 | 41 | 0 | 0 | 0 | 43 | 46 | 0 | 0 | 31 | 10 | 82 | 58 | 0 | 0 | 0 | 40 | 56 | 49 | 38 | 0 | 0 | 60 | 0 | 0 | 200 | 0 | 0 | 0 | 270 | 16 | 0 | 0 | 195 | 0 | 0 | 107 | 0 | 99 | 0 | 62 | 136 | 35 | 352 | 97 | 52 | 51 | 0 | 52 | 35 | 110 | 97 | 73 | 60 | 385 | 70 | 0 | 162 | 50 | 0 | 0 | 0 | 83 | 0 | 280 | 163 | 0 | 488 | 47 | 526 | 0 | 0 | 0 |  | 920 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 33 | 45 | 40 | 130 | 2 | 48 | 0 | 0 | 0 | 40 | 20 | 85 | 35 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 64 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 370 | 90 | 0 | 113 | 85 | 104 | 0 | 0 | 113 | 870 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 276 | 1319 | 0 | 0 |  | 14623 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 310 | 90 | 80 | 55 | 300 | 0 | 0 | 90 | 90 | 150 | 15 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 23 | 33 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 25 | 150 | 0 | 0 | 0 |  | 12 | 64 | 85 | 70 | 60 | 20 | 0 | 20 | 0 | 0 | 0 | 0 | 280 | 220 | 0 | 50 | 36 | 50 | 0 | 0 | 0 | 40 | 52 | 0 | 0 | 32 | 20 | 151 | 80 | 0 | 0 | 0 | 42 | 60 | 50 | 42 | 0 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 105 | 0 | 149 | 0 | 62 | 155 | 50 | 400 | 100 | 50 | 51 | 0 | 52 | 35 | 110 | 114 | 75 | 60 | 360 | 72 | 0 | 162 | 53 | 0 | 50 | 0 | 115 | 35 | 280 | 163 | 0 | 490 | 40 | 575 | 0 | 0 |  |  | 655 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 42 | 60 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 25 | 90 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 11 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 414 | 90 | 0 | 113 | 100 | 107 | 0 | 0 | 113 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1425 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 310 | 90 | 80 | 55 | 150 | 0 | 0 | 85 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 20 | 23 | 33 | 33 | 8 | 0 | 0 | 30 | 0 | 0 | 8 | 150 |  | 0 | 0 | 0 | 12 | 55 | 51 | 70 | 45 | 6 | 0 | 10 | 0 | 0 | 0 | 0 | 270 | 210 | 0 | 50 | 35 | 50 | 0 | 0 | 0 | 39 | 25 | 0 | 0 | 32 | 20 | 146 | 45 | 0 | 0 | 1.6 | 42 | 60 | 50 | 42 | 0 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 24 | 5 | 0 | 300 | 0 | 0 | 58 | 0 | 115 | 20 | 49 | 100 | 12 | 400 | 57 | 17 | 34 | 5 | 52 | 35 | 51 | 52 | 36 | 48 | 345 | 53 | 50 | 162 | 35 | 0 | 50 | 35 | 115 | 17 | 250 | 54 | 0 | 490 | 40 | 575 | 0 | 0 | 70 |  | 944 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 0 | 0 | 14 | 0 | 42 | 0 | 0 | 0 | 0 | 11 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 350 | 53 | 0 | 50 | 15 | 70 | 0 | 8 | 50 | 1244 | 220 |  | 17 | 6 | 100 | 115 | 0 | 0 | 620 | 30 | 250 | 1425 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 450 | 320 | 89 | 80 | 30 | 0 | 0 | 0 | 68 | 82 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 23 | 33 | 14 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 0 | 12 | 58 | 17 | 25 | 31 | 6 | 0 | 5 | 0 | 0 | 0 | 0 | 240 | 183 | 0 | 50 | 20 | 10 | 0 | 0 | 0 | 39 | 25 | 0 | 0 | 32 | 17 | 76 | 31 | 0 | 0 | 1 | 40 | 30 | 46 | 42 | 0 | 0 | 61 | 0 | 0 | 206 | 0 | 0 | 0 | 270 | 24 | 2 | 0 | 145 | 0 | 0 | 58 | 0 | 34 | 2 | 37 | 68 | 13 | 318 | 49 | 17 | 17 | 0 | 52 | 35 | 68 | 52 | 38 | 48 | 310 | 51 | 9 | 162 | 35 | 0 | 17 | 6 | 108 | 17 | 210 | 17 | 0 | 368 | 59 | 576 | 0 | 0 | 21 | 0 | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 33 | 28 | 32 | 80 | 0 | 16 | 0 | 0 | 0 | 23 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 335 | 53 | 0 | 70 | 15 | 70 | 0 | 2 | 70 | 1020 | 180 | 0 | 17 | 1 | 10 | 75 | 0 | 0 | 512 | 9 | 250 | 1318 | 44 | 0 | 0 |  |  |  | 125966215 | 20288000 | 10000 | 111680170 | 73011830 | 1824960 | 3848520 | 526560 | 723300 |  |  | 337869555
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 125.9662 | 20.288 | 0.01 | 111.6802 | 73.0118 | 1.825 | 3.8485 | 0.52656 | 0.7233
| Minimum Generation |  | 12749 | 9:00
| Highest Generation |  | 14707 | 1:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 337.8796
| Day Peak Generation |  | 13726 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 14623 | 19:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 926 | 3:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 920 | 19:00
| Load factor L.F |  | 95.73% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-05-26
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-05-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13726 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12391
Evening Peak Generation : |  |  | 14623 | MW Hour : | 19:00 | Available Max Generation : |  | 15838
E.P. Demand (at gen end) : |  |  | 14900 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 14707 | MW Hour : | 1:00 | Reserve(Generation end) |  | 838
Total Gen. (MKWH) : |  |  | 337.8796 | System Load Factor : | 95.73% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 244 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-05-26
Actual : |  | 71.68 | Ft.(MSL) , | Rule curve : | 77.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 915.18 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 383488310.808
: |  |  | Coal : | 761279198.46 | Oil : | 1338948456.76 | Total : | 2483715966.028
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 75 | 1800:00 | 5019.2107 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1381.88 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1936.5624 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1683.9775 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1385.229 |  |  | 0 | 0%
Mymensingh Area |  | 190 | 4560:00 | 1030.6659 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 577.2872 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 481.4952 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 941.7111 |  |  | 0 | 0%
Total |  | 265 |  | 14438.019 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:15 | 18:35 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D
8:16 | 18:36 | Fatullah-Madanganj 132 kV Ckt-2 Project Work S/D from Fatullah 132/33kV end.
8:44 | 8:53 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance relay. relays Due to There are no
reason finding till now.
9:21 | 9:27 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance Relay. relays Due to There are no
reason finding till now.
9:22 | 9:28 | Rampur 230/132/33 S/S Halishahar-2 Tripped showing REL670 relays Due to Zone-1, B-PH Trip, ZCOM/WEI Trip,General trip. |  |  |  |  | 115.0MW load interrup.
Distance: 6.314km
9:23 | 11:32 | Ullahpara 132/33kV S/S Power Transformer -1 LT Project Work S/D Due to 132 kV T-1 BKR SF6 Gas Leakage Maintenance work.
9:25 | 11:30 | Ullahpara 132/33kV S/S Power Transformer -1 HT Project Work S/D Due to 132kV T1 BKR SF6 gas leakage Maintenance work
9:37 | 9:46 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end.
10:00 | 10:15 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing C phase relays Due to No reason find told till now
10:01 | 10:10 | Rampur 230/132/33 S/S Halishahar-2 Tripped showing REL670 relays Due to Zone-1, B-PH Trip, ZCOM/WEI Trip,General trip. |  |  |  |  | 114.0MW load interrup.
Distance: 6.264km
10:09 | 10:23 | Hathazari 230/132/33kV S/S T-02 LT Tripped showing special protection relays. |  |  |  |  | 15.0MW load interrup.
10:09 | 10:23 | Hathazari 230/132/33kV S/S T-01 LT Tripped showing special protection relays Due to None |  |  |  |  | 47.0MW load interrup.
- | 10:20 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 is restored.
- | 10:25 | Khulshi-MSML 132kV Ckt-2 is restored.
- | 10:28 | Nawabganj 132/33kV S/S TR-1 HT is restored.
- | 10:30 | Nawabganj 132/33kV S/S TR-1 LT is restored.
10:37 | 13:55 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Tr-2 main Bus-2 Isolator 411 replacement work.
10:37 | 13:55 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Tr-2 main Bus-2 Isolator 411 replacement work.
10:48 | 13:45 | Savar 132/33kV S/S Transfer Bus Scheduled S/D Due to Maintenance work
- | 11:10 | Savar 132/33kV S/S Capacitor Bank-3 is restored.
- | 11:10 | Savar 132/33kV S/S Capacitor Bank-2 is restored.
- | 11:11 | Bakulia-Khulshi 132 kV Ckt-1 is restored.
- | 11:38 | Rampur 230/132/33 S/S 132kV BUS-02 is restored.
11:58 | 12:43 | Joydebpur 132/33kV S/S GT-2 HT Tripped showing Back-Up Protection Trip relays. |  |  |  |  | 82.0MW load interrup.
12:00 | - | Day peak generation is 13726 MW.
12:57 | 13:16 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Forced S/D Due to Ordered by ALDC Bagura
13:11 | 14:00 | Joydebpur 132/33kV S/S GT-2 HT Tripped showing Back-Up Protection Trip relays. |  |  |  |  | 95.0MW load interrup.
- | 13:22 | Hathazari 230/132/33kV S/S MT-03 LT is restored.
- | 13:22 | Hathazari 230/132/33kV S/S MT-03 HT is restored.
- | 13:28 | AKSML-Khulshi 132kV Ckt-1 is restored.
13:32 | 16:43 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Scheduled S/D |  |  |  |  | 60.0MW load interrup.
14:26 | 0:31 | Cumilla(N)-Kachua 132 kV Ckt-2 Forced S/D from Kachua 132/33kV end Due to Emergency work at Cumilla North end
14:27 | 0:44 | Cumilla(S)-Kachua 132 kV Ckt-1 Forced S/D from Cumilla(N) 230/132/33kV end Due to R-phase CVT remove and installation.
15:32 | 16:43 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Scheduled S/D |  |  |  |  | 60.0MW load interrup.
- | 15:43 | Joypurhat 132/33kV S/S Naogaon Ckt.-2 is restored.
- | 15:47 | Jamalpur 132/33kV S/S T-2 HT is restored.
- | 15:48 | Jamalpur 132/33kV S/S T-2 LT is restored.
- | 15:49 | Jamalpur 132/33kV S/S T-1 LT is restored.
- | 15:49 | Jamalpur 132/33kV S/S T-1 HT is restored.
- | 18:28 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT is restored.
- | 18:31 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT is restored.
19:00 | - | Evening Peak Gen. 14631 MW
19:01 | 19:08 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-2 Tripped showing 7SD5 relays Due to Dir. Over Current |  |  |  |  | 135.0MW load interrup.
19:01 | 20:43 | Ashuganj-Kishoreganj 132kV Ckt-2 Tripped from Kishoreganj 132/33kV end showing Dist: R,Y, Z1, 32.4 km relays Due to
Dist: R,Y, Z1, 32.4 km
19:01 | 20:19 | Ashuganj-Kishoreganj 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing Dist: R,Y, Z1, 33.2 km relays Due to
Dist: R,Y, Z1, 33.2 km
19:01 | 19:09 | Bhaluka 132/33kV S/S Sreepur Ckt- 02 Tripped showing Siprotec Model 7SD5 relays Due to Over current |  |  |  |  | 140.0MW load interrup.
19:01 | 19:09 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Tripped showing Siprotec Model 7SD5 relays Due to Overcurrent |  |  |  |  | 140.0MW load interrup.
- | 19:03 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 is restored.
19:25 | 22:51 | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 Scheduled S/D from Cumilla(S) 132/33kV end Due to Old CVT Open for Cumilla North S/S
19:37 | 19:57 | Kodda-Rajendrapur 132kV Ckt-2 Tripped from Kodda 132/33kV end showing Distance Relay relays Due to Without Reason
20:03 | 20:23 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing Phase Y, Z1, Dist. send. relays Due to Unknown.
20:05 | - | Bhola CCPP tripped due to voltage fluctuation
20:06 | - | Bhola Nutan Bidyut CCPP GT-12 & ST tripped due to voltage fluctuation.
20:06 | 20:17 | Barishal 230/132kV S/S T-4 LT Tripped showing Micom P142 relays Due to Pbs Jhalokathi 33kv ct blast |  |  |  |  | 25.0MW load interrup.
20:06 | 20:17 | Barishal 230/132kV S/S T-5 LT Tripped showing Micom P142 relays Due to Pbs jhalokathi 33kv ct Blast |  |  |  |  | 25.0MW load interrup.
20:18 | - | Bhola CCPP GT-1 was synch.
20:23 | - | Bhola CCPP GT-2 was synch.
- | 20:43 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
21:17 | - | Bhola Nutan Bidyut CCPP GT-12 was synch.
23:25 | 1:04 | Chauddagram 132/33kV S/S 132 kv T-2 LT Forced S/D Due to Emergency red hot maintenance. |  |  |  |  | 33.0MW load interrup.
23:25 | 1:04 | Chauddagram 132/33kV S/S 132 kv T-2 HT Forced S/D Due to Emergency red hot maintenance. |  |  |  |  | 33.0MW load interrup.
7:00 | - | Minimum Generation = 12,759MW
06:41 |  | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from
Shikalbaha 230/132kV end Due to Bus-Shut down at Shahmirpur
End.
06:47 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from
Kaliakoir 400/230/132kV end Due to BY NLDC
06:48 |  | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from
Kaliakoir 400/230/132kV end Due to By NLDC
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-05-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4221000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 224772 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 396 | 9342000
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9772000 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 93 | 1423680 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 7137193 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 80 | 1360544 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 40 | 780776 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 10 | 44411 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 70 | 1371840 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 286 | 6394421 | DP high
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 1819440 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1056960
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1660320
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1322032
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1301931
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 876120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 509760
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 14 | 552800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 117120 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 5339345 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 99 | 2298384 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 683520 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1672320 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3476160
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 214911
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 390600 | Engine problem
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 1397272 | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | Gas shortage
| Dhaka area Total |  |  |  | 5332 | 2927 | 66761632
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 100000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 186561
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 93690
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 223200 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 723300 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 137 | 3354051 | ST Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 913309 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 72 | 1428864 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 946902 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 69 | 1044240 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 1202880 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 467040
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 1064640 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17836
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1259564 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 748943 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2042391
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 1208640 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 50 | 1028727 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 812945
60 | SS Power I |  | SS Power | 2*612 | 1224 | 488 | 11470908
| Cox's Bazar Wind |  | IPP | 66 | 60 | 47 | 526560 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 526 | 12560000
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 539245
| Chattogram area Total |  |  |  | 4404 | 2138 | 43964436
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 4108000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 3131500 | Under maint.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6826000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 280 | 6664500 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 719568 | Engine problem
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 41 | 900480 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 117091 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Gas shortage
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 35 | 546981 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 1023984 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1380330 | ST Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2422560 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 82 | 1824960
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 31 | 671300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 46 | 827006
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 10 | 332440 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1347480 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1232280 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 485640
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 83 | 1972800 | Fuel shortage
| Cumilla Area Total |  |  |  | 2929 | 1547 | 36534900
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 58 | 1780800 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3200
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 107 | 1802400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 97 | 1550400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 399280
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 285600 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 274 | 5821680
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 896000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 56 | 1407360 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1142400
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 38 | 914112 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 33072 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1283424
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 200 | 4044320 | Machine problem
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 475056 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7133500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 352 | 8857000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 385 | 8324200 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1466 | 34510444
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 920 | 20288000
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 85 | 997440
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 648480 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 1019264 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 40 | 464250
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1939680 | Engine problem
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1502928 | Engine problem
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 685440
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 600 | 14509090
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1898 | 42054572
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 1799136 | Reserve
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 2 | 183351
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2462000 | Engine problem
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 870 | 28825000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4374600
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 614400 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 276 | 6785500
| Barisal Area Total |  |  |  | 2235 | 1563 | 45043987
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 808215 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 144516 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 493050
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 607910 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 195609
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 157 | 4652300 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 370 | 8494109 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 286497 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 113364 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 485152 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1794720
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1764096
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38160
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1319 | 30916363
| Rajshahi Area Total |  |  |  | 3431 | 2317 | 50794061
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 64 | 1465309
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5148000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 10000
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1599984 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 58953
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2313792
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 249615
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1548190
| Rangpur Area Total |  |  |  | 950 | 493 | 12393843
| Total |  |  |  | 25903 | 14623 | 337879555
| Eastern Grid Total |  |  |  | 15588 | 8352 | 187593092
| Western Grid Total |  |  |  | 10315 | 6271 | 150286463
| National Grid Total |  |  |  | 25903 | 14623 | 337879555
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-05-25
| (a) ENTIRE EASTERN GRID : |  | 9753.94 | MW | (b) ENTIRE WESTERN GRID : |  | 4452.5 | MW
| i) Dhaka area |  | 5869.44 | MW | i) Khulna area |  | 1862.2 | MW
| ii) Chittagong area |  | 1422.5 | MW | ii) Rajshahi area |  | 1440.8 | MW
| iii) Comilla area |  | 1116 | MW | iii) Barisal area |  | 193.5 | MW
| iv) Mymensingh area |  | 1062 | MW | iv) Rangpur area |  | 956 | MW
| v) Sylhet area |  | 284 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14206.44 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 9 | 20:00 | Chhatak | 38 | 20:00 | Kalurghat | 39 | 15:00 | Narail | 65 | 00:00 | Shariatpur | 97 | 00:00
2 | AKSML | 106 | 03:00 | Chowmuhani | 228 | 00:00 | Kamrangirchar | 58.8 | 16:00 | Narinda | 53 | 12:00 | Sherpur | 154 | 21:00
3 | Aftabnagar | 48 | 00:00 | Chuadanga | 118 | 23:00 | Kaptai | N/A | N/A | Narshingdi | 174 | 05:00 | Shikalbaha | 32 | 00:00
4 | Agargaon | 124 | 16:00 | Coxsbazar | 127 | 19:30 | Kazla | 132 | 16:00 | Natore | 164 | 00:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 84 | 12:00 | Cumilla(N) | 205 | 00:00 | Keranigonj | 84 | 19:00 | Nawabganj | 57.2 | 22:00 | Shitalakhya | 122.2 | 16:00
6 | Amnura | 73 | 21:00 | Cumilla(S) | 194 | 15:00 | Khagrachori | 34 | 19:00 | Netrakona | 126 | 10:00 | Sholosohor | 53 | 09:00
7 | Ashuganj | 98 | 00:00 | Daudkandi | 166 | 00:00 | Khulna | 103 | 00:00 | New | 59.9 | 12:00 | Shyampur | 182 | 12:00
8 | BIPTC | N/A | N/A | Dhaka | 48 | 13:00 | Khulshi | 197 | 18:30 | Niamatpur | 84 | 22:00 | Siddhirganj | 134 | 16:00
9 | BSRM | 159 | 00:00 | Dhamrai | 136 | 08:00 | Kishoreganj | 132 | 01:00 | Noapara | 54 | 19:30 | Sirajganj | 124 | 20:00
10 | Bagerhat | 98 | 00:00 | Dhanmondi | 165 | 16:00 | Kodda | 268 | 19:00 | PHP | 9 | 21:00 | Sonargaon | 97 | 15:00
11 | Bakulia | 106 | 15:00 | Dohazari | 86 | 21:00 | Kulaura | 54 | 17:00 | Pabna | 136 | 21:00 | Sreemongol | 72 | 00:00
12 | Banani | 39.6 | 13:00 | Faridpur | 180 | 20:00 | Kurigram | 68 | 19:00 | Palashbari | 134 | 21:00 | Sreepur | 63 | 07:00
13 | Bangabhaban | 8 | 11:00 | Fatullah | 77 | 15:00 | Kushtia | 172 | 19:00 | Panchagarh | 63 | 22:00 | Srinagar | 52.34 | 21:00
14 | Barapukuria | 69 | 20:00 | Fenchuganj | 41 | 03:00 | Lalbag | 107 | 18:30 | Patuakhali | 83.5 | 00:00 | Sunamganj | 65 | 00:00
15 | Barguna | 24 | 00:00 | Feni | 121 | 20:00 | Lalmonirhat | 56 | 22:00 | Payra | 42 | 00:00 | Sylhet | 48 | 03:00
16 | Barishal | 123 | 23:00 | GPH | 83 | 05:00 | MI_Cement | 10.6 | 00:00 | Postogola | 68 | 16:00 | Sylhet-132 | 139 | 17:00
17 | Barishal-230 | 126 | 00:00 | Ghatail | 60 | 14:00 | Madanganj | 44 | 19:00 | Purbachal | 26 | 15:00 | TK | 35 | 22:00
18 | Baroaulia | 72 | 09:00 | Ghorashal | 88 | 12:00 | Madaripur | 128 | 22:00 | Purbasadipur | 145 | 20:00 | Tangail | 224 | 20:00
19 | Baroirhat | 66 | 14:00 | Goalpara | 36 | 23:00 | Madartek | 104.43 | 00:00 | Rahim | 54 | 13:00 | Thakurgaon | 117 | 20:00
20 | Bashundhara | 244 | 15:00 | Gollamari | 84 | 00:00 | Madunaghat | 55 | 19:00 | Rajbari | 86 | 20:00 | Tongi | 154 | 15:00
21 | BashundharaCement | 12 | 12:00 | Gopalganj | 121 | 00:00 | Magura | 73 | 00:00 | Rajendrapur | 134 | 19:30 | Ullahpara | 32 | 21:00
22 | Beanibazar | 85 | 22:00 | Gulshan | 134 | 16:00 | Mahasthangarh | 88 | 00:00 | Rajshahi | 167 | 20:00 | Ullon | 71 | 21:00
23 | Benapole | 72 | 00:00 | Halishahar | 85 | 10:00 | Manikganj | 139 | 21:00 | Rajshahi-230 | 66 | 23:00 | Uttara | 91 | 16:00
24 | Bhaluka | 134 | 10:00 | HaripurSBU | 191 | 18:00 | Maniknagar | 84 | 15:00 | Ramganj | 124 | 22:00 | UttaraNew | 40 | 17:00
25 | Bhandaria | 59 | 03:00 | Hasnabad | 115 | 23:00 | Matarbari | 45 | 03:00 | Rampur | 44 | 06:00 | Zigatola | 107 | 16:00
26 | Bhangura | 44 | 20:00 | Hathazari | 84 | 20:00 | Matuail | 80 | 15:00 | Rangamati | 18 | 19:30
27 | Bheramara(GK) | 67 | 00:00 | Ishurdi | 90 | 20:00 | Millgate | 139 | 15:00 | Rangpur | 160 | 20:00
28 | Bhulta | 242 | 22:00 | Jaldhaka | 89 | 21:00 | Mirpur | 179.5 | 19:00 | Ruppur | 5 | 12:00
29 | Bog-Sherpur | 72 | 01:00 | Jamalpur | 141 | 21:00 | Mirsorai | 5 | 19:00 | SSM | 14 | 23:00
30 | Bogura | 191 | 01:00 | Jashore | 172 | 19:00 | Mirzapur | 62 | 12:00 | Saidpur | 128 | 19:30
31 | Borhanuddin | 94 | 01:00 | Jhenaidah | 143 | 20:00 | Mithapukur | 64 | 22:00 | Satkhira | 155 | 01:00
32 | Brahmanbaria | 180 | 03:00 | Joydebpur | 200 | 19:00 | Modern | 0 | 00:00 | Satmasjid | 133 | 19:00
33 | Cantonment | 182 | 16:00 | Joypurhat | 71 | 00:00 | Mogbazar | 145.8 | 15:00 | Savar | 227 | 19:00
34 | Chandpur | 79 | 00:00 | Juldah | 23 | 15:00 | Mongla | 32 | 09:00 | SevenRings | 19.19 | 04:00
35 | Chandraghona | 39 | 19:30 | KSRM | 21 | 08:00 | Motijheel | 56 | 16:00 | ShahCement | 29 | 00:00
36 | Chapai | 73 | 00:00 | Kabirpur | 303 | 20:00 | Munshiganj | 118 | 04:00 | Shahjadpur | 86 | 00:00
37 | Charsaidpur | 39 | 00:00 | Kachua | 92 | 22:00 | Mymensingh | 242 | 05:00 | Shahjibazar | 119 | 05:00
38 | Chauddagram | 84 | 00:00 | Kallyanpur | 141 | 00:00 | Naogaon | 151 | 00:00 | Shahmirpur | 56 | 21:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-05-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 388 | 05:00 | 364 | 15:00 | Kaliakoir | 379 | 21:00 | 357 | 15:00
| Ashuganj | 408 | 7:00 | 398 | 15:00 | Madunaghat_I | 404 | 22:00 | 387 | 12:00
| Bhulta | 402 | 05:00 | 371 | 12:00 | Meghnaghat | 391 | 05:00 | 354 | 22:00
| Bibiana | 399 | 01:00 | 387 | 11:00 | Payra | 406 | 08:00 | 398 | 12:00
| BIPTC | 404 | 02:00 | 390 | 15:00 | Rahanpur | 400 | 18:00 | 378 | 00:00
| Bogura | 390 | 18:30 | 368 | 00:00 | Rampal | 399 | 18:30 | 384 | 13:00
| Gopalganj | 396 | 05:00 | 378 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 05:00 | 210 | 12:00 | Hasnabad | 227 | 00:00 | 212 | 12:00
| AKSML | 235 | 18:30 | 219 | 11:00 | Hathazari | 235 | 18:30 | 221 | 12:00
| Aminbazar | 226 | 04:00 | 211 | 14:00 | Ishurdi | 236 | 18:30 | 223 | 11:00
| Ashuganj | 232 | 01:00 | 221 | 11:00 | Jhenaidah | 228 | 18:30 | 212 | 19:00
| Ashuganj-400 | 234 | 3:00 | 214 | 14:00 | Kaliakoir | 229 | 05:00 | 213 | 15:00
| Baghabari | 229 | 18:00 | 220 | 13:00 | Keranigonj | 227 | 05:00 | 210 | 12:00
| Barapukuria | 218 | 18:00 | 206 | 19:30 | Khulna(S) | 231 | 18:30 | 218 | 13:00
| Barapukuria-230 | 220 | 10:00 | 212 | 20:00 | Madunaghat_I | 236 | 18:30 | 225 | 12:00
| Barishal | 238 | 05:00 | 225 | 21:00 | Maniknagar | 229 | 03:00 | 212 | 11:00
| Bheramara | 237 | 01:00 | 222 | 11:00 | Meghnaghat | 236 | 04:00 | 220 | 11:00
| Bhulta | 232 | 05:00 | 212 | 15:00 | Meghnaghat-400 | 231 | 05:00 | 216 | 12:00
| Bibiana | 228 | 02:00 | 220 | 11:00 | Mirsorai | 235 | 20:00 | 218 | 11:00
| BIPTC | 236 | 18:30 | 222 | 03:00 | Rajshahi | 237 | 18:00 | 221 | 11:00
| Bogura | 224 | 18:00 | 213 | 07:00 | Rampal | 230 | 18:30 | 216 | 13:00
| Bogura-400 | 226 | 18:30 | 214 | 02:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 02:00 | 226 | 21:00 | Rampura | 229 | 04:00 | 209 | 15:00
| BSRM | 235 | 20:00 | 220 | 11:00 | Shikalbaha | 232 | 18:30 | 221 | 12:00
| Cumilla(N) | 228 | 08:00 | 216 | 11:00 | Shyampur | 229 | 05:00 | 212 | 12:00
| Fenchuganj | 231 | 08:00 | 223 | 12:00 | Siddhirganj | 230 | 01:00 | 214 | 14:00
| Ghorashal | 230 | 01:00 | 225 | 00:00 | Sirajgonj | 235 | 18:30 | 227 | 11:00
| Ghorashal-230 | 229 | 01:00 | 213 | 12:00 | Sreepur | 233 | 20:00 | 219 | 13:00
| GPH | 235 | 18:30 | 221 | 11:00 | Tongi | 226 | 05:00 | 211 | 15:00
| Haripur | 227 | 00:00 | 211 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 07:00 | 122 | 11:00 | Kushtia | 132 | 18:30 | 122 | 19:00
| Agargaon | 137 | 05:00 | 123 | 15:00 | Lalbag | 134 | 20:00 | 122 | 11:00
| Agrabad | 136 | 09:00 | 124 | 12:00 | Lalmonirhat | 128 | 15:00 | 115 | 19:30
| AKS | 134 | 18:30 | 125 | 10:00 | Madanganj | 134 | 05:00 | 122 | 11:00
| Aminbazar | 133 | 23:00 | 121 | 12:00 | Madaripur | 130 | 01:00 | 123 | 22:00
| Amnura | 138 | 01:00 | 119 | 00:00 | Madartek | 132 | 05:00 | 120 | 11:00
| Ashuganj | 138 | 01:00 | 132 | 17:00 | Madunaghat | 137 | 18:30 | 126 | 12:00
| Bagerhat | 137 | 18:30 | 120 | 00:00 | Magura | 135 | 18:30 | 123 | 13:00
| Bakulia | 137 | 09:00 | 127 | 12:00 | Mahasthangarh | 134 | 18:00 | 124 | 21:00
| Banani | 132 | 05:00 | 119 | 15:00 | Manikganj | 133 | 05:00 | 118 | 12:00
| Bangabhaban | 133 | 05:00 | 120 | 12:00 | Maniknagar | 132 | 02:00 | 120 | 12:00
| Barapukuria | 136 | 18:00 | 124 | 19:30 | Matarbari | 130 | 16:00 | 115 | 06:00
| Barguna | 136 | 09:00 | 125 | 00:00 | Matuail | 134.6 | 05:00 | 121.4 | 12:00
| Barishal | 137 | 01:00 | 120 | 00:00 | Millgate | 133 | 05:00 | 121 | 12:00
| Barishal-230 | 136 | 02:00 | 127 | 21:00 | Mirpur | 132 | 20:00 | 118 | 15:00
| Baroaulia | 137 | 18:30 | 127 | 11:00 | Mirzapur | 134 | 21:00 | 126 | 18:00
| Baroirhat | 131 | 18:30 | 121 | 11:00 | Mithapukur | 133 | 18:00 | 118 | 19:30
| Bashundhara | 133 | 05:00 | 120 | 15:00 | MI_Cement | 134 | 01:00 | 121 | 12:00
| BashundharaCement | 134 | 05:00 | 122 | 12:00 | Modern | 136 | 18:30 | 126 | 11:00
| Beanibazar | 130 | 19:00 | 119 | 17:00 | Mogbazar | 134 | 04:00 | 122 | 11:00
| Benapole | 135 | 18:30 | 121 | 00:00 | Mongla | 136 | 18:30 | 121 | 00:00
| Bhaluka | 131 | 20:00 | 117 | 16:00 | Motijheel | 132 | 02:00 | 120 | 12:00
| Bhandaria | 137 | 19:00 | 116 | 00:00 | Munshiganj | 134 | 20:00 | 122 | 11:00
| Bhangura | 136 | 18:00 | 129 | 11:00 | Mymensingh | 134 | 23:00 | 114 | 16:00
| Bheramara | 133 | 01:00 | 125 | 14:00 | Naogaon | 131 | 18:00 | 121 | 00:00
| Bheramara(GK) | 133 | 18:30 | 125 | 13:00 | Narail | 136 | 18:30 | 124 | 00:00
| Bhulta | 131 | 20:00 | 115 | 12:00 | Narinda | 132 | 2:00 | 120 | 12:00
| Bog-Sherpur | 132 | 18:00 | 125 | 12:00 | Narshingdi | 135 | 20:00 | 114 | 11:00
| Bogura | 138 | 19:00 | 127 | 07:00 | Natore | 133 | 18:30 | 126 | 03:00
| Bogura-230 | 137 | 18:30 | 127 | 07:00 | Nawabganj | 133 | 20:00 | 122 | 11:00
| Brahmanbaria | 134 | 20:00 | 119 | 16:00 | Netrakona | 132 | 23:00 | 120 | 11:00
| Cantonment | 136 | 05:00 | 123 | 12:00 | New | 133 | 06:00 | 122 | 15:00
| Chandpur | 134 | 23:00 | 120 | 10:00 | Niamatpur | 134 | 18:00 | 124 | 00:00
| Chandraghona | 136 | 19:00 | 127 | 12:00 | Noapara | 138 | 18:30 | 124 | 13:00
| Chapai | 132 | 18:30 | 123 | 00:00 | Pabna | 133 | 18:30 | 126 | 03:00
| Charsaidpur | 135 | 05:00 | 122 | 11:00 | Palashbari | 131 | 18:00 | 116 | 21:00
| Chauddagram | 130 | 18:30 | 120 | 11:00 | Panchagarh | 135 | 18:00 | 112 | 03:00
| Chhatak | 129 | 19:00 | 122 | 15:00 | Patuakhali | 135 | 09:00 | 128 | 00:00
| Chowmuhani | 129 | 23:00 | 117 | 15:00 | Payra | 135 | 09:00 | 131 | 00:00
| Chuadanga | 128 | 18:00 | 112 | 19:00 | PHP | 132 | 23:00 | 119 | 11:00
| Coxsbazar | 125 | 17:00 | 116 | 07:00 | Postogola | 135 | 05:00 | 122 | 11:00
| Cumilla(N) | 133 | 23:00 | 125 | 11:00 | Purbachal | 133 | 05:00 | 120 | 15:00
| Cumilla(S) | 133 | 18:30 | 123 | 15:00 | Purbasadipur | 132 | 18:00 | 113 | 19:30
| Daudkandi | 128 | 05:00 | 114 | 11:00 | Rahanpur | 136 | 18:30 | 128 | 00:00
| Dhaka | 134 | 05:00 | 121 | 11:00 | Rahim | 134 | 20:00 | 122 | 11:00
| Dhamrai | 131 | 00:00 | 120 | 15:00 | Rajbari | 129 | 18:30 | 120 | 19:00
| Dhanmondi | 135 | 05:00 | 122 | 12:00 | Rajendrapur | 136 | 21:00 | 120 | 12:00
| Dohazari | 137 | 18:30 | 125 | 12:00 | Rajshahi | 132 | 18:00 | 126 | 13:00
| Faridpur | 130 | 18:30 | 122 | 00:00 | Rajshahi-230 | 136 | 18:30 | 116 | 00:00
| Fatullah | 134 | 20:00 | 121 | 12:00 | Ramganj | 130 | 23:00 | 115 | 15:00
| Fenchuganj | 134 | 19:30 | 127 | 15:00 | Rampur | 135 | 18:30 | 126 | 12:00
| Feni | 130 | 23:00 | 119 | 11:00 | Rampura | 133 | 04:00 | 121 | 11:00
| Ghatail | 132 | 21:00 | 119 | 15:00 | Rangamati | 133 | 18:30 | 127 | 10:00
| Ghorashal | 137 | 22:00 | 128 | 11:00 | Rangpur | 132 | 18:00 | 115 | 19:30
| Goalpara | 141 | 18:30 | 127 | 12:00 | Ruppur | 135 | 18:00 | 128 | 13:00
| Gollamari | 136 | 20:00 | 127 | 13:00 | Saidpur | 131 | 18:00 | 116 | 19:30
| Gopalganj | 135 | 18:30 | 127 | 00:00 | Satkhira | 135 | 18:30 | 118 | 00:00
| Gopalganj-400 | 130 | 05:00 | 124 | 15:00 | Satmasjid | 135 | 01:00 | 122 | 15:00
| Gulshan | 133 | 20:00 | 121 | 11:00 | Savar | 133 | 20:00 | 120 | 12:00
| Halishahar | 137 | 18:30 | 126 | 12:00 | SevenRings | 139 | 20:00 | 127 | 15:00
| Haripur | 134 | 20:00 | 122 | 10:00 | ShahCement | 135 | 05:00 | 122 | 11:00
| HaripurSBU | 134 | 20:00 | 122 | 11:00 | Shahjadpur | 137 | 18:00 | 131 | 11:00
| Hasnabad | 133 | 20:00 | 123 | 15:00 | Shahjibazar | 133 | 19:30 | 119 | 16:00
| Hathazari | 137 | 19:30 | 129 | 12:00 | Shahmirpur | 138 | 18:30 | 128 | 12:00
| Ishurdi | 136 | 18:30 | 128 | 13:00 | Shariatpur | 130 | 18:30 | 121 | 22:00
| Jaldhaka | 130 | 17:00 | 111 | 19:30 | Sherpur | 132 | 18:30 | 119 | 07:00
| Jamalpur | 136 | 23:00 | 119 | 18:00 | Shikalbaha | 126 | 18:30 | 117 | 12:00
| Jashore | 134 | 18:30 | 126 | 19:00 | Shikalbaha-230 | 139 | 18:30 | 128 | 12:00
| Jhenaidah | 135 | 18:00 | 124 | 13:00 | Shitalakhya | 134.2 | 05:00 | 121 | 12:00
| Jhenaidah-230 | 136 | 18:30 | 124 | 19:00 | Sholosohor | 135 | 18:30 | 125 | 12:00
| Joydebpur | 136 | 20:00 | 121 | 16:00 | Shyampur | 132 | 20:00 | 123 | 15:00
| Joypurhat | 128 | 18:00 | 116 | 21:00 | Shyampur-230 | 133 | 05:00 | 121 | 12:00
| Juldah | 138 | 18:30 | 128 | 12:00 | Siddhirganj | 135 | 05:00 | 123 | 11:00
| Kabirpur | 137 | 21:00 | 120 | 11:00 | Sirajganj | 132 | 18:00 | 126 | 00:00
| Kachua | 132 | 23:00 | 121 | 15:00 | Sonargaon | 133 | 03:00 | 122 | 11:00
| Kaliakoir | 137 | 21:00 | 125 | 14:00 | Sreemongol | 133 | 18:30 | 120 | 16:00
| Kallyanpur | 128 | 04:00 | 118 | 19:00 | Sreepur | 133 | 20:00 | 124 | 12:00
| Kalurghat | 136 | 23:00 | 127 | 11:00 | Srinagar | 133 | 05:00 | 122 | 11:00
| Kamrangirchar | 135 | 20:00 | 116 | 19:00 | SSM | 140 | 18:30 | 130 | 11:00
| Kaptai | 130 | 4:00 | 126 | 14:00 | Sunamganj | 126 | 19:30 | 120 | 15:00
| Kazla | 132 | 05:00 | 120 | 12:00 | Sylhet | 130 | 18:30 | 124 | 15:00
| Keranigonj | 135 | 20:00 | 123 | 11:00 | Sylhet-132 | 130 | 05:00 | 126 | 13:00
| Khagrachori | 135 | 00:00 | 124 | 11:00 | Tangail | 133 | 21:00 | 118 | 15:00
| Khulna | 135 | 18:00 | 129 | 02:00 | Thakurgaon | 135 | 18:00 | 113 | 19:30
| Khulna(S) | 138 | 18:30 | 128 | 00:00 | TK | 135 | 18:30 | 126 | 11:00
| Khulshi | 135 | 18:30 | 124 | 11:00 | Tongi | 135 | 05:00 | 122 | 15:00
| Kishoreganj | 130 | 20:00 | 119 | 19:30 | Ullahpara | 134 | 18:00 | 127 | 14:00
| Kodda | 138 | 21:00 | 119 | 11:00 | Ullon | 134 | 05:00 | 121 | 11:00
| KSRM | 136 | 19:00 | 128 | 12:00 | Uttara | 132 | 20:00 | 118 | 15:00
| Kulaura | 133 | 18:30 | 126 | 15:00 | UttaraNew | 132 | 20:00 | 120 | 15:00
| Kurigram | 132 | 17:00 | 112 | 07:00 | Zigatola | 133 | 06:00 | 122 | 12:00

## L-Curve
Date | 2024-05-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 832 | 7741 | 6536 | 14277 |  |  |  | QF-LDC-11
0:30 | 668 | 7972.5 | 6519.5 | 14492 | Date: | 2024-05-25
1:00 | 504 | 8204 | 6503 | 14707
1:30 | 451 | 8182 | 6396 | 14578
2:00 | 398 | 8160 | 6289 | 14449
2:30 | 452 | 8141.5 | 6346.5 | 14488 | [5 empty] | Gen. at Eve. Peak | 14623 | 14623 MW (19:00 )
3:00 | 506 | 8123 | 6404 | 14527 | [6 empty] | 19:00
3:30 | 544 | 8051.5 | 6391 | 14442.5 | [5 empty] | Gen. at Day Peak | 13726 | 13726 MW (12:00 )
4:00 | 582 | 7980 | 6378 | 14358 | [6 empty] | 12:00
4:30 | 581 | 7977 | 6353 | 14330 | [5 empty] | Highest Generation | 14707
5:00 | 580 | 7974 | 6328 | 14302 | [6 empty] | 1:00
5:30 | 580 | 7722.5 | 6106.5 | 13829
6:00 | 580 | 7471 | 5885 | 13356
6:30 | 587 | 7417 | 5874 | 13291
7:00 | 594 | 7363 | 5863 | 13226
7:30 | 694 | 7262 | 5828.5 | 13090.5
8:00 | 794 | 7161 | 5794 | 12955
8:30 | 825 | 7138.5 | 5713.5 | 12852
9:00 | 856 | 7116 | 5633 | 12749
9:30 | 993 | 7116.5 | 5681.5 | 12798
10:00 | 1130 | 7117 | 5730 | 12847
10:30 | 1123 | 7215 | 5821.5 | 13036.5
11:00 | 1116 | 7313 | 5913 | 13226
11:30 | 1127 | 7465.5 | 6010.5 | 13476
12:00 | 1138 | 7618 | 6108 | 13726
12:30 | 1073 | 7791 | 6105 | 13896
13:00 | 1008 | 7964 | 6102 | 14066
13:30 | 1034 | 7975 | 6208 | 14183
14:00 | 1060 | 7986 | 6314 | 14300
14:30 | 1103 | 7962.5 | 6393.5 | 14356
15:00 | 1146 | 7939 | 6473 | 14412
15:30 | 1159 | 7940.5 | 6424 | 14364.5
16:00 | 1172 | 7942 | 6375 | 14317
16:30 | 1170 | 7941.5 | 6241 | 14182.5
17:00 | 1168 | 7941 | 6107 | 14048
17:30 | 1158 | 7821.5 | 6045 | 13866.5
18:00 | 1148 | 7702 | 5983 | 13685
18:30 | 972 | 8027 | 6127 | 14154
19:00 | 796 | 8352 | 6271 | 14623
19:30 | 432 | 8176 | 6270 | 14446
20:00 | 244 | 8085 | 6134 | 14219 |  |  |  | Executive Engineer
20:30 | 246 | 8160.5 | 6095 | 14255.5 |  |  |  | Network Operation Division
21:00 | 248 | 8236 | 6056 | 14292
21:30 | 403 | 8233 | 6194.5 | 14427.5
22:00 | 558 | 8230 | 6333 | 14563 |  |  |  |  | Page 6 of 7
22:30 | 670 | 8095.5 | 6402.5 | 14498
23:00 | 782 | 7961 | 6472 | 14433
23:30 | 807 | 7851 | 6504 | 14355
24:00 | 832 | 7741 | 6536 | 14277
14623 MW (19:00 )
13726 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-05-25 |  | Energy |  | 337879555
[14 empty] | Date: | 2024-05-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3212 | 621 | 1805 | 0 | 3075 | 4831 | 30 | 0 | 573 | 90 | 0 | 40 | 1168
0:30 | 3527 | 631 | 1917 | 0 | 2980.5 | 4840 | 30 | 0 | 456.5 | 77 | 0 | 33 | 1082.0325 |  |  | Date: | 43975
1:00 | 3842 | 641 | 2029 | 0 | 2886 | 4849 | 30 | 0 | 340 | 64 | 0 | 26 | 996.065
1:30 | 3756 | 641 | 2020 | 0 | 2864.5 | 4852.5 | 30 | 0 | 323.5 | 62 | 0 | 28.5 | 952.135 | [9 empty] | Total Energy | 337.8796 | 337.8796 | Total Energy Gen 337.880 MKWHr Energy Not Served 9.336 MKWHr Energy Requirement 347.215 MKWHr
2:00 | 3670 | 641 | 2011 | 0 | 2843 | 4856 | 30 | 0 | 307 | 60 | 0 | 31 | 908.205 | [9 empty] | Energy not Served | 9.3359 | 9.3359
2:30 | 3666.5 | 783.5 | 1991.5 | 0 | 2837 | 4779 | 30 | 0 | 314.5 | 61 | 0 | 25 | 608.335 | [9 empty] | Energy Requirement | 347.2154 | 347.2154
3:00 | 3663 | 926 | 1972 | 0 | 2831 | 4702 | 30 | 0 | 322 | 62 | 0 | 19 | 308.465
3:30 | 3673 | 926 | 1994 | 0 | 2823 | 4610.5 | 30 | 0 | 311 | 62 | 0 | 13 | 269.7875 | [8 empty] | Shortage
4:00 | 3683 | 926 | 2016 | 0 | 2815 | 4519 | 30 | 0 | 300 | 62 | 0 | 7 | 231.11
4:30 | 3676 | 926 | 1986.5 | 0 | 2819.5 | 4522 | 30 | 0 | 300.5 | 61 | 0 | 8.5 | 222.0375
5:00 | 3669 | 926 | 1957 | 0 | 2824 | 4525 | 30 | 0 | 301 | 60 | 0 | 10 | 212.965
5:30 | 3666.5 | 925.5 | 1855 | 0 | 2486.5 | 4484.5 | 30 | 0 | 301 | 58 | 16 | 6 | 199.1175
6:00 | 3664 | 925 | 1753 | 0 | 2149 | 4444 | 30 | 0 | 301 | 56 | 32 | 2 | 185.27
6:30 | 3650.5 | 925 | 1776 | 0 | 2024.5 | 4446 | 30 | 0 | 301 | 56 | 81 | 1 | 199.595 | [7 empty] | Coal
7:00 | 3637 | 925 | 1799 | 0 | 1900 | 4448 | 30 | 0 | 301 | 56 | 130 | 0 | 213.92
7:30 | 3567.5 | 925.5 | 1706.5 | 0 | 1860.5 | 4449.5 | 30 | 0 | 300.5 | 61 | 189.5 | 0 | 200.0725 | [6 empty] | Oil
8:00 | 3498 | 926 | 1614 | 0 | 1821 | 4451 | 30 | 0 | 300 | 66 | 249 | 0 | 186.225
8:30 | 3475.5 | 926 | 1564 | 0 | 1804.5 | 4376 | 30 | 0 | 295 | 68 | 312 | 1 | 131.79
9:00 | 3453 | 926 | 1514 | 0 | 1788 | 4301 | 30 | 0 | 290 | 70 | 375 | 2 | 77.355
9:30 | 3467 | 926 | 1560.5 | 0 | 1772 | 4264.5 | 40 | 0 | 286 | 70 | 410 | 2 | 111.735
10:00 | 3481 | 926 | 1607 | 0 | 1756 | 4228 | 50 | 0 | 282 | 70 | 445 | 2 | 146.115
10:30 | 3509 | 923 | 1725 | 0 | 1767.5 | 4263 | 40 | 0 | 282 | 72 | 452 | 3 | 165.6925
11:00 | 3537 | 920 | 1843 | 0 | 1779 | 4298 | 30 | 0 | 282 | 74 | 459 | 4 | 185.27
11:30 | 3528 | 920 | 1844 | 0 | 1920 | 4391 | 30 | 4 | 289 | 76 | 468 | 6 | 199.595
12:00 | 3519 | 920 | 1845 | 0 | 2061 | 4484 | 30 | 8 | 296 | 78 | 477 | 8 | 213.92
12:30 | 3504 | 920 | 1781.5 | 0 | 2232 | 4516.5 | 30 | 4 | 329.5 | 78 | 489.5 | 11 | 226.46
13:00 | 3489 | 920 | 1718 | 0 | 2403 | 4549 | 30 | 0 | 363 | 78 | 502 | 14 | 239
13:30 | 3489 | 920 | 1718 | 0 | 2403 | 4549 | 30 | 0 | 363 | 78 | 502 | 14 | 239
14:00 | 3489 | 920 | 1718 | 0 | 2403 | 4549 | 30 | 0 | 363 | 78 | 502 | 14 | 239
14:30 | 3478.5 | 920 | 1769 | 0 | 2506.5 | 4657.5 | 30 | 0 | 368.5 | 85 | 413.5 | 10.5 | 305
15:00 | 3468 | 920 | 1820 | 0 | 2610 | 4766 | 30 | 0 | 374 | 92 | 325 | 7 | 371
15:30 | 3497 | 919.5 | 1802 | 0 | 2656 | 4669.5 | 30 | 6 | 383 | 94 | 278.5 | 29 | 488
16:00 | 3526 | 919 | 1784 | 0 | 2702 | 4573 | 30 | 12 | 392 | 96 | 232 | 51 | 605
16:30 | 3511 | 919 | 1763 | 0 | 2720.5 | 4521.5 | 30 | 6 | 415.5 | 94 | 162.5 | 39.5 | 614
17:00 | 3496 | 919 | 1742 | 0 | 2739 | 4470 | 30 | 0 | 439 | 92 | 93 | 28 | 623
17:30 | 3428.5 | 919.5 | 1651 | 0 | 2795 | 4398 | 30 | 0 | 465.5 | 87 | 59.5 | 32.5 | 557.5
18:00 | 3361 | 920 | 1560 | 0 | 2851 | 4326 | 30 | 0 | 492 | 82 | 26 | 37 | 492
18:30 | 3400 | 920 | 1635 | 0 | 3046.5 | 4339.5 | 30 | 0 | 646 | 82 | 13 | 42 | 378.5
19:00 | 3439 | 920 | 1710 | 0 | 3242 | 4353 | 30 | 0 | 800 | 82 | 0 | 47 | 265
19:30 | 3179 | 919 | 1444 | 0 | 3396 | 4541 | 30 | 0 | 799 | 90 | 0 | 48 | 266.5
20:00 | 3119 | 629 | 1631 | 0 | 3294 | 4548 | 30 | 0 | 839 | 84 | 0 | 45 | 268
20:30 | 3247.5 | 629 | 1616 | 0 | 3210.5 | 4601 | 30 | 0 | 800.5 | 87 | 0 | 34 | 134
21:00 | 3376 | 629 | 1601 | 0 | 3127 | 4654 | 30 | 0 | 762 | 90 | 0 | 23 | 0
21:30 | 3359 | 629 | 1623 | 0 | 3210 | 4739.5 | 30 | 0 | 713.5 | 90 | 0 | 33.5 | 17.5
22:00 | 3342 | 629 | 1645 | 0 | 3293 | 4825 | 30 | 0 | 665 | 90 | 0 | 44 | 35
22:30 | 3289.5 | 625 | 1671 | 0 | 3282 | 4839 | 30 | 0 | 632 | 90 | 0 | 39.5 | 503
23:00 | 3237 | 621 | 1697 | 0 | 3271 | 4853 | 30 | 0 | 599 | 90 | 0 | 35 | 971
23:30 | 3224.5 | 621 | 1751 | 0 | 3173 | 4842 | 30 | 0 | 586 | 90 | 0 | 37.5 | 1069.5 |  |  | Max Temp. in Dhaka |  | 38.8°C
24:00 | 3212 | 621 | 1805 | 0 | 3075 | 4831 | 30 | 0 | 573 | 90 | 0 | 40 | 1168
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 337.880 MKWHr Energy Not Served 9.336 MKWHr Energy Requirement 347.215 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-05-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [9 empty] | 20 | 0 | [15 empty] | 3300
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720000
3 | Chattogram TPP-1 | [26 empty] | 100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 6 | 8 | 8 | 12 | 19 |  | 25 | 25 | 25 | 25 | 25 | 11 | 8 | 186561
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 4 |  | 7 | 13 | 14 | 20 | 18 | 14 |  | 9 | 4 | 0 | [8 empty] | 93690
6 | Sikalbaha 225MW CCPP (Gas) | 153 | 151 | 151 | 151 | 152 | 151 | 151 | 150 | 148 | 143 | 145 | 143 | 135 | 130 | 133 | 130 | 131 | 136 |  | 137 | 136 | 136 | 136 | 136 | 136 | 136 | 3354051
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 34 | 34 | 51 | 51 | 73 |  | 85 | 85 | 85 | 85 | 85 | 85 | 68 | 946902
12 | Hathazari 100 MW peaking PP | 74 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 47 | 53 | 52 | 45 | 47 | 47 | 64 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1428864
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 34 | 36 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 34 | 913309
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 44 | 45 | 45 | 45 | 46 | 46 | 46 | 45 | 43 | 36 | 36 | 36 | 41 | 43 | 43 | 43 | 43 | 41 |  | 43 | 44 | 44 | 44 | 44 | 46 | 46 | 1023984
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 260 | 261 | 266 | 260 | 245 | 245 | 245 | 254 | 285 | 287 | 286 | 286 | 286 | 285 | 290 | 290 | 291 | 290 |  | 286 | 290 | 285 | 220 | 220 | 220 | 220 | 6394421
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 195 | 195 | 198 | 210 | 213 | 296 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 293 | 215 | 193 | 195 |  | 195 | 195 | 130 | 95 | 95 | 95 | 95 | 5339345
19 | Ashuganj 195 MW PP (APSCL-United) | [9 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 20 | 8 |  |  | 117091
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4221000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 493 | 491 | 490 | 490 | 490 | 490 | 491 | 473 | 403 | 400 | 410 | 456 | 477 | 492 | 490 | 485 | 485 |  | 488 | 489 | 490 | 490 | 490 | 490 | 490 | 11470908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 31 | 32 | 30 | 33 | 29 | 29 | 29 | 30 | 31 | 29 |  | 33 | 0 |  | 29 | 31 | 31 | 31 | 719568
33 | Ashuganj 225 MW CCPP | 206 | 201 | 191 | 215 | 219 | 218 | 202 | 194 | 194 | 209 | 196 | 200 | 206 | 209 | 207 | 205 | 203 | 209 |  | 214 | 0 |  | 28 | 46 | 56 | 68 | 4108000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 260 | 240 | 240 | 240 | 240 | 240 | 240 | 285 | 305 | 270 | 310 | 305 | 305 | 305 | 320 | 270 |  | 265 | 270 | 270 | 335 | 330 | 270 | 240 | 6826000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 155 | 75 | 50 | [14 empty] | 3131500
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 240 | 230 | 230 | 270 | 260 | 315 | 320 | 350 | 355 | 355 | 320 |  | 280 | 300 | 300 | 385 | 305 | 215 | 215 | 6664500
35 | Ashuganj 55 MW PP (Precision) | 50 | 52 | 53 | 43 | 40 | 43 | 45 | 45 | 45 | 45 | 44 | 43 | 42 | 40 | 38 | 38 | 37 | 37 |  | 41 | 0 |  | 1 | 24 | 30 | 30 | 900480
36 | Chandpur 150 MW CCPP | 20 | 31 | 40 | 51 | 50 | 51 | 51 | 50 | 50 | 70 | 72 | 75 | 80 | 90 | 85 | 80 | 80 | 74 |  | 70 | 70 | 70 | 70 | 50 | 50 | 70 | 1380330
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 406 | 404 | 404 | 402 | 401 | 402 | 355 | 321 | 322 | 391 | 396 | 399 | 394 | 390 | 397 | 396 | 403 |  | 396 | 372 | 381 | 401 | 401 | 393 | 368 | 9342000
| Meghnaghat Unique power | 255 | 230 | 230 | 230 | 230 | [21 empty] | 1397272
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 350 | 350 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 380 |  | 400 | 330 | 400 | 400 | 400 | 400 | 400 | 9772000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 113 | 111 | 110 | 111 | 115 | 115 | 82 | 89 | 89 | 87 | 76 | 66 | 56 | 67 | 57 | 60 | 59 | 59 |  | 58 | 55 | 50 | 54 | 70 | 70 | 64 | 1780800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 13 | 26 | 38 | 47 | 50 | 51 | 49 | 45 | 37 | 25 | 12 | 2 | [8 empty] | 399280
44 | Fenchugonj CCPP Phase-1 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 38 | 33 | 33 | 33 | 33 | 33 | 39 |  | 40 | 40 | 40 | 40 | 43 | 40 | 40 | 896000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 57 | 60 | 56 | 56 | 56 |  | 56 | 58 | 58 | 58 | 58 | 58 | 30 | 1407360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 61 | 40 | 40 | 54 | 54 | 51 | 54 | 42 | 50 | 49 | 58 |  | 60 | 60 | 61 | 60 | 54 | 59 | 55 | 1283424
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 198 | 201 | 203 | 204 | 203 | 204 | 204 | 204 | 205 | 200 | 199 | 197 | 197 | 196 | 195 | 198 | 194 | 196 |  | 200 | 203 | 202 | 198 | 198 | 204 | 205 | 4044320
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | [8 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 0 |  |  |  | 2 | 2 | 2 | 33072
55 | Fenchugonj 51 MW PP (Barakatullah) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 45 | 44 | 45 | 45 | 47 | 47 | 47 | 47 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1142400
56 | Shahjahanulla 25 MW PP |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 19 | 16 | 16 | 19 | 19 | 19 | 19 |  | 16 | 16 | 23 | 24 | 24 | 24 | 24 | 475056
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 285 | 300 | 295 | 270 | 305 | 270 | 260 | 295 | 305 | 300 | 280 | 290 | 295 | 275 | 300 | 285 |  | 270 | 290 | 280 | 310 | 315 | 300 | 310 | 7133500
| Bibiyana South 400 MW | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 310 | 310 | 330 | 330 | 360 | 350 | 345 | 358 | 354 | 352 | 310 |  | 385 | 350 | 340 | 352 | 370 | 385 | 382 | 8324200
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1301931
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 10 | 5 | 12 | 12 | 285600
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 64 | 60 | 62 | 62 | 60 | 56 | 56 | 66 | 70 | 70 | 74 | 78 | 78 | 96 | 92 | 96 | 92 | 82 |  | 82 | 90 | 84 | 90 | 90 | 90 | 90 | 1824960
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 8 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 2 | 5 | 9 |  | 12 | 12 | 14 | 20 | 27 | 16 | 30 | 467040
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 31 | 31 | 24 | 31 | 31 | 31 |  |  |  | 31 |  | 31 | 32 | 32 | 32 | 32 | 32 | 31 | 671300
68 | Cumilla 25 MW PP (Summit) | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 17 | 16 | 16 | 16 | 16 |  | 10 | 5 | 5 | 17 | 17 | 17 | 17 | 332440
69 | Summit Ashulia | 25 | 25 | 24 | 24 | 24 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 |  | 16 | 16 | 14 |  | 17 | 18 | 17 | 17 | 0 | 19 | 19 | 421800
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 0 | 23 | 23 | 23 |  | 23 | 23 |  | 23 | 23 | 15 | 23 | 454320
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 29 | 29 | 29 |  | 29 | 30 | 30 | 0 |  | 25 | 33 | 509760
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 14 | 14 | 14 |  | 14 | 14 |  |  | 14 | 14 | 14 | 552800
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 0 | [6 empty] | 224772
| Feni Lanka Power | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 55 |  | 97 | 97 | 97 | 97 | 97 | 97 | 52 | 1347480
| Chowmuhani 113 MW | 46 | 46 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 39 | 45 | 45 | 45 | 45 | 44 | 44 | 47 |  | 73 | 75 | 75 | 76 | 78 | 85 | 86 | 1232280
| Manikgonj 162MW PP(MPGL) | 144 | 162 | 162 | 162 | 162 | 90 | 54 | 54 | 108 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 126 | 144 | 162 | 162 | 3476160
77 | Siddhirganj 100 PP(Dutch Bangla) | 83 | 83 | 83 | 83 | 83 | 83 | 43 | 25 | 25 |  |  | 10 | 55 | 70 | 75 | 79 | 80 | 75 |  | 70 | 75 | 75 | 75 | 68 | 60 | 62 | 1371840
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 117120
79 | Kodda 150 MW PP | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 64 | 82 | 82 | 82 | 82 | 98 |  | 149 | 149 | 149 | 149 | 149 | 82 | 82 | 1660320
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 25 | 8 | 8 | 20 | 34 | 34 | 33 | 34 | 31 | 31 |  | 46 | 51 | 51 | 51 | 51 | 51 | 50 | 827006
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 | 50 | 50 | 17 | 17 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 52 | 17 | 683520
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 4 | 3 |  | 4 | 0 |  |  | 0 | 0 | [9 empty] | 17836
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 27 | 17 | 17 |  |  | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 17 | 23 | 35 | 35 | 35 | 748943
| Karnaphuli Power Ltd. | 68 | 68 | 68 | 68 | 68 | 34 | 34 | 34 | 34 | 34 | 35 | 76 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 99 | 2042391
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 72 | 34 | 34 | 34 | 7 |  | 2 | 38 | 50 | 70 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1360544
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 10 | 12 | 13 | 13 | 13 |  |  | 44411
86 | Meghnaghat CCPP ( Summit) | 295 | 300 | 297 | 305 | 300 | 304 | 315 | 290 | 295 | 300 | 309 | 306 | 300 | 310 | 307 | 305 | 306 | 250 |  | 300 | 250 | 305 | 315 | 310 | 315 | 312 | 7137193
87 | Meghnaghat 100 MW(IEL) | 73 | 73 | 74 | 74 | 72 | 73 | 48 | 24 | 25 |  |  | 4 | 34 | 41 | 41 | 57 | 63 | 72 |  | 93 | 96 | 96 | 96 | 94 | 99 | 98 | 1423680
| Meghnaghat 104 MW PP (OPCL) | 72 | 60 | 70 | 70 | 70 | 71 | 71 | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1672320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 68 | 58 | 58 | 58 | 58 | 12 | 12 | 12 |  |  | 12 | 58 | 58 | 58 | 58 | 58 | 69 | 69 |  | 69 | 69 | 25 | 16 | 68 | 68 | 68 | 1044240
92 | Fenchuganj 44 MW (Energyprima) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 10 | 10 | 26 | 38 | 40 | 39 | 39 | 39 | 39 | 37 |  | 38 | 38 | 42 | 42 | 42 | 42 | 42 | 914112
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 90 | 90 | 90 | 90 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 82 | 82 | 1819440
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 223200
96 | Chattogram 108 MW PP (ECPV) | 44 | 44 | 46 | 45 | 46 | 45 | 46 | 45 | 45 | 44 | 44 | 44 | 44 | 43 | 43 | 38 | 44 | 44 |  | 45 | 45 | 44 | 45 | 44 | 44 | 44 | 1064640
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 26 | 40 | 40 | 40 |  | 40 | 55 | 55 | 55 | 55 | 30 | 30 | 780776
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1322032
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | [7 empty] | 2 | 1 | 1 | 0 | [8 empty] | 3200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 35 | 38 | 54 | 54 | 1056960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 78 | 78 | 78 | 78 | 78 | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 56 | 54 | 54 | 58 | 61 |  | 107 | 111 | 115 | 112 | 116 | 107 | 107 | 1802400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 53 | 53 | 53 | 53 | 51 | 53 | 53 | 51 | 108 | 149 | 146 | 149 | 145 | 142 | 113 | 66 | 70 | 66 |  | 99 | 149 | 146 | 149 | 149 | 111 | 52 | 2298384
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 49 | 49 | 37 | 37 | 37 | 49 | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 49 | 1202880
116 | Chandpur 200 MW (Desh energy) | 90 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 71 | 100 | 104 | 103 | 102 | 103 | 103 | 105 |  | 136 | 155 | 145 | 155 | 155 | 155 | 155 | 2422560
117 | Ashuganj 150 MW PP (Midland) | 18 | 12 | 13 | 12 | 13 | 12 | 13 | 12 | 12 | 12 | 12 | 10 | 12 | 10 | 12 | 12 | 12 | 21 |  | 35 | 60 | 58 | 60 | 58 | 55 | 53 | 546981
118 | Bibiyana-III 400 MW CCPP | 366 | 364 | 365 | 368 | 366 | 365 | 365 | 316 | 318 | 350 | 366 | 368 | 394 | 368 | 369 | 369 | 377 | 330 |  | 352 | 385 | 365 | 395 | 402 | 390 | 406 | 8857000
| Jamalpur 115 MW PP (United) | 69 | 70 | 68 | 68 | 69 | 69 | 49 | 49 | 48 | 48 | 48 | 47 | 46 | 45 | 45 | 45 | 46 | 46 |  | 97 | 98 | 99 | 98 | 99 | 99 | 99 | 1550400
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 51 | 51 | 52 | 1259564
| Juldah unit-2 (Acorn) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 60 |  | 60 | 60 | 60 | 60 | 60 | 48 | 48 | 1208640
| Anlima Energy Ltd. | 53 | 53 | 53 | 37 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 1028727
| Bhairob 54.5 MW | 35 | 35 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 | [5 empty] | 14 | 35 | 35 | 485640
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 7 | 14 | 23 | 28 | 32 | 31 | 29 | 24 | 19 |  | 7 | 1 | [8 empty] | 214911
| Chandpur 115(Doreen) | 111 | 112 | 112 | 112 | 112 | 60 | 17 | 17 | 17 | 17 | 17 | 54 | 91 | 103 | 84 | 82 | 84 | 83 |  | 83 | 100 | 96 | 108 | 111 | 111 | 111 | 1972800
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 20 | 25 | 17 | 17 | 390600
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 54 | 54 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 | 108 | 17 | 17 | 17 | 812945
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 26 | 31 | 19 | 7 | 10 | 2 | 0 | 0 | 2 | 2 | 4 | 8 | 14 | 28 | 7 | 51 | 28 | 37 |  | 47 | 48 | 45 | 23 | 44 | 35 | 40 | 526560
| Sonagazi 75 MW Solar Plant | [5 empty] | 5 | 20 | 39 | 54 | 65 | 71 | 72 | 69 | 61 | 28 | 32 | 12 | 1 | [8 empty] | 539245
| Matarbari 2*600 MW (CPGCL) | 550 | 550 | 550 | 410 | 418 | 466 | 470 | 574 | 539 | 503 | 500 | 506 | 453 | 454 | 567 | 571 | 575 | 504 |  | 526 | 574 | 573 | 577 | 575 | 576 | 575 | 12560000
120 | Eastern Zone Total | 8204 | 8160 | 8123 | 7980 | 7974 | 7471 | 7363 | 7161 | 7116 | 7117 | 7313 | 7618 | 7964 | 7986 | 7939 | 7942 | 7941 | 7702 |  | 8352 | 8176 | 8085 | 8236 | 8230 | 7961 | 7741 | 187593092
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 52 | 44 | 44 | 45 | 45 | 45 | 16 | 16 | 16 | [5 empty] | 8 | 40 | 62 | 76 |  | 85 | 87 | 90 | 91 | 92 | 92 | 91 | 997440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 26 | 27 | 32 | 33 |  | 33 | 33 | 42 | 34 | 34 | 34 | 33 | 648480
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 72 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1939680
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 5 | 27 | 50 | 75 | 74 | 53 | 52 | 101 | 79 | 76 | 44 | 14 | 4 | [8 empty] | 685440
131 | Rampal 1320 MW (BIFPCL) | 621 | 621 | 623 | 622 | 625 | 622 | 623 | 624 | 557 | 557 | 559 | 580 | 620 | 626 | 624 | 552 | 558 | 558 |  | 600 | 624 | 626 | 624 | 622 | 625 | 625 | 14509090
132 | United Payra Power Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 614400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 220 | 220 | 220 | 180 | 180 |  | 220 | 220 | 220 | 22 | 48 | 121 | 220 | 4374600
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 32 | 32 | 32 |  | 48 | 48 | 64 | 32 | 32 | 64 | 64 | 1799136
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 307 | 307 | 250 | 250 | 250 | 250 | 250 | 307 | 307 | 270 | 270 | 307 | 250 | 250 | 250 |  | 276 | 307 | 307 | 307 | 307 | 307 | 307 | 6785500
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 130 | 80 | 130 | 130 | 130 | 80 | 80 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2462000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 7 | 7 | 8 | 8 | 8 | 7 | 7 | 9 | 8 | 8 | 8 |  | 2 | 2 | 8 | 8 | 8 | 10 | 1 | 183351
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | 32 | [8 empty] | 32 | 32 | 32 | 32 |  | 40 | 40 | 40 | 8 | 32 | 40 | 40 | 464250
143 | Gopalganj 100 MW Peaking PP | 14 | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 36 | 36 | 36 | 36 | 36 |  | 45 | 48 | 60 | 55 | 51 | 52 | 52 | 1019264
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 32 | 45 | 85 | 32 | 49 |  | 85 | 85 | 105 | 50 | 95 | 105 | 105 | 1502928
146 | Bheramara HVDC | 641 | 641 | 926 | 926 | 926 | 925 | 925 | 926 | 926 | 926 | 920 | 920 | 920 | 920 | 920 | 919 | 919 | 920 |  | 920 | 919 | 629 | 629 | 629 | 621 | 621 | 20288000
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1222 | 1182 | 1182 | 1120 | 1110 | 1020 | 980 | 1010 | 1030 | 1140 | 1160 | 1160 | 1170 | 1120 | 1020 | 940 |  | 870 | 960 | 970 | 1070 | 1244 | 1244 | 1244 | 28825000
149
150 | Barapukuria TPP Unit-1 | 64 | 63 | 63 | 64 | 64 | 64 | 64 | 63 | 63 | 63 | 63 | 62 | 62 | 63 | 63 | 63 | 62 | 63 |  | 64 | 64 | 65 | 65 | 64 | 65 | 64 | 1465309
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 220 | 220 | 5148000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 32 | 32 | 32 | 39 | 40 | 40 | 39 | 39 |  | 40 | 39 | 40 | 40 | 40 | 40 | 40 | 808215
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 38160
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 153 | [25 empty] | 195609
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 190 | 188 | 187 | 193 | 191 | 187 | 192 | 183 | 176 | 163 | 178 | 192 | 173 | 186 | 192 | 185 | 190 | 174 |  | 157 | 134 | 136 | 184 | 198 | 197 | 204 | 4652300
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 314 | 354 | 322 | 353 | 307 | 351 | 352 | 311 | 304 | 351 | 414 | 414 | 351 | 352 | 392 | 380 | 350 | 307 |  | 370 | 245 | 305 | 414 | 414 | 414 | 411 | 8494109
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 15 | 20 |  | 20 | 20 | 30 | 30 | 30 | 30 | 20 | 144516
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [11 empty] | 8 | 8 | 8 | 8 | 5 | 5 | 113364
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 35 | 35 | 14 | 14 | 14 | [7 empty] | 21 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 493050
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 21 | 14 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 21 | 28 | 36 | 33 | 33 | 30 | 33 |  | 35 | 39 | 47 | 44 | 42 | 42 | 42 | 607910
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | [10 empty] | 10 | 16 | 16 | 30 | 30 |  | 30 | 22 | 22 | 22 | 22 | 22 | 22 | 286497
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 46 | [18 empty] | 85 | 85 | 85 | 79 | 79 | 77 | 79 | 485152
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | [5 empty] | 14 | 35 | 102 | 112 | 112 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1794720
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | [5 empty] | 35 | 60 | 95 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1764096
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [11 empty] | 8 |  |  |  | 12 | [10 empty] | 10000
176 | Rangpur 113 MW PP (Confidence) | 106 | 100 | 100 | 100 | 100 | 35 | 35 | 35 | 35 | 10 |  |  |  | 11 | 34 | 65 | 92 | 94 |  | 104 | 105 | 105 | 106 | 106 | 106 | 107 | 1599984
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 7 | 7 | 8 | 4 | 7 | 6 | 4 | 3 | 1 | [8 empty] | 58953
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 74 | 74 | 74 | 35 | 35 | 35 | 41 | 70 | 85 | 112 | 113 | 114 | 114 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2313792
| Intraco Solar 30 MW | [5 empty] | 2 | 7 | 15 | 22 | 28 | 33 | 31 | 33 | 29 | 18 | 16 | 7 | 2 |  | 0 | [6 empty] | 249615
| Adani Power Jharkhanda Ltd | 1363 | 1368 | 1236 | 1234 | 1229 | 1222 | 1231 | 1219 | 1219 | 1222 | 1219 | 1259 | 1308 | 1357 | 1323 | 1307 | 1310 | 1316 |  | 1319 | 1313 | 1307 | 1311 | 1313 | 1326 | 1306 | 30916363
178 | Teesta Solar Limited | [5 empty] | 13 | 48 | 98 | 144 | 176 | 194 | 203 | 194 | 174 | 136 | 99 | 32 | 15 | [8 empty] | 1548190