## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-03-20 | Wednesday
|  | Date (day): | 2019-03-20 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12560 | MW |  |  | (b) At Evening Peak Hour : |  | 13380 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-03-19 | 2019-03-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 36 | 71 | 74 | 74
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 239 | 286 | 280 | 280
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 100 | 0 | 0 |  |  | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 220 | 360 | 360 |  |  | FGMO
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 73 | 77 | 75 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 |  |  | Relay replacement
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 40 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 352 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 70 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under Maint.
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 19 | 92 | 92 |  | 8 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 100 | 260 | 225 | 335
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 25 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 90 | 110 | 110 | 110
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 43 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 115 | 115 | 0 | 0 |  | 217 | Under maint.
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 70 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 40 | 41 | 40 | 41 |  | 9 | Engine problem
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 48 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 59 | 60 | 60 | 60 |  | 48 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 47 | 49 | 49 |  | 31 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 37 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 65 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 50 | 99 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2233 | 2861 | 4095 | 4409 | 355 | 673
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 24 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19.6 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 75 | 117 | 117 | 117 |  | 113 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 201 | 202 | 225 | 225 |  |  | FGMO
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 146 | 145 | 100 | 100
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 38 | 51 | 51 | 51
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 65 | 70 | 75
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 78 | 78 | 78 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 4 | 5 | 10
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 26 | 99 | 105 | 105
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 773.6 | 1109 | 1173 | 1163 | 240 | 175
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 80 | 100 | 100 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint.
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 184 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 300 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 349 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 37 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 4 | 6 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 63 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 10 | 0 | 42
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 0 | 90 | 90 |  | 73 | ST Under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 70 | 125 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 3 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 122 | 154 | 130 | 167
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 10 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 21 | 21
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1459 | 1517 | 2043 | 2222 | 349 | 223
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 155 | 128 | 130 | 130 | 72 |  | Gas shortage
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 80 | 87 | 87 | 87 |  | 8 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.2 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 0 | 103 | 200 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 107 | 107 | 106 | 107
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 344.2 | 425 | 525 | 546 | 72 | 8
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 59 | 40 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 62 | 62 | 62 | 62
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 173 | 170 | 170 | 170 |  | 160 | GT-2 Under maint.
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 37 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 40 | 66 | 66 |  |  | FGMO
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 85 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 47 | 47 | 47
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 101 | 104 | 115 | 115
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 48 | 48 | 48
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 25 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 255 | 341 | 341 |  |  | FGMO
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1141 | 1133 | 1319 | 1319 | 0 | 160
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 794 | 946 | 810 | 958
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 28 | 33 | 35 | 35
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 40 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 220 | 250 | 270 | 410
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
| Madhumati Power Plant |  | HFO | IPP | 100 MW | 0 | 0 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1128 | 1584 | 1515 | 1889 | 0 | 0
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 110 | 110 |  | 0
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 24 | 0 | 22
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 29 | 24 | 26 |  | 7 | Engine problem
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 120 | 120 | 175 | 175
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 261 | 380 | 404 | 428 | 0 | 7
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 55 | 60 | 60
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 48 | 0 | 48
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 50 | 50 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 40 | 40
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 209 | 182 | 195 | 195 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under S/D.
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 178 | 200 | 200 |  |  | FGMO
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 45 | 57 | 430 | 220 |  |  | ON test
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 21 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 17 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 25 | 100 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
| Confidence CPBL-2 |  | HFO | IPP | 113 MW | 0 | 0 | 90 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1835 | 1825 | 808 | 928 | 1227 | 1145 | 100 | 220
126 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 74 | 74
127 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 149 | 149 | 125 |  | Coal shortage
128 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
129 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 12 | 19 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 178 | 259 | 259 | 125 | 85
| Total |  |  |  |  | 18079 | 17536 | 8296.8 | 10115 | 12560 | 13380 | 1241 | 1551
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7910.4636 | 9644 | 11975.1498 | 12756.9669
A. |  | 2019-03-19 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10115 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 7030 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10115 | MW
3 | Day peak Generation : |  |  | 8296.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9644 | MW
4 | Evening peak Generation : |  |  | 10115 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 201.1296 | MKWHr | By Solar | 0.14908 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 141.8933 | MKWHr |  | By Oil: | 31.4172 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.7179 | MKWHr |  | By Hydro: | 2.1299 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1241 | MW | Dhaka | 3452 | 3452 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1551 | MW | Chittagong | 1086 | 1086 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2792 | MW | Khulna | 1128 | 1128 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1247.05 | MMCFD |  |  | Rajshahi | 1112 | 1112 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 102420015.656 | ii) Oil : | Taka | 242407891.77 | Comilla | 856 | 856 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14484245.26 | Total | Taka | 359312152.686 | Mymensingh | 784 | 784 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.67 | MKWHr. | Sylhet | 350 | 350 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -310 | MW (E to W) at | 19:00 | hrs | Barisal | 233 | 233 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -460 | MW at | 1:00 | hrs | Rangpur | 643 | 643 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.2° C |  |  | Total | 9644 | 9644 |  | 0
B. |  | 2019-03-20 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13380 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8700 | MW
4 | Reserve(Generation end) |  |  |  | 2680 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 212.7619 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7164 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.0364 | MKWHr. | ii) HVDC Flow at Peak Time |  | 946 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7859 | MKWHr. | iii) Maximum HVDC Flow : |  | 948 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 89.01 |  | (b) Today: | 88.77 |  | (c) Rule Curve: |  | 90.12
.

## YesterdayGen
2019-03-19
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | Madhumati Power Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 36 | 281 | 0 | 190 | 260 | 0 | 35 | 348 | 0 | 0 | 40 | 380 | 150 | 0 | 0 | 0 | 115 | 110 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 51 | 0 | 42 | 30 | 120 | 0 | 0 | 196 | 0 | 155 | 0 | 0 | 28 | 0 | 0 | 10 | 0 | 0 | 22 | 18 | 80 | 80 | 0 | 320 | 320 | 183 | 8 | 90 | 40 | 4 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 110 | 163 | 21 | 0 | 0 | 60 | 62 | 53 | 50 | 100 | 160 | 40 | 85 | 47 | 103 | 19 | 46 | 10 | 270 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 72 | 0 | 0 | 107 |  | 647 | 0 | 280 | 0 | 44 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 21 | 96 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 185 | 0 | 0 | 0 | 96 | 0 | 152 | 0 | 25 | 105 | 0 | 0 | 0 |  | 5716 | 2154 | 7870 | 4686 | 647 | 1324 | 752 | 149 | 72 | 130 | 110 | 0 | 0 | 89.04
2:00 | 36 | 281 | 0 | 190 | 260 | 0 | 35 | 353 | 0 | 0 | 40 | 380 | 150 | 0 | 0 | 0 | 115 | 110 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 42 | 30 | 120 | 0 | 0 | 189 | 0 | 155 | 0 | 0 | 28 | 0 | 0 | 10 | 0 | 0 | 22 | 21 | 80 | 80 | 0 | 320 | 320 | 184 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 104 | 160 | 0 | 0 | 0 | 60 | 62 | 5 | 50 | 100 | 160 | 40 | 85 | 47 | 114 | 0 | 46 | 10 | 290 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 107 |  | 646 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 21 | 48 | 0 | 0 | 60 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 193 | 0 | 0 | 0 | 97 | 0 | 158 | 0 | 25 | 70 | 0 | 0 | 0 |  | 5541 | 2001 | 7542 | 4694 | 646 | 1270 | 517 | 149 | 72 | 90 | 104 | 0 | 0 | 89.04
3:00 | 36 | 278 | 0 | 190 | 260 | 0 | 35 | 351 | 0 | 0 | 40 | 380 | 150 | 0 | 0 | 0 | 115 | 110 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 42 | 30 | 120 | 0 | 0 | 189 | 0 | 154 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 22 | 23 | 80 | 80 | 0 | 320 | 320 | 202 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 96 | 160 | 0 | 0 | 0 | 58 | 62 | 5 | 5 | 100 | 161 | 40 | 60 | 5 | 117 | 0 | 7 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 80 |  | 646 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 20 | 16 | 0 | 0 | 60 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 22 | 15 | 8 | 0 | 0 | 150 | 0 | 0 | 192 | 0 | 0 | 0 | 97 | 0 | 155 | 0 | 25 | 35 | 0 | 0 | 0 |  | 5345 | 1921 | 7266 | 4702 | 646 | 1131 | 389 | 150 | 72 | 80 | 96 | 0 | 0 | 89.03
4:00 | 36 | 282 | 0 | 190 | 260 | 0 | 35 | 352 | 0 | 0 | 40 | 380 | 150 | 0 | 0 | 0 | 115 | 110 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 42 | 30 | 120 | 0 | 0 | 188 | 0 | 154 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 22 | 28 | 80 | 80 | 0 | 320 | 320 | 183 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 94 | 161 | 0 | 0 | 0 | 58 | 62 | 5 | 5 | 100 | 160 | 40 | 60 | 5 | 105 | 0 | 7 | 10 | 300 | 23 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 60 |  | 647 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 158 | 0 | 25 | 17 | 0 | 0 | 0 |  | 5274 | 1854 | 7128 | 4676 | 647 | 1136 | 324 | 149 | 72 | 30 | 94 | 0 | 0 | 89.03
5:00 | 36 | 280 | 0 | 190 | 260 | 0 | 35 | 348 | 0 | 0 | 40 | 360 | 150 | 0 | 0 | 0 | 115 | 110 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 42 | 30 | 120 | 0 | 0 | 188 | 0 | 155 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 22 | 29 | 80 | 80 | 0 | 300 | 300 | 183 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 90 | 163 | 0 | 0 | 0 | 58 | 62 | 5 | 5 | 100 | 160 | 40 | 60 | 5 | 110 | 0 | 7 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 |  | 646 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 152 | 0 | 25 | 17 | 0 | 0 | 0 |  | 5196 | 1834 | 7030 | 4592 | 646 | 1108 | 343 | 149 | 72 | 30 | 90 | 0 | 0 | 89.02
6:00 | 36 | 284 | 0 | 190 | 260 | 0 | 35 | 350 | 0 | 0 | 40 | 360 | 150 | 0 | 0 | 0 | 115 | 110 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 42 | 30 | 120 | 0 | 0 | 190 | 0 | 155 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 22 | 26 | 80 | 80 | 0 | 290 | 298 | 183 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 90 | 164 | 0 | 0 | 0 | 58 | 62 | 5 | 5 | 130 | 162 | 40 | 60 | 5 | 104 | 0 | 42 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 23 | 0 | 0 | 60 |  | 706 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 18 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 6 | 8 | 0 | 52 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 0 | 0 | 97 | 0 | 155 | 0 | 25 | 17 | 0 | 0 | 0 |  | 5287.09 | 1906 | 7193.09 | 4589 | 706 | 1168 | 389 | 149 | 72 | 30 | 90 | 0.09 | 0 | 89.01
7:00 | 36 | 276 | 0 | 190 | 261 | 0 | 35 | 360 | 0 | 0 | 40 | 330 | 120 | 0 | 0 | 0 | 115 | 110 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 25 | 0 | 43 | 30 | 120 | 0 | 0 | 215 | 0 | 155 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 22 | 8 | 80 | 80 | 0 | 280 | 280 | 204 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 90 | 160 | 0 | 0 | 0.2 | 58 | 62 | 5 | 5 | 130 | 160 | 51 | 60 | 47 | 90 | 0 | 43 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.56 | 0 | 53 | 0 | 0 | 107 |  | 794 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 120 | 17 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 35 | 43 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 192 | 0 | 0 | 0 | 97 | 0 | 162 | 0 | 25 | 87 | 0 | 0 | 0 |  | 5354.76 | 2162 | 7516.76 | 4589 | 794 | 1173 | 616 | 149 | 73 | 30 | 90 | 2.76 | 0 | 89
8:00 | 36 | 279 | 0 | 190 | 260 | 0 | 35 | 353 | 0 | 0 | 40 | 330 | 120 | 0 | 0 | 0 | 115 | 110 | 60 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 0 | 0 | 0 | 22 | 25 | 31 | 33 | 33 | 43 | 0 | 45 | 30 | 120 | 0 | 0 | 202 | 0 | 153 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 22 | 7 | 80 | 80 | 0 | 300 | 280 | 190 | 8 | 90 | 40 | 4 | 5 | 5 | 0 | 0 | 0 | 22 | 3 | 25 | 15 | 92 | 160 | 7 | 0 | 0.8 | 60 | 62 | 5 | 5 | 130 | 162 | 40 | 60 | 47 | 95 | 0 | 43 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8 | 10 | 52 | 0 | 0 | 107 |  | 793 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 29 | 0 | 0 | 120 | 17 | 48 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 50 | 0 | 52 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 186 | 0 | 0 | 0 | 98 | 0 | 157 | 0 | 25 | 105 | 0 | 0 | 0 |  | 5392.6 | 2209 | 7601.6 | 4566 | 793 | 1165 | 724 | 149 | 75 | 29 | 92 | 8.6 | 0 | 88.99
9:00 | 36 | 278 | 0 | 190 | 260 | 0 | 40 | 370 | 0 | 0 | 40 | 400 | 150 | 0 | 0 | 0 | 115 | 110 | 62 | 0 | 0 | 0 | 10 | 0 | 32 | 0 | 39 | 0 | 18 | 0 | 22 | 25 | 31 | 33 | 33 | 51 | 0 | 45 | 30 | 120 | 0 | 0 | 201 | 0 | 152 | 0 | 0 | 18 | 0 | 0 | 10 | 0 | 0 | 22 | 2 | 80 | 80 | 0 | 300 | 300 | 185 | 8 | 86 | 40 | 4 | 5 | 8 | 0 | 0 | 0 | 22 | 3 | 25 | 15 | 106 | 159 | 23 | 0 | 1.1 | 58 | 62 | 35 | 19 | 163 | 171 | 53 | 78 | 47 | 85 | 0 | 43 | 10 | 295 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 10 | 52 | 0 | 0 | 107 |  | 794 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 10 | 48 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 50 | 0 | 52 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 196 | 0 | 0 | 0 | 96 | 0 | 165 | 0 | 25 | 105 | 0 | 0 | 0 |  | 5727.7 | 2218 | 7945.7 | 4625 | 794 | 1324 | 821 | 149 | 75 | 38 | 106 | 13.7 | 0 | 0
10:00 | 36 | 239 | 0 | 140 | 260 | 0 | 40 | 349 | 0 | 0 | 40 | 400 | 150 | 0 | 0 | 0 | 115 | 100 | 38 | 0 | 0 | 0 | 16 | 0 | 53 | 0 | 40 | 0 | 18 | 0 | 22 | 25 | 24 | 8 | 33 | 51 | 0 | 45 | 30 | 120 | 0 | 0 | 202 | 0 | 154 | 0 | 0 | 31 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 80 | 0 | 300 | 300 | 184 | 8 | 90 | 37 | 4 | 5 | 25 | 0 | 0 | 0 | 22 | 3 | 25 | 15 | 112 | 158 | 67 | 0 | 1.9 | 60 | 62 | 48 | 47 | 163 | 170 | 49 | 80 | 47 | 84 | 0 | 42 | 10 | 275 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16.7 | 10 | 55 | 0 | 0 | 107 |  | 793 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 10 | 32 | 0 | 0 | 60 | 0 | 0 | 24 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 0 | 0 | 95 | 0 | 152 | 0 | 40 | 70 | 0 | 66 | 0 |  | 5707.6 | 2255 | 7962.6 | 4419 | 793 | 1377 | 951 | 149 | 75 | 68 | 112 | 18.6 | 0 | 0
11:00 | 36 | 239 | 0 | 100 | 260 | 0 | 40 | 350 | 0 | 0 | 40 | 400 | 100 | 0 | 0 | 0 | 115 | 100 | 40 | 0 | 0 | 5 | 16 | 0 | 59 | 0 | 41 | 0 | 18 | 0 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 45 | 30 | 120 | 0 | 2 | 202 | 0 | 150 | 0 | 0 | 38 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 150 | 0 | 300 | 300 | 184 | 8 | 90 | 40 | 4 | 5 | 35 | 0 | 0 | 0 | 22 | 3 | 25 | 15 | 118 | 155 | 80 | 0 | 2 | 58 | 62 | 50 | 47 | 100 | 170 | 55 | 83 | 47 | 84 | 0 | 42 | 0 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 18.9 | 68 | 70 | 0 | 0 | 107 |  | 794 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 13 | 32 | 0 | 0 | 60 | 0 | 0 | 24 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 183 | 0 | 0 | 0 | 96 | 0 | 153 | 0 | 41 | 70 | 0 | 90 | 0 |  | 5814.9 | 2288 | 8102.9 | 4480 | 794 | 1339 | 1059 | 149 | 75 | 68 | 118 | 20.9 | 0 | 0
12:00 | 36 | 239 | 0 | 100 | 260 | 0 | 73 | 350 | 0 | 0 | 40 | 400 | 100 | 0 | 0 | 0 | 115 | 90 | 43 | 0 | 0 | 16 | 16 | 0 | 59 | 0 | 40 | 0 | 18 | 0 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 45 | 30 | 120 | 0 | 17 | 201 | 0 | 146 | 0 | 0 | 38 | 0 | 0 | 10 | 26 | 0 | 19 | 2 | 80 | 100 | 0 | 360 | 300 | 185 | 8 | 90 | 40 | 4 | 0 | 35 | 0 | 0 | 0 | 22 | 3 | 25 | 15 | 122 | 155 | 80 | 0 | 2.2 | 59 | 62 | 53 | 47 | 100 | 173 | 59 | 83 | 45 | 101 | 0 | 42 | 0 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19.6 | 100 | 70 | 0 | 0 | 107 |  | 794 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 14 | 32 | 0 | 0 | 60 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 209 | 0 | 0 | 0 | 95 | 0 | 180 | 0 | 45 | 70 | 0 | 90 | 0 |  | 5950.8 | 2346 | 8296.8 | 4557 | 794 | 1367 | 1142 | 149 | 75 | 69 | 122 | 21.8 | 0 | 0
13:00 | 46 | 238 | 0 | 90 | 260 | 0 | 73 | 387 | 0 | 0 | 40 | 400 | 150 | 0 | 0 | 0 | 115 | 90 | 96 | 0 | 0 | 16 | 16 | 0 | 57 | 0 | 40 | 0 | 18 | 0 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 80 | 30 | 120 | 0 | 23 | 216 | 0 | 135 | 0 | 0 | 39 | 0 | 0 | 10 | 31 | 0 | 19 | 5 | 80 | 100 | 0 | 360 | 349 | 198 | 8 | 100 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 19 | 3 | 25 | 15 | 120 | 153 | 80 | 0 | 2.2 | 58 | 62 | 53 | 47 | 100 | 170 | 63 | 85 | 45 | 99 | 0 | 42 | 0 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19.3 | 100 | 70 | 0 | 0 | 107 |  | 798 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 14 | 32 | 0 | 0 | 55 | 0 | 0 | 25 | 50 | 25 | 0 | 52 | 0 | 21 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 205 | 0 | 0 | 0 | 97 | 0 | 205 | 0 | 45 | 70 | 0 | 107 | 44 |  | 6213.5 | 2406 | 8619.5 | 4731 | 798 | 1383 | 1238 | 149 | 110 | 69 | 120 | 21.5 | 0 | 0
14:00 | 51 | 238 | 0 | 90 | 260 | 0 | 40 | 354 | 0 | 0 | 40 | 350 | 150 | 0 | 0 | 0 | 115 | 95 | 40 | 0 | 0 | 16 | 16 | 0 | 55 | 0 | 40 | 0 | 18 | 0 | 22 | 25 | 26 | 33 | 33 | 51 | 0 | 85 | 30 | 120 | 0 | 23 | 216 | 0 | 135 | 0 | 0 | 40 | 0 | 0 | 10 | 44 | 0 | 19 | 2 | 80 | 100 | 0 | 300 | 300 | 198 | 8 | 80 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 21 | 3 | 25 | 15 | 128 | 151 | 80 | 0 | 1.5 | 60 | 62 | 50 | 47 | 100 | 178 | 63 | 85 | 45 | 98 | 0 | 44 | 0 | 265 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 17.3 | 100 | 88 | 0 | 0 | 107 |  | 798 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 15 | 32 | 0 | 0 | 55 | 0 | 0 | 25 | 50 | 25 | 0 | 52 | 0 | 20 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 186 | 0 | 0 | 0 | 97 | 0 | 188 | 0 | 46 | 90 | 0 | 108 | 54 |  | 5954.8 | 2418 | 8372.8 | 4502 | 798 | 1277 | 1316 | 149 | 115 | 69 | 128 | 18.8 | 0 | 89.34
15:00 | 71 | 238 | 0 | 90 | 250 | 0 | 60 | 379 | 0 | 0 | 40 | 350 | 220 | 0 | 0 | 0 | 115 | 95 | 87 | 0 | 0 | 16 | 16 | 0 | 51 | 0 | 41 | 0 | 18 | 0 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 85 | 30 | 120 | 0 | 23 | 213 | 0 | 135 | 0 | 0 | 40 | 0 | 0 | 10 | 52 | 0 | 19 | 2 | 80 | 100 | 0 | 330 | 300 | 204 | 8 | 80 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 21 | 3 | 25 | 15 | 132 | 152 | 87 | 0 | 1.5 | 60 | 62 | 50 | 47 | 130 | 179 | 61 | 83 | 45 | 117 | 0 | 42 | 10 | 310 | 25 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 13.4 | 100 | 105 | 5 | 0 | 107 |  | 798 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 26 | 0 | 0 | 120 | 14 | 32 | 0 | 0 | 55 | 0 | 0 | 25 | 50 | 25 | 0 | 52 | 0 | 21 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 201 | 0 | 0 | 0 | 97 | 0 | 204 | 0 | 45 | 105 | 0 | 108 | 40 |  | 6297.9 | 2447 | 8744.9 | 4665 | 798 | 1377 | 1427 | 149 | 115 | 67 | 132 | 14.9 | 0 | 89.33
16:00 | 71 | 239 | 0 | 90 | 250 | 0 | 72 | 377 | 0 | 0 | 40 | 350 | 140 | 0 | 0 | 0 | 115 | 105 | 93 | 0 | 0 | 16 | 16 | 0 | 51 | 0 | 41 | 0 | 18 | 0 | 22 | 25 | 13 | 33 | 33 | 51 | 0 | 84 | 30 | 120 | 0 | 23 | 203 | 0 | 135 | 0 | 0 | 40 | 0 | 0 | 10 | 52 | 0 | 19 | 2 | 80 | 100 | 0 | 360 | 330 | 184 | 8 | 85 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 21 | 3 | 25 | 18 | 122 | 156 | 87 | 0 | 1 | 60 | 62 | 50 | 47 | 130 | 170 | 64 | 83 | 45 | 103 | 0 | 44 | 10 | 285 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 100 | 105 | 12 | 0 | 107 |  | 798 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 27 | 0 | 0 | 120 | 14 | 32 | 0 | 0 | 55 | 0 | 0 | 25 | 50 | 25 | 0 | 52 | 0 | 21 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 199 | 0 | 0 | 0 | 96 | 0 | 202 | 0 | 45 | 105 | 0 | 6 | 56 |  | 6208 | 2387 | 8595 | 4709 | 798 | 1365 | 1261 | 149 | 114 | 68 | 122 | 9 | 0 | 89.32
17:00 | 71 | 238 | 0 | 90 | 220 | 0 | 75 | 320 | 0 | 0 | 40 | 300 | 210 | 0 | 0 | 0 | 115 | 105 | 0 | 0 | 0 | 16 | 0 | 0 | 57 | 0 | 41 | 0 | 18 | 17 | 22 | 25 | 13 | 33 | 33 | 25 | 0 | 84 | 30 | 120 | 0 | 23 | 201 | 0 | 100 | 0 | 0 | 40 | 0 | 0 | 10 | 52 | 0 | 19 | 5 | 80 | 100 | 0 | 320 | 330 | 167 | 8 | 90 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 21 | 3 | 25 | 20 | 122 | 137 | 86 | 0 | 0.3 | 60 | 62 | 11 | 10 | 130 | 156 | 40 | 50 | 10 | 95 | 0 | 12 | 10 | 255 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 3 | 100 | 105 | 12 | 0 | 106 |  | 798 | 0 | 200 | 0 | 32 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 22 | 32 | 0 | 0 | 55 | 0 | 16 | 25 | 50 | 25 | 0 | 52 | 0 | 21 | 17 | 11 | 0 | 0 | 150 | 0 | 0 | 182 | 0 | 0 | 0 | 97 | 0 | 184 | 0 | 45 | 105 | 0 | 0 | 86 |  | 5688.3 | 2353 | 8041.3 | 4297 | 798 | 1124 | 1364 | 150 | 114 | 69 | 122 | 3.3 | 0 | 89.31
18:00 | 71 | 238 | 0 | 90 | 220 | 0 | 76 | 280 | 0 | 0 | 40 | 300 | 210 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 16 | 16 | 0 | 59 | 0 | 41 | 49 | 50 | 55 | 22 | 25 | 22 | 33 | 33 | 25 | 0 | 85 | 30 | 120 | 0 | 23 | 211 | 0 | 99 | 0 | 0 | 51 | 18 | 0 | 20 | 69 | 0 | 19 | 4 | 80 | 80 | 0 | 300 | 300 | 178 | 8 | 90 | 10 | 6 | 5 | 35 | 0 | 0 | 0 | 22 | 3 | 25 | 20 | 136 | 137 | 84 | 0 | 0 | 40 | 62 | 11 | 10 | 100 | 155 | 51 | 50 | 10 | 97 | 0 | 12 | 10 | 260 | 25 | 8 | 0 | 14 | 0 | 0 | 3 | 0 | 74 | 0 | 100 | 105 | 15 | 0 | 106 |  | 798 | 0 | 200 | 0 | 46 | 0 | 0 | 0 | 31 | 10 | 8 | 120 | 23 | 64 | 0 | 0 | 55 | 20 | 28 | 90 | 50 | 50 | 0 | 52 | 4 | 21 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 177 | 0 | 0 | 0 | 98 | 0 | 167 | 0 | 45 | 105 | 0 | 0 | 37 |  | 5782 | 2476 | 8258 | 4161 | 798 | 1101 | 1581 | 149 | 115 | 217 | 136 | 0 | 0 | 89.3
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 71 | 286 | 0 | 100 | 220 | 0 | 77 | 352 | 0 | 70 | 0 | 400 | 260 | 19 | 0 | 30 | 115 | 110 | 0 | 0 | 7 | 70 | 48 | 25 | 60 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 37 | 0 | 87 | 30 | 120 | 0 | 24 | 202 | 0 | 145 | 0 | 0 | 51 | 65 | 85 | 78 | 99 | 0 | 19 | 4 | 80 | 80 | 0 | 300 | 349 | 184 | 8 | 0 | 37 | 6 | 5 | 35 | 0 | 10 | 10 | 22 | 3 | 25 | 21 | 154 | 128 | 87 | 0 | 0 | 40 | 62 | 53 | 37 | 130 | 170 | 40 | 85 | 47 | 104 | 19 | 48 | 10 | 255 | 25 | 8 | 0 | 65 | 0 | 0 | 103 | 0 | 99 | 0 | 100 | 125 | 63 | 0 | 107 |  | 946 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 33 | 45 | 40 | 120 | 29 | 110 | 24 | 0 | 55 | 50 | 48 | 100 | 50 | 50 | 28 | 52 | 29 | 21 | 17 | 11 | 0 | 0 | 149 | 17 | 12 | 182 | 0 | 0 | 0 | 97 | 50 | 178 | 0 | 57 | 105 | 0 | 0 | 0 |  | 7045 | 3070 | 10115 | 4368 | 946 | 1421 | 2366 | 149 | 117 | 594 | 154 | 0 | 0 | 89.29
19:30 | 71 | 284 | 0 | 100 | 220 | 0 | 77 | 320 | 0 | 40 | 0 | 350 | 230 | 50 | 0 | 40 | 115 | 110 | 0 | 0 | 24 | 70 | 48 | 18 | 61 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 87 | 30 | 120 | 0 | 24 | 200 | 0 | 100 | 0 | 0 | 51 | 54 | 85 | 78 | 99 | 0 | 19 | 10 | 80 | 80 | 0 | 270 | 310 | 184 | 8 | 0 | 37 | 6 | 5 | 35 | 0 | 0 | 16 | 22 | 3 | 25 | 22 | 136 | 128 | 87 | 0 | 0 | 40 | 62 | 53 | 47 | 100 | 172 | 40 | 85 | 47 | 107 | 19 | 49 | 10 | 270 | 25 | 11 | 0 | 100 | 0 | 0 | 135 | 0 | 149 | 0 | 100 | 145 | 128 | 0 | 107 |  | 948 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 34 | 60 | 40 | 120 | 29 | 110 | 24 | 0 | 55 | 50 | 49 | 100 | 50 | 50 | 0 | 52 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 14 | 182 | 0 | 0 | 0 | 97 | 50 | 184 | 0 | 70 | 105 | 0 | 0 | 0 |  | 7033 | 3053 | 10086 | 4213 | 948 | 1387 | 2572 | 149 | 117 | 564 | 136 | 0 | 0 | 89.29
20:00 | 71 | 275 | 0 | 100 | 220 | 0 | 77 | 310 | 0 | 0 | 0 | 300 | 230 | 39 | 0 | 0 | 115 | 110 | 0 | 0 | 15 | 70 | 48 | 0 | 61 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 84 | 30 | 120 | 0 | 24 | 215 | 0 | 100 | 0 | 0 | 51 | 54 | 85 | 88 | 99 | 0 | 19 | 13 | 80 | 80 | 0 | 270 | 300 | 205 | 8 | 0 | 40 | 6 | 5 | 35 | 0 | 0 | 16 | 22 | 3 | 25 | 22 | 136 | 126 | 87 | 0 | 0 | 40 | 62 | 53 | 47 | 100 | 176 | 65 | 85 | 47 | 117 | 19 | 49 | 10 | 245 | 25 | 11 | 0 | 85 | 0 | 0 | 100 | 0 | 149 | 0 | 100 | 144 | 123 | 0 | 107 |  | 947 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 34 | 72 | 40 | 120 | 28 | 110 | 22 | 0 | 55 | 50 | 49 | 100 | 50 | 50 | 0 | 52 | 29 | 22 | 17 | 11 | 0 | 38 | 149 | 17 | 14 | 185 | 0 | 0 | 0 | 97 | 50 | 188 | 0 | 78 | 105 | 0 | 0 | 0 |  | 6849 | 3114 | 9963 | 4267 | 947 | 1322 | 2416 | 187 | 114 | 574 | 136 | 0 | 0 | 89.28
21:00 | 71 | 277 | 0 | 90 | 220 | 0 | 77 | 320 | 0 | 0 | 0 | 400 | 300 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 40 | 54 | 55 | 17 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 30 | 120 | 0 | 17 | 216 | 0 | 100 | 0 | 0 | 51 | 16 | 85 | 50 | 99 | 0 | 19 | 20 | 80 | 80 | 0 | 270 | 300 | 206 | 8 | 90 | 40 | 6 | 5 | 35 | 0 | 0 | 16 | 22 | 0 | 25 | 22 | 140 | 120 | 87 | 0 | 0 | 40 | 62 | 53 | 47 | 130 | 178 | 65 | 85 | 47 | 116 | 19 | 49 | 10 | 300 | 25 | 11 | 0 | 32 | 0 | 0 | 50 | 0 | 110 | 0 | 100 | 140 | 128 | 0 | 107 |  | 948 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 33 | 50 | 40 | 120 | 27 | 110 | 22 | 0 | 55 | 50 | 49 | 100 | 50 | 50 | 0 | 52 | 29 | 22 | 17 | 11 | 0 | 68 | 149 | 17 | 14 | 200 | 0 | 0 | 0 | 97 | 50 | 202 | 0 | 116 | 105 | 0 | 0 | 0 |  | 6765 | 3188 | 9953 | 4382 | 948 | 1551 | 2137 | 217 | 113 | 465 | 140 | 0 | 0 | 89.27
22:00 | 71 | 279 | 0 | 90 | 220 | 0 | 77 | 354 | 0 | 0 | 0 | 400 | 320 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 40 | 17 | 18 | 0 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 30 | 120 | 0 | 24 | 202 | 0 | 100 | 0 | 0 | 50 | 1 | 51 | 50 | 99 | 0 | 22 | 25 | 80 | 80 | 0 | 300 | 330 | 184 | 8 | 90 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 22 | 0 | 25 | 22 | 134 | 119 | 88 | 0 | 0 | 40 | 62 | 53 | 47 | 130 | 170 | 67 | 85 | 47 | 104 | 19 | 49 | 10 | 285 | 25 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 135 | 30 | 0 | 107 |  | 947 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 30 | 60 | 40 | 120 | 27 | 110 | 22 | 0 | 50 | 50 | 48 | 100 | 50 | 50 | 0 | 52 | 29 | 22 | 17 | 11 | 0 | 71 | 149 | 17 | 14 | 192 | 0 | 0 | 0 | 97 | 0 | 193 | 0 | 118 | 105 | 0 | 0 | 0 |  | 6419 | 3126 | 9545 | 4404 | 947 | 1543 | 1762 | 220 | 113 | 422 | 134 | 0 | 0 | 89.26
23:00 | 71 | 239 | 0 | 0 | 220 | 0 | 40 | 355 | 0 | 0 | 0 | 400 | 300 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 40 | 17 | 18 | 0 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 30 | 120 | 0 | 25 | 202 | 0 | 80 | 0 | 0 | 50 | 0 | 34 | 50 | 99 | 0 | 22 | 25 | 80 | 80 | 0 | 300 | 330 | 196 | 8 | 90 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 22 | 0 | 25 | 22 | 122 | 120 | 88 | 0 | 0 | 50 | 62 | 53 | 47 | 130 | 172 | 66 | 85 | 47 | 110 | 19 | 48 | 10 | 275 | 25 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 106 | 30 | 0 | 107 |  | 851 | 0 | 220 | 0 | 115 | 0 | 0 | 0 | 30 | 62 | 0 | 120 | 27 | 110 | 0 | 0 | 60 | 50 | 0 | 100 | 50 | 0 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 75 | 149 | 0 | 0 | 190 | 0 | 0 | 0 | 97 | 0 | 191 | 0 | 115 | 105 | 0 | 0 | 0 |  | 6175 | 2819 | 8994 | 4291 | 851 | 1492 | 1625 | 224 | 113 | 276 | 122 | 0 | 0 | 89.25
24:00 | 71 | 239 | 0 | 0 | 220 | 0 | 40 | 350 | 0 | 0 | 0 | 400 | 300 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 24 | 17 | 18 | 0 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 30 | 120 | 0 | 24 | 203 | 0 | 80 | 0 | 0 | 51 | 0 | 0 | 20 | 99 | 0 | 22 | 27 | 80 | 80 | 0 | 300 | 330 | 183 | 8 | 90 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 22 | 0 | 25 | 21 | 118 | 127 | 88 | 0 | 0 | 49 | 62 | 53 | 47 | 130 | 167 | 48 | 85 | 47 | 104 | 20 | 47 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 95 | 0 | 0 | 107 |  | 851 | 0 | 220 | 0 | 44 | 0 | 0 | 0 | 30 | 62 | 0 | 120 | 26 | 82 | 0 | 0 | 60 | 0 | 0 | 100 | 0 | 0 | 0 | 47 | 0 | 22 | 17 | 11 | 0 | 74 | 149 | 0 | 0 | 186 | 0 | 0 | 0 | 97 | 0 | 186 | 0 | 116 | 105 | 0 | 0 | 0 |  | 5995 | 2605 | 8600 | 4241 | 851 | 1478 | 1384 | 223 | 113 | 192 | 118 | 0 | 0 | 89.24
KWH | 1092000 | 6547600 | 0 | 3068100 | 5916409 | 0 | 1382976 | 8527870 | 0 | 70400 | 660000 | 8498250 | 4292218 | 67200 | 0 | 69950 | 2755401 | 2516850 | 1001000 | 0 | 32640 | 290304 | 223680 | 48456 | 871680 | 0 | 813216 | 237600 | 394520 | 209600 | 491976 | 600000 | 646740 | 744000 | 794700 | 1006500 | 0 | 1401862 | 728000 | 2800000 | 0 | 296460 | 4790253 | 0 | 3213548 | 0 | 0 | 829920 | 177416 | 333792 | 587160 | 940800 | 0 | 499440 | 290400 | 1996972 | 2048265 | 0 | 7739500 | 7609500 | 4600000 | 200727 | 1890660 | 875160 | 129600 | 120000 | 604502 | 0 | 6424 | 46104 | 506124 | 121500 | 611900 | 420920 | 2785920 | 3474000 | 1343040 | 0 | 9760 | 1287000 | 1489020 | 795000 | 770000 | 3264202 | 3874000 | 1247616 | 1806720 | 936720 | 2518950 | 132000 | 900300 | 204660 | 7249500 | 563952 | 238080 | 0 | 208250 | 0 | 0 | 516000 | 0 | 878400 | 139320 | 1449600 | 1999680 | 503490 | 0 | 2349600 |  | 19036363 | 0 | 6243400 | 0 | 987840 | 0 | 0 | 0 | 675360 | 308864 | 178500 | 2879000 | 454300 | 1328640 | 81762 | 0 | 1385000 | 277354 | 236602 | 960304 | 824460 | 669536 | 11997 | 985440 | 135306 | 505440 | 373284 | 238878 | 0 | 60218 | 3657700 | 70000 | 66000 | 4830900 | 0 | 0 | 0 | 2324992 | 161280 | 4412190 | 0 | 1181363 | 2062560 | 0 | 541440 | 301248 |  | 143223525 | 57906081 | 201129606 | 109900374 | 19036363 | 31992936 | 27852292 | 3717918 | 2129862 | 3564861 | 2785920 | 149080 | 0
Fuel Cost | 939120 | 5630936 | 0 | 2638566 | 3786501.76 | 0 | 1299997.44 | 5202000.7 | 0 | 676544 | 904200 | 5693827.5 | 65198791.42 | 422016 | 0 | 427394.5 | 1791010.65 | 2416176 | 1111110 | 0 | 204000 | 1913103.36 | 2162985.6 | 308664.72 | 5221363.2 | 0 | 5424150.72 | 1694088 | 2465750 | 1314192 | 368982 | 450000 | 0 | 0 | 0 | 9521490 | 0 | 0 | 0 | 3080000 | 0 | 2807476.2 | 3161566.98 | 0 | 3695580.2 | 0 | 0 | 7294996.8 | 1910770.32 | 3247796.16 | 3634520.4 | 6077568 | 0 | 424524 | 0 | 1817244.52 | 1863921.15 | 0 | 4798490 | 5250555 | 3220000 | 138501.63 | 1815033.6 | 586357.2 | 111456 | 110400 | 495691.64 | 0 | 69636.16 | 342091.68 | 389715.48 | 91125 | 471163 | 315690 | 19055692.8 | 2605500 | 12342537.6 | 0 | 0 | 1338480 | 1548580.8 | 763200 | 693000 | 2546077.56 | 2711800 | 1422282.24 | 1933190.4 | 1030392 | 2871603 | 168960 | 837279 | 190333.8 | 4639680 | 422964 | 180940.8 | 0 | 1511895 | 0 | 0 | 3689400 | 0 | 0 | 0 | 0 | 18677011.2 | 4702596.6 | 0 | 0 |  | 97085451.3 | 0 | 4183078 | 0 | 8189193.6 | 0 | 0 | 0 | 7604553.6 | 3638417.92 | 1406580 | 1986510 | 449757 | 9831936 | 2753744.16 | 0 | 1454250 | 3175703.3 | 2536373.44 | 8604323.84 | 7131579 | 5958870.4 | 127768.05 | 9775564.8 | 1592551.62 | 555984 | 350886.96 | 180830.646 | 0 | 365523.26 | 14118722 | 2256100 | 1766820 | 3285012 | 0 | 0 | 0 | 0 | 2794982.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 272292229.49 | 203161067.296 | 475453296.786 | 80580360.726 | 97085451.3 | 21839654.93 | 200960347.6 | 14484245.26 | 0 | 41447544.17 | 19055692.8 | 0 | 0
Yesterday Day Peak | 36 | 239 | 0 | 100 | 260 | 0 | 73 | 350 | 0 | 0 | 40 | 400 | 100 | 0 | 0 | 0 | 115 | 90 | 43 | 0 | 0 | 16 | 16 | 0 | 59 | 0 | 40 | 0 | 18 | 0 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 45 | 30 | 120 | 0 | 17 | 201 | 0 | 146 | 0 | 0 | 38 | 0 | 0 | 10 | 26 | 0 | 19 | 2 | 80 | 100 | 0 | 360 | 300 | 185 | 8 | 90 | 40 | 4 | 0 | 35 | 0 | 0 | 0 | 22 | 3 | 25 | 15 | 122 | 155 | 80 | 0 | 2.2 | 59 | 62 | 53 | 47 | 100 | 173 | 59 | 83 | 45 | 101 | 0 | 42 | 0 | 285 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19.6 | 100 | 70 | 0 | 0 | 107 |  | 794 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 28 | 0 | 0 | 120 | 14 | 32 | 0 | 0 | 60 | 0 | 0 | 25 | 50 | 50 | 0 | 52 | 0 | 22 | 14 | 11 | 0 | 0 | 149 | 0 | 0 | 209 | 0 | 0 | 0 | 95 | 0 | 180 | 0 | 45 | 70 | 0 | 90 | 0 |  | 8296.8 | DayPeak
Yesterday Evening Peak | 71 | 286 | 0 | 100 | 220 | 0 | 77 | 352 | 0 | 70 | 0 | 400 | 260 | 19 | 0 | 30 | 115 | 110 | 0 | 0 | 7 | 70 | 48 | 25 | 60 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 37 | 0 | 87 | 30 | 120 | 0 | 24 | 202 | 0 | 145 | 0 | 0 | 51 | 65 | 85 | 78 | 99 | 0 | 19 | 4 | 80 | 80 | 0 | 300 | 349 | 184 | 8 | 0 | 37 | 6 | 5 | 35 | 0 | 10 | 10 | 22 | 3 | 25 | 21 | 154 | 128 | 87 | 0 | 0 | 40 | 62 | 53 | 37 | 130 | 170 | 40 | 85 | 47 | 104 | 19 | 48 | 10 | 255 | 25 | 8 | 0 | 65 | 0 | 0 | 103 | 0 | 99 | 0 | 100 | 125 | 63 | 0 | 107 |  | 946 | 0 | 250 | 0 | 115 | 0 | 0 | 0 | 33 | 45 | 40 | 120 | 29 | 110 | 24 | 0 | 55 | 50 | 48 | 100 | 50 | 50 | 28 | 52 | 29 | 21 | 17 | 11 | 0 | 0 | 149 | 17 | 12 | 182 | 0 | 0 | 0 | 97 | 50 | 178 | 0 | 57 | 105 | 0 | 0 | 0 |  | 10115 | EvPeak
Forecast for Evening | 74 | 280 | 0 | 0 | 360 | 0 | 78 | 412 | 0 | 110 | 0 | 450 | 335 | 92 | 100 | 55 | 0 | 110 | 0 | 100 | 100 | 102 | 149 | 100 | 60 | 0 | 41 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 87 | 30 | 120 | 0 | 25 | 225 | 0 | 100 | 0 | 0 | 51 | 75 | 85 | 78 | 105 | 50 | 22 | 10 | 100 | 100 | 0 | 360 | 360 | 221 | 8 | 90 | 40 | 5 | 5 | 35 | 0 | 42 | 52 | 22 | 11 | 33 | 21 | 167 | 130 | 87 | 22 | 0 | 60 | 62 | 51 | 44 | 163 | 170 | 66 | 86 | 47 | 115 | 20 | 48 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 107 |  | 958 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 35 | 80 | 40 | 175 | 26 | 110 | 22 | 0 | 60 | 50 | 48 | 100 | 50 | 50 | 40 | 52 | 30 | 22 | 17 | 11 | 0 | 74 | 149 | 17 | 19 | 195 | 0 | 0 | 0 | 95 | 100 | 200 | 0 | 220 | 105 | 0
Forecast for Day | 74 | 280 | 0 | 0 | 360 | 0 | 75 | 412 | 0 | 110 | 0 | 450 | 225 | 92 | 100 | 55 | 0 | 110 | 0 | 100 | 100 | 102 | 149 | 100 | 60 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 51 | 0 | 87 | 30 | 120 | 0 | 25 | 225 | 0 | 100 | 0 | 0 | 51 | 70 | 85 | 78 | 105 | 50 | 22 | 5 | 100 | 100 | 0 | 360 | 360 | 221 | 8 | 90 | 40 | 5 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 130 | 130 | 87 | 0 | 2 | 60 | 62 | 51 | 44 | 163 | 170 | 66 | 86 | 47 | 115 | 20 | 48 | 10 | 341 | 25 | 11 | 100 | 200 | 200 | 100 | 200 | 100 | 149 | 20 | 100 | 200 | 150 | 0 | 106 |  | 810 | 0 | 270 | 0 | 115 | 0 | 0 | 0 | 35 | 40 | 40 | 175 | 24 | 110 | 0 | 0 | 60 | 0 | 0 | 100 | 50 | 50 | 40 | 52 | 0 | 22 | 17 | 11 | 0 | 74 | 149 | 17 | 19 | 195 | 0 | 0 | 0 | 95 | 100 | 200 | 0 | 430 | 105 | 0
Generation at 08:00(Today) | 74 | 239 | 0 | 0 | 220 | 0 | 40 | 349 | 0 | 0 | 0 | 400 | 225 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 12 | 0 | 0 | 0 | 22 | 25 | 32 | 33 | 33 | 16 | 0 | 83 | 30 | 120 | 0 | 0 | 201 | 0 | 80 | 0 | 0 | 22 | 0 | 0 | 10 | 0 | 0 | 22 | 25 | 80 | 80 | 0 | 270 | 280 | 188 | 8 | 90 | 40 | 6 | 5 | 35 | 0 | 0 | 0 | 22 | 0 | 25 | 21 | 98 | 127 | 40 | 0 | 0.8 | 50 | 62 | 50 | 47 | 100 | 170 | 35 | 40 | 47 | 110 | 20 | 46 | 10 | 265 | 24 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 8.5 | 30 | 0 | 0 | 0 | 107 | 0 | 801 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 120 | 12 | 32 | 0 | 0 | 60 | 0 | 0 | 51 | 50 | 0 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 74 | 149 | 0 | 0 | 155 | 0 | 0 | 0 | 97 | 0 | 177 | 0 | 438 | 105 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7030 | 5:00
| Highest Generation |  | 10115 | 19:00
| Day Peak Generation |  | 8296.8 | 12:00
| Evening Peak Generation |  | 10115 | 19:00
| HVDC Max Flow |  | 948 | 19:30
| HVDC EvPeak Flow |  | 946 | 19:00
| Load factor L.F |  | 82.85%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-03-20
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-03-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8296.8 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7164 | MW
Evening Peak Generation : |  | 10115 | MW Hour : | 19:00 | Available Max Generation : |  | 13380 | MW
E.P. Demand (at gen end) : |  | 10115 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 10700 | MW
Maximum Generation : |  | 10115 | MW Hour : | 19:00 | Reserve(Generation end) |  | 2680 | MW
Total Gen. (MKWH) : |  | 201.1296 | System Load Factor : | 82.85% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -460 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-03-20
Actual : | 88.77 | Ft.(MSL) , | Rule curve : | 90.12 | Ft.( MSL )
Gas Consumed : | Total = | 1247.05 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 102420015.656
|  | Coal : | 14484245.26 | Oil : | 242407891.77 | Total : | 359312152.686
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3800.5535 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1291.33 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1156.7984 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1045.1974 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 944.567 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 762.2294 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 427.5763 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 196.29 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 587.8626 |  |  | 0 | 0%
Total | 0 |  | 10212.4045 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Siddirganj-335 MW
2) Khulna ST 110 MW
3) Ghorasal Unit-4,5
4) Bhagabari 100 MW
5) Shajibazar 330 MW GT-2
6) Haripur 360 MW
7) Ashuganj #5
8) Sirajganj #2
9) Haripur SBU-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Shyampur(N)-Shyampur(O) 132 kV Ckt-2 was under shut down from 09:21 to 12:07 for D/W.
b) Mymensing-Jamalpur 132 kV Ckt-2 was under shut down from 09:28 to 16:51 for C/M.
c) Hasnabad 132/33 kV T-2 transformer was under shut down from 08:04 to 17:24 for C/M.
d) Rampura-Bashundhara 132 kV Ckt-2 was under shut down from 07:15 to 09:11 for C/M.
e) Cumilla(N) 230/132 kV T-02 transformer tripped at 17:12 showing DTT-1 at 230 kV and was switched on at 17:23.
f) Tongi-Bashundhara 132 kV Ckt-1 tripped at 16:29 showing BN from both end and was switched on at 16:52.
g) Tongi-Kabirpur 132 kV Ckt-1 tripped at 16:29 showing dist.Z1 from both end and was switched on at 16:44.
h) After maintenance Barapukuria #2 was synchronized at 19:30.
i) Joydevpur 132/33 kV T-1 transformer was under shut down from 19:31 to 19:57 for C/M.
j) Ghorasal #5 was shut down at 22:23 due to problem with vacuum system.
k) Ashuganj-Ghorasal 230 kV Ckt-2 tripped at 23:05 showing voltage fail and was switched on at 10:57(20/3/19).
l) Siddirganj-335 MW CCPP GT was shut down at 07:03(20/3/19) for replacing air filter.
m) Ishurdi 33 kV Bus-1 was under shut down from 06:17 to 08:05(20/3/19) for D/W. |  |  |  | About 10 MW power interruption occurred under Ishurdi S/S
n) Bakulia-Kulshi 132 kV Ckt tripped from 07:21 to 08:02(20/3/19) showing dist.Z1,E/F relay. |  |  |  | area from 07:21 to 08:02(20/3/2019).
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-03-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 71 | 1092000 | #2 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 286 | 6547600 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 100 | 3068100 | Frequency control
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 220 | 5916409 | Frequency control
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 77 | 1382976 | Frequency control
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Relay replacement
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 660000 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 352 | 8527870 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 70 | 70400 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 8498250 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 19 | 67200 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 4292218 | Frequency control
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 69950 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 25 | 48456 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 491976
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 110 | 2516850
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 1001000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 7 | 32640 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 115 | 2755401 | Machine problem
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 70 | 290304 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 41 | 813216 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 237600
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 223680 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 394520
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 209600
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 60 | 871680 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1246740 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 744000
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 794700
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 37 | 1006500
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 65 | 208250 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 99 | 878400 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2861 | 54958486
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 24 | 296460
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 139320
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 0 | 0 | 33 kV feeder fault
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 117 | 2129862 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4790253 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 145 | 3213548
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 829920
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 65 | 177416 | Low demand
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 85 | 333792
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 78 | 587160 | Engine problem
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1449600
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 499440
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 4 | 290400
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 940800 | Engine problem
| Chattogram area Total |  |  |  | 1681 | 1109 | 18477971
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1996972 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 2048265 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 184 | 4600000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7739500 | Frequency control
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 349 | 7609500 | Frequency control
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 37 | 875160 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 6 | 129600 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 604502 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 63 | 503490 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 10 | 6424 | Low demand
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 1890660 | Gas shortage
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 125 | 1999680 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 506124
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 3 | 121500
** | Tripura |  | Imported power | 0 | 160 | 154 | 2785920
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 611900 | Engine problem
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 10 | 46104 | Low demand
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 420920 | Engine problem
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1517 | 34816948
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 128 | 3474000 | Gas shortage
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | gas pipe maint.
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 87 | 1343040 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 9760
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 103 | 516000 | Low demand
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 107 | 2349600
| Mymensingh Area Total |  |  |  | 637 | 425 | 7692400
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 40 | 1287000 | ST Under maint.
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1489020
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3264202 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 170 | 3874000 | ST Under maint.FGMO
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 795000
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 37 | 770000 | Frequency control
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 8 | 238080
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 40 | 1247616 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 85 | 1806720
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 936720
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 104 | 2518950
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 132000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 48 | 900300
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 563952
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 255 | 7249500 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 0 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 204660
| Sylhet Area Total |  |  |  | 1549 | 1133 | 27277720
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 946 | 19036363
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 987840
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 33 | 675360
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 45 | 308864 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 250 | 6243400 | Frequency control
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 178500
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 50 | 161280 | Low demand
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 2062560
| Madhumati Power Plant |  | IPP | 100 MW | 0 | 0 | 301248
| Khulna Area Total |  |  |  | 2209 | 1584 | 29955415
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1328640
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 24 | 81762
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 29 | 454300 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 120 | 2879000 | Gas shortage
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2324992
| Barisal Area Total |  |  |  | 462 | 380 | 7068694
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 55 | 1385000 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 277354
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 48 | 236602
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 824460
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 669536
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 28 | 11997
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 182 | 4830900 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 178 | 4412190 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 57 | 1181363 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 29 | 135306
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 21 | 505440
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 17 | 373284
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238878
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 985440
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 960304
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 0 | 0 | 541440 | On test
| Rajshahi Area Total |  |  |  | 1825 | 928 | 17569494
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 60218 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3657700
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 70000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 12 | 66000
| Rangpur Area Total |  |  |  | 484 | 178 | 3853918
| Total |  |  |  | 17536 | 10115 | 201671046
| Eastern Grid Total |  |  |  | 12556 | 7045 | 143223525
| Western Grid Total |  |  |  | 4980 | 3070 | 58447521
| National Grid Total |  |  |  | 17536 | 10115 | 201671046
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-03-19 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6528 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3116 | MW
i) Dhaka area |  |  | 3452 | MW | i) Khulna area |  |  | 1128 | MW
ii) Chittagong area |  |  | 1086 | MW | ii) Rajshahi area |  |  | 1112 | MW
iii) Comilla area |  |  | 856 | MW | iii) Barisal area |  |  | 233 | MW
iv) Mymensingh area |  |  | 784 | MW | iv) Rangpur area |  |  | 643 | MW
v) Sylhet area |  |  | 350 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9644 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 1830 | Netrokona | 83 | 800 | Central s/s | 81 | 1900
Munsiganj | 98 | 1900 | Jamalpur | 106 | 1830 | Noapara | 85 | 1900
Sonargaon | 61 | 2000 | Sherpur | 90 | 1900 | Jessore | 130 | 1900
Shyampur | 170 | 1600 | Srimongal | 26 | 1830 | Jhenida | 82 | 1930
Bhulta | 170 | 2400 | Shahjibazar | 91 | 1900 | Bottail | 100 | 1900
Madanganj | 58 | 1300 | Fenchuganj | 31 | 1900 | G.K Project | 44 | 1900
Shitalakhya | 111 | 1700 | Kulawara | 29 | 1930 | Faridpur | 124 | 1900
Rahim steel | 21 | 800 | Sylhet | 108 | 1900 | Madaripur | 97 | 2100
Matuail | 95 | 1000 | Chatak | 23 | 1900 | Gopalganj | 71 | 1930
Ghorasal | 61 | 1830 | Sunamganj | 23 | 1830 | Bagerhat | 71 | 1900
Narsingdi | 100 | 2000 | Biani Bazar | 27 | 1830 | Mongla | 38 | 100
Haripur (SBU) | 82 | 1700 | Comilla (S) | 154 | 1900 | Satkhira | 73 | 1930
Ullon | 59 | 2000 | Comilla(N) | 93 | 1930 | Gallamari | 41 | 2100
Hasnabad | 181 | 2000 | Chandpur | 89 | 2100 | Magura | 50 | 1900
Magbazar | 107 | 1500 | Feni | 89 | 1900 | Chuadanga | 65 | 1900
Maniknagar | 96 | 1800 | Chowmuhani | 140 | 1930 | Barisal | 104 | 1900
Bangabhaban | 24 | 1600 | Ashuganj | 50 | 2000 | Patuakhali | 72 | 1930
Narinda | 88 | 1700 | Daudkandi | 112 | 1900 | Bhandaria | 42 | 2000
Dhanmondi | 82 | 1200 | B.Baria | 111 | 1830 | Ishurdi | 44 | 1930
Lalbag | 88 | 1900 | Ramganj | 40 | 1830 | Ruppur Paromanobik | 1 | 100
Madartek | 52 | 2200 | Madunaghat | 53.5 | 1900 | Natore | 108 | 2000
Mirpur | 93 | 1930 | Hathazari | 83 | 1830 | Bogra | 214 | 1900
Kalyanpur | 96 | 1930 | Khulshi | 196 | 1200 | Noagaon | 122 | 2000
Gulshan | 114 | 1600 | Halishahar | 127 | 1200 | Rajshahi | 128 | 2000
Uttara | 52 | 1900 | Baraulia | 144 | 1830 | C.Nawabganj | 67 | 2000
Uttara(New) | 13 | 1700 | Sikalbaha | 33 | 1900 | Amnura | 43 | 1900
Kamrangirchar | 73 | 1900 | Dohazari | 76 | 1830 | Pabna | 95 | 1930
Savar | 118 | 1500 | Cox'sbazar | 87 | 1900 | Shahjadpur | 86 | 1900
Bhasantec | 139 | 1300 | Chandraghona | 21 | 2000 | Serajganj | 86 | 1930
Agargaon | 47 | 1300 | Kaptai | 4.2 | 1900 | Niyamatpur | 94 | 1930
Satmosjid | 79 | 1900 | A. Khaer Stl. | 0 | 0 | Joypurhat | 45 | 1830
Tongi | 122 | 1600 | Bakulia | 91 | 1830 | Mohastangor | 11 | 2000
Kabirpur | 187 | 1500 | Julda | 21 | 1800 | Rangpur | 108 | 1830
Basundhara | 120 | 1500 | TK chemical | 5 | 1000 | Lalmonirhat | 83 | 2000
Manikganj | 78 | 1930 | Modern Steel | 17 | 400 | Saidpur | 99 | 1830
Joydevpur | 181 | 900 | Shahmirpur | 29 | 2400 | Purbasadipur | 90 | 2000
New Tongi | 98 | 1500 | Khagrachhari | 16 | 1830 | Thakurgaon | 71 | 1900
Kodda | 235 | 1000 | Matarbari | 23 | 1900 | Palashbari | 101 | 1900
Dhamrai | 46 | 1900 | Baroiar Hat | 36 | 2000 | Barapukuria | 51 | 900
Valuka | 58 | 1930 | Rangamati | 10 | 1830 | Panchagar | 38 | 1900
Tangail | 156 | 1900 | Abul Khair 230 | 137 | 500 | Joldhaka | 18 | 1900
Mymensing | 211 | 1830 | BSRM | 119 | 2100
Kishorganj | 92 | 1900 | Goalpara | 24 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-03-19
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 405 | 19:00 | 394 | 9:00 | Kaliakoir | 387 | 4:00 | 374 | 15:00
Bheramara | 400 | 2:00 | 383 | 19:30 | Bhulta | 401 | 4:00 | 389 | 15:00
Ashuganj(N) | 404 | 4:00 | 394 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 235 | 21:00 | 230 | 1:00 | Hathazari | 220 | 18:00 | 215 | 15:00
Ishurdi | 237 | 24:00 | 225 | 18:30 | Megnaghat | 230 | 1:00 | 225 | 17:00
Ashuganj | 242 | 4:00 | 235 | 15:00 | Fenchuganj | 242 | 19:00 | 236 | 15:00
Serajganj | 230 | 2:00 | 221 | 8:00 | Siddhirganj | 231 | 4:00 | 223 | 13:00
Baghabari | 230 | 23:00 | 222 | 7:00 | Maniknagar | 229 | 6:00 | 221 | 15:00
Barapukuria | 233 | 3:00 | 218 | 19:00 | Old Airport | 229 | 6:00 | 219 | 16:00
Bogra | 222 | 3:00 | 205 | 18:30 | Barisal | 238 | 10:00 | 226 | 13:00
Khulna South | 233 | 23:00 | 219 | 14:00 | AKSML | 221 | 6:00 | 215 | 15:00
Rampura | 229 | 5:00 | 220 | 16:00 | BSRM | 225 | 19:00 | 219 | 13:00
Haripur | 230 | 4:00 | 220 | 15:00 | Bibiyana | 241 | 6:00 | 232 | 15:00
Hasnabad | 228 | 6:00 | 220 | 15:00 | Bhulta | 230 | 4:00 | 222 | 15:00
Aminbazar | 229 | 4:00 | 221 | 16:00 | Ashuganj (S) | 239 | 4:00 | 234 | 12:00
Tongi | 226 | 4:00 | 217 | 15:00 | Kaliakoir | 231 | 5:00 | 217 | 15:00
Comilla (N) | 238 | 6:00 | 233 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 600 | 129 | 1500 | Madanhat | 132 | 1800 | 128 | 900
Munsiganj | 134 | 1900 | 128 | 1300 | Hathazari | 132 | 1900 | 128 | 900
Megnaghat | 134 | 1830 | 130 | 900 | Khulshi | 130 | 1930 | 124 | 1000
Shyampur | 133 | 200 | 128 | 1300 | Halishahar | 133 | 1930 | 126 | 1000
Bhulta | 130 | 400 | 124 | 1500 | Baraulia | 132 | 1930 | 126 | 900
Madanganj | 133 | 300 | 126 | 1600 | Sikalbaha | 132 | 1930 | 127 | 900
Shitalakhya | 139 | 1900 | 126 | 1600 | Dohazari | 130 | 1900 | 125 | 300
Rahim steal | 134 | 500 | 130 | 1500 | Cox'sbazar | 125 | 200 | 120 | 1000
Matuail | 133 | 500 | 128 | 1500 | Chandraghona | 133 | 1930 | 128 | 900
Ghorasal | 140 | 1800 | 135 | 100 | Kaptai | 134 | 300 | 129 | 800
Narsinghdi | 133 | 500 | 128 | 1300 | A. Khaer Stl. | 129 | 200 | 126 | 900
Haripur (SBU) | 134 | 500 | 130 | 1700 | Bakulia | 130 | 1930 | 125 | 900
Ullon | 135 | 600 | 130 | 1500 | Julda | 131 | 1800 | 125 | 800
Hasnabad | 135 | 600 | 128 | 1500 | TK Chemical | 133 | 2000 | 127 | 1000
Magbazar | 136 | 500 | 129 | 1600 | Modern Steel | 132 | 2400 | 125 | 900
Maniknagar | 132 | 600 | 127 | 1300 | Shahmirpur | 131 | 1900 | 125 | 700
Bangabhaban | 135 | 600 | 125 | 1600 | Khagrachhari | 132 | 1900 | 128 | 200
Narinda | 130 | 600 | 129 | 1600 | Matarbari | 125 | 1930 | 122 | 100
Dhanmondi | 135 | 600 | 130 | 1500 | Baroiar Hat | 132 | 2100 | 127 | 1400
Lalbag | 135 | 600 | 125 | 1600 | Rangamati | 133 | 1930 | 128 | 900
Madartek | 130 | 600 | 129 | 1600 | Goalpara | 138 | 2100 | 129 | 1300
Mirpur | 130 | 1830 | 124 | 1400 | Central s/s | 137 | 2100 | 128 | 1300
Kalyanpur | 132 | 600 | 121 | 1200 | Noapara | 135 | 900 | 125 | 1300
Gulshan | 136 | 500 | 130 | 1300 | Jessore | 132 | 1800 | 123 | 600
Uttara | 129 | 1900 | 124 | 1300 | Jhenida | 130 | 1800 | 107 | 1900
Uttara New | 129 | 600 | 123 | 1500 | Bottail | 136 | 600 | 127 | 1830
Kamrangirchar | 132 | 600 | 125 | 1300 | G.K.Project | 141 | 300 | 135 | 1830
Savar | 128 | 600 | 123 | 1500 | Faridpur | 133 | 1000 | 127 | 1900
Bhasantec | 131 | 600 | 124 | 1400 | Madaripur | 134 | 300 | 125 | 1830
Agargaon | 132 | 600 | 125 | 1500 | Gopalganj | 137 | 1700 | 123 | 1830
Satmosjid | 131 | 600 | 124 | 1500 | Bagerhat | 138 | 2200 | 128 | 700
Tongi | 133 | 1800 | 126 | 1500 | Mongla | 135 | 2300 | 126 | 1200
Kabirpur | 136 | 400 | 129 | 1300 | Satkhira | 136 | 2200 | 127 | 1300
Basundhara | 131 | 400 | 121 | 1200 | Gallamari | 138 | 2200 | 129 | 1300
Manikganj | 140 | 300 | 134 | 1500 | Magura | 130 | 2200 | 121 | 1300
Joydevpur | 140 | 1800 | 134 | 2200 | Chuadanga | 123 | 400 | 98 | 1830
New Tongi | 134 | 500 | 126 | 1500 | Barisal | 140 | 900 | 135 | 1400
Kodda | 140 | 1500 | 132 | 500 | Patuakhali | 139 | 900 | 131 | 1500
Dhamrai | 135 | 100 | 129 | 1500 | Bhandaria | 136 | 800 | 130 | 1830
Valuka | 132 | 100 | 122 | 800 | Ishurdi | 138 | 100 | 133 | 1900
Tangail | 133 | 300 | 125 | 700 | Ruppur Paromanobik | 139 | 100 | 134 | 1900
Mymensing | 130 | 2300 | 120 | 700 | Natore | 134 | 1200 | 128 | 1900
Kishorganj | 132 | 300 | 125 | 1300 | Bogra | 133 | 500 | 121 | 1900
Netrokona | 130 | 100 | 118 | 1300 | Noagaon | 128 | 200 | 117 | 1900
Jamalpur | 136 | 1930 | 118 | 700 | Rajshahi | 133 | 1000 | 126 | 1900
Sherpur | 134 | 1830 | 119 | 700 | C.Nawabganj | 130 | 1700 | 123 | 700
Srimongal | 139 | 500 | 136 | 1100 | Amnura | 136 | 1800 | 124 | 400
Shahjibazar | 137 | 500 | 134 | 1300 | Pabna | 132 | 100 | 126 | 1900
Fenchuganj | 138 | 600 | 134 | 1200 | Shahjadpur | 140 | 600 | 133 | 1300
Khulawara | 137 | 400 | 132 | 900 | Serajganj | 135 | 200 | 125 | 1830
Sylhet | 135 | 400 | 132 | 1300 | Niyamatpur | 123 | 300 | 109 | 1900
Chatak | 136 | 500 | 132 | 1200 | Joypurhat | 125 | 600 | 113 | 1900
Sunamganj | 135 | 500 | 132 | 1200 | Mohastangor | 132 | 100 | 120 | 1900
Biani Bazar | 136 | 600 | 132 | 1300 | Rangpur | 130 | 200 | 114 | 1900
Comilla(s) | 128 | 200 | 120 | 1900 | Lalmonirhat | 128 | 500 | 105 | 1900
Comilla(n) | 138 | 700 | 135 | 1200 | Saidpur | 132 | 600 | 113 | 1900
Chandpur | 137 | 800 | 134 | 2200 | Purbasadipur | 132 | 600 | 113 | 1900
Feni | 131 | 700 | 127 | 1500 | Thakurgaon | 127 | 500 | 100 | 1900
Chowmuhani | 130 | 800 | 126 | 1830 | Palashbari | 130 | 500 | 115 | 1900
Ashuganj | 140 | 600 | 136 | 1200 | Barapukuria | 133 | 500 | 118 | 1900
Daudkandi | 133 | 700 | 128 | 1500 | Panchagar | 124 | 600 | 95 | 1900
B.Baria | 135 | 1700 | 131 | 2200 | Joldhaka | 131 | 400 | 110 | 1900

## L-Curve
Date | 2019-03-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 70 | 5995 | 2605 | 8600 |  |  |  | QF-LDC-12
0:30 | 265 | 5855.5 | 2379.5 | 8235 | Date: | 2019-03-19
1:00 | 460 | 5716 | 2154 | 7870
1:30 | 440 | 5628.5 | 2077.5 | 7706
2:00 | 420 | 5541 | 2001 | 7542
2:30 | 405 | 5443 | 1961 | 7404 | [5 empty] | Gen. at Eve. Peak | 10115 | 10115 MW (19:00 )
3:00 | 390 | 5345 | 1921 | 7266 | [6 empty] | 19:00
3:30 | 365 | 5309.5 | 1887.5 | 7197 | [5 empty] | Gen. at Day Peak | 8296.8 | 8296.8 MW (12:00 )
4:00 | 340 | 5274 | 1854 | 7128 | [6 empty] | 12:00
4:30 | 340 | 5235 | 1844 | 7079 | [5 empty] | Highest Generation | 10115
5:00 | 340 | 5196 | 1834 | 7030 | [6 empty] | 19:00
5:30 | 310 | 5241.545 | 1870 | 7111.545
6:00 | 280 | 5287.09 | 1906 | 7193.09
6:30 | 355 | 5320.925 | 2034 | 7354.925
7:00 | 430 | 5354.76 | 2162 | 7516.76
7:30 | 385 | 5373.68 | 2185.5 | 7559.18
8:00 | 340 | 5392.6 | 2209 | 7601.6
8:30 | 325 | 5560.15 | 2213.5 | 7773.65
9:00 | 310 | 5727.7 | 2218 | 7945.7
9:30 | 270 | 5717.65 | 2236.5 | 7954.15
10:00 | 230 | 5707.6 | 2255 | 7962.6
10:30 | 235 | 5761.25 | 2271.5 | 8032.75
11:00 | 240 | 5814.9 | 2288 | 8102.9
11:30 | 235 | 5882.85 | 2317 | 8199.85
12:00 | 230 | 5950.8 | 2346 | 8296.8
12:30 | 260 | 6082.15 | 2376 | 8458.15
13:00 | 290 | 6213.5 | 2406 | 8619.5
13:30 | 255 | 6084.15 | 2412 | 8496.15
14:00 | 220 | 5954.8 | 2418 | 8372.8
14:30 | 140 | 6126.35 | 2432.5 | 8558.85
15:00 | 60 | 6297.9 | 2447 | 8744.9
15:30 | 40 | 6252.95 | 2417 | 8669.95
16:00 | 20 | 6208 | 2387 | 8595
16:30 | 15 | 5948.15 | 2370 | 8318.15
17:00 | 10 | 5688.3 | 2353 | 8041.3
17:30 | 30 | 5735.15 | 2414.5 | 8149.65
18:00 | 50 | 5782 | 2476 | 8258
18:30 | 180 | 6413.5 | 2773 | 9186.5
19:00 | 310 | 7045 | 3070 | 10115
19:30 | 60 | 7033 | 3053 | 10086
20:00 | 80 | 6849 | 3114 | 9963 |  |  |  | Executive Engineer
20:30 | 60 | 6807 | 3151 | 9958 |  |  |  | Network Operation Division
21:00 | 40 | 6765 | 3188 | 9953
21:30 | 40 | 6592 | 3157 | 9749
22:00 | 40 | 6419 | 3126 | 9545 |  |  |  |  | Page 6 of 7
22:30 | 30 | 6297 | 2972.5 | 9269.5
23:00 | 20 | 6175 | 2819 | 8994
23:30 | 45 | 6085 | 2712 | 8797
24:00 | 70 | 5995 | 2605 | 8600
10115 MW (19:00 )
8296.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-03-19 |  | Energy | 201129606
[10 empty] | 2019-03-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4241 | 851 | 1478 | 1384 | 223 | 113 | 192 | 0 | 118
0:30 | 4463.5 | 749 | 1401 | 1068 | 186 | 92.5 | 161 | 0 | 114 | Date: | 2019-03-19
1:00 | 4686 | 647 | 1324 | 752 | 149 | 72 | 130 | 0 | 110
1:30 | 4690 | 646.5 | 1297 | 634.5 | 149 | 72 | 110 | 0 | 107 | [7 empty] | Total Energy | 201.1296 | Total Energy Gen 201.130 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 201.130 MKWHr
2:00 | 4694 | 646 | 1270 | 517 | 149 | 72 | 90 | 0 | 104 | [7 empty] | Energy not Served | 0
2:30 | 4698 | 646 | 1200.5 | 453 | 149.5 | 72 | 85 | 0 | 100 | [7 empty] | Energy Requirement | 201.1296
3:00 | 4702 | 646 | 1131 | 389 | 150 | 72 | 80 | 0 | 96
3:30 | 4689 | 646.5 | 1133.5 | 356.5 | 149.5 | 72 | 55 | 0 | 95 | [6 empty] | Shortage
4:00 | 4676 | 647 | 1136 | 324 | 149 | 72 | 30 | 0 | 94
4:30 | 4634 | 646.5 | 1122 | 333.5 | 149 | 72 | 30 | 0 | 92
5:00 | 4592 | 646 | 1108 | 343 | 149 | 72 | 30 | 0 | 90
5:30 | 4590.5 | 676 | 1138 | 366 | 149 | 72 | 30 | 0 | 90
6:00 | 4589 | 706 | 1168 | 389 | 149 | 72 | 30 | 0 | 90
6:30 | 4589 | 750 | 1170.5 | 502.5 | 149 | 72.5 | 30 | 0 | 90 |  |  |  |  | Coal
7:00 | 4589 | 794 | 1173 | 616 | 149 | 73 | 30 | 0 | 90
7:30 | 4577.5 | 793.5 | 1169 | 670 | 149 | 74 | 29.5 | 0 | 91 |  |  |  | Oil |  |  |  | ,
8:00 | 4566 | 793 | 1165 | 724 | 149 | 75 | 29 | 0 | 92
8:30 | 4595.5 | 793.5 | 1244.5 | 772.5 | 149 | 75 | 33.5 | 0 | 99
9:00 | 4625 | 794 | 1324 | 821 | 149 | 75 | 38 | 0 | 106
9:30 | 4522 | 793.5 | 1350.5 | 886 | 149 | 75 | 53 | 0 | 109
10:00 | 4419 | 793 | 1377 | 951 | 149 | 75 | 68 | 0 | 112
10:30 | 4449.5 | 793.5 | 1358 | 1005 | 149 | 75 | 68 | 0 | 115
11:00 | 4480 | 794 | 1339 | 1059 | 149 | 75 | 68 | 0 | 118
11:30 | 4518.5 | 794 | 1353 | 1100.5 | 149 | 75 | 68.5 | 0 | 120
12:00 | 4557 | 794 | 1367 | 1142 | 149 | 75 | 69 | 0 | 122
12:30 | 4644 | 796 | 1375 | 1190 | 149 | 92.5 | 69 | 0 | 121
13:00 | 4731 | 798 | 1383 | 1238 | 149 | 110 | 69 | 0 | 120
13:30 | 4731 | 798 | 1383 | 1238 | 149 | 110 | 69 | 0 | 120
14:00 | 4731 | 798 | 1383 | 1238 | 149 | 110 | 69 | 0 | 120
14:30 | 4698 | 798 | 1380 | 1332.5 | 149 | 112.5 | 68 | 0 | 126
15:00 | 4665 | 798 | 1377 | 1427 | 149 | 115 | 67 | 0 | 132
15:30 | 4687 | 798 | 1371 | 1344 | 149 | 114.5 | 67.5 | 0 | 127
16:00 | 4709 | 798 | 1365 | 1261 | 149 | 114 | 68 | 0 | 122
16:30 | 4503 | 798 | 1244.5 | 1312.5 | 149.5 | 114 | 68.5 | 0 | 122
17:00 | 4297 | 798 | 1124 | 1364 | 150 | 114 | 69 | 0 | 122
17:30 | 4229 | 798 | 1112.5 | 1472.5 | 149.5 | 114.5 | 143 | 0 | 129
18:00 | 4161 | 798 | 1101 | 1581 | 149 | 115 | 217 | 0 | 136
18:30 | 4264.5 | 872 | 1261 | 1973.5 | 149 | 116 | 405.5 | 0 | 145
19:00 | 4368 | 946 | 1421 | 2366 | 149 | 117 | 594 | 0 | 154
19:30 | 4213 | 948 | 1387 | 2572 | 149 | 117 | 564 | 0 | 136
20:00 | 4267 | 947 | 1322 | 2416 | 187 | 114 | 574 | 0 | 136
20:30 | 4324.5 | 947.5 | 1436.5 | 2276.5 | 202 | 113.5 | 519.5 | 0 | 138
21:00 | 4382 | 948 | 1551 | 2137 | 217 | 113 | 465 | 0 | 140
21:30 | 4393 | 947.5 | 1547 | 1949.5 | 218.5 | 113 | 443.5 | 0 | 137
22:00 | 4404 | 947 | 1543 | 1762 | 220 | 113 | 422 | 0 | 134
22:30 | 4347.5 | 899 | 1517.5 | 1693.5 | 222 | 113 | 349 | 0 | 128
23:00 | 4291 | 851 | 1492 | 1625 | 224 | 113 | 276 | 0 | 122
23:30 | 4266 | 851 | 1485 | 1504.5 | 223.5 | 113 | 234 | 0 | 120 | Max Temp. in Dhaka |  | 30.2° C
24:00 | 4241 | 851 | 1478 | 1384 | 223 | 113 | 192 | 0 | 118
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 201.130 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 201.130 MKWHr
Note on W13: Author:

## Generation
2019-03-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 45 | 45 | 45 | 45 | 45 | 80 | 85 | 85 | 84 | 84 | 85 |  | 87 | 87 | 84 | 83 | 83 | 83 | 83 | 1401862
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram ST-1 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 0 | [5 empty] | 0 | 0 |  |  | 2 | 17 | 23 | 23 | 23 | 23 | 23 | 23 |  | 24 | 24 | 24 | 17 | 24 | 25 | 24 | 296460
| Teknaf Solartech 20MW | [5 empty] | 0.09 | 2.56 | 7.8 | 12.6 | 16.7 | 18.9 | 19.6 | 19.3 | 17.3 | 13.4 | 8 | 3 | 0 |  | 0 | [6 empty] | 139320
6 | Sikalbaha 225MW (Gas) | 196 | 189 | 189 | 188 | 188 | 190 | 215 | 202 | 201 | 202 | 202 | 201 | 216 | 216 | 213 | 203 | 201 | 211 |  | 202 | 200 | 215 | 216 | 202 | 202 | 203 | 4790253
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas) | 155 | 155 | 154 | 154 | 155 | 155 | 155 | 153 | 152 | 154 | 150 | 146 | 135 | 135 | 135 | 135 | 100 | 99 |  | 145 | 100 | 100 | 100 | 100 | 80 | 80 | 3213548
10 | Sikalbaha GT 150MW (Oil) | [17 empty] | 0
| Dohazari Peaking | [17 empty] | 0 |  | 85 | 85 | 85 | 85 | 51 | 34 | 0 | 333792
12 | Hathazari peaking | [17 empty] | 18 |  | 65 | 54 | 54 | 16 | 1 | 0 | 0 | 177416
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 10 | 0 | 0 |  |  |  |  | 6424
15 | Siddhirgonj ST 210MW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 90 | 90 | 95 | 95 | 105 | 105 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2516850
16 | Siddhirgonj GT Unit-1& 2 | 35 | 41 | 41 | 41 | 40 | 70 | 40 | 60 | 62 | 38 | 40 | 43 | 96 | 40 | 87 | 93 | 0 | 0 | [8 empty] | 1001000
17 | Siddhirganj CCPP-335 MW | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2755401
18 | Summit Gazipur -2 | [17 empty] | 14 |  | 65 | 100 | 85 | 32 | 0 |  |  | 208250
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal ST: Unit-1,2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 46 | 51 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1092000
21 | Ghorasal GT: Unit-3 | 281 | 281 | 278 | 282 | 280 | 284 | 276 | 279 | 278 | 239 | 239 | 239 | 238 | 238 | 238 | 239 | 238 | 238 |  | 286 | 284 | 275 | 277 | 279 | 239 | 239 | 6547600
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 140 | 100 | 100 | 90 | 90 | 90 | 90 | 90 | 90 |  | 100 | 100 | 100 | 90 | 90 | 0 | 0 | 3068100
24
25 | Ghorasal ST: Unit-7 | 260 | 260 | 260 | 260 | 260 | 260 | 261 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 250 | 250 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5916409
26
28 | Ashuganj ST: Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1996972
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 150 | 100 | 100 | 100 | 100 | 100 | 100 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2048265
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 10 |  | 37 | 37 | 40 | 40 | 40 | 40 | 40 | 875160
33 | Ashuganj CCPP 225 MW | 183 | 184 | 202 | 183 | 183 | 183 | 204 | 190 | 185 | 184 | 184 | 185 | 198 | 198 | 204 | 184 | 167 | 178 |  | 184 | 184 | 205 | 206 | 184 | 196 | 183 | 4600000
34 | Ashuganj CCPP(South) | 320 | 320 | 320 | 320 | 300 | 298 | 280 | 280 | 300 | 300 | 300 | 300 | 349 | 300 | 300 | 330 | 330 | 300 |  | 349 | 310 | 300 | 300 | 330 | 330 | 330 | 7609500
| Ashuganj CCPP(North) | 320 | 320 | 320 | 320 | 300 | 290 | 280 | 300 | 300 | 300 | 300 | 360 | 360 | 300 | 330 | 360 | 320 | 300 |  | 300 | 270 | 270 | 270 | 300 | 300 | 300 | 7739500
35 | Ashuganj (Precision) 55MW | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 129600
36 | Chandpur CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 86 | 90 | 90 | 90 | 100 | 80 | 80 | 85 | 90 | 90 |  | 0 | 0 | 0 | 90 | 90 | 90 | 90 | 1890660
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 0 | 0 | 0 | 0 |  |  |  | 660000
39 | Haripur 412 MW CCPP | 348 | 353 | 351 | 352 | 348 | 350 | 360 | 353 | 370 | 349 | 350 | 350 | 387 | 354 | 379 | 377 | 320 | 280 |  | 352 | 320 | 310 | 320 | 354 | 355 | 350 | 8527870
40 | Meghnaghat CCPP 450MW | 380 | 380 | 380 | 380 | 360 | 360 | 330 | 330 | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 300 | 300 |  | 400 | 350 | 300 | 400 | 400 | 400 | 400 | 8498250
41 | Haripur Power CCPP 360MW
42 | Mymensingh RPCL 210MW | 163 | 160 | 160 | 161 | 163 | 164 | 160 | 160 | 159 | 158 | 155 | 155 | 153 | 151 | 152 | 156 | 137 | 137 |  | 128 | 128 | 126 | 120 | 119 | 120 | 127 | 3474000
43 | Haripur NEPC 110MW | [19 empty] | 70 | 40 | 0 | 0 |  |  |  | 70400
44 | Fenchugonj CCPP-1 | 60 | 60 | 58 | 58 | 58 | 58 | 58 | 60 | 58 | 60 | 58 | 59 | 58 | 60 | 60 | 60 | 60 | 40 |  | 40 | 40 | 40 | 40 | 40 | 50 | 49 | 1287000
45 | Fenchugonj CCPP-2 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1489020
46 | Shajibazar 330 MW | 160 | 160 | 161 | 160 | 160 | 162 | 160 | 162 | 171 | 170 | 170 | 173 | 170 | 178 | 179 | 170 | 156 | 155 |  | 170 | 172 | 176 | 178 | 170 | 172 | 167 | 3874000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 40 | 40 | 40 | 40 | 40 | 51 | 40 | 53 | 49 | 55 | 59 | 63 | 63 | 61 | 64 | 40 | 51 |  | 40 | 40 | 65 | 65 | 67 | 66 | 48 | 1247616
48 | Shahjibazar 86MW | 85 | 85 | 60 | 60 | 60 | 60 | 60 | 60 | 78 | 80 | 83 | 83 | 85 | 85 | 83 | 83 | 50 | 50 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1806720
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 5 | 5 | 5 | 5 | 47 | 47 | 47 | 47 | 47 | 45 | 45 | 45 | 45 | 45 | 10 | 10 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 936720
50 | Sylhet GT 150 MW | 103 | 114 | 117 | 105 | 110 | 104 | 90 | 95 | 85 | 84 | 84 | 101 | 99 | 98 | 117 | 103 | 95 | 97 |  | 104 | 107 | 117 | 116 | 104 | 110 | 104 | 2518950
51 | Sylhet GT 20 MW | 19 | 0 | [17 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 132000
52 | Sylhet (EPL) 50MW | 46 | 46 | 7 | 7 | 7 | 42 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 44 | 42 | 44 | 12 | 12 |  | 48 | 49 | 49 | 49 | 49 | 48 | 47 | 900300
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 |  |  | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 204660
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 10 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 238080
55 | Fenchugonj (Barakatullah) 51MW | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 35 | 48 | 50 | 53 | 53 | 50 | 50 | 50 | 11 | 11 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 795000
56 | Shahjahanulla 25 MW | 25 | 25 | 23 | 23 | 24 | 24 | 24 | 16 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 17 | 24 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 563952
57 | Summit Bibiana- 2 | 270 | 290 | 300 | 300 | 290 | 290 | 300 | 295 | 295 | 275 | 290 | 285 | 285 | 265 | 310 | 285 | 255 | 260 |  | 255 | 270 | 245 | 300 | 285 | 275 | 260 | 7249500
58 | Southern 55MW | 0 | [14 empty] | 0 | 17 | 55 |  | 55 | 55 | 55 | 17 | 0 |  |  | 209600
59 | Sikalbaha (Energis) | 28 | 28 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 31 | 38 | 38 | 39 | 40 | 40 | 40 | 40 | 51 |  | 51 | 51 | 51 | 51 | 50 | 50 | 51 | 829920
60 | Barabkunda (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 499440
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491976
62 | Tangail (Doreen) 22MW
63 | Tripura | 110 | 104 | 96 | 94 | 90 | 90 | 90 | 92 | 106 | 112 | 118 | 122 | 120 | 128 | 132 | 122 | 122 | 136 |  | 154 | 136 | 136 | 140 | 134 | 122 | 118 | 2785920
64 | Malancha, Ctg. EPZ (United) | 18 | 21 | 23 | 28 | 29 | 26 | 8 | 7 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 5 | 4 |  | 4 | 10 | 13 | 20 | 25 | 25 | 27 | 290400
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 506124
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 0 |  |  |  | 121500
67 | Jangalia (Summit) 33MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 611900
68 | Summit Cumilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 20 | 20 |  | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 420920
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 24 | 24 | 24 | 24 | 26 | 24 | 13 | 13 | 22 |  | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 646740
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 744000
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 794700
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | [17 empty] | 0 |  | 7 | 24 | 15 | 0 |  |  |  | 32640
78 | Gazipur (RPCL) | 51 | 25 | 25 | 25 | 25 | 25 | 25 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 25 | 25 |  | 37 | 43 | 51 | 51 | 51 | 51 | 51 | 1006500
79 | Kodda 149MW | [8 empty] | 10 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 16 |  | 48 | 48 | 48 | 0 |  |  |  | 223680
80 | Jamalpur 95MW | 21 | 0 | [5 empty] | 7 | 23 | 67 | 80 | 80 | 80 | 80 | 87 | 87 | 86 | 84 |  | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 1343040
81 | Lakdhanvi 52 MW | [19 empty] | 10 | 16 | 16 | 16 | 0 | 0 |  | 46104
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW | [17 empty] | 0 |  | 25 | 18 | 0 | 0 |  |  |  | 48456
86 | Meghnaghat CCPP(Summit) | 150 | 150 | 150 | 150 | 150 | 150 | 120 | 120 | 150 | 150 | 100 | 100 | 150 | 150 | 220 | 140 | 210 | 210 |  | 260 | 230 | 230 | 300 | 320 | 300 | 300 | 4292218
87 | Meghnaghat (IEL) | [17 empty] | 0 |  | 19 | 50 | 39 | 0 |  |  |  | 67200
88 | Ghorashal 78MW (MAX) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 40 | 40 | 73 | 73 | 40 | 60 | 72 | 75 | 76 |  | 77 | 77 | 77 | 77 | 77 | 40 | 40 | 1382976
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 |  | 78 | 78 | 88 | 50 | 50 | 50 | 20 | 587160
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 19 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 10 | 10 |  | 37 | 47 | 47 | 47 | 47 | 47 | 47 | 770000
93 | Ashuganj (Midland) 51MW | 35 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 604502
94 | Gagnagar (Orion) | [10 empty] | 5 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 70 | 70 | 70 | 0 | 0 |  |  | 290304
95 | Patenga 50MW
96 | Chattogram ECPV 108 MW | 0 | [9 empty] | 0 | 26 | 31 | 44 | 52 | 52 | 52 | 69 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 940800
97 | Katpotti 51 MW | 18 | 12 | 6 | 6 | 6 | 6 | 36 | 40 | 39 | 40 | 41 | 40 | 40 | 40 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 40 | 40 | 40 | 24 | 813216
98 | Bosila 108MW | [7 empty] | 8 | 32 | 53 | 59 | 59 | 57 | 55 | 51 | 51 | 57 | 59 |  | 60 | 61 | 61 | 61 | 61 | 62 | 62 | 871680
99 | Madanganj-55 MW | [17 empty] | 0 |  | 30 | 40 | 0 | 0 |  |  |  | 69950
100 | Northern 55 MW | [8 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 50 |  | 55 | 55 | 55 | 55 | 18 | 18 | 18 | 394520
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 100 |  | 130 | 100 | 100 | 130 | 130 | 130 | 130 | 3264202
102 | Sarishabari (Solar) | [6 empty] | 0.2 | 0.8 | 1.1 | 1.9 | 2 | 2.2 | 2.2 | 1.5 | 1.5 | 1 | 0.3 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 9760
103 | Banco Energy 54MW | [16 empty] | 0 | 49 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 237600
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 0 | [16 empty] | 3 |  | 103 | 135 | 100 | 50 | 50 | 50 | 50 | 516000
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 0 | [7 empty] | 0 | 23 | 50 | 50 | 50 | 51 | 57 | 50 | 64 | 74 |  | 99 | 149 | 149 | 110 | 0 |  |  | 878400
115 | Juldah 100 MW Unit-3 | 50 | 0 | [5 empty] | 10 | 10 | 10 | 68 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1449600
116 | Chandpur Desh 200MW | 72 | 67 | 51 | 24 | 17 | 23 | 53 | 52 | 52 | 55 | 70 | 70 | 70 | 88 | 105 | 105 | 105 | 105 |  | 125 | 145 | 144 | 140 | 135 | 106 | 95 | 1999680
117 | Midland 150MW | [13 empty] | 0 | 5 | 12 | 12 | 15 |  | 63 | 128 | 123 | 128 | 30 | 30 | 0 | 503490
118 | Bibiyana-3 285MW
| United Jamalpur PPL | 107 | 107 | 80 | 60 | 60 | 60 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 106 | 106 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2349600
120 | Eastern Zone Total | 5716 | 5541 | 5345 | 5274 | 5196 | 5287.09 | 5354.76 | 5392.6 | 5727.7 | 5707.6 | 5814.9 | 5950.8 | 6213.5 | 5954.8 | 6297.9 | 6208 | 5671.3 | 5782 |  | 7045 | 7033 | 6849 | 6765 | 6419 | 6175 | 5995 | 143223525
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | 44 | 0 |  |  |  |  | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 46 |  | 115 | 115 | 115 | 115 | 115 | 115 | 44 | 987840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 27 | 28 | 31 |  | 33 | 34 | 34 | 33 | 30 | 30 | 30 | 675360
Khulna CCPP 225MW
129 | Labon Chora 105 MW | 105 | 70 | 35 | 17 | 17 | 17 | 87 | 105 | 105 | 70 | 70 | 70 | 70 | 90 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2062560
130
131
132
133
| Summit Barisal 110 MW | 96 | 48 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 64 |  | 110 | 110 | 110 | 110 | 110 | 110 | 82 | 1328640
136 | Barisal GT: Unit-1, 2 | [19 empty] | 24 | 24 | 22 | 22 | 22 | 0 |  | 81762
137 | Bhola Aggreko 95MW | 96 | 97 | 97 | 97 | 97 | 97 | 97 | 98 | 96 | 95 | 96 | 95 | 97 | 97 | 97 | 96 | 97 | 98 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 2324992
| Bhola CCPP 194MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2879000
140 | Bhola (Venture) 33MW | 21 | 21 | 20 | 19 | 19 | 18 | 17 | 17 | 10 | 10 | 13 | 14 | 14 | 15 | 14 | 14 | 22 | 23 |  | 29 | 29 | 28 | 27 | 27 | 27 | 26 | 454300
141 | Bangla Trak Noapara | [19 empty] | 50 | 50 | 50 | 50 | 0 |  |  | 161280
142 | Noapara (KZA) 40MW | [17 empty] | 8 |  | 40 | 40 | 40 | 40 | 40 | 0 |  | 178500
143 | Gopalganj Peaking | [17 empty] | 10 |  | 45 | 60 | 72 | 50 | 60 | 62 | 62 | 308864
144 | Bheramara GT-1,2,3
145 | Madhumati Power Plant | [12 empty] | 44 | 54 | 40 | 56 | 86 | 37 |  | 0 | [6 empty] | 301248
146 | Bheramara HVDC | 647 | 646 | 646 | 647 | 646 | 706 | 794 | 793 | 794 | 793 | 794 | 794 | 798 | 798 | 798 | 798 | 798 | 798 |  | 946 | 948 | 947 | 948 | 947 | 851 | 851 | 19036363
147 | Bheramara 360 MW | 280 | 280 | 280 | 280 | 250 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 250 | 200 | 200 |  | 250 | 220 | 220 | 220 | 220 | 220 | 220 | 6243400
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2 | [20 empty] | 0 | 38 | 68 | 71 | 75 | 74 | 60218
152 | Barapukuria Unit-3 | 149 | 149 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3657700
153 | Baghabari GT 71MW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 50 | 60 | 60 | 1385000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 0 | [16 empty] | 20 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 277354
157 | Sirajgonj Unit-1 225MW (Gas) | 185 | 193 | 192 | 190 | 180 | 181 | 192 | 186 | 196 | 181 | 183 | 209 | 205 | 186 | 201 | 199 | 182 | 177 |  | 182 | 182 | 185 | 200 | 192 | 190 | 186 | 4830900
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 152 | 158 | 155 | 158 | 152 | 155 | 162 | 157 | 165 | 152 | 153 | 180 | 205 | 188 | 204 | 202 | 184 | 167 |  | 178 | 184 | 188 | 202 | 193 | 191 | 186 | 4412190
| Sirajgonj Unit-3 225 MW(Oil) | [25 empty] | 0
160 | Sirajgonj Unit-4 414 MW(Gas) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 40 | 41 | 45 | 45 | 46 | 45 | 45 | 45 | 45 |  | 57 | 70 | 78 | 116 | 118 | 115 | 116 | 1181363
161 | Bera Peaking | [16 empty] | 16 | 28 |  | 48 | 49 | 49 | 49 | 48 | 0 |  | 236602
162 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 21 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 505440
163 | Bogra (EPL) | 14 | 14 | 15 | 16 | 17 | 16 | 17 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 373284
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 238878
165 | Amnura 50MW | 0 |  |  |  | 0 | 6 | 35 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 824460
166 | Katakhali (Northern) | 0 |  |  |  | 0 | 8 | 43 | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 25 | 25 | 25 | 50 |  | 50 | 50 | 50 | 50 | 50 | 0 |  | 669536
167 | Katakhali Peaking | [17 empty] | 0 |  | 28 | 0 | 0 | 0 |  |  |  | 11997
168 | Santahar Peaking | 0 | [16 empty] | 4 |  | 29 | 29 | 29 | 29 | 29 | 0 |  | 135306
169 | Rajlanka 52 MW | 0 |  |  | 0 | 26 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 47 | 985440
170 | Chapainawabganj-100 MW | 100 | 60 | 50 | 0 | [5 empty] | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 960304
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [9 empty] | 66 | 90 | 90 | 107 | 108 | 108 | 6 | 0 | 0
173 | Rangpur GT | [17 empty] | 0 |  | 17 | 17 | 17 | 17 | 17 | 0 |  | 70000
175 | Saidpur GT | [17 empty] | 0 |  | 12 | 14 | 14 | 14 | 14 | 0 |  | 66000
176
177
178
178 | Western Zone Total | 2154 | 2001 | 1921 | 1854 | 1834 | 1906 | 2162 | 2209 | 2218 | 2255 | 2288 | 2346 | 2406 | 2418 | 2447 | 2387 | 2353 | 2476 |  | 3070 | 3053 | 3114 | 3188 | 3126 | 2819 | 2605 | 57906081