## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-05 | Wednesday
|  | Date (day): | 2024-06-05 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14194.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15985 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-04 | 2024-06-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 376 | 356 | 350 | 350 | 50 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 390 | 380 | 380 | 380 | 70 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 16 | 25 | 25 | 25 |  |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 153 | 136 | 150 | 150 | 185 |  | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 66 | 66 | 60 | 66 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 22 | 0 | 22 | 53 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 17 | 25 | 17 | 25 |  |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 320 | 320 | 320
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 25 | 90 | 24 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 149 | 48 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 17 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 33 | 33 | 33 |  | 47 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 24 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 6 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 153 | 243 | 150 | 260 | 40 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 131 | 115 | 132 |  | 17 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 17 | 88 | 17 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 51 | 70 | 50 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 |  | 584 | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 2377 | 2777 | 2295 | 2810 | 1096 | 1461
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 16 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 46 | 45 | 6 | 45
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 92 | 100 | 95 | 95 | 135 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 222 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 17 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 55 | 57 | 55 | 70 | 28 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 68 | 85 | 51 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 68 | 68 | 40 | 68 | 32 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 22 | 22 | 25 | 25 | 75 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 12 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 38 | 38 | 30 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 84 | 92 | 85 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 24 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 72 | 35 | 72 | 44 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 145 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 473 | 480 | 450 | 490 |  | 734 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 2 | 7 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 436 | 792 | 850 | 900
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 40 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1881 | 2417 | 2282 | 2626 | 968 | 1103
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 218 | 218 | 200 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 280 | 280 | 280 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 270 | 280 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 260 | 230 | 260 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 15 | 15 | 30 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 85 | 66 | 70 | 100 | 50 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 46 | 45 | 46 |  | 6 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 50 | 50 |  | 113 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 84 | 92 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 32 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 33 | 43 | 42 | 42 |  | 10 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 97 | 17 | 17 | 97 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 73 | 46 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 | 37 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 105 | 104 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1534 | 1704 | 1646 | 1772 | 685 | 150
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 31 | 30 | 40 | 162 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 78 | 106 | 65 | 107 | 93 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 69 | 87 | 80 | 98 | 17 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 6 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 225 | 236 | 232.6 | 257 | 162 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 40 | 53 | 53 | 53
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 43 | 40 | 43 |  | 7 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 40 | 56 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 210 | 211 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 265 | 280 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 402 | 387 | 350 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 345 | 350 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1684 | 1626 | 1624 | 1711 | 0 | 452
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 921 | 905 | 940 | 795
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 16 | 78 | 20 | 80
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 49 | 30 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 56 | 50 | 66 |  | 43 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 200 | 205 | 210 | 200 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 16 | 40 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 90 | 53 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 64 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 565 | 509 | 450 | 500
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1872 | 1927 | 1880 | 1831 | 797 | 43
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 3 | 8 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1000 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 280 | 250 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1633 | 1636 | 1700 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 30 | 30 |  | 22 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 35 | 14 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 0 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 140 | 140 | 150 | 60
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 370 | 320 | 320 | 380 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 5 | 5 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 94 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1214 | 1190 | 1200 | 1400
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1784 | 2101 | 1972 | 2406 | 743 | 93
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 64 | 60 | 65
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44 | Coal Shortage.
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 10 | 104 | 70 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 187 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 565 | 513 | 563 | 516 | 40 | 136
| Total |  |  |  |  | 27054 | 25903 | 13555 | 14937 | 14194.6 | 15985 | 4606 | 3502
A. |  | 2024-06-04 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 14937 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 11768 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15080 | MW
3 | Day peak Generation : |  |  | 13555 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14607.16 | MW
4 | Evening peak Generation : |  |  | 14937 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 137 | MW
5 | Total Energy Generation : |  | 327.9044 | MKWHr | By Solar | 2.5759 | MKWHr
| By Gas : | 133.8503 | MKWHr |  | By Oil: | 56.4657 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 109.1711 | MKWHr |  | By Hydro: | 2.2609 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.3072 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4606 | MW | Dhaka | 5257.26 | 5217.26 |  | 40 |  | 18:00 |  | 90
|  |  | For Plants S/D or M/C prob = |  |  | 3502 | MW | Chittagong | 1544.4 | 1544.4 |  | 0 |  | 19:00 |  | 44
|  |  | Total = |  |  | 8108 | MW | Khulna | 1790 | 1790 |  | 0 |  | 19:30 |  | 136.565
7 | Total Gas Supplied : |  |  | 985.86 | MMCFD |  |  | Rajshahi | 1573.8 | 1573.8 |  | 0 |  | 20:00 |  | 154.71
8 | Fuel Cost : | i) Gas : | Taka | 411140053.8 | ii) Oil : | Taka | 1025383167.27 | Comilla | 1376 | 1376 |  | 0 |  | 21:00 |  | 183
|  | iii) Coal : | Taka | 747545918.79 | Total | Taka | 2184069139.86 | Mymensingh | 1187 | 1090 |  | 97 |  | 22:00 |  | 240.66
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 8314.35 | MKWHr. | Sylhet | 497 | 497 |  | 0 |  | 23:00 |  | 352.395
| ii) During Peak Demand : |  |  | 644 | MW (W to E) at | 19:30 | hrs | Barisal | 427.7 | 427.7 |  | 0 |  | 24:00 |  | 344.755
| iii) Maximum : |  |  | 550 | MW at | 20:00 | hrs | Rangpur | 954 | 954 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 36.0°C |  |  | Total | 14607.16 | 14470.16 |  | 137
B. |  | 2024-06-05 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15985 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13850 | MW
4 | Reserve(Generation end) |  |  |  | 85 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 349.0446 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12071 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3033 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9699 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.58 |  | (b) Today: | 81.57 |  | (c) Rule Curve: |  | 77.04

## YesterdayGen
2024-06-04 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 378 | 0 |  | 0 | 380 | 150 | 24 | 66 | 30 | 328 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 14 | 23 | 0 | 12 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 55 | 85 | 70 | 29 | 6 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 203 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 78 | 45 | 0 | 0 | 0 | 43 | 58 | 50 | 36 | 163 | 0 | 61 | 0 | 0 | 208 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 173 | 0 | 0 | 78 | 0 | 35 | 0 | 24 | 17 | 60 | 369 | 69 | 17 | 17 | 0 | 52 | 35 | 92 | 34 | 50 | 24 | 394 | 34 | 0 | 108 | 72 | 0 | 17 | 0 | 107 | 35 | 230 | 17 | 0 | 490 | 12 | 281 | 0 | 0 | 0 |  | 778 | 0 | 175 | 0 | 85 | 0 | 0 | 0 | 19 | 45 | 40 | 126 | 10 | 64 | 0 | 0 | 0 | 22 | 0 | 85 | 28 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 113 | 0 | 90 | 0 | 0 | 95 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 596 | 0 | 307 | 1320 | 0 | 0 |  | 7274 | 6353 | 13627 | 3871 | 778 | 1765 | 0 | 2213 | 4324 | 95 | 0 | 491 | 78 | 0 | 12 | 642.715 | 81.58
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 388 | 0 |  | 0 | 380 | 143 | 17 | 66 | 30 | 321 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 14 | 23 | 10 | 12 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 55 | 85 | 70 | 25 | 6 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 78 | 45 | 0 | 0 | 0 | 43 | 58 | 50 | 40 | 163 | 0 | 61 | 0 | 0 | 208 | 0 | 0 | 0 | 270 | 16 | 8 | 0 | 273 | 0 | 0 | 78 | 0 | 35 | 0 | 24 | 17 | 82 | 400 | 69 | 17 | 17 | 0 | 52 | 35 | 92 | 34 | 38 | 24 | 310 | 34 | 0 | 108 | 72 | 0 | 0 | 0 | 115 | 35 | 230 | 17 | 0 | 490 | 21 | 280 | 0 | 0 | 0 |  | 779 | 0 | 180 | 0 | 95 | 0 | 0 | 0 | 19 | 45 | 40 | 126 | 9 | 100 | 0 | 0 | 0 | 22 | 0 | 0 | 28 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 57 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 113 | 0 | 100 | 0 | 0 | 35 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 592 | 0 | 307 | 1318 | 0 | 0 |  | 7270 | 6320 | 13590 | 3833 | 779 | 1721 | 0 | 2299 | 4374 | 95 | 0 | 390 | 78 | 0 | 21 | 391.55 | 81.58
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 388 | 0 |  | 0 | 380 | 144 | 17 | 66 | 30 | 321 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 14 | 23 | 0 | 12 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 55 | 51 | 25 | 25 | 6 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 74 | 45 | 0 | 0 | 0 | 43 | 58 | 50 | 40 | 163 | 0 | 62 | 0 | 0 | 208 | 0 | 0 | 0 | 275 | 16 | 8 | 0 | 278 | 0 | 0 | 78 | 0 | 35 | 0 | 24 | 17 | 88 | 400 | 69 | 17 | 17 | 0 | 52 | 0 | 92 | 34 | 38 | 24 | 310 | 34 | 0 | 108 | 72 | 0 | 0 | 0 | 106 | 35 | 230 | 17 | 0 | 490 | 9 | 281 | 0 | 0 | 0 |  | 923 | 0 | 185 | 0 | 97 | 0 | 0 | 0 | 8 | 15 | 40 | 126 | 10 | 110 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 595 | 0 | 307 | 1318 | 0 | 0 |  | 7138 | 6138 | 13276 | 3827 | 923 | 1728 | 0 | 1957 | 4381 | 95 | 0 | 282 | 74 | 0 | 9 | 309.42 | 81.58
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 388 | 0 |  | 0 | 380 | 144 | 17 | 66 | 30 | 326 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 14 | 23 | 0 | 12 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 55 | 17 | 25 | 25 | 6 | 0 | 24 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 37 | 43 | 0 | 0 | 32 | 12 | 74 | 46 | 0 | 0 | 0 | 43 | 58 | 47 | 40 | 163 | 0 | 62 | 0 | 0 | 211 | 0 | 0 | 0 | 260 | 16 | 8 | 0 | 195 | 0 | 0 | 78 | 0 | 35 | 0 | 20 | 17 | 92 | 399 | 69 | 17 | 17 | 0 | 52 | 0 | 92 | 34 | 38 | 24 | 310 | 34 | 0 | 108 | 40 | 0 | 0 | 0 | 105 | 35 | 230 | 17 | 0 | 485 | 22 | 281 | 0 | 0 | 0 |  | 923 | 0 | 190 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 40 | 126 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 594 | 0 | 307 | 1314 | 0 | 0 |  | 6979 | 5996 | 12975 | 3840 | 923 | 1711 | 0 | 1781 | 4371 | 95 | 0 | 158 | 74 | 0 | 22 | 262.625 | 81.58
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 394 | 0 |  | 0 | 380 | 132 | 18 | 66 | 30 | 325 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 14 | 23 | 0 | 12 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 55 | 17 | 25 | 25 | 6 | 0 | 29 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 51 | 15 | 0 | 0 | 43 | 0 | 37 | 43 | 0 | 0 | 32 | 12 | 68 | 46 | 0 | 0 | 0 | 43 | 58 | 47 | 40 | 163 | 0 | 62 | 0 | 0 | 211 | 0 | 0 | 0 | 270 | 16 | 8 | 0 | 95 | 0 | 0 | 78 | 0 | 35 | 0 | 23 | 17 | 87 | 317 | 69 | 17 | 17 | 0 | 52 | 0 | 92 | 34 | 37 | 24 | 310 | 34 | 0 | 108 | 35 | 0 | 0 | 0 | 105 | 21 | 230 | 17 | 0 | 470 | 9 | 274 | 0 | 0 | 0 |  | 923 | 0 | 190 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 40 | 126 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 600 | 0 | 307 | 1328 | 0 | 0 |  | 6746 | 5876 | 12622 | 3765 | 923 | 1654 | 0 | 1597 | 4369 | 95 | 0 | 142 | 68 | 0 | 9 | 265.49 | 81.58
6:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 396 | 0 |  | 0 | 380 | 145 | 16 | 66 | 30 | 328 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 14 | 23 | 25 | 12 | 0 | 0 | 55 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 55 | 17 | 0 | 25 | 6 | 0 | 12 | 0 | 0 | 0 | 280 | 240 | 203 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 37 | 43 | 0 | 0 | 32 | 12 | 58 | 46 | 0 | 0 | 0 | 43 | 58 | 47 | 40 | 163 | 0 | 62 | 0 | 0 | 211 | 0 | 0 | 0 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 35 | 0 | 22 | 17 | 85 | 316 | 70 | 17 | 17 | 0 | 50 | 0 | 92 | 34 | 37 | 24 | 310 | 34 | 1 | 17 | 35 | 0 | 0 | 2 | 104 | 31 | 230 | 17 | 0 | 470 | 2 | 283 | 0 | 0 | 2 |  | 923 | 0 | 195 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 604 | 0 | 307 | 1332 | 9 | 0 |  | 6574 | 5542 | 12116 | 3803 | 923 | 1660 | 0 | 1126 | 4286 | 95 | 0 | 142 | 58 | 21 | 2 | 223.47 | 81.58
7:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 390 | 145 | 18 | 66 | 30 | 324 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 23 | 25 | 12 | 2 | 0 | 55 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 55 | 17 | 0 | 25 | 6 | 0 | 18 | 0 | 0 | 0 | 280 | 240 | 202 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 37 | 42 | 0 | 0 | 32 | 12 | 64 | 34 | 0 | 0 | 0 | 43 | 58 | 47 | 35 | 163 | 0 | 61 | 0 | 0 | 211 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 34 | 0 | 22 | 17 | 85 | 316 | 70 | 17 | 17 | 0 | 52 | 0 | 34 | 34 | 37 | 24 | 310 | 34 | 7 | 17 | 35 | 0 | 0 | 6 | 105 | 17 | 230 | 17 | 0 | 470 | 25 | 283 | 0 | 0 | 3 |  | 923 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 220 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 574 | 0 | 307 | 1166 | 0 | 0 |  | 6520 | 5345 | 11865 | 3799 | 923 | 1680 | 0 | 1024 | 4070 | 95 | 0 | 142 | 64 | 43 | 25 | 224.425 | 81.58
8:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 390 | 147 | 17 | 66 | 30 | 322 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 23 | 8 | 12 | 8 | 0 | 55 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 55 | 17 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 191 | 0 | 51 | 15 | 0 | 0 | 43 | 0 | 37 | 41 | 0 | 0 | 32 | 12 | 70 | 34 | 0 | 0 | 0 | 43 | 58 | 47 | 37 | 163 | 0 | 60 | 0 | 0 | 211 | 0 | 0 | 0 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 36 | 1 | 22 | 17 | 85 | 303 | 70 | 17 | 17 | 1 | 52 | 0 | 34 | 34 | 37 | 24 | 335 | 34 | 21 | 17 | 35 | 0 | 0 | 13 | 104 | 17 | 230 | 17 | 0 | 473 | 17 | 282 | 0 | 0 | 9 |  | 923 | 0 | 205 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 920 | 220 | 0 | 0 | 1 | 31 | 0 | 0 | 0 | 505 | 2 | 307 | 1188 | 6 | 0 |  | 6513 | 5255 | 11768 | 3783 | 923 | 1653 | 0 | 1033 | 3965 | 95 | 0 | 142 | 70 | 87 | 17 | 269.31 | 81.58
9:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 364 | 0 |  | 0 | 390 | 144 | 17 | 66 | 30 | 320 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 8 | 17 | 17 | 0 | 0 | 0 | 33 | 12 | 8 | 0 | 60 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 55 | 17 | 68 | 31 | 6 | 0 | 0 | 0 | 0 | 0 | 300 | 240 | 204 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 37 | 41 | 0 | 0 | 0 | 12 | 76 | 30 | 0 | 0 | 0 | 43 | 58 | 47 | 37 | 163 | 0 | 61 | 0 | 0 | 210 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 3 | 0 | 0 | 78 | 0 | 80 | 6 | 22 | 17 | 85 | 324 | 70 | 52 | 51 | 1 | 52 | 12 | 46 | 52 | 37 | 24 | 345 | 34 | 2 | 115 | 35 | 0 | 0 | 20 | 57 | 17 | 230 | 17 | 0 | 472 | 5 | 282 | 0 | 0 | 13 |  | 923 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 990 | 180 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 515 | 7 | 307 | 1167 | 23 | 0 |  | 6797 | 5285 | 12082 | 3680 | 923 | 1689 | 0 | 1296 | 4023 | 100 | 0 | 142 | 76 | 148 | 5 | 227.29 | 81.58
10:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 364 | 0 |  | 0 | 390 | 150 | 16 | 66 | 30 | 316 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 0 | 23 | 33 | 12 | 8 | 0 | 55 | 40 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 55 | 17 | 68 | 31 | 9 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 37 | 41 | 0 | 0 | 0 | 12 | 78 | 28 | 0 | 0 | 1 | 41 | 58 | 47 | 40 | 163 | 0 | 61 | 0 | 0 | 211 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 125 | 0 | 0 | 78 | 0 | 117 | 12 | 22 | 24 | 89 | 400 | 70 | 52 | 51 | 1 | 52 | 35 | 56 | 52 | 38 | 25 | 310 | 50 | 32 | 162 | 35 | 0 | 0 | 12 | 49 | 26 | 230 | 54 | 0 | 477 | 5 | 282 | 0 | 0 | 14 |  | 924 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 230 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1100 | 180 | 0 | 0 | 4 | 59 | 0 | 0 | 0 | 574 | 14 | 307 | 1118 | 80 | 0 |  | 7200 | 5413 | 12613 | 3732 | 924 | 1623 | 0 | 1594 | 4149 | 95 | 0 | 179 | 78 | 234 | 5 | 159.485 | 81.58
11:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 355 | 0 |  | 0 | 390 | 152 | 17 | 66 | 30 | 288 | 0 | 0 | 17 | 25 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 0 | 0 | 23 | 33 | 12 | 8 | 0 | 55 | 38 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 55 | 17 | 68 | 39 | 29 | 0 | 0 | 0 | 0 | 0 | 280 | 340 | 213 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 29 | 25 | 0 | 0 | 0 | 12 | 80 | 28 | 0 | 0 | 2 | 40 | 58 | 10 | 40 | 120 | 0 | 59 | 0 | 0 | 211 | 0 | 0 | 0 | 315 | 16 | 8 | 0 | 147 | 0 | 0 | 78 | 0 | 115 | 11 | 22 | 17 | 89 | 400 | 69 | 52 | 51 | 2 | 51 | 35 | 62 | 44 | 37 | 25 | 340 | 50 | 1 | 162 | 0 | 0 | 3 | 29 | 49 | 35 | 230 | 54 | 0 | 475 | 3 | 282 | 0 | 0 | 33 |  | 923 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 230 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 90 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1100 | 220 | 0 | 0 | 4 | 95 | 0 | 0 | 0 | 604 | 29 | 307 | 1117 | 103 | 0 |  | 7265 | 5696 | 12961 | 3871 | 923 | 1595 | 0 | 1732 | 4177 | 93 | 0 | 171 | 80 | 316 | 3 | 161.395 | 81.58
12:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 376 | 0 |  | 0 | 390 | 153 | 16 | 66 | 30 | 315 | 0 | 0 | 17 | 25 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 14 | 22 | 33 | 12 | 8 | 0 | 55 | 37 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 55 | 68 | 68 | 38 | 46 | 0 | 0 | 0 | 0 | 0 | 305 | 290 | 218 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 29 | 33 | 0 | 0 | 0 | 12 | 84 | 28 | 0 | 0 | 2 | 40 | 58 | 40 | 43 | 163 | 0 | 59 | 0 | 0 | 210 | 0 | 0 | 0 | 305 | 16 | 8 | 0 | 153 | 0 | 0 | 78 | 0 | 113 | 16 | 22 | 17 | 85 | 402 | 69 | 52 | 51 | 1 | 51 | 35 | 84 | 52 | 37 | 25 | 340 | 51 | 42 | 162 | 0 | 0 | 0 | 32 | 49 | 35 | 230 | 54 | 0 | 473 | 2 | 436 | 0 | 0 | 40 |  | 921 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 230 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 90 | 0 | 0 | 0 | 10 | 0 | 7 | 0 | 1050 | 220 | 0 | 0 | 0 | 64 | 35 | 0 | 0 | 565 | 34 | 280 | 1214 | 187 | 0 |  | 7701 | 5854 | 13555 | 3922 | 921 | 1730 | 0 | 1847 | 4310 | 92 | 0 | 222 | 84 | 425 | 2 | 91 | 81.58
13:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 369 | 0 |  | 0 | 390 | 150 | 17 | 66 | 30 | 316 | 0 | 0 | 17 | 25 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 13 | 22 | 33 | 12 | 8 | 0 | 55 | 37 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 64 | 68 | 68 | 38 | 50 | 0 | 0 | 0 | 0 | 0 | 280 | 270 | 190 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 29 | 25 | 0 | 0 | 32 | 12 | 90 | 28 | 0 | 0 | 2 | 40 | 58 | 50 | 43 | 120 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 145 | 0 | 0 | 78 | 0 | 129 | 19 | 22 | 17 | 87 | 402 | 69 | 52 | 51 | 2 | 51 | 35 | 92 | 52 | 37 | 25 | 376 | 50 | 27 | 162 | 13 | 0 | 0 | 30 | 49 | 35 | 250 | 54 | 0 | 472 | 16 | 447 | 0 | 0 | 42 |  | 921 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 230 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 89 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 1080 | 220 | 0 | 0 | 0 | 21 | 53 | 0 | 0 | 563 | 13 | 307 | 1260 | 192 | 0 |  | 7730 | 5943 | 13673 | 3936 | 921 | 1682 | 0 | 1915 | 4419 | 92 | 0 | 247 | 90 | 355 | 16 | 64 | 81.58
14:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 390 | 151 | 16 | 66 | 30 | 317 | 0 | 0 | 17 | 25 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 13 | 22 | 33 | 12 | 8 | 0 | 55 | 37 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 64 | 85 | 68 | 38 | 50 | 0 | 4 | 0 | 0 | 0 | 280 | 270 | 189 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 29 | 25 | 0 | 0 | 32 | 12 | 92 | 25 | 0 | 0 | 2 | 40 | 58 | 50 | 39 | 163 | 0 | 62 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 8 | 0 | 156 | 0 | 0 | 78 | 0 | 120 | 19 | 22 | 17 | 99 | 402 | 69 | 52 | 51 | 5 | 51 | 35 | 92 | 52 | 36 | 25 | 310 | 50 | 38 | 162 | 35 | 0 | 0 | 14 | 48 | 35 | 300 | 54 | 0 | 470 | 20 | 449 | 0 | 0 | 59 |  | 921 | 0 | 190 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 89 | 0 | 6 | 0 | 34 | 0 | 7 | 25 | 1130 | 220 | 0 | 0 | 4 | 37 | 110 | 0 | 0 | 574 | 13 | 307 | 1280 | 167 | 0 |  | 7829 | 6153 | 13982 | 3925 | 921 | 1697 | 0 | 2036 | 4501 | 92 | 0 | 333 | 92 | 365 | 20 | 64.94 | 81.58
15:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 400 | 150 | 17 | 66 | 30 | 310 | 0 | 0 | 17 | 25 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 0 | 22 | 33 | 12 | 8 | 0 | 60 | 37 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 64 | 85 | 68 | 38 | 50 | 0 | 2 | 0 | 0 | 0 | 300 | 290 | 198 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 37 | 25 | 0 | 0 | 32 | 12 | 90 | 26 | 0 | 0 | 1 | 40 | 58 | 50 | 39 | 163 | 0 | 59 | 0 | 0 | 210 | 0 | 0 | 0 | 315 | 16 | 8 | 0 | 143 | 0 | 0 | 78 | 0 | 104 | 13 | 22 | 17 | 99 | 402 | 69 | 52 | 51 | 2 | 52 | 35 | 92 | 52 | 36 | 25 | 320 | 50 | 22 | 162 | 35 | 0 | 19 | 22 | 48 | 35 | 230 | 17 | 0 | 470 | 28 | 751 | 0 | 0 | 35 |  | 921 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 126 | 7 | 0 | 0 | 0 | 0 | 30 | 0 | 44 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 89 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1172 | 220 | 0 | 0 | 3 | 63 | 115 | 0 | 0 | 567 | 22 | 307 | 1266 | 107 | 0 |  | 8123 | 6235 | 14358 | 3875 | 921 | 1803 | 0 | 2090 | 4827 | 97 | 0 | 335 | 90 | 292 | 28 | 183.36 | 81.58
16:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 390 | 152 | 16 | 66 | 29 | 313 | 0 | 0 | 17 | 25 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 0 | 22 | 33 | 10 | 8 | 0 | 60 | 38 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 64 | 85 | 68 | 38 | 45 | 0 | 3 | 0 | 0 | 0 | 280 | 290 | 196 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 37 | 25 | 0 | 0 | 32 | 0 | 94 | 27 | 0 | 0 | 1 | 40 | 58 | 50 | 40 | 163 | 0 | 58 | 0 | 0 | 209 | 0 | 0 | 0 | 320 | 16 | 8 | 0 | 155 | 0 | 0 | 77 | 0 | 88 | 8 | 22 | 17 | 100 | 375 | 68 | 52 | 51 | 3 | 52 | 35 | 92 | 52 | 37 | 25 | 340 | 51 | 12 | 162 | 35 | 0 | 20 | 15 | 46 | 35 | 230 | 17 | 0 | 470 | 26 | 777 | 0 | 0 | 8 |  | 924 | 0 | 180 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 40 | 126 | 7 | 32 | 0 | 0 | 0 | 30 | 0 | 44 | 11 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 89 | 0 | 37 | 0 | 34 | 0 | 4 | 90 | 1000 | 220 | 0 | 0 | 0 | 50 | 115 | 0 | 0 | 526 | 15 | 200 | 1271 | 74 | 0 |  | 8053 | 5986 | 14039 | 3836 | 924 | 1758 | 0 | 2234 | 4539 | 98 | 0 | 340 | 94 | 190 | 26 | 254.985 | 81.58
17:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 372 | 0 |  | 0 | 390 | 133 | 16 | 66 | 29 | 280 | 0 | 0 | 17 | 25 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 12 | 22 | 33 | 0 | 8 | 0 | 60 | 40 | 0 | 0 | 7 | 223 | 0 | 0 | 0 |  | 6 | 64 | 85 | 35 | 38 | 45 | 0 | 4 | 0 | 0 | 0 | 280 | 270 | 214 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 37 | 25 | 0 | 0 | 32 | 0 | 90 | 28 | 0 | 0 | 1 | 43 | 58 | 52 | 10 | 120 | 0 | 62 | 0 | 0 | 208 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 158 | 0 | 0 | 77 | 0 | 86 | 3 | 22 | 17 | 97 | 329 | 68 | 52 | 51 | 0 | 52 | 35 | 92 | 52 | 41 | 25 | 310 | 70 | 7 | 162 | 35 | 0 | 17 | 6 | 64 | 0 | 230 | 17 | 0 | 470 | 25 | 792 | 0 | 0 | 9 |  | 924 | 0 | 175 | 0 | 66 | 0 | 0 | 0 | 21 | 0 | 40 | 76 | 6 | 32 | 0 | 0 | 0 | 30 | 0 | 44 | 12 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 89 | 0 | 90 | 0 | 34 | 0 | 2 | 95 | 800 | 180 | 0 | 0 | 1 | 13 | 54 | 0 | 0 | 426 | 7 | 179 | 1181 | 35 | 0 |  | 7747 | 5381 | 13128 | 3648 | 924 | 1528 | 0 | 2226 | 4142 | 100 | 0 | 361 | 90 | 84 | 25 | 164.26 | 81.57
18:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 301 | 0 |  | 0 | 390 | 150 | 22 | 66 | 30 | 240 | 0 | 0 | 18 | 32 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 12 | 19 | 33 | 10 | 8 | 0 | 60 | 40 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 7 | 64 | 85 | 35 | 38 | 45 | 0 | 2 | 0 | 0 | 0 | 280 | 305 | 206 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 25 | 0 | 0 | 32 | 12 | 84 | 28 | 0 | 0 | 0 | 43 | 58 | 11 | 10 | 120 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 142 | 0 | 0 | 77 | 0 | 88 | 1 | 22 | 17 | 99 | 303 | 68 | 52 | 51 | 0 | 52 | 35 | 92 | 97 | 73 | 25 | 340 | 70 | 1 | 162 | 35 | 0 | 17 | 1 | 84 | 16 | 230 | 17 | 0 | 443 | 16 | 795 | 0 | 0 | 4 |  | 924 | 0 | 180 | 0 | 77 | 0 | 0 | 0 | 38 | 20 | 40 | 80 | 7 | 32 | 0 | 0 | 0 | 30 | 0 | 44 | 12 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 89 | 0 | 113 | 0 | 40 | 0 | 1 | 113 | 660 | 180 | 0 | 0 | 0 | 5 | 54 | 0 | 0 | 378 | 2 | 150 | 1060 | 11 | 0 |  | 7786 | 5060 | 12846 | 3576 | 924 | 1453 | 0 | 2402 | 3780 | 100 | 0 | 485 | 84 | 26 | 16 | 90 | 81.57
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 368 | 0 |  | 0 | 390 | 151 | 25 | 66 | 35 | 319 | 0 | 0 | 25 | 90 | 149 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 60 | 40 | 0 | 0 | 13 | 222 | 0 | 0 | 0 |  | 12 | 65 | 85 | 44 | 38 | 45 | 0 | 10 | 0 | 0 | 0 | 280 | 335 | 213 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 42 | 0 | 0 | 32 | 12 | 96 | 29 | 0 | 0 | 0 | 40 | 58 | 53 | 43 | 120 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 183 | 0 | 0 | 106 | 0 | 94 | 0 | 22 | 17 | 107 | 327 | 97 | 74 | 51 | 0 | 52 | 35 | 92 | 97 | 73 | 25 | 380 | 70 | 0 | 162 | 62 | 0 | 17 | 0 | 102 | 35 | 240 | 145 | 0 | 407 | 9 | 796 | 0 | 0 | 0 |  | 924 | 0 | 180 | 0 | 78 | 0 | 0 | 0 | 39 | 56 | 40 | 126 | 10 | 32 | 0 | 0 | 0 | 30 | 0 | 88 | 35 | 0 | 40 | 0 | 14 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 730 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 437 | 0 | 220 | 1082 | 0 | 0 |  | 8643 | 5646 | 14289 | 3879 | 924 | 1660 | 0 | 2897 | 3967 | 100 | 0 | 757 | 96 | 0 | 9 | 44 | 81.57
19:30 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 356 | 0 |  | 0 | 380 | 136 | 25 | 66 | 55 | 320 | 0 | 0 | 25 | 90 | 149 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 21 | 33 | 6 | 8 | 0 | 60 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 12 | 57 | 85 | 68 | 38 | 45 | 0 | 12 | 0 | 0 | 0 | 280 | 270 | 218 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 0 | 0 | 32 | 12 | 92 | 31 | 0 | 0 | 0 | 40 | 58 | 53 | 43 | 163 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 265 | 16 | 5 | 0 | 243 | 0 | 0 | 106 | 0 | 131 | 0 | 22 | 17 | 66 | 387 | 87 | 88 | 51 | 0 | 52 | 35 | 92 | 97 | 73 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 0 | 0 | 105 | 35 | 260 | 145 | 0 | 480 | 7 | 792 | 0 | 0 | 0 |  | 905 | 0 | 200 | 0 | 78 | 0 | 0 | 0 | 49 | 56 | 40 | 126 | 8 | 32 | 0 | 0 | 0 | 30 | 0 | 88 | 35 | 0 | 42 | 0 | 30 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 1000 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 509 | 0 | 250 | 1190 | 0 | 0 |  | 8760 | 6177 | 14937 | 3871 | 905 | 1643 | 0 | 3027 | 4515 | 100 | 0 | 777 | 92 | 0 | 7 | 136.565 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 359 | 0 |  | 0 | 370 | 150 | 25 | 66 | 55 | 320 | 0 | 0 | 25 | 90 | 149 | 20 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 60 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 12 | 60 | 85 | 68 | 38 | 45 | 0 | 19 | 0 | 0 | 0 | 280 | 270 | 218 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 0 | 0 | 32 | 12 | 94 | 31 | 0 | 0 | 0 | 40 | 58 | 53 | 43 | 163 | 0 | 40 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 145 | 0 | 0 | 107 | 0 | 133 | 0 | 22 | 17 | 76 | 389 | 89 | 88 | 51 | 0 | 52 | 35 | 92 | 97 | 75 | 25 | 345 | 70 | 0 | 108 | 72 | 0 | 0 | 0 | 105 | 35 | 260 | 163 | 0 | 474 | 5 | 797 | 0 | 0 | 0 |  | 782 | 0 | 195 | 0 | 84 | 0 | 0 | 0 | 41 | 67 | 8 | 126 | 8 | 32 | 0 | 0 | 0 | 30 | 0 | 88 | 14 | 0 | 48 | 0 | 30 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 1040 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 502 | 0 | 268 | 1235 | 0 | 0 |  | 8668 | 6110 | 14778 | 3874 | 782 | 1679 | 0 | 2827 | 4610 | 100 | 0 | 807 | 94 | 0 | 5 | 154.71 | 81.57
21:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 347 | 0 |  | 0 | 350 | 153 | 15 | 66 | 55 | 320 | 0 | 0 | 14 | 24 | 125 | 13 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 13 | 21 | 33 | 10 | 8 | 0 | 60 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 12 | 66 | 85 | 35 | 38 | 45 | 0 | 15 | 0 | 0 | 0 | 280 | 315 | 211 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 0 | 0 | 32 | 12 | 92 | 31 | 0 | 0 | 0 | 42 | 58 | 53 | 43 | 163 | 0 | 58 | 0 | 0 | 211 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 107 | 0 | 133 | 0 | 22 | 17 | 6 | 399 | 99 | 88 | 51 | 0 | 51 | 17 | 92 | 97 | 75 | 25 | 381 | 67 | 0 | 108 | 72 | 0 | 6 | 0 | 108 | 35 | 280 | 163 | 0 | 492 | 11 | 798 | 0 | 0 | 0 |  | 781 | 0 | 200 | 0 | 47 | 0 | 0 | 0 | 41 | 53 | 8 | 126 | 10 | 16 | 0 | 0 | 0 | 30 | 0 | 90 | 14 | 0 | 45 | 0 | 30 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 70 | 0 | 107 | 0 | 0 | 35 | 1190 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 541 | 0 | 307 | 1418 | 0 | 0 |  | 8420 | 6338 | 14758 | 3993 | 781 | 1670 | 0 | 2297 | 5040 | 100 | 0 | 774 | 92 | 0 | 11 | 183 | 81.57
22:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 340 | 0 |  | 0 | 350 | 144 | 8 | 66 | 45 | 323 | 0 | 0 | 8 | 24 | 133 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 14 | 21 | 33 | 10 | 8 | 0 | 60 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 12 | 66 | 85 | 35 | 37 | 45 | 0 | 28 | 0 | 0 | 0 | 280 | 270 | 220 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 0 | 0 | 32 | 12 | 92 | 33 | 0 | 0 | 0 | 42 | 58 | 53 | 43 | 163 | 0 | 55 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 15 | 0 | 0 | 107 | 0 | 133 | 0 | 22 | 17 | 6 | 400 | 99 | 88 | 51 | 0 | 51 | 17 | 92 | 97 | 75 | 25 | 345 | 67 | 0 | 108 | 72 | 0 | 17 | 0 | 115 | 35 | 280 | 163 | 0 | 492 | 11 | 797 | 0 | 0 | 0 |  | 781 | 0 | 205 | 0 | 47 | 0 | 0 | 0 | 40 | 53 | 8 | 126 | 10 | 16 | 0 | 0 | 0 | 31 | 0 | 90 | 14 | 0 | 45 | 0 | 30 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 70 | 0 | 107 | 0 | 0 | 35 | 1160 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 544 | 0 | 307 | 1412 | 0 | 0 |  | 8337 | 6311 | 14648 | 3922 | 781 | 1674 | 0 | 2279 | 5007 | 100 | 0 | 782 | 92 | 0 | 11 | 240.66 | 81.57
23:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 333 | 0 |  | 0 | 350 | 153 | 9 | 45 | 30 | 325 | 0 | 0 | 8 | 42 | 133 | 0 | 0 | 0 | 0 | 21 | 55 | 35 | 0 | 14 | 21 | 33 | 10 | 8 | 0 | 55 | 40 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 66 | 85 | 35 | 39 | 45 | 0 | 28 | 0 | 0 | 0 | 280 | 285 | 211 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 94 | 33 | 0 | 0 | 0 | 42 | 58 | 53 | 43 | 163 | 0 | 55 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 18 | 0 | 0 | 107 | 0 | 79 | 0 | 22 | 17 | 13 | 402 | 99 | 88 | 17 | 0 | 52 | 19 | 92 | 97 | 75 | 25 | 355 | 68 | 0 | 162 | 72 | 0 | 17 | 0 | 91 | 35 | 280 | 17 | 0 | 492 | 7 | 861 | 0 | 0 | 0 |  | 782 | 0 | 220 | 0 | 47 | 0 | 0 | 0 | 0 | 53 | 8 | 130 | 9 | 16 | 0 | 0 | 0 | 31 | 0 | 90 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 40 | 0 | 107 | 0 | 0 | 70 | 1040 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 541 | 0 | 307 | 1429 | 0 | 0 |  | 8182 | 6269 | 14451 | 3954 | 782 | 1766 | 0 | 2193 | 4965 | 95 | 0 | 595 | 94 | 0 | 7 | 352.395 | 81.57
24:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 363 | 0 |  | 0 | 370 | 155 | 8 | 66 | 30 | 328 | 0 | 0 | 8 | 91 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 14 | 21 | 25 | 10 | 0 | 0 | 55 | 40 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 12 | 65 | 85 | 35 | 37 | 6 | 0 | 33 | 0 | 0 | 0 | 280 | 270 | 218 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 92 | 32 | 0 | 0 | 0 | 42 | 58 | 53 | 43 | 163 | 0 | 59 | 0 | 0 | 210 | 0 | 0 | 0 | 310 | 16 | 5 | 0 | 72 | 0 | 0 | 107 | 0 | 41 | 0 | 22 | 17 | 12 | 402 | 89 | 35 | 17 | 0 | 52 | 35 | 110 | 97 | 75 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 17 | 0 | 67 | 35 | 230 | 17 | 0 | 490 | 4 | 858 | 0 | 0 | 0 |  | 782 | 0 | 215 | 0 | 48 | 0 | 0 | 0 | 0 | 53 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 31 | 0 | 90 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 70 | 0 | 107 | 0 | 0 | 70 | 1040 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 543 | 0 | 307 | 1413 | 0 | 0 |  | 8107 | 6282 | 14389 | 3910 | 782 | 1814 | 0 | 2203 | 4946 | 95 | 0 | 543 | 92 | 0 | 4 | 344.755 | 81.57
KWH | 0 | 0 | 0 | 4221000 | 0 | 0 | 0 | 9007200 | 0 |  | 0 | 8536500 | 3506036 | 390720 | 1441388 | 811768 | 7560940 | 0 | 0 | 316800 | 587664 | 1336800 | 62429 | 0 | 0 | 0 | 879480 | 664812 | 607401 | 0 | 288600 | 482760 | 575800 | 338400 | 137280 | 0 | 1320944 | 940000 | 0 | 0 | 98528 | 5252391 | 0 | 0 | 0 |  | 186960 | 1408656 | 1410636 | 1057440 | 807360 | 643200 | 0 | 262080 | 0 | 0 | 0 | 7237500 | 6476000 | 4994000 | 0 | 1183060 | 132768 | 0 | 0 | 995712 | 0 | 937792 | 891490 | 0 | 0 | 626700 | 256900 | 1969920 | 771840 | 0 | 0 | 10450 | 985000 | 1383240 | 1106400 | 932904 | 3880309 | 0 | 1385472 | 0 | 0 | 5243490 | 0 | 0 | 0 | 7181500 | 380688 | 168576 | 0 | 3058582 | 0 | 0 | 2042400 | 0 | 1953072 | 96255 | 528000 | 424800 | 1868436 | 8955000 | 1804800 | 1112640 | 907454 | 16563 | 1249527 | 633365 | 2043227 | 1406760 | 1181040 | 591360 | 8151500 | 1202880 | 199340 | 2950560 | 1124073 | 0 | 202320 | 176600 | 1992960 | 749880 | 5993800 | 1142472 | 0 | 11438180 | 307200 | 12138181 | 0 | 0 | 291055 |  | 21303272 | 0 | 4764960 | 0 | 1146240 | 0 | 0 | 0 | 271200 | 432768 | 495750 | 2817000 | 189938 | 686688 | 0 | 0 | 0 | 376770 | 0 | 776768 | 179590 | 0 | 352100 | 0 | 259906 | 0 | 0 | 0 | 1886836 | 0 | 5583000 | 0 | 0 | 3848173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8520872 | 1825440 | 0 | 1096992 | 0 | 1095974 | 0 | 44123 | 949536 | 27217700 | 5255291 | 0 | 0 | 23520 | 541440 | 1670784 | 0 | 0 | 14094549 | 166464 | 6763600 | 30049091 | 1010060 | 0 |  | 182207966 | 145696395 | 327904361 | 93482758 | 21303272 | 40367542 | 0 | 47759850 | 109171137 | 2260944 | 0 | 8705868 | 1969920 | 2575870 | 307200 | 0
Fuel Cost | 0 | 0 | 0 | 18783450 | 0 | 0 | 0 | 25940736 | 0 |  | 0 | 27146070 | 11990643.12 | 7720627.2 | 26953955.6 | 14303352.16 | 23060867 | 0 | 0 | 6259968 | 10548568.8 | 25960656 | 1164300.85 | 0 | 0 | 0 | 16059304.8 | 10477437.12 | 11109364.29 | 0 | 216450 | 0 | 0 | 0 | 2458684.8 | 0 | 0 | 0 | 0 | 0 | 1866120.32 | 16755127.29 | 0 | 0 | 0 |  | 3288626.4 | 24806432.16 | 25264490.76 | 20154806.4 | 15800035.2 | 10587072 | 0 | 0 | 0 | 0 | 0 | 20192625 | 19816560 | 16580080 | 0 | 3821283.8 | 447428.16 | 0 | 0 | 3992805.12 | 0 | 16795854.72 | 16100309.4 | 0 | 0 | 2331324 | 192675 | 12922675.2 | 2400422.4 | 0 | 0 | 0 | 3841500 | 5159485.2 | 5034120 | 4244713.2 | 13270656.78 | 0 | 7689369.6 | 0 | 0 | 14629337.1 | 0 | 0 | 0 | 22190835 | 285516 | 128117.76 | 0 | 62395072.8 | 0 | 0 | 39234504 | 0 | 34393597.92 | 0 | 9403680 | 7370280 | 30978668.88 | 23730750 | 34399488 | 20873126.4 | 16279724.76 | 0 | 20429766.45 | 12312615.6 | 36655492.38 | 26883183.6 | 22923986.4 | 10532121.6 | 21682990 | 20533161.6 | 0 | 53965742.4 | 18861944.94 | 0 | 3615458.4 | 0 | 35913139.2 | 12702967.2 | 17801586 | 16086005.76 | 0 | 79724114.6 | 0 | 71615267.9 | 0 | 0 | 0 |  | 59862194.32 | 0 | 14056632 | 0 | 19887264 | 0 | 0 | 0 | 5101272 | 8140366.08 | 8824350 | 8901720 | 900306.12 | 11838501.12 | 0 | 0 | 0 | 6747950.7 | 0 | 13057470.08 | 3821675.2 | 0 | 6306111 | 0 | 4654916.46 | 0 | 0 | 0 | 20811801.08 | 0 | 47120520 | 0 | 0 | 12698970.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24880946.24 | 31178515.2 | 0 | 21742381.44 | 0 | 21831802.08 | 0 | 0 | 18838794.24 | 176370696 | 16343955.01 | 0 | 0 | 0 | 0 | 28988102.4 | 0 | 0 | 102890207.7 | 0 | 50388820 | 198624491.51 | 0 | 0 |  | 1312043276.5 | 944810732.88 | 2256854009.38 | 281145003.21 | 59862194.32 | 129995050.59 | 0 | 872461641.55 | 747545918.79 | 0 | 0 | 152921525.72 | 12922675.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 376 | 0 |  | 0 | 390 | 153 | 16 | 66 | 30 | 315 | 0 | 0 | 17 | 25 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 14 | 22 | 33 | 12 | 8 | 0 | 55 | 37 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 55 | 68 | 68 | 38 | 46 | 0 | 0 | 0 | 0 | 0 | 305 | 290 | 218 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 29 | 33 | 0 | 0 | 0 | 12 | 84 | 28 | 0 | 0 | 2 | 40 | 58 | 40 | 43 | 163 | 0 | 59 | 0 | 0 | 210 | 0 | 0 | 0 | 305 | 16 | 8 | 0 | 153 | 0 | 0 | 78 | 0 | 113 | 16 | 22 | 17 | 85 | 402 | 69 | 52 | 51 | 1 | 51 | 35 | 84 | 52 | 37 | 25 | 340 | 51 | 42 | 162 | 0 | 0 | 0 | 32 | 49 | 35 | 230 | 54 | 0 | 473 | 2 | 436 | 0 | 0 | 40 |  | 921 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 230 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 90 | 0 | 0 | 0 | 10 | 0 | 7 | 0 | 1050 | 220 | 0 | 0 | 0 | 64 | 35 | 0 | 0 | 565 | 34 | 280 | 1214 | 187 | 0 |  | 13555 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 356 | 0 |  | 0 | 380 | 136 | 25 | 66 | 55 | 320 | 0 | 0 | 25 | 90 | 149 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 21 | 33 | 6 | 8 | 0 | 60 | 40 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 0 | 12 | 57 | 85 | 68 | 38 | 45 | 0 | 12 | 0 | 0 | 0 | 280 | 270 | 218 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 0 | 0 | 32 | 12 | 92 | 31 | 0 | 0 | 0 | 40 | 58 | 53 | 43 | 163 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 265 | 16 | 5 | 0 | 243 | 0 | 0 | 106 | 0 | 131 | 0 | 22 | 17 | 66 | 387 | 87 | 88 | 51 | 0 | 52 | 35 | 92 | 97 | 73 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 0 | 0 | 105 | 35 | 260 | 145 | 0 | 480 | 7 | 792 | 0 | 0 | 0 |  | 905 | 0 | 200 | 0 | 78 | 0 | 0 | 0 | 49 | 56 | 40 | 126 | 8 | 32 | 0 | 0 | 0 | 30 | 0 | 88 | 35 | 0 | 42 | 0 | 30 | 0 | 0 | 0 | 64 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 90 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 1000 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 509 | 0 | 250 | 1190 | 0 | 0 |  | 14937 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 350 | 0 |  | 0 | 380 | 150 | 25 | 66 | 55 | 320 | 0 | 0 | 25 | 90 | 150 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 21 | 33 | 12 | 8 | 0 | 55 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 70 | 85 | 68 | 38 | 45 | 0 | 20 | 0 | 0 | 0 | 280 | 280 | 220 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 46 | 42 | 0 | 0 | 32 | 12 | 151 | 40 | 0 | 0 | 0 | 40 | 58 | 53 | 43 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 260 | 0 | 0 | 107 | 0 | 132 | 0 | 25 | 17 | 100 | 400 | 98 | 88 | 51 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 360 | 70 | 0 | 162 | 72 | 0 | 17 | 0 | 115 | 35 | 260 | 163 | 0 | 490 | 40 | 900 | 0 | 0 |  |  | 795 | 0 | 210 | 0 | 80 | 0 | 0 | 0 | 50 | 66 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 30 | 25 | 90 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 500 | 0 | 307 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 380 | 150 | 25 | 60 | 30 | 320 | 0 | 0 | 17 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 12 | 21 | 24 | 12 | 8 | 0 | 55 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 55 | 51 | 40 | 30 | 6 | 0 | 10 | 0 | 0 |  | 280 | 280 | 200 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 45 | 42 | 0 | 0 | 32 | 12 | 146 | 30 | 0 | 0 | 1.6 | 40 | 58 | 53 | 40 | 163 | 0 | 56 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 16 | 8 | 0 | 150 | 0 | 0 | 65 | 0 | 115 | 20 | 25 | 17 | 70 | 350 | 80 | 17 | 17 | 5 | 52 | 35 | 85 | 17 | 46 | 24 | 350 | 50 | 50 | 162 | 35 | 0 | 17 | 35 | 104 | 17 | 230 | 54 | 0 | 450 | 40 | 850 | 0 | 0 | 70 |  | 940 | 0 | 205 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 16 | 0 | 0 | 0 | 30 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 53 | 0 | 94 | 0 | 70 | 0 | 8 | 113 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 450 | 30 | 307 | 1200 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 350 | 153 | 33 | 1 | 15 | 280 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 25 | 12 | 8 | 0 | 55 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 6 | 63 | 51 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 305 | 219 | 0 | 50 | 15 | 0 | 0 | 43 | 0 | 44 | 42 | 0 | 0 | 32 | 12 | 80 | 29 | 0 | 0 | 1 | 42 | 58 | 50 | 43 | 120 | 0 | 61 | 0 | 0 | 211 | 0 | 0 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 78 | 0 | 34 | 9 | 22 | 17 | 0 | 327 | 70 | 17 | 17 | 3 | 51 | 0 | 110 | 17 | 37 | 25 | 340 | 51 | 7 | 0 | 35 | 0 | 0 | 12 | 90 | 17 | 230 | 0 | 0 | 492 | 0 | 863 | 0 | 0 | 35 | 0 | 926 | 0 | 210 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 24 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 35 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 910 | 180 | 0 | 0 | 1 | 40 | 35 | 0 | 0 | 401 | 13 | 250 | 1125 | 48 | 0 | 0 |  |  |  | 133850300 | 21303272 | 0 | 109171137 | 56465718 | 1969920 | 2575870 | 307200 | 2260944 |  |  | 327904361
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [14 empty] | 299772 | [10 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 133.8503 | 21.3033 | 0 | 109.1711 | 56.4657 | 1.9699 | 2.5759 | 0.3072 | 2.2609
| Minimum Generation |  | 11768 | 8:00
| Highest Generation |  | 14937 | 19:30 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 327.9044
| Day Peak Generation |  | 13555 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 14937 | 19:30 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 924 | 10:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 905 | 19:30
| Load factor L.F |  | 91.47% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-05
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13555 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12071
Evening Peak Generation : |  |  | 14937 | MW Hour : | 19:30 | Available Max Generation : |  | 15985
E.P. Demand (at gen end) : |  |  | 15080 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 15900
Maximum Generation : |  |  | 14937 | MW Hour : | 19:30 | Reserve(Generation end) |  | 85
Total Gen. (MKWH) : |  |  | 327.9044 | System Load Factor : | 91.47% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 550 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-05
Actual : |  | 81.57 | Ft.(MSL) , | Rule curve : | 77.04 | Ft.( MSL )
Gas Consumed : |  | Total = | 985.86 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 411140053.8
: |  |  | Coal : | 747545918.79 | Oil : | 1025383167.27 | Total : | 2184069139.86
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 40 | 960:00 | 5504.1317 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1518.068 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2128.2186 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1851.3752 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1522.5519 |  |  | 0 | 0%
Mymensingh Area |  | 97 | 2328:00 | 1133.2325 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 634.316 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 529.4448 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 1035.4822 |  |  | 0 | 0%
Total |  | 137 |  | 15856.8209 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:19 |  | Niamatpur 132/33kV S/S Transformer-1(407T) LT Scheduled S/D Due to 132 kV Bus Bar scheme Change
08:19 |  | Niamatpur 132/33kV S/S Transformer-1(407T) HT Scheduled S/D Due to 132 kV Bus Bar scheme Change
| 10:07 | Aminbazar-Keraniganj 230kV Ckt-1 is restored.
| 11:12 | Goalpara 132/33kV S/S T-5 HT is restored.
| 11:14 | Goalpara 132/33kV S/S T-5 LT is restored.
| 11:16 | Goalpara 132/33kV S/S T-6 HT is restored.
| 11:18 | Goalpara 132/33kV S/S T-6 LT is restored.
11:26 | 12:16 | Khulna (C) S/S Auxiliary Transformer HT Forced S/D Due to Cable maintenance
11:26 | 12:16 | Khulna (C) S/S Auxiliary Transformer LT Forced S/D Due to Cable maintenance
12:00 |  | Day Peak Generation: 13555 MW.
| 12:27 | Chandpur 132/33kV S/S Bus A is restored.
12:32 | 13:30 | Jaldhaka 132/33kV S/S 416T-2 LT Tripped showing O/C Y phase relays Due to 33kv Feeder fault PBS Jaldhaka and Dommer. |  |  |  |  | 21.0MW load interruption.
12:32 | 13:53 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing O/C Y phase relays Due to 33kv Feeder fault PBS Jaldhaka and Dommer.
14:17 | 14:41 | Magura 132/33kV S/S T-2 (415T) HT Project Work S/D Due to Power flow direction change at 33kV CRP panel.
14:41 | 19:09 | Kaliakoir-Tongi 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Emergency Maintenance.
14:43 | 17:11 | Fenchuganj 230/132/33kV S/S TR-02 HT Project Work S/D Due to G2G Project Work.
14:53 | 17:50 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to 33kv Tr_1 Shutdown due to 33kv BUS D/S post Insulator change By PBS |  |  |  |  | 15.0MW load interruption.
14:53 | 17:50 | Jaldhaka 132/33kV S/S 416T-2 LT Forced S/D Due to 33kv Tr_2 Shutdown due to 33kv BUS D/S post Insulator change By PBS |  |  |  |  | 30.0MW load interruption.
15:03 | 16:33 | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to G2G project works
| 15:25 | Sonargaon 132/33kV S/S BUS B is restored.
16:32 | 16:59 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Z-1, BN relays Due to Rainfall.
18:54 | 19:01 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance protection relay, R phase, |  |  |  |  | 29.0MW load interruption.
distance 34.1km. relays Due to None
19:13 | 00:33 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance protection relay, R phase,
distance 27.5km. relays.
19:30 |  | Evening Peak Gen. 14938 MW
00:57 | 01:29 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to Shutdown taken by DPBS-1 due to red hot maintenance at 33 |  |  |  |  | 50.0MW load interruption.
kV DEPZ feeder's bus DS (B phase) load side.
06:00 |  | Minimum Generation = 12,111MW
06:34 |  | Dohazari-Sikalbaha 132 kV Ckt-1 Project Work S/D from Dohazari 132/33kV end Due to patiya LILO work
06:53 |  | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D
06:59 |  | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end Due to New Tower Conducting by Project.CB
open:- 06:59 Line Isolator Open:- 07:11 Earth switch Close:- 07:14
07:06 |  | Jashore 132/33kV S/S JH-1(L2) Forced S/D Due to Jhenaidah 230 kv T1-xformer overloaded due to T2-xformer shutdown.
07:09 |  | Jashore 132/33kV S/S JH-2(L1) Forced S/D Due to Jhenaidah 230 kv T1-xformer overloaded due to T2-xformer shutdown.
07:14 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-2 Forced S/D Due to As per order of ALDC
07:14 |  | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Forced S/D Due to As per order of ALDC
07:18 |  | Jhenaidah 230/132kV S/S Transformer- 2 LT Scheduled S/D Due to Emergency Maintenance
07:19 |  | Jhenaidah 230/132kV S/S Transformer- 2 HT Scheduled S/D Due to Emergency Maintenance

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4221000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 356 | 9007200 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8536500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 25 | 390720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 136 | 3506036 | GT-1 Under Maint
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 66 | 1441388 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 811768
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 22 | 62429 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 25 | 316800 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7560940 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 587664 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 879480
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1336800
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 664812
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 607401
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 771360 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 575800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 6 | 338400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 137280 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 243 | 3058582 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 1953072 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1112640 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1202880 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2950560
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 176600
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 749880 | Engine problem
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under maint.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5332 | 2777 | 52957992
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 98528 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 96255
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 643200 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 100 | 2260944 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5252391
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 907454 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 57 | 1408656 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1410636 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 68 | 1057440 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 22 | 528000 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 262080
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 807360 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 16563
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1249527 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 633365 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 2043227 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 591360 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 1124073 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 1142472
60 | SS Power I |  | SS Power | 2*612 | 1224 | 480 | 11438180
| Cox's Bazar Wind |  | IPP | 66 | 60 | 7 | 307200 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 792 | 12138181
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 291055
| Chattogram area Total |  |  |  | 4404 | 2417 | 45708147
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 4994000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7237500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6476000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 260 | 5993800 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 132768 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 995712 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 66 | 1868436 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 937792 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1183060 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 424800 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 92 | 1969920
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 626700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 891490 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 256900 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1406760 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 73 | 1181040 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 202320 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 105 | 1992960
| Cumilla Area Total |  |  |  | 2929 | 1704 | 38771958
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 31 | 771840 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10450
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 106 | 2042400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1804800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 199340
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 186960 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 236 | 5015790
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 985000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1383240 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3880309
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1106400
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 43 | 932904 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 168576 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 40 | 1385472
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 211 | 5243490
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 380688
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 7181500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 387 | 8955000
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8151500 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1626 | 39754079
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 21303272
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 78 | 1146240 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 49 | 271200 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 56 | 432768 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 4764960 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 40 | 495750
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1825440 | Engine problem
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 541440
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 509 | 14094549 | Unit -1 under maint.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1927 | 44875619
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 686688 | Low demand.
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 8 | 189938
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2817000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1000 | 27217700 | Amin Bazar Tx O/L.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5255291
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 6763600 | Amin Bazar Tx O/L.
| Barisal Area Total |  |  |  | 2235 | 1636 | 42930217
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 376770 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 179590
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 352100 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 140 | 3848173 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 320 | 8520872 | Gas shortage
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 259906 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 776768 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1096992
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 949536
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23520
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1190 | 30049091
| Rajshahi Area Total |  |  |  | 3431 | 2101 | 46433318
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 64 | 1886836
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5583000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 104 | 1095974
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 44123
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1670784
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 166464
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1010060
| Rangpur Area Total |  |  |  | 950 | 513 | 11457241
| Total |  |  |  | 25903 | 14937 | 327904361
| Eastern Grid Total |  |  |  | 15588 | 8760 | 182207966
| Western Grid Total |  |  |  | 10315 | 6177 | 145696395
| National Grid Total |  |  |  | 25903 | 14937 | 327904361
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-06-04
| (a) ENTIRE EASTERN GRID : |  | 9724.66 | MW | (b) ENTIRE WESTERN GRID : |  | 4745.5 | MW
| i) Dhaka area |  | 5217.26 | MW | i) Khulna area |  | 1790 | MW
| ii) Chittagong area |  | 1544.4 | MW | ii) Rajshahi area |  | 1573.8 | MW
| iii) Comilla area |  | 1376 | MW | iii) Barisal area |  | 427.7 | MW
| iv) Mymensingh area |  | 1090 | MW | iv) Rangpur area |  | 954 | MW
| v) Sylhet area |  | 497 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 14470.16 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 26 | 23:00 | Kalurghat | 40 | 10:00 | Narail | 63 | 20:00 | Shariatpur | 85 | 19:30
2 | AKSML | 111 | 09:00 | Chowmuhani | 231 | 20:00 | Kamrangirchar | 56 | 12:00 | Narinda | 49.5 | 13:00 | Sherpur | 132 | 20:00
3 | Aftabnagar | 44 | 15:00 | Chuadanga | 122 | 00:00 | Kaptai | N/A | N/A | Narshingdi | 162 | 22:00 | Shikalbaha | 37 | 18:30
4 | Agargaon | 121 | 13:00 | Coxsbazar | 139 | 19:30 | Kazla | 105 | 12:00 | Natore | 164 | 00:00 | Shikalbaha-230 | N/A | N/A
5 | Agrabad | 102 | 17:00 | Cumilla(N) | 190 | 22:00 | Keranigonj | 81 | 17:00 | Nawabganj | 48.9 | 00:00 | Shitalakhya | 116.6 | 15:00
6 | Amnura | 73 | 22:00 | Cumilla(S) | 188 | 23:00 | Khagrachori | 32 | 19:30 | Netrakona | 114 | 19:00 | Sholosohor | 46 | 09:00
7 | Ashuganj | 81 | 23:00 | Daudkandi | 148 | 02:00 | Khulna | 94 | 13:00 | New | 60.6 | 12:00 | Shyampur | 176 | 10:00
8 | BIPTC | N/A | N/A | Dhaka | 54 | 13:00 | Khulshi | 185 | 16:00 | Niamatpur | 82 | 01:00 | Siddhirganj | 120 | 00:00
9 | BSRM | 195 | 09:00 | Dhamrai | 136 | 17:00 | Kishoreganj | 142 | 19:30 | Noapara | 56 | 20:00 | Sirajganj | 148 | 20:00
10 | Bagerhat | 93 | 23:00 | Dhanmondi | 173 | 13:00 | Kodda | 288 | 18:00 | PHP | 10 | 15:00 | Sonargaon | 101 | 02:00
11 | Bakulia | 100 | 19:30 | Dohazari | 106 | 19:00 | Kulaura | 40 | 19:30 | Pabna | 127 | 00:00 | Sreemongol | 55 | 20:00
12 | Banani | 51 | 13:00 | Faridpur | 169 | 00:00 | Kurigram | 62 | 20:00 | Palashbari | 116 | 20:00 | Sreepur | 66 | 09:00
13 | Bangabhaban | 23 | 10:00 | Fatullah | 71 | 15:00 | Kushtia | 162 | 19:30 | Panchagarh | 57 | 19:00 | Srinagar | 45.58 | 00:00
14 | Barapukuria | 64 | 19:30 | Fenchuganj | 34 | 19:30 | Lalbag | 104 | 12:00 | Patuakhali | 86.5 | 22:00 | Sunamganj | 46 | 03:00
15 | Barguna | 22 | 22:00 | Feni | 117 | 23:00 | Lalmonirhat | 58 | 19:30 | Payra | 24 | 00:00 | Sylhet | 36 | 19:30
16 | Barishal | 114 | 21:00 | GPH | 101 | 05:00 | MI_Cement | 10.1 | 09:00 | Postogola | 64 | 16:00 | Sylhet-132 | 99 | 19:00
17 | Barishal-230 | 90 | 19:30 | Ghatail | 50 | 19:30 | Madanganj | 27 | 00:00 | Purbachal | 21 | 00:00 | TK | 33.8 | 20:00
18 | Baroaulia | 76 | 12:00 | Ghorashal | 43 | 19:00 | Madaripur | 111 | 00:00 | Purbasadipur | 134 | 19:30 | Tangail | 180 | 19:00
19 | Baroirhat | 76 | 19:00 | Goalpara | 38 | 00:00 | Madartek | 99.08 | 23:00 | Rahim | 52 | 00:00 | Thakurgaon | 99 | 22:00
20 | Bashundhara | 214 | 13:00 | Gollamari | 94 | 13:00 | Madunaghat | 58 | 19:00 | Rajbari | 76 | 00:00 | Tongi | 142 | 12:00
21 | BashundharaCement | 6 | 01:00 | Gopalganj | 114 | 19:30 | Magura | 68 | 19:00 | Rajendrapur | 114 | 21:00 | Ullahpara | 44 | 21:00
22 | Beanibazar | 58 | 19:00 | Gulshan | 144 | 13:00 | Mahasthangarh | 84 | 00:00 | Rajshahi | 149 | 19:30 | Ullon | 65 | 00:00
23 | Benapole | 80 | 19:00 | Halishahar | 93.5 | 10:00 | Manikganj | 129 | 12:00 | Rajshahi-230 | 83 | 00:00 | Uttara | 80 | 15:00
24 | Bhaluka | 144 | 09:00 | HaripurSBU | 191 | 11:00 | Maniknagar | 92 | 13:00 | Ramganj | 120 | 19:30 | UttaraNew | 33 | 00:00
25 | Bhandaria | 44 | 21:00 | Hasnabad | 96 | 00:00 | Matarbari | 49 | 20:00 | Rampur | 30 | 00:00 | Zigatola | 98 | 15:00
26 | Bhangura | 38 | 00:00 | Hathazari | 81 | 20:00 | Matuail | 80 | 15:00 | Rangamati | 18 | 19:00
27 | Bheramara(GK) | 75 | 19:30 | Ishurdi | 87 | 19:30 | Millgate | 138 | 14:00 | Rangpur | 152 | 19:30
28 | Bhulta | 250 | 19:30 | Jaldhaka | 72 | 20:00 | Mirpur | 160 | 15:00 | Ruppur | 6.6 | 12:00
29 | Bog-Sherpur | 68 | 00:00 | Jamalpur | 114 | 19:30 | Mirsorai | 3 | 13:00 | SSM | 15 | 00:00
30 | Bogura | 193 | 20:00 | Jashore | 157 | 23:00 | Mirzapur | 40 | 10:00 | Saidpur | 116 | 20:00
31 | Borhanuddin | 86 | 23:00 | Jhenaidah | 148 | 19:30 | Mithapukur | 56 | 20:00 | Satkhira | 146 | 22:00
32 | Brahmanbaria | 175 | 22:00 | Joydebpur | 207 | 22:00 | Modern | 0 | 00:00 | Satmasjid | 126 | 16:00
33 | Cantonment | 166 | 15:00 | Joypurhat | 63 | 20:00 | Mogbazar | 152.7 | 15:00 | Savar | 218 | 15:00
34 | Chandpur | 72 | 23:00 | Juldah | 32 | 16:00 | Mongla | 41 | 17:00 | SevenRings | 8.09 | 08:00
35 | Chandraghona | 36 | 19:00 | KSRM | 45 | 00:00 | Motijheel | 52 | 16:00 | ShahCement | 30 | 10:00
36 | Chapai | 75 | 00:00 | Kabirpur | 293 | 21:00 | Munshiganj | 110 | 00:00 | Shahjadpur | 81 | 00:00
37 | Charsaidpur | 43 | 01:00 | Kachua | 81 | 22:00 | Mymensingh | 220 | 00:00 | Shahjibazar | 123 | 21:00
38 | Chauddagram | 76 | 00:00 | Kallyanpur | 120 | 13:00 | Naogaon | 166 | 00:00 | Shahmirpur | 53 | 23:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 381 | 18:30 | 361 | 16:00 | Kaliakoir | 367 | 18:30 | 345 | 15:00
| Ashuganj | 403.4 | 4:06 | 379.3 | 15:11 | Madunaghat_I | 418 | 17:00 | 413 | 00:00
| Bhulta | 396 | 04:00 | 371 | 15:00 | Meghnaghat | 374 | 18:00 | 352 | 15:00
| Bibiana | 397 | 19:30 | 384 | 15:00 | Payra | 410 | 18:00 | 399 | 15:00
| BIPTC | 403 | 21:00 | 389 | 15:00 | Rahanpur | 404 | 18:30 | 384 | 21:00
| Bogura | 400 | 18:30 | 376 | 21:00 | Rampal | 400 | 18:30 | 380 | 15:00
| Gopalganj | 396 | 18:00 | 374 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 04:00 | 210 | 15:00 | Hasnabad | 224 | 18:00 | 211 | 15:00
| AKSML | 231 | 18:30 | 219 | 04:00 | Hathazari | 230 | 18:30 | 222 | 23:00
| Aminbazar | 223 | 03:00 | 211 | 14:00 | Ishurdi | 236 | 17:00 | 225 | 13:00
| Ashuganj | 231 | 03:00 | 221 | 15:00 | Jhenaidah | 227 | 18:30 | 213 | 21:00
| Ashuganj-400 | 231 | 03:00 | 221 | 15:00 | Kaliakoir | 231 | 18:30 | 216 | 15:00
| Baghabari | 231 | 18:00 | 221 | 13:00 | Keranigonj | 225 | 18:30 | 209 | 15:00
| Barapukuria | 220 | 00:00 | 208 | 21:00 | Khulna(S) | 231 | 18:30 | 216 | 13:00
| Barapukuria-230 | 220 | 00:00 | 208 | 21:00 | Madunaghat_I | 231 | 19:00 | 225 | 05:00
| Barishal | 237 | 18:30 | 227 | 15:00 | Maniknagar | 223 | 02:00 | 210 | 15:00
| Bheramara | 235 | 17:00 | 224 | 13:00 | Meghnaghat | 230 | 00:00 | 219 | 16:00
| Bhulta | 226 | 02:00 | 210 | 15:00 | Meghnaghat-400 | 228 | 18:00 | 214 | 15:00
| Bibiana | 229 | 19:30 | 222 | 14:00 | Mirsorai | 231 | 19:00 | 218 | 04:00
| BIPTC | 236 | 17:00 | 222 | 13:00 | Rajshahi | 235 | 18:00 | 221 | 13:00
| Bogura | 226 | 18:30 | 212 | 21:00 | Rampal | 229 | 18:30 | 215 | 15:00
| Bogura-400 | 227 | 18:30 | 213 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 14:00 | 233 | 15:00 | Rampura | 225 | 04:00 | 207 | 15:00
| BSRM | 231 | 18:30 | 219 | 15:00 | Shikalbaha | 231 | 18:30 | 222 | 05:00
| Cumilla(N) | 227 | 18:30 | 214 | 15:00 | Shyampur | 226 | 18:30 | 211 | 15:00
| Fenchuganj | 235 | 19:30 | 227 | 13:00 | Siddhirganj | 224 | 04:00 | 21 | 10:00
| Ghorashal | 230 | 00:00 | 220 | 13:00 | Sirajgonj | 236 | 19:00 | 228 | 15:00
| Ghorashal-230 | 226 | 02:00 | 212 | 15:00 | Sreepur | 227 | 18:30 | 219 | 15:00
| GPH | 231 | 18:30 | 220 | 04:00 | Tongi | 228 | 04:00 | 210 | 15:00
| Haripur | 223 | 17:00 | 212 | 16:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 04:00 | 120 | 15:00 | Kushtia | 134 | 18:00 | 127 | 13:00
| Agargaon | 136 | 04:00 | 123 | 15:00 | Lalbag | 133 | 04:00 | 122 | 15:00
| Agrabad | 132 | 18:30 | 126 | 00:00 | Lalmonirhat | 133 | 00:00 | 118 | 21:00
| AKS | 128 | 18:00 | 125 | 00:00 | Madanganj | 132 | 17:00 | 122 | 15:00
| Aminbazar | 136 | 19:00 | 122 | 12:00 | Madaripur | 131 | 18:00 | 123 | 14:00
| Amnura | 139 | 18:30 | 120 | 21:00 | Madartek | 134 | 04:00 | 121 | 15:00
| Ashuganj | 136 | 07:00 | 126 | 18:30 | Madunaghat | 133 | 18:30 | 127 | 15:00
| Bagerhat | 136 | 18:00 | 123 | 21:00 | Magura | 137 | 18:30 | 126 | 21:00
| Bakulia | 133 | 18:30 | 127 | 00:00 | Mahasthangarh | 133 | 02:00 | 122 | 21:00
| Banani | 135 | 04:00 | 120 | 15:00 | Manikganj | 129 | 19:00 | 116 | 04:00
| Bangabhaban | 130 | 03:00 | 119 | 15:00 | Maniknagar | 130 | 02:00 | 119 | 15:00
| Barapukuria | 138 | 00:00 | 127 | 21:00 | Matarbari | 122 | 18:30 | 110 | 23:00
| Barguna | 135 | 18:00 | 124 | 00:00 | Matuail | 134.4 | 16:00 | 122.4 | 15:00
| Barishal | 136 | 03:00 | 121 | 00:00 | Millgate | 132 | 03:00 | 120 | 14:00
| Barishal-230 | 136 | 18:30 | 127 | 15:00 | Mirpur | 136 | 18:30 | 125 | 15:00
| Baroaulia | 134 | 18:30 | 128 | 01:00 | Mirzapur | 127 | 18:30 | 118 | 21:00
| Baroirhat | 129 | 18:30 | 118 | 15:00 | Mithapukur | 134 | 00:00 | 123 | 20:00
| Bashundhara | 134 | 03:00 | 118 | 15:00 | MI_Cement | 133 | 18:30 | 123 | 15:00
| BashundharaCement | 132 | 17:00 | 122 | 15:00 | Modern | 132 | 18:00 | 127 | 03:00
| Beanibazar | 130 | 06:00 | 125 | 21:00 | Mogbazar | 135 | 04:00 | 120 | 15:00
| Benapole | 135 | 18:30 | 121 | 21:00 | Mongla | 135 | 18:30 | 123 | 21:00
| Bhaluka | 129 | 18:30 | 121 | 15:00 | Motijheel | 130 | 03:00 | 119 | 15:00
| Bhandaria | 135 | 18:00 | 119 | 00:00 | Munshiganj | 131 | 17:00 | 123 | 15:00
| Bhangura | 136 | 18:30 | 129 | 13:00 | Mymensingh | 134 | 02:00 | 117 | 21:00
| Bheramara | 135 | 18:30 | 129 | 14:00 | Naogaon | 130 | 18:30 | 118 | 21:00
| Bheramara(GK) | 135 | 18:00 | 129 | 14:00 | Narail | 138 | 18:30 | 127 | 14:00
| Bhulta | 130 | 17:00 | 117 | 15:00 | Narinda | 130 | 02:00 | 119 | 15:00
| Bog-Sherpur | 132 | 17:00 | 124 | 21:00 | Narshingdi | 132 | 17:00 | 116 | 15:00
| Bogura | 135 | 18:30 | 125 | 21:00 | Natore | 134 | 18:00 | 125 | 21:00
| Bogura-230 | 135 | 18:30 | 124 | 21:00 | Nawabganj | 134 | 18:30 | 123 | 15:00
| Brahmanbaria | 128 | 18:30 | 121 | 23:00 | Netrakona | 134 | 18:30 | 124 | 07:00
| Cantonment | 135 | 03:00 | 123 | 15:00 | New | 131 | 01:00 | 120 | 15:00
| Chandpur | 127 | 18:30 | 115 | 15:00 | Niamatpur | 136 | 18:30 | 127 | 21:00
| Chandraghona | 133 | 18:00 | 128 | 03:00 | Noapara | 139 | 18:30 | 125 | 21:00
| Chapai | 133 | 18:30 | 124 | 00:00 | Pabna | 134 | 18:30 | 126 | 13:00
| Charsaidpur | 133 | 18:30 | 124 | 15:00 | Palashbari | 133 | 01:00 | 119 | 21:00
| Chauddagram | 128 | 18:30 | 116 | 15:00 | Panchagarh | 137 | 02:00 | 118 | 21:00
| Chhatak | 131 | 18:00 | 127 | 00:00 | Patuakhali | 132 | 18:00 | 127 | 00:00
| Chowmuhani | 123 | 18:00 | 112 | 13:00 | Payra | 135 | 18:00 | 130 | 00:00
| Chuadanga | 130 | 18:00 | 116 | 21:00 | PHP | 128 | 18:30 | 115 | 15:00
| Coxsbazar | 122 | 09:00 | 112 | 19:00 | Postogola | 133 | 18:00 | 124 | 14:00
| Cumilla(N) | 132 | 18:30 | 122 | 15:00 | Purbachal | 133 | 01:00 | 119 | 15:00
| Cumilla(S) | 132 | 05:00 | 120 | 15:00 | Purbasadipur | 136 | 00:00 | 118 | 21:00
| Daudkandi | 133 | 17:00 | 115 | 15:00 | Rahanpur | 137 | 18:30 | 129 | 21:00
| Dhaka | 133 | 03:00 | 120 | 15:00 | Rahim | 134 | 17:00 | 123 | 15:00
| Dhamrai | 135 | 03:00 | 123 | 15:00 | Rajbari | 131 | 18:30 | 122 | 14:00
| Dhanmondi | 134 | 03:00 | 123 | 15:00 | Rajendrapur | 128 | 19:30 | 115 | 07:00
| Dohazari | 130 | 18:30 | 122 | 00:00 | Rajshahi | 134 | 18:00 | 125 | 13:00
| Faridpur | 131 | 18:30 | 122 | 15:00 | Rajshahi-230 | 136 | 18:30 | 117 | 21:00
| Fatullah | 133 | 18:30 | 123 | 15:00 | Ramganj | 124 | 18:30 | 110 | 23:00
| Fenchuganj | 133 | 00:00 | 130 | 01:00 | Rampur | 130 | 18:00 | 125 | 15:00
| Feni | 126 | 18:30 | 115 | 15:00 | Rampura | 134 | 04:00 | 120 | 15:00
| Ghatail | 129 | 10:00 | 120 | 21:00 | Rangamati | 132 | 18:30 | 127 | 04:00
| Ghorashal | 134 | 03:00 | 128 | 13:00 | Rangpur | 137 | 01:00 | 119 | 21:00
| Goalpara | 139 | 05:00 | 126 | 21:00 | Ruppur | 134 | 01:00 | 128 | 15:00
| Gollamari | 138 | 18:30 | 128 | 13:00 | Saidpur | 136 | 01:00 | 120 | 21:00
| Gopalganj | 133 | 18:30 | 122 | 15:00 | Satkhira | 136 | 18:00 | 121 | 23:00
| Gopalganj-400 | 130 | 18:30 | 122 | 15:00 | Satmasjid | 135 | 03:00 | 123 | 15:00
| Gulshan | 133 | 02:00 | 120 | 15:00 | Savar | 136 | 18:30 | 125 | 15:00
| Halishahar | 133 | 18:30 | 126 | 00:00 | SevenRings | 135 | 01:00 | 127 | 15:00
| Haripur | 134 | 17:00 | 123 | 15:00 | ShahCement | 133 | 18:30 | 124 | 15:00
| HaripurSBU | 134 | 17:00 | 123 | 15:00 | Shahjadpur | 138 | 18:00 | 132 | 13:00
| Hasnabad | 135 | 18:30 | 126 | 12:00 | Shahjibazar | 127 | 07:00 | 122 | 21:00
| Hathazari | 136 | 18:30 | 130 | 00:00 | Shahmirpur | 133 | 18:30 | 127 | 04:00
| Ishurdi | 137 | 18:00 | 130 | 14:00 | Shariatpur | 130 | 18:30 | 121 | 14:00
| Jaldhaka | 136 | 02:00 | 119 | 21:00 | Sherpur | 138 | 02:00 | 124 | 19:00
| Jamalpur | 139 | 09:00 | 127 | 19:00 | Shikalbaha | 122 | 18:00 | 115 | 23:00
| Jashore | 136 | 18:00 | 123 | 21:00 | Shikalbaha-230 | 134 | 18:30 | 128 | 00:00
| Jhenaidah | 138 | 18:30 | 127 | 21:00 | Shitalakhya | 133 | 18:30 | 123 | 15:00
| Jhenaidah-230 | 138 | 18:00 | 129 | 21:00 | Sholosohor | 131 | 18:30 | 126 | 16:00
| Joydebpur | 129 | 01:00 | 121 | 16:00 | Shyampur | 131 | 18:30 | 30 | 20:00
| Joypurhat | 128 | 07:00 | 115 | 21:00 | Shyampur-230 | 132 | 18:30 | 122 | 15:00
| Juldah | 134 | 18:30 | 128 | 03:00 | Siddhirganj | 134 | 17:00 | 123 | 15:00
| Kabirpur | 130 | 20:00 | 118 | 15:00 | Sirajganj | 131 | 18:00 | 123 | 21:00
| Kachua | 128 | 18:30 | 116 | 15:00 | Sonargaon | 135 | 17:00 | 123 | 12:00
| Kaliakoir | 137 | 18:30 | 121 | 07:00 | Sreemongol | 128 | 07:00 | 124 | 21:00
| Kallyanpur | 128 | 02:00 | 119 | 15:00 | Sreepur | 131 | 02:00 | 126 | 15:00
| Kalurghat | 132 | 18:30 | 127 | 04:00 | Srinagar | 133 | 19:30 | 122 | 15:00
| Kamrangirchar | 134 | 18:30 | 118 | 15:00 | SSM | 138 | 18:30 | 130 | 00:00
| Kaptai | 134 | 10:00 | 131 | 15:00 | Sunamganj | 130 | 06:00 | 125 | 23:00
| Kazla | 130 | 04:00 | 119 | 16:00 | Sylhet | 130 | 05:00 | 128 | 04:00
| Keranigonj | 134 | 19:30 | 124 | 15:00 | Sylhet-132 | 131 | 08:00 | 129 | 00:00
| Khagrachori | 132 | 18:30 | 126 | 04:00 | Tangail | 128 | 10:00 | 118 | 16:00
| Khulna | 139 | 18:30 | 127 | 21:00 | Thakurgaon | 139 | 01:00 | 120 | 10:00
| Khulna(S) | 138 | 18:00 | 128 | 21:00 | TK | 133 | 18:30 | 127 | 00:00
| Khulshi | 131 | 18:30 | 125 | 16:00 | Tongi | 135 | 04:00 | 122 | 15:00
| Kishoreganj | 130 | 11:00 | 123 | 21:00 | Ullahpara | 135 | 18:30 | 127 | 13:00
| Kodda | 130 | 19:30 | 116 | 08:00 | Ullon | 133 | 03:00 | 122 | 16:00
| KSRM | 133 | 18:30 | 126 | 04:00 | Uttara | 136 | 04:00 | 127 | 15:00
| Kulaura | 132 | 18:30 | 129 | 21:00 | UttaraNew | 136 | 01:00 | 125 | 15:00
| Kurigram | 135 | 01:00 | 119 | 21:00 | Zigatola | 133 | 18:30 | 123 | 16:00

## L-Curve
Date | 2024-06-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1004 | 8107 | 6282 | 14389 |  |  |  | QF-LDC-11
0:30 | 1071 | 7690.5 | 6317.5 | 14008 | Date: | 2024-06-04
1:00 | 1138 | 7274 | 6353 | 13627
1:30 | 1118 | 7272 | 6336.5 | 13608.5
2:00 | 1098 | 7270 | 6320 | 13590
2:30 | 1080 | 7204 | 6229 | 13433 | [5 empty] | Gen. at Eve. Peak | 14937 | 14937 MW (19:30 )
3:00 | 1062 | 7138 | 6138 | 13276 | [6 empty] | 19:30
3:30 | 1054 | 7058.5 | 6067 | 13125.5 | [5 empty] | Gen. at Day Peak | 13555 | 13555 MW (12:00 )
4:00 | 1046 | 6979 | 5996 | 12975 | [6 empty] | 12:00
4:30 | 1116 | 6862.5 | 5936 | 12798.5 | [5 empty] | Highest Generation | 14937
5:00 | 1186 | 6746 | 5876 | 12622 | [6 empty] | 19:30
5:30 | 1230 | 6660 | 5709 | 12369
6:00 | 1274 | 6574 | 5542 | 12116
6:30 | 1236 | 6547 | 5443.5 | 11990.5
7:00 | 1198 | 6520 | 5345 | 11865
7:30 | 1286 | 6516.5 | 5300 | 11816.5
8:00 | 1374 | 6513 | 5255 | 11768
8:30 | 1373 | 6655 | 5270 | 11925
9:00 | 1372 | 6797 | 5285 | 12082
9:30 | 1277 | 6998.5 | 5349 | 12347.5
10:00 | 1182 | 7200 | 5413 | 12613
10:30 | 1155 | 7232.5 | 5554.5 | 12787
11:00 | 1128 | 7265 | 5696 | 12961
11:30 | 1136 | 7483 | 5775 | 13258
12:00 | 1144 | 7701 | 5854 | 13555
12:30 | 1112 | 7715.5 | 5898.5 | 13614
13:00 | 1080 | 7730 | 5943 | 13673
13:30 | 1104 | 7779.5 | 6048 | 13827.5
14:00 | 1128 | 7829 | 6153 | 13982
14:30 | 1157 | 7976 | 6194 | 14170
15:00 | 1186 | 8123 | 6235 | 14358
15:30 | 1192 | 8088 | 6110.5 | 14198.5
16:00 | 1198 | 8053 | 5986 | 14039
16:30 | 1090 | 7900 | 5683.5 | 13583.5
17:00 | 982 | 7747 | 5381 | 13128
17:30 | 956 | 7766.5 | 5220.5 | 12987
18:00 | 930 | 7786 | 5060 | 12846
18:30 | 848 | 8214.5 | 5353 | 13567.5
19:00 | 766 | 8643 | 5646 | 14289
19:30 | 644 | 8760 | 6177 | 14937
20:00 | 550 | 8668 | 6110 | 14778 |  |  |  | Executive Engineer
20:30 | 612 | 8544 | 6224 | 14768 |  |  |  | Network Operation Division
21:00 | 674 | 8420 | 6338 | 14758
21:30 | 714 | 8378.5 | 6324.5 | 14703
22:00 | 754 | 8337 | 6311 | 14648 |  |  |  |  | Page 6 of 7
22:30 | 870 | 8259.5 | 6290 | 14549.5
23:00 | 986 | 8182 | 6269 | 14451
23:30 | 995 | 8144.5 | 6275.5 | 14420
24:00 | 1004 | 8107 | 6282 | 14389
14937 MW (19:30 )
13555 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-04 |  | Energy |  | 327904361
[15 empty] | 2024-06-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3910 | 782 | 1814 | 0 | 2203 | 4946 | 95 | 0 | 543 | 92 | 0 | 4 | 344.755
0:30 | 3890.5 | 780 | 1789.5 | 0 | 2208 | 4635 | 95 | 0 | 517 | 85 | 0 | 8 | 493.735 |  |  | Date: | 43985
1:00 | 3871 | 778 | 1765 | 0 | 2213 | 4324 | 95 | 0 | 491 | 78 | 0 | 12 | 642.715
1:30 | 3852 | 778.5 | 1743 | 0 | 2256 | 4349 | 95 | 0 | 440.5 | 78 | 0 | 16.5 | 517.1325 | [9 empty] | Total Energy | 327.9044 | 327.9044 | Total Energy Gen 327.904 MKWHr Energy Not Served 5.321 MKWHr Energy Requirement 333.225 MKWHr
2:00 | 3833 | 779 | 1721 | 0 | 2299 | 4374 | 95 | 0 | 390 | 78 | 0 | 21 | 391.55 | [9 empty] | Energy not Served | 5.3209 | 5.3209
2:30 | 3830 | 851 | 1724.5 | 0 | 2128 | 4377.5 | 95 | 0 | 336 | 76 | 0 | 15 | 350.485 | [9 empty] | Energy Requirement | 333.2252 | 333.2252
3:00 | 3827 | 923 | 1728 | 0 | 1957 | 4381 | 95 | 0 | 282 | 74 | 0 | 9 | 309.42
3:30 | 3833.5 | 923 | 1719.5 | 0 | 1869 | 4376 | 95 | 0 | 220 | 74 | 0 | 15.5 | 286.0225 | [8 empty] | Shortage
4:00 | 3840 | 923 | 1711 | 0 | 1781 | 4371 | 95 | 0 | 158 | 74 | 0 | 22 | 262.625
4:30 | 3802.5 | 923 | 1682.5 | 0 | 1689 | 4370 | 95 | 0 | 150 | 71 | 0 | 15.5 | 264.0575
5:00 | 3765 | 923 | 1654 | 0 | 1597 | 4369 | 95 | 0 | 142 | 68 | 0 | 9 | 265.49
5:30 | 3784 | 923 | 1657 | 0 | 1361.5 | 4327.5 | 95 | 0 | 142 | 63 | 10.5 | 5.5 | 244.48
6:00 | 3803 | 923 | 1660 | 0 | 1126 | 4286 | 95 | 0 | 142 | 58 | 21 | 2 | 223.47
6:30 | 3801 | 923 | 1670 | 0 | 1075 | 4178 | 95 | 0 | 142 | 61 | 32 | 13.5 | 223.9475 | [7 empty] | Coal
7:00 | 3799 | 923 | 1680 | 0 | 1024 | 4070 | 95 | 0 | 142 | 64 | 43 | 25 | 224.425
7:30 | 3791 | 923 | 1666.5 | 0 | 1028.5 | 4017.5 | 95 | 0 | 142 | 67 | 65 | 21 | 246.8675 | [6 empty] | Oil
8:00 | 3783 | 923 | 1653 | 0 | 1033 | 3965 | 95 | 0 | 142 | 70 | 87 | 17 | 269.31
8:30 | 3731.5 | 923 | 1671 | 0 | 1164.5 | 3994 | 97.5 | 0 | 142 | 73 | 117.5 | 11 | 248.3
9:00 | 3680 | 923 | 1689 | 0 | 1296 | 4023 | 100 | 0 | 142 | 76 | 148 | 5 | 227.29
9:30 | 3706 | 923.5 | 1656 | 0 | 1445 | 4086 | 97.5 | 0 | 160.5 | 77 | 191 | 5 | 193.3875
10:00 | 3732 | 924 | 1623 | 0 | 1594 | 4149 | 95 | 0 | 179 | 78 | 234 | 5 | 159.485
10:30 | 3801.5 | 923.5 | 1609 | 0 | 1663 | 4163 | 94 | 0 | 175 | 79 | 275 | 4 | 160.44
11:00 | 3871 | 923 | 1595 | 0 | 1732 | 4177 | 93 | 0 | 171 | 80 | 316 | 3 | 161.395
11:30 | 3896.5 | 922 | 1662.5 | 0 | 1789.5 | 4243.5 | 92.5 | 0 | 196.5 | 82 | 370.5 | 2.5 | 126.1975
12:00 | 3922 | 921 | 1730 | 0 | 1847 | 4310 | 92 | 0 | 222 | 84 | 425 | 2 | 91
12:30 | 3929 | 921 | 1706 | 0 | 1881 | 4364.5 | 92 | 0 | 234.5 | 87 | 390 | 9 | 77.97
13:00 | 3936 | 921 | 1682 | 0 | 1915 | 4419 | 92 | 0 | 247 | 90 | 355 | 16 | 64.94
13:30 | 3936 | 921 | 1682 | 0 | 1915 | 4419 | 92 | 0 | 247 | 90 | 355 | 16 | 64.94
14:00 | 3936 | 921 | 1682 | 0 | 1915 | 4419 | 92 | 0 | 247 | 90 | 355 | 16 | 64.94
14:30 | 3905.5 | 921 | 1742.5 | 0 | 2002.5 | 4623 | 94.5 | 0 | 291 | 90 | 323.5 | 22 | 124.15
15:00 | 3875 | 921 | 1803 | 0 | 2090 | 4827 | 97 | 0 | 335 | 90 | 292 | 28 | 183.36
15:30 | 3855.5 | 922.5 | 1780.5 | 0 | 2162 | 4683 | 97.5 | 0 | 337.5 | 92 | 241 | 27 | 219.1725
16:00 | 3836 | 924 | 1758 | 0 | 2234 | 4539 | 98 | 0 | 340 | 94 | 190 | 26 | 254.985
16:30 | 3742 | 924 | 1643 | 0 | 2230 | 4340.5 | 99 | 0 | 350.5 | 92 | 137 | 25.5 | 209.6225
17:00 | 3648 | 924 | 1528 | 0 | 2226 | 4142 | 100 | 0 | 361 | 90 | 84 | 25 | 164.26
17:30 | 3612 | 924 | 1490.5 | 0 | 2314 | 3961 | 100 | 0 | 423 | 87 | 55 | 20.5 | 127.13
18:00 | 3576 | 924 | 1453 | 0 | 2402 | 3780 | 100 | 0 | 485 | 84 | 26 | 16 | 90
18:30 | 3727.5 | 924 | 1556.5 | 0 | 2649.5 | 3873.5 | 100 | 0 | 621 | 90 | 13 | 12.5 | 67
19:00 | 3879 | 924 | 1660 | 0 | 2897 | 3967 | 100 | 0 | 757 | 96 | 0 | 9 | 44
19:30 | 3871 | 905 | 1643 | 0 | 3027 | 4515 | 100 | 0 | 777 | 92 | 0 | 7 | 99.355
20:00 | 3874 | 782 | 1679 | 0 | 2827 | 4610 | 100 | 0 | 807 | 94 | 0 | 5 | 154.71
20:30 | 3933.5 | 781.5 | 1674.5 | 0 | 2562 | 4825 | 100 | 0 | 790.5 | 93 | 0 | 8 | 168.855
21:00 | 3993 | 781 | 1670 | 0 | 2297 | 5040 | 100 | 0 | 774 | 92 | 0 | 11 | 183
21:30 | 3957.5 | 781 | 1672 | 0 | 2288 | 5023.5 | 100 | 0 | 778 | 92 | 0 | 11 | 211.83
22:00 | 3922 | 781 | 1674 | 0 | 2279 | 5007 | 100 | 0 | 782 | 92 | 0 | 11 | 240.66
22:30 | 3938 | 781.5 | 1720 | 0 | 2236 | 4986 | 97.5 | 0 | 688.5 | 93 | 0 | 9 | 296.5275
23:00 | 3954 | 782 | 1766 | 0 | 2193 | 4965 | 95 | 0 | 595 | 94 | 0 | 7 | 352.395
23:30 | 3932 | 782 | 1790 | 0 | 2198 | 4955.5 | 95 | 0 | 569 | 93 | 0 | 5.5 | 348.575 |  |  | Max Temp. in Dhaka |  | 36.0°C
24:00 | 3910 | 782 | 1814 | 0 | 2203 | 4946 | 95 | 0 | 543 | 92 | 0 | 4 | 344.755
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 327.904 MKWHr Energy Not Served 5.321 MKWHr Energy Requirement 333.225 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 1320944
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 37 | 37 | 37 | 37 | 38 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 940000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 7 | 8 |  | 13 | 17 | 17 | 17 | 17 | 8 | 8 | 98528
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 1 | 6 | 12 | 11 | 16 | 19 | 19 | 13 | 8 | 3 | 1 | [8 empty] | 96255
6 | Sikalbaha 225MW CCPP (Gas) | 221 | 222 | 220 | 220 | 221 | 222 | 222 | 220 | 225 | 227 | 227 | 224 | 224 | 224 | 221 | 222 | 223 | 222 |  | 222 | 222 | 222 | 222 | 222 | 222 | 223 | 5252391
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 68 | 68 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1410636
12 | Hathazari 100 MW peaking PP | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 64 | 64 | 64 | 64 | 64 | 64 |  | 65 | 57 | 60 | 66 | 66 | 66 | 65 | 1408656
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 907454
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 45 | 45 | 45 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 29 | 29 | 29 | 29 | 37 | 37 | 37 | 46 |  | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 937792
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 328 | 321 | 321 | 326 | 325 | 328 | 324 | 322 | 320 | 316 | 288 | 315 | 316 | 317 | 310 | 313 | 280 | 240 |  | 319 | 320 | 320 | 320 | 323 | 325 | 328 | 7560940
18 | Kodda 300 MW PP Unit-2 (Summit) | 173 | 273 | 278 | 195 | 95 |  |  |  | 3 | 125 | 147 | 153 | 145 | 156 | 143 | 155 | 158 | 142 |  | 183 | 243 | 145 | 45 | 15 | 18 | 72 | 3058582
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4221000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 490 | 490 | 485 | 470 | 470 | 470 | 473 | 472 | 477 | 475 | 473 | 472 | 470 | 470 | 470 | 470 | 443 |  | 407 | 480 | 474 | 492 | 492 | 492 | 490 | 11438180
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [18 empty] | 132768
33 | Ashuganj 225 MW CCPP | 203 | 199 | 199 | 199 | 199 | 203 | 202 | 191 | 204 | 217 | 213 | 218 | 190 | 189 | 198 | 196 | 214 | 206 |  | 213 | 218 | 218 | 211 | 220 | 211 | 218 | 4994000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 340 | 290 | 270 | 270 | 290 | 290 | 270 | 305 |  | 335 | 270 | 270 | 315 | 270 | 285 | 270 | 6476000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 280 | 280 | 305 | 280 | 280 | 300 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7237500
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 300 | 230 | 230 | 230 | 230 |  | 240 | 260 | 260 | 280 | 280 | 280 | 230 | 5993800
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 51 | 50 | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1183060
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 378 | 388 | 388 | 388 | 394 | 396 | 401 | 400 | 364 | 364 | 355 | 376 | 369 | 370 | 400 | 401 | 372 | 301 |  | 368 | 356 | 359 | 347 | 340 | 333 | 363 | 9007200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 380 | 380 | 380 | 380 | 380 | 380 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 400 | 390 | 390 | 390 |  | 390 | 380 | 370 | 350 | 350 | 350 | 370 | 8536500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 45 | 45 | 45 | 46 | 46 | 46 | 34 | 34 | 30 | 28 | 28 | 28 | 28 | 25 | 26 | 27 | 28 | 28 |  | 29 | 31 | 31 | 31 | 33 | 33 | 32 | 771840
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 7 | 21 | 2 | 32 | 1 | 42 | 27 | 38 | 22 | 12 | 7 | 1 |  | 0 | [6 empty] | 199340
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 43 | 43 |  | 40 | 40 | 40 | 42 | 42 | 42 | 42 | 985000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1383240
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 62 | 62 | 62 | 62 | 61 | 60 | 61 | 61 | 59 | 59 | 60 | 62 | 59 | 58 | 62 | 40 |  | 40 | 40 | 40 | 58 | 55 | 55 | 59 | 1385472
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 208 | 208 | 208 | 211 | 211 | 211 | 211 | 211 | 210 | 211 | 211 | 210 | 210 | 210 | 210 | 209 | 208 | 211 |  | 211 | 211 | 210 | 211 | 210 | 210 | 210 | 5243490
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 168576
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 10 | 40 | 50 | 50 | 50 | 50 | 52 | 11 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1106400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 380688
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 270 | 275 | 260 | 270 | 280 | 290 | 280 | 310 | 285 | 315 | 305 | 290 | 290 | 315 | 320 | 270 | 280 |  | 300 | 265 | 290 | 300 | 300 | 290 | 310 | 7181500
| Bibiyana South 400 MW | 394 | 310 | 310 | 310 | 310 | 310 | 310 | 335 | 345 | 310 | 340 | 340 | 376 | 310 | 320 | 340 | 310 | 340 |  | 380 | 345 | 345 | 381 | 345 | 355 | 345 | 8151500
58 | Nababganj 55 MW PP (Southern power ) |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 17 | 35 | 35 | 35 | 607401
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 186960
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 78 | 78 | 74 | 74 | 68 | 58 | 64 | 70 | 76 | 78 | 80 | 84 | 90 | 92 | 90 | 94 | 90 | 84 |  | 96 | 92 | 94 | 92 | 92 | 94 | 92 | 1969920
64 | Malancha, Ctg. EPZ (United) | 23 | 23 | 23 | 24 | 29 | 12 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 3 | 4 | 2 |  | 10 | 12 | 19 | 15 | 28 | 28 | 33 | 262080
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  |  |  |  | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 626700
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 256900
69 | Summit Ashulia | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 |  |  | 14 | 13 | 13 |  |  | 12 | 12 |  | 12 | 12 | 12 | 13 | 14 | 14 | 14 | 288600
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482760
71 | Maona 33 MW PP(Summit) |  | 10 |  |  |  | 25 | 25 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 575800
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 |  | 10 |  | 10 | 6 | 10 | 10 | 10 | 10 | 10 | 338400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 52 | 44 | 52 | 52 | 52 | 52 | 52 | 52 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 1406760
| Chowmuhani 113 MW | 50 | 38 | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 38 | 37 | 37 | 37 | 36 | 36 | 37 | 41 | 73 |  | 73 | 73 | 75 | 75 | 75 | 75 | 75 | 1181040
| Manikgonj 162MW PP(MPGL) | 108 | 108 | 108 | 108 | 108 | 17 | 17 | 17 | 115 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 108 | 108 | 108 | 162 | 162 | 2950560
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 25 | 25 | 25 | 14 | 8 | 8 | 8 | 316800
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 137280
79 | Kodda 150 MW PP | 48 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 48 | 48 | 48 | 115 |  | 149 | 149 | 149 | 125 | 133 | 133 | 82 | 1336800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 41 | 41 | 41 | 25 | 33 | 25 | 25 | 25 | 25 | 25 | 25 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 891490
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 74 | 88 | 88 | 88 | 88 | 88 | 35 | 1112640
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 2 | 5 | 2 | 3 | 0 | [9 empty] | 16563
| Jodiac Power | 35 | 35 | [6 empty] | 12 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 17 | 17 | 19 | 35 | 633365
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 92 | 92 | 92 | 34 | 34 | 46 | 56 | 62 | 84 | 92 | 92 | 92 | 92 | 92 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 110 | 2043227
82 | Madanganj 102 PP(Summit) | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 45 | 66 | 1441388
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 22 | 22 | 20 | 13 | 13 |  |  | 62429
86 | Meghnaghat CCPP ( Summit) | 150 | 143 | 144 | 144 | 132 | 145 | 145 | 147 | 144 | 150 | 152 | 153 | 150 | 151 | 150 | 152 | 133 | 150 |  | 151 | 136 | 150 | 153 | 144 | 153 | 155 | 3506036
87 | Meghnaghat 100 MW(IEL) | 24 | 17 | 17 | 17 | 18 | 16 | 18 | 17 | 17 | 16 | 17 | 16 | 17 | 16 | 17 | 16 | 16 | 22 |  | 25 | 25 | 25 | 15 | 8 | 9 | 8 | 390720
| Meghnaghat 104 MW PP (OPCL) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 50 | 50 | 51 | 50 | 50 | 50 | 51 | 70 | 70 |  | 70 | 70 | 70 | 67 | 67 | 68 | 70 | 1202880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 70 | 70 | 25 | 25 | 25 |  |  |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 35 | 35 |  | 44 | 68 | 68 | 35 | 35 | 35 | 35 | 1057440
92 | Fenchuganj 44 MW (Energyprima) | 36 | 40 | 40 | 40 | 40 | 40 | 35 | 37 | 37 | 40 | 40 | 43 | 43 | 39 | 39 | 40 | 10 | 10 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 932904
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 995712
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 |  | 90 | 90 | 90 | 24 | 24 | 42 | 91 | 587664
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 9 | 29 | 46 | 50 | 50 | 50 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 6 | 643200
96 | Chattogram 108 MW PP (ECPV) | 29 | 25 | 25 | 25 | 25 | 25 | 25 | 27 | 31 | 31 | 39 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 37 | 39 | 37 | 807360
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 30 |  | 35 | 55 | 55 | 55 | 45 | 30 | 30 | 811768
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 664812
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 163 | 120 | 163 | 163 | 163 | 120 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3880309
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 10450
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 0 |  | 8 | 17 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 35 | 17 | 17 | 21 | 54 | 879480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 77 | 77 | 77 |  | 106 | 106 | 107 | 107 | 107 | 107 | 107 | 2042400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 36 | 80 | 117 | 115 | 113 | 129 | 120 | 104 | 88 | 86 | 88 |  | 94 | 131 | 133 | 133 | 133 | 79 | 41 | 1953072
115 | Juldah 100 MW PP Unit-3 (Acorn) | 24 | 24 | 24 | 20 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 424800
117 | Ashuganj 150 MW PP (Midland) | 60 | 82 | 88 | 92 | 87 | 85 | 85 | 85 | 85 | 89 | 89 | 85 | 87 | 99 | 99 | 100 | 97 | 99 |  | 107 | 66 | 76 | 6 | 6 | 13 | 12 | 1868436
118 | Bibiyana-III 400 MW CCPP | 369 | 400 | 400 | 399 | 317 | 316 | 316 | 303 | 324 | 400 | 400 | 402 | 402 | 402 | 402 | 375 | 329 | 303 |  | 327 | 387 | 389 | 399 | 400 | 402 | 402 | 8955000
| Jamalpur 115 MW PP (United) | 69 | 69 | 69 | 69 | 69 | 70 | 70 | 70 | 70 | 70 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 68 |  | 97 | 87 | 89 | 99 | 99 | 99 | 89 | 1804800
| Anwara 300 MW PP (United) | 52 | 52 | 52 | 52 | 52 | 50 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 51 | 51 | 52 | 52 | 1249527
| Juldah unit-2 (Acorn) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 591360
| Anlima Energy Ltd. | 72 | 72 | 72 | 40 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 13 | 35 | 35 | 35 | 35 | 35 |  | 62 | 72 | 72 | 72 | 72 | 72 | 72 | 1124073
| Bhairob 54.5 MW | 17 | [9 empty] | 3 |  |  |  | 19 | 20 | 17 | 17 |  | 17 |  |  | 6 | 17 | 17 | 17 | 202320
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 6 | 13 | 20 | 12 | 29 | 32 | 30 | 14 | 22 | 15 | 6 | 1 | [8 empty] | 176600
| Chandpur 115(Doreen) | 107 | 115 | 106 | 105 | 105 | 104 | 105 | 104 | 57 | 49 | 49 | 49 | 49 | 48 | 48 | 46 | 64 | 84 |  | 102 | 105 | 105 | 108 | 115 | 91 | 67 | 1992960
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 21 | 31 | 17 | 17 | 17 | 26 | 35 | 35 | 35 | 35 | 35 | 35 |  | 16 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 749880
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 145 | 145 | 163 | 163 | 163 | 17 | 17 | 1142472
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 12 | 21 | 9 | 22 | 9 | 2 | 25 | 17 | 5 | 5 | 3 | 2 | 16 | 20 | 28 | 26 | 25 | 16 |  | 9 | 7 | 5 | 11 | 11 | 7 | 4 | 307200
| Sonagazi 75 MW Solar Plant | [5 empty] | 2 | 3 | 9 | 13 | 14 | 33 | 40 | 42 | 59 | 35 | 8 | 9 | 4 | [8 empty] | 291055
| Matarbari 2*600 MW (CPGCL) | 281 | 280 | 281 | 281 | 274 | 283 | 283 | 282 | 282 | 282 | 282 | 436 | 447 | 449 | 751 | 777 | 792 | 795 |  | 796 | 792 | 797 | 798 | 797 | 861 | 858 | 12138181
120 | Eastern Zone Total | 7274 | 7270 | 7138 | 6979 | 6746 | 6574 | 6520 | 6513 | 6797 | 7200 | 7265 | 7701 | 7730 | 7829 | 8123 | 8053 | 7747 | 7786 |  | 8643 | 8760 | 8668 | 8420 | 8337 | 8182 | 8107 | 182207966
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 85 | 95 | 97 | 98 | 97 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 16 | 47 | 66 | 77 |  | 78 | 78 | 84 | 47 | 47 | 47 | 48 | 1146240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 8 | [13 empty] | 21 | 38 |  | 39 | 49 | 41 | 41 | 40 |  |  | 271200
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 90 | 90 | 90 | 90 | 17 | 17 | 17 | 17 | 17 | 90 | 90 | 89 | 89 | 89 | 89 | 89 | 89 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1825440
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 7 | 27 | 31 | 72 | 59 | 95 | 64 | 21 | 37 | 63 | 50 | 13 | 5 | [8 empty] | 541440
131 | Rampal 1320 MW (BIFPCL) | 596 | 592 | 595 | 594 | 600 | 604 | 574 | 505 | 515 | 574 | 604 | 565 | 563 | 574 | 567 | 526 | 426 | 378 |  | 437 | 509 | 502 | 541 | 544 | 541 | 543 | 14094549
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5255291
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 100 | 110 | 110 | 32 | 16 | 16 | 16 | [7 empty] | 32 | 32 | 32 |  | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 686688
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 280 | 307 | 307 | 307 | 200 | 179 | 150 |  | 220 | 250 | 268 | 307 | 307 | 307 | 307 | 6763600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 126 | 126 | 126 | 126 | 126 | 126 | 130 | 130 | 80 | 80 | 130 | 80 | 130 | 130 | 126 | 126 | 76 | 80 |  | 126 | 126 | 126 | 126 | 126 | 130 | 130 | 2817000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 10 | 10 | 10 | 10 | 9 | 6 | 5 | 5 | 5 | 3 | 6 | 7 | 7 | 7 | 6 | 7 |  | 10 | 8 | 8 | 10 | 10 | 9 | 10 | 189938
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 40 | [5 empty] | 16 | 16 | 16 | 16 | 16 | 40 | 40 | 40 |  | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 495750
143 | Gopalganj 100 MW Peaking PP | 45 | 45 | 15 | [14 empty] | 20 |  | 56 | 56 | 67 | 53 | 53 | 53 | 53 | 432768
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 778 | 779 | 923 | 923 | 923 | 923 | 923 | 923 | 923 | 924 | 923 | 921 | 921 | 921 | 921 | 924 | 924 | 924 |  | 924 | 905 | 782 | 781 | 781 | 782 | 782 | 21303272
147 | Bheramara 410 MW CCPP | 175 | 180 | 185 | 190 | 190 | 195 | 200 | 205 | 200 | 200 | 200 | 200 | 190 | 190 | 180 | 180 | 175 | 180 |  | 180 | 200 | 195 | 200 | 205 | 220 | 215 | 4764960
148 | Payra 1320 MW | 1100 | 1100 | 1100 | 1100 | 1100 | 1000 | 980 | 920 | 990 | 1100 | 1100 | 1050 | 1080 | 1130 | 1172 | 1000 | 800 | 660 |  | 730 | 1000 | 1040 | 1190 | 1160 | 1040 | 1040 | 27217700
149
150 | Barapukuria TPP Unit-1 |  | 57 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 61 | 62 | 62 | 60 | 61 | 64 | 65 | 64 | 64 |  | 65 | 64 | 64 | 64 | 65 | 65 | 65 | 1886836
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5583000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 22 | 22 | 14 | [10 empty] | 25 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 376770
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 0 | 4 | 4 | 0 | 0 | 4 | 3 | 0 | 1 | 0 | [8 empty] | 23520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 135 | 135 | 138 | 200 | 165 | 170 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3848173
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 380 | 380 | 380 | 320 | 320 | 320 | 320 | 370 | 320 | 300 | 370 | 370 | 340 | 414 | 370 | 320 | 260 |  | 320 | 320 | 320 | 320 | 320 | 414 | 414 | 8520872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit)
165 | Amnura 50 MW PP(Sinha) | 28 | 28 | [13 empty] | 11 | 12 | 12 |  | 35 | 35 | 14 | 14 | 14 |  |  | 179590
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 35 | 35 | 15 | [11 empty] | 10 | 15 | 15 | 26 |  | 40 | 42 | 48 | 45 | 45 | 45 | 45 | 352100
168 | Santahar 50 MW Peaking PP | 35 | 35 | 30 | [16 empty] | 14 | 30 | 30 | 30 | 30 | 30 | 30 | 259906
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | 85 | [12 empty] | 44 | 44 | 44 | 44 | 44 |  | 88 | 88 | 88 | 90 | 90 | 90 | 90 | 776768
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | [11 empty] | 6 | 35 | 37 | 90 | 113 |  | 113 | 113 | 113 | 70 | 70 | 40 | 70 | 1096992
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 35 | [11 empty] | 25 | 35 | 90 | 95 | 113 |  | 113 | 113 | 113 | 35 | 35 | 70 | 70 | 949536
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 90 | 100 | [9 empty] | 10 | 34 | 34 | 34 | 34 | 34 | 40 |  | 104 | 104 | 107 | 107 | 107 | 107 | 107 | 1095974
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 4 | 5 | 7 | 7 | 7 | 7 | 2 | 4 | 2 | 1 | [8 empty] | 44123
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 54 | 53 | [6 empty] | 35 | 53 | 110 | 115 | 115 | 54 | 54 |  | 90 | 115 | 115 | 115 | 115 | 115 | 115 | 1670784
| Intraco Solar 30 MW | [5 empty] | 0 | 0 | 2 | 7 | 14 | 29 | 34 | 13 | 13 | 22 | 15 | 7 | 2 |  | 0 | [6 empty] | 166464
| Adani Power Jharkhanda Ltd | 1320 | 1318 | 1318 | 1314 | 1328 | 1332 | 1166 | 1188 | 1167 | 1118 | 1117 | 1214 | 1260 | 1280 | 1266 | 1271 | 1181 | 1060 |  | 1082 | 1190 | 1235 | 1418 | 1412 | 1429 | 1413 | 30049091
178 | Teesta Solar Limited | [5 empty] | 9 | 0 | 6 | 23 | 80 | 103 | 187 | 192 | 167 | 107 | 74 | 35 | 11 | [8 empty] | 1010060