## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-07 | Friday
|  | Date (day): | 2024-06-07 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14375.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16114 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-06 | 2024-06-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 370 | 404 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 420 | 420 | 30 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 14 | 81 | 50 | 75 |  |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 153 | 152 | 150 | 150 | 185 |  | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 64 | 64 | 64 | 64 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 25 | 0 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 28 | 77 | 80 | 80 |  |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 322 | 290 | 310 | 25 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 82 | 90 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 149 | 32 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55 |  |  | Fuel Shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 17 | 55 |  |  | Fuel Shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 24 | 33 | 33 |  | 47 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 10 | 10 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 260 | 150 | 270 | 30 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 108 | 149 | 115 | 132 |  | 17 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 52 | 88 | 17 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 50 | 70 | 50 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 136 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 2254 | 3004 | 2584 | 3006 | 1602 | 877
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 24 | 6 | 18 | 32 |  | fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 74 | 70 | 70 | 160 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 220 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 51 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 47 | 32 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 50 | 85 | 50 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 78 | 80 | 70 | 80 | 20 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 5 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 32 | 37 | 30 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 61 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 93 | 110 | 85 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 24 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 72 | 35 | 72 | 44 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 480 | 485 | 490 | 490 |  | 734 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 7 | 8 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 827 | 827 | 820 | 820
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 60 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 2282 | 2445 | 2302 | 2500 | 1019 | 1103
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 220 | 216 | 200 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 280 | 280 | 280 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 270 | 280 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 230 | 260 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 43 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 28 | 128 | 70 | 130 | 20 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 46 | 41 | 45 | 46 |  | 6 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 88 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 34 | 25 | 34 |  | 18 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 0 | 17 | 17 | 97 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 84 | 37 | 84 | 29 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 | 37 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 104 | 50 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1404 | 1587 | 1509 | 1754 | 653 | 200
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 26 | 34 | 30 | 40 | 162 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 94 | 121 | 90 | 120 | 80 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 78 | 60 | 80 | 35 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 21 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 208 | 239 | 237.6 | 252 | 162 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 28 | 28 |  | 62 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 53 | 53
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 42 | 40 | 43 |  | 7 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 3 | 3 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 58 | 56 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 209 | 206 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 22 | 22 |  | 3 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 285 | 280 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 367 | 350 | 380 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 345 | 350 | 360 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1656 | 1606 | 1600 | 1667 | 0 | 476
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 927 | 923 | 943 | 801
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 21 | 31 | 20 | 80
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 47 | 30 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 55 | 50 | 66 |  | 43 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 230 | 220 | 210 | 220 | 190 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 8 | 8 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 53 | 90 | 15 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 547 | 602 | 500 | 600
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1844 | 1921 | 1938 | 1947 | 787 | 43
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 790 | 1080 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 307 | 307 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1454 | 1763 | 1700 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 28 | 0 | 40 |  | 12 | engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 25 |  | 46 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 14 | 14 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 140 | 140 | 150 | 60 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 414 | 320 | 380 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 5 | 5 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 45 | 94 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1285 | 1406 | 1200 | 1400
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1807 | 2288 | 1942 | 2416 | 743 | 83
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 67 | 65 | 60 | 65
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 230 | 230 | 230 |  | 44 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 98 | 70 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 25 | 94 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 194 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 594 | 487 | 563 | 516 | 40 | 136
| Total |  |  |  |  | 27054 | 25903 | 13503 | 15340 | 14375.6 | 16114 | 5121 | 2982
A. |  | 2024-06-06 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 15340 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 11044 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15725 | MW
3 | Day peak Generation : |  |  | 13503 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15109.63 | MW
4 | Evening peak Generation : |  |  | 15340 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 368 | MW
5 | Total Energy Generation : |  | 327.5871 | MKWHr | By Solar | 3.0823 | MKWHr
| By Gas : | 133.234 | MKWHr |  | By Oil: | 51.8336 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 113.4373 | MKWHr |  | By Hydro: | 2.3624 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.12864 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5121 | MW | Dhaka | 5655.23 | 5572.23 |  | 83 |  | 18:00 |  | 209
|  |  | For Plants S/D or M/C prob = |  |  | 2982 | MW | Chittagong | 1429.6 | 1429.6 |  | 0 |  | 19:00 |  | 318
|  |  | Total = |  |  | 8103 | MW | Khulna | 1916.9 | 1916.9 |  | 0 |  | 19:30 |  | 368
7 | Total Gas Supplied : |  |  | 979.59 | MMCFD |  |  | Rajshahi | 1504.4 | 1504.4 |  | 0 |  | 20:00 |  | 433
8 | Fuel Cost : | i) Gas : | Taka | 409449949.97 | ii) Oil : | Taka | 942663914.99 | Comilla | 1431 | 1306 |  | 125 |  | 21:00 |  | 510
|  | iii) Coal : | Taka | 768112063.92 | Total | Taka | 2120225928.88 | Mymensingh | 1155 | 995 |  | 160 |  | 22:00 |  | 652.265
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7231.95 | MKWHr. | Sylhet | 570 | 570 |  | 0 |  | 23:00 |  | 696.195
| ii) During Peak Demand : |  |  | 730 | MW (W to E) at | 19:30 | hrs | Barisal | 460.5 | 460.5 |  | 0 |  | 24:00 |  | 786.92
| iii) Maximum : |  |  | 574 | MW at | 22:00 | hrs | Rangpur | 987 | 987 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.5°C |  |  | Total | 15109.63 | 14741.63 |  | 368
B. |  | 2024-06-07 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 34.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16114 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12800 | MW
4 | Reserve(Generation end) |  |  |  | 1114 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 320.3263 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11850 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4996 | MKWHr. | ii) HVDC Flow at Peak Time |  | 923 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0093 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.5 |  | (b) Today: | 81.28 |  | (c) Rule Curve: |  | 77.56
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-06-06 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 353 | 0 |  | 0 | 410 | 135 | 49 | 68 | 55 | 270 | 0 | 0 | 40 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 13 | 22 | 33 | 12 | 0 | 0 | 90 | 39 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 1 | 64 | 68 | 68 | 26 | 6 | 0 | 28 | 0 | 0 | 0 | 280 | 280 | 214 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 44 | 41 | 0 | 0 | 32 | 12 | 90 | 35 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 51 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 3 | 0 | 95 | 0 | 0 | 98 | 0 | 131 | 0 | 22 | 17 | 80 | 346 | 59 | 17 | 17 | 0 | 51 | 35 | 110 | 17 | 51 | 25 | 340 | 53 | 0 | 90 | 72 | 0 | 0 | 0 | 77 | 17 | 230 | 17 | 0 | 480 | 0 | 826 | 0 | 0 | 0 |  | 773 | 0 | 205 | 0 | 81 | 0 | 0 | 0 | 30 | 47 | 8 | 126 | 10 | 64 | 0 | 0 | 0 | 39 | 0 | 85 | 0 | 0 | 38 | 0 | 35 | 0 | 0 | 0 | 62 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 620 | 0 | 307 | 1356 | 0 | 0 |  | 7712 | 6075 | 13787 | 3697 | 773 | 1747 | 0 | 1977 | 4891 | 129 | 0 | 483 | 90 | 0 | 0 | 298.915 | 81.52
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 352 | 0 |  | 0 | 350 | 152 | 37 | 68 | 55 | 270 | 0 | 0 | 33 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 13 | 0 | 0 | 12 | 0 | 0 | 70 | 38 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 64 | 51 | 68 | 25 | 6 | 0 | 28 | 0 | 0 | 0 | 280 | 280 | 214 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 44 | 42 | 0 | 0 | 32 | 12 | 90 | 36 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 51 | 0 | 0 | 211 | 0 | 0 | 0 | 290 | 16 | 3 | 0 | 0 | 0 | 0 | 98 | 0 | 131 | 0 | 22 | 17 | 6 | 352 | 59 | 0 | 17 | 0 | 52 | 17 | 110 | 17 | 37 | 25 | 370 | 53 | 0 | 17 | 72 | 0 | 0 | 0 | 115 | 17 | 230 | 17 | 0 | 481 | 3 | 827 | 0 | 0 | 0 |  | 777 | 0 | 210 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 126 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 0 | 307 | 1267 | 0 | 0 |  | 7308 | 5458 | 12766 | 3682 | 777 | 1684 | 0 | 1502 | 4728 | 108 | 0 | 192 | 90 | 0 | 3 | 223.47 | 81.52
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 155 | 20 | 68 | 55 | 270 | 0 | 0 | 25 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 13 | 0 | 0 | 12 | 0 | 0 | 70 | 38 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 16 | 34 | 68 | 25 | 6 | 0 | 31 | 0 | 0 | 0 | 280 | 280 | 220 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 44 | 42 | 0 | 0 | 32 | 12 | 88 | 36 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 52 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 16 | 3 | 0 | 0 | 0 | 0 | 98 | 0 | 118 | 0 | 22 | 17 | 6 | 366 | 59 | 0 | 17 | 0 | 52 | 17 | 110 | 17 | 37 | 25 | 340 | 53 | 0 | 0 | 72 | 0 | 0 | 0 | 108 | 12 | 230 | 17 | 0 | 482 | 2 | 825 | 0 | 0 | 0 |  | 926 | 0 | 215 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1070 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547 | 0 | 307 | 1268 | 0 | 0 |  | 7253 | 5640 | 12893 | 3682 | 926 | 1800 | 0 | 1377 | 4783 | 108 | 0 | 127 | 88 | 0 | 2 | 102.185 | 81.51
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 351 | 0 |  | 0 | 450 | 153 | 8 | 58 | 55 | 270 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 13 | 0 | 0 | 12 | 0 | 0 | 70 | 38 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 32 | 34 | 68 | 26 | 6 | 0 | 36 | 0 | 0 | 0 | 280 | 280 | 222 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 44 | 43 | 0 | 0 | 32 | 12 | 88 | 36 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 52 | 0 | 0 | 209 | 0 | 0 | 0 | 290 | 16 | 3 | 0 | 0 | 0 | 0 | 97 | 0 | 100 | 0 | 22 | 17 | 6 | 366 | 59 | 0 | 17 | 0 | 52 | 17 | 110 | 17 | 37 | 25 | 340 | 35 | 0 | 0 | 41 | 0 | 0 | 0 | 105 | 17 | 230 | 17 | 0 | 480 | 2 | 827 | 0 | 0 | 0 |  | 929 | 0 | 220 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 250 | 1277 | 0 | 0 |  | 7160 | 5487 | 12647 | 3684 | 929 | 1792 | 0 | 1233 | 4668 | 108 | 0 | 143 | 88 | 0 | 2 | 103.14 | 81.51
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 348 | 0 |  | 0 | 450 | 154 | 8 | 34 | 55 | 270 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 13 | 0 | 25 | 12 | 0 | 0 | 70 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 5 | 32 | 24 | 36 | 24 | 6 | 0 | 38 | 0 | 0 | 0 | 280 | 280 | 219 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 82 | 37 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 52 | 0 | 0 | 209 | 0 | 0 | 0 | 280 | 16 | 3 | 0 | 0 | 0 | 0 | 45 | 0 | 80 | 0 | 22 | 17 | 5 | 366 | 45 | 17 | 17 | 0 | 52 | 0 | 102 | 17 | 37 | 25 | 340 | 35 | 0 | 0 | 35 | 0 | 0 | 0 | 104 | 17 | 230 | 17 | 0 | 480 | 0 | 826 | 0 | 0 | 0 |  | 929 | 0 | 225 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 0 | 250 | 1257 | 0 | 0 |  | 6969 | 5244 | 12213 | 3711 | 929 | 1725 | 0 | 1010 | 4512 | 110 | 0 | 134 | 82 | 0 | 0 | 102.185 | 81.5
6:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 302 | 0 |  | 0 | 350 | 155 | 8 | 17 | 55 | 270 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 0 | 0 | 12 | 0 | 0 | 70 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 32 | 17 | 36 | 25 | 6 | 0 | 38 | 0 | 0 | 0 | 280 | 280 | 220 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 82 | 36 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 52 | 0 | 0 | 209 | 0 | 0 | 0 | 290 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 2 | 22 | 17 | 6 | 366 | 45 | 17 | 17 | 0 | 52 | 0 | 68 | 17 | 37 | 25 | 340 | 35 | 0 | 0 | 35 | 0 | 0 | 2 | 104 | 17 | 230 | 17 | 0 | 480 | 0 | 827 | 0 | 0 | 5 |  | 929 | 0 | 230 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 418 | 0 | 200 | 1157 | 2 | 0 |  | 6674 | 4804 | 11478 | 3645 | 929 | 1565 | 0 | 836 | 4167 | 110 | 0 | 127 | 82 | 17 | 0 | 97.41 | 81.5
7:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 302 | 0 |  | 0 | 350 | 150 | 8 | 17 | 55 | 270 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 0 | 0 | 12 | 0 | 0 | 70 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 24 | 17 | 0 | 25 | 6 | 0 | 36 | 0 | 0 | 0 | 280 | 280 | 164 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 45 | 43 | 0 | 0 | 32 | 12 | 70 | 36 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 62 | 0 | 0 | 209 | 0 | 0 | 0 | 270 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 3 | 22 | 17 | 0 | 366 | 45 | 17 | 17 | 2 | 52 | 0 | 68 | 17 | 38 | 25 | 340 | 35 | 0 | 0 | 35 | 0 | 0 | 5 | 104 | 17 | 230 | 17 | 0 | 480 | 0 | 825 | 0 | 0 | 18 |  | 928 | 0 | 235 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 600 | 180 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 380 | 4 | 190 | 1111 | 18 | 0 |  | 6550 | 4520 | 11070 | 3605 | 928 | 1518 | 0 | 779 | 3870 | 110 | 0 | 119 | 70 | 71 | 0 | 47.75 | 81.49
8:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 302 | 0 |  | 0 | 350 | 155 | 8 | 17 | 55 | 270 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 13 | 0 | 6 | 0 | 0 | 70 | 40 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 16 | 17 | 0 | 25 | 6 | 0 | 12 | 0 | 0 | 0 | 280 | 280 | 160 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 43 | 0 | 0 | 32 | 12 | 86 | 30 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 120 | 0 | 61 | 0 | 0 | 210 | 0 | 0 | 0 | 285 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 6 | 22 | 17 | 0 | 408 | 45 | 0 | 17 | 3 | 52 | 0 | 34 | 17 | 37 | 25 | 380 | 35 | 1 | 0 | 35 | 0 | 0 | 15 | 104 | 17 | 230 | 0 | 0 | 480 | 0 | 829 | 0 | 0 | 42 |  | 929 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 570 | 180 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 377 | 7 | 150 | 1068 | 35 | 0 |  | 6609 | 4435 | 11044 | 3697 | 929 | 1515 | 0 | 705 | 3769 | 110 | 0 | 96 | 86 | 137 | 0 | 58.255 | 81.49
9:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 350 | 0 |  | 0 | 380 | 152 | 8 | 17 | 55 | 270 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 14 | 0 | 10 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 1 | 16 | 17 | 0 | 25 | 6 | 0 | 2 | 0 | 0 | 0 | 315 | 360 | 190 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 43 | 0 | 0 | 32 | 0 | 58 | 30 | 0 | 0 | 1 | 40 | 28 | 53 | 42 | 163 | 0 | 62 | 0 | 0 | 209 | 0 | 0 | 0 | 315 | 16 | 3 | 0 | 0 | 0 | 0 | 20 | 0 | 53 | 8 | 22 | 17 | 0 | 365 | 59 | 52 | 51 | 3 | 52 | 0 | 34 | 17 | 38 | 25 | 360 | 35 | 4 | 0 | 35 | 0 | 0 | 17 | 60 | 24 | 230 | 0 | 0 | 481 | 0 | 824 | 0 | 0 | 41 |  | 929 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 650 | 180 | 0 | 0 | 3 | 64 | 0 | 0 | 0 | 376 | 16 | 150 | 1053 | 87 | 0 |  | 6896 | 4644 | 11540 | 3815 | 929 | 1653 | 0 | 799 | 3829 | 115 | 0 | 96 | 58 | 246 | 0 | 57.3 | 81.48
10:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 356 | 0 |  | 0 | 420 | 151 | 9 | 17 | 55 | 270 | 0 | 0 | 5 | 8 | 16 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 12 | 15 | 25 | 10 | 3 | 0 | 75 | 40 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 16 | 25 | 68 | 25 | 6 | 0 | 3 | 0 | 0 | 0 | 280 | 305 | 189 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 47 | 43 | 0 | 0 | 32 | 12 | 74 | 29 | 0 | 0 | 2 | 40 | 28 | 47 | 42 | 163 | 0 | 40 | 0 | 0 | 208 | 0 | 0 | 0 | 295 | 16 | 3 | 0 | 0 | 0 | 0 | 94 | 0 | 97 | 11 | 22 | 17 | 0 | 330 | 59 | 52 | 51 | 5 | 52 | 7 | 42 | 17 | 38 | 25 | 340 | 35 | 16 | 70 | 35 | 0 | 0 | 10 | 50 | 35 | 230 | 53 | 0 | 481 | 0 | 826 | 0 | 0 | 53 |  | 927 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 275 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 740 | 220 | 0 | 0 | 2 | 74 | 0 | 0 | 0 | 433 | 32 | 200 | 1156 | 158 | 0 |  | 7154 | 5159 | 12313 | 3717 | 927 | 1707 | 0 | 1072 | 4176 | 115 | 0 | 157 | 74 | 368 | 0 | 49.66 | 81.48
11:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 356 | 0 |  | 0 | 420 | 152 | 8 | 44 | 55 | 270 | 0 | 0 | 16 | 68 | 16 | 0 | 0 | 0 | 0 | 46 | 17 | 5 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 3 | 16 | 33 | 68 | 32 | 6 | 0 | 2 | 0 | 0 | 0 | 305 | 325 | 216 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 46 | 29 | 0 | 0 | 32 | 12 | 82 | 29 | 0 | 0 | 1 | 40 | 28 | 47 | 39 | 163 | 0 | 41 | 0 | 0 | 209 | 0 | 0 | 0 | 300 | 16 | 3 | 0 | 0 | 0 | 0 | 94 | 0 | 106 | 16 | 22 | 17 | 1 | 345 | 60 | 52 | 51 | 5 | 51 | 35 | 87 | 17 | 37 | 25 | 360 | 47 | 43 | 72 | 35 | 0 | 0 | 13 | 51 | 35 | 230 | 54 | 0 | 482 | 0 | 825 | 0 | 0 | 26 |  | 927 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 780 | 220 | 0 | 0 | 2 | 77 | 0 | 0 | 0 | 431 | 28 | 263 | 1172 | 124 | 0 |  | 7545 | 5201 | 12746 | 3840 | 927 | 1709 | 0 | 1317 | 4250 | 115 | 0 | 165 | 82 | 341 | 0 | 175.72 | 81.47
12:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 420 | 153 | 14 | 64 | 55 | 270 | 0 | 0 | 28 | 82 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 16 | 50 | 78 | 32 | 6 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 220 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 46 | 25 | 0 | 0 | 32 | 12 | 82 | 26 | 0 | 0 | 2 | 40 | 28 | 50 | 43 | 163 | 0 | 60 | 0 | 0 | 209 | 0 | 0 | 0 | 305 | 8 | 3 | 0 | 0 | 0 | 0 | 94 | 0 | 108 | 18 | 25 | 17 | 28 | 367 | 59 | 52 | 51 | 5 | 51 | 35 | 93 | 17 | 38 | 25 | 380 | 50 | 21 | 136 | 35 | 0 | 0 | 31 | 51 | 35 | 230 | 54 | 0 | 480 | 7 | 827 | 0 | 0 | 60 |  | 927 | 0 | 230 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 17 | 0 | 0 | 0 | 35 | 0 | 8 | 0 | 790 | 220 | 0 | 0 | 2 | 94 | 25 | 0 | 0 | 547 | 35 | 307 | 1285 | 194 | 0 |  | 7804 | 5699 | 13503 | 3823 | 927 | 1754 | 0 | 1610 | 4533 | 115 | 0 | 182 | 82 | 470 | 7 | 121.285 | 81.46
13:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 406 | 0 |  | 0 | 350 | 150 | 39 | 64 | 55 | 270 | 0 | 0 | 70 | 82 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 70 | 40 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 16 | 49 | 78 | 32 | 6 | 0 | 11 | 0 | 0 | 0 | 285 | 270 | 215 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 45 | 25 | 0 | 0 | 32 | 12 | 88 | 11 | 0 | 0 | 1 | 40 | 28 | 53 | 43 | 163 | 0 | 58 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 16 | 3 | 0 | 90 | 0 | 0 | 94 | 0 | 124 | 12 | 25 | 17 | 94 | 373 | 59 | 52 | 51 | 2 | 52 | 35 | 104 | 17 | 37 | 25 | 370 | 51 | 47 | 162 | 35 | 0 | 0 | 29 | 51 | 35 | 230 | 54 | 0 | 480 | 10 | 828 | 0 | 0 | 62 |  | 928 | 0 | 225 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 8 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 780 | 220 | 0 | 0 | 4 | 82 | 50 | 0 | 0 | 584 | 34 | 307 | 1264 | 181 | 0 |  | 8032 | 5641 | 13673 | 3792 | 928 | 1629 | 0 | 1937 | 4539 | 110 | 0 | 180 | 88 | 460 | 10 | 121.285 | 81.45
14:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 350 | 151 | 71 | 64 | 55 | 300 | 0 | 0 | 77 | 82 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 0 | 21 | 33 | 10 | 8 | 0 | 70 | 35 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 23 | 49 | 78 | 30 | 6 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 213 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 45 | 25 | 0 | 0 | 24 | 12 | 92 | 12 | 0 | 0 | 2 | 40 | 28 | 53 | 39 | 163 | 0 | 58 | 0 | 0 | 210 | 0 | 0 | 0 | 315 | 16 | 8 | 0 | 145 | 0 | 0 | 102 | 0 | 124 | 17 | 25 | 17 | 117 | 373 | 59 | 52 | 51 | 4 | 52 | 35 | 110 | 17 | 38 | 25 | 340 | 52 | 37 | 162 | 35 | 0 | 0 | 26 | 51 | 35 | 230 | 54 | 0 | 480 | 16 | 825 | 0 | 0 | 10 |  | 927 | 0 | 220 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 24 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 67 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 55 | 0 | 0 | 0 | 35 | 0 | 8 | 0 | 850 | 220 | 0 | 0 | 2 | 75 | 50 | 0 | 0 | 591 | 23 | 307 | 1257 | 134 | 0 |  | 8114 | 5712 | 13826 | 3762 | 927 | 1656 | 0 | 2136 | 4607 | 105 | 0 | 187 | 92 | 338 | 16 | 281 | 81.47
15:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 151 | 82 | 64 | 55 | 300 | 0 | 0 | 77 | 82 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 70 | 35 | 0 | 0 | 2 | 214 | 0 | 0 | 0 |  | 6 | 24 | 49 | 78 | 33 | 6 | 0 | 3 | 0 | 0 | 0 | 300 | 290 | 213 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 25 | 0 | 0 | 32 | 12 | 90 | 12 | 0 | 0 | 2 | 40 | 48 | 53 | 42 | 163 | 0 | 58 | 0 | 0 | 207 | 0 | 0 | 0 | 315 | 16 | 8 | 0 | 195 | 0 | 0 | 103 | 0 | 124 | 7 | 25 | 17 | 122 | 378 | 59 | 52 | 51 | 1 | 52 | 35 | 110 | 17 | 39 | 25 | 350 | 52 | 38 | 162 | 35 | 0 | 7 | 25 | 50 | 35 | 230 | 17 | 0 | 482 | 18 | 824 | 0 | 0 | 9 |  | 926 | 0 | 220 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 24 | 126 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 55 | 0 | 0 | 0 | 35 | 0 | 2 | 0 | 900 | 220 | 0 | 0 | 3 | 63 | 50 | 0 | 0 | 585 | 24 | 307 | 1370 | 109 | 0 |  | 8320 | 5839 | 14159 | 3853 | 926 | 1726 | 0 | 2248 | 4763 | 105 | 0 | 147 | 90 | 283 | 18 | 311 | 81.43
16:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 152 | 75 | 64 | 55 | 317 | 0 | 0 | 77 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 12 | 21 | 33 | 5 | 8 | 0 | 70 | 35 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 31 | 49 | 65 | 31 | 6 | 0 | 2 | 0 | 0 | 0 | 285 | 280 | 209 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 40 | 25 | 0 | 0 | 32 | 12 | 88 | 12 | 0 | 0 | 1 | 40 | 48 | 53 | 42 | 163 | 0 | 58 | 0 | 0 | 207 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 245 | 0 | 0 | 93 | 0 | 125 | 4 | 25 | 17 | 125 | 368 | 59 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 63 | 25 | 345 | 52 | 24 | 162 | 35 | 0 | 17 | 12 | 50 | 35 | 230 | 17 | 0 | 480 | 17 | 823 | 0 | 0 | 21 |  | 927 | 0 | 220 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 24 | 126 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 58 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 910 | 220 | 0 | 0 | 2 | 46 | 50 | 0 | 0 | 585 | 17 | 307 | 1368 | 100 | 0 |  | 8360 | 5818 | 14178 | 3824 | 927 | 1721 | 0 | 2313 | 4768 | 105 | 0 | 185 | 88 | 230 | 17 | 308 | 81.42
17:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 403 | 0 |  | 0 | 410 | 150 | 72 | 64 | 55 | 317 | 0 | 0 | 77 | 82 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 13 | 21 | 33 | 5 | 8 | 0 | 0 | 37 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 6 | 32 | 50 | 65 | 34 | 9 | 0 | 7 | 0 | 0 | 0 | 285 | 270 | 214 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 40 | 25 | 0 | 0 | 32 | 12 | 88 | 21 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 163 | 0 | 58 | 0 | 0 | 207 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 260 | 0 | 0 | 93 | 0 | 132 | 2 | 25 | 21 | 125 | 368 | 66 | 52 | 51 | 1 | 52 | 35 | 110 | 0 | 70 | 25 | 320 | 69 | 11 | 162 | 35 | 0 | 0 | 7 | 65 | 35 | 230 | 17 | 0 | 480 | 11 | 824 | 0 | 0 | 12 |  | 928 | 0 | 220 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 24 | 126 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 70 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 900 | 220 | 0 | 0 | 1 | 18 | 49 | 0 | 0 | 530 | 7 | 303 | 1309 | 46 | 0 |  | 8265 | 5628 | 13893 | 3807 | 928 | 1689 | 0 | 2351 | 4641 | 37 | 0 | 233 | 88 | 108 | 11 | 317 | 81.41
18:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 405 | 0 |  | 0 | 410 | 152 | 74 | 64 | 55 | 318 | 0 | 0 | 77 | 82 | 149 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 30 | 38 | 0 | 0 | 10 | 220 | 0 | 0 | 0 |  | 6 | 32 | 51 | 65 | 38 | 14 | 0 | 5 | 0 | 0 | 0 | 285 | 270 | 214 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 40 | 27 | 0 | 0 | 32 | 12 | 82 | 31 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 120 | 0 | 60 | 0 | 0 | 206 | 0 | 0 | 0 | 280 | 24 | 3 | 0 | 260 | 0 | 0 | 93 | 0 | 149 | 1 | 25 | 17 | 123 | 368 | 68 | 52 | 51 | 0 | 52 | 35 | 110 | 0 | 79 | 25 | 320 | 69 | 3 | 162 | 38 | 0 | 0 | 2 | 86 | 35 | 230 | 17 | 0 | 480 | 0 | 825 | 0 | 0 | 3 |  | 923 | 0 | 220 | 0 | 31 | 0 | 0 | 0 | 4 | 20 | 8 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 35 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 740 | 180 | 0 | 0 | 0 | 1 | 50 | 0 | 0 | 460 | 2 | 250 | 1272 | 11 | 0 |  | 8381 | 5150 | 13531 | 3787 | 923 | 1602 | 0 | 2348 | 4322 | 68 | 0 | 375 | 82 | 24 | 0 | 209 | 81.4
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 392 | 0 |  | 0 | 350 | 150 | 80 | 64 | 55 | 318 | 0 | 0 | 77 | 90 | 149 | 20 | 0 | 0 | 0 | 54 | 55 | 40 | 0 | 12 | 0 | 33 | 10 | 8 | 0 | 35 | 39 | 0 | 0 | 17 | 218 | 0 | 0 | 0 |  | 5 | 47 | 68 | 80 | 37 | 21 | 0 | 11 | 0 | 0 | 0 | 315 | 305 | 213 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 40 | 34 | 0 | 0 | 32 | 0 | 94 | 34 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 120 | 0 | 58 | 0 | 0 | 206 | 0 | 0 | 0 | 290 | 16 | 3 | 0 | 263 | 0 | 0 | 121 | 0 | 149 | 0 | 25 | 17 | 125 | 400 | 68 | 70 | 51 | 0 | 52 | 35 | 110 | 0 | 84 | 25 | 370 | 70 | 0 | 162 | 60 | 0 | 0 | 0 | 104 | 35 | 230 | 163 | 0 | 485 | 3 | 829 | 0 | 0 | 0 |  | 923 | 0 | 220 | 0 | 31 | 0 | 0 | 0 | 38 | 55 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 28 | 4 | 82 | 14 | 0 | 30 | 0 | 36 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 35 | 0 | 9 | 0 | 70 | 0 | 0 | 35 | 810 | 180 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 554 | 0 | 307 | 1423 | 0 | 0 |  | 8815 | 5832 | 14647 | 3878 | 923 | 1582 | 0 | 2650 | 4703 | 74 | 0 | 740 | 94 | 0 | 3 | 318 | 81.37
19:30 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 152 | 81 | 64 | 55 | 322 | 0 | 0 | 77 | 90 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 12 | 33 | 10 | 8 | 0 | 35 | 39 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 47 | 85 | 80 | 37 | 24 | 0 | 16 | 0 | 0 | 0 | 280 | 270 | 216 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 34 | 0 | 0 | 32 | 12 | 88 | 34 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 163 | 0 | 58 | 0 | 0 | 206 | 0 | 0 | 0 | 285 | 16 | 3 | 0 | 260 | 0 | 0 | 121 | 0 | 149 | 0 | 25 | 17 | 128 | 367 | 78 | 70 | 51 | 0 | 61 | 35 | 110 | 0 | 84 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 0 | 0 | 104 | 35 | 230 | 163 | 0 | 485 | 8 | 827 | 0 | 0 | 0 |  | 923 | 0 | 220 | 0 | 31 | 0 | 0 | 0 | 47 | 55 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 28 | 4 | 88 | 14 | 0 | 38 | 0 | 36 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 45 | 0 | 98 | 0 | 0 | 70 | 1080 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 602 | 0 | 307 | 1406 | 0 | 0 |  | 8881 | 6459 | 15340 | 3825 | 923 | 1826 | 0 | 2813 | 5002 | 74 | 0 | 781 | 88 | 0 | 8 | 368 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 152 | 81 | 64 | 55 | 322 | 0 | 0 | 77 | 90 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 21 | 33 | 10 | 8 | 0 | 35 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 47 | 85 | 80 | 37 | 19 | 0 | 16 | 0 | 0 | 0 | 285 | 270 | 216 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 43 | 0 | 0 | 32 | 12 | 76 | 34 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 163 | 0 | 59 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 16 | 3 | 0 | 260 | 0 | 0 | 121 | 0 | 149 | 0 | 25 | 17 | 128 | 367 | 78 | 70 | 51 | 0 | 50 | 35 | 110 | 0 | 85 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 0 | 0 | 103 | 35 | 230 | 163 | 0 | 485 | 11 | 826 | 0 | 0 | 0 |  | 782 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 41 | 56 | 8 | 126 | 10 | 16 | 0 | 0 | 0 | 30 | 4 | 88 | 14 | 0 | 48 | 0 | 36 | 0 | 0 | 8 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 52 | 0 | 107 | 0 | 0 | 70 | 1090 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 612 | 0 | 307 | 1406 | 0 | 0 |  | 8886 | 6361 | 15247 | 3840 | 782 | 1831 | 0 | 2823 | 5021 | 75 | 0 | 788 | 76 | 0 | 11 | 433 | 81.38
21:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 146 | 81 | 64 | 55 | 324 | 0 | 0 | 77 | 90 | 0 | 16 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 21 | 33 | 10 | 8 | 0 | 35 | 40 | 0 | 0 | 6 | 221 | 0 | 0 | 0 |  | 7 | 47 | 85 | 80 | 50 | 19 | 0 | 25 | 0 | 0 | 0 | 280 | 270 | 213 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 45 | 0 | 0 | 32 | 12 | 72 | 34 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 163 | 0 | 59 | 0 | 0 | 207 | 0 | 0 | 0 | 285 | 24 | 3 | 0 | 263 | 0 | 0 | 121 | 0 | 0 | 0 | 25 | 19 | 128 | 366 | 78 | 70 | 51 | 0 | 52 | 35 | 110 | 10 | 85 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 0 | 0 | 104 | 35 | 230 | 163 | 0 | 490 | 5 | 828 | 0 | 0 | 0 |  | 781 | 0 | 210 | 0 | 46 | 0 | 0 | 0 | 41 | 56 | 24 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 11 | 88 | 14 | 0 | 45 | 0 | 36 | 0 | 0 | 8 | 65 | 0 | 230 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 70 | 0 | 107 | 0 | 0 | 70 | 1180 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 607 | 0 | 307 | 1405 | 0 | 0 |  | 8637 | 6529 | 15166 | 3868 | 781 | 1829 | 0 | 2771 | 5112 | 75 | 0 | 653 | 72 | 0 | 5 | 510 | 81.37
22:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 405 | 0 |  | 0 | 420 | 150 | 81 | 64 | 55 | 321 | 0 | 0 | 77 | 90 | 10 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 33 | 10 | 8 | 0 | 35 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 10 | 48 | 85 | 80 | 62 | 19 | 0 | 30 | 0 | 0 | 0 | 290 | 280 | 210 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 12 | 72 | 34 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 163 | 0 | 55 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 24 | 3 | 0 | 260 | 0 | 0 | 121 | 0 | 0 | 0 | 25 | 17 | 133 | 370 | 78 | 70 | 51 | 0 | 52 | 35 | 110 | 17 | 85 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 8 | 0 | 103 | 35 | 230 | 17 | 0 | 495 | 0 | 828 | 0 | 0 | 0 |  | 781 | 0 | 205 | 0 | 47 | 0 | 0 | 0 | 41 | 46 | 24 | 126 | 10 | 16 | 0 | 0 | 0 | 39 | 11 | 88 | 14 | 0 | 35 | 0 | 36 | 0 | 0 | 8 | 65 | 0 | 210 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 70 | 0 | 107 | 0 | 0 | 70 | 1240 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 613 | 0 | 307 | 1420 | 0 | 0 |  | 8537 | 6580 | 15117 | 3893 | 781 | 1843 | 0 | 2778 | 5178 | 75 | 0 | 497 | 72 | 0 | 0 | 652.265 | 81.36
23:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 151 | 81 | 64 | 55 | 327 | 0 | 0 | 77 | 90 | 148 | 0 | 0 | 0 | 0 | 54 | 50 | 35 | 0 | 13 | 22 | 33 | 10 | 8 | 0 | 35 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 9 | 48 | 85 | 80 | 62 | 19 | 0 | 34 | 0 | 0 | 0 | 280 | 280 | 198 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 42 | 51 | 0 | 0 | 32 | 12 | 90 | 35 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 163 | 0 | 51 | 0 | 0 | 208 | 0 | 0 | 0 | 315 | 24 | 3 | 0 | 260 | 0 | 0 | 121 | 0 | 0 | 0 | 25 | 17 | 128 | 366 | 68 | 70 | 17 | 0 | 52 | 35 | 110 | 17 | 79 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 17 | 0 | 81 | 35 | 230 | 17 | 0 | 492 | 35 | 828 | 0 | 0 | 0 |  | 781 | 0 | 190 | 0 | 44 | 0 | 0 | 0 | 41 | 44 | 24 | 130 | 10 | 45 | 0 | 0 | 0 | 38 | 11 | 86 | 35 | 0 | 35 | 0 | 36 | 0 | 0 | 8 | 65 | 0 | 210 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 58 | 0 | 77 | 0 | 107 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 610 | 0 | 307 | 1422 | 0 | 0 |  | 8646 | 6605 | 15251 | 3859 | 781 | 1809 | 0 | 2793 | 5178 | 75 | 0 | 631 | 90 | 0 | 35 | 696.195 | 81.35
24:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 151 | 81 | 68 | 55 | 327 | 0 | 0 | 77 | 90 | 95 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 13 | 22 | 33 | 11 | 0 | 0 | 35 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 48 | 85 | 80 | 63 | 6 | 0 | 35 | 0 | 0 | 0 | 280 | 250 | 198 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 12 | 90 | 35 | 0 | 0 | 0 | 40 | 48 | 53 | 42 | 163 | 0 | 51 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 24 | 3 | 0 | 260 | 0 | 0 | 121 | 0 | 0 | 0 | 25 | 17 | 130 | 366 | 68 | 35 | 17 | 0 | 52 | 35 | 110 | 34 | 77 | 25 | 345 | 71 | 0 | 162 | 72 | 0 | 17 | 0 | 69 | 35 | 230 | 17 | 0 | 490 | 17 | 827 | 0 | 0 | 0 |  | 781 | 0 | 190 | 0 | 48 | 0 | 0 | 0 | 21 | 40 | 24 | 130 | 9 | 48 | 0 | 0 | 0 | 38 | 11 | 86 | 35 | 0 | 35 | 0 | 36 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 108 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 611 | 0 | 307 | 1417 | 0 | 0 |  | 8465 | 6661 | 15126 | 3831 | 781 | 1784 | 0 | 2805 | 5190 | 75 | 0 | 553 | 90 | 0 | 17 | 786.92 | 81.34
KWH | 0 | 0 | 0 | 4221000 | 0 | 0 | 0 | 9043200 | 0 |  | 0 | 9384500 | 3601047 | 1073280 | 1179799 | 1324582 | 7081285 | 0 | 0 | 1029178 | 1311552 | 1026240 | 68089 | 0 | 0 | 0 | 840600 | 670167 | 671219 | 0 | 263400 | 336600 | 555000 | 224200 | 117600 | 0 | 1426375 | 936000 | 0 | 0 | 68407 | 5175487 | 0 | 0 | 0 |  | 122160 | 790752 | 1150519 | 1395240 | 834240 | 229440 | 0 | 457440 | 0 | 0 | 0 | 7374400 | 6896000 | 5079000 | 100364 | 0 | 0 | 0 | 0 | 1163161 | 0 | 1060256 | 904930 | 0 | 0 | 756500 | 266400 | 2009280 | 662400 | 0 | 0 | 13850 | 948000 | 860880 | 1252200 | 1014336 | 3596154 | 0 | 1322880 | 0 | 0 | 5180560 | 0 | 0 | 0 | 7216500 | 419112 | 92544 | 0 | 2983309 | 0 | 0 | 2078400 | 0 | 2307888 | 95985 | 575040 | 424800 | 1742981 | 8834000 | 1467600 | 945600 | 907454 | 29281 | 1272109 | 646271 | 2348499 | 347700 | 1299480 | 597120 | 8304200 | 1282560 | 264310 | 2312640 | 1188055 | 0 | 83160 | 187308 | 1965120 | 703080 | 5674300 | 938400 | 0 | 11612726 | 128640 | 19934545 | 0 | 0 | 407936 |  | 21499636 | 0 | 5486112 | 0 | 781440 | 0 | 0 | 0 | 237600 | 336512 | 253875 | 2978000 | 218789 | 430848 | 0 | 0 | 0 | 242949 | 48245 | 615472 | 110570 | 0 | 217353 | 0 | 266440 | 0 | 0 | 49770 | 1495418 | 0 | 5519000 | 0 | 0 | 3895400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8072581 | 1247520 | 0 | 450912 | 0 | 870432 | 0 | 46144 | 469824 | 24130800 | 5176255 | 0 | 0 | 27060 | 642240 | 968064 | 0 | 0 | 13403640 | 228466 | 6480000 | 30861206 | 1139690 | 0 |  | 188688802 | 138898263 | 327587065 | 91980630 | 21499636 | 41253327 | 0 | 44902834 | 113437335 | 2362375 | 0 | 6930738 | 2009280 | 3082270 | 128640 | 0
Fuel Cost | 0 | 0 | 0 | 18783450 | 0 | 0 | 0 | 26044416 | 0 |  | 0 | 29842710 | 12315580.74 | 21208012.8 | 22062241.3 | 23339134.84 | 21597919.25 | 0 | 0 | 20336557.28 | 23542358.4 | 19929580.8 | 1269859.85 | 0 | 0 | 0 | 15349356 | 10561831.92 | 12276595.51 | 0 | 197550 | 0 | 0 | 0 | 2106216 | 0 | 0 | 0 | 0 | 0 | 1295628.58 | 16509803.53 | 0 | 0 | 0 |  | 2148794.4 | 13925142.72 | 20605795.29 | 26593274.4 | 16326076.8 | 3776582.4 | 0 | 0 | 0 | 0 | 0 | 20574576 | 21101760 | 16862280 | 336219.4 | 0 | 0 | 0 | 0 | 4664275.61 | 0 | 18989184.96 | 16343035.8 | 0 | 0 | 2814180 | 199800 | 13180876.8 | 2060064 | 0 | 0 | 0 | 3697200 | 3211082.4 | 5697510 | 4615228.8 | 12298846.68 | 0 | 7341984 | 0 | 0 | 14453762.4 | 0 | 0 | 0 | 22298985 | 314334 | 70333.44 | 0 | 60859503.6 | 0 | 0 | 39926064 | 0 | 40641907.68 | 0 | 10241462.4 | 7370280 | 28898624.98 | 23410100 | 27972456 | 17739456 | 16279724.76 | 0 | 20798982.15 | 12563508.24 | 42132072.06 | 6644547 | 25222906.8 | 10634707.2 | 22089172 | 21893299.2 | 0 | 42298185.6 | 19935562.9 | 0 | 1486069.2 | 0 | 35411462.4 | 11910175.2 | 16852671 | 13212672 | 0 | 80940700.22 | 0 | 117613815.5 | 0 | 0 | 0 |  | 60413977.16 | 0 | 16184030.4 | 0 | 13557984 | 0 | 0 | 0 | 4469256 | 6329790.72 | 4518975 | 9410480 | 1037059.86 | 7427819.52 | 0 | 0 | 0 | 4351216.59 | 885295.75 | 10346084.32 | 2352929.6 | 0 | 3892792.23 | 0 | 4771940.4 | 0 | 0 | 37675.89 | 16494460.54 | 0 | 46580360 | 0 | 0 | 12854820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23571936.52 | 21307641.6 | 0 | 8937075.84 | 0 | 17339005.44 | 0 | 0 | 9321308.16 | 156367584 | 16098153.05 | 0 | 0 | 0 | 0 | 16795910.4 | 0 | 0 | 97846572 | 0 | 48276000 | 203992571.66 | 0 | 0 |  | 1348050076.19 | 845770706.65 | 2193820782.84 | 276673444.31 | 60413977.16 | 132776505.66 | 0 | 820955163.21 | 768112063.92 | 0 | 0 | 121708751.78 | 13180876.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 420 | 153 | 14 | 64 | 55 | 270 | 0 | 0 | 28 | 82 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 12 | 21 | 33 | 10 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 16 | 50 | 78 | 32 | 6 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 220 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 46 | 25 | 0 | 0 | 32 | 12 | 82 | 26 | 0 | 0 | 2 | 40 | 28 | 50 | 43 | 163 | 0 | 60 | 0 | 0 | 209 | 0 | 0 | 0 | 305 | 8 | 3 | 0 | 0 | 0 | 0 | 94 | 0 | 108 | 18 | 25 | 17 | 28 | 367 | 59 | 52 | 51 | 5 | 51 | 35 | 93 | 17 | 38 | 25 | 380 | 50 | 21 | 136 | 35 | 0 | 0 | 31 | 51 | 35 | 230 | 54 | 0 | 480 | 7 | 827 | 0 | 0 | 60 |  | 927 | 0 | 230 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 230 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 17 | 0 | 0 | 0 | 35 | 0 | 8 | 0 | 790 | 220 | 0 | 0 | 2 | 94 | 25 | 0 | 0 | 547 | 35 | 307 | 1285 | 194 | 0 |  | 13503 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 152 | 81 | 64 | 55 | 322 | 0 | 0 | 77 | 90 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 12 | 33 | 10 | 8 | 0 | 35 | 39 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 6 | 47 | 85 | 80 | 37 | 24 | 0 | 16 | 0 | 0 | 0 | 280 | 270 | 216 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 41 | 34 | 0 | 0 | 32 | 12 | 88 | 34 | 0 | 0 | 0 | 40 | 28 | 53 | 42 | 163 | 0 | 58 | 0 | 0 | 206 | 0 | 0 | 0 | 285 | 16 | 3 | 0 | 260 | 0 | 0 | 121 | 0 | 149 | 0 | 25 | 17 | 128 | 367 | 78 | 70 | 51 | 0 | 61 | 35 | 110 | 0 | 84 | 25 | 345 | 70 | 0 | 162 | 72 | 0 | 0 | 0 | 104 | 35 | 230 | 163 | 0 | 485 | 8 | 827 | 0 | 0 | 0 |  | 923 | 0 | 220 | 0 | 31 | 0 | 0 | 0 | 47 | 55 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 28 | 4 | 88 | 14 | 0 | 38 | 0 | 36 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 45 | 0 | 98 | 0 | 0 | 70 | 1080 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 602 | 0 | 307 | 1406 | 0 | 0 |  | 15340 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 420 | 150 | 75 | 64 | 55 | 310 | 0 | 0 | 80 | 90 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 12 | 21 | 33 | 12 | 8 | 0 | 30 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 64 | 85 | 80 | 38 | 18 | 0 | 20 | 0 | 0 | 0 | 280 | 280 | 220 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 46 | 34 | 0 | 0 | 32 | 12 | 151 | 40 | 0 | 0 | 0 | 40 | 28 | 53 | 43 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 22 | 8 | 0 | 270 | 0 | 0 | 120 | 0 | 132 | 0 | 25 | 17 | 130 | 380 | 80 | 88 | 51 | 0 | 52 | 35 | 110 | 17 | 84 | 25 | 360 | 70 | 0 | 162 | 72 | 0 | 17 | 0 | 115 | 35 | 260 | 163 | 0 | 490 | 40 | 820 | 0 | 0 |  |  | 801 | 0 | 220 | 0 | 80 | 0 | 0 | 0 | 50 | 66 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 25 | 90 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 307 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 420 | 150 | 50 | 64 | 55 | 290 | 0 | 0 | 80 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 0 | 12 | 21 | 33 | 12 | 8 | 0 | 30 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 32 | 50 | 70 | 30 | 6 | 0 | 5 | 0 | 0 |  | 280 | 280 | 200 | 8 | 0 | 0 | 0 | 0 | 43 | 0 | 45 | 25 | 0 | 0 | 32 | 12 | 146 | 30 | 0 | 0 | 1.6 | 40 | 28 | 53 | 40 | 163 | 0 | 56 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 22 | 8 | 0 | 150 | 0 | 0 | 90 | 0 | 115 | 20 | 25 | 17 | 70 | 350 | 60 | 52 | 51 | 5 | 52 | 35 | 85 | 17 | 37 | 24 | 350 | 50 | 50 | 162 | 35 | 0 | 17 | 35 | 50 | 17 | 230 | 54 | 0 | 490 | 40 | 820 | 0 | 0 | 70 |  | 943 | 0 | 210 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 53 | 0 | 94 | 0 | 70 | 0 | 8 | 113 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 307 | 1200 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 420 | 152 | 17 | 17 | 55 | 250 | 0 | 0 | 17 | 24 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 12 | 0 | 33 | 11 | 8 | 0 | 30 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 6 | 48 | 51 | 62 | 25 | 6 | 0 | 20 | 0 | 0 | 0 | 280 | 280 | 195 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 43 | 34 | 0 | 0 | 32 | 12 | 70 | 28 | 0 | 0 | 1 | 40 | 48 | 53 | 42 | 120 | 0 | 40 | 0 | 0 | 207 | 0 | 0 | 0 | 280 | 22 | 8 | 0 | 0 | 0 | 0 | 92 | 0 | 17 | 2 | 25 | 17 | 10 | 305 | 59 | 17 | 17 | 1 | 52 | 35 | 51 | 17 | 37 | 25 | 310 | 53 | 22 | 35 | 17 | 0 | 0 | 14 | 83 | 17 | 230 | 17 | 0 | 490 | 3 | 828 | 0 | 0 | 33 | 0 | 928 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 790 | 220 | 0 | 0 | 0 | 26 | 35 | 0 | 0 | 418 | 15 | 250 | 1010 | 94 | 0 | 0 |  |  |  | 133233957 | 21499636 | 0 | 113437335 | 51833572 | 2009280 | 3082270 | 128640 | 2362375 |  |  | 327587065
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [8 empty] | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 133.234 | 21.4996 | 0 | 113.4373 | 51.8336 | 2.0093 | 3.0823 | 0.12864 | 2.3624
| Minimum Generation |  | 11044 | 8:00
| Highest Generation |  | 15340 | 19:30 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 327.5871
| Day Peak Generation |  | 13503 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15340 | 19:30 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 929 | 4:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 923 | 19:30
| Load factor L.F |  | 88.98% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-07
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13503 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 11850
Evening Peak Generation : |  |  | 15340 | MW Hour : | 19:30 | Available Max Generation : |  | 16114
E.P. Demand (at gen end) : |  |  | 15725 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 15340 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1114
Total Gen. (MKWH) : |  |  | 327.5871 | System Load Factor : | 88.98% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 574 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-07
Actual : |  | 81.28 | Ft.(MSL) , | Rule curve : | 77.56 | Ft.( MSL )
Gas Consumed : |  | Total = | 979.59 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 409449949.97
: |  |  | Coal : | 768112063.92 | Oil : | 942663914.99 | Total : | 2120225928.88
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 83 | 1992:00 | 5277.8352 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1454.5136 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2038.779 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1773.2563 |  |  | 0 | 0%
Cumilla Area |  | 125 | 3000:00 | 1458.4679 |  |  | 0 | 0%
Mymensingh Area |  | 160 | 3840:00 | 1085.3681 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 607.7026 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 507.0683 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 991.7224 |  |  | 0 | 0%
Total |  | 368 |  | 15194.7134 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:21 | 9:37 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For Transformer Bay Maintenance
8:21 | 9:37 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For Transformer Bay Maintenance
8:25 | 12:59 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Project Work S/D Due to P/W
8:26 | 12:58 | Niamatpur 132/33kV S/S Transformer-3(426T) HT Project Work S/D Due to P/W
8:34 | 11:36 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Scheduled S/D Due to Kalai Feder Maintenance |  |  |  |  | 15.0MW load interrup.
8:35 | 11:36 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Scheduled S/D |  |  |  |  | 15.0MW load interrup.
8:36 | 9:58 | Daudkandi 132/33kV S/S Transformer-3 LT Forced S/D Due to Taken by pbs-3 for Red Hot maintanence
8:37 | 9:56 | Daudkandi 132/33kV S/S Transformer-3 HT Forced S/D Due to Taken by pbs-3 for Red Hot maintanence
9:09 | 17:26 | Patuakhali-Payra 132kV Ckt-1 Project Work S/D from Payra 400/132/33kV end Due to Project work and from Patuakhali 132/33kV
end Due to Payra Grid working.
9:32 | 21:28 | Khulna(S) 230/132kV S/S 230 KV Main Bus 2 Project Work S/D
- | 10:02 | Gopalganj(N)-Madaripur 132kV Ckt-1 is restored.
10:21 | 11:19 | Shikalbaha 230/132kV S/S Intermediate-2 Tripped showing FN1&FN relays.
- | 10:30 | Saidpur 132/33kV S/S TR-5 (434T) HT is restored.
- | 10:36 | Saidpur 132/33kV S/S TR-5 (434T) LT is restored.
- | 10:56 | Chandpur 132/33kV S/S 402T HT is restored.
- | 10:58 | Chandpur 132/33kV S/S 402T LT is restored.
12:00 | - | Day peak gen. 13503 MW.
- | 13:35 | Dohazari-Sikalbaha 132 kV Ckt-1 is restored.
13:36 | 14:27 | Dohazari-Sikalbaha 132 kV Ckt-2 Project Work S/D from Dohazari 132/33kV end Due to SD taken by Shikalbaha Grid and from
Shikalbaha 230/132kV end.
- | 17:27 | Patuakhali-Payra 132kV Ckt-1 is restored.
17:32 | 17:49 | Bogura 230/132kV S/S 230KV Main 2 Project Work S/D Due to Bogura(W) ckt1&2 commissioning .
18:40 | - | Charged 230 KV Line bay (Bogura West ckt -1 and ckt-2) at Bogura South 230/132 KV sub station. [ckt-2 charged at 18:29 hrs
and ckt-1 at 18:31 hrs].
19:21 | 19:43 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Tripped showing Lock realy k862 Trip relays Due to Special O/C Protection |  |  |  |  | 75.0MW load interrup.
Operated from hathazari Grid.
19:30 | - | Evening Peak Generation :15340 MW
20:04 | 20:18 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Tripped showing Earth Fault Relay relays Due to due to 33 kv Zinzira ckt-3 feeder |  |  |  |  | 28.0MW load interrup.
of DPBS-4 fault.
20:04 | 20:18 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Tripped showing Earth fault relay relays Due to due to 33 kv Zinzira ckt-3 feeder of |  |  |  |  | 28.0MW load interrup.
DPBS-4 fault.
- | 21:12 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt is restored.
3:27 | - | Savar 132/33kV S/S Bus-B Scheduled S/D Due to For T-4 Transformer installation work by CCCE.
3:27 | - | Savar 132/33kV S/S Bus-A Scheduled S/D Due to For T-4 Transformer installation work by CCCE.
3:30 | - | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to For T-4 Transformer installation work by CCCE. |  |  |  |  | 75.0MW load interrup.
3:30 | - | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to For T-4 Transformer installation work by CCCE. |  |  |  |  | 75.0MW load interrup.
3:30 | - | Savar 132/33kV S/S Transfer Bus Scheduled S/D Due to For T-4 Transformer installation work by CCCE.
3:30 | - | Savar 132/33kV S/S Main Bus Scheduled S/D Due to For T-4 Transformer installation work by CCCE.
5:34 | - | Cumilla(S)-Kachua 132 kV Ckt-1 Project Work S/D from Cumilla(N) 230/132/33kV end Due to 132KV Kachua-Laksham
Transmission line Conductor Stringing.
5:35 | - | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 132/33kV end.
5:44 | - | Baghabari-Sirajganj 230 kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to Rooppur Project work. and from
Sirajgonj 230 end Due to Ruppur project work.
5:44 | - | Baghabari-Sirajganj 230 kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to Rooppur Project work. and from
Sirajgonj 230 end Due to Ruppur Project Work.
5:51 | - | Cumilla(S)-Kachua 132 kV Ckt-1 Project Work S/D from Cumilla(S) 132/33kV end. and from Kachua 132/33kVend.
6:05 | - | Rangpur 132/33kV S/S T-1(414T) HT Scheduled S/D |  |  |  |  | 50.0MW load interrup.
6:06 | - | Rangpur 132/33kV S/S T-1(414T) LT Scheduled S/D |  |  |  |  | 50.0MW load interrup.
6:07 | - | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D |  |  |  |  | 50.0MW load interrup.
6:08 | - | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D |  |  |  |  | 50.0MW load interrup.
6:08 | - | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Redhot maintenance
6:09 | - | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D
6:36 | - | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end.
6:42 | - | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to High temperature maintenance work 33 KV TR-2 bus DS R phase. |  |  |  |  | 70.0MW load interrup.
6:43 | - | Kurigram-Rangpur 132kV Ckt-1 Project Work S/D from Rangpur 132/33kV end. and from Kurigram 132/33kV end Due to |  |  |  |  | 50.0MW load interrup. Rangpur 132/33kV
|  | Rangpur-Kurigram 132kV ckt-1 development work. |  |  |  |  | end and 35.0MW load interrup. at
Kurigram 132/33kV end
6:52 | - | Shahmirpur-Sikalbaha 132kV Ckt-2 Scheduled S/D from Shikalbaha 230/132kV end.
7:00 | - | Minimum generation 12331 MW
7:03 | - | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 33KV Bus-01 s/D taken by BPDB for 33/11 KV new GIS Substation |  |  |  |  | 10.0MW load interrup.
Incomer work.
7:03 | - | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to 33KV Bus -01 S/D taken by BPDB for 33/11KV New GIS Substation |  |  |  |  | 10.0MW load interrup.
Inconer work.
7:13 | - | Dohazari-Sikalbaha 132 kV Ckt-2 Project Work S/D from Shikalbaha 230/132kV end.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4221000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 404 | 9043200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9384500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 81 | 1073280 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3601047 | GT-1 Under Maint
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 64 | 1179799 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1324582
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 68089 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 77 | 1029178 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7081285
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 1311552 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 840600
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1026240
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 670167
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 671219
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 24 | 600000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 555000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 10 | 224200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 117600 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 2983309 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2307888
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 945600 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 70 | 1282560 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2312640
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 187308
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 703080 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under maint.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5332 | 3004 | 54744923
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 68407 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 95985
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 229440 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 74 | 2362375 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5175487
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 907454 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 47 | 790752 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1150519 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 80 | 1395240 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 575040 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 457440
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 834240 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29281
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 61 | 1272109 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 646271 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2348499
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 597120 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 72 | 1188055 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 938400
60 | SS Power I |  | SS Power | 2*612 | 1224 | 485 | 11612726
| Cox's Bazar Wind |  | IPP | 66 | 60 | 8 | 128640 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 827 | 19934545
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 407936
| Chattogram area Total |  |  |  | 4404 | 2445 | 53145961
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 216 | 5079000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7374400
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6896000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5674300 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 100364 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1163161
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 128 | 1742981 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 1060256 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 424800 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 88 | 2009280
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 756500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 904930 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 266400 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 347700 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 84 | 1299480 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 83160 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 104 | 1965120 | Engine problem
| Cumilla Area Total |  |  |  | 2929 | 1587 | 37147832
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 34 | 662400 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13850
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 121 | 2078400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1467600 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 264310
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 122160 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 239 | 4608720
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 948000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 860880 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3596154
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1252200
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 42 | 1014336 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 92544 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 58 | 1322880
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 206 | 5180560 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 419112 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7216500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8834000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8304200 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1606 | 39041366
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 923 | 21499636
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 31 | 781440 | Low demand
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 47 | 237600
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 55 | 336512 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 220 | 5486112 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 8 | 253875 | Low demand
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 1247520 | Low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 642240
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 602 | 13403640 | Unit -1 under maint.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 1921 | 43888575
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 430848 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 218789
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2978000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1080 | 24130800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5176255
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6480000
| Barisal Area Total |  |  |  | 2235 | 1763 | 39414692
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 242949 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 48245 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 14 | 110570 | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 217353 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 140 | 3895400 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8072581
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 266440 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 49770 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 615472 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 450912 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 469824 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27060
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1406 | 30861206
| Rajshahi Area Total |  |  |  | 3431 | 2288 | 45327782
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 65 | 1495418
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 230 | 5519000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 870432 | Fuel shortage
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46144
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 968064 | Fuel shortage
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 228466
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1139690
| Rangpur Area Total |  |  |  | 950 | 487 | 10267214
| Total |  |  |  | 25903 | 15340 | 327587065
| Eastern Grid Total |  |  |  | 15588 | 8881 | 188688802
| Western Grid Total |  |  |  | 10315 | 6459 | 138898263
| National Grid Total |  |  |  | 25903 | 15340 | 327587065
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-06-06
(a) ENTIRE EASTERN GRID: |  | 9872.83 | MW | (b) ENTIRE WESTERN GRID: |  | 4868.8 | MW
i) Dhaka area |  | 5572.23 | MW | i) Khulna area |  | 1916.9 | MW
ii) Chattogram area |  | 1429.6 | MW | ii) Barishal area |  | 460.5 | MW
iii) Cumilla area |  | 1306 | MW | iii) Rajshahi area |  | 1504.4 | MW
iv) Mymensingh area |  | 995 | MW | iv) Rangpur area |  | 987 | MW
v) Sylhet area |  | 570 | MW
System Total Demand at Evening Peak Hour (a + b) = |  |  |  | 14741.63 | MW
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | KSRM | 27 | 03:00 | Satkhira | 149 | 01:00
AKSML | 98 | 05:00 | Kabirpur | 289 | 19:30 | Satmasjid | 126 | 00:00
Aftabnagar | 44 | 00:00 | Kachua | 85 | 19:00 | Savar | 211 | 19:30
Agargaon | 113 | 15:00 | Kallyanpur | 126 | 00:00 | SevenRings | 20.4 | 12:00
Agrabad | 88 | 14:00 | Kalurghat | 37 | 18:00 | ShahCement | 32 | 03:00
Amnura | 73 | 01:00 | Kamrangirchar | 56.6 | 17:00 | Shahjadpur | 91 | 20:00
Ashuganj | 87 | 23:00 | Kaptai | N/A | N/A | Shahjibazar | 136 | 23:00
BIPTC | N/A | N/A | Kazla | 116 | 13:00 | Shahmirpur | 54 | 01:00
BSRM | 190 | 17:00 | Keranigonj | 91 | 22:00 | Shariatpur | 96 | 00:00
Bagerhat | 101 | 00:00 | Khagrachori | 36 | 19:30 | Sherpur | 124 | 00:00
Bakulia | 113 | 19:30 | Khulna | 96 | 19:30 | Shikalbaha | 26 | 00:00
Banani | 66.4 | 15:00 | Khulshi | 197 | 21:00 | Shikalbaha-230 | N/A | N/A
Bangabhaban | 19 | 10:00 | Kishoreganj | 132 | 02:00 | Shitalakhya | 110.6 | 15:00
Barapukuria | 66 | 22:00 | Kodda | 255 | 08:00 | Sholosohor | 50 | 15:00
Barguna | 24 | 00:00 | Kulaura | 52 | 19:00 | Shyampur | 180 | 13:00
Barishal | 125 | 23:00 | Kurigram | 70 | 00:00 | Siddhirganj | 126 | 00:00
Barishal-230 | 110 | 23:00 | Kushtia | 166 | 19:30 | Sirajganj | 112 | 22:00
Baroaulia | 77 | 00:00 | Lalbag | 104 | 18:30 | Sonargaon | 123 | 21:00
Baroirhat | 61 | 23:00 | Lalmonirhat | 65 | 00:00 | Sreemongol | 71 | 23:00
Bashundhara | 202 | 19:00 | MI_Cement | 10.7 | 11:00 | Sreepur | 66 | 18:30
BashundharaCement | 6 | 04:00 | Madanganj | 27 | 00:00 | Srinagar | 52 | 22:00
Beanibazar | 72 | 19:00 | Madaripur | 135 | 23:00 | Sunamganj | 53 | 19:00
Benapole | 74 | 19:30 | Madartek | 99.35 | 00:00 | Sylhet | 42 | 19:30
Bhaluka | 142 | 12:00 | Madunaghat | 60 | 19:00 | Sylhet-132 | 110 | 14:00
Bhandaria | 51 | 01:00 | Magura | 75 | 23:00 | TK | 64 | 02:00
Bhangura | 40 | 20:00 | Mahasthangarh | 86 | 00:00 | Tangail | 178 | 18:30
Bheramara(GK) | 74 | 00:00 | Manikganj | 135 | 20:00 | Thakurgaon | 108 | 20:00
Bhulta | 252 | 10:00 | Maniknagar | 86 | 13:00 | Tongi | 146 | 15:00
Bog-Sherpur | 66 | 20:00 | Matarbari | 52 | 21:00 | Ullahpara | 26 | 19:30
Bogura | 174 | 00:00 | Matuail | 80 | 17:00 | Ullon | 55 | 00:00
Borhanuddin | 87 | 22:00 | Millgate | 127 | 17:00 | Uttara | 76 | 16:00
Brahmanbaria | 185 | 23:00 | Mirpur | 159 | 00:00 | UttaraNew | 35 | 00:00
Cantonment | 154 | 00:00 | Mirsorai | 5 | 13:00 | Zigatola | 100 | 19:00
Chandpur | 78 | 19:00 | Mirzapur | 38 | 13:00
Chandraghona | 39 | 19:30 | Mithapukur | 58 | 20:00
Chapai | 78 | 01:00 | Modern | 0 | 00:00
Charsaidpur | 47 | 13:00 | Mogbazar | 143.2 | 16:00
Chauddagram | 78 | 19:00 | Mongla | 46 | 01:00
Chhatak | 28 | 19:00 | Motijheel | 48 | 17:00
Chowmuhani | 197 | 22:00 | Munshiganj | 124 | 00:00
Chuadanga | 121 | 01:00 | Mymensingh | 232 | 19:00
Coxsbazar | 135 | 19:30 | Naogaon | 141 | 23:00
Cumilla(N) | 203 | 22:00 | Narail | 66 | 20:00
Cumilla(S) | 179 | 19:00 | Narinda | 47.5 | 17:00
Daudkandi | 164 | 00:00 | Narshingdi | 170 | 22:00
Dhaka | 48 | 12:00 | Natore | 144 | 22:00
Dhamrai | 134 | 16:00 | Nawabganj | 55 | 22:00
Dhanmondi | 166 | 13:00 | Netrakona | 130 | 02:00
Dohazari | 102 | 21:00 | New | 58 | 15:00
Faridpur | 187 | 23:00 | Niamatpur | 82 | 23:00
Fatullah | 76 | 16:00 | Noapara | 55 | 00:00
Fenchuganj | 44 | 21:00 | PHP | 5 | 02:00
Feni | 108 | 00:00 | Pabna | 135 | 21:00
GPH | 98 | 05:00 | Palashbari | 130 | 00:00
Ghatail | 66 | 19:30 | Panchagarh | 60 | 20:00
Ghorashal | 44 | 12:00 | Patuakhali | 98 | 22:00
Goalpara | 40 | 01:00 | Payra | 26 | 22:00
Gollamari | 90 | 00:00 | Postogola | 66 | 00:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 378 | 07:00 | 363 | 00:00 | Kaliakoir | 355 | 01:00 | 348 | 09:00
| Ashuganj | 395 | 6:29 | 376 | 11:14 | Madunaghat_I | 412 | 00:00 | 410 | 04:00
| Bhulta | 400 | 02:00 | 377 | 12:00 | Meghnaghat | 371 | 07:00 | 356 | 12:00
| Bibiana | 392 | 18:30 | 384 | 10:00 | Payra | 408 | 07:00 | 398 | 23:00
| BIPTC | 404 | 21:00 | 387 | 15:00 | Rahanpur | 403 | 07:00 | 384 | 22:00
| Bogura | 398 | 07:00 | 375 | 19:30 | Rampal | 394 | 07:00 | 379 | 21:00
| Gopalganj | 391 | 07:00 | 376 | 22:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 08:00 | 213 | 12:00 | Hasnabad | 225 | 08:00 | 214 | 11:00
| AKSML | 228 | 19:00 | 216 | 15:00 | Hathazari | 227 | 18:00 | 220 | 00:00
| Aminbazar | 222 | 02:00 | 213 | 16:00 | Ishurdi | 234 | 07:00 | 224 | 15:00
| Ashuganj | 230 | 08:00 | 222 | 12:00 | Jhenaidah | 222 | 18:30 | 212 | 00:00
| Ashuganj-400 | 230 | 08:00 | 222 | 12:00 | Kaliakoir | 224 | 01:00 | 218 | 09:00
| Baghabari | 229 | 06:00 | 220 | 15:00 | Keranigonj | 224 | 07:00 | 212 | 12:00
| Barapukuria | 218 | 04:00 | 207 | 19:30 | Khulna(S) | 224 | 18:30 | 213 | 21:00
| Barapukuria-230 | 218 | 04:00 | 207 | 19:30 | Madunaghat_I | 223 | 00:00 | 221 | 04:00
| Barishal | 232 | 07:00 | 224 | 22:00 | Maniknagar | 224 | 07:00 | 212 | 12:00
| Bheramara | 233 | 07:00 | 222 | 15:00 | Meghnaghat | 225 | 07:00 | 220 | 11:00
| Bhulta | 227 | 07:00 | 214 | 12:00 | Meghnaghat-400 | 226 | 07:00 | 217 | 12:00
| Bibiana | 226 | 01:00 | 221 | 12:00 | Mirsorai | 229 | 20:00 | 214 | 05:00
| BIPTC | 234 | 08:00 | 222 | 15:00 | Rajshahi | 233 | 07:00 | 220 | 15:00
| Bogura | 223 | 07:00 | 212 | 19:30 | Rampal | 224 | 08:00 | 214 | 21:00
| Bogura-400 | 226 | 07:00 | 214 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 235 | 06:00 | 230 | 19:00 | Rampura | 221 | 06:00 | 211 | 12:00
| BSRM | 228 | 19:30 | 216 | 02:00 | Shikalbaha | 229 | 19:30 | 220 | 04:00
| Cumilla(N) | 223 | 07:00 | 215 | 12:00 | Shyampur | 225 | 07:00 | 214 | 15:00
| Fenchuganj | 234 | 07:00 | 129 | 02:00 | Siddhirganj | 222 | 18:00 | 215 | 10:00
| Ghorashal | 230 | 00:00 | 220 | 15:00 | Sirajgonj | 236 | 07:00 | 227 | 14:00
| Ghorashal-230 | 225 | 01:00 | 216 | 09:00 | Sreepur | 230 | 07:00 | 219 | 12:00
| GPH | 227 | 19:30 | 216 | 05:00 | Tongi | 227 | 07:00 | 212 | 11:00
| Haripur | 222 | 18:00 | 213 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 07:00 | 124 | 16:00 | Kushtia | 132 | 07:00 | 126 | 19:30
| Agargaon | 136 | 07:00 | 126 | 15:00 | Lalbag | 133 | 07:00 | 124 | 12:00
| Agrabad | 129 | 19:30 | 122 | 09:00 | Lalmonirhat | 132 | 02:00 | 115 | 19:30
| AKS | 126 | 10:00 | 122 | 14:00 | Madanganj | 131 | 18:00 | 124 | 10:00
| Aminbazar | 136 | 02:00 | 123 | 00:00 | Madaripur | 128 | 07:00 | 120 | 22:00
| Amnura | 140 | 04:00 | 120 | 21:00 | Madartek | 134 | 07:00 | 123 | 12:00
| Ashuganj | 137 | 07:00 | 132 | 12:00 | Madunaghat | 130 | 19:30 | 124 | 16:00
| Bagerhat | 129 | 18:00 | 118 | 13:00 | Magura | 134 | 08:00 | 123 | 19:30
| Bakulia | 132 | 19:30 | 125 | 05:00 | Mahasthangarh | 132 | 06:00 | 121 | 19:30
| Banani | 132 | 06:00 | 123 | 12:00 | Manikganj | 128 | 01:00 | 116 | 14:00
| Bangabhaban | 129 | 06:00 | 121 | 11:00 | Maniknagar | 129 | 07:00 | 121 | 12:00
| Barapukuria | 136 | 01:00 | 125 | 19:30 | Matarbari | 119 | 19:30 | 106 | 00:00
| Barguna | 134 | 18:00 | 124 | 00:00 | Matuail | 131.3 | 07:00 | 124.9 | 12:00
| Barishal | 132 | 18:00 | 121 | 00:00 | Millgate | 133 | 01:00 | 120 | 12:00
| Barishal-230 | 132 | 18:00 | 125 | 22:00 | Mirpur | 135 | 07:00 | 127 | 11:00
| Baroaulia | 130 | 20:00 | 124 | 09:00 | Mirzapur | 127 | 00:00 | 116 | 13:00
| Baroirhat | 124 | 18:30 | 116 | 07:00 | Mithapukur | 131 | 01:00 | 118 | 19:30
| Bashundhara | 134 | 07:00 | 120 | 11:00 | MI_Cement | 131 | 07:00 | 124 | 10:00
| BashundharaCement | 130 | 18:30 | 124 | 10:00 | Modern | 131 | 19:30 | 124 | 16:00
| Beanibazar | 130 | 10:00 | 122 | 19:00 | Mogbazar | 133 | 05:00 | 124 | 16:00
| Benapole | 130 | 18:30 | 119 | 19:30 | Mongla | 127 | 18:00 | 117 | 22:00
| Bhaluka | 134 | 06:00 | 121 | 12:00 | Motijheel | 129 | 06:00 | 121 | 11:00
| Bhandaria | 134 | 18:00 | 117 | 00:00 | Munshiganj | 131 | 18:00 | 124 | 10:00
| Bhangura | 136 | 03:00 | 128 | 16:00 | Mymensingh | 135 | 22:00 | 114 | 19:00
| Bheramara | 134 | 07:00 | 129 | 15:00 | Naogaon | 130 | 07:00 | 118 | 15:00
| Bheramara(GK) | 133 | 06:00 | 129 | 15:00 | Narail | 133 | 07:00 | 123 | 19:30
| Bhulta | 127 | 07:00 | 116 | 10:00 | Narinda | 129 | 07:00 | 121 | 12:00
| Bog-Sherpur | 133 | 06:00 | 123 | 13:00 | Narshingdi | 127 | 07:00 | 116 | 12:00
| Bogura | 134 | 07:00 | 124 | 13:00 | Natore | 134 | 07:00 | 126 | 13:00
| Bogura-230 | 133 | 06:00 | 124 | 19:30 | Nawabganj | 132 | 07:00 | 125 | 12:00
| Brahmanbaria | 133 | 08:00 | 120 | 00:00 | Netrakona | 132 | 00:00 | 118 | 01:00
| Cantonment | 135 | 07:00 | 126 | 12:00 | New | 133 | 01:00 | 121 | 12:00
| Chandpur | 126 | 18:30 | 114 | 03:00 | Niamatpur | 134 | 06:00 | 126 | 22:00
| Chandraghona | 130 | 18:30 | 125 | 17:00 | Noapara | 132 | 18:00 | 123 | 19:30
| Chapai | 132 | 09:00 | 122 | 21:00 | Pabna | 133 | 07:00 | 127 | 15:00
| Charsaidpur | 131 | 18:00 | 124 | 10:00 | Palashbari | 130 | 05:00 | 116 | 19:30
| Chauddagram | 125 | 18:30 | 116 | 05:00 | Panchagarh | 137 | 00:00 | 115 | 19:30
| Chhatak | 130 | 09:00 | 124 | 19:00 | Patuakhali | 131 | 07:00 | 125 | 22:00
| Chowmuhani | 125 | 18:30 | 111 | 04:00 | Payra | 134 | 08:00 | 130 | 00:00
| Chuadanga | 126 | 09:00 | 115 | 21:00 | PHP | 123 | 18:30 | 115 | 03:00
| Coxsbazar | 119 | 18:00 | 106 | 13:00 | Postogola | 134 | 07:00 | 126 | 12:00
| Cumilla(N) | 130 | 18:00 | 123 | 00:00 | Purbachal | 134 | 07:00 | 118 | 12:00
| Cumilla(S) | 133 | 09:00 | 121 | 00:00 | Purbasadipur | 132 | 00:00 | 116 | 19:30
| Daudkandi | 128 | 08:00 | 117 | 00:00 | Rahanpur | 136 | 07:00 | 129 | 21:00
| Dhaka | 132 | 02:00 | 124 | 12:00 | Rahim | 130 | 06:00 | 105 | 10:00
| Dhamrai | 135 | 01:00 | 124 | 12:00 | Rajbari | 128 | 08:00 | 121 | 22:00
| Dhanmondi | 132 | 07:00 | 125 | 10:00 | Rajendrapur | 129 | 02:00 | 116 | 11:00
| Dohazari | 127 | 19:30 | 117 | 13:00 | Rajshahi | 132 | 06:00 | 125 | 15:00
| Faridpur | 128 | 07:00 | 122 | 00:00 | Rajshahi-230 | 135 | 07:00 | 115 | 22:00
| Fatullah | 130 | 07:00 | 124 | 11:00 | Ramganj | 122 | 18:30 | 109 | 04:00
| Fenchuganj | 134 | 07:00 | 129 | 00:00 | Rampur | 128 | 18:00 | 122 | 09:00
| Feni | 122 | 18:30 | 115 | 02:00 | Rampura | 132 | 06:00 | 124 | 12:00
| Ghatail | 131 | 05:00 | 118 | 18:00 | Rangamati | 130 | 20:00 | 124 | 05:00
| Ghorashal | 134 | 20:00 | 129 | 11:00 | Rangpur | 132 | 01:00 | 116 | 19:30
| Goalpara | 133 | 09:00 | 123 | 21:00 | Ruppur | 135 | 09:00 | 129 | 15:00
| Gollamari | 133 | 18:30 | 125 | 19:30 | Saidpur | 134 | 01:00 | 116 | 19:30
| Gopalganj | 129 | 18:30 | 121 | 21:00 | Satkhira | 128 | 18:30 | 116 | 22:00
| Gopalganj-400 | 128 | 07:00 | 122 | 22:00 | Satmasjid | 135 | 07:00 | 126 | 12:00
| Gulshan | 134 | 07:00 | 124 | 12:00 | Savar | 134 | 20:00 | 126 | 11:00
| Halishahar | 130 | 19:30 | 124 | 08:00 | SevenRings | 137 | 07:00 | 128 | 12:00
| Haripur | 130 | 06:00 | 125 | 10:00 | ShahCement | 131 | 18:00 | 124 | 10:00
| HaripurSBU | 130 | 01:00 | 125 | 10:00 | Shahjadpur | 139 | 05:00 | 132 | 12:00
| Hasnabad | 132 | 03:00 | 126 | 12:00 | Shahjibazar | 132 | 08:00 | 120 | 00:00
| Hathazari | 132 | 18:00 | 127 | 00:00 | Shahmirpur | 130 | 20:00 | 125 | 06:00
| Ishurdi | 136 | 07:00 | 130 | 15:00 | Shariatpur | 126 | 07:00 | 118 | 22:00
| Jaldhaka | 133 | 01:00 | 114 | 19:30 | Sherpur | 138 | 05:00 | 119 | 01:00
| Jamalpur | 140 | 22:00 | 123 | 01:00 | Shikalbaha | 119 | 20:00 | 113 | 04:00
| Jashore | 130 | 09:00 | 120 | 19:00 | Shikalbaha-230 | 132 | 19:30 | 126 | 04:00
| Jhenaidah | 134 | 08:00 | 126 | 19:00 | Shitalakhya | 131.1 | 18:00 | 124 | 10:00
| Jhenaidah-230 | 135 | 18:30 | 127 | 00:00 | Sholosohor | 130 | 19:30 | 124 | 05:00
| Joydebpur | 141 | 01:00 | 125 | 12:00 | Shyampur | 127 | 09:00 | 123 | 12:00
| Joypurhat | 130 | 06:00 | 115 | 15:00 | Shyampur-230 | 130 | 07:00 | 120 | 11:00
| Juldah | 132 | 19:30 | 125 | 09:00 | Siddhirganj | 132 | 07:00 | 125 | 10:00
| Kabirpur | 131 | 01:00 | 117 | 12:00 | Sirajganj | 132 | 02:00 | 123 | 16:00
| Kachua | 126 | 18:30 | 115 | 04:00 | Sonargaon | 131 | 07:00 | 124 | 10:00
| Kaliakoir | 133 | 00:00 | 121 | 02:00 | Sreemongol | 130 | 07:00 | 121 | 23:00
| Kallyanpur | 128 | 07:00 | 121 | 00:00 | Sreepur | 134 | 07:00 | 124 | 19:00
| Kalurghat | 131 | 19:30 | 125 | 09:00 | Srinagar | 133 | 07:00 | 125 | 12:00
| Kamrangirchar | 133 | 03:00 | 120 | 12:00 | SSM | 132 | 20:00 | 129 | 12:00
| Kaptai | 132 | 18:00 | 129 | 4:00 | Sunamganj | 129 | 07:00 | 123 | 00:00
| Kazla | 129 | 08:00 | 120 | 12:00 | Sylhet | 131 | 10:00 | 126 | 00:00
| Keranigonj | 134 | 07:00 | 126 | 12:00 | Sylhet-132 | 131 | 06:00 | 128 | 00:00
| Khagrachori | 129 | 20:00 | 123 | 00:00 | Tangail | 128 | 06:00 | 116 | 13:00
| Khulna | 132 | 18:30 | 123 | 22:00 | Thakurgaon | 138 | 00:00 | 115 | 19:30
| Khulna(S) | 132 | 07:00 | 124 | 22:00 | TK | 130 | 19:30 | 12 | 18:00
| Khulshi | 129 | 19:30 | 122 | 04:00 | Tongi | 136 | 05:00 | 123 | 11:00
| Kishoreganj | 134 | 07:00 | 122 | 19:00 | Ullahpara | 133 | 01:00 | 129 | 17:00
| Kodda | 136 | 01:00 | 116 | 06:00 | Ullon | 132 | 02:00 | 124 | 14:00
| KSRM | 131 | 19:30 | 17 | 06:00 | Uttara | 135 | 07:00 | 126 | 11:00
| Kulaura | 132 | 09:00 | 128 | 00:00 | UttaraNew | 135 | 20:00 | 127 | 11:00
| Kurigram | 134 | 03:00 | 114 | 19:30 | Zigatola | 133 | 07:00 | 125 | 12:00

## L-Curve
Date | 2024-06-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 836 | 8465 | 6661 | 15126 |  |  |  | QF-LDC-11
0:30 | 918 | 8088.5 | 6368 | 14456.5 | Date: | 2024-06-06
1:00 | 1000 | 7712 | 6075 | 13787
1:30 | 933 | 7510 | 5766.5 | 13276.5
2:00 | 866 | 7308 | 5458 | 12766
2:30 | 959 | 7280.5 | 5549 | 12829.5 | [5 empty] | Gen. at Eve. Peak | 15340 | 15340 MW (19:30 )
3:00 | 1052 | 7253 | 5640 | 12893 | [6 empty] | 19:30
3:30 | 1109 | 7206.5 | 5563.5 | 12770 | [5 empty] | Gen. at Day Peak | 13503 | 13503 MW (12:00 )
4:00 | 1166 | 7160 | 5487 | 12647 | [6 empty] | 12:00
4:30 | 1165 | 7064.5 | 5365.5 | 12430 | [5 empty] | Highest Generation | 15340
5:00 | 1164 | 6969 | 5244 | 12213 | [6 empty] | 19:30
5:30 | 1064 | 6821.5 | 5024 | 11845.5
6:00 | 964 | 6674 | 4804 | 11478
6:30 | 876 | 6612 | 4662 | 11274
7:00 | 788 | 6550 | 4520 | 11070
7:30 | 812 | 6579.5 | 4477.5 | 11057
8:00 | 836 | 6609 | 4435 | 11044
8:30 | 915 | 6752.5 | 4539.5 | 11292
9:00 | 994 | 6896 | 4644 | 11540
9:30 | 1138 | 7025 | 4901.5 | 11926.5
10:00 | 1282 | 7154 | 5159 | 12313
10:30 | 1191 | 7349.5 | 5180 | 12529.5
11:00 | 1100 | 7545 | 5201 | 12746
11:30 | 1129 | 7674.5 | 5450 | 13124.5
12:00 | 1158 | 7804 | 5699 | 13503
12:30 | 1065 | 7918 | 5670 | 13588
13:00 | 972 | 8032 | 5641 | 13673
13:30 | 967 | 8073 | 5676.5 | 13749.5
14:00 | 962 | 8114 | 5712 | 13826
14:30 | 951 | 8217 | 5775.5 | 13992.5
15:00 | 940 | 8320 | 5839 | 14159
15:30 | 950 | 8340 | 5828.5 | 14168.5
16:00 | 960 | 8360 | 5818 | 14178
16:30 | 951 | 8312.5 | 5723 | 14035.5
17:00 | 942 | 8265 | 5628 | 13893
17:30 | 912 | 8323 | 5389 | 13712
18:00 | 882 | 8381 | 5150 | 13531
18:30 | 917 | 8598 | 5491 | 14089
19:00 | 952 | 8815 | 5832 | 14647
19:30 | 730 | 8881 | 6459 | 15340
20:00 | 588 | 8886 | 6361 | 15247 |  |  |  | Executive Engineer
20:30 | 588 | 8761.5 | 6445 | 15206.5 |  |  |  | Network Operation Division
21:00 | 588 | 8637 | 6529 | 15166
21:30 | 581 | 8587 | 6554.5 | 15141.5
22:00 | 574 | 8537 | 6580 | 15117 |  |  |  |  | Page 6 of 7
22:30 | 633 | 8591.5 | 6592.5 | 15184
23:00 | 692 | 8646 | 6605 | 15251
23:30 | 764 | 8555.5 | 6633 | 15188.5
24:00 | 836 | 8465 | 6661 | 15126
15340 MW (19:30 )
13503 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-06 |  | Energy |  | 327587065
[14 empty] | Date: | 2024-06-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3831 | 781 | 1784 | 0 | 2805 | 5190 | 75 | 0 | 553 | 90 | 0 | 17 | 786.92
0:30 | 3764 | 777 | 1765.5 | 0 | 2391 | 5040.5 | 102 | 0 | 518 | 90 | 0 | 8.5 | 542.9175 |  |  | Date: | 43987
1:00 | 3697 | 773 | 1747 | 0 | 1977 | 4891 | 129 | 0 | 483 | 90 | 0 | 0 | 298.915
1:30 | 3689.5 | 775 | 1715.5 | 0 | 1739.5 | 4809.5 | 118.5 | 0 | 337.5 | 90 | 0 | 1.5 | 261.1925 | [8 empty] | Total Energy | 327.5871 | 327.5871 | Total Energy Gen 327.587 MKWHr Energy Not Served 6.657 MKWHr Energy Requirement 334.244 MKWHr
2:00 | 3682 | 777 | 1684 | 0 | 1502 | 4728 | 108 | 0 | 192 | 90 | 0 | 3 | 223.47 | [8 empty] | Energy not Served | 6.6568 | 6.6568
2:30 | 3682 | 851.5 | 1742 | 0 | 1439.5 | 4755.5 | 108 | 0 | 159.5 | 89 | 0 | 2.5 | 162.8275 | [8 empty] | Energy Requirement | 334.2438 | 334.2438
3:00 | 3682 | 926 | 1800 | 0 | 1377 | 4783 | 108 | 0 | 127 | 88 | 0 | 2 | 102.185
3:30 | 3683 | 927.5 | 1796 | 0 | 1305 | 4725.5 | 108 | 0 | 135 | 88 | 0 | 2 | 102.6625
4:00 | 3684 | 929 | 1792 | 0 | 1233 | 4668 | 108 | 0 | 143 | 88 | 0 | 2 | 103.14
4:30 | 3697.5 | 929 | 1758.5 | 0 | 1121.5 | 4590 | 109 | 0 | 138.5 | 85 | 0 | 1 | 102.6625
5:00 | 3711 | 929 | 1725 | 0 | 1010 | 4512 | 110 | 0 | 134 | 82 | 0 | 0 | 102.185
5:30 | 3678 | 929 | 1645 | 0 | 923 | 4339.5 | 110 | 0 | 130.5 | 82 | 8.5 | 0 | 99.7975
6:00 | 3645 | 929 | 1565 | 0 | 836 | 4167 | 110 | 0 | 127 | 82 | 17 | 0 | 97.41
6:30 | 3625 | 928.5 | 1541.5 | 0 | 807.5 | 4018.5 | 110 | 0 | 123 | 76 | 44 | 0 | 72.58 | [7 empty] | Coal
7:00 | 3605 | 928 | 1518 | 0 | 779 | 3870 | 110 | 0 | 119 | 70 | 71 | 0 | 47.75
7:30 | 3651 | 928.5 | 1516.5 | 0 | 742 | 3819.5 | 110 | 0 | 107.5 | 78 | 104 | 0 | 53.0025 | [6 empty] | Oil
8:00 | 3697 | 929 | 1515 | 0 | 705 | 3769 | 110 | 0 | 96 | 86 | 137 | 0 | 58.255
8:30 | 3756 | 929 | 1584 | 0 | 752 | 3799 | 112.5 | 0 | 96 | 72 | 191.5 | 0 | 57.7775
9:00 | 3815 | 929 | 1653 | 0 | 799 | 3829 | 115 | 0 | 96 | 58 | 246 | 0 | 57.3
9:30 | 3766 | 928 | 1680 | 0 | 935.5 | 4002.5 | 115 | 0 | 126.5 | 66 | 307 | 0 | 53.48
10:00 | 3717 | 927 | 1707 | 0 | 1072 | 4176 | 115 | 0 | 157 | 74 | 368 | 0 | 49.66
10:30 | 3778.5 | 927 | 1708 | 0 | 1194.5 | 4213 | 115 | 0 | 161 | 78 | 354.5 | 0 | 112.69
11:00 | 3840 | 927 | 1709 | 0 | 1317 | 4250 | 115 | 0 | 165 | 82 | 341 | 0 | 175.72
11:30 | 3831.5 | 927 | 1731.5 | 0 | 1463.5 | 4391.5 | 115 | 0 | 173.5 | 82 | 405.5 | 3.5 | 148.5025
12:00 | 3823 | 927 | 1754 | 0 | 1610 | 4533 | 115 | 0 | 182 | 82 | 470 | 7 | 121.285
12:30 | 3807.5 | 927.5 | 1691.5 | 0 | 1773.5 | 4536 | 112.5 | 0 | 181 | 85 | 465 | 8.5 | 201.1425
13:00 | 3792 | 928 | 1629 | 0 | 1937 | 4539 | 110 | 0 | 180 | 88 | 460 | 10 | 281
13:30 | 3792 | 928 | 1629 | 0 | 1937 | 4539 | 110 | 0 | 180 | 88 | 460 | 10 | 281
14:00 | 3792 | 928 | 1629 | 0 | 1937 | 4539 | 110 | 0 | 180 | 88 | 460 | 10 | 281
14:30 | 3822.5 | 927 | 1677.5 | 0 | 2092.5 | 4651 | 107.5 | 0 | 163.5 | 89 | 371.5 | 14 | 296
15:00 | 3853 | 926 | 1726 | 0 | 2248 | 4763 | 105 | 0 | 147 | 90 | 283 | 18 | 311
15:30 | 3838.5 | 926.5 | 1723.5 | 0 | 2280.5 | 4765.5 | 105 | 0 | 166 | 89 | 256.5 | 17.5 | 309.5
16:00 | 3824 | 927 | 1721 | 0 | 2313 | 4768 | 105 | 0 | 185 | 88 | 230 | 17 | 308
16:30 | 3815.5 | 927.5 | 1705 | 0 | 2332 | 4704.5 | 71 | 0 | 209 | 88 | 169 | 14 | 312.5
17:00 | 3807 | 928 | 1689 | 0 | 2351 | 4641 | 37 | 0 | 233 | 88 | 108 | 11 | 317
17:30 | 3797 | 925.5 | 1645.5 | 0 | 2349.5 | 4481.5 | 52.5 | 0 | 304 | 85 | 66 | 5.5 | 263
18:00 | 3787 | 923 | 1602 | 0 | 2348 | 4322 | 68 | 0 | 375 | 82 | 24 | 0 | 209
18:30 | 3832.5 | 923 | 1592 | 0 | 2499 | 4512.5 | 71 | 0 | 557.5 | 88 | 12 | 1.5 | 263.5
19:00 | 3878 | 923 | 1582 | 0 | 2650 | 4703 | 74 | 0 | 740 | 94 | 0 | 3 | 318
19:30 | 3825 | 923 | 1826 | 0 | 2813 | 5002 | 74 | 0 | 781 | 88 | 0 | 8 | 375.5
20:00 | 3840 | 782 | 1831 | 0 | 2823 | 5021 | 75 | 0 | 788 | 76 | 0 | 11 | 433
20:30 | 3854 | 781.5 | 1830 | 0 | 2797 | 5066.5 | 75 | 0 | 720.5 | 74 | 0 | 8 | 471.5
21:00 | 3868 | 781 | 1829 | 0 | 2771 | 5112 | 75 | 0 | 653 | 72 | 0 | 5 | 510
21:30 | 3880.5 | 781 | 1836 | 0 | 2774.5 | 5145 | 75 | 0 | 575 | 72 | 0 | 2.5 | 581.1325
22:00 | 3893 | 781 | 1843 | 0 | 2778 | 5178 | 75 | 0 | 497 | 72 | 0 | 0 | 652.265
22:30 | 3876 | 781 | 1826 | 0 | 2785.5 | 5178 | 75 | 0 | 564 | 81 | 0 | 17.5 | 674.23
23:00 | 3859 | 781 | 1809 | 0 | 2793 | 5178 | 75 | 0 | 631 | 90 | 0 | 35 | 696.195
23:30 | 3845 | 781 | 1796.5 | 0 | 2799 | 5184 | 75 | 0 | 592 | 90 | 0 | 26 | 741.5575 |  |  | Max Temp. in Dhaka |  | 34.5°C
24:00 | 3831 | 781 | 1784 | 0 | 2805 | 5190 | 75 | 0 | 553 | 90 | 0 | 17 | 786.92
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 327.587 MKWHr Energy Not Served 6.657 MKWHr Energy Requirement 334.244 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 75 | 75 | 75 | 75 | 70 | 70 | 70 | 70 | 0 | 30 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1426375
2 | Karnaphuli Hydro PP Unit-4 & 5 | 39 | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 35 | 35 | 37 | 38 |  | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 936000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [14 empty] | 2 | 8 | 8 | 10 |  | 17 |  |  | 6 |  |  |  | 68407
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 3 | 6 | 8 | 11 | 16 | 18 | 12 | 17 | 7 | 4 | 2 | 1 | [8 empty] | 95985
6 | Sikalbaha 225MW CCPP (Gas) | 226 | 224 | 225 | 226 | 224 | 224 | 225 | 223 | 223 | 219 | 217 | 217 | 216 | 216 | 214 | 217 | 215 | 220 |  | 218 | 220 | 221 | 221 | 220 | 222 | 221 | 5175487
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 51 | 34 | 34 | 24 | 17 | 17 | 17 | 17 | 25 | 33 | 50 | 49 | 49 | 49 | 49 | 50 | 51 |  | 68 | 85 | 85 | 85 | 85 | 85 | 85 | 1150519
12 | Hathazari 100 MW peaking PP | 64 | 64 | 16 | 32 | 32 | 32 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 23 | 24 | 31 | 32 | 32 |  | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 790752
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 907454
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 44 | 44 | 44 | 44 | 45 | 45 | 45 | 47 | 47 | 47 | 46 | 46 | 45 | 45 | 41 | 40 | 40 | 40 |  | 40 | 41 | 41 | 41 | 41 | 42 | 41 | 1060256
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 300 | 317 | 317 | 318 |  | 318 | 322 | 322 | 324 | 321 | 327 | 327 | 7081285
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | [11 empty] | 90 | 145 | 195 | 245 | 260 | 260 |  | 263 | 260 | 260 | 263 | 260 | 260 | 260 | 2983309
19 | Ashuganj 195 MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [15 empty] | 100364
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4221000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 480 | 481 | 482 | 480 | 480 | 480 | 480 | 480 | 481 | 481 | 482 | 480 | 480 | 480 | 482 | 480 | 480 | 480 |  | 485 | 485 | 485 | 490 | 495 | 492 | 490 | 11612726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 214 | 214 | 220 | 222 | 219 | 220 | 164 | 160 | 190 | 189 | 216 | 220 | 215 | 213 | 213 | 209 | 214 | 214 |  | 213 | 216 | 216 | 213 | 210 | 198 | 198 | 5079000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 360 | 305 | 325 | 270 | 270 | 270 | 290 | 280 | 270 | 270 |  | 305 | 270 | 270 | 270 | 280 | 280 | 250 | 6896000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 315 | 280 | 305 | 285 | 285 | 280 | 300 | 285 | 285 | 285 |  | 315 | 280 | 285 | 280 | 290 | 280 | 280 | 7374400
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5674300
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 353 | 352 | 352 | 351 | 348 | 302 | 302 | 302 | 350 | 356 | 356 | 370 | 406 | 400 | 401 | 401 | 403 | 405 |  | 392 | 404 | 402 | 404 | 405 | 402 | 408 | 9043200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 410 | 350 | 450 | 450 | 450 | 350 | 350 | 350 | 380 | 420 | 420 | 420 | 350 | 350 | 420 | 420 | 410 | 410 |  | 350 | 420 | 420 | 420 | 420 | 420 | 420 | 9384500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 35 | 36 | 36 | 36 | 37 | 36 | 36 | 30 | 30 | 29 | 29 | 26 | 11 | 12 | 12 | 12 | 21 | 31 |  | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 662400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 1 | 4 | 16 | 43 | 21 | 47 | 37 | 38 | 24 | 11 | 3 |  | 0 | [6 empty] | 264310
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 948000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 48 | 48 | 48 | 48 |  | 48 | 28 | 28 | 48 | 48 | 48 | 48 | 860880
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 51 | 52 | 52 | 52 | 52 | 62 | 61 | 62 | 40 | 41 | 60 | 58 | 58 | 58 | 58 | 58 | 60 |  | 58 | 58 | 59 | 59 | 55 | 51 | 51 | 1322880
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 211 | 210 | 209 | 209 | 209 | 209 | 210 | 209 | 208 | 209 | 209 | 210 | 210 | 207 | 207 | 207 | 206 |  | 206 | 206 | 207 | 207 | 207 | 208 | 207 | 5180560
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 8 | 8 | 8 | 8 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 92544
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 47 | 47 | 50 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1252200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 24 |  | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 419112
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 300 | 290 | 280 | 290 | 270 | 285 | 315 | 295 | 300 | 305 | 280 | 315 | 315 | 310 | 285 | 280 |  | 290 | 285 | 290 | 285 | 290 | 315 | 290 | 7216500
| Bibiyana South 400 MW | 340 | 370 | 340 | 340 | 340 | 340 | 340 | 380 | 360 | 340 | 360 | 380 | 370 | 340 | 350 | 345 | 320 | 320 |  | 370 | 345 | 345 | 345 | 345 | 345 | 345 | 8304200
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 17 | 17 | 17 | 0 |  |  |  |  | 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 40 | 55 | 55 | 55 | 35 | 35 | 35 | 671219
59 | Tangail Palli Power Gen 22 MW | 1 | 6 | 6 | 6 | 5 | 0 |  |  | 1 | 0 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 5 | 6 | 6 | 7 | 10 | 9 | 12 | 122160
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 90 | 90 | 88 | 88 | 82 | 82 | 70 | 86 | 58 | 74 | 82 | 82 | 88 | 92 | 90 | 88 | 88 | 82 |  | 94 | 88 | 76 | 72 | 72 | 90 | 90 | 2009280
64 | Malancha, Ctg. EPZ (United) | 28 | 28 | 31 | 36 | 38 | 38 | 36 | 12 | 2 | 3 | 2 | 2 | 11 | 5 | 3 | 2 | 7 | 5 |  | 11 | 16 | 16 | 25 | 30 | 34 | 35 | 457440
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 756500
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 266400
69 | Summit Ashulia | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 12 |  | 12 | 12 | 13 | 12 |  | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 263400
70 | Summit Madhabdi | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 14 | 15 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 0 | 12 | 21 | 21 | 22 | 22 | 22 | 336600
71 | Maona 33 MW PP(Summit) | 33 |  | 0 | 0 | 25 | 0 |  |  |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 555000
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 224200
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 10 | 17 | 17 | 34 | 347700
| Chowmuhani 113 MW | 51 | 37 | 37 | 37 | 37 | 37 | 38 | 37 | 38 | 38 | 37 | 38 | 37 | 38 | 39 | 63 | 70 | 79 |  | 84 | 84 | 85 | 85 | 85 | 79 | 77 | 1299480
| Manikgonj 162MW PP(MPGL) | 90 | 17 | [7 empty] | 70 | 72 | 136 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 2312640
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 33 | 25 | 8 | [5 empty] | 5 | 16 | 28 | 70 | 77 | 77 | 77 | 77 | 77 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1029178
78 | Gazipur 52 MW PP | [8 empty] | 8 | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 |  | 117600
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 64 | 149 |  | 149 | 149 | 149 |  | 10 | 148 | 95 | 1026240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 41 | 42 | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 29 | 25 | 25 | 25 | 25 | 25 | 25 | 27 |  | 34 | 34 | 43 | 45 | 51 | 51 | 51 | 904930
| Gazipur 100 MW PP | 17 |  |  |  | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 945600
| Kaptai 7 MW Solar PP | [6 empty] | 2 | 3 | 3 | 5 | 5 | 5 | 2 | 4 | 1 | 0 | 1 | 0 | [8 empty] | 29281
| Jodiac Power | 35 | 17 | 17 | 17 | [5 empty] | 7 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 646271
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 102 | 68 | 68 | 34 | 34 | 42 | 87 | 93 | 104 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2348499
82 | Madanganj 102 PP(Summit) | 68 | 68 | 68 | 58 | 34 | 17 | 17 | 17 | 17 | 17 | 44 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 64 | 64 | 64 | 64 | 64 | 64 | 68 | 1179799
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 20 | 25 | 25 | 16 | 13 |  |  | 68089
86 | Meghnaghat CCPP ( Summit) | 135 | 152 | 155 | 153 | 154 | 155 | 150 | 155 | 152 | 151 | 152 | 153 | 150 | 151 | 151 | 152 | 150 | 152 |  | 150 | 152 | 152 | 146 | 150 | 151 | 151 | 3601047
87 | Meghnaghat 100 MW(IEL) | 49 | 37 | 20 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 8 | 14 | 39 | 71 | 82 | 75 | 72 | 74 |  | 80 | 81 | 81 | 81 | 81 | 81 | 81 | 1073280
| Meghnaghat 104 MW PP (OPCL) | 53 | 53 | 53 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 47 | 50 | 51 | 52 | 52 | 52 | 69 | 69 |  | 70 | 70 | 70 | 70 | 70 | 70 | 71 | 1282560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 68 | 68 | 68 | 68 | 36 | 36 |  |  |  | 68 | 68 | 78 | 78 | 78 | 78 | 65 | 65 | 65 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1395240
92 | Fenchuganj 44 MW (Energyprima) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 43 | 43 | 39 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1014336
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1163161
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 68 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1311552
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 14 |  | 21 | 24 | 19 | 19 | 19 | 19 | 6 | 229440
96 | Chattogram 108 MW PP (ECPV) | 26 | 25 | 25 | 26 | 24 | 25 | 25 | 25 | 25 | 25 | 32 | 32 | 32 | 30 | 33 | 31 | 34 | 38 |  | 37 | 37 | 37 | 50 | 62 | 62 | 63 | 834240
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1324582
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 50 | 35 | 670167
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3596154
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 2 | 1 | 2 | 1 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 13850
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | [5 empty] | 1 | 46 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 840600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 98 | 98 | 98 | 97 | 45 | 0 |  |  | 20 | 94 | 94 | 94 | 94 | 102 | 103 | 93 | 93 | 93 |  | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 2078400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 131 | 118 | 100 | 80 | 58 | 50 | 52 | 53 | 97 | 106 | 108 | 124 | 124 | 124 | 125 | 132 | 149 |  | 149 | 149 | 149 |  |  |  |  | 2307888
115 | Juldah 100 MW PP Unit-3 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575040
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 17 |  | 17 | 17 | 17 | 19 | 17 | 17 | 17 | 424800
117 | Ashuganj 150 MW PP (Midland) | 80 | 6 | 6 | 6 | 5 | 6 |  |  |  |  | 1 | 28 | 94 | 117 | 122 | 125 | 125 | 123 |  | 125 | 128 | 128 | 128 | 133 | 128 | 130 | 1742981
118 | Bibiyana-III 400 MW CCPP | 346 | 352 | 366 | 366 | 366 | 366 | 366 | 408 | 365 | 330 | 345 | 367 | 373 | 373 | 378 | 368 | 368 | 368 |  | 400 | 367 | 367 | 366 | 370 | 366 | 366 | 8834000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 45 | 45 | 45 | 45 | 59 | 59 | 60 | 59 | 59 | 59 | 59 | 59 | 66 | 68 |  | 68 | 78 | 78 | 78 | 78 | 68 | 68 | 1467600
| Anwara 300 MW PP (United) | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 61 | 50 | 52 | 52 | 52 | 52 | 1272109
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 597120
| Anlima Energy Ltd. | 72 | 72 | 72 | 41 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 38 |  | 60 | 72 | 72 | 72 | 72 | 72 | 72 | 1188055
| Bhairob 54.5 MW | [14 empty] | 7 | 17 | [7 empty] | 8 | 17 | 17 | 83160
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 15 | 17 | 10 | 13 | 31 | 29 | 26 | 25 | 12 | 7 | 2 | [8 empty] | 187308
| Chandpur 115(Doreen) | 77 | 115 | 108 | 105 | 104 | 104 | 104 | 104 | 60 | 50 | 51 | 51 | 51 | 51 | 50 | 50 | 65 | 86 |  | 104 | 104 | 103 | 104 | 103 | 81 | 69 | 1965120
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 12 | 17 | 17 | 17 | 17 | 17 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 703080
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 53 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 | 163 | 17 | 17 | 17 | 938400
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 3 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 10 | 16 | 18 | 17 | 11 | 0 |  | 3 | 8 | 11 | 5 | 0 | 35 | 17 | 128640
| Sonagazi 75 MW Solar Plant | [5 empty] | 5 | 18 | 42 | 41 | 53 | 26 | 60 | 62 | 10 | 9 | 21 | 12 | 3 | [8 empty] | 407936
| Matarbari 2*600 MW (CPGCL) | 826 | 827 | 825 | 827 | 826 | 827 | 825 | 829 | 824 | 826 | 825 | 827 | 828 | 825 | 824 | 823 | 824 | 825 |  | 829 | 827 | 826 | 828 | 828 | 828 | 827 | 19934545
120 | Eastern Zone Total | 7712 | 7308 | 7253 | 7160 | 6969 | 6674 | 6550 | 6609 | 6896 | 7154 | 7545 | 7804 | 8032 | 8114 | 8320 | 8360 | 8265 | 8381 |  | 8815 | 8881 | 8886 | 8637 | 8537 | 8646 | 8465 | 188688802
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 81 | 49 | 49 | 16 | 16 | 16 | 8 |  |  |  |  | 21 | 46 | 60 | 59 | 59 | 45 | 31 |  | 31 | 31 | 32 | 46 | 47 | 44 | 48 | 781440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 30 | [16 empty] | 4 |  | 38 | 47 | 41 | 41 | 41 | 41 | 21 | 237600
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 90 | 90 | 90 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 58 | 70 | 35 |  | 35 | 35 | 35 | 53 | 53 | 58 | 90 | 1247520
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 6 | 20 | 27 | 64 | 74 | 77 | 94 | 82 | 75 | 63 | 46 | 18 | 1 | [8 empty] | 642240
131 | Rampal 1320 MW (BIFPCL) | 620 | 542 | 547 | 550 | 515 | 418 | 380 | 377 | 376 | 433 | 431 | 547 | 584 | 591 | 585 | 585 | 530 | 460 |  | 554 | 602 | 612 | 607 | 613 | 610 | 611 | 13403640
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 |  | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 5176255
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 48 | 16 | 16 | 16 | 16 | 16 | [7 empty] | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 45 | 48 | 430848
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 250 | 250 | 200 | 190 | 150 | 150 | 200 | 263 | 307 | 307 | 307 | 307 | 307 | 303 | 250 |  | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 6480000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 126 | 126 | 130 | 126 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 126 | 126 | 126 | 126 | 126 | 80 |  | 80 | 130 | 126 | 126 | 126 | 130 | 130 | 2978000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 9 | 7 | 7 | 7 | 7 | 8 | 9 | 8 | 8 | 8 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 218789
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | [8 empty] | 8 | 8 | 24 | 24 | 24 | 24 | 8 |  | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 253875
143 | Gopalganj 100 MW Peaking PP | 47 | [16 empty] | 20 |  | 55 | 55 | 56 | 56 | 46 | 44 | 40 | 336512
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 773 | 777 | 926 | 929 | 929 | 929 | 928 | 929 | 929 | 927 | 927 | 927 | 928 | 927 | 926 | 927 | 928 | 923 |  | 923 | 923 | 782 | 781 | 781 | 781 | 781 | 21499636
147 | Bheramara 410 MW CCPP | 205 | 210 | 215 | 220 | 225 | 230 | 235 | 250 | 245 | 245 | 240 | 230 | 225 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 210 | 205 | 190 | 190 | 5486112
148 | Payra 1320 MW | 1020 | 1020 | 1070 | 1000 | 900 | 800 | 600 | 570 | 650 | 740 | 780 | 790 | 780 | 850 | 900 | 910 | 900 | 740 |  | 810 | 1080 | 1090 | 1180 | 1240 | 1244 | 1244 | 24130800
149
150 | Barapukuria TPP Unit-1 | 62 | 64 | 64 | 64 | 64 | 65 | 64 | 65 | 65 | 65 | 67 | 67 | 66 | 67 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 1495418
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 230 | 230 | 275 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 210 | 210 | 230 | 5519000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 39 | [18 empty] | 28 | 28 | 30 | 40 | 39 | 38 | 38 | 242949
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 3 | 2 | 2 | 2 | 4 | 2 | 3 | 2 | 1 | 0 | [8 empty] | 27060
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 173 | 180 | 180 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 155 | 170 | 170 | 170 | 3895400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 380 | 360 | 360 | 360 | 300 | 270 | 250 | 250 | 300 | 300 | 300 | 340 | 300 | 300 | 300 | 300 | 300 | 300 |  | 325 | 414 | 414 | 414 | 414 | 350 | 350 | 8072581
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 4 | 4 | 4 | 11 | 11 | 11 | 11 | 48245
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | [13 empty] | 2 | 2 | 2 | 5 | 5 |  | 5 | 5 | 8 | 8 | 8 | 8 | 5 | 49770
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 14 | 14 | 14 | 14 | 14 | 35 | 35 | 110570
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 38 | [18 empty] | 30 | 38 | 48 | 45 | 35 | 35 | 35 | 217353
168 | Santahar 50 MW Peaking PP | 35 | [16 empty] | 22 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 266440
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 85 | [15 empty] | 30 | 40 |  | 82 | 88 | 88 | 88 | 88 | 86 | 86 | 615472
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 9 | 45 | 52 | 70 | 70 | 77 | 108 | 450912
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 35 | 70 | 70 | 70 | 70 | 113 | 113 | 469824
173 | Rangpur 20 MW GTPP | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 44 | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 70 | 98 | 107 | 107 | 107 | 107 | 106 | 870432
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 5 | 6 | 8 | 6 | 8 | 2 | 3 | 3 | 1 | [8 empty] | 46144
178 | Energypac Power Venture Thakurgaon Ltd. | 75 | [10 empty] | 25 | 50 | 50 | 50 | 50 | 49 | 50 |  | 69 | 94 | 94 | 94 | 94 | 94 | 94 | 968064
| Intraco Solar 30 MW | [5 empty] | 0 | 4 | 7 | 16 | 32 | 28 | 35 | 34 | 23 | 24 | 17 | 7 | 2 |  | 0 | [6 empty] | 228466
| Adani Power Jharkhanda Ltd | 1356 | 1267 | 1268 | 1277 | 1257 | 1157 | 1111 | 1068 | 1053 | 1156 | 1172 | 1285 | 1264 | 1257 | 1370 | 1368 | 1309 | 1272 |  | 1423 | 1406 | 1406 | 1405 | 1420 | 1422 | 1417 | 30861206
178 | Teesta Solar Limited | [5 empty] | 2 | 18 | 35 | 87 | 158 | 124 | 194 | 181 | 134 | 109 | 100 | 46 | 11 | [8 empty] | 1139690