## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-09 | Sunday
|  | Date (day): | 2024-06-09 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15063.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16300 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-08 | 2024-06-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 400 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 420 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 19 | 90 | 90 | 90 |  |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 150 | 150 | 150 | 185 |  | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 12 | 20 | 65 | 65 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 25 | 0 | 25 | 50 |  | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 25 | 72 | 70 | 76 |  |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 316 | 290 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 81 | 82 | 82 |  | 20 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 147 | 48 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55 |  |  | Fuel Shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 17 | 55 |  |  | Fuel Shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 36 | 33 | 36 |  | 44 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 32 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 18 | 19 | 20 | 28 |  | 5 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 33 | 32 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 240 | 270 | 270 | 30 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 91 | 97 | 90 | 97 | 52 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 52 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 51 | 71 | 50 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 34 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 2111 | 2872 | 2743 | 3008 | 1635 | 849
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 3 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 18 | 32 |  | fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 113 | 115 | 115 | 115 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 219 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 51 | 51 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 46 | 58 | 32 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 85 | 50 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 70 | 70 | 70 | 30 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 26 | 15 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 32 | 38 | 30 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 35 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 110 | 85 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 24 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 53 | 35 | 53 | 63 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 125 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 440 | 470 | 470 | 470 |  | 754 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 32 | 17 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 748 | 624 | 700 | 700
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 34 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 1924 | 2232 | 2212 | 2371 | 1003 | 1123
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 214 | 217 | 200 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 300 | 280 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 300 | 280 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 245 | 240 | 250 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 10 | 10 | 35 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 43 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 122 | 130 | 130 | 20 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 41 | 40 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 80 | 80 | 80 |  | 83 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 78 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 51 | 25 | 51
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 6 | 6 | 6 |  | 19 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 | 97 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 39 | 75 | 37 | 75 | 38 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 115 | 115 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1351 | 1772 | 1723 | 1851 | 652 | 113
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 34 | 30 | 40 | 162 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 93 | 120 | 90 | 120 | 80 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 78 | 60 | 80 | 35 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 6 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 234 | 244 | 237.6 | 252 | 162 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 41 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 48 | 48 | 48 | 48 |  | 42 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 53 | 53
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 34 | 39 | 40 | 40 |  | 10 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 56 | 56 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 205 | 204 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 14 | 16 | 16 |  | 9 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 280 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 367 | 350 | 380 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 383 | 340 | 320 | 340 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1679 | 1620 | 1581 | 1655 | 0 | 468
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 779 | 943 | 801
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 46 | 20 | 50
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 30 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 215 | 190 | 200 | 200 | 210 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 40 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 36 | 36 | 17 | 53 | 52 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 84 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 405 | 1013 | 1000 | 1000
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1663 | 2190 | 2392 | 2254 | 844 | 49
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 0 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 1244 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 299 | 307 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1505 | 1923 | 1700 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 0 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 35 | 14 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 0 | 45
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 160 | 140 | 150 | 150 | 60 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 340 | 300 | 350 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 50 | 88 |  | 16 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 94 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1209 | 1456 | 1200 | 1400
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1726 | 2421 | 1932 | 2379 | 743 | 95
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 61 | 60 | 64
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 210 | 210 | 210 |  | 64 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 70 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 94 | 35 | 94 |  | 21 | Engin problem
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 106 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 488 | 471 | 543 | 474 | 40 | 177
| Total |  |  |  |  | 27054 | 25903 | 12681 | 15745 | 15063.6 | 16300 | 5194 | 2938
A. |  | 2024-06-08 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 15745 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11237 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 16400 | MW
3 | Day peak Generation : |  |  | 12681 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15631.2 | MW
4 | Evening peak Generation : |  |  | 15745 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 626 | MW
5 | Total Energy Generation : |  | 323.2432 | MKWHr | By Solar | 2.8001 | MKWHr
| By Gas : | 133.0419 | MKWHr |  | By Oil: | 47.9273 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 113.378 | MKWHr |  | By Hydro: | 2.6512 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.30768 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5194 | MW | Dhaka | 5577.9 | 5422.9 |  | 155 |  | 18:00 |  | 533.845
|  |  | For Plants S/D or M/C prob = |  |  | 2938 | MW | Chittagong | 1473 | 1407 |  | 66 |  | 19:00 |  | 493.735
|  |  | Total = |  |  | 8132 | MW | Khulna | 2039.4 | 2024.4 |  | 15 |  | 19:30 |  | 564.405
7 | Total Gas Supplied : |  |  | 975.65 | MMCFD |  |  | Rajshahi | 1643.8 | 1643.8 |  | 0 |  | 20:00 |  | 607.38
8 | Fuel Cost : | i) Gas : | Taka | 407913093.772 | ii) Oil : | Taka | 871803656.34 | Comilla | 1509 | 1376 |  | 133 |  | 21:00 |  | 625.525
|  | iii) Coal : | Taka | 769619355.55 | Total | Taka | 2049336105.662 | Mymensingh | 1226 | 1036 |  | 190 |  | 22:00 |  | 684.735
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5364.15 | MKWHr. | Sylhet | 594 | 594 |  | 0 |  | 23:00 |  | 634.12
| ii) During Peak Demand : |  |  | 536 | MW (W to E) at | 21:00 | hrs | Barisal | 516.1 | 516.1 |  | 0 |  | 24:00 |  | 571.09
| iii) Maximum : |  |  | 306 | MW at | 2:00 | hrs | Rangpur | 1052 | 985 |  | 67
10 | Maximum Temperature in Dhaka was |  |  |  | 35.6°C |  |  | Total | 15631.2 | 15005.2 |  | 626
B. |  | 2024-06-09 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 568 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16300 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14500 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 346.9552 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12608 | MW at | 8:00 | 100 | 70 | 80 | 80 | 80 | 100 | 0 | 0 | 58
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3178 | MKWHr. | ii) HVDC Flow at Peak Time |  | 779 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8192 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.17 |  | (b) Today: | 81.2 |  | (c) Rule Curve: |  | 78.08

## YesterdayGen
2024-06-08 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 142 | 48 | 48 | 30 | 330 | 0 | 0 | 65 | 58 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 15 | 23 | 25 | 21 | 0 | 0 | 70 | 38 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 48 | 85 | 80 | 26 | 6 | 0 | 42 | 0 | 0 | 0 | 285 | 240 | 221 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 43 | 0 | 0 | 32 | 12 | 68 | 43 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 45 | 0 | 0 | 97 | 0 | 97 | 0 | 25 | 17 | 130 | 366 | 58 | 17 | 34 | 0 | 52 | 17 | 110 | 17 | 43 | 25 | 340 | 56 | 0 | 35 | 35 | 0 | 17 | 0 | 69 | 35 | 240 | 17 | 0 | 490 | 23 | 764 | 0 | 0 | 0 |  | 783 | 0 | 210 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 76 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 70 | 0 | 99 | 0 | 0 | 70 | 1120 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 613 | 0 | 307 | 1391 | 0 | 0 |  | 7721 | 6065 | 13786 | 3888 | 783 | 1710 | 0 | 1998 | 4980 | 108 | 0 | 228 | 68 | 0 | 23 | 100 | 81.17
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 148 | 0 | 30 | 30 | 328 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 23 | 0 | 21 | 0 | 0 | 70 | 36 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 48 | 68 | 80 | 25 | 6 | 0 | 42 | 0 | 0 | 0 | 285 | 240 | 220 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 43 | 0 | 0 | 32 | 12 | 66 | 43 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 97 | 0 | 25 | 20 | 130 | 376 | 59 | 0 | 34 | 0 | 50 | 0 | 51 | 17 | 43 | 25 | 340 | 53 | 0 | 0 | 35 | 0 | 17 | 0 | 91 | 17 | 240 | 17 | 0 | 490 | 22 | 768 | 0 | 0 | 0 |  | 783 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 35 | 0 | 99 | 0 | 0 | 0 | 1040 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 591 | 0 | 307 | 1248 | 0 | 0 |  | 7273 | 5576 | 12849 | 3817 | 783 | 1716 | 0 | 1422 | 4738 | 106 | 0 | 179 | 66 | 0 | 22 | 0 | 81.17
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 151 | 0 | 0 | 30 | 331 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 23 | 0 | 21 | 0 | 0 | 70 | 36 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 48 | 51 | 80 | 26 | 6 | 0 | 42 | 0 | 0 | 0 | 285 | 240 | 220 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 43 | 0 | 0 | 32 | 12 | 64 | 43 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 60 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 97 | 0 | 25 | 17 | 0 | 366 | 45 | 0 | 34 | 0 | 50 | 0 | 34 | 17 | 38 | 25 | 340 | 53 | 0 | 0 | 18 | 0 | 0 | 0 | 115 | 17 | 240 | 17 | 0 | 490 | 13 | 768 | 0 | 0 | 0 |  | 925 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 521 | 0 | 307 | 1218 | 0 | 0 |  | 7041 | 5548 | 12589 | 3819 | 925 | 1739 | 0 | 1163 | 4598 | 106 | 0 | 162 | 64 | 0 | 13 | 0 | 81.17
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 150 | 0 | 0 | 30 | 334 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 23 | 25 | 21 | 0 | 0 | 70 | 35 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 1 | 48 | 51 | 80 | 25 | 6 | 0 | 42 | 0 | 0 | 0 | 285 | 240 | 220 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 43 | 0 | 0 | 32 | 0 | 56 | 44 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 60 | 0 | 0 | 207 | 0 | 0 | 0 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 97 | 0 | 25 | 17 | 0 | 366 | 45 | 0 | 34 | 0 | 52 | 0 | 34 | 17 | 38 | 25 | 340 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 109 | 17 | 240 | 17 | 0 | 490 | 17 | 765 | 0 | 0 | 0 |  | 924 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 990 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 531 | 0 | 220 | 1215 | 0 | 0 |  | 6992 | 5450 | 12442 | 3842 | 924 | 1733 | 0 | 1110 | 4493 | 105 | 0 | 162 | 56 | 0 | 17 | 0 | 81.17
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 149 | 0 | 0 | 30 | 334 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 23 | 25 | 21 | 0 | 0 | 70 | 36 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 48 | 51 | 80 | 25 | 6 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 221 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 30 | 34 | 0 | 0 | 32 | 12 | 54 | 44 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 60 | 0 | 0 | 207 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 97 | 0 | 25 | 17 | 0 | 366 | 45 | 0 | 34 | 0 | 52 | 0 | 34 | 17 | 38 | 25 | 340 | 53 | 0 | 0 | 17 | 0 | 0 | 0 | 108 | 17 | 240 | 17 | 0 | 490 | 20 | 768 | 0 | 0 | 0 |  | 925 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 920 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 528 | 0 | 220 | 1110 | 0 | 0 |  | 6995 | 5273 | 12268 | 3851 | 925 | 1727 | 0 | 1105 | 4318 | 106 | 0 | 162 | 54 | 0 | 20 | 0 | 81.17
6:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 412 | 0 |  | 0 | 370 | 150 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 23 | 25 | 21 | 0 | 0 | 70 | 36 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 48 | 51 | 36 | 25 | 6 | 0 | 42 | 0 | 0 | 0 | 285 | 240 | 222 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 34 | 0 | 0 | 32 | 12 | 56 | 44 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 62 | 0 | 0 | 207 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 97 | 1 | 25 | 17 | 0 | 366 | 45 | 0 | 34 | 0 | 52 | 0 | 34 | 20 | 38 | 25 | 340 | 45 | 4 | 0 | 17 | 0 | 0 | 1 | 106 | 17 | 240 | 17 | 0 | 440 | 16 | 763 | 0 | 0 | 0 |  | 925 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 870 | 180 | 0 | 0 | 0 | 4 | 75 | 0 | 0 | 475 | 1 | 220 | 1059 | 10 | 0 |  | 6749 | 5050 | 11799 | 3804 | 925 | 1630 | 0 | 970 | 4109 | 106 | 0 | 162 | 56 | 21 | 16 | 50 | 81.17
7:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 368 | 0 |  | 0 | 370 | 148 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 14 | 23 | 25 | 19 | 2 | 0 | 70 | 37 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 48 | 51 | 36 | 25 | 6 | 0 | 38 | 0 | 0 | 0 | 285 | 240 | 222 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 34 | 0 | 0 | 32 | 6 | 48 | 34 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 62 | 0 | 0 | 207 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 91 | 0 | 25 | 17 | 0 | 366 | 45 | 0 | 34 | 1 | 52 | 0 | 34 | 17 | 39 | 25 | 340 | 34 | 5 | 0 | 17 | 0 | 0 | 5 | 105 | 17 | 240 | 17 | 0 | 442 | 18 | 768 | 0 | 0 | 1 |  | 926 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 90 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 780 | 180 | 0 | 0 | 0 | 13 | 35 | 0 | 0 | 462 | 4 | 220 | 1017 | 11 | 0 |  | 6681 | 4881 | 11562 | 3742 | 926 | 1634 | 0 | 912 | 3972 | 107 | 0 | 162 | 48 | 41 | 18 | 46 | 81.17
8:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 361 | 0 |  | 0 | 330 | 148 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 14 | 23 | 25 | 18 | 8 | 0 | 70 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 3 | 47 | 51 | 12 | 25 | 6 | 0 | 14 | 0 | 0 | 0 | 285 | 240 | 218 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 34 | 0 | 0 | 32 | 6 | 62 | 28 | 0 | 0 | 0 | 41 | 48 | 53 | 42 | 120 | 0 | 61 | 0 | 0 | 207 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 92 | 8 | 25 | 17 | 0 | 316 | 24 | 0 | 34 | 0 | 52 | 0 | 34 | 17 | 38 | 25 | 310 | 35 | 2 | 0 | 17 | 0 | 0 | 0 | 100 | 34 | 240 | 17 | 0 | 440 | 10 | 767 | 0 | 0 | 6 |  | 925 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 91 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 700 | 180 | 0 | 0 | 0 | 32 | 35 | 0 | 0 | 416 | 5 | 220 | 1017 | 22 | 0 |  | 6488 | 4749 | 11237 | 3650 | 925 | 1510 | 0 | 855 | 3844 | 110 | 0 | 193 | 62 | 78 | 10 | 41.065 | 81.17
9:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 363 | 0 |  | 0 | 330 | 151 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 14 | 23 | 17 | 18 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 46 | 51 | 12 | 24 | 0 | 0 | 3 | 0 | 0 | 0 | 345 | 240 | 217 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 34 | 0 | 0 | 32 | 6 | 70 | 28 | 0 | 0 | 1 | 41 | 48 | 53 | 42 | 120 | 0 | 61 | 0 | 0 | 207 | 0 | 0 | 0 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 97 | 13 | 25 | 17 | 0 | 310 | 24 | 35 | 34 | 0 | 52 | 0 | 34 | 17 | 39 | 25 | 326 | 33 | 9 | 0 | 17 | 0 | 0 | 15 | 50 | 35 | 240 | 17 | 0 | 440 | 7 | 768 | 0 | 0 | 19 |  | 925 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 91 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 700 | 180 | 0 | 0 | 1 | 51 | 35 | 0 | 0 | 410 | 6 | 220 | 1015 | 81 | 0 |  | 6592 | 4823 | 11415 | 3713 | 925 | 1527 | 0 | 841 | 3847 | 115 | 0 | 169 | 70 | 201 | 7 | 57.3 | 81.17
10:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 390 | 0 |  | 0 | 380 | 150 | 0 | 0 | 30 | 315 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 13 | 23 | 25 | 18 | 33 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 51 | 12 | 28 | 0 | 0 | 6 | 0 | 0 | 0 | 320 | 240 | 207 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 28 | 0 | 0 | 32 | 6 | 68 | 28 | 0 | 0 | 1 | 41 | 48 | 53 | 42 | 120 | 0 | 61 | 0 | 0 | 209 | 0 | 0 | 0 | 315 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 97 | 5 | 25 | 17 | 0 | 402 | 56 | 52 | 34 | 1 | 52 | 0 | 34 | 17 | 38 | 25 | 370 | 46 | 8 | 0 | 17 | 0 | 0 | 17 | 50 | 35 | 240 | 17 | 0 | 440 | 6 | 765 | 0 | 0 | 32 |  | 925 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 700 | 220 | 0 | 0 | 2 | 88 | 35 | 0 | 0 | 410 | 7 | 220 | 1017 | 99 | 0 |  | 6902 | 4901 | 11803 | 3919 | 925 | 1629 | 0 | 878 | 3847 | 115 | 0 | 153 | 68 | 263 | 6 | 83.085 | 81.17
11:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 148 | 2 | 0 | 30 | 316 | 0 | 0 | 3 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 13 | 23 | 25 | 18 | 33 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 51 | 12 | 31 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 240 | 218 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 26 | 25 | 0 | 0 | 32 | 6 | 76 | 28 | 0 | 0 | 1 | 41 | 48 | 53 | 36 | 163 | 0 | 62 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 84 | 0 | 97 | 7 | 25 | 17 | 8 | 366 | 59 | 52 | 34 | 5 | 52 | 0 | 34 | 17 | 38 | 25 | 340 | 50 | 51 | 0 | 17 | 0 | 0 | 31 | 50 | 35 | 230 | 17 | 0 | 440 | 13 | 749 | 0 | 0 | 40 |  | 924 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 800 | 220 | 0 | 0 | 1 | 90 | 35 | 0 | 0 | 402 | 11 | 299 | 1119 | 179 | 0 |  | 7117 | 5310 | 12427 | 3838 | 924 | 1766 | 0 | 999 | 4103 | 115 | 0 | 172 | 76 | 421 | 13 | 117.465 | 81.18
12:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 152 | 19 | 12 | 30 | 317 | 0 | 0 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 13 | 23 | 33 | 18 | 33 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 34 | 12 | 32 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 35 | 16 | 0 | 0 | 32 | 6 | 82 | 28 | 0 | 0 | 2 | 41 | 48 | 53 | 34 | 163 | 0 | 61 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 93 | 0 | 91 | 3 | 25 | 17 | 50 | 367 | 59 | 52 | 34 | 2 | 51 | 0 | 34 | 17 | 39 | 25 | 383 | 51 | 46 | 0 | 17 | 0 | 0 | 32 | 50 | 35 | 230 | 17 | 0 | 440 | 32 | 748 | 0 | 0 | 34 |  | 923 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 860 | 220 | 0 | 0 | 2 | 84 | 35 | 0 | 0 | 405 | 28 | 299 | 1209 | 106 | 0 |  | 7299 | 5382 | 12681 | 3870 | 923 | 1768 | 0 | 1126 | 4244 | 115 | 0 | 180 | 82 | 341 | 32 | 161.395 | 81.18
13:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 146 | 24 | 19 | 30 | 312 | 0 | 0 | 25 | 24 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 13 | 23 | 33 | 18 | 33 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 34 | 12 | 32 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 207 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 35 | 16 | 0 | 0 | 32 | 6 | 84 | 11 | 0 | 0 | 1 | 40 | 48 | 53 | 36 | 163 | 0 | 55 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 93 | 0 | 87 | 13 | 25 | 17 | 50 | 408 | 59 | 52 | 34 | 5 | 51 | 0 | 34 | 17 | 37 | 25 | 370 | 51 | 38 | 54 | 17 | 0 | 0 | 29 | 50 | 22 | 230 | 17 | 0 | 440 | 0 | 750 | 0 | 0 | 40 |  | 924 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 940 | 220 | 0 | 0 | 1 | 90 | 35 | 0 | 0 | 404 | 24 | 307 | 1220 | 140 | 0 |  | 7372 | 5505 | 12877 | 3850 | 924 | 1771 | 0 | 1173 | 4345 | 115 | 0 | 230 | 84 | 385 | 0 | 151 | 81.18
14:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 150 | 34 | 17 | 55 | 312 | 0 | 0 | 35 | 40 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 13 | 23 | 33 | 18 | 33 | 0 | 75 | 38 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 34 | 70 | 37 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 41 | 16 | 0 | 0 | 32 | 3 | 88 | 11 | 0 | 0 | 1 | 41 | 48 | 53 | 33 | 120 | 0 | 55 | 0 | 0 | 205 | 0 | 0 | 0 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 93 | 0 | 89 | 1 | 25 | 17 | 55 | 367 | 59 | 52 | 34 | 4 | 51 | 0 | 34 | 17 | 38 | 25 | 345 | 51 | 30 | 108 | 17 | 0 | 0 | 19 | 50 | 32 | 230 | 17 | 0 | 485 | 0 | 750 | 0 | 0 | 60 |  | 924 | 0 | 200 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 | 0 | 34 | 0 | 6 | 0 | 1060 | 180 | 0 | 0 | 3 | 80 | 35 | 0 | 0 | 450 | 21 | 307 | 1266 | 161 | 0 |  | 7500 | 5679 | 13179 | 3736 | 924 | 1698 | 0 | 1398 | 4600 | 113 | 0 | 236 | 88 | 386 | 0 | 211.055 | 81.18
15:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 397 | 0 |  | 0 | 450 | 150 | 47 | 17 | 55 | 310 | 0 | 0 | 63 | 80 | 115 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 13 | 23 | 33 | 18 | 33 | 0 | 75 | 36 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 34 | 70 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 41 | 16 | 0 | 0 | 32 | 6 | 92 | 11 | 0 | 0 | 1 | 41 | 48 | 53 | 33 | 163 | 0 | 55 | 0 | 0 | 200 | 0 | 0 | 0 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 93 | 0 | 88 | 2 | 25 | 17 | 78 | 367 | 58 | 52 | 35 | 3 | 52 | 0 | 38 | 17 | 38 | 25 | 345 | 51 | 24 | 160 | 17 | 0 | 4 | 15 | 50 | 19 | 230 | 17 | 0 | 490 | 7 | 771 | 0 | 0 | 41 |  | 923 | 0 | 180 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 1 | 0 | 34 | 0 | 5 | 25 | 1100 | 220 | 0 | 0 | 2 | 70 | 65 | 0 | 0 | 493 | 11 | 307 | 1351 | 106 | 0 |  | 7724 | 5871 | 13595 | 3730 | 923 | 1781 | 0 | 1624 | 4794 | 111 | 0 | 253 | 92 | 280 | 7 | 434.525 | 81.18
16:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 341 | 0 |  | 0 | 450 | 149 | 63 | 17 | 55 | 260 | 0 | 0 | 76 | 80 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 13 | 23 | 33 | 18 | 33 | 0 | 75 | 36 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 46 | 34 | 70 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 210 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 35 | 16 | 0 | 0 | 32 | 2 | 90 | 12 | 0 | 0 | 1 | 41 | 48 | 50 | 33 | 163 | 0 | 54 | 0 | 0 | 201 | 0 | 0 | 0 | 290 | 8 | 8 | 0 | 35 | 0 | 0 | 93 | 0 | 76 | 0 | 25 | 25 | 105 | 389 | 58 | 52 | 51 | 2 | 52 | 0 | 51 | 17 | 37 | 25 | 345 | 51 | 7 | 162 | 17 | 0 | 17 | 9 | 50 | 35 | 230 | 17 | 0 | 490 | 5 | 780 | 0 | 0 | 18 |  | 922 | 0 | 185 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1060 | 220 | 0 | 0 | 2 | 51 | 72 | 0 | 0 | 494 | 13 | 307 | 1358 | 65 | 0 |  | 7733 | 5776 | 13509 | 3640 | 922 | 1708 | 0 | 1847 | 4769 | 111 | 0 | 247 | 90 | 170 | 5 | 564.405 | 81.18
17:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 340 | 0 |  | 0 | 450 | 148 | 78 | 18 | 55 | 260 | 0 | 0 | 76 | 80 | 92 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 13 | 23 | 33 | 18 | 32 | 0 | 75 | 36 | 0 | 0 | 5 | 219 | 0 | 0 | 0 |  | 0 | 46 | 34 | 70 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 20 | 0 | 0 | 0 | 10 | 0 | 39 | 25 | 0 | 0 | 32 | 6 | 86 | 18 | 0 | 0 | 1 | 41 | 48 | 11 | 10 | 120 | 0 | 40 | 0 | 0 | 201 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 45 | 0 | 0 | 93 | 0 | 70 | 1 | 25 | 17 | 107 | 367 | 58 | 52 | 51 | 0 | 52 | 0 | 51 | 17 | 39 | 25 | 345 | 51 | 8 | 162 | 17 | 0 | 17 | 7 | 66 | 35 | 230 | 17 | 0 | 490 | 19 | 750 | 0 | 0 | 13 |  | 923 | 0 | 185 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 14 | 0 | 20 | 0 | 0 | 5 | 59 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 36 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1000 | 220 | 0 | 0 | 0 | 24 | 72 | 0 | 0 | 608 | 5 | 263 | 1330 | 41 | 0 |  | 7622 | 5732 | 13354 | 3644 | 923 | 1579 | 0 | 1911 | 4710 | 111 | 0 | 270 | 86 | 101 | 19 | 569.18 | 81.18
18:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 340 | 0 |  | 0 | 400 | 137 | 89 | 17 | 55 | 260 | 0 | 0 | 76 | 80 | 114 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 13 | 0 | 31 | 18 | 32 | 0 | 75 | 36 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 2 | 65 | 51 | 70 | 38 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 214 | 8 | 50 | 0 | 0 | 0 | 10 | 0 | 41 | 34 | 0 | 0 | 32 | 6 | 80 | 20 | 0 | 0 | 0 | 41 | 48 | 11 | 10 | 120 | 0 | 40 | 0 | 0 | 202 | 0 | 0 | 0 | 280 | 24 | 8 | 0 | 45 | 0 | 0 | 93 | 0 | 78 | 0 | 25 | 17 | 108 | 317 | 58 | 52 | 51 | 0 | 50 | 11 | 71 | 17 | 70 | 25 | 310 | 59 | 3 | 162 | 17 | 0 | 17 | 2 | 70 | 35 | 230 | 17 | 0 | 440 | 13 | 750 | 0 | 0 | 5 |  | 924 | 0 | 190 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 16 | 0 | 50 | 0 | 0 | 21 | 0 | 36 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 36 | 0 | 35 | 0 | 40 | 0 | 0 | 35 | 930 | 220 | 0 | 0 | 0 | 6 | 73 | 0 | 0 | 715 | 2 | 220 | 1264 | 5 | 0 |  | 7573 | 5668 | 13241 | 3584 | 924 | 1475 | 0 | 2031 | 4589 | 111 | 0 | 411 | 80 | 23 | 13 | 533.845 | 81.18
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 372 | 0 |  | 0 | 450 | 150 | 88 | 17 | 55 | 309 | 0 | 0 | 76 | 80 | 146 | 16 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 6 | 32 | 18 | 32 | 0 | 75 | 37 | 0 | 0 | 15 | 220 | 0 | 0 | 0 |  | 5 | 65 | 85 | 70 | 38 | 12 | 0 | 12 | 0 | 0 | 0 | 280 | 240 | 210 | 8 | 50 | 0 | 0 | 0 | 32 | 0 | 41 | 43 | 0 | 0 | 32 | 0 | 92 | 31 | 0 | 0 | 0 | 41 | 48 | 53 | 25 | 120 | 0 | 40 | 0 | 0 | 202 | 0 | 0 | 0 | 285 | 24 | 5 | 0 | 100 | 0 | 0 | 121 | 0 | 89 | 0 | 25 | 17 | 103 | 368 | 77 | 52 | 51 | 0 | 50 | 27 | 95 | 17 | 74 | 25 | 370 | 70 | 0 | 162 | 38 | 0 | 17 | 0 | 103 | 35 | 230 | 72 | 0 | 440 | 14 | 747 | 0 | 0 | 0 |  | 923 | 0 | 190 | 0 | 31 | 0 | 0 | 0 | 28 | 23 | 0 | 126 | 10 | 16 | 0 | 0 | 0 | 31 | 9 | 85 | 25 | 0 | 35 | 0 | 36 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 35 | 0 | 78 | 0 | 0 | 35 | 970 | 180 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 716 | 0 | 276 | 1354 | 0 | 0 |  | 8329 | 6104 | 14433 | 3782 | 923 | 1675 | 0 | 2405 | 4774 | 112 | 0 | 656 | 92 | 0 | 14 | 493.735 | 81.18
19:30 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 151 | 89 | 17 | 55 | 317 | 0 | 0 | 76 | 80 | 146 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 23 | 32 | 18 | 32 | 0 | 75 | 37 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 12 | 58 | 85 | 70 | 38 | 15 | 0 | 16 | 0 | 0 | 0 | 280 | 240 | 215 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 6 | 90 | 31 | 0 | 0 | 0 | 41 | 48 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 285 | 24 | 5 | 0 | 260 | 0 | 0 | 121 | 0 | 97 | 0 | 25 | 17 | 115 | 367 | 77 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 74 | 25 | 340 | 70 | 0 | 162 | 53 | 0 | 17 | 0 | 105 | 35 | 230 | 72 | 0 | 440 | 14 | 751 | 0 | 0 | 0 |  | 923 | 0 | 190 | 0 | 47 | 0 | 0 | 0 | 38 | 32 | 24 | 126 | 10 | 16 | 0 | 0 | 0 | 38 | 9 | 88 | 35 | 0 | 35 | 0 | 36 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 50 | 0 | 103 | 0 | 0 | 90 | 1200 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 773 | 0 | 307 | 1415 | 0 | 0 |  | 8698 | 6661 | 15359 | 3866 | 923 | 1713 | 0 | 2806 | 5157 | 112 | 0 | 678 | 90 | 0 | 14 | 564.405 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 89 | 17 | 55 | 316 | 0 | 0 | 76 | 81 | 147 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 23 | 32 | 18 | 32 | 0 | 75 | 38 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 12 | 58 | 85 | 70 | 37 | 19 | 0 | 12 | 0 | 0 | 0 | 300 | 250 | 215 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 6 | 86 | 31 | 0 | 0 | 0 | 42 | 48 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 290 | 24 | 5 | 0 | 253 | 0 | 0 | 121 | 0 | 97 | 0 | 25 | 17 | 115 | 367 | 78 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 340 | 71 | 0 | 162 | 53 | 0 | 17 | 0 | 104 | 35 | 230 | 80 | 0 | 448 | 15 | 750 | 0 | 0 | 0 |  | 779 | 0 | 190 | 0 | 58 | 0 | 0 | 0 | 47 | 40 | 24 | 126 | 10 | 16 | 0 | 0 | 0 | 39 | 10 | 88 | 35 | 0 | 48 | 0 | 36 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 90 | 0 | 106 | 0 | 0 | 110 | 1220 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 823 | 0 | 307 | 1409 | 0 | 0 |  | 8737 | 6677 | 15414 | 3892 | 779 | 1703 | 0 | 2879 | 5228 | 113 | 0 | 719 | 86 | 0 | 15 | 607.38 | 81.18
21:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 90 | 20 | 55 | 316 | 0 | 0 | 72 | 81 | 147 | 25 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 13 | 23 | 32 | 19 | 32 | 0 | 75 | 38 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 12 | 58 | 85 | 70 | 38 | 19 | 0 | 26 | 0 | 0 | 0 | 300 | 300 | 217 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 6 | 78 | 34 | 0 | 0 | 0 | 41 | 48 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 290 | 14 | 5 | 0 | 240 | 0 | 0 | 120 | 0 | 97 | 0 | 25 | 17 | 122 | 367 | 78 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 340 | 71 | 0 | 162 | 53 | 0 | 17 | 0 | 115 | 35 | 245 | 125 | 0 | 470 | 17 | 624 | 0 | 0 | 0 |  | 779 | 0 | 190 | 0 | 46 | 0 | 0 | 0 | 41 | 45 | 40 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 10 | 88 | 35 | 0 | 45 | 0 | 36 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 1013 | 0 | 307 | 1456 | 0 | 0 |  | 8740 | 7005 | 15745 | 3952 | 779 | 1800 | 0 | 2860 | 5385 | 113 | 0 | 761 | 78 | 0 | 17 | 625.525 | 81.18
22:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 355 | 0 |  | 0 | 450 | 153 | 89 | 55 | 55 | 270 | 0 | 0 | 70 | 81 | 147 | 14 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 13 | 23 | 32 | 19 | 32 | 0 | 75 | 40 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 12 | 66 | 85 | 70 | 38 | 6 | 0 | 32 | 0 | 0 | 0 | 280 | 255 | 200 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 36 | 51 | 0 | 0 | 32 | 6 | 96 | 34 | 0 | 0 | 0 | 42 | 48 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 206 | 0 | 0 | 0 | 275 | 16 | 5 | 0 | 263 | 0 | 0 | 120 | 0 | 97 | 0 | 25 | 17 | 133 | 367 | 78 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 320 | 71 | 0 | 162 | 53 | 0 | 17 | 0 | 106 | 35 | 230 | 125 | 0 | 470 | 18 | 616 | 0 | 0 | 0 |  | 779 | 0 | 190 | 0 | 34 | 0 | 0 | 0 | 41 | 44 | 32 | 126 | 10 | 16 | 0 | 0 | 0 | 39 | 10 | 88 | 35 | 0 | 38 | 0 | 36 | 0 | 0 | 5 | 62 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 1021 | 0 | 307 | 1474 | 0 | 0 |  | 8580 | 7003 | 15583 | 3749 | 779 | 1794 | 0 | 2873 | 5404 | 115 | 0 | 755 | 96 | 0 | 18 | 684.735 | 81.18
23:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 382 | 0 |  | 0 | 450 | 151 | 88 | 65 | 55 | 320 | 0 | 0 | 70 | 81 | 132 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 13 | 23 | 25 | 19 | 15 | 0 | 75 | 40 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 66 | 85 | 70 | 38 | 6 | 0 | 30 | 0 | 0 | 0 | 295 | 240 | 214 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 36 | 50 | 0 | 0 | 32 | 6 | 96 | 35 | 0 | 0 | 0 | 40 | 48 | 53 | 39 | 163 | 0 | 55 | 0 | 0 | 207 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 270 | 0 | 0 | 120 | 0 | 97 | 0 | 25 | 17 | 135 | 375 | 78 | 52 | 17 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 312 | 71 | 0 | 162 | 53 | 0 | 17 | 0 | 80 | 35 | 250 | 17 | 0 | 475 | 14 | 642 | 0 | 0 | 0 |  | 779 | 0 | 190 | 0 | 30 | 0 | 0 | 0 | 33 | 45 | 32 | 130 | 10 | 32 | 0 | 0 | 0 | 38 | 10 | 83 | 35 | 0 | 38 | 0 | 36 | 0 | 0 | 5 | 62 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 1069 | 0 | 307 | 1479 | 0 | 0 |  | 8527 | 7059 | 15586 | 3858 | 779 | 1815 | 0 | 2802 | 5488 | 115 | 0 | 619 | 96 | 0 | 14 | 634.12 | 81.18
24:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 150 | 89 | 65 | 44 | 320 | 0 | 0 | 70 | 82 | 132 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 13 | 23 | 25 | 23 | 8 | 0 | 75 | 40 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 66 | 85 | 70 | 37 | 6 | 0 | 26 | 0 | 0 | 0 | 280 | 240 | 215 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 36 | 50 | 0 | 0 | 32 | 6 | 96 | 34 | 0 | 0 | 0 | 40 | 48 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 8 | 0 | 0 | 278 | 0 | 0 | 126 | 0 | 97 | 0 | 25 | 17 | 137 | 367 | 78 | 35 | 17 | 0 | 52 | 35 | 110 | 17 | 69 | 25 | 310 | 71 | 0 | 162 | 53 | 0 | 17 | 0 | 72 | 35 | 250 | 17 | 0 | 472 | 17 | 601 | 0 | 0 | 0 |  | 779 | 0 | 190 | 0 | 30 | 0 | 0 | 0 | 29 | 52 | 32 | 130 | 10 | 48 | 0 | 0 | 0 | 38 | 10 | 83 | 35 | 0 | 37 | 0 | 36 | 0 | 0 | 5 | 63 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 1067 | 0 | 307 | 1474 | 0 | 0 |  | 8380 | 7072 | 15452 | 3847 | 779 | 1810 | 0 | 2729 | 5438 | 115 | 0 | 621 | 96 | 0 | 17 | 571.09 | 81.18
KWH | 0 | 0 | 0 | 4205250 | 0 | 0 | 0 | 9356400 | 0 |  | 0 | 9926500 | 3552204 | 936960 | 400009 | 997231 | 7300412 | 0 | 0 | 833280 | 984528 | 1768800 | 75781 | 0 | 0 | 0 | 365760 | 664980 | 667280 | 0 | 32700 | 503640 | 608000 | 450500 | 453120 | 0 | 1735200 | 916000 | 0 | 0 | 97837 | 5286388 | 0 | 0 | 0 |  | 133920 | 1134096 | 1359918 | 1258320 | 775680 | 123360 | 0 | 494400 | 0 | 0 | 0 | 7324100 | 5997000 | 5238000 | 66909 | 466270 | 0 | 0 | 0 | 1038610 | 0 | 811584 | 825590 | 0 | 0 | 753000 | 152900 | 1819200 | 678720 | 0 | 0 | 9500 | 967000 | 1142400 | 1194600 | 885240 | 3468191 | 0 | 1357920 | 0 | 0 | 5127220 | 0 | 0 | 0 | 7112000 | 384240 | 139728 | 0 | 1605818 | 0 | 0 | 1934400 | 0 | 2231280 | 61560 | 589440 | 433920 | 1737963 | 8796000 | 1382400 | 821760 | 952618 | 21602 | 1242000 | 259172 | 1556471 | 430920 | 1181040 | 598080 | 8148700 | 1306560 | 253780 | 1804320 | 658636 | 0 | 198000 | 179886 | 1944960 | 734040 | 5821000 | 744363 | 0 | 11203635 | 307680 | 17832727 | 0 | 0 | 337055 |  | 21317818 | 0 | 5105664 | 0 | 446400 | 0 | 0 | 0 | 187200 | 213888 | 181875 | 2510000 | 177554 | 123840 | 0 | 0 | 0 | 222732 | 46520 | 534800 | 168560 | 0 | 211208 | 0 | 238267 | 0 | 0 | 129726 | 1455272 | 0 | 5346000 | 0 | 0 | 3984127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8206400 | 1403040 | 0 | 847104 | 0 | 1584998 | 0 | 36485 | 799968 | 25851700 | 4952318 | 0 | 0 | 21960 | 713520 | 1700736 | 0 | 0 | 15061815 | 136963 | 6632700 | 29994124 | 1027750 | 0 |  | 181670162 | 141573032 | 323243194 | 91967005 | 21317818 | 41074926 | 0 | 40453955 | 113377973 | 2651200 | 0 | 7473376 | 1819200 | 2800061 | 307680 | 0
Fuel Cost | 0 | 0 | 0 | 18713362.5 | 0 | 0 | 0 | 26946432 | 0 |  | 0 | 31566270 | 12148537.68 | 18514329.6 | 7480168.3 | 17571210.22 | 22266256.6 | 0 | 0 | 16465612.8 | 17672277.6 | 34350096 | 1413315.65 | 0 | 0 | 0 | 6678777.6 | 10480084.8 | 12204551.2 | 0 | 24525 | 0 | 0 | 0 | 8115379.2 | 0 | 0 | 0 | 0 | 0 | 1853032.78 | 16863577.72 | 0 | 0 | 0 |  | 2355652.8 | 19971430.56 | 24356131.38 | 23983579.2 | 15180057.6 | 2030505.6 | 0 | 0 | 0 | 0 | 0 | 20434239 | 18350820 | 17390160 | 224145.15 | 1506052.1 | 0 | 0 | 0 | 4164826.1 | 0 | 14535469.44 | 14910155.4 | 0 | 0 | 2801160 | 114675 | 11933952 | 2110819.2 | 0 | 0 | 0 | 3771300 | 4261152 | 5435430 | 4027842 | 11861213.22 | 0 | 7536456 | 0 | 0 | 14304943.8 | 0 | 0 | 0 | 21976080 | 288180 | 106193.28 | 0 | 32758687.2 | 0 | 0 | 37159824 | 0 | 39292840.8 | 0 | 10497926.4 | 7528512 | 28815426.54 | 23309400 | 26348544 | 15416217.6 | 17089966.92 | 0 | 20306700 | 5038303.68 | 27923089.74 | 8234881.2 | 22923986.4 | 10651804.8 | 21675542 | 22302979.2 | 0 | 33001012.8 | 11051912.08 | 0 | 3538260 | 0 | 35048179.2 | 12434637.6 | 17288370 | 10480631.04 | 0 | 78089335.95 | 0 | 105213089.3 | 0 | 0 | 0 |  | 59903068.58 | 0 | 15061708.8 | 0 | 7745040 | 0 | 0 | 0 | 3521232 | 4023233.28 | 3237375 | 7931600 | 841605.96 | 2135001.6 | 0 | 0 | 0 | 3989130.12 | 853642 | 8989988 | 3586956.8 | 0 | 3782735.28 | 0 | 4267361.97 | 0 | 0 | 98202.582 | 16051650.16 | 0 | 45120240 | 0 | 0 | 13147619.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23962688 | 23963923.2 | 0 | 16789601.28 | 0 | 31573160.16 | 0 | 0 | 15871365.12 | 167519016 | 15401708.98 | 0 | 0 | 0 | 0 | 29507769.6 | 0 | 0 | 109951249.5 | 0 | 49413615 | 198261159.64 | 0 | 0 |  | 1234670478.53 | 886502647.712 | 2121173126.242 | 276302746.682 | 59903068.58 | 131610347.09 | 0 | 738682575.27 | 769619355.55 | 0 | 0 | 133121081.07 | 11933952 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 152 | 19 | 12 | 30 | 317 | 0 | 0 | 25 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 13 | 23 | 33 | 18 | 33 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 46 | 34 | 12 | 32 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 35 | 16 | 0 | 0 | 32 | 6 | 82 | 28 | 0 | 0 | 2 | 41 | 48 | 53 | 34 | 163 | 0 | 61 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 93 | 0 | 91 | 3 | 25 | 17 | 50 | 367 | 59 | 52 | 34 | 2 | 51 | 0 | 34 | 17 | 39 | 25 | 383 | 51 | 46 | 0 | 17 | 0 | 0 | 32 | 50 | 35 | 230 | 17 | 0 | 440 | 32 | 748 | 0 | 0 | 34 |  | 923 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 36 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 860 | 220 | 0 | 0 | 2 | 84 | 35 | 0 | 0 | 405 | 28 | 299 | 1209 | 106 | 0 |  | 12681 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 90 | 20 | 55 | 316 | 0 | 0 | 72 | 81 | 147 | 25 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 13 | 23 | 32 | 19 | 32 | 0 | 75 | 38 | 0 | 0 | 17 | 219 | 0 | 0 | 0 | 0 | 12 | 58 | 85 | 70 | 38 | 19 | 0 | 26 | 0 | 0 | 0 | 300 | 300 | 217 | 8 | 80 | 0 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 6 | 78 | 34 | 0 | 0 | 0 | 41 | 48 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 204 | 0 | 0 | 0 | 290 | 14 | 5 | 0 | 240 | 0 | 0 | 120 | 0 | 97 | 0 | 25 | 17 | 122 | 367 | 78 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 340 | 71 | 0 | 162 | 53 | 0 | 17 | 0 | 115 | 35 | 245 | 125 | 0 | 470 | 17 | 624 | 0 | 0 | 0 |  | 779 | 0 | 190 | 0 | 46 | 0 | 0 | 0 | 41 | 45 | 40 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 10 | 88 | 35 | 0 | 45 | 0 | 36 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 36 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 1013 | 0 | 307 | 1456 | 0 | 0 |  | 15745 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 90 | 65 | 55 | 330 | 0 | 0 | 76 | 82 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 23 | 33 | 28 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 12 | 64 | 85 | 70 | 38 | 18 | 0 | 20 | 0 | 0 | 0 | 300 | 280 | 220 | 8 | 80 | 10 | 0 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 6 | 151 | 40 | 0 | 0 | 0 | 40 | 48 | 53 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 270 | 0 | 0 | 120 | 0 | 97 | 0 | 25 | 17 | 130 | 380 | 80 | 52 | 51 | 0 | 52 | 35 | 110 | 17 | 75 | 25 | 340 | 70 | 0 | 162 | 53 | 0 | 17 | 0 | 115 | 35 | 250 | 163 | 0 | 470 | 40 | 700 | 0 | 0 |  |  | 801 | 0 | 200 | 0 | 50 | 0 | 0 | 0 | 50 | 60 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 88 | 35 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 64 | 0 | 210 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 53 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 94 | 0 | 0 | 1000 | 0 | 307 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 420 | 150 | 90 | 65 | 55 | 290 | 0 | 0 | 70 | 82 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 0 | 12 | 21 | 33 | 20 | 8 | 0 | 75 | 40 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 32 | 50 | 70 | 30 | 6 | 0 | 15 | 0 | 0 |  | 280 | 280 | 200 | 8 | 80 | 10 | 0 | 0 | 43 | 0 | 40 | 25 | 0 | 0 | 32 | 6 | 146 | 30 | 0 | 0 | 1.6 | 40 | 48 | 53 | 40 | 163 | 0 | 56 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 270 | 0 | 0 | 90 | 0 | 90 | 20 | 25 | 17 | 130 | 350 | 60 | 52 | 51 | 5 | 52 | 35 | 85 | 17 | 37 | 24 | 320 | 50 | 50 | 162 | 35 | 0 | 17 | 35 | 115 | 34 | 240 | 54 | 0 | 470 | 40 | 700 | 0 | 0 | 70 |  | 943 | 0 | 200 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 94 | 0 | 70 | 0 | 8 | 113 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 1000 | 30 | 307 | 1200 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 420 | 152 | 9 | 17 | 55 | 250 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 14 | 23 | 25 | 28 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 6 | 48 | 34 | 58 | 25 | 6 | 0 | 6 | 0 | 0 | 0 | 280 | 240 | 205 | 0 | 80 | 10 | 0 | 0 | 51 | 0 | 0 | 34 | 0 | 0 | 32 | 0 | 84 | 29 | 0 | 0 | 0 | 40 | 48 | 53 | 40 | 120 | 0 | 63 | 0 | 0 | 208 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 98 | 0 | 88 | 10 | 25 | 17 | 130 | 366 | 59 | 17 | 17 | 3 | 52 | 35 | 94 | 17 | 38 | 25 | 320 | 35 | 1 | 0 | 17 | 0 | 0 | 4 | 93 | 35 | 230 | 0 | 0 | 470 | 1 | 605 | 0 | 0 | 33 | 0 | 923 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 210 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 900 | 220 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 1016 | 1 | 250 | 1121 | 8 | 0 | 0 |  |  |  | 133041931 | 21317818 | 0 | 113377973 | 47927331 | 1819200 | 2800061 | 307680 | 2651200 |  |  | 323243194
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [8 empty] | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 133.0419 | 21.3178 | 0 | 113.378 | 47.9273 | 1.8192 | 2.8001 | 0.30768 | 2.6512
| Minimum Generation |  | 11237 | 8:00
| Highest Generation |  | 15745 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 323.2432
| Day Peak Generation |  | 12681 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15745 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 926 | 7:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 779 | 21:00
| Load factor L.F |  | 85.54% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-09
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12681 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12608
Evening Peak Generation : |  |  | 15745 | MW Hour : | 21:00 | Available Max Generation : |  | 16300
E.P. Demand (at gen end) : |  |  | 16400 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16900
Maximum Generation : |  |  | 15745 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 323.2432 | System Load Factor : | 85.54% | Load Shed : |  | 568
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 306 | MW at | 2:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-09
Actual : |  | 81.2 | Ft.(MSL) , | Rule curve : | 78.08 | Ft.( MSL )
Gas Consumed : |  | Total = | 975.65 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 407913093.772
: |  |  | Coal : | 769619355.55 | Oil : | 871803656.34 | Total : | 2049336105.662
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 155 | 3720:00 | 5277.8352 |  |  | 100 | 1.895%
Chittagong Area |  | 66 | 1584:00 | 1454.5136 |  |  | 70 | 4.813%
Khulna Area |  | 15 | 360:00 | 2038.779 |  |  | 80 | 3.924%
Rajshahi Area |  | 0 | 0:00 | 1773.2563 |  |  | 80 | 4.511%
Cumilla Area |  | 133 | 3192:00 | 1458.4679 |  |  | 80 | 5.485%
Mymensingh Area |  | 190 | 4560:00 | 1085.3681 |  |  | 100 | 9.213%
Sylhet Area |  | 0 | 0:00 | 607.7026 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 507.0683 |  |  | 0 | 0%
Rangpur Area |  | 67 | 1608:00 | 991.7224 |  |  | 58 | 5.848%
Total |  | 626 |  | 15194.7134 |  |  | 568
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:17 | 11:42 | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 Project Work S/D Due to 132 kv busbar scheme change.
08:31 | 17:47 | Mymensingh RPCL-Tangail 132kV Ckt-2 Project Work S/D from Ghatail 132/33kV end Due to LILO Connection work for 132kV
Muktagasa ss Under G2G Project.
08:41 | 12:54 | Hasnabad 230/132kV S/S Bus-1 Scheduled S/D Due to DS-811M high temperature found.
08:53 | 12:10 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Project Work S/D Due to PROJECT WORK OF NESCO
09:08 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 LT Scheduled S/D Due to Control Cable Re-winding
09:09 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-02 HT Scheduled S/D Due to Control Cable Re-winding
09:14 | 12:23 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to By order NLDC.Work at
Mymensingh End. and from Mymensingh 132/33kV end Due to Tower Space Measurment
| 09:15 | Jamalpur 132/33kV S/S T-2 LT is restored.
| 09:15 | Jamalpur 132/33kV S/S T-2 HT is restored.
| 09:15 | Jamalpur 132/33kV S/S T-1 HT is restored.
| 09:15 | Jamalpur 132/33kV S/S T-1 LT is restored.
| 09:30 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT is restored.
| 09:31 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT is restored.
09:54 | 12:11 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Project Work S/D Due to PROJECT WORK OF NESCO
| 10:18 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
10:21 |  | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to Oil Centrifuzing Work.
10:24 |  | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to Oil Centrifuzing Work.
| 10:37 | Feni 132/33kV S/S T-2(415T) HT is restored.
| 10:37 | Feni 132/33kV S/S T-2(415T) LT is restored.
10:48 | 12:18 | Chhatak 132/33kV S/S T-3 HT Forced S/D Due to Red hot maintenance work
10:49 | 12:20 | Chhatak 132/33kV S/S T-3 LT Forced S/D Due to Red hot maintenance work
11:23 | 13:41 | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Forced S/D Due to Maintenance work on 33 KV Bus coupler DS-4(Y Phase Clamp) |  |  |  |  | 30.0MW load interruption.
11:24 | 13:41 | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Forced S/D
12:00 |  | Day Peak Gen.12681 MW
| 12:55 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
| 12:58 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
| 14:10 | Chandpur 132/33kV S/S 422T HT is restored.
| 14:11 | Chandpur 132/33kV S/S 422T LT is restored.
16:32 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
17:57 | 19:48 | Bhulta-Rampura 230 kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to NLDC and from Bhulta 400/230kV end Due
to Shutdown taken by NLDC.
| 18:26 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt is restored.
21:00 |  | Evening Peak Generation = 15,745MW
23:34 | 00:14 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Forced S/D Due to 33kv Nandail-2 feeder Red-hot Maintenance works. |  |  |  |  | 55.0MW load interruption.
23:34 | 00:14 | Kishoreganj 132/33kV S/S Tr-2 (414T) HT Forced S/D Due to 33kv Nandail-2 feeder Red-hot Maintenance works.
07:00 |  | Minimum generation 12634 MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4205250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 400 | 9356400
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9926500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 90 | 936960 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3552204 | GT-1 Under Maint
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 20 | 400009 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 997231
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 25 | 75781 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 72 | 833280 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 316 | 7300412
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 81 | 984528 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 365760
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1768800
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 664980
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 667280
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 36 | 536340 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 608000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 19 | 450500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 32 | 453120 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 240 | 1605818 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 97 | 2231280 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 821760 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 1306560 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1804320
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 179886
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 734040 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under maint.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5332 | 2872 | 52766999
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 97837 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 61560
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 123360 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 113 | 2651200 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 219 | 5286388
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 952618 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 58 | 1134096 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1359918 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 70 | 1258320 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 589440 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 494400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 775680 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21602
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1242000 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 259172 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1556471
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 598080 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 658636 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 125 | 744363 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 470 | 11203635
| Cox's Bazar Wind |  | IPP | 66 | 60 | 17 | 307680 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 624 | 17832727
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 337055
| Chattogram area Total |  |  |  | 4404 | 2232 | 49546238
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 5238000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7324100
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 5997000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 245 | 5821000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 0 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 66909 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1038610
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 122 | 1737963 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 811584 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 466270 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 433920 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 78 | 1819200
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 753000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 51 | 825590
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 6 | 152900 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 430920 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 75 | 1181040 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 198000 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1944960 | Engine problem
| Cumilla Area Total |  |  |  | 2929 | 1772 | 36240966
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 34 | 678720 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9500
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 120 | 1934400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1382400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 253780
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 133920 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 244 | 4392720
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 967000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 48 | 1142400 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3468191
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1194600
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 885240 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 139728 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1357920
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 204 | 5127220 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 14 | 384240 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7112000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8796000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8148700 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1620 | 38723239
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 779 | 21317818
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 46 | 446400 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 187200
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 213888 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 190 | 5105664 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 40 | 181875
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 36 | 1403040 | Low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 713520
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 1013 | 15061815
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2190 | 44631220
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 123840 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 177554
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2510000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 25851700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4952318
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6632700
| Barisal Area Total |  |  |  | 2235 | 1923 | 40248112
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 222732
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 46520 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 168560 | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 211208
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 140 | 3984127 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 340 | 8206400 | Gas shortage
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 238267 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 129726 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 534800 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 847104 | Engine problem
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 799968
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 21960
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1456 | 29994124
| Rajshahi Area Total |  |  |  | 3431 | 2421 | 45405496
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1455272
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 210 | 5346000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1584998 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36485
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 1700736 | Engine problem
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 136963
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1027750
| Rangpur Area Total |  |  |  | 950 | 471 | 11288204
| Total |  |  |  | 25903 | 15745 | 323243194
| Eastern Grid Total |  |  |  | 15588 | 8740 | 181670162
| Western Grid Total |  |  |  | 10315 | 7005 | 141573032
| National Grid Total |  |  |  | 25903 | 15745 | 323243194
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-06-08
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  | 9852.9 | MW | (b) ENTIRE WESTERN GRID: |  | 5169.3 | MW
i) Dhaka area |  | 5422.9 | MW | i) Khulna area |  | 2024.4 | MW
ii) Chattogram area |  | 1407 | MW | ii) Barishal area |  | 516.1 | MW
iii) Cumilla area |  | 1393 | MW | iii) Rajshahi area |  | 1643.8 | MW
iv) Mymensingh area |  | 1036 | MW | iv) Rangpur area |  | 985 | MW
v) Sylhet area |  | 594 | MW
System Total Demand at Evening Peak Hour (a + b) = |  |  |  | 15022.2 | MW
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | KSRM | 28 | 11:00 | Satkhira | 149 | 01:00
AKSML | 13.1 | 23:00 | Kabirpur | 201 | 07:00 | Satmasjid | 129 | 19:30
Aftabnagar | 44 | 19:30 | Kachua | 90 | 21:00 | Savar | 219 | 19:00
Agargaon | 109 | 19:30 | Kallyanpur | 121 | 23:00 | SevenRings | 21.97 | 04:00
Agrabad | 98 | 15:00 | Kalurghat | 38 | 10:00 | ShahCement | 29 | 08:00
Amnura | 76 | 22:00 | Kamrangirchar | 56 | 19:30 | Shahjadpur | 91 | 20:00
Ashuganj | 83 | 02:00 | Kaptai | N/A | N/A | Shahjibazar | 138 | 22:00
BIPTC | N/A | N/A | Kazla | 121 | 17:00 | Shahmirpur | 52 | 01:00
BSRM | 188 | 23:00 | Keranigonj | 95 | 19:30 | Shariatpur | 97 | 22:00
Bagerhat | 102 | 22:00 | Khagrachori | 32 | 19:00 | Sherpur | 140 | 00:00
Bakulia | 100 | 19:00 | Khulna | 104 | 13:00 | Shikalbaha | 31 | 20:00
Banani | 38.8 | 13:00 | Khulshi | 183 | 14:00 | Shikalbaha-230 | N/A | N/A
Bangabhaban | 9 | 12:00 | Kishoreganj | 142 | 00:00 | Shitalakhya | 111.2 | 15:00
Barapukuria | 66 | 21:00 | Kodda | 287 | 19:00 | Sholosohor | 45 | 12:00
Barguna | 28 | 22:00 | Kulaura | 56 | 19:00 | Shyampur | 172 | 10:00
Barishal | 128 | 22:00 | Kurigram | 65 | 01:00 | Siddhirganj | 134 | 12:00
Barishal-230 | 116 | 00:00 | Kushtia | 174 | 19:30 | Sirajganj | 118 | 20:00
Baroaulia | 66 | 15:00 | Lalbag | 104 | 17:00 | Sonargaon | 122 | 16:00
Baroirhat | 64 | 19:00 | Lalmonirhat | 59 | 01:00 | Sreemongol | 74 | 22:00
Bashundhara | 217 | 19:00 | MI_Cement | 10.6 | 20:00 | Sreepur | 70 | 19:30
BashundharaCement | 6 | 00:00 | Madanganj | 28 | 19:30 | Srinagar | 52.7 | 22:00
Beanibazar | 79 | 20:00 | Madaripur | 137 | 23:00 | Sunamganj | 56 | 04:00
Benapole | 80 | 22:00 | Madartek | 94.05 | 23:00 | Sylhet | 46 | 19:00
Bhaluka | 136 | 16:00 | Madunaghat | 56 | 18:00 | Sylhet-132 | 122 | 15:00
Bhandaria | 53 | 21:00 | Magura | 73 | 23:00 | TK | 32.3 | 22:00
Bhangura | 44 | 20:00 | Mahasthangarh | 80 | 20:00 | Tangail | 188 | 20:00
Bheramara(GK) | 77 | 20:00 | Manikganj | 155 | 20:00 | Thakurgaon | 114 | 20:00
Bhulta | 256 | 19:30 | Maniknagar | 78 | 13:00 | Tongi | 155 | 17:00
Bog-Sherpur | 70 | 19:30 | Matarbari | 45 | 00:00 | Ullahpara | 31 | 21:00
Bogura | 177 | 23:00 | Matuail | 76 | 12:00 | Ullon | 57 | 19:30
Borhanuddin | 88 | 21:00 | Millgate | 130 | 15:00 | Uttara | 79 | 19:30
Brahmanbaria | 191 | 21:00 | Mirpur | 167.5 | 19:30 | UttaraNew | 52 | 23:00
Cantonment | 146 | 19:30 | Mirsorai | 41 | 22:00 | Zigatola | 100 | 19:30
Chandpur | 86 | 19:00 | Mirzapur | 58 | 14:00
Chandraghona | 34 | 19:30 | Mithapukur | 56 | 21:00
Chapai | 80 | 21:00 | Modern | 0 | 00:00
Charsaidpur | 45 | 00:00 | Mogbazar | 132.4 | 16:00
Chauddagram | 67 | 19:00 | Mongla | 50 | 16:00
Chhatak | 30 | 01:00 | Motijheel | 49 | 18:30
Chowmuhani | 200 | 05:00 | Munshiganj | 118 | 23:00
Chuadanga | 122 | 21:00 | Mymensingh | 233 | 22:00
Coxsbazar | 115 | 20:00 | Naogaon | 150 | 21:00
Cumilla(N) | 197 | 20:00 | Narail | 68 | 22:00
Cumilla(S) | 194 | 23:00 | Narinda | 47 | 19:00
Daudkandi | 160 | 21:00 | Narshingdi | 161 | 00:00
Dhaka | 46 | 13:00 | Natore | 152 | 22:00
Dhamrai | 134 | 22:00 | Nawabganj | 55.6 | 22:00
Dhanmondi | 154.2 | 13:00 | Netrakona | 134 | 01:00
Dohazari | 97 | 23:00 | New | 58.8 | 15:00
Faridpur | 191 | 23:00 | Niamatpur | 84 | 23:00
Fatullah | 72 | 16:00 | Noapara | 52 | 21:00
Fenchuganj | 43 | 19:00 | PHP | 8 | 16:00
Feni | 94 | 19:00 | Pabna | 145 | 21:00
GPH | 96 | 21:00 | Palashbari | 127 | 20:00
Ghatail | 40 | 13:00 | Panchagarh | 60 | 00:00
Ghorashal | 45 | 23:00 | Patuakhali | 98 | 01:00
Goalpara | 38 | 00:00 | Payra | 34 | 22:00
Gollamari | 90 | 00:00 | Postogola | 65 | 23:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 382 | 06:00 | 361 | 13:00 | Kaliakoir | 366 | 06:00 | 345 | 13:00
| Ashuganj | 400 | 8:00 | 394 | 18:00 | Madunaghat_I | 410 | 15:00 | 408 | 20:00
| Bhulta | 401 | 06:00 | 379 | 13:00 | Meghnaghat | 378 | 06:00 | 357 | 13:00
| Bibiana | 395 | 01:00 | 383 | 13:00 | Payra | 409 | 08:00 | 400 | 05:00
| BIPTC | 403 | 06:00 | 393 | 15:00 | Rahanpur | 401 | 06:00 | 382 | 23:00
| Bogura | 396 | 06:00 | 375 | 23:00 | Rampal | 397 | 06:00 | 382 | 16:00
| Gopalganj | 395 | 06:00 | 376 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 06:00 | 210 | 13:00 | Hasnabad | 227 | 05:00 | 213 | 12:00
| AKSML | 232 | 07:00 | 220 | 13:00 | Hathazari | 232 | 21:00 | 225 | 16:00
| Aminbazar | 227 | 05:00 | 212 | 12:00 | Ishurdi | 237 | 06:00 | 224 | 13:00
| Ashuganj | 234 | 07:00 | 124 | 15:00 | Jhenaidah | 225 | 08:00 | 211 | 16:00
| Ashuganj-400 | 232 | 8:00 | 222 | 19:00 | Kaliakoir | 266 | 22:00 | 217 | 16:00
| Baghabari | 232 | 06:00 | 221 | 13:00 | Keranigonj | 227 | 06:00 | 210 | 13:00
| Barapukuria | 217 | 05:00 | 208 | 23:00 | Khulna(S) | 226 | 08:00 | 213 | 16:00
| Barapukuria-230 | 216 | 13:00 | 206 | 19:00 | Madunaghat_I | 231 | 17:00 | 221 | 00:00
| Barishal | 233 | 18:00 | 129 | 02:00 | Maniknagar | 228 | 06:00 | 214 | 12:00
| Bheramara | 235 | 05:00 | 223 | 16:00 | Meghnaghat | 232 | 07:00 | 220 | 12:00
| Bhulta | 230 | 06:00 | 215 | 13:00 | Meghnaghat-400 | 230 | 06:00 | 22 | 19:00
| Bibiana | 228 | 04:00 | 221 | 13:00 | Mirsorai | 230 | 22:00 | 220 | 13:00
| BIPTC | 236 | 06:00 | 222 | 13:00 | Rajshahi | 234 | 06:00 | 220 | 13:00
| Bogura | 224 | 06:00 | 213 | 19:30 | Rampal | 226 | 06:00 | 215 | 13:00
| Bogura-400 | 225 | 06:00 | 215 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 237 | 18:00 | 229 | 23:00 | Rampura | 227 | 06:00 | 213 | 13:00
| BSRM | 229 | 06:00 | 220 | 13:00 | Shikalbaha | 231 | 19:30 | 222 | 13:00
| Cumilla(N) | 229 | 07:00 | 215 | 13:00 | Shyampur | 227 | 05:00 | 213 | 13:00
| Fenchuganj | 234 | 07:00 | 227 | 16:00 | Siddhirganj | 228 | 07:00 | 215 | 11:00
| Ghorashal | 232 | 01:00 | 230 | 00:00 | Sirajgonj | 236 | 05:00 | 227 | 16:00
| Ghorashal-230 | 230 | 02:00 | 216 | 13:00 | Sreepur | 230 | 06:00 | 218 | 16:00
| GPH | 230 | 02:00 | 220 | 13:00 | Tongi | 227 | 07:00 | 212 | 12:00
| Haripur | 226 | 05:00 | 214 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 04:00 | 124 | 13:00 | Kushtia | 134 | 06:00 | 126 | 19:00
| Agargaon | 138 | 06:00 | 125 | 13:00 | Lalbag | 135 | 06:00 | 123 | 13:00
| Agrabad | 132 | 07:00 | 127 | 12:00 | Lalmonirhat | 129 | 05:00 | 117 | 19:00
| AKS | 130 | 06:00 | 126 | 09:00 | Madanganj | 132 | 05:00 | 122 | 12:00
| Aminbazar | 138 | 04:00 | 121 | 14:00 | Madaripur | 128 | 10:00 | 121 | 23:00
| Amnura | 140 | 20:00 | 117 | 21:00 | Madartek | 135 | 05:00 | 125 | 13:00
| Ashuganj | 137 | 03:00 | 132 | 13:00 | Madunaghat | 132 | 08:00 | 127 | 13:00
| Bagerhat | 133 | 08:00 | 118 | 16:00 | Magura | 137 | 09:00 | 124 | 13:00
| Bakulia | 132 | 07:00 | 125 | 13:00 | Mahasthangarh | 130 | 06:00 | 121 | 19:00
| Banani | 135 | 06:00 | 122 | 13:00 | Manikganj | 126 | 02:00 | 114 | 10:00
| Bangabhaban | 133 | 05:00 | 120 | 09:00 | Maniknagar | 132 | 05:00 | 121 | 13:00
| Barapukuria | 135 | 05:00 | 127 | 00:00 | Matarbari | 128 | 12:00 | 115 | 23:00
| Barguna | 132 | 18:30 | 123 | 00:00 | Matuail | 134 | 05:00 | 124 | 12:00
| Barishal | 130 | 05:00 | 119 | 01:00 | Millgate | 135 | 01:00 | 121 | 10:00
| Barishal-230 | 131 | 08:00 | 125 | 00:00 | Mirpur | 136 | 04:00 | 124 | 12:00
| Baroaulia | 132 | 01:00 | 127 | 13:00 | Mirzapur | 128 | 02:00 | 112 | 14:00
| Baroirhat | 128 | 06:00 | 118 | 13:00 | Mithapukur | 127 | 09:00 | 120 | 19:00
| Bashundhara | 136 | 05:00 | 122 | 11:00 | MI_Cement | 133 | 01:00 | 123 | 13:00
| BashundharaCement | 132 | 05:00 | 122 | 12:00 | Modern | 132 | 07:00 | 126 | 14:00
| Beanibazar | 128 | 09:00 | 120 | 19:00 | Mogbazar | 137 | 05:00 | 126 | 13:00
| Benapole | 133 | 07:00 | 118 | 23:00 | Mongla | 132 | 08:00 | 114 | 23:00
| Bhaluka | 131 | 05:00 | 121 | 16:00 | Motijheel | 133 | 05:00 | 122 | 12:00
| Bhandaria | 126 | 11:00 | 115 | 00:00 | Munshiganj | 132 | 01:00 | 124 | 11:00
| Bhangura | 136 | 07:00 | 128 | 16:00 | Mymensingh | 135 | 11:00 | 115 | 19:00
| Bheramara | 135 | 06:00 | 129 | 16:00 | Naogaon | 127 | 06:00 | 119 | 13:00
| Bheramara(GK) | 135 | 05:00 | 129 | 13:00 | Narail | 137 | 09:00 | 123 | 13:00
| Bhulta | 127 | 03:00 | 116 | 11:00 | Narinda | 132 | 05:00 | 121 | 13:00
| Bog-Sherpur | 131 | 06:00 | 125 | 13:00 | Narshingdi | 128 | 05:00 | 115 | 12:00
| Bogura | 132 | 06:00 | 126 | 12:00 | Natore | 134 | 06:00 | 125 | 13:00
| Bogura-230 | 132 | 06:00 | 124 | 19:30 | Nawabganj | 134 | 05:00 | 124 | 12:00
| Brahmanbaria | 130 | 05:00 | 121 | 19:00 | Netrakona | 133 | 11:00 | 116 | 13:00
| Cantonment | 137 | 05:00 | 124 | 13:00 | New | 133 | 04:00 | 123 | 10:00
| Chandpur | 127 | 07:00 | 114 | 11:00 | Niamatpur | 133 | 05:00 | 125 | 21:00
| Chandraghona | 133 | 07:00 | 127 | 13:00 | Noapara | 134 | 09:00 | 122 | 23:00
| Chapai | 132 | 15:00 | 122 | 21:00 | Pabna | 135 | 06:00 | 126 | 00:00
| Charsaidpur | 132 | 00:00 | 124 | 12:00 | Palashbari | 127 | 06:00 | 117 | 22:00
| Chauddagram | 129 | 06:00 | 118 | 13:00 | Panchagarh | 133 | 04:00 | 117 | 00:00
| Chhatak | 129 | 05:00 | 123 | 18:30 | Patuakhali | 131 | 08:00 | 123 | 01:00
| Chowmuhani | 124 | 08:00 | 114 | 11:00 | Payra | 133 | 06:00 | 130 | 00:00
| Chuadanga | 130 | 08:00 | 115 | 16:00 | PHP | 127 | 07:00 | 117 | 13:00
| Coxsbazar | 127 | 12:00 | 116 | 23:00 | Postogola | 135 | 05:00 | 124 | 13:00
| Cumilla(N) | 133 | 06:00 | 122 | 13:00 | Purbachal | 136 | 05:00 | 120 | 11:00
| Cumilla(S) | 135 | 10:00 | 121 | 13:00 | Purbasadipur | 127 | 05:00 | 115 | 19:00
| Daudkandi | 129 | 18:00 | 118 | 19:00 | Rahanpur | 135 | 06:00 | 128 | 21:00
| Dhaka | 136 | 05:00 | 125 | 13:00 | Rahim | 133 | 01:00 | 125 | 11:00
| Dhamrai | 134 | 04:00 | 126 | 16:00 | Rajbari | 129 | 06:00 | 121 | 23:00
| Dhanmondi | 136 | 05:00 | 124 | 13:00 | Rajendrapur | 129 | 02:00 | 114 | 10:00
| Dohazari | 131 | 07:00 | 124 | 23:00 | Rajshahi | 134 | 08:00 | 125 | 13:00
| Faridpur | 129 | 06:00 | 121 | 23:00 | Rajshahi-230 | 134 | 05:00 | 111 | 21:00
| Fatullah | 133 | 01:00 | 123 | 13:00 | Ramganj | 123 | 08:00 | 110 | 13:00
| Fenchuganj | 133 | 08:00 | 129 | 01:00 | Rampur | 132 | 18:30 | 31 | 06:00
| Feni | 125 | 07:00 | 116 | 11:00 | Rampura | 136 | 06:00 | 125 | 13:00
| Ghatail | 130 | 06:00 | 111 | 13:00 | Rangamati | 132 | 06:00 | 127 | 13:00
| Ghorashal | 137 | 01:00 | 133 | 15:00 | Rangpur | 128 | 05:00 | 116 | 19:00
| Goalpara | 135 | 08:00 | 124 | 23:00 | Ruppur | 138 | 06:00 | 129 | 15:00
| Gollamari | 134 | 09:00 | 124 | 23:00 | Saidpur | 129 | 05:00 | 119 | 19:30
| Gopalganj | 129 | 08:00 | 121 | 16:00 | Satkhira | 130 | 09:00 | 116 | 23:00
| Gopalganj-400 | 128 | 06:00 | 122 | 16:00 | Satmasjid | 137 | 06:00 | 124 | 13:00
| Gulshan | 135 | 05:00 | 125 | 13:00 | Savar | 136 | 04:00 | 122 | 12:00
| Halishahar | 132 | 06:00 | 127 | 13:00 | SevenRings | 139 | 02:00 | 128 | 12:00
| Haripur | 133 | 01:00 | 125 | 11:00 | ShahCement | 132 | 00:00 | 124 | 12:00
| HaripurSBU | 133 | 01:00 | 125 | 11:00 | Shahjadpur | 138 | 07:00 | 132 | 01:00
| Hasnabad | 134 | 03:00 | 125 | 12:00 | Shahjibazar | 128 | 05:00 | 121 | 22:00
| Hathazari | 134 | 18:00 | 130 | 00:00 | Shahmirpur | 133 | 06:00 | 127 | 13:00
| Ishurdi | 137 | 06:00 | 130 | 16:00 | Shariatpur | 127 | 06:00 | 119 | 22:00
| Jaldhaka | 128 | 06:00 | 116 | 19:30 | Sherpur | 135 | 07:00 | 118 | 13:00
| Jamalpur | 137 | 23:00 | 120 | 13:00 | Shikalbaha | 122 | 07:00 | 115 | 13:00
| Jashore | 133 | 08:00 | 120 | 23:00 | Shikalbaha-230 | 133 | 07:00 | 127 | 13:00
| Jhenaidah | 137 | 07:00 | 124 | 19:00 | Shitalakhya | 133 | 01:00 | 123 | 13:00
| Jhenaidah-230 | 137 | 08:00 | 127 | 16:00 | Sholosohor | 132 | 07:00 | 125 | 13:00
| Joydebpur | 133 | 01:00 | 123 | 11:00 | Shyampur | 132 | 01:00 | 123 | 12:00
| Joypurhat | 126 | 06:00 | 116 | 23:00 | Shyampur-230 | 132 | 01:00 | 123 | 12:00
| Juldah | 133 | 01:00 | 129 | 13:00 | Siddhirganj | 134 | 04:00 | 125 | 12:00
| Kabirpur | 133 | 02:00 | 118 | 10:00 | Sirajganj | 131 | 09:00 | 124 | 15:00
| Kachua | 126 | 07:00 | 115 | 13:00 | Sonargaon | 132 | 03:00 | 123 | 13:00
| Kaliakoir | 137 | 04:00 | 118 | 13:00 | Sreemongol | 129 | 06:00 | 122 | 19:00
| Kallyanpur | 130 | 05:00 | 120 | 16:00 | Sreepur | 133 | 02:00 | 125 | 16:00
| Kalurghat | 133 | 07:00 | 127 | 13:00 | Srinagar | 135 | 06:00 | 124 | 12:00
| Kamrangirchar | 135 | 05:00 | 119 | 16:00 | SSM | 134 | 09:00 | 127 | 14:00
| Kaptai | 131 | 5:00 | 128 | 14:00 | Sunamganj | 128 | 07:00 | 122 | 00:00
| Kazla | 132 | 06:00 | 121 | 13:00 | Sylhet | 130 | 07:00 | 126 | 00:00
| Keranigonj | 135 | 05:00 | 124 | 13:00 | Sylhet-132 | 130 | 05:00 | 127 | 00:00
| Khagrachori | 132 | 06:00 | 125 | 13:00 | Tangail | 129 | 05:00 | 110 | 13:00
| Khulna | 133 | 09:00 | 122 | 19:00 | Thakurgaon | 131 | 05:00 | 119 | 19:30
| Khulna(S) | 134 | 08:00 | 125 | 16:00 | TK | 132 | 04:00 | 125 | 16:00
| Khulshi | 130 | 07:00 | 124 | 13:00 | Tongi | 134 | 07:00 | 124 | 10:00
| Kishoreganj | 132 | 05:00 | 122 | 13:00 | Ullahpara | 134 | 07:00 | 127 | 13:00
| Kodda | 132 | 01:00 | 114 | 10:00 | Ullon | 135 | 05:00 | 124 | 12:00
| KSRM | 133 | 20:00 | 126 | 13:00 | Uttara | 137 | 06:00 | 123 | 13:00
| Kulaura | 131 | 06:00 | 127 | 17:00 | UttaraNew | 138 | 06:00 | 124 | 11:00
| Kurigram | 128 | 05:00 | 112 | 00:00 | Zigatola | 135 | 06:00 | 123 | 13:00

## L-Curve
Date | 2024-06-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 536 | 8380 | 7072 | 15452 |  |  |  | QF-LDC-11
0:30 | 524 | 8050.5 | 6568.5 | 14619 | Date: | 2024-06-08
1:00 | 512 | 7721 | 6065 | 13786
1:30 | 409 | 7497 | 5820.5 | 13317.5
2:00 | 306 | 7273 | 5576 | 12849
2:30 | 375 | 7157 | 5562 | 12719 | [5 empty] | Gen. at Eve. Peak | 15745 | 15745 MW (21:00 )
3:00 | 444 | 7041 | 5548 | 12589 | [6 empty] | 21:00
3:30 | 503 | 7016.5 | 5499 | 12515.5 | [5 empty] | Gen. at Day Peak | 12681 | 12681 MW (12:00 )
4:00 | 562 | 6992 | 5450 | 12442 | [6 empty] | 12:00
4:30 | 568 | 6993.5 | 5361.5 | 12355 | [5 empty] | Highest Generation | 15745
5:00 | 574 | 6995 | 5273 | 12268 | [6 empty] | 21:00
5:30 | 570 | 6872 | 5161.5 | 12033.5
6:00 | 566 | 6749 | 5050 | 11799
6:30 | 549 | 6715 | 4965.5 | 11680.5
7:00 | 532 | 6681 | 4881 | 11562
7:30 | 591 | 6584.5 | 4815 | 11399.5
8:00 | 650 | 6488 | 4749 | 11237
8:30 | 757 | 6540 | 4786 | 11326
9:00 | 864 | 6592 | 4823 | 11415
9:30 | 887 | 6747 | 4862 | 11609
10:00 | 910 | 6902 | 4901 | 11803
10:30 | 956 | 7009.5 | 5105.5 | 12115
11:00 | 1002 | 7117 | 5310 | 12427
11:30 | 953 | 7208 | 5346 | 12554
12:00 | 904 | 7299 | 5382 | 12681
12:30 | 895 | 7335.5 | 5443.5 | 12779
13:00 | 886 | 7372 | 5505 | 12877
13:30 | 865 | 7436 | 5592 | 13028
14:00 | 844 | 7500 | 5679 | 13179
14:30 | 867 | 7612 | 5775 | 13387
15:00 | 890 | 7724 | 5871 | 13595
15:30 | 888 | 7728.5 | 5823.5 | 13552
16:00 | 886 | 7733 | 5776 | 13509
16:30 | 907 | 7677.5 | 5754 | 13431.5
17:00 | 928 | 7622 | 5732 | 13354
17:30 | 919 | 7597.5 | 5700 | 13297.5
18:00 | 910 | 7573 | 5668 | 13241
18:30 | 848 | 7951 | 5886 | 13837
19:00 | 786 | 8329 | 6104 | 14433
19:30 | 580 | 8698 | 6661 | 15359
20:00 | 536 | 8737 | 6677 | 15414 |  |  |  | Executive Engineer
20:30 | 536 | 8738.5 | 6841 | 15579.5 |  |  |  | Network Operation Division
21:00 | 536 | 8740 | 7005 | 15745
21:30 | 543 | 8660 | 7004 | 15664
22:00 | 550 | 8580 | 7003 | 15583 |  |  |  |  | Page 6 of 7
22:30 | 560 | 8553.5 | 7031 | 15584.5
23:00 | 570 | 8527 | 7059 | 15586
23:30 | 553 | 8453.5 | 7065.5 | 15519
24:00 | 536 | 8380 | 7072 | 15452
15745 MW (21:00 )
12681 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-08 |  | Energy |  | 323243194
[15 empty] | 2024-06-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3847 | 779 | 1810 | 0 | 2729 | 5438 | 115 | 0 | 621 | 96 | 0 | 17 | 571.09
0:30 | 3867.5 | 781 | 1760 | 0 | 2363.5 | 5209 | 111.5 | 0 | 424.5 | 82 | 0 | 20 | 335.545 |  |  | Date: | 43989
1:00 | 3888 | 783 | 1710 | 0 | 1998 | 4980 | 108 | 0 | 228 | 68 | 0 | 23 | 100
1:30 | 3852.5 | 783 | 1713 | 0 | 1710 | 4859 | 107 | 0 | 203.5 | 67 | 0 | 22.5 | 50 | [9 empty] | Total Energy | 323.2432 | 323.2432 | Total Energy Gen 323.243 MKWHr Energy Not Served 6.799 MKWHr Energy Requirement 330.042 MKWHr
2:00 | 3817 | 783 | 1716 | 0 | 1422 | 4738 | 106 | 0 | 179 | 66 | 0 | 22 | 0 | [9 empty] | Energy not Served | 6.7992 | 6.7992
2:30 | 3818 | 854 | 1727.5 | 0 | 1292.5 | 4668 | 106 | 0 | 170.5 | 65 | 0 | 17.5 | 0 | [9 empty] | Energy Requirement | 330.0424 | 330.0424
3:00 | 3819 | 925 | 1739 | 0 | 1163 | 4598 | 106 | 0 | 162 | 64 | 0 | 13 | 0
3:30 | 3830.5 | 924.5 | 1736 | 0 | 1136.5 | 4545.5 | 105.5 | 0 | 162 | 60 | 0 | 15 | 0 | [8 empty] | Shortage
4:00 | 3842 | 924 | 1733 | 0 | 1110 | 4493 | 105 | 0 | 162 | 56 | 0 | 17 | 0
4:30 | 3846.5 | 924.5 | 1730 | 0 | 1107.5 | 4405.5 | 105.5 | 0 | 162 | 55 | 0 | 18.5 | 0
5:00 | 3851 | 925 | 1727 | 0 | 1105 | 4318 | 106 | 0 | 162 | 54 | 0 | 20 | 0
5:30 | 3827.5 | 925 | 1678.5 | 0 | 1037.5 | 4213.5 | 106 | 0 | 162 | 55 | 10.5 | 18 | 25
6:00 | 3804 | 925 | 1630 | 0 | 970 | 4109 | 106 | 0 | 162 | 56 | 21 | 16 | 50
6:30 | 3773 | 925.5 | 1632 | 0 | 941 | 4040.5 | 106.5 | 0 | 162 | 52 | 31 | 17 | 48 | [7 empty] | Coal
7:00 | 3742 | 926 | 1634 | 0 | 912 | 3972 | 107 | 0 | 162 | 48 | 41 | 18 | 46
7:30 | 3696 | 925.5 | 1572 | 0 | 883.5 | 3908 | 108.5 | 0 | 177.5 | 55 | 59.5 | 14 | 43.5325 | [6 empty] | Oil
8:00 | 3650 | 925 | 1510 | 0 | 855 | 3844 | 110 | 0 | 193 | 62 | 78 | 10 | 41.065
8:30 | 3681.5 | 925 | 1518.5 | 0 | 848 | 3845.5 | 112.5 | 0 | 181 | 66 | 139.5 | 8.5 | 49.1825
9:00 | 3713 | 925 | 1527 | 0 | 841 | 3847 | 115 | 0 | 169 | 70 | 201 | 7 | 57.3
9:30 | 3816 | 925 | 1578 | 0 | 859.5 | 3847 | 115 | 0 | 161 | 69 | 232 | 6.5 | 70.1925
10:00 | 3919 | 925 | 1629 | 0 | 878 | 3847 | 115 | 0 | 153 | 68 | 263 | 6 | 83.085
10:30 | 3878.5 | 924.5 | 1697.5 | 0 | 938.5 | 3975 | 115 | 0 | 162.5 | 72 | 342 | 9.5 | 100.275
11:00 | 3838 | 924 | 1766 | 0 | 999 | 4103 | 115 | 0 | 172 | 76 | 421 | 13 | 117.465
11:30 | 3854 | 923.5 | 1767 | 0 | 1062.5 | 4173.5 | 115 | 0 | 176 | 79 | 381 | 22.5 | 139.43
12:00 | 3870 | 923 | 1768 | 0 | 1126 | 4244 | 115 | 0 | 180 | 82 | 341 | 32 | 161.395
12:30 | 3860 | 923.5 | 1769.5 | 0 | 1149.5 | 4294.5 | 115 | 0 | 205 | 83 | 363 | 16 | 186.225
13:00 | 3850 | 924 | 1771 | 0 | 1173 | 4345 | 115 | 0 | 230 | 84 | 385 | 0 | 211.055
13:30 | 3850 | 924 | 1771 | 0 | 1173 | 4345 | 115 | 0 | 230 | 84 | 385 | 0 | 211.055
14:00 | 3850 | 924 | 1771 | 0 | 1173 | 4345 | 115 | 0 | 230 | 84 | 385 | 0 | 211.055
14:30 | 3790 | 923.5 | 1776 | 0 | 1398.5 | 4569.5 | 113 | 0 | 241.5 | 88 | 332.5 | 3.5 | 322.79
15:00 | 3730 | 923 | 1781 | 0 | 1624 | 4794 | 111 | 0 | 253 | 92 | 280 | 7 | 434.525
15:30 | 3685 | 922.5 | 1744.5 | 0 | 1735.5 | 4781.5 | 111 | 0 | 250 | 91 | 225 | 6 | 499.465
16:00 | 3640 | 922 | 1708 | 0 | 1847 | 4769 | 111 | 0 | 247 | 90 | 170 | 5 | 564.405
16:30 | 3642 | 922.5 | 1643.5 | 0 | 1879 | 4739.5 | 111 | 0 | 258.5 | 88 | 135.5 | 12 | 566.7925
17:00 | 3644 | 923 | 1579 | 0 | 1911 | 4710 | 111 | 0 | 270 | 86 | 101 | 19 | 569.18
17:30 | 3614 | 923.5 | 1527 | 0 | 1971 | 4649.5 | 111 | 0 | 340.5 | 83 | 62 | 16 | 551.5125
18:00 | 3584 | 924 | 1475 | 0 | 2031 | 4589 | 111 | 0 | 411 | 80 | 23 | 13 | 533.845
18:30 | 3683 | 923.5 | 1575 | 0 | 2218 | 4681.5 | 111.5 | 0 | 533.5 | 86 | 11.5 | 13.5 | 513.79
19:00 | 3782 | 923 | 1675 | 0 | 2405 | 4774 | 112 | 0 | 656 | 92 | 0 | 14 | 493.735
19:30 | 3866 | 923 | 1713 | 0 | 2806 | 5157 | 112 | 0 | 678 | 90 | 0 | 14 | 550.5575
20:00 | 3892 | 779 | 1703 | 0 | 2879 | 5228 | 113 | 0 | 719 | 86 | 0 | 15 | 607.38
20:30 | 3922 | 779 | 1751.5 | 0 | 2869.5 | 5306.5 | 113 | 0 | 740 | 82 | 0 | 16 | 616.4525
21:00 | 3952 | 779 | 1800 | 0 | 2860 | 5385 | 113 | 0 | 761 | 78 | 0 | 17 | 625.525
21:30 | 3850.5 | 779 | 1797 | 0 | 2866.5 | 5394.5 | 114 | 0 | 758 | 87 | 0 | 17.5 | 655.13
22:00 | 3749 | 779 | 1794 | 0 | 2873 | 5404 | 115 | 0 | 755 | 96 | 0 | 18 | 684.735
22:30 | 3803.5 | 779 | 1804.5 | 0 | 2837.5 | 5446 | 115 | 0 | 687 | 96 | 0 | 16 | 659.4275
23:00 | 3858 | 779 | 1815 | 0 | 2802 | 5488 | 115 | 0 | 619 | 96 | 0 | 14 | 634.12
23:30 | 3852.5 | 779 | 1812.5 | 0 | 2765.5 | 5463 | 115 | 0 | 620 | 96 | 0 | 15.5 | 602.605 |  |  | Max Temp. in Dhaka |  | 35.6°C
24:00 | 3847 | 779 | 1810 | 0 | 2729 | 5438 | 115 | 0 | 621 | 96 | 0 | 17 | 571.09
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 323.243 MKWHr Energy Not Served 6.799 MKWHr Energy Requirement 330.042 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1735200
2 | Karnaphuli Hydro PP Unit-4 & 5 | 38 | 36 | 36 | 35 | 36 | 36 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 36 | 36 | 36 | 36 |  | 37 | 37 | 38 | 38 | 40 | 40 | 40 | 916000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 5 | 8 |  | 15 | 17 | 17 | 17 | 17 | 8 | 8 | 97837
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 |  | 8 | 13 | 5 | 7 | 3 | 13 | 1 | 2 |  | 1 | 0 | [8 empty] | 61560
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 220 | 223 | 222 | 223 | 223 | 224 | 221 | 221 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 219 | 219 |  | 220 | 219 | 219 | 219 | 219 | 221 | 222 | 5286388
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 68 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 34 | 34 | 51 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1359918
12 | Hathazari 100 MW peaking PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 65 |  | 65 | 58 | 58 | 58 | 66 | 66 | 66 | 1134096
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 17 | 17 | 952618
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 23 | 23 | 26 | 35 | 35 | 41 | 41 | 35 | 39 | 41 |  | 41 | 41 | 41 | 41 | 36 | 36 | 36 | 811584
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 330 | 328 | 331 | 334 | 334 | 280 | 280 | 280 | 280 | 315 | 316 | 317 | 312 | 312 | 310 | 260 | 260 | 260 |  | 309 | 317 | 316 | 316 | 270 | 320 | 320 | 7300412
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | [14 empty] | 35 | 45 | 45 |  | 100 | 260 | 253 | 240 | 263 | 270 | 278 | 1605818
19 | Ashuganj 195 MW PP (APSCL-United) | [17 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 66909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4205250
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 490 | 490 | 490 | 490 | 440 | 442 | 440 | 440 | 440 | 440 | 440 | 440 | 485 | 490 | 490 | 490 | 440 |  | 440 | 440 | 448 | 470 | 470 | 475 | 472 | 11203635
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 221 | 220 | 220 | 220 | 221 | 222 | 222 | 218 | 217 | 207 | 218 | 214 | 207 | 213 | 214 | 210 | 212 | 214 |  | 210 | 215 | 215 | 217 | 200 | 214 | 215 | 5238000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 250 | 300 | 255 | 240 | 240 | 5997000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 280 | 285 | 285 | 285 | 345 | 320 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 300 | 300 | 280 | 295 | 280 | 7324100
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 245 | 230 | 250 | 250 | 5821000
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP | [16 empty] | 20 | 50 |  | 50 | 80 | 80 | 80 | 80 | 80 | 80 | 466270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 413 | 413 | 411 | 413 | 413 | 412 | 368 | 361 | 363 | 390 | 404 | 401 | 403 | 398 | 397 | 341 | 340 | 340 |  | 372 | 406 | 400 | 400 | 355 | 382 | 405 | 9356400
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 370 | 370 | 330 | 330 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9926500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 43 | 43 | 43 | 44 | 44 | 44 | 34 | 28 | 28 | 28 | 28 | 28 | 11 | 11 | 11 | 12 | 18 | 20 |  | 31 | 31 | 31 | 34 | 34 | 35 | 34 | 678720
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 4 | 5 | 2 | 9 | 8 | 51 | 46 | 38 | 30 | 24 | 7 | 8 | 3 |  | 0 | [6 empty] | 253780
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 42 | 41 | 42 | 40 | 40 | 967000
45 | Fenchugonj CCPP Phase-2 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1142400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 60 | 60 | 60 | 60 | 62 | 62 | 61 | 61 | 61 | 62 | 61 | 55 | 55 | 55 | 54 | 40 | 40 |  | 40 | 56 | 56 | 56 | 56 | 55 | 56 | 1357920
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 204 | 204 | 207 | 207 | 207 | 207 | 207 | 207 | 207 | 209 | 205 | 205 | 205 | 205 | 200 | 201 | 201 | 202 |  | 202 | 202 | 204 | 204 | 206 | 207 | 205 | 5127220
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 139728
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 11 | 11 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1194600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 16 | 16 | 16 | 8 | 8 | 16 | 24 |  | 24 | 24 | 24 | 14 | 16 | 16 | 8 | 384240
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 270 | 290 | 285 | 280 | 270 | 280 | 270 | 305 | 315 | 300 | 300 | 300 | 305 | 310 | 290 | 300 | 280 |  | 285 | 285 | 290 | 290 | 275 | 300 | 300 | 7112000
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 310 | 326 | 370 | 340 | 383 | 370 | 345 | 345 | 345 | 345 | 310 |  | 370 | 340 | 340 | 340 | 320 | 312 | 310 | 8148700
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 667280
59 | Tangail Palli Power Gen 22 MW |  |  |  | 1 | 6 | 6 | 6 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  |  | 2 |  | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 133920
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 68 | 66 | 64 | 56 | 54 | 56 | 48 | 62 | 70 | 68 | 76 | 82 | 84 | 88 | 92 | 90 | 86 | 80 |  | 92 | 90 | 86 | 78 | 96 | 96 | 96 | 1819200
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 38 | 14 | 3 | 6 | 3 | 3 | 10 | 6 | 0 | 0 | 0 | 0 |  | 12 | 16 | 12 | 26 | 32 | 30 | 26 | 494400
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 753000
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 0 | 12 | 12 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 6 | 2 | 6 | 6 |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 152900
69 | Summit Ashulia | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 32700
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 |  | 6 | 23 | 23 | 23 | 23 | 23 | 23 | 503640
71 | Maona 33 MW PP(Summit) | 25 |  |  | 25 | 25 | 25 | 25 | 25 | 17 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 31 |  | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 608000
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 19 | 19 | 19 | 23 | 450500
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 430920
| Chowmuhani 113 MW | 43 | 43 | 38 | 38 | 38 | 38 | 39 | 38 | 39 | 38 | 38 | 39 | 37 | 38 | 38 | 37 | 39 | 70 |  | 74 | 74 | 75 | 75 | 75 | 75 | 69 | 1181040
| Manikgonj 162MW PP(MPGL) | 35 | [11 empty] | 54 | 108 | 160 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 1804320
77 | Siddhirganj 100 PP(Dutch Bangla) | 65 | [9 empty] | 3 | 25 | 25 | 35 | 63 | 76 | 76 | 76 |  | 76 | 76 | 76 | 72 | 70 | 70 | 70 | 833280
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 15 | 8 | 453120
79 | Kodda 150 MW PP | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 32 | 16 | 32 | 48 | 98 | 98 | 115 | 115 | 92 | 114 |  | 146 | 146 | 147 | 147 | 147 | 132 | 132 | 1768800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 34 | 34 | 34 | 34 | 34 | 28 | 25 | 16 | 16 | 16 | 16 | 16 | 25 | 34 |  | 43 | 51 | 51 | 51 | 51 | 50 | 50 | 825590
| Gazipur 100 MW PP | 17 | [7 empty] | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 821760
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 0 | 0 | 1 | 5 | 2 | 5 | 4 | 3 | 2 | 0 | [9 empty] | 21602
| Jodiac Power | 17 | [16 empty] | 11 |  | 27 | 35 | 35 | 35 | 35 | 35 | 35 | 259172
| Karnaphuli Power Ltd. | 110 | 51 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 38 | 51 | 51 | 71 |  | 95 | 110 | 110 | 110 | 110 | 110 | 110 | 1556471
82 | Madanganj 102 PP(Summit) | 48 | 30 | [9 empty] | 12 | 19 | 17 | 17 | 17 | 18 | 17 |  | 17 | 17 | 17 | 20 | 55 | 65 | 65 | 400009
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 16 | 25 | 25 | 25 | 14 |  |  | 75781
86 | Meghnaghat CCPP ( Summit) | 142 | 148 | 151 | 150 | 149 | 150 | 148 | 148 | 151 | 150 | 148 | 152 | 146 | 150 | 150 | 149 | 148 | 137 |  | 150 | 151 | 150 | 150 | 153 | 151 | 150 | 3552204
87 | Meghnaghat 100 MW(IEL) | 48 | [9 empty] | 2 | 19 | 24 | 34 | 47 | 63 | 78 | 89 |  | 88 | 89 | 89 | 90 | 89 | 88 | 89 | 936960
| Meghnaghat 104 MW PP (OPCL) | 56 | 53 | 53 | 53 | 53 | 45 | 34 | 35 | 33 | 46 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 59 |  | 70 | 70 | 71 | 71 | 71 | 71 | 71 | 1306560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 36 | 36 | 12 | 12 | 12 | 12 | 12 | 12 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1258320
92 | Fenchuganj 44 MW (Energyprima) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 36 | 34 | 36 | 33 | 33 | 33 | 10 | 10 |  | 25 | 39 | 39 | 39 | 39 | 39 | 39 | 885240
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 |  | 32 | 51 | 51 | 51 | 51 | 51 | 51 | 1038610
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 16 | [8 empty] | 24 | 24 | 24 | 40 | 80 | 80 | 80 | 80 |  | 80 | 80 | 81 | 81 | 81 | 81 | 82 | 984528
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | [9 empty] | 6 |  | 12 | 15 | 19 | 19 | 6 | 6 | 6 | 123360
96 | Chattogram 108 MW PP (ECPV) | 26 | 25 | 26 | 25 | 25 | 25 | 25 | 25 | 24 | 28 | 31 | 32 | 32 | 37 | 39 | 38 | 36 | 38 |  | 38 | 38 | 37 | 38 | 38 | 38 | 37 | 775680
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 44 | 997231
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 664980
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 163 | 163 | 120 | 120 |  | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 3468191
102 | Sarishabari 3 MW Solar Plant | [8 empty] | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | [9 empty] | 9500
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | [14 empty] | 35 | 54 | 54 |  | 54 | 54 | 54 |  |  |  |  | 365760
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 93 | 93 | 45 | 45 | 45 | 45 | 16 | 16 | 24 | 84 | 93 | 93 | 93 | 93 | 93 | 93 | 93 |  | 121 | 121 | 121 | 120 | 120 | 120 | 126 | 1934400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 91 | 92 | 97 | 97 | 97 | 91 | 87 | 89 | 88 | 76 | 70 | 78 |  | 89 | 97 | 97 | 97 | 97 | 97 | 97 | 2231280
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 589440
116 | Chandpur 200 MW (Desh energy) | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433920
117 | Ashuganj 150 MW PP (Midland) | 130 | 130 | [8 empty] | 8 | 50 | 50 | 55 | 78 | 105 | 107 | 108 |  | 103 | 115 | 115 | 122 | 133 | 135 | 137 | 1737963
118 | Bibiyana-III 400 MW CCPP | 366 | 376 | 366 | 366 | 366 | 366 | 366 | 316 | 310 | 402 | 366 | 367 | 408 | 367 | 367 | 389 | 367 | 317 |  | 368 | 367 | 367 | 367 | 367 | 375 | 367 | 8796000
| Jamalpur 115 MW PP (United) | 58 | 59 | 45 | 45 | 45 | 45 | 45 | 24 | 24 | 56 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 |  | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 1382400
| Anwara 300 MW PP (United) | 52 | 50 | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 52 | 52 | 52 | 50 |  | 50 | 52 | 52 | 52 | 52 | 52 | 52 | 1242000
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 598080
| Anlima Energy Ltd. | 35 | 35 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 38 | 53 | 53 | 53 | 53 | 53 | 53 | 658636
| Bhairob 54.5 MW | 17 | 17 | [12 empty] | 4 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 198000
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 |  | 15 | 17 | 31 | 32 | 29 | 19 | 15 | 9 | 7 | 2 | [8 empty] | 179886
| Chandpur 115(Doreen) | 69 | 91 | 115 | 109 | 108 | 106 | 105 | 100 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 66 | 70 |  | 103 | 105 | 104 | 115 | 106 | 80 | 72 | 1944960
| Kanchan Purbachal Power Generation Ltd. | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 35 | 35 | 35 | 35 | 22 | 32 | 19 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 734040
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 72 | 72 | 80 | 125 | 125 | 17 | 17 | 744363
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 23 | 22 | 13 | 17 | 20 | 16 | 18 | 10 | 7 | 6 | 13 | 32 | 0 | 0 | 7 | 5 | 19 | 13 |  | 14 | 14 | 15 | 17 | 18 | 14 | 17 | 307680
| Sonagazi 75 MW Solar Plant | [6 empty] | 1 | 6 | 19 | 32 | 40 | 34 | 40 | 60 | 41 | 18 | 13 | 5 | [8 empty] | 337055
| Matarbari 2*600 MW (CPGCL) | 764 | 768 | 768 | 765 | 768 | 763 | 768 | 767 | 768 | 765 | 749 | 748 | 750 | 750 | 771 | 780 | 750 | 750 |  | 747 | 751 | 750 | 624 | 616 | 642 | 601 | 17832727
120 | Eastern Zone Total | 7721 | 7273 | 7041 | 6992 | 6995 | 6749 | 6681 | 6488 | 6592 | 6902 | 7117 | 7299 | 7372 | 7500 | 7724 | 7733 | 7622 | 7573 |  | 8329 | 8698 | 8737 | 8740 | 8580 | 8527 | 8380 | 181670162
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 64 | [12 empty] | 31 | 30 | 28 | 30 | 30 |  | 31 | 47 | 58 | 46 | 34 | 30 | 30 | 446400
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 28 | 38 | 47 | 41 | 41 | 33 | 29 | 187200
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 1403040
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 13 | 32 | 51 | 88 | 90 | 84 | 90 | 80 | 70 | 51 | 24 | 6 | [8 empty] | 713520
131 | Rampal 1320 MW (BIFPCL) | 613 | 591 | 521 | 531 | 528 | 475 | 462 | 416 | 410 | 410 | 402 | 405 | 404 | 450 | 493 | 494 | 608 | 715 |  | 716 | 773 | 823 | 1013 | 1021 | 1069 | 1067 | 15061815
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 |  | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 4952318
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 123840
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 299 | 299 | 307 | 307 | 307 | 307 | 263 | 220 |  | 276 | 307 | 307 | 307 | 307 | 307 | 307 | 6632700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 120 | 126 | 126 | 122 | 80 | 126 | 122 | 124 | 126 |  | 126 | 126 | 126 | 126 | 126 | 130 | 130 | 2510000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [5 empty] | 8 | 9 | 10 | 10 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 177554
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 24 | [19 empty] | 24 | 24 | 40 | 32 | 32 | 32 | 181875
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 23 | 32 | 40 | 45 | 44 | 45 | 52 | 213888
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 783 | 783 | 925 | 924 | 925 | 925 | 926 | 925 | 925 | 925 | 924 | 923 | 924 | 924 | 923 | 922 | 923 | 924 |  | 923 | 923 | 779 | 779 | 779 | 779 | 779 | 21317818
147 | Bheramara 410 MW CCPP | 210 | 210 | 215 | 220 | 220 | 220 | 220 | 230 | 230 | 225 | 220 | 215 | 205 | 200 | 180 | 185 | 185 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 5105664
148 | Payra 1320 MW | 1120 | 1040 | 1000 | 990 | 920 | 870 | 780 | 700 | 700 | 700 | 800 | 860 | 940 | 1060 | 1100 | 1060 | 1000 | 930 |  | 970 | 1200 | 1220 | 1244 | 1244 | 1244 | 1244 | 25851700
149
150 | Barapukuria TPP Unit-1 | 65 | 64 | 64 | 62 | 62 | 62 | 63 | 64 | 64 | 65 | 64 | 63 | 64 | 62 | 62 | 60 | 59 | 60 |  | 61 | 61 | 61 | 61 | 62 | 62 | 63 | 1455272
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 230 | 230 | 230 | 220 | 220 | 220 | 220 | 220 | 230 | 230 | 230 | 220 | 220 | 220 | 220 | 220 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 5346000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 16 |  | 31 | 38 | 39 | 40 | 39 | 38 | 38 | 222732
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 1 | 2 | 1 | 2 | 1 | 3 | 2 | 2 | 0 | 0 | [8 empty] | 21960
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3984127
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 270 |  | 350 | 350 | 340 | 340 | 340 | 340 | 340 | 8206400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 46520
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 129726
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 168560
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 14 | 21 |  | 35 | 35 | 48 | 45 | 38 | 38 | 37 | 211208
168 | Santahar 50 MW Peaking PP | [16 empty] | 20 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 238267
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 8 | 50 |  | 85 | 88 | 88 | 88 | 88 | 83 | 83 | 534800
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | [12 empty] | 1 | 35 | 35 | 35 |  | 35 | 50 | 90 | 113 | 113 | 113 | 113 | 847104
172 | Confidence Power Bogura Unit-1 113 MW | 70 | [13 empty] | 25 | 35 | 35 | 35 |  | 35 | 90 | 110 | 113 | 113 | 113 | 113 | 799968
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 99 | 99 | 99 | 99 | 99 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 40 |  | 78 | 103 | 106 | 106 | 106 | 106 | 106 | 1584998
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 3 | 5 | 2 | 4 | 6 | 5 | 2 | 1 | 0 | [8 empty] | 36485
178 | Energypac Power Venture Thakurgaon Ltd. | 94 | 94 | 94 | 94 | 94 | 75 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 65 | 72 | 72 | 73 |  | 90 | 94 | 94 | 94 | 94 | 94 | 95 | 1700736
| Intraco Solar 30 MW | [5 empty] | 1 | 4 | 5 | 6 | 7 | 11 | 28 | 24 | 21 | 11 | 13 | 5 | 2 |  | 0 | [6 empty] | 136963
| Adani Power Jharkhanda Ltd | 1391 | 1248 | 1218 | 1215 | 1110 | 1059 | 1017 | 1017 | 1015 | 1017 | 1119 | 1209 | 1220 | 1266 | 1351 | 1358 | 1330 | 1264 |  | 1354 | 1415 | 1409 | 1456 | 1474 | 1479 | 1474 | 29994124
178 | Teesta Solar Limited | [5 empty] | 10 | 11 | 22 | 81 | 99 | 179 | 106 | 140 | 161 | 106 | 65 | 41 | 5 | [8 empty] | 1027750