## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-11 | Tuesday
|  | Date (day): | 2024-06-11 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15570.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16840 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-10 | 2024-06-11 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 404 | 374 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 0 | 0 | 30 | 51 | 50 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 151 | 130 | 150 | 150 | 185 |  | GT-1 Under S/D
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 0 | 0 | 50 | 36 | 64 | 64 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 25 | 50 |  | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 0 | 0 | 55 | 39 | 70 | 85 |  |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 325 | 320 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 82 | 48 | 82 | 82 |  | 20 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 149 | 100 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55 |  |  | Fuel Shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 35 | 55 |  |  | Fuel Shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 41 | 39 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 31 | 33 | 33 |  | 0 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 195 | 270 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 97 | 92 | 90 | 97 | 52 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 70 | 52 | 88 | 17 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 72 | 50 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 60 | 35 | 54 | 108
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6045 | 5332 | 2356 | 2578 | 2744 | 3048 | 1569 | 839
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 18 | 32 |  | fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 115 | 115 | 115 | 115 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 224 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 68 | 51 | 51 | 54 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 25 | 57 | 48 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 85 | 50 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 36 | 68 | 70 | 70 | 30 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 23 | 23 | 25 | 25 | 75 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 25 | 6 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 31 | 38 | 30 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 110 | 85 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 53 | 35 | 53 | 63 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 17 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 905 | 1011 | 1000 | 1000 |  | 224 | Madunaghat Transformer Limitation
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 4 | 11 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 402 | 275 | 340 | 340 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 0 | 0 | 18 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4464 | 4404 | 2048 | 2310 | 2390 | 2541 | 1003 | 593
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 219 | 218 | 220 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 270 | 280 | 280 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 285 | 240 | 320 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 36 | 37 | 37 | 8 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 36 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 16 | 10 | 12 | 50 | 100 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 6 | 27 | 40 | 41 |  | 11 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 85 | 85 |  | 78 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 74 | 82 | 146 | 151
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 51 | 33 | 51
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 6 | 6 | 6 |  | 19 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114 |  |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 40 | 86 | 38 | 85 | 28 |  | Fuel shortage
80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 16 | 52 | 34 | 52 | 2 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 115 | 115 | 115
| Cumilla Area Total |  |  |  |  | 2937 | 2929 | 1539 | 1861 | 1793 | 2020 | 558 | 108
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 29 | 70 | 60 | 80 | 122 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 93 | 121 | 97 | 120 | 80 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 79 | 68 | 80 | 35 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 24 | 6 | 24 | -2 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 695 | 592 | 201 | 294 | 282.6 | 304 | 122 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 35 | 35 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 2 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 59 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 207 | 206 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 280 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 365 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 396 | 340 | 370 | 375 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1702 | 1637 | 1692 | 1717 | 0 | 458
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 926 | 781 | 943 | 798
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 0 | 0 | 0 | 15 | 20 | 50
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 30 | 50
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 51 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 235 | 200 | 200 | 210 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 0 | 0 | 0 | 24 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 73 | 17 | 73 | 32 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 711 | 955 | 1000 | 1000
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3703 | 3699 | 1936 | 2176 | 2392 | 2271 | 824 | 49
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 8 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 63 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 660 | 1100 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 307 | 307 | 307
| Barisal Area Total |  |  |  |  | 2265 | 2235 | 1091 | 1763 | 1700 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 7 | 0 | 0 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 14 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 0 | 45
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 145 | 200 | 180 | 30 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 414 | 350 | 350 |  |  | FGMO
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 30 | 20 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 40 | 50 | 88 |  | 16 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 94 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1226 | 1363 | 1200 | 1400
| Rajshahi Area Total |  |  |  |  | 3453 | 3431 | 1729 | 2157 | 2032 | 2409 | 713 | 95
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 60 | 62 | 64
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 230 | 220 | 210 | 210 |  | 64 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 70 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 78 | 94 | 35 | 94 |  | 21 | Engin problem
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 188 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 591 | 481 | 545 | 474 | 40 | 177
| Total |  |  |  |  | 27054 | 25903 | 13193 | 15257 | 15570.6 | 16840 | 4944 | 2383
A. |  | 2024-06-10 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 15257 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10963 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15450 | MW
3 | Day peak Generation : |  |  | 13193 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14842.46 | MW
4 | Evening peak Generation : |  |  | 15257 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 184 | MW
5 | Total Energy Generation : |  | 328.5431 | MKWHr | By Solar | 2.4848 | MKWHr
| By Gas : | 136.733 | MKWHr |  | By Oil: | 47.2973 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 115.9843 | MKWHr |  | By Hydro: | 2.764 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.08688 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4944 | MW | Dhaka | 5195.03 | 5145.03 |  | 50 |  | 18:00 |  | 51.57
|  |  | For Plants S/D or M/C prob = |  |  | 2383 | MW | Chittagong | 1470 | 1470 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7327 | MW | Khulna | 1833.5 | 1833.5 |  | 0 |  | 19:30 |  | 150
7 | Total Gas Supplied : |  |  | 1026.43 | MMCFD |  |  | Rajshahi | 1616.1 | 1616.1 |  | 0 |  | 20:00 |  | 231
8 | Fuel Cost : | i) Gas : | Taka | 418641013.79 | ii) Oil : | Taka | 865634927.16 | Comilla | 1369 | 1369 |  | 0 |  | 21:00 |  | 184
|  | iii) Coal : | Taka | 798777468.72 | Total | Taka | 2083053409.67 | Mymensingh | 1262 | 1152 |  | 110 |  | 22:00 |  | 207.235
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 4172.85 | MKWHr. | Sylhet | 564 | 564 |  | 0 |  | 23:00 |  | 201.505
| ii) During Peak Demand : |  |  | 508 | MW (W to E) at | 21:00 | hrs | Barisal | 551.83 | 551.83 |  | 0 |  | 24:00 |  | 238.75
| iii) Maximum : |  |  | 394 | MW at | 7:00 | hrs | Rangpur | 981 | 957 |  | 24
10 | Maximum Temperature in Dhaka was |  |  |  | 30.5°C |  |  | Total | 14842.46 | 14658.46 |  | 184
B. |  | 2024-06-11 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16840 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14500 | MW
4 | Reserve(Generation end) |  |  |  | 340 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 355.3098 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12517 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.3505 | MKWHr. | ii) HVDC Flow at Peak Time |  | 781 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8422 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.37 |  | (b) Today: | 81.52 |  | (c) Rule Curve: |  | 78.6
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-06-10 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 150 | 42 | 0 | 55 | 307 | 0 | 0 | 56 | 81 | 98 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 23 | 33 | 22 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 32 | 68 | 70 | 25 | 6 | 0 | 35 | 0 | 0 | 0 | 280 | 260 | 204 | 0 | 85 | 20 | 0 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 32 | 2 | 86 | 34 | 0 | 0 | 0 | 36 | 58 | 53 | 37 | 163 | 0 | 55 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 273 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 11 | 367 | 59 | 17 | 17 | 0 | 52 | 35 | 110 | 97 | 45 | 25 | 340 | 60 | 0 | 54 | 53 | 0 | 35 | 0 | 76 | 0 | 240 | 17 | 0 | 790 | 6 | 566 | 0 | 0 | 0 |  | 781 | 0 | 210 | 0 | 78 | 0 | 0 | 0 | 26 | 49 | 40 | 130 | 10 | 32 | 0 | 0 | 0 | 32 | 0 | 48 | 35 | 0 | 33 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 73 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 1110 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 914 | 0 | 307 | 1455 | 0 | 0 |  | 8169 | 6743 | 14912 | 3931 | 781 | 1741 | 0 | 2365 | 5426 | 115 | 0 | 461 | 86 | 0 | 6 | 418 | 81.32
2:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 145 | 49 | 0 | 55 | 308 | 0 | 0 | 50 | 81 | 98 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 23 | 33 | 22 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 32 | 68 | 70 | 25 | 6 | 0 | 37 | 0 | 0 | 0 | 280 | 260 | 204 | 0 | 85 | 20 | 0 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 32 | 0 | 84 | 34 | 0 | 0 | 0 | 36 | 58 | 53 | 40 | 163 | 0 | 55 | 0 | 0 | 210 | 0 | 0 | 0 | 275 | 16 | 5 | 0 | 110 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 13 | 367 | 59 | 17 | 17 | 0 | 51 | 35 | 110 | 97 | 45 | 25 | 340 | 50 | 0 | 54 | 53 | 0 | 35 | 0 | 115 | 0 | 240 | 17 | 0 | 787 | 9 | 565 | 0 | 0 | 0 |  | 782 | 0 | 210 | 0 | 78 | 0 | 0 | 0 | 26 | 49 | 40 | 130 | 10 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 33 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 73 | 0 | 70 | 0 | 82 | 0 | 0 | 70 | 1090 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 911 | 0 | 307 | 1361 | 0 | 0 |  | 8025 | 6439 | 14464 | 3929 | 782 | 1734 | 0 | 2095 | 5305 | 115 | 0 | 411 | 84 | 0 | 9 | 416 | 81.33
3:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 145 | 50 | 0 | 55 | 313 | 0 | 0 | 50 | 81 | 98 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 14 | 23 | 33 | 22 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 24 | 68 | 70 | 24 | 6 | 0 | 37 | 0 | 0 | 0 | 280 | 260 | 208 | 0 | 85 | 20 | 0 | 0 | 51 | 0 | 30 | 41 | 0 | 0 | 32 | 0 | 84 | 34 | 0 | 0 | 0 | 36 | 58 | 50 | 33 | 120 | 0 | 55 | 0 | 0 | 210 | 0 | 0 | 0 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 13 | 367 | 59 | 17 | 17 | 0 | 51 | 35 | 110 | 97 | 38 | 25 | 340 | 50 | 0 | 54 | 37 | 0 | 35 | 0 | 109 | 0 | 240 | 14 | 0 | 790 | 1 | 566 | 0 | 0 | 0 |  | 925 | 0 | 225 | 0 | 47 | 0 | 0 | 0 | 26 | 49 | 0 | 130 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 902 | 0 | 307 | 1278 | 0 | 0 |  | 7866 | 6058 | 13924 | 3954 | 925 | 1691 | 0 | 1638 | 5207 | 115 | 0 | 309 | 84 | 0 | 1 | 359 | 81.34
4:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 373 | 0 |  | 0 | 450 | 144 | 40 | 0 | 55 | 316 | 0 | 0 | 45 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 14 | 23 | 33 | 30 | 8 | 0 | 75 | 38 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 2 | 24 | 34 | 70 | 25 | 6 | 0 | 37 | 0 | 0 | 0 | 280 | 260 | 209 | 0 | 85 | 20 | 0 | 0 | 51 | 0 | 32 | 41 | 0 | 0 | 32 | 0 | 82 | 34 | 0 | 0 | 0 | 36 | 58 | 50 | 40 | 120 | 0 | 62 | 0 | 0 | 210 | 0 | 0 | 0 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 13 | 349 | 59 | 17 | 17 | 0 | 51 | 35 | 110 | 97 | 37 | 25 | 340 | 50 | 0 | 0 | 21 | 0 | 35 | 0 | 106 | 0 | 240 | 0 | 0 | 790 | 6 | 566 | 0 | 0 | 0 |  | 923 | 0 | 225 | 0 | 16 | 0 | 0 | 0 | 26 | 49 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 307 | 1260 | 0 | 0 |  | 7537 | 5844 | 13381 | 3927 | 923 | 1697 | 0 | 1323 | 5097 | 113 | 0 | 213 | 82 | 0 | 6 | 352 | 81.35
5:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 143 | 8 | 0 | 55 | 280 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 14 | 23 | 33 | 30 | 8 | 0 | 75 | 36 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 4 | 24 | 34 | 70 | 25 | 6 | 0 | 40 | 0 | 0 | 0 | 280 | 240 | 218 | 0 | 90 | 20 | 0 | 0 | 51 | 0 | 32 | 33 | 0 | 0 | 32 | 0 | 76 | 35 | 0 | 0 | 0 | 36 | 58 | 50 | 40 | 120 | 0 | 62 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 45 | 0 | 97 | 0 | 23 | 17 | 11 | 317 | 58 | 17 | 17 | 0 | 51 | 35 | 110 | 97 | 37 | 25 | 320 | 52 | 0 | 0 | 17 | 0 | 35 | 0 | 107 | 0 | 230 | 0 | 0 | 775 | 3 | 566 | 0 | 0 | 0 |  | 924 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 26 | 49 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 0 | 273 | 1220 | 0 | 0 |  | 7286 | 5581 | 12867 | 3771 | 924 | 1664 | 0 | 1165 | 4940 | 111 | 0 | 213 | 76 | 0 | 3 | 223 | 81.36
6:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 358 | 0 |  | 0 | 380 | 141 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 16 | 30 | 8 | 0 | 75 | 36 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 1 | 24 | 34 | 70 | 24 | 6 | 0 | 38 | 0 | 0 | 0 | 280 | 240 | 218 | 0 | 90 | 20 | 0 | 0 | 10 | 0 | 0 | 33 | 0 | 0 | 32 | 0 | 58 | 0 | 0 | 0 | 0 | 36 | 58 | 11 | 10 | 120 | 0 | 61 | 0 | 0 | 208 | 0 | 0 | 0 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 1 | 23 | 17 | 0 | 317 | 0 | 17 | 17 | 0 | 51 | 35 | 96 | 97 | 38 | 25 | 310 | 35 | 0 | 0 | 17 | 0 | 35 | 1 | 108 | 0 | 230 | 0 | 0 | 751 | 4 | 565 | 0 | 0 | 5 |  | 924 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 180 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 828 | 0 | 200 | 1112 | 0 | 0 |  | 6718 | 5101 | 11819 | 3695 | 924 | 1420 | 0 | 908 | 4580 | 111 | 0 | 106 | 58 | 13 | 4 | 173 | 81.37
7:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 343 | 0 |  | 0 | 320 | 150 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 23 | 0 | 30 | 8 | 0 | 75 | 37 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 5 | 24 | 34 | 36 | 25 | 6 | 0 | 38 | 0 | 0 | 0 | 280 | 240 | 220 | 0 | 85 | 20 | 0 | 0 | 10 | 0 | 0 | 34 | 0 | 0 | 32 | 0 | 70 | 5 | 0 | 0 | 0 | 36 | 58 | 11 | 10 | 120 | 0 | 61 | 0 | 0 | 208 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 23 | 17 | 0 | 317 | 0 | 17 | 17 | 2 | 51 | 0 | 96 | 97 | 37 | 25 | 310 | 35 | 0 | 0 | 17 | 0 | 35 | 4 | 104 | 0 | 230 | 0 | 0 | 751 | 2 | 565 | 0 | 0 | 17 |  | 925 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 180 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 754 | 2 | 150 | 1029 | 3 | 0 |  | 6604 | 4783 | 11387 | 3681 | 925 | 1388 | 0 | 842 | 4244 | 112 | 0 | 74 | 70 | 49 | 2 | 0 | 81.38
8:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 335 | 0 |  | 0 | 320 | 148 | 0 | 0 | 55 | 260 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 23 | 0 | 30 | 0 | 0 | 75 | 39 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 24 | 34 | 0 | 24 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 32 | 0 | 78 | 18 | 0 | 0 | 0 | 36 | 58 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 208 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 8 | 23 | 17 | 0 | 400 | 0 | 0 | 17 | 2 | 52 | 0 | 51 | 97 | 37 | 25 | 340 | 35 | 4 | 0 | 17 | 0 | 0 | 2 | 103 | 0 | 230 | 0 | 0 | 697 | 0 | 568 | 0 | 0 | 35 |  | 925 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 180 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 712 | 5 | 140 | 893 | 12 | 0 |  | 6381 | 4582 | 10963 | 3717 | 925 | 1470 | 0 | 684 | 3805 | 114 | 0 | 58 | 78 | 112 | 0 | 0 | 81.39
9:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 362 | 0 |  | 0 | 420 | 155 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 23 | 15 | 31 | 8 | 0 | 75 | 39 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 24 | 34 | 0 | 25 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 219 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 32 | 0 | 58 | 18 | 0 | 0 | 1 | 35 | 58 | 22 | 5 | 163 | 0 | 61 | 0 | 0 | 208 | 0 | 0 | 0 | 315 | 0 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 46 | 10 | 23 | 17 | 0 | 388 | 28 | 35 | 17 | 4 | 52 | 0 | 51 | 97 | 36 | 25 | 365 | 35 | 17 | 0 | 17 | 0 | 0 | 5 | 75 | 0 | 280 | 0 | 0 | 660 | 0 | 565 | 0 | 0 | 34 |  | 924 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 620 | 220 | 0 | 0 | 1 | 66 | 0 | 0 | 0 | 715 | 8 | 140 | 916 | 13 | 0 |  | 6824 | 4757 | 11581 | 3920 | 924 | 1669 | 0 | 751 | 3911 | 114 | 0 | 74 | 58 | 160 | 0 | 0 | 81.4
10:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 157 | 0 | 3 | 55 | 331 | 0 | 0 | 5 | 44 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 23 | 33 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 24 | 34 | 12 | 29 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 220 | 0 | 85 | 7 | 0 | 0 | 28 | 0 | 0 | 24 | 0 | 0 | 32 | 0 | 66 | 21 | 0 | 0 | 0 | 35 | 58 | 50 | 37 | 163 | 0 | 62 | 0 | 0 | 208 | 0 | 0 | 0 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 97 | 11 | 23 | 17 | 2 | 366 | 67 | 35 | 17 | 5 | 52 | 0 | 51 | 97 | 37 | 25 | 345 | 40 | 17 | 0 | 17 | 0 | 0 | 6 | 49 | 0 | 300 | 0 | 0 | 743 | 1 | 566 | 0 | 0 | 53 |  | 925 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 640 | 220 | 0 | 0 | 2 | 81 | 11 | 0 | 0 | 717 | 15 | 140 | 1127 | 70 | 0 |  | 7226 | 5085 | 12311 | 3978 | 925 | 1785 | 0 | 876 | 4228 | 115 | 0 | 74 | 66 | 263 | 1 | 0 | 81.41
11:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 156 | 3 | 36 | 55 | 300 | 0 | 0 | 40 | 82 | 98 | 0 | 0 | 0 | 0 | 10 | 35 | 0 | 0 | 15 | 23 | 33 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 3 | 23 | 34 | 36 | 31 | 6 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 219 | 0 | 85 | 20 | 0 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 32 | 4 | 72 | 21 | 0 | 0 | 2 | 35 | 58 | 50 | 37 | 120 | 0 | 61 | 0 | 0 | 208 | 0 | 0 | 0 | 285 | 8 | 8 | 0 | 10 | 0 | 0 | 36 | 0 | 97 | 9 | 23 | 17 | 12 | 344 | 88 | 35 | 17 | 4 | 52 | 0 | 51 | 52 | 41 | 25 | 345 | 53 | 20 | 35 | 17 | 0 | 0 | 18 | 49 | 0 | 260 | 35 | 0 | 850 | 0 | 554 | 0 | 0 | 7 |  | 926 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 640 | 220 | 0 | 0 | 2 | 89 | 77 | 0 | 0 | 713 | 15 | 140 | 1123 | 105 | 0 |  | 7501 | 5065 | 12566 | 3837 | 926 | 1679 | 0 | 1156 | 4315 | 115 | 0 | 190 | 72 | 276 | 0 | 52 | 81.42
12:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 151 | 30 | 50 | 55 | 330 | 0 | 0 | 55 | 82 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 15 | 23 | 33 | 25 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 25 | 34 | 36 | 31 | 6 | 0 | 2 | 0 | 0 | 0 | 280 | 315 | 219 | 0 | 85 | 36 | 0 | 0 | 51 | 0 | 6 | 16 | 0 | 0 | 32 | 5 | 74 | 29 | 0 | 0 | 1 | 35 | 58 | 53 | 40 | 163 | 0 | 61 | 0 | 0 | 207 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 45 | 0 | 0 | 93 | 0 | 97 | 15 | 23 | 17 | 16 | 365 | 59 | 35 | 17 | 0 | 52 | 0 | 51 | 52 | 40 | 25 | 396 | 53 | 13 | 60 | 17 | 0 | 16 | 25 | 49 | 0 | 230 | 54 | 0 | 905 | 4 | 402 | 0 | 0 | 18 |  | 926 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 660 | 220 | 0 | 0 | 1 | 82 | 78 | 0 | 0 | 711 | 29 | 140 | 1226 | 188 | 0 |  | 7846 | 5347 | 13193 | 4011 | 926 | 1788 | 0 | 1339 | 4337 | 115 | 0 | 224 | 74 | 375 | 4 | 54 | 81.43
13:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 150 | 48 | 50 | 55 | 328 | 0 | 0 | 63 | 82 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 23 | 33 | 25 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 32 | 34 | 36 | 31 | 6 | 0 | 6 | 0 | 0 | 0 | 280 | 260 | 219 | 0 | 85 | 35 | 0 | 0 | 51 | 0 | 24 | 16 | 0 | 0 | 16 | 5 | 78 | 29 | 0 | 0 | 1 | 35 | 58 | 53 | 40 | 120 | 0 | 61 | 0 | 0 | 207 | 0 | 0 | 0 | 295 | 16 | 8 | 0 | 30 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 41 | 365 | 59 | 35 | 17 | 2 | 52 | 0 | 51 | 75 | 38 | 25 | 330 | 53 | 19 | 72 | 17 | 0 | 17 | 27 | 49 | 0 | 230 | 54 | 0 | 940 | 4 | 402 | 0 | 0 | 7 |  | 926 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 63 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 17 | 0 | 0 | 0 | 3 | 0 | 4 | 0 | 770 | 220 | 0 | 0 | 3 | 73 | 70 | 0 | 0 | 715 | 22 | 140 | 1212 | 189 | 0 |  | 7808 | 5442 | 13250 | 3881 | 926 | 1723 | 0 | 1479 | 4471 | 115 | 0 | 226 | 78 | 347 | 4 | 0 | 81.44
14:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 143 | 50 | 45 | 55 | 280 | 0 | 0 | 64 | 82 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 0 | 0 | 33 | 25 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 32 | 34 | 46 | 30 | 6 | 0 | 6 | 0 | 0 | 0 | 285 | 260 | 217 | 0 | 86 | 33 | 0 | 0 | 51 | 0 | 27 | 16 | 0 | 0 | 32 | 5 | 76 | 32 | 0 | 0 | 1 | 35 | 58 | 50 | 39 | 120 | 0 | 61 | 0 | 0 | 207 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 30 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 50 | 366 | 59 | 35 | 17 | 2 | 52 | 0 | 51 | 70 | 39 | 25 | 345 | 35 | 24 | 54 | 17 | 0 | 17 | 22 | 49 | 0 | 285 | 54 | 0 | 980 | 6 | 361 | 0 | 0 | 13 |  | 925 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 63 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 53 | 0 | 0 | 0 | 3 | 0 | 4 | 0 | 770 | 220 | 0 | 0 | 2 | 63 | 54 | 0 | 0 | 718 | 15 | 200 | 1268 | 153 | 0 |  | 7824 | 5487 | 13311 | 3901 | 925 | 1643 | 0 | 1495 | 4589 | 115 | 0 | 262 | 76 | 299 | 6 | 0 | 81.42
15:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 152 | 49 | 51 | 55 | 280 | 0 | 0 | 70 | 82 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 18 | 23 | 33 | 31 | 8 | 0 | 75 | 37 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 32 | 34 | 46 | 32 | 6 | 0 | 4 | 0 | 0 | 0 | 325 | 310 | 213 | 8 | 85 | 36 | 1 | 0 | 51 | 0 | 29 | 16 | 0 | 0 | 32 | 5 | 78 | 32 | 0 | 0 | 1 | 35 | 58 | 50 | 36 | 120 | 0 | 58 | 0 | 0 | 204 | 0 | 0 | 0 | 315 | 16 | 2 | 0 | 30 | 0 | 0 | 93 | 0 | 97 | 0 | 23 | 17 | 52 | 403 | 59 | 35 | 17 | 2 | 52 | 0 | 51 | 98 | 38 | 25 | 345 | 35 | 23 | 54 | 17 | 0 | 17 | 13 | 49 | 0 | 320 | 17 | 0 | 1020 | 5 | 275 | 0 | 0 | 26 |  | 925 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 61 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 54 | 0 | 0 | 0 | 5 | 0 | 4 | 0 | 860 | 220 | 0 | 0 | 2 | 66 | 53 | 0 | 0 | 763 | 13 | 250 | 1314 | 68 | 0 |  | 7991 | 5646 | 13637 | 4041 | 925 | 1717 | 0 | 1539 | 4775 | 112 | 0 | 227 | 78 | 218 | 5 | 55 | 81.45
16:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 394 | 0 |  | 0 | 450 | 144 | 51 | 51 | 55 | 324 | 0 | 0 | 70 | 82 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 18 | 23 | 33 | 25 | 8 | 0 | 75 | 38 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 32 | 34 | 58 | 36 | 6 | 0 | 4 | 0 | 0 | 0 | 285 | 270 | 217 | 8 | 85 | 36 | 8 | 0 | 51 | 0 | 23 | 16 | 0 | 0 | 32 | 5 | 78 | 46 | 0 | 0 | 1 | 35 | 58 | 49 | 39 | 163 | 0 | 61 | 0 | 0 | 203 | 0 | 0 | 0 | 300 | 16 | 2 | 0 | 65 | 0 | 0 | 92 | 0 | 89 | 8 | 23 | 17 | 52 | 340 | 59 | 35 | 44 | 1 | 52 | 0 | 78 | 114 | 38 | 25 | 335 | 35 | 18 | 54 | 32 | 0 | 17 | 9 | 62 | 0 | 285 | 17 | 0 | 1062 | 0 | 273 | 0 | 0 | 23 |  | 924 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 63 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 72 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 900 | 220 | 0 | 0 | 1 | 38 | 53 | 0 | 0 | 731 | 7 | 250 | 1296 | 82 | 0 |  | 8081 | 5726 | 13807 | 3937 | 924 | 1796 | 0 | 1744 | 4804 | 113 | 0 | 221 | 78 | 190 | 0 | 55 | 81.45
17:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 152 | 66 | 51 | 55 | 300 | 0 | 0 | 70 | 82 | 115 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 18 | 23 | 33 | 31 | 8 | 0 | 75 | 37 | 0 | 0 | 2 | 222 | 0 | 0 | 0 |  | 6 | 32 | 48 | 58 | 38 | 6 | 0 | 11 | 0 | 0 | 0 | 280 | 270 | 214 | 8 | 85 | 36 | 16 | 0 | 51 | 0 | 32 | 16 | 0 | 0 | 32 | 5 | 78 | 46 | 0 | 0 | 1 | 35 | 58 | 49 | 39 | 120 | 0 | 61 | 0 | 0 | 203 | 0 | 0 | 0 | 290 | 16 | 2 | 0 | 125 | 0 | 0 | 84 | 0 | 93 | 4 | 23 | 17 | 56 | 304 | 59 | 35 | 85 | 1 | 52 | 0 | 93 | 114 | 47 | 25 | 320 | 53 | 11 | 54 | 35 | 0 | 17 | 5 | 69 | 0 | 285 | 17 | 0 | 1050 | 1 | 275 | 0 | 0 | 14 |  | 925 | 0 | 200 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 24 | 63 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 72 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 800 | 220 | 0 | 0 | 0 | 24 | 35 | 0 | 0 | 718 | 6 | 200 | 1225 | 39 | 0 |  | 8098 | 5364 | 13462 | 3873 | 925 | 1665 | 0 | 1897 | 4560 | 112 | 0 | 244 | 78 | 107 | 1 | 45.84 | 81.46
18:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 320 | 0 |  | 0 | 350 | 150 | 81 | 51 | 55 | 240 | 0 | 0 | 70 | 82 | 115 | 0 | 0 | 0 | 0 | 25 | 35 | 55 | 0 | 18 | 23 | 33 | 31 | 8 | 0 | 75 | 38 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 14 | 56 | 51 | 58 | 37 | 19 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 216 | 8 | 85 | 36 | 24 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 32 | 5 | 62 | 56 | 0 | 0 | 0 | 35 | 58 | 52 | 39 | 120 | 0 | 40 | 0 | 0 | 204 | 0 | 0 | 0 | 285 | 16 | 2 | 0 | 125 | 0 | 0 | 100 | 0 | 94 | 0 | 23 | 17 | 57 | 305 | 69 | 35 | 85 | 0 | 52 | 0 | 97 | 114 | 64 | 25 | 310 | 72 | 3 | 54 | 35 | 0 | 17 | 1 | 70 | 0 | 230 | 17 | 0 | 1000 | 0 | 275 | 0 | 0 | 3 |  | 926 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 4 | 20 | 24 | 80 | 8 | 16 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 72 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 740 | 180 | 0 | 0 | 0 | 6 | 35 | 0 | 0 | 713 | 3 | 150 | 1223 | 19 | 0 |  | 7891 | 5198 | 13089 | 3672 | 926 | 1552 | 0 | 2025 | 4394 | 113 | 0 | 309 | 62 | 36 | 0 | 51.57 | 81.46
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 322 | 0 |  | 0 | 360 | 153 | 81 | 51 | 55 | 280 | 0 | 0 | 72 | 82 | 133 | 12 | 0 | 0 | 0 | 45 | 55 | 55 | 0 | 18 | 23 | 18 | 31 | 8 | 0 | 75 | 38 | 0 | 0 | 13 | 221 | 0 | 0 | 0 |  | 24 | 64 | 85 | 58 | 38 | 19 | 0 | 11 | 0 | 0 | 0 | 340 | 335 | 214 | 8 | 85 | 36 | 25 | 0 | 51 | 0 | 36 | 47 | 0 | 0 | 32 | 5 | 86 | 90 | 0 | 0 | 0 | 35 | 58 | 53 | 40 | 120 | 0 | 58 | 0 | 0 | 204 | 0 | 0 | 0 | 280 | 16 | 2 | 0 | 150 | 0 | 0 | 121 | 0 | 79 | 0 | 23 | 17 | 56 | 400 | 78 | 70 | 76 | 0 | 52 | 11 | 107 | 114 | 83 | 25 | 375 | 72 | 0 | 54 | 50 | 0 | 30 | 0 | 71 | 0 | 365 | 72 | 0 | 950 | 4 | 275 | 0 | 0 | 0 |  | 925 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 38 | 50 | 8 | 126 | 10 | 0 | 0 | 0 | 0 | 11 | 10 | 40 | 0 | 0 | 18 | 0 | 35 | 0 | 0 | 5 | 62 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 73 | 0 | 12 | 0 | 47 | 0 | 0 | 35 | 700 | 180 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 850 | 0 | 183 | 1316 | 0 | 0 |  | 8716 | 5710 | 14426 | 4214 | 925 | 1591 | 0 | 2335 | 4566 | 113 | 0 | 592 | 86 | 0 | 4 | 0 | 81.49
19:30 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 370 | 0 |  | 0 | 420 | 148 | 81 | 64 | 55 | 280 | 0 | 0 | 72 | 82 | 133 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 0 | 31 | 8 | 0 | 75 | 39 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 24 | 56 | 85 | 58 | 38 | 19 | 0 | 14 | 0 | 0 | 0 | 285 | 290 | 218 | 8 | 85 | 36 | 33 | 0 | 51 | 0 | 36 | 51 | 0 | 0 | 32 | 5 | 76 | 80 | 0 | 0 | 0 | 35 | 58 | 53 | 40 | 163 | 0 | 60 | 0 | 0 | 204 | 0 | 0 | 0 | 275 | 16 | 2 | 0 | 150 | 0 | 0 | 121 | 0 | 79 | 0 | 23 | 17 | 57 | 366 | 78 | 70 | 85 | 0 | 52 | 17 | 110 | 114 | 85 | 25 | 340 | 72 | 0 | 54 | 53 | 0 | 54 | 0 | 104 | 0 | 320 | 72 | 0 | 950 | 12 | 274 | 0 | 0 | 0 |  | 896 | 0 | 200 | 0 | 26 | 0 | 0 | 0 | 42 | 56 | 24 | 130 | 10 | 0 | 0 | 0 | 0 | 32 | 10 | 88 | 0 | 0 | 22 | 0 | 35 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 73 | 0 | 35 | 0 | 76 | 0 | 0 | 35 | 900 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 903 | 0 | 240 | 1423 | 0 | 0 |  | 8736 | 6257 | 14993 | 4032 | 896 | 1695 | 0 | 2529 | 4972 | 114 | 0 | 667 | 76 | 0 | 12 | 150 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 367 | 0 |  | 0 | 420 | 122 | 80 | 55 | 55 | 280 | 0 | 0 | 72 | 82 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 0 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 24 | 56 | 85 | 58 | 39 | 19 | 0 | 10 | 0 | 0 | 0 | 280 | 270 | 220 | 8 | 85 | 37 | 33 | 0 | 51 | 0 | 36 | 51 | 0 | 0 | 32 | 6 | 78 | 80 | 0 | 0 | 0 | 35 | 58 | 53 | 40 | 163 | 0 | 60 | 0 | 0 | 206 | 0 | 0 | 0 | 280 | 16 | 2 | 0 | 168 | 0 | 0 | 121 | 0 | 79 | 0 | 23 | 17 | 10 | 343 | 79 | 70 | 85 | 0 | 52 | 17 | 110 | 114 | 87 | 25 | 340 | 72 | 0 | 35 | 53 | 0 | 52 | 0 | 102 | 0 | 290 | 35 | 0 | 965 | 8 | 270 | 0 | 0 | 0 |  | 782 | 0 | 200 | 0 | 48 | 0 | 0 | 0 | 47 | 56 | 24 | 126 | 10 | 0 | 0 | 0 | 0 | 36 | 10 | 85 | 0 | 0 | 45 | 0 | 35 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 73 | 0 | 35 | 0 | 104 | 0 | 0 | 45 | 940 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 915 | 0 | 289 | 1412 | 0 | 0 |  | 8539 | 6269 | 14808 | 3954 | 782 | 1620 | 0 | 2518 | 5074 | 115 | 0 | 659 | 78 | 0 | 8 | 231 | 81.48
21:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 374 | 0 |  | 0 | 450 | 130 | 51 | 36 | 55 | 325 | 0 | 0 | 39 | 48 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 33 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 224 | 0 | 0 | 0 |  | 24 | 57 | 85 | 68 | 38 | 19 | 0 | 25 | 0 | 0 | 0 | 280 | 270 | 218 | 8 | 85 | 36 | 36 | 0 | 51 | 0 | 27 | 51 | 0 | 0 | 32 | 6 | 82 | 70 | 0 | 0 | 0 | 35 | 58 | 53 | 40 | 163 | 0 | 59 | 0 | 0 | 206 | 0 | 0 | 0 | 300 | 16 | 2 | 0 | 195 | 0 | 0 | 121 | 0 | 92 | 0 | 23 | 17 | 10 | 365 | 79 | 70 | 68 | 0 | 52 | 17 | 110 | 114 | 86 | 25 | 340 | 72 | 0 | 35 | 53 | 0 | 52 | 0 | 115 | 0 | 285 | 17 | 0 | 1011 | 11 | 275 | 0 | 0 | 0 |  | 781 | 0 | 235 | 0 | 15 | 0 | 0 | 0 | 42 | 51 | 24 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 45 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 73 | 0 | 50 | 0 | 107 | 0 | 0 | 50 | 1100 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 955 | 0 | 307 | 1363 | 0 | 0 |  | 8680 | 6577 | 15257 | 4082 | 781 | 1900 | 0 | 2437 | 5291 | 115 | 0 | 558 | 82 | 0 | 11 | 184 | 81.49
22:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 152 | 48 | 34 | 55 | 280 | 0 | 0 | 33 | 48 | 149 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 18 | 23 | 33 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 24 | 64 | 85 | 68 | 38 | 19 | 0 | 34 | 0 | 0 | 0 | 295 | 290 | 215 | 8 | 86 | 36 | 42 | 0 | 43 | 0 | 27 | 51 | 0 | 0 | 32 | 6 | 82 | 71 | 0 | 0 | 0 | 35 | 58 | 53 | 40 | 120 | 0 | 54 | 0 | 0 | 207 | 0 | 0 | 0 | 290 | 16 | 2 | 0 | 145 | 0 | 0 | 120 | 0 | 97 | 0 | 23 | 17 | 10 | 366 | 78 | 70 | 51 | 0 | 52 | 0 | 110 | 114 | 86 | 25 | 340 | 70 | 0 | 35 | 53 | 0 | 52 | 0 | 104 | 0 | 295 | 17 | 0 | 1010 | 8 | 274 | 0 | 0 | 0 |  | 774 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 41 | 51 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 45 | 0 | 36 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 50 | 0 | 108 | 0 | 0 | 50 | 1100 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 967 | 0 | 250 | 1312 | 0 | 0 |  | 8500 | 6363 | 14863 | 4068 | 774 | 1876 | 0 | 2202 | 5183 | 115 | 0 | 555 | 82 | 0 | 8 | 207.235 | 0
23:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 382 | 0 |  | 0 | 450 | 150 | 49 | 34 | 55 | 320 | 0 | 0 | 33 | 48 | 149 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 19 | 23 | 33 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 9 | 221 | 0 | 0 | 0 |  | 12 | 66 | 85 | 68 | 38 | 19 | 0 | 36 | 0 | 0 | 0 | 320 | 270 | 185 | 0 | 86 | 36 | 45 | 0 | 43 | 0 | 28 | 51 | 0 | 0 | 32 | 6 | 80 | 71 | 0 | 0 | 0 | 35 | 58 | 25 | 40 | 163 | 0 | 53 | 0 | 0 | 207 | 0 | 0 | 0 | 310 | 16 | 2 | 0 | 145 | 0 | 0 | 120 | 0 | 97 | 0 | 24 | 17 | 10 | 405 | 79 | 70 | 17 | 0 | 51 | 0 | 110 | 114 | 87 | 25 | 375 | 70 | 0 | 35 | 53 | 0 | 52 | 0 | 78 | 25 | 270 | 17 | 0 | 1028 | 3 | 335 | 0 | 0 | 0 |  | 781 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 41 | 51 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 42 | 0 | 36 | 0 | 0 | 5 | 61 | 0 | 210 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 50 | 0 | 110 | 0 | 0 | 50 | 1110 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 975 | 0 | 298 | 1323 | 0 | 0 |  | 8597 | 6492 | 15089 | 4177 | 781 | 1906 | 0 | 2132 | 5340 | 115 | 0 | 555 | 80 | 0 | 3 | 201.505 | 81.51
24:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 152 | 62 | 43 | 55 | 320 | 0 | 0 | 50 | 82 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 20 | 23 | 33 | 32 | 8 | 0 | 75 | 40 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 64 | 79 | 68 | 38 | 6 | 0 | 36 | 0 | 0 | 0 | 280 | 270 | 171 | 0 | 85 | 37 | 49 | 0 | 43 | 0 | 29 | 51 | 0 | 0 | 32 | 6 | 80 | 83 | 0 | 0 | 0 | 35 | 58 | 50 | 40 | 163 | 0 | 50 | 0 | 0 | 208 | 0 | 0 | 0 | 320 | 16 | 2 | 0 | 145 | 0 | 0 | 125 | 0 | 97 | 0 | 24 | 17 | 20 | 402 | 79 | 35 | 17 | 0 | 51 | 0 | 110 | 114 | 86 | 25 | 340 | 70 | 0 | 35 | 53 | 0 | 36 | 0 | 68 | 35 | 240 | 17 | 0 | 1029 | 0 | 344 | 0 | 0 | 0 |  | 711 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 31 | 51 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 42 | 0 | 36 | 0 | 0 | 5 | 63 | 0 | 210 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 1110 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 994 | 0 | 307 | 1408 | 0 | 0 |  | 8485 | 6515 | 15000 | 4083 | 711 | 1947 | 0 | 2112 | 5465 | 115 | 0 | 487 | 80 | 0 | 0 | 238.75 | 81.52
KWH | 0 | 0 | 0 | 4243050 | 0 | 0 | 0 | 9219600 | 0 |  | 0 | 10148500 | 3528785 | 936960 | 780238 | 1337224 | 7253576 | 0 | 0 | 966720 | 1388160 | 2181600 | 14241 | 0 | 0 | 0 | 488880 | 664458 | 665473 | 0 | 381000 | 522000 | 641520 | 679300 | 189120 | 0 | 1824000 | 940000 | 0 | 0 | 91715 | 5233687 | 0 | 0 | 0 |  | 197760 | 872784 | 1203546 | 1151640 | 761280 | 199680 | 0 | 474720 | 0 | 0 | 0 | 7375200 | 6487000 | 5182000 | 66909 | 1927270 | 630144 | 279360 | 0 | 988420 | 0 | 520480 | 809194 | 0 | 0 | 746800 | 79900 | 1842240 | 868800 | 0 | 0 | 8550 | 839000 | 1381920 | 1063800 | 821304 | 3471955 | 0 | 1368672 | 0 | 0 | 5177000 | 0 | 0 | 0 | 7171500 | 336528 | 111312 | 0 | 1999745 | 0 | 0 | 1912800 | 0 | 2159280 | 58455 | 560640 | 432960 | 607200 | 8622000 | 1369200 | 857280 | 818800 | 23281 | 1252036 | 295822 | 2169525 | 2335860 | 1260840 | 590400 | 8196100 | 1240320 | 168310 | 858240 | 782836 | 0 | 685080 | 136667 | 1948800 | 61920 | 6504800 | 501818 | 0 | 21332725 | 86880 | 10392727 | 0 | 0 | 267218 |  | 21350545 | 0 | 5341536 | 0 | 368640 | 0 | 0 | 0 | 354240 | 548608 | 267375 | 2267000 | 228383 | 242976 | 0 | 0 | 0 | 118813 | 34553 | 320224 | 46540 | 0 | 258400 | 0 | 248382 | 0 | 0 | 108720 | 1455272 | 0 | 5488000 | 0 | 0 | 3771273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7853455 | 1049760 | 0 | 534816 | 0 | 881798 | 0 | 28906 | 525120 | 22912000 | 5139245 | 0 | 0 | 19980 | 684720 | 1374528 | 0 | 0 | 19941815 | 136693 | 5432700 | 29029091 | 952000 | 0 |  | 189227040 | 139316107 | 328543147 | 95496708 | 21350545 | 41236336 | 0 | 40133880 | 115984330 | 2764000 | 0 | 7163448 | 1842240 | 2484780 | 86880 | 0
Fuel Cost | 0 | 0 | 0 | 18881572.5 | 0 | 0 | 0 | 26552448 | 0 |  | 0 | 32272230 | 12068444.7 | 18514329.6 | 14590450.6 | 23561886.88 | 22123406.8 | 0 | 0 | 19102387.2 | 24917472 | 42366672 | 265594.65 | 0 | 0 | 0 | 8926948.8 | 10471858.08 | 12171501.17 | 0 | 285750 | 0 | 0 | 0 | 3387139.2 | 0 | 0 | 0 | 0 | 0 | 1737082.1 | 16695461.53 | 0 | 0 | 0 |  | 3478598.4 | 15369726.24 | 21555508.86 | 21950258.4 | 14898249.6 | 3286732.8 | 0 | 0 | 0 | 0 | 0 | 20576808 | 19850220 | 17204240 | 224145.15 | 6225082.1 | 2123585.28 | 1223596.8 | 0 | 3963564.2 | 0 | 9321796.8 | 14614043.64 | 0 | 0 | 2778096 | 59925 | 12085094.4 | 2701968 | 0 | 0 | 0 | 3272100 | 5154561.6 | 4840290 | 3736933.2 | 11874086.1 | 0 | 7596129.6 | 0 | 0 | 14443830 | 0 | 0 | 0 | 22159935 | 252396 | 84597.12 | 0 | 40794798 | 0 | 0 | 36744888 | 0 | 38024920.8 | 0 | 9984998.4 | 7511856 | 10067376 | 22848300 | 26096952 | 16082572.8 | 14689272 | 0 | 20470788.6 | 5750779.68 | 38921278.5 | 44638284.6 | 24472904.4 | 10515024 | 21801626 | 21172262.4 | 0 | 15697209.6 | 13135988.08 | 0 | 12242379.6 | 0 | 35117376 | 1048924.8 | 19319256 | 7065597.44 | 0 | 148689093.25 | 0 | 61317089.3 | 0 | 0 | 0 |  | 59995031.45 | 0 | 15757531.2 | 0 | 6395904 | 0 | 0 | 0 | 6663254.4 | 10319316.48 | 4759275 | 7163720 | 1082535.42 | 4188906.24 | 0 | 0 | 0 | 2127940.83 | 634047.55 | 5382965.44 | 990371.2 | 0 | 4627944 | 0 | 4448521.62 | 0 | 0 | 82301.04 | 16051650.16 | 0 | 46318720 | 0 | 0 | 12445200.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22932088.6 | 17929900.8 | 0 | 10600053.12 | 0 | 17565416.16 | 0 | 0 | 10418380.8 | 148469760 | 15983051.95 | 0 | 0 | 0 | 0 | 23848060.8 | 0 | 0 | 145575249.5 | 0 | 40473615 | 191882291.51 | 0 | 0 |  | 1300020530.35 | 855113005.17 | 2155133535.52 | 286280112.67 | 59995031.45 | 132360901.12 | 0 | 735751635.5 | 798777468.72 | 0 | 0 | 129883291.66 | 12085094.4 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 151 | 30 | 50 | 55 | 330 | 0 | 0 | 55 | 82 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 15 | 23 | 33 | 25 | 8 | 0 | 75 | 40 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 25 | 34 | 36 | 31 | 6 | 0 | 2 | 0 | 0 | 0 | 280 | 315 | 219 | 0 | 85 | 36 | 0 | 0 | 51 | 0 | 6 | 16 | 0 | 0 | 32 | 5 | 74 | 29 | 0 | 0 | 1 | 35 | 58 | 53 | 40 | 163 | 0 | 61 | 0 | 0 | 207 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 45 | 0 | 0 | 93 | 0 | 97 | 15 | 23 | 17 | 16 | 365 | 59 | 35 | 17 | 0 | 52 | 0 | 51 | 52 | 40 | 25 | 396 | 53 | 13 | 60 | 17 | 0 | 16 | 25 | 49 | 0 | 230 | 54 | 0 | 905 | 4 | 402 | 0 | 0 | 18 |  | 926 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 230 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 660 | 220 | 0 | 0 | 1 | 82 | 78 | 0 | 0 | 711 | 29 | 140 | 1226 | 188 | 0 |  | 13193 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 374 | 0 |  | 0 | 450 | 130 | 51 | 36 | 55 | 325 | 0 | 0 | 39 | 48 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 33 | 31 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 224 | 0 | 0 | 0 | 0 | 24 | 57 | 85 | 68 | 38 | 19 | 0 | 25 | 0 | 0 | 0 | 280 | 270 | 218 | 8 | 85 | 36 | 36 | 0 | 51 | 0 | 27 | 51 | 0 | 0 | 32 | 6 | 82 | 70 | 0 | 0 | 0 | 35 | 58 | 53 | 40 | 163 | 0 | 59 | 0 | 0 | 206 | 0 | 0 | 0 | 300 | 16 | 2 | 0 | 195 | 0 | 0 | 121 | 0 | 92 | 0 | 23 | 17 | 10 | 365 | 79 | 70 | 68 | 0 | 52 | 17 | 110 | 114 | 86 | 25 | 340 | 72 | 0 | 35 | 53 | 0 | 52 | 0 | 115 | 0 | 285 | 17 | 0 | 1011 | 11 | 275 | 0 | 0 | 0 |  | 781 | 0 | 235 | 0 | 15 | 0 | 0 | 0 | 42 | 51 | 24 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 40 | 0 | 0 | 45 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 73 | 0 | 50 | 0 | 107 | 0 | 0 | 50 | 1100 | 220 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 955 | 0 | 307 | 1363 | 0 | 0 |  | 15257 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 100 | 64 | 55 | 330 | 0 | 0 | 85 | 82 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 33 | 33 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 24 | 64 | 85 | 70 | 38 | 18 | 0 | 20 | 0 | 0 | 0 | 300 | 280 | 220 | 8 | 85 | 37 | 5 | 0 | 51 | 0 | 41 | 51 | 0 | 0 | 32 | 6 | 151 | 80 | 0 | 0 | 0 | 40 | 58 | 50 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 300 | 0 | 0 | 120 | 0 | 97 | 0 | 25 | 17 | 50 | 400 | 80 | 88 | 51 | 0 | 52 | 35 | 110 | 114 | 85 | 25 | 375 | 70 | 0 | 108 | 53 | 0 | 52 | 0 | 115 | 35 | 320 | 163 | 0 | 1000 | 40 | 340 | 0 | 0 |  |  | 798 | 0 | 200 | 0 | 50 | 0 | 0 | 0 | 50 | 60 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 88 | 35 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 64 | 0 | 210 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 73 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 94 | 0 | 0 | 1000 | 0 | 307 | 1400 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 50 | 64 | 55 | 320 | 0 | 0 | 70 | 82 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 18 | 21 | 33 | 33 | 8 | 0 | 75 | 40 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 48 | 50 | 70 | 30 | 6 | 0 | 6 | 0 | 0 |  | 280 | 280 | 220 | 8 | 85 | 37 | 5 | 0 | 51 | 0 | 40 | 33 | 0 | 0 | 32 | 6 | 146 | 60 | 0 | 0 | 1.6 | 40 | 58 | 50 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 16 | 5 | 0 | 270 | 0 | 0 | 97 | 0 | 90 | 20 | 25 | 17 | 12 | 400 | 68 | 52 | 51 | 5 | 52 | 35 | 85 | 114 | 38 | 25 | 370 | 50 | 50 | 54 | 35 | 0 | 34 | 35 | 115 | 35 | 240 | 54 | 0 | 1000 | 40 | 340 | 0 | 0 | 70 |  | 943 | 0 | 200 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 210 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 94 | 0 | 70 | 0 | 8 | 113 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 1000 | 30 | 307 | 1200 | 130 | 0 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 370 | 152 | 8 | 17 | 15 | 319 | 0 | 0 | 8 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 0 | 33 | 32 | 8 | 0 | 75 | 38 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 6 | 48 | 34 | 0 | 25 | 6 | 0 | 6 | 0 | 0 | 0 | 285 | 270 | 174 | 0 | 85 | 37 | 5 | 0 | 51 | 0 | 28 | 33 | 0 | 0 | 32 | 6 | 76 | 67 | 0 | 0 | 1 | 36 | 58 | 50 | 39 | 120 | 0 | 60 | 0 | 0 | 207 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 97 | 0 | 80 | 0 | 24 | 17 | 0 | 395 | 68 | 17 | 17 | 0 | 15 | 0 | 51 | 114 | 39 | 25 | 370 | 16 | 12 | 0 | 17 | 0 | 34 | 11 | 65 | 35 | 240 | 0 | 0 | 1030 | 0 | 344 | 0 | 0 | 35 | 0 | 925 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 210 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 800 | 220 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 871 | 9 | 200 | 1115 | 61 | 0 | 0 |  |  |  | 136733044 | 21350545 | 0 | 115984330 | 47297328 | 1842240 | 2484780 | 86880 | 2764000 |  |  | 328543147
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [8 empty] | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [9 empty] | 136.733 | 21.3505 | 0 | 115.9843 | 47.2973 | 1.8422 | 2.4848 | 0.08688 | 2.764
| Minimum Generation |  | 10963 | 8:00
| Highest Generation |  | 15257 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [71 empty] | 328.5431
| Day Peak Generation |  | 13193 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15257 | 21:00 |  |  |  |  | 10500 | [196 empty] | 202699852
| HVDC Max Flow |  | 926 | 11:00 | [201 empty] | 202.6999
| HVDC EvPeak Flow |  | 781 | 21:00
| Load factor L.F |  | 89.72% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-11
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-10 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13193 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 12517
Evening Peak Generation : |  |  | 15257 | MW Hour : | 21:00 | Available Max Generation : |  | 16840
E.P. Demand (at gen end) : |  |  | 15450 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16500
Maximum Generation : |  |  | 15257 | MW Hour : | 21:00 | Reserve(Generation end) |  | 340
Total Gen. (MKWH) : |  |  | 328.5431 | System Load Factor : | 89.72% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 394 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-11
Actual : |  | 81.52 | Ft.(MSL) , | Rule curve : | 78.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 1026.43 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 418641013.79
: |  |  | Coal : | 798777468.72 | Oil : | 865634927.16 | Total : | 2083053409.67
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 50 | 1200:00 | 5310.1633 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1463.5928 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2051.5561 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1784.4161 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1467.6227 |  |  | 0 | 0%
Mymensingh Area |  | 110 | 2640:00 | 1092.2058 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 611.5045 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 510.265 |  |  | 0 | 0%
Rangpur Area |  | 24 | 576:00 | 997.9738 |  |  | 0 | 0%
Total |  | 184 |  | 15289.3002 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:03 | Jashore 132/33kV S/S T-1 HT is restored.
| 08:03 | Jashore 132/33kV S/S T-1 LT is restored.
| 08:09 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
08:58 | 10:35 | Maniknagar-Narinda 132kV Ckt-2 Forced S/D from Maniknagar 132/33kV end Due to Narinda ckt 2 cable flute maintenance.
09:09 | 16:44 | Mymensingh RPCL-Tangail 132kV Ckt-1 Project Work S/D from Ghatail 132/33kV end Due to LILO connection for 132KV
Muktagacha Grid S/S.
09:27 |  | Maniknagar 132/33kV S/S Motijheel Ckt-2 Scheduled S/D Due to Motijheel Ckt-2 Maintenance works.
| 09:53 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT is restored.
| 9:54 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT is restored.
10:07 | 13:52 | Naogaon-Niyamatpur 132kV Ckt-1 Project Work S/D from Naogaon 132/33kV end Due to bus upgradetion for Niamatpur S/S.
10:12 | 11:47 | Gopalganj 132/33kV S/S Gallamari-1 Project Work S/D Due to Due to punch point rectification work by siemens
11:00 | 13:00 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to Shutdown taken by DPBS1 due to 33 kV TR-1 & TR-2 section DS | [5 empty] | 70 MW load interrup.
maintenance purpose.
11:25 | 15:22 | Sreepur 230/132/33kV S/S Sreepur-Ashuganj Ckt-1 Scheduled S/D Due to Project work.
13:58 | 16:10 | Niamatpur 132/33kV S/S 132kV Rahanpur Ckt-1 Scheduled S/D Due to Project work.
16:12 | 16:56 | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 Project Work S/D Due to 132 kv busbar scheme change interlock testing &
protection shift to bus coupler cb relay open.
00:40 | 00:57 | Chapai 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to 33 kV bus section red hot. |  |  | Chapai 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to Red hot.A90:H105 |  |  | 25 MW load interrup.
00:41 | 00:56 | Chapai 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to Red hot.
04:57 | 05:30 | Sirajganj 132/33kV S/S Sherpur-2 Tripped showing Distance relay (A Phase) relays.
05:57 |  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to Shutdown taken for red hot maintenance. | [5 empty] | 20 Mw load interrup.
05:58 |  | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to Shutdown taken for red hot maintenance.
06:11 |  | Bashundhara-Rampura 132 kV Ckt-2 Forced S/D from Rampura 230/132kV end Due to Red hot Maintenance at Basundhara S/S End.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-10 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4243050
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 374 | 9219600 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10148500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 0 | 51 | 936960 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 130 | 3528785 | GT-1 Under Maint
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 0 | 36 | 780238 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1337224
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 14241 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 0 | 39 | 966720 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7253576
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 1388160 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 488880
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2181600
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 664458
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 665473
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 903000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 641520
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 31 | 679300
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 189120 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 1999745 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 92 | 2159280 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 857280 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1240320 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 858240 | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 136667
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 61920 | Engine problem
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under maint.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5332 | 2578 | 53543857
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 91715 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 58455
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 199680 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 115 | 2764000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 224 | 5233687
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 818800 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 57 | 872784 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1203546 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 68 | 1151640 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 23 | 560640 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 474720
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 761280 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23281
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1252036 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 295822 | Fuel shortage
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2169525
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 590400 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 782836 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 501818
60 | SS Power I |  | SS Power | 2*612 | 1224 | 1011 | 21332725
| Cox's Bazar Wind |  | IPP | 66 | 60 | 11 | 86880 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 275 | 10392727
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 0 | 0 | 267218
| Chattogram area Total |  |  |  | 4404 | 2310 | 51886215
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 5182000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7375200
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6487000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 6504800 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 630144 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 36 | 279360 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 66909 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 988420
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 10 | 607200 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 27 | 520480 | Low demand
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 1927270 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 432960 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 82 | 1842240
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 746800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 51 | 809194
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 6 | 79900 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2335860
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 86 | 1260840 | Fuel shortage
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 52 | 685080 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1948800
| Cumilla Area Total |  |  |  | 2929 | 1861 | 40710457
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 70 | 868800 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8550
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 121 | 1912800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 1369200 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 168310
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 197760 | Fuel shortage
| Mymensingh Area Total |  |  |  | 592 | 294 | 4525420
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 35 | 839000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1381920 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3471955
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1063800
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 40 | 821304 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 111312 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1368672
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 206 | 5177000
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 336528 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7171500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 8622000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8196100 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1637 | 38561091
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 781 | 21350545
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 0 | 15 | 368640 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 354240
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 51 | 548608 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 235 | 5341536 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 0 | 24 | 267375
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 73 | 1049760 | Low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 684720
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 955 | 19941815
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3699 | 2176 | 49907239
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 242976 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 228383
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2267000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1100 | 22912000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5139245
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5432700
| Barisal Area Total |  |  |  | 2235 | 1763 | 36222304
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 118813
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 34553 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 46540 | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 258400
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 145 | 3771273 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7853455
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 248382 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 108720 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 320224 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 534816 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 525120 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19980
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1363 | 29029091
| Rajshahi Area Total |  |  |  | 3431 | 2157 | 42869367
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 60 | 1455272
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5488000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 881798 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28906
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 1374528 | Engine problem
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 136693
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 952000
| Rangpur Area Total |  |  |  | 950 | 481 | 10317197
| Total |  |  |  | 25903 | 15257 | 328543147
| Eastern Grid Total |  |  |  | 15588 | 8680 | 189227040
| Western Grid Total |  |  |  | 10315 | 6577 | 139316107
| National Grid Total |  |  |  | 25903 | 15257 | 328543147
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-06-10
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  | 9700.03 | MW | (b) ENTIRE WESTERN GRID: |  | 4958.43 | MW
i) Dhaka area |  | 5145.03 | MW | i) Khulna area |  | 1833.5 | MW
ii) Chattogram area |  | 1470 | MW | ii) Barishal area |  | 551.83 | MW
iii) Cumilla area |  | 1369 | MW | iii) Rajshahi area |  | 1616.1 | MW
iv) Mymensingh area |  | 1152 | MW | iv) Rangpur area |  | 957 | MW
v) Sylhet area |  | 564 | MW
System Total Demand at Evening Peak Hour (a + b) = |  |  |  | 14658.46 | MW
Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
AKS | 0 | 00:00 | KSRM | 31 | 14:00 | Satkhira | 147 | 21:00
AKSML | 123 | 13:00 | Kabirpur | 271 | 16:00 | Satmasjid | 116 | 00:00
Aftabnagar | 42 | 00:00 | Kachua | 81 | 00:00 | Savar | 212 | 16:00
Agargaon | 107 | 13:00 | Kallyanpur | 120 | 00:00 | SevenRings | 20.94 | 05:00
Agrabad | 106 | 14:00 | Kalurghat | 38 | 10:00 | ShahCement | 36 | 10:00
Amnura | 76 | 00:00 | Kamrangirchar | 54 | 13:00 | Shahjadpur | 88 | 20:00
Ashuganj | 90.5 | 19:30 | Kaptai | N/A | N/A | Shahjibazar | 134 | 22:00
BIPTC | N/A | N/A | Kazla | 104 | 00:00 | Shahmirpur | 59 | 00:00
BSRM | 193 | 18:00 | Keranigonj | 89 | 00:00 | Shariatpur | 97 | 22:00
Bagerhat | 117 | 22:00 | Khagrachori | 34 | 21:00 | Sherpur | 120 | 19:00
Bakulia | 101 | 21:00 | Khulna | 103 | 19:30 | Shikalbaha | 30 | 00:00
Banani | 42 | 12:00 | Khulshi | 187 | 20:00 | Shikalbaha-230 | N/A | N/A
Bangabhaban | 19 | 10:00 | Kishoreganj | 188 | 22:00 | Shitalakhya | 103.2 | 12:00
Barapukuria | 71 | 22:00 | Kodda | 291 | 21:00 | Sholosohor | 46 | 09:00
Barguna | 25.9 | 23:00 | Kulaura | 48 | 19:30 | Shyampur | 154 | 00:00
Barishal | 128 | 21:00 | Kurigram | 62 | 21:00 | Siddhirganj | 118 | 19:30
Barishal-230 | 108 | 00:00 | Kushtia | 176 | 00:00 | Sirajganj | 116 | 21:00
Baroaulia | 84 | 13:00 | Lalbag | 98 | 11:00 | Sonargaon | 120 | 00:00
Baroirhat | 60 | 19:30 | Lalmonirhat | 58 | 19:00 | Sreemongol | 67 | 23:00
Bashundhara | 184 | 13:00 | MI_Cement | 10.8 | 18:30 | Sreepur | 66 | 19:30
BashundharaCement | 6 | 01:00 | Madanganj | 27 | 00:00 | Srinagar | 48.48 | 00:00
Beanibazar | 72 | 19:00 | Madaripur | 133 | 23:00 | Sunamganj | 52 | 23:00
Benapole | 86 | 19:00 | Madartek | 93.18 | 00:00 | Sylhet | 40 | 22:00
Bhaluka | 150 | 19:00 | Madunaghat | 57 | 19:30 | Sylhet-132 | 106 | 19:00
Bhandaria | 60.13 | 22:00 | Magura | 74 | 00:00 | TK | 34 | 00:00
Bhangura | 38 | 00:00 | Mahasthangarh | 82 | 20:00 | Tangail | 253 | 22:00
Bheramara(GK) | 76 | 00:00 | Manikganj | 149 | 01:00 | Thakurgaon | 110 | 20:00
Bhulta | 258 | 15:00 | Maniknagar | 82 | 12:00 | Tongi | 133 | 23:00
Bog-Sherpur | 68 | 00:00 | Matarbari | 51 | 21:00 | Ullahpara | 28 | 21:00
Bogura | 169 | 21:00 | Matuail | 76 | 12:00 | Ullon | 52 | 00:00
Borhanuddin | 111 | 23:00 | Millgate | 123 | 12:00 | Uttara | 68 | 19:30
Brahmanbaria | 173 | 22:00 | Mirpur | 153 | 00:00 | UttaraNew | 48 | 00:00
Cantonment | 132 | 13:00 | Mirsorai | 4 | 22:00 | Zigatola | 92 | 00:00
Chandpur | 82 | 00:00 | Mirzapur | 54 | 13:00
Chandraghona | 37 | 21:00 | Mithapukur | 54 | 23:00
Chapai | 82 | 00:00 | Modern | 0 | 00:00
Charsaidpur | 47 | 17:00 | Mogbazar | 127.5 | 16:00
Chauddagram | 71 | 01:00 | Mongla | 30 | 01:00
Chhatak | 30 | 22:00 | Motijheel | 43 | 00:00
Chowmuhani | 227 | 22:00 | Munshiganj | 122 | 00:00
Chuadanga | 120 | 03:00 | Mymensingh | 222 | 00:00
Coxsbazar | 127 | 18:30 | Naogaon | 149 | 22:00
Cumilla(N) | 160 | 22:00 | Narail | 66 | 01:00
Cumilla(S) | 186 | 01:00 | Narinda | 57 | 13:00
Daudkandi | 153 | 01:00 | Narshingdi | 170 | 18:30
Dhaka | 46 | 12:00 | Natore | 154 | 21:00
Dhamrai | 140 | 19:30 | Nawabganj | 63 | 22:00
Dhanmondi | 157 | 13:00 | Netrakona | 95 | 03:00
Dohazari | 99 | 00:00 | New | 57.4 | 12:00
Faridpur | 191 | 22:00 | Niamatpur | 80 | 00:00
Fatullah | 69 | 16:00 | Noapara | 55 | 00:00
Fenchuganj | 41 | 21:00 | PHP | 10 | 21:00
Feni | 108 | 00:00 | Pabna | 133 | 00:00
GPH | 81 | 17:00 | Palashbari | 117 | 00:00
Ghatail | 70 | 20:00 | Panchagarh | 61 | 20:00
Ghorashal | 45 | 01:00 | Patuakhali | 101.6 | 23:00
Goalpara | 40 | 22:00 | Payra | 40 | 22:00
Gollamari | 86 | 01:00 | Postogola | 63 | 00:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-10 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 384 | 17:00 | 357 | 13:00 | Kaliakoir | 368 | 18:00 | 350 | 15:00
| Ashuganj | 405 | 8:00 | 396 | 16:00 | Madunaghat_I | 416 | 06:00 | 413 | 08:00
| Bhulta | 402 | 18:00 | 387 | 00:00 | Meghnaghat | 380 | 18:00 | 363 | 00:00
| Bibiana | 396 | 18:00 | 387 | 08:00 | Payra | 411 | 18:00 | 401 | 00:00
| BIPTC | 404 | 06:00 | 390 | 15:00 | Rahanpur | 400 | 09:00 | 382 | 00:00
| Bogura | 394 | 09:00 | 374 | 19:30 | Rampal | 404 | 18:00 | 389 | 00:00
| Gopalganj | 399 | 18:30 | 382 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 18:30 | 217 | 00:00 | Hasnabad | 228 | 04:00 | 219 | 00:00
| AKSML | 228 | 19:00 | 217 | 14:00 | Hathazari | 230 | 18:30 | 222 | 10:00
| Aminbazar | 227 | 17:00 | 217 | 00:00 | Ishurdi | 235 | 18:30 | 223 | 15:00
| Ashuganj | 234 | 07:00 | 225 | 00:00 | Jhenaidah | 226 | 18:30 | 212 | 15:00
| Ashuganj-400 | 230 | 6:00 | 220 | 16:00 | Kaliakoir | 232 | 18:00 | 220 | 15:00
| Baghabari | 230 | 18:30 | 221 | 15:00 | Keranigonj | 228 | 18:30 | 217 | 00:00
| Barapukuria | 216 | 10:00 | 206 | 19:30 | Khulna(S) | 230 | 18:30 | 218 | 00:00
| Barapukuria-230 | 215 | 14:00 | 208 | 21:00 | Madunaghat_I | 227 | 06:00 | 223 | 08:00
| Barishal | 235 | 18:00 | 224 | 23:00 | Maniknagar | 229 | 07:00 | 219 | 10:00
| Bheramara | 235 | 07:00 | 222 | 15:00 | Meghnaghat | 233 | 07:00 | 225 | 00:00
| Bhulta | 229 | 18:00 | 220 | 15:00 | Meghnaghat-400 | 231 | 18:00 | 222 | 00:00
| Bibiana | 229 | 20:00 | 222 | 04:00 | Mirsorai | 230 | 18:30 | 217 | 15:00
| BIPTC | 235 | 18:30 | 221 | 15:00 | Rajshahi | 234 | 07:00 | 219 | 15:00
| Bogura | 223 | 07:00 | 213 | 00:00 | Rampal | 230 | 18:00 | 219 | 00:00
| Bogura-400 | 223 | 07:00 | 213 | 19:30 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 238 | 18:00 | 230 | 01:00 | Rampura | 226 | 08:00 | 218 | 15:00
| BSRM | 228 | 19:30 | 216 | 11:00 | Shikalbaha | 229 | 18:30 | 219 | 10:00
| Cumilla(N) | 229 | 18:30 | 219 | 00:00 | Shyampur | 229 | 18:30 | 219 | 00:00
| Fenchuganj | 234 | 18:00 | 228 | 15:00 | Siddhirganj | 230 | 07:00 | 221 | 15:00
| Ghorashal | 230 | 01:00 | 228 | 00:00 | Sirajgonj | 234 | 18:00 | 228 | 15:00
| Ghorashal-230 | 228 | 18:30 | 221 | 10:00 | Sreepur | 230 | 06:00 | 222 | 00:00
| GPH | 229 | 18:30 | 217 | 11:00 | Tongi | 227 | 07:00 | 214 | 15:00
| Haripur | 228 | 07:00 | 219 | 00:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 07:00 | 129 | 14:00 | Kushtia | 133 | 07:00 | 127 | 00:00
| Agargaon | 137 | 18:30 | 130 | 00:00 | Lalbag | 135 | 18:30 | 123 | 10:00
| Agrabad | 134 | 18:00 | 124 | 11:00 | Lalmonirhat | 127 | 02:00 | 116 | 19:30
| AKS | 130 | 18:00 | 125 | 11:00 | Madanganj | 135 | 20:00 | 128 | 00:00
| Aminbazar | 138 | 17:00 | 126 | 12:00 | Madaripur | 129 | 18:30 | 122 | 00:00
| Amnura | 136 | 00:00 | 120 | 00:00 | Madartek | 134 | 07:00 | 129 | 00:00
| Ashuganj | 138 | 06:00 | 134 | 00:00 | Madunaghat | 134 | 20:00 | 127 | 11:00
| Bagerhat | 133 | 18:00 | 118 | 23:00 | Magura | 138 | 22:00 | 124 | 13:00
| Bakulia | 135 | 18:00 | 127 | 09:00 | Mahasthangarh | 129 | 06:00 | 121 | 19:30
| Banani | 135 | 07:00 | 128 | 15:00 | Manikganj | 128 | 06:00 | 117 | 16:00
| Bangabhaban | 131 | 07:00 | 126 | 10:00 | Maniknagar | 132 | 08:00 | 126 | 00:00
| Barapukuria | 134 | 10:00 | 125 | 19:30 | Matarbari | 125 | 12:00 | 113 | 23:00
| Barguna | 132 | 18:00 | 125 | 00:00 | Matuail | 134 | 18:00 | 127 | 10:00
| Barishal | 134 | 18:00 | 124 | 04:00 | Millgate | 133 | 07:00 | 123 | 15:00
| Barishal-230 | 134 | 18:00 | 124 | 23:00 | Mirpur | 136 | 18:00 | 129 | 00:00
| Baroaulia | 134 | 18:00 | 128 | 09:00 | Mirzapur | 128 | 06:00 | 116 | 15:00
| Baroirhat | 128 | 18:00 | 121 | 00:00 | Mithapukur | 129 | 02:00 | 118 | 19:30
| Bashundhara | 135 | 07:00 | 123 | 15:00 | MI_Cement | 135 | 18:00 | 128 | 04:00
| BashundharaCement | 135 | 19:30 | 128 | 00:00 | Modern | 133 | 18:00 | 127 | 10:00
| Beanibazar | 128 | 06:00 | 122 | 19:00 | Mogbazar | 136 | 07:00 | 130 | 00:00
| Benapole | 135 | 22:00 | 119 | 15:00 | Mongla | 132 | 18:00 | 118 | 23:00
| Bhaluka | 129 | 13:00 | 123 | 23:00 | Motijheel | 131 | 07:00 | 126 | 10:00
| Bhandaria | 130 | 18:00 | 118 | 00:00 | Munshiganj | 134 | 18:00 | 127 | 09:00
| Bhangura | 134 | 06:00 | 128 | 15:00 | Mymensingh | 135 | 05:00 | 116 | 00:00
| Bheramara | 135 | 07:00 | 129 | 15:00 | Naogaon | 126 | 06:00 | 118 | 15:00
| Bheramara(GK) | 135 | 07:00 | 129 | 15:00 | Narail | 139 | 22:00 | 125 | 00:00
| Bhulta | 125 | 18:00 | 117 | 23:00 | Narinda | 132 | 08:00 | 126 | 00:00
| Bog-Sherpur | 129 | 06:00 | 123 | 14:00 | Narshingdi | 125 | 07:00 | 118 | 23:00
| Bogura | 130 | 06:00 | 125 | 15:00 | Natore | 132 | 07:00 | 125 | 15:00
| Bogura-230 | 131 | 07:00 | 124 | 19:30 | Nawabganj | 135 | 18:30 | 128 | 00:00
| Brahmanbaria | 132 | 08:00 | 121 | 00:00 | Netrakona | 133 | 05:00 | 120 | 03:00
| Cantonment | 136 | 18:30 | 129 | 00:00 | New | 134 | 07:00 | 124 | 15:00
| Chandpur | 125 | 18:00 | 118 | 00:00 | Niamatpur | 135 | 08:00 | 127 | 00:00
| Chandraghona | 133 | 13:00 | 128 | 10:00 | Noapara | 134 | 18:00 | 124 | 15:00
| Chapai | 132 | 08:00 | 124 | 00:00 | Pabna | 133 | 07:00 | 126 | 15:00
| Charsaidpur | 135 | 18:00 | 128 | 00:00 | Palashbari | 126 | 04:00 | 116 | 19:30
| Chauddagram | 130 | 18:30 | 120 | 00:00 | Panchagarh | 132 | 02:00 | 116 | 19:30
| Chhatak | 130 | 10:00 | 124 | 23:00 | Patuakhali | 133 | 18:00 | 126 | 23:00
| Chowmuhani | 124 | 09:00 | 114 | 00:00 | Payra | 134 | 07:00 | 130 | 00:00
| Chuadanga | 137 | 22:00 | 114 | 13:00 | PHP | 126 | 18:00 | 120 | 00:00
| Coxsbazar | 124 | 13:00 | 115 | 11:00 | Postogola | 135 | 18:00 | 129 | 00:00
| Cumilla(N) | 132 | 18:00 | 123 | 12:00 | Purbachal | 136 | 07:00 | 122 | 15:00
| Cumilla(S) | 131 | 05:00 | 124 | 00:00 | Purbasadipur | 126 | 11:00 | 116 | 19:30
| Daudkandi | 131 | 18:00 | 118 | 00:00 | Rahanpur | 138 | 09:00 | 131 | 00:00
| Dhaka | 136 | 07:00 | 129 | 15:00 | Rahim | 134 | 18:00 | 127 | 00:00
| Dhamrai | 134 | 07:00 | 126 | 15:00 | Rajbari | 129 | 18:30 | 122 | 00:00
| Dhanmondi | 135 | 18:30 | 129 | 00:00 | Rajendrapur | 126 | 18:30 | 114 | 09:00
| Dohazari | 132 | 18:00 | 126 | 10:00 | Rajshahi | 134 | 07:00 | 125 | 13:00
| Faridpur | 129 | 18:30 | 123 | 00:00 | Rajshahi-230 | 134 | 07:00 | 113 | 00:00
| Fatullah | 134 | 18:00 | 128 | 00:00 | Ramganj | 123 | 20:00 | 113 | 23:00
| Fenchuganj | 133 | 06:00 | 129 | 23:00 | Rampur | 132 | 06:00 | 126 | 10:00
| Feni | 126 | 18:00 | 120 | 00:00 | Rampura | 135 | 07:00 | 128 | 15:00
| Ghatail | 130 | 06:00 | 113 | 16:00 | Rangamati | 132 | 12:00 | 127 | 09:00
| Ghorashal | 139 | 07:00 | 132 | 09:00 | Rangpur | 127 | 06:00 | 117 | 19:30
| Goalpara | 135 | 18:30 | 124 | 15:00 | Ruppur | 136 | 03:00 | 129 | 15:00
| Gollamari | 136 | 18:00 | 125 | 13:00 | Saidpur | 128 | 04:00 | 118 | 19:30
| Gopalganj | 131 | 18:00 | 123 | 15:00 | Satkhira | 132 | 18:00 | 118 | 23:00
| Gopalganj-400 | 130 | 18:00 | 123 | 00:00 | Satmasjid | 136 | 18:00 | 129 | 00:00
| Gulshan | 135 | 07:00 | 128 | 15:00 | Savar | 136 | 18:00 | 127 | 10:00
| Halishahar | 134 | 18:30 | 125 | 11:00 | SevenRings | 138 | 07:00 | 131 | 15:00
| Haripur | 134 | 18:00 | 127 | 00:00 | ShahCement | 135 | 18:00 | 128 | 00:00
| HaripurSBU | 132 | 19:00 | 127 | 00:00 | Shahjadpur | 136 | 04:00 | 132 | 13:00
| Hasnabad | 136 | 18:00 | 129 | 00:00 | Shahjibazar | 130 | 09:00 | 121 | 00:00
| Hathazari | 135 | 18:00 | 128 | 15:00 | Shahmirpur | 136 | 18:00 | 129 | 08:00
| Ishurdi | 136 | 07:00 | 130 | 15:00 | Shariatpur | 130 | 18:00 | 119 | 23:00
| Jaldhaka | 127 | 03:00 | 115 | 19:30 | Sherpur | 137 | 04:00 | 116 | 08:00
| Jamalpur | 138 | 17:00 | 121 | 08:00 | Shikalbaha | 123 | 18:00 | 117 | 11:00
| Jashore | 136 | 22:00 | 121 | 13:00 | Shikalbaha-230 | 136 | 18:30 | 129 | 10:00
| Jhenaidah | 138 | 22:00 | 126 | 15:00 | Shitalakhya | 135 | 18:30 | 128 | 04:00
| Jhenaidah-230 | 138 | 22:00 | 128 | 00:00 | Sholosohor | 132 | 13:00 | 125 | 11:00
| Joydebpur | 136 | 07:00 | 125 | 15:00 | Shyampur | 134 | 18:00 | 130 | 22:00
| Joypurhat | 125 | 09:00 | 115 | 15:00 | Shyampur-230 | 134 | 18:30 | 127 | 10:00
| Juldah | 135 | 18:00 | 128 | 11:00 | Siddhirganj | 134 | 07:00 | 128 | 05:00
| Kabirpur | 132 | 07:00 | 116 | 08:00 | Sirajganj | 131 | 06:00 | 124 | 15:00
| Kachua | 126 | 18:30 | 119 | 00:00 | Sonargaon | 133 | 21:00 | 125 | 00:00
| Kaliakoir | 137 | 07:00 | 121 | 08:00 | Sreemongol | 131 | 08:00 | 123 | 00:00
| Kallyanpur | 130 | 18:00 | 123 | 00:00 | Sreepur | 134 | 06:00 | 127 | 01:00
| Kalurghat | 133 | 18:00 | 127 | 09:00 | Srinagar | 135 | 18:30 | 127 | 00:00
| Kamrangirchar | 135 | 18:00 | 122 | 00:00 | SSM | 138 | 18:00 | 130 | 08:00
| Kaptai | 130 | 6:00 | 127 | 18:00 | Sunamganj | 133 | 07:00 | 122 | 23:00
| Kazla | 132 | 08:00 | 125 | 16:00 | Sylhet | 131 | 07:00 | 126 | 00:00
| Keranigonj | 136 | 18:30 | 129 | 00:00 | Sylhet-132 | 132 | 07:00 | 127 | 23:00
| Khagrachori | 131 | 18:30 | 126 | 09:00 | Tangail | 130 | 06:00 | 112 | 16:00
| Khulna | 136 | 18:30 | 124 | 13:00 | Thakurgaon | 129 | 02:00 | 116 | 19:30
| Khulna(S) | 137 | 18:30 | 126 | 13:00 | TK | 134 | 19:30 | 127 | 10:00
| Khulshi | 132 | 18:30 | 124 | 11:00 | Tongi | 135 | 07:00 | 125 | 15:00
| Kishoreganj | 134 | 06:00 | 121 | 23:00 | Ullahpara | 133 | 06:00 | 129 | 00:00
| Kodda | 132 | 20:00 | 112 | 08:00 | Ullon | 134 | 18:00 | 128 | 15:00
| KSRM | 133 | 19:00 | 126 | 11:00 | Uttara | 138 | 18:30 | 130 | 00:00
| Kulaura | 132 | 07:00 | 128 | 22:00 | UttaraNew | 136 | 18:30 | 130 | 00:00
| Kurigram | 130 | 02:00 | 116 | 19:30 | Zigatola | 135 | 18:30 | 128 | 00:00

## L-Curve
Date | 2024-06-10
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 484 | 8485 | 6515 | 15000 |  |  |  | QF-LDC-11
0:30 | 519 | 8327 | 6629 | 14956 | Date: | 2024-06-10
1:00 | 554 | 8169 | 6743 | 14912
1:30 | 533 | 8097 | 6591 | 14688
2:00 | 512 | 8025 | 6439 | 14464
2:30 | 525 | 7945.5 | 6248.5 | 14194 | [5 empty] | Gen. at Eve. Peak | 15257 | 15257 MW (21:00 )
3:00 | 538 | 7866 | 6058 | 13924 | [6 empty] | 21:00
3:30 | 599 | 7701.5 | 5951 | 13652.5 | [5 empty] | Gen. at Day Peak | 13193 | 13193 MW (12:00 )
4:00 | 660 | 7537 | 5844 | 13381 | [6 empty] | 12:00
4:30 | 641 | 7411.5 | 5712.5 | 13124 | [5 empty] | Highest Generation | 15257
5:00 | 622 | 7286 | 5581 | 12867 | [6 empty] | 21:00
5:30 | 700 | 7002 | 5341 | 12343
6:00 | 778 | 6718 | 5101 | 11819
6:30 | 586 | 6661 | 4942 | 11603
7:00 | 394 | 6604 | 4783 | 11387
7:30 | 410 | 6492.5 | 4682.5 | 11175
8:00 | 426 | 6381 | 4582 | 10963
8:30 | 500 | 6602.5 | 4669.5 | 11272
9:00 | 574 | 6824 | 4757 | 11581
9:30 | 698 | 7025 | 4921 | 11946
10:00 | 822 | 7226 | 5085 | 12311
10:30 | 779 | 7363.5 | 5075 | 12438.5
11:00 | 736 | 7501 | 5065 | 12566
11:30 | 745 | 7673.5 | 5206 | 12879.5
12:00 | 754 | 7846 | 5347 | 13193
12:30 | 696 | 7827 | 5394.5 | 13221.5
13:00 | 638 | 7808 | 5442 | 13250
13:30 | 647 | 7816 | 5464.5 | 13280.5
14:00 | 656 | 7824 | 5487 | 13311
14:30 | 659 | 7907.5 | 5566.5 | 13474
15:00 | 662 | 7991 | 5646 | 13637
15:30 | 685 | 8036 | 5686 | 13722
16:00 | 708 | 8081 | 5726 | 13807
16:30 | 674 | 8089.5 | 5545 | 13634.5
17:00 | 640 | 8098 | 5364 | 13462
17:30 | 673 | 7994.5 | 5281 | 13275.5
18:00 | 706 | 7891 | 5198 | 13089
18:30 | 691 | 8303.5 | 5454 | 13757.5
19:00 | 676 | 8716 | 5710 | 14426
19:30 | 470 | 8736 | 6257 | 14993
20:00 | 434 | 8539 | 6269 | 14808 |  |  |  | Executive Engineer
20:30 | 471 | 8609.5 | 6423 | 15032.5 |  |  |  | Network Operation Division
21:00 | 508 | 8680 | 6577 | 15257
21:30 | 549 | 8590 | 6470 | 15060
22:00 | 590 | 8500 | 6363 | 14863 |  |  |  |  | Page 6 of 7
22:30 | 545 | 8548.5 | 6427.5 | 14976
23:00 | 500 | 8597 | 6492 | 15089
23:30 | 492 | 8541 | 6503.5 | 15044.5
24:00 | 484 | 8485 | 6515 | 15000
15257 MW (21:00 )
13193 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-10 |  | Energy |  | 328543147
[15 empty] | 2024-06-10 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4083 | 711 | 1947 | 0 | 2112 | 5465 | 115 | 0 | 487 | 80 | 0 | 0 | 238.75
0:30 | 4007 | 746 | 1844 | 0 | 2238.5 | 5445.5 | 115 | 0 | 474 | 83 | 0 | 3 | 328.375 |  |  | Date: | 43991
1:00 | 3931 | 781 | 1741 | 0 | 2365 | 5426 | 115 | 0 | 461 | 86 | 0 | 6 | 418
1:30 | 3930 | 781.5 | 1737.5 | 0 | 2230 | 5365.5 | 115 | 0 | 436 | 85 | 0 | 7.5 | 417 | [9 empty] | Total Energy | 328.5431 | 328.5431 | Total Energy Gen 328.543 MKWHr Energy Not Served 3.299 MKWHr Energy Requirement 331.842 MKWHr
2:00 | 3929 | 782 | 1734 | 0 | 2095 | 5305 | 115 | 0 | 411 | 84 | 0 | 9 | 416 | [9 empty] | Energy not Served | 3.2988 | 3.2988
2:30 | 3941.5 | 853.5 | 1712.5 | 0 | 1866.5 | 5256 | 115 | 0 | 360 | 84 | 0 | 5 | 387.5 | [9 empty] | Energy Requirement | 331.842 | 331.842
3:00 | 3954 | 925 | 1691 | 0 | 1638 | 5207 | 115 | 0 | 309 | 84 | 0 | 1 | 359
3:30 | 3940.5 | 924 | 1694 | 0 | 1480.5 | 5152 | 114 | 0 | 261 | 83 | 0 | 3.5 | 355.5 | [8 empty] | Shortage
4:00 | 3927 | 923 | 1697 | 0 | 1323 | 5097 | 113 | 0 | 213 | 82 | 0 | 6 | 352
4:30 | 3849 | 923.5 | 1680.5 | 0 | 1244 | 5018.5 | 112 | 0 | 213 | 79 | 0 | 4.5 | 287.5
5:00 | 3771 | 924 | 1664 | 0 | 1165 | 4940 | 111 | 0 | 213 | 76 | 0 | 3 | 223
5:30 | 3733 | 924 | 1542 | 0 | 1036.5 | 4760 | 111 | 0 | 159.5 | 67 | 6.5 | 3.5 | 198
6:00 | 3695 | 924 | 1420 | 0 | 908 | 4580 | 111 | 0 | 106 | 58 | 13 | 4 | 173
6:30 | 3688 | 924.5 | 1404 | 0 | 875 | 4412 | 111.5 | 0 | 90 | 64 | 31 | 3 | 86.5 | [7 empty] | Coal
7:00 | 3681 | 925 | 1388 | 0 | 842 | 4244 | 112 | 0 | 74 | 70 | 49 | 2 | 0
7:30 | 3699 | 925 | 1429 | 0 | 763 | 4024.5 | 113 | 0 | 66 | 74 | 80.5 | 1 | 0 | [6 empty] | Oil
8:00 | 3717 | 925 | 1470 | 0 | 684 | 3805 | 114 | 0 | 58 | 78 | 112 | 0 | 0
8:30 | 3818.5 | 924.5 | 1569.5 | 0 | 717.5 | 3858 | 114 | 0 | 66 | 68 | 136 | 0 | 0
9:00 | 3920 | 924 | 1669 | 0 | 751 | 3911 | 114 | 0 | 74 | 58 | 160 | 0 | 0
9:30 | 3949 | 924.5 | 1727 | 0 | 813.5 | 4069.5 | 114.5 | 0 | 74 | 62 | 211.5 | 0.5 | 0
10:00 | 3978 | 925 | 1785 | 0 | 876 | 4228 | 115 | 0 | 74 | 66 | 263 | 1 | 0
10:30 | 3907.5 | 925.5 | 1732 | 0 | 1016 | 4271.5 | 115 | 0 | 132 | 69 | 269.5 | 0.5 | 26
11:00 | 3837 | 926 | 1679 | 0 | 1156 | 4315 | 115 | 0 | 190 | 72 | 276 | 0 | 52
11:30 | 3924 | 926 | 1733.5 | 0 | 1247.5 | 4326 | 115 | 0 | 207 | 73 | 325.5 | 2 | 53
12:00 | 4011 | 926 | 1788 | 0 | 1339 | 4337 | 115 | 0 | 224 | 74 | 375 | 4 | 54
12:30 | 3946 | 926 | 1755.5 | 0 | 1409 | 4404 | 115 | 0 | 225 | 76 | 361 | 4 | 27
13:00 | 3881 | 926 | 1723 | 0 | 1479 | 4471 | 115 | 0 | 226 | 78 | 347 | 4 | 0
13:30 | 3881 | 926 | 1723 | 0 | 1479 | 4471 | 115 | 0 | 226 | 78 | 347 | 4 | 0
14:00 | 3881 | 926 | 1723 | 0 | 1479 | 4471 | 115 | 0 | 226 | 78 | 347 | 4 | 0
14:30 | 3961 | 925.5 | 1720 | 0 | 1509 | 4623 | 113.5 | 0 | 226.5 | 78 | 282.5 | 4.5 | 27.5
15:00 | 4041 | 925 | 1717 | 0 | 1539 | 4775 | 112 | 0 | 227 | 78 | 218 | 5 | 55
15:30 | 3989 | 924.5 | 1756.5 | 0 | 1641.5 | 4789.5 | 112.5 | 0 | 224 | 78 | 204 | 2.5 | 55
16:00 | 3937 | 924 | 1796 | 0 | 1744 | 4804 | 113 | 0 | 221 | 78 | 190 | 0 | 55
16:30 | 3905 | 924.5 | 1730.5 | 0 | 1820.5 | 4682 | 112.5 | 0 | 232.5 | 78 | 148.5 | 0.5 | 50.42
17:00 | 3873 | 925 | 1665 | 0 | 1897 | 4560 | 112 | 0 | 244 | 78 | 107 | 1 | 45.84
17:30 | 3772.5 | 925.5 | 1608.5 | 0 | 1961 | 4477 | 112.5 | 0 | 276.5 | 70 | 71.5 | 0.5 | 48.705
18:00 | 3672 | 926 | 1552 | 0 | 2025 | 4394 | 113 | 0 | 309 | 62 | 36 | 0 | 51.57
18:30 | 3943 | 925.5 | 1571.5 | 0 | 2180 | 4480 | 113 | 0 | 450.5 | 74 | 18 | 2 | 25.785
19:00 | 4214 | 925 | 1591 | 0 | 2335 | 4566 | 113 | 0 | 592 | 86 | 0 | 4 | 0
19:30 | 4032 | 896 | 1695 | 0 | 2529 | 4972 | 114 | 0 | 667 | 76 | 0 | 12 | 115.5
20:00 | 3954 | 782 | 1620 | 0 | 2518 | 5074 | 115 | 0 | 659 | 78 | 0 | 8 | 231
20:30 | 4018 | 781.5 | 1760 | 0 | 2477.5 | 5182.5 | 115 | 0 | 608.5 | 80 | 0 | 9.5 | 207.5
21:00 | 4082 | 781 | 1900 | 0 | 2437 | 5291 | 115 | 0 | 558 | 82 | 0 | 11 | 184
21:30 | 4075 | 777.5 | 1888 | 0 | 2319.5 | 5237 | 115 | 0 | 556.5 | 82 | 0 | 9.5 | 195.6175
22:00 | 4068 | 774 | 1876 | 0 | 2202 | 5183 | 115 | 0 | 555 | 82 | 0 | 8 | 207.235
22:30 | 4122.5 | 777.5 | 1891 | 0 | 2167 | 5261.5 | 115 | 0 | 555 | 81 | 0 | 5.5 | 204.37
23:00 | 4177 | 781 | 1906 | 0 | 2132 | 5340 | 115 | 0 | 555 | 80 | 0 | 3 | 201.505
23:30 | 4130 | 746 | 1926.5 | 0 | 2122 | 5402.5 | 115 | 0 | 521 | 80 | 0 | 1.5 | 220.1275 |  |  | Max Temp. in Dhaka |  | 30.5°C
24:00 | 4083 | 711 | 1947 | 0 | 2112 | 5465 | 115 | 0 | 487 | 80 | 0 | 0 | 238.75
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 328.543 MKWHr Energy Not Served 3.299 MKWHr Energy Requirement 331.842 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-10
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1824000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 38 | 36 | 36 | 37 | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 37 | 38 | 37 | 38 |  | 38 | 39 | 40 | 40 | 40 | 40 | 40 | 940000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 2 | 8 |  | 13 | 17 | 17 | 17 | 17 | 9 | 8 | 91715
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 |  | 8 | 10 | 11 | 9 | 15 |  |  |  | 8 | 4 | 0 | [8 empty] | 58455
6 | Sikalbaha 225MW CCPP (Gas) | 222 | 221 | 222 | 222 | 222 | 222 | 222 | 216 | 217 | 216 | 216 | 216 | 225 | 224 | 221 | 221 | 222 | 222 |  | 221 | 223 | 224 | 224 | 223 | 221 | 224 | 5233687
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 48 | 51 |  | 85 | 85 | 85 | 85 | 85 | 85 | 79 | 1203546
12 | Hathazari 100 MW peaking PP | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 25 | 32 | 32 | 32 | 32 | 32 | 56 |  | 64 | 56 | 56 | 57 | 64 | 66 | 64 | 872784
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 44 | 85 | 85 |  | 76 | 85 | 85 | 68 | 51 | 17 | 17 | 818800
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 30 | 32 | 32 | [6 empty] | 6 | 24 | 27 | 29 | 23 | 32 | 36 |  | 36 | 36 | 36 | 27 | 27 | 28 | 29 | 520480
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 307 | 308 | 313 | 316 | 280 | 280 | 280 | 260 | 329 | 331 | 300 | 330 | 328 | 280 | 280 | 324 | 300 | 240 |  | 280 | 280 | 280 | 325 | 280 | 320 | 320 | 7253576
18 | Kodda 300 MW PP Unit-2 (Summit) | 273 | 110 | [8 empty] | 10 | 45 | 30 | 30 | 30 | 65 | 125 | 125 |  | 150 | 150 | 168 | 195 | 145 | 145 | 145 | 1999745
19 | Ashuganj 195 MW PP (APSCL-United) | [14 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 66909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4243050
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 790 | 787 | 790 | 790 | 775 | 751 | 751 | 697 | 660 | 743 | 850 | 905 | 940 | 980 | 1020 | 1062 | 1050 | 1000 |  | 950 | 950 | 965 | 1011 | 1010 | 1028 | 1029 | 21332725
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 7 | 20 | 36 | 35 | 33 | 36 | 36 | 36 | 36 |  | 36 | 36 | 37 | 36 | 36 | 36 | 37 | 630144
33 | Ashuganj 225 MW CCPP | 204 | 204 | 208 | 209 | 218 | 218 | 220 | 215 | 219 | 220 | 219 | 219 | 219 | 217 | 213 | 217 | 214 | 216 |  | 214 | 218 | 220 | 218 | 215 | 185 | 171 | 5182000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 315 | 260 | 260 | 310 | 270 | 270 | 270 |  | 335 | 290 | 270 | 270 | 290 | 270 | 270 | 6487000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 325 | 285 | 280 | 280 |  | 340 | 285 | 280 | 280 | 295 | 320 | 280 | 7375200
| Ashuganj 420 MW CCPP(East) | 240 | 240 | 240 | 240 | 230 | 230 | 230 | 230 | 280 | 300 | 260 | 230 | 230 | 285 | 320 | 285 | 285 | 230 |  | 365 | 320 | 290 | 285 | 295 | 270 | 240 | 6504800
35 | Ashuganj 55 MW PP (Precision) | [14 empty] | 1 | 8 | 16 | 24 |  | 25 | 33 | 33 | 36 | 42 | 45 | 49 | 279360
36 | Chandpur 150 MW CCPP | 85 | 85 | 85 | 85 | 90 | 90 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 86 | 86 | 85 | 1927270
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 401 | 401 | 401 | 373 | 370 | 358 | 343 | 335 | 362 | 403 | 404 | 404 | 405 | 400 | 370 | 394 | 406 | 320 |  | 322 | 370 | 367 | 374 | 380 | 382 | 403 | 9219600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 380 | 320 | 320 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 350 |  | 360 | 420 | 420 | 450 | 450 | 450 | 450 | 10148500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 34 | 34 | 34 | 34 | 35 | 0 | 5 | 18 | 18 | 21 | 21 | 29 | 29 | 32 | 32 | 46 | 46 | 56 |  | 90 | 80 | 80 | 70 | 71 | 71 | 83 | 868800
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 4 | 17 | 17 | 20 | 13 | 19 | 24 | 23 | 18 | 11 | 3 |  | 0 | [6 empty] | 168310
44 | Fenchugonj CCPP Phase-1 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 839000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1381920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 55 | 55 | 62 | 62 | 61 | 61 | 40 | 61 | 62 | 61 | 61 | 61 | 61 | 58 | 61 | 61 | 40 |  | 58 | 60 | 60 | 59 | 54 | 53 | 50 | 1368672
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 210 | 210 | 210 | 210 | 208 | 208 | 208 | 208 | 208 | 208 | 207 | 207 | 207 | 204 | 203 | 203 | 204 |  | 204 | 204 | 206 | 206 | 207 | 207 | 208 | 5177000
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 111312
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 50 | 50 | 50 | 11 | 11 |  | 22 | 50 | 50 | 53 | 53 | 50 | 50 | 49 | 49 | 52 |  | 53 | 53 | 53 | 53 | 53 | 25 | 50 | 1063800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 336528
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 285 | 285 | 290 | 270 | 290 | 290 | 315 | 310 | 285 | 300 | 295 | 285 | 315 | 300 | 290 | 285 |  | 280 | 275 | 280 | 300 | 290 | 310 | 320 | 7171500
| Bibiyana South 400 MW | 340 | 340 | 340 | 340 | 320 | 310 | 310 | 340 | 365 | 345 | 345 | 396 | 330 | 345 | 345 | 335 | 320 | 310 |  | 375 | 340 | 340 | 340 | 340 | 375 | 340 | 8196100
58 | Nababganj 55 MW PP (Southern power ) |  |  | 35 | 35 | 35 | [7 empty] | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 665473
59 | Tangail Palli Power Gen 22 MW |  |  |  | 2 | 4 | 1 | 5 |  |  |  | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 14 |  | 24 | 24 | 24 | 24 | 24 | 12 | 12 | 197760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 86 | 84 | 84 | 82 | 76 | 58 | 70 | 78 | 58 | 66 | 72 | 74 | 78 | 76 | 78 | 78 | 78 | 62 |  | 86 | 76 | 78 | 82 | 82 | 80 | 80 | 1842240
64 | Malancha, Ctg. EPZ (United) | 35 | 37 | 37 | 37 | 40 | 38 | 38 | 7 | 2 | 2 | 2 | 2 | 6 | 6 | 4 | 4 | 11 | 5 |  | 11 | 14 | 10 | 25 | 34 | 36 | 36 | 474720
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 746800
68 | Cumilla 25 MW PP (Summit) | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 79900
69 | Summit Ashulia | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 20 | 381000
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 522000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 16 |  |  | 15 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 18 | 0 | 0 | 33 | 33 | 33 | 33 | 641520
72 | Rupganj 33 MW PP(Summit) | 22 | 22 | 22 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 25 | 25 | 25 | 31 | 25 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 679300
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 52 | 52 | 75 | 70 | 98 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2335860
| Chowmuhani 113 MW | 45 | 45 | 38 | 37 | 37 | 38 | 37 | 37 | 36 | 37 | 41 | 40 | 38 | 39 | 38 | 38 | 47 | 64 |  | 83 | 85 | 87 | 86 | 86 | 87 | 86 | 1260840
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 54 | [7 empty] | 35 | 60 | 72 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 858240
77 | Siddhirganj 100 PP(Dutch Bangla) | 56 | 50 | 50 | 45 | 9 |  |  |  |  | 5 | 40 | 55 | 63 | 64 | 70 | 70 | 70 | 70 |  | 72 | 72 | 72 | 39 | 33 | 33 | 50 | 966720
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 189120
79 | Kodda 150 MW PP | 98 | 98 | 98 | 48 | 48 | 48 | 16 |  | 16 | 16 | 98 | 98 | 82 | 115 | 115 | 115 | 115 | 115 |  | 133 | 133 | 133 | 149 | 149 | 149 | 98 | 2181600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 42 | 42 | 41 | 41 | 33 | 33 | 34 | 34 | 34 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 25 |  | 47 | 51 | 51 | 51 | 51 | 51 | 51 | 809194
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 857280
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 4 | 5 | 4 |  | 2 | 2 | 2 | 1 | 1 | [9 empty] | 23281
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | [13 empty] | 11 | 17 | 17 | 17 |  |  |  | 295822
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 96 | 96 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 78 | 93 | 97 |  | 107 | 110 | 110 | 110 | 110 | 110 | 110 | 2169525
82 | Madanganj 102 PP(Summit) | [9 empty] | 3 | 36 | 50 | 50 | 45 | 51 | 51 | 51 | 51 |  | 51 | 64 | 55 | 36 | 34 | 34 | 43 | 780238
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 12 | 13 | [5 empty] | 14241
86 | Meghnaghat CCPP ( Summit) | 150 | 145 | 145 | 144 | 143 | 141 | 150 | 148 | 155 | 157 | 156 | 151 | 150 | 143 | 152 | 144 | 152 | 150 |  | 153 | 148 | 122 | 130 | 152 | 150 | 152 | 3528785
87 | Meghnaghat 100 MW(IEL) | 42 | 49 | 50 | 40 | 8 | [5 empty] | 3 | 30 | 48 | 50 | 49 | 51 | 66 | 81 |  | 81 | 81 | 80 | 51 | 48 | 49 | 62 | 936960
| Meghnaghat 104 MW PP (OPCL) | 60 | 50 | 50 | 50 | 52 | 35 | 35 | 35 | 35 | 40 | 53 | 53 | 53 | 35 | 35 | 35 | 53 | 72 |  | 72 | 72 | 72 | 72 | 70 | 70 | 70 | 1240320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 70 | 70 | 70 | 70 | 70 | 70 | 36 |  |  | 12 | 36 | 36 | 36 | 46 | 46 | 58 | 58 | 58 |  | 58 | 58 | 58 | 68 | 68 | 68 | 68 | 1151640
92 | Fenchuganj 44 MW (Energyprima) | 37 | 40 | 33 | 40 | 40 | 10 | 10 |  | 5 | 37 | 37 | 40 | 40 | 39 | 36 | 39 | 39 | 39 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 821304
93 | Ashuganj 51 MW PP (Midland) | 43 | 51 | 51 | 51 | 51 | 10 | 10 |  |  | 28 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 988420
94 | Gagnagar 102 MW PP (Digital Power) | 81 | 81 | 81 | 8 | 8 |  | 8 | 16 | 16 | 44 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 48 | 48 | 48 | 82 | 1388160
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  |  |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 6 | 199680
96 | Chattogram 108 MW PP (ECPV) | 25 | 25 | 24 | 25 | 25 | 24 | 25 | 24 | 25 | 29 | 31 | 31 | 31 | 30 | 32 | 36 | 38 | 37 |  | 38 | 38 | 39 | 38 | 38 | 38 | 38 | 761280
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1337224
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 664458
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 120 | 163 | 120 | 120 | 120 | 163 | 120 | 120 |  | 120 | 163 | 163 | 163 | 120 | 163 | 163 | 3471955
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 0 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 8550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | [7 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 25 |  | 45 | 54 | 54 | 54 |  |  |  | 488880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 93 | 93 | 93 | 93 | 45 |  |  |  | 24 | 24 | 36 | 93 | 93 | 93 | 93 | 92 | 84 | 100 |  | 121 | 121 | 121 | 121 | 120 | 120 | 125 | 1912800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 97 | 97 | 97 | 97 | 97 | 83 | 77 | 46 | 46 | 97 | 97 | 97 | 97 | 97 | 97 | 89 | 93 | 94 |  | 79 | 79 | 79 | 92 | 97 | 97 | 97 | 2159280
115 | Juldah 100 MW PP Unit-3 (Acorn) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 560640
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432960
117 | Ashuganj 150 MW PP (Midland) | 11 | 13 | 13 | 13 | 11 |  |  |  |  | 2 | 12 | 16 | 41 | 50 | 52 | 52 | 56 | 57 |  | 56 | 57 | 10 | 10 | 10 | 10 | 20 | 607200
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 367 | 349 | 317 | 317 | 317 | 400 | 388 | 366 | 344 | 365 | 365 | 366 | 403 | 340 | 304 | 305 |  | 400 | 366 | 343 | 365 | 366 | 405 | 402 | 8622000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 58 |  |  |  | 28 | 67 | 88 | 59 | 59 | 59 | 59 | 59 | 59 | 69 |  | 78 | 78 | 79 | 79 | 78 | 79 | 79 | 1369200
| Anwara 300 MW PP (United) | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 1252036
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 590400
| Anlima Energy Ltd. | 53 | 53 | 37 | 21 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 35 | 35 |  | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 782836
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 0 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 30 | 54 | 52 | 52 | 52 | 52 | 36 | 685080
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 2 | 5 | 6 | 18 | 25 | 27 | 22 | 13 | 9 | 5 | 1 | [8 empty] | 136667
| Chandpur 115(Doreen) | 76 | 115 | 109 | 106 | 107 | 108 | 104 | 103 | 75 | 49 | 49 | 49 | 49 | 49 | 49 | 62 | 69 | 70 |  | 71 | 104 | 102 | 115 | 104 | 78 | 68 | 1948800
| Kanchan Purbachal Power Generation Ltd. | [24 empty] | 25 | 35 | 61920
| Mirsharai 150 MW (Oil) | 17 | 17 | 14 | [7 empty] | 35 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 72 | 72 | 35 | 17 | 17 | 17 | 17 | 501818
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 6 | 9 | 1 | 6 | 3 | 4 | 2 | 0 | 0 | 1 | 0 | 4 | 4 | 6 | 5 | 0 | 1 | 0 |  | 4 | 12 | 8 | 11 | 8 | 3 | 0 | 86880
| Sonagazi 75 MW Solar Plant | [5 empty] | 5 | 17 | 35 | 34 | 53 | 7 | 18 | 7 | 13 | 26 | 23 | 14 | 3 | [8 empty] | 267218
| Matarbari 2*600 MW (CPGCL) | 566 | 565 | 566 | 566 | 566 | 565 | 565 | 568 | 565 | 566 | 554 | 402 | 402 | 361 | 275 | 273 | 275 | 275 |  | 275 | 274 | 270 | 275 | 274 | 335 | 344 | 10392727
120 | Eastern Zone Total | 8169 | 8025 | 7866 | 7537 | 7286 | 6718 | 6604 | 6381 | 6824 | 7226 | 7501 | 7846 | 7808 | 7824 | 7991 | 8081 | 8098 | 7891 |  | 8716 | 8736 | 8539 | 8680 | 8500 | 8597 | 8485 | 189227040
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 78 | 78 | 47 | 16 | [11 empty] | 16 | 15 | 16 |  | 16 | 26 | 48 | 15 |  |  |  | 368640
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 26 | 26 | 26 | 26 | 26 | [12 empty] | 4 |  | 38 | 42 | 47 | 42 | 41 | 41 | 31 | 354240
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 73 | 73 | 73 | 53 | 53 | 17 | [5 empty] | 17 | 17 | 53 | 54 | 72 | 72 | 72 |  | 73 | 73 | 73 | 73 | 35 | 35 | 35 | 1049760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 6 | 21 | 43 | 66 | 81 | 89 | 82 | 73 | 63 | 66 | 38 | 24 | 6 | [8 empty] | 684720
131 | Rampal 1320 MW (BIFPCL) | 914 | 911 | 902 | 901 | 881 | 828 | 754 | 712 | 715 | 717 | 713 | 711 | 715 | 718 | 763 | 731 | 718 | 713 |  | 850 | 903 | 915 | 955 | 967 | 975 | 994 | 19941815
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 |  | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 5139245
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 16 | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | [8 empty] | 242976
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 307 | 307 | 307 | 307 | 273 | 200 | 150 | 140 | 140 | 140 | 140 | 140 | 140 | 200 | 250 | 250 | 200 | 150 |  | 183 | 240 | 289 | 307 | 250 | 298 | 307 | 5432700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 126 | 126 | 126 | 62 | 63 | 63 | 63 | 61 | 63 | 63 | 80 |  | 126 | 130 | 126 | 126 | 80 | 126 | 126 | 2267000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 9 | 10 | 10 | 9 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 228383
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | [10 empty] | 24 | 24 | 24 | 24 | 24 | 24 |  | 8 | 24 | 24 | 24 |  |  |  | 267375
143 | Gopalganj 100 MW Peaking PP | 49 | 49 | 49 | 49 | 49 | [12 empty] | 20 |  | 50 | 56 | 56 | 51 | 51 | 51 | 51 | 548608
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 781 | 782 | 925 | 923 | 924 | 924 | 925 | 925 | 924 | 925 | 926 | 926 | 926 | 925 | 925 | 924 | 925 | 926 |  | 925 | 896 | 782 | 781 | 774 | 781 | 711 | 21350545
147 | Bheramara 410 MW CCPP | 210 | 210 | 225 | 225 | 225 | 230 | 245 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 235 | 240 | 240 | 230 | 5341536
148 | Payra 1320 MW | 1110 | 1090 | 1080 | 990 | 940 | 840 | 700 | 500 | 620 | 640 | 640 | 660 | 770 | 770 | 860 | 900 | 800 | 740 |  | 700 | 900 | 940 | 1100 | 1100 | 1110 | 1110 | 22912000
149
150 | Barapukuria TPP Unit-1 | 64 | 64 | 64 | 63 | 65 | 64 | 65 | 65 | 65 | 65 | 65 | 63 | 62 | 62 | 63 | 62 | 62 | 63 |  | 62 | 62 | 63 | 60 | 60 | 61 | 63 | 1455272
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 220 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 220 | 220 | 220 | 210 | 210 | 210 | 5488000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 30 | [9 empty] | 7 | [7 empty] | 11 | 32 | 36 |  |  |  |  | 118813
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 2 | 2 | 1 | 3 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 19980
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 160 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 145 | 171 | 170 | 172 | 3771273
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 290 | 290 | 290 | 290 | 290 | 250 | 250 | 396 | 359 | 360 | 300 | 350 | 330 | 270 | 300 | 350 | 300 | 280 |  | 300 | 300 | 250 | 414 | 414 | 414 | 414 | 7853455
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 10 | 10 | 10 | 10 |  |  |  | 34553
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 108720
165 | Amnura 50 MW PP(Sinha) | 35 | [25 empty] | 46540
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 33 | 33 | [17 empty] | 18 | 22 | 45 | 45 | 45 | 42 | 42 | 258400
168 | Santahar 50 MW Peaking PP | 22 | 22 | [17 empty] | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 248382
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 48 | [18 empty] | 40 | 88 | 85 | 40 | 40 | 40 | 40 | 320224
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | [17 empty] | 12 | 35 | 35 | 50 | 50 | 50 | 50 | 534816
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 70 | [17 empty] | 35 | 35 | 45 | 50 | 50 | 50 | 50 | 525120
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 99 | 82 | [10 empty] | 3 | 3 | 5 | 34 | 34 | 34 |  | 47 | 76 | 104 | 107 | 108 | 110 | 106 | 881798
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 3 | 5 | 3 | 4 | 4 | 4 | 2 | 2 | 1 | [8 empty] | 28906
178 | Energypac Power Venture Thakurgaon Ltd. | 94 | 94 | 35 | [6 empty] | 11 | 77 | 78 | 70 | 54 | 53 | 53 | 35 | 35 |  | 90 | 94 | 94 | 94 | 94 | 94 | 94 | 1374528
| Intraco Solar 30 MW | [5 empty] | 0 | 2 | 5 | 8 | 15 | 15 | 29 | 22 | 15 | 13 | 7 | 6 | 3 |  | 0 | [6 empty] | 136693
| Adani Power Jharkhanda Ltd | 1455 | 1361 | 1278 | 1260 | 1220 | 1112 | 1029 | 893 | 916 | 1127 | 1123 | 1226 | 1212 | 1268 | 1314 | 1296 | 1225 | 1223 |  | 1316 | 1423 | 1412 | 1363 | 1312 | 1323 | 1408 | 29029091
178 | Teesta Solar Limited | [6 empty] | 3 | 12 | 13 | 70 | 105 | 188 | 189 | 153 | 68 | 82 | 39 | 19 | [8 empty] | 952000