## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:April 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-04-01 |  | 2024-03-01 |  | 2023-04-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16477 | 2024-04-30 | 13898 | 2024-03-31 | 15648 | 2023-04-19 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 8472 | 2024-04-11 | 7249 | 2024-03-22 | 5602 | 2023-04-01 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16477 | 2024-04-30 | 13898 | 2024-03-31 | 15648 | 2023-04-19 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 14301 | 2024-04-30 | 11821 | 2024-03-27 | 13415 | 2023-04-19 | 14301 | 2024-04-30
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 17200 | 2024-04-29 | 14050 | 2024-03-30 | 16221 | 2023-04-30 | 17200 | 2024-04-29
|  |  | 21:00 |  | 21:00 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14226.8667 |  | 11984.9032 |  | 12833.0667 |  | - | -
7 | Average Generation (MW) at Day Peak | 12460.6333 |  | 10819.7097 |  | 11504.2 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 938 | 2024-04-14 | 964 | 2024-03-28 | 936 | 2023-04-24 | 964 | 2024-03-28
|  |  | 12:30 |  | 13:30 |  | 11:30 |  | 13:30
9 | Maximum Power Import from Tripura, India (MW) | 164 | 2024-04-04 | 165 | 2024-03-31 | 165 | 2023-04-04 | 194 | 12/06/19
|  |  | 9:30 |  | 21:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1533 | 2024-04-29 | 666 | 2024-03-30 | 1291 | 2023-04-16 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 15595 | 2024-04-29 | 13353 | 2024-03-30 | 14599 | 45032 | 13200 | 04/10/2022
|  | - | 21:00 | - | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-04-12 | 0 | 2024-03-26 | 0 | 45017 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11762 | 2024-04-12 | 12107 | 2024-03-26 | 10593 | 2023-04-01 | - | -
|  |  | 21:00 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 2640 | 2024-04-29 | 513 | 2024-03-14 | 1167 | 45031 | - | -
|  |  | 12:00 |  | 12:00 |  | 21:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 13036 | 2024-04-29 | 11763 | 2024-03-14 | 12715 | 45031 | - | -
|  |  | 12:00 |  | 12:00 |  | 21:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-04-12 | 0 | 2024-03-26 | 0 | 45017 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 9637 | 2024-04-12 | 9801 | 2024-03-26 | 9272 | 45017 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 26 |  | 23 |  | 21 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 25 |  | 23 |  | 15 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 2294.259 |  | 2159.2989 |  | 1652.1779 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 206.7694 |  | 33.0767 |  | 47.9101 |  | - | -
22 | Net Generation of BPDB (MKWH) | 2087.4896 |  | 2126.2221 |  | 1604.2678 |  | - | -
23 | Net Generation of IPP (MKWH) | 5224.0519 |  | 4044.7402 |  | 4861.0541 |  | - | -
24 | Net Generation of REB (MKWH) | 104.2242 |  | 99.727 |  | 114.4874 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 150.1603 |  | 104.0822 |  | 397.804 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7565.926 |  | 6374.7716 |  | 6977.6134 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4739.6465 |  | 3706.1266 |  | 4284.183 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 30.5077 |  | 23.3688 |  | 117.8792 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 990.3125 |  | 599.397 |  | 1634.0628 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 23.0087 |  | 23.5131 |  | 9.4966 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 58.4751 |  | 57.0855 |  | 47.6176 |  | 57.09 | March-24
31 | Energy Generation by Coal (MKWH) | 1047.9615 |  | 932.5694 |  | 932.2843 |  | 1047.9615 | April'24
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 676.6991 |  | 724.0301 |  | 678.729 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 73.8657 |  | 73.5217 |  | 74.4409 |  | 92.62 | August-22

## QF-LDC-22
QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:April 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16477 | 2024-04-30 | 21:00
Generation Period
| Dhaka | MW | 5673.68
| Chattogram | MW | 1447.7
| Cumilla | MW | 1551.5
| Mymensingh | MW | 1208
| Sylhet | MW | 360
a) | Total supply in East zone | MW | 10240.88
| Khulna | MW | 1966.7
| Barisal | MW | 511.8
| Rajshahi | MW | 1872.2
| Rangpur | MW | 991
b) | Total supply in West zone | MW | 5341.7
c) | Total supply in both zone ( a+b) | MW | 15582.58
Ref: | 27.21.0000.603.16.087.20.805 | Date: 19/05/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 640 | 2024-04-15 | 23:00
| b) Ishurdi end | MW | 240 | 2024-04-28 | 15:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1000 | 2024-04-06 | 12:00
| b) Ishurdi end | MW | 180 | 2024-04-12 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 11.4351
| b) Ishurdi end | MKWH | 46.3697
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 44.9786
| b) Ishurdi end | MKWH | 11.1021
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 |  |  |  |  | 2.955
| a) Ashuganj end | MW | 360 | 2024-04-12 | 21:00
| b)Serajganj end | MW | 570 | 2024-04-28 | 18:30
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 210 | 2024-04-27 | 14:00
| b)Sirajganj end | MW | 150 | 2024-04-16 | 18:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.8141
| b)Sirajganj end | MKWH | 184.65
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 179.509
| b)Sirajganj end | MKWH | 1.848
30 | Transmission loss of EWI /NO-2 | % | 2.739'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2058 | 2024-04-02 | 14:00
|  | MW | 1302
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2035 | 2024-04-02 | 14:00
|  | MW | 1290
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 26350 | 2024-04-02 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 26250 | 2024-04-02
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 354883.074
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 345788.365
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 2.5627
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan HT | 2024-04-12 12:05 | 2024-04-14 13:57 | 49:52 | E/O | kolabagan-3(33KV) CT burst | 12 | 598.4 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-04-07 11:25 | 2024-04-07 11:57 | 0:32 | E/O | Temperature high | 0 | 0 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-04-07 11:23 | 2024-04-07 11:57 | 0:34 | E/O | Temperature high | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-04-16 11:25 | 2024-04-16 12:44 | 1:19 | E/O | T-2 33 kv bushing clamp high temperature | 0 | 0 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-04-27 10:57 | 2024-04-27 12:10 | 1:13 | E/O | Shutdown taken by DPBS-1 due to 33 kV Nayerhat feeder bus DS to 33kV bus B-phase loop changing work. | 70 | 85.1667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-04-27 10:58 | 2024-04-27 12:09 | 1:11 | E/O | Shutdown taken by DPBS-1 due to 33 kV Nayerhat feeder bus DS to 33kV bus B-phase loop changing work. | 40 | 47.3333 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-04-19 21:12 | 2024-04-20 12:22 | 15:10 | T | CT of 33kV was damage | 110 | 84.3333 | Power interruption 21:12 to 21:58
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-04-02 20:02 | 2024-04-02 20:10 | 0:08 | T | E/F | 40 | 5.3333 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-04-14 04:10 | 2024-04-14 04:29 | 0:19 | T | 33 kv pakundina feeder tigal our T-2 transfomer 33 kv incoming trip | 70 | 22.1667 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2024-04-19 21:12 | 2024-04-19 22:12 | 1:00 | T | CT damage of Tr-2 when both transformer (Tr-2 & Tr-3) both were operating parallel. | 70 | 70 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2024-04-22 11:03 | 2024-04-22 11:28 | 0:25 | E/O | 33kV Katiadi feeder's Bus side DS red hot maintenance by KPBS. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2024-04-17 18:06 | 2024-04-17 18:55 | 0:49 | T | 33KV L10 (Yearpur 1) Feeder fault. | 38 | 31.0333 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2024-04-17 18:06 | 2024-04-17 19:00 | 0:54 | T | 33KV L10 (Yearpur 1) Feeder fault. | 42 | 37.8 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2024-04-17 18:06 | 2024-04-17 19:01 | 0:55 | T | 33KV L10 (Yearpur 1) Feeder fault | 38 | 34.8333 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2024-04-17 18:06 | 2024-04-17 19:02 | 0:56 | T | 33KV L10 (Yearpur 1) Feeder fault | 42 | 39.2 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-04-17 18:06 | 2024-04-17 19:14 | 1:08 | T | 33KV L10 (Yearpur 1) Feeder fault | 38 | 43.0667 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-04-01 13:31 | 2024-04-01 13:40 | 0:09 | T | Mirzapur 132kv GIS Grid: 33 kV incomer-01 & 2 trip . Trip reason for PBS two feeder (Kurni + Kumarzani) trip at a time. | 25 | 3.75 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-04-01 13:31 | 2024-04-01 13:40 | 0:09 | T | PBS feeder trip. | 25 | 3.75 | Power interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-04-09 13:00 | 2024-04-09 13:50 | 0:50 | E/O | Bird nest remove | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-04-09 10:42 | 2024-04-09 14:01 | 3:19 | E/O | Bird nest remove | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132 kV BUS-2 | 2024-04-09 15:43 | 2024-04-25 09:27 | 377:44 | E/O | Bird nest removal | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2024-04-11 01:16 | 2024-04-11 01:16 | 0:00 | T |  | 0 | 0 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-04-29 08:49 | 2024-04-29 09:16 | 0:27 | T | DF/DT | 65 | 29.25 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 HT | 2024-04-28 13:19 | 2024-04-28 13:30 | 0:11 | T | Wrong work (temperature setting for fan) by Project | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-04-02 08:28 | 2024-04-02 09:53 | 1:25 | T | New Reb feeder faulth | 45 | 63.75 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-04-02 10:21 | 2024-04-02 11:08 | 0:47 | E/O | T-2 Transformer DS Maintenance | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2024-04-02 08:28 | 2024-04-02 09:06 | 0:38 | T | New Reb feeder faulth | 45 | 28.5 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 LT | 2024-04-17 10:23 | 2024-04-17 11:07 | 0:44 | E/O | High temperature point solving | 30 | 22 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2024-04-25 10:09 | 2024-04-25 10:47 | 0:38 | T | None | 190 | 120.3333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-02 HT | 2024-04-25 10:09 | 2024-04-25 10:48 | 0:39 | T |  | 190 | 123.5 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2024-04-25 10:09 | 2024-04-25 10:34 | 0:25 | T |  | 190 | 79.1667 | Power interruption
|  |  | Total : | 464:30 |  | Unserved Energy: |  | 1572.6667
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2024-04-16 16:03 | 2024-04-16 16:33 | 0:30 | T | 1. General Trip 2. REF Trip | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2024-04-16 17:17 | 2024-04-16 17:32 | 0:15 | T | General, REF Trip | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-2 | 2024-04-25 11:15 | 2024-04-25 17:38 | 6:23 | E/O | Bus PT Y phase oil leakage Maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2024-04-25 15:40 | 2024-04-25 16:12 | 0:32 | E/O | Breaking bird's nest | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2024-04-01 20:32 | 2024-04-01 20:54 | 0:22 | T | over current, | 60 | 22 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-04-19 10:40 | 2024-04-19 10:54 | 0:14 | T | Due to 33kV Agla feeder trip | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-04-19 19:55 | 2024-04-19 20:00 | 0:05 | T | Due to 33kV Agla feeder fault | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-04-22 13:46 | 2024-04-22 21:17 | 7:31 | E/O | Red hot Maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2024-04-01 10:40 | 2024-04-01 11:20 | 0:40 | E/O | 33 kv kabilganj feeder source side riser sparking | 45 | 30 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2024-04-02 11:30 | 2024-04-02 13:38 | 2:08 | E/O | 33 kv T2 bus shutdown | 16 | 34.1333 | Power interruption
|  |  | Total : | 18:40 |  | Unserved Energy: |  | 86.1333
Chattogram Grid Circle :
Bakulia 132/33kV Grid Sub-Station | T-1 (402T) LT | 2024-04-22 10:59 | 2024-04-22 11:24 | 0:25 | E/O | To Remove G.I wire from T-01 HT loop. | 12 | 5 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2024-04-22 09:50 | 2024-04-22 10:29 | 0:39 | E/O | Emergency shutdown taken by PDB for Red hot maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 LT | 2024-04-07 08:06 | 2024-04-07 09:40 | 1:34 | T | WTI trip nd OIl temp high | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | TR-1 LT | 2024-04-25 07:01 | 2024-04-25 08:25 | 1:24 | E/O | Red hot at 33kV bus isolator | 10 | 14 | Power interruption
Khagrachori 132/33kV Grid Sub-Station | TR-2 LT | 2024-04-24 07:10 | 2024-04-24 09:17 | 2:07 | E/O | Emergency Maintenance work due to red hot of T2 secondary side bus isolator. | 8 | 16.9333 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) HT | 2024-04-25 07:51 | 2024-04-25 08:19 | 0:28 | T | over current, | 44 | 20.5333 | Power interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | TR-1 HT | 2024-04-29 00:12 | 2024-04-29 00:40 | 0:28 | T | No signal. at sas 132kv Tr-1 inter trip | 28 | 13.0667 | Power interruption
|  |  | Total : | 7:05 |  | Unserved Energy: |  | 69.5333
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-04-04 06:56 | 2024-04-04 06:58 | 0:02 | T | E/F, B-phase=2.65KA | 60 | 2 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2024-04-09 12:11 | 2024-04-09 12:39 | 0:28 | E/O | Tr-03 33kv side C.T terminal hot spot maintenance. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T HT | 2024-04-16 19:06 | 2024-04-16 19:30 | 0:24 | T | Heavy Strom | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T HT | 2024-04-16 21:58 | 2024-04-16 23:02 | 1:04 | E/O | 132/33 KV Tr-02 shutdown for Redhot maintenance of 33kv incoming DS "Y" phase Bus side Risere. Load shade will occur 25.0MW. Inform all utilities and XEN sir, GMD, PGCB, Cumilla. | 25 | 26.6667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3-435T LT | 2024-04-16 19:10 | 2024-04-16 19:20 | 0:10 | T | Heavy Strom | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2024-04-05 19:20 | 2024-04-05 19:28 | 0:08 | T | Over Current Protection operated | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-04-12 11:00 | 2024-04-12 12:27 | 1:27 | E/O | 33KV Busbar S/D due to Summit power 33KV ckt R-phase redhot remove. | 30 | 43.5 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2024-04-05 19:20 | 2024-04-05 19:30 | 0:10 | T | over current, | 59 | 9.8333 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Main | 2024-04-27 07:15 | 2024-04-27 08:15 | 1:00 | E/O | Remove Nest | 110 | 110 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-04-21 15:10 | 2024-04-21 16:32 | 1:22 | E/O | Relay Maintenance work (SPMD) | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-04-20 15:10 | 2024-04-20 17:12 | 2:02 | E/O | Emergency Maintenance work of P122 Relay ( Over current relay) of T-1. | 30 | 61 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-04-23 07:01 | 2024-04-23 07:05 | 0:04 | T | Shaistaganj, Lakhai, Bisic 33 kv feeder, OC/EF, | 0 | 0 | No interruption
|  |  | Total : | 8:21 |  | Unserved Energy: |  | 253
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) HT | 2024-04-23 14:45 | 2024-04-23 15:13 | 0:28 | T | Wrong operation of 33kv bus DS of Bagerhat wzpdcl instead of 33kv wzpdcl pirojpur feeder. | 15 | 7 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) HT | 2024-04-23 14:45 | 2024-04-23 15:14 | 0:29 | T | Wrong operation of 33kv bus DS of Bagerhat wzpdcl instead of 33kv wzpdcl pirojpur feeder. | 15 | 7.25 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-04-01 15:22 | 2024-04-01 15:58 | 0:36 | T | Due to Jhalokathi (WZPDCL) 33 KV feeder burnt | 100 | 60 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-04-16 16:53 | 2024-04-16 17:05 | 0:12 | T | Polashpur 33kV feeder fault. | 66 | 13.2 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-04-17 17:52 | 2024-04-17 18:06 | 0:14 | T | 33kV Feeder Fault ( chadmari 33kv) | 40 | 9.3333 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-04-01 15:22 | 2024-04-01 15:59 | 0:37 | T | Due to Jhalokathi (WZPDCL) 33 KV feeder burnt | 100 | 61.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-04-16 16:53 | 2024-04-16 17:05 | 0:12 | T | Polashpur 33kV feeder fault. | 42 | 8.4 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-04-17 17:52 | 2024-04-17 18:07 | 0:15 | T | 33kv feeder fault (chadmari 33kv) | 25 | 6.25 | Power interruption
Barishal 230/132kV Grid Sub-Station | 132 kV BUS | 2024-04-03 09:40 | 2024-04-03 11:37 | 1:57 | E/O | Red hot | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-04-21 17:18 | 2024-04-21 17:40 | 0:22 | T | 33kv jalokathy feeder fault | 37 | 13.5667 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-04-21 23:49 | 2024-04-21 23:56 | 0:07 | E/O | 33 kV bus coupler -1 B phase red hot. | 89 | 10.3833 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-04-21 17:18 | 2024-04-21 17:40 | 0:22 | T | Jalokathy feeder fault | 37 | 13.5667 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2024-04-15 09:53 | 2024-04-15 09:53 | 0:00 | T | U/F trip | 44 | 0 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-04-08 20:27 | 2024-04-08 20:38 | 0:11 | T | Due to Rajapur 33 kv feeder fault | 40 | 7.3333 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-04-26 15:08 | 2024-04-26 17:23 | 2:15 | E/O | Gopalganj PBS-4 Red hot maintenance work. | 20 | 45 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2024-04-04 06:22 | 2024-04-04 08:50 | 2:28 | E/O | 33 kv incomer-2 DS B phase Red hot maintenance | 9 | 22.2 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-04-06 12:47 | 2024-04-06 13:04 | 0:17 | E/O | Due to Metering core changing by XEN Energy Auditing Khulna. | 34 | 9.6333 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-04-08 10:02 | 2024-04-08 12:01 | 1:59 | E/O | Red hot maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-04-11 14:48 | 2024-04-11 15:55 | 1:07 | E/O | 132 kv T1 , TCS Faulty Signal . | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-04-24 10:56 | 2024-04-25 03:38 | 16:42 | T | Due to 33 kv Under Ground Cable Faulty. | 46 | 768.2 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-04-25 11:05 | 2024-04-25 19:28 | 8:23 | E/O | Tr-1 33 kv Side cable trench sand filling. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-04-27 00:23 | 2024-04-27 18:30 | 18:07 | T | underground couple fault red phase | 30 | 543.5 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T HT | 2024-04-06 08:01 | 2024-04-06 08:34 | 0:33 | T | Tripped showing E/F relay. | 10 | 5.5 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T HT | 2024-04-09 15:59 | 2024-04-09 17:13 | 1:14 | T | 33kv Bus-Section-2, BUS PT Y-phase & B-Phase Fuse Burn. | 9 | 11.1 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2024-04-06 08:01 | 2024-04-06 08:36 | 0:35 | T | No relay | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2024-04-09 15:59 | 2024-04-09 16:54 | 0:55 | T | 33kv Bus-Section-2, BUS PT Y-phase & B-Phase Fuse Burn. | 9 | 8.25 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-1 LT | 2024-04-15 08:02 | 2024-04-15 10:00 | 1:58 | T | Tripped showing BBP Trip, BFP Trip. relays. | 107 | 210.4333 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 HT | 2024-04-15 08:02 | 2024-04-15 13:41 | 5:39 | T | Tripped showing BBP Trip, BFP Trip. relays. | 107 | 604.55 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 HT | 2024-04-15 08:02 | 2024-04-15 10:05 | 2:03 | T | Tripped showing BBP Trip, BFP Trip. relays. | 136 | 278.8 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2024-04-26 06:12 | 2024-04-26 09:15 | 3:03 | E/O | Red hot maintenance | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2024-04-19 16:50 | 2024-04-19 17:22 | 0:32 | T | Tripped showing OC/EF(50) relays. | 17 | 9.0667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-04-25 06:19 | 2024-04-25 06:41 | 0:22 | T | R-2 33KV FEEDER FAULT (CB Mid Pole Blast) | 20 | 7.3333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-04-25 06:19 | 2024-04-25 06:41 | 0:22 | T | R-2 33KV FEEDER FAULT (CB Mid Pole Blast) | 20 | 7.3333 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-04-06 08:12 | 2024-04-06 11:02 | 2:50 | E/O | Red Hot Some of point T-3 Transformer Bay | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T HT | 2024-04-16 12:24 | 2024-04-16 15:08 | 2:44 | E/O | Red Hot Maintenance by PBS | 20 | 54.6667 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2024-04-16 12:23 | 2024-04-16 15:10 | 2:47 | E/O | Red Hot Maintenance by PBS | 20 | 55.6667 | Power interruption
|  |  | Total : | 82:57 |  | Unserved Energy: |  | 2859.1833
HVDC Grid Circle :
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2024-04-07 06:08 | 2024-04-07 10:01 | 3:53 | T | on load tap changer trip | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2024-04-17 07:12 | 2024-04-17 09:01 | 1:49 | E/O | Red hot maintenance | 60 | 109 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2024-04-21 12:25 | 2024-04-21 12:31 | 0:06 | T | High Temperature | 86 | 8.6 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2024-04-21 06:22 | 2024-04-21 06:29 | 0:07 | T | WZPDCL 33 kv Campus feeder fault | 50 | 5.8333 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 HT | 2024-04-22 07:30 | 2024-04-22 11:38 | 4:08 | E/O | Due to emergency maint.work | 20 | 82.6667 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2024-04-29 12:10 | 2024-04-29 13:25 | 1:15 | E/O | CT nut-bolt tait | 0 | 0 | No interruption
|  |  | Total : | 11:18 |  | Unserved Energy: |  | 206.1
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2024-04-19 08:55 | 2024-04-19 11:28 | 2:33 | E/O | Red hot maintenance | 29 | 73.95 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2024-04-19 08:58 | 2024-04-19 11:29 | 2:31 | E/O | Red hot maintenance | 29 | 72.9833 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-04-28 07:40 | 2024-04-28 12:16 | 4:36 | E/O | Red hot. | 5 | 23 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-04-29 08:50 | 2024-04-29 09:08 | 0:18 | T | Tripped showing p142 relays. | 43 | 12.9 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-04-29 08:50 | 2024-04-29 09:08 | 0:18 | T | Tripped showing p142 relays. | 43 | 12.9 | Power interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) LT | 2024-04-08 05:40 | 2024-04-08 09:36 | 3:56 | E/O | Tr-01 Y-ph LT Bushing Connector Red hot | 10 | 39.3333 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 HT | 2024-04-20 21:46 | 2024-04-20 22:52 | 1:06 | E/O | T-1,- 132/33Transformer (33kv side)red hot. | 28 | 30.8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-04-24 08:24 | 2024-04-24 08:32 | 0:08 | T | 33kV CB Problem. | 60 | 8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-04-20 22:39 | 2024-04-20 22:44 | 0:05 | T | Overload | 68 | 5.6667 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) LT | 2024-04-30 00:37 | 2024-04-30 01:07 | 0:30 | T | PBS Raj-1 feeder trip | 23 | 11.5 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | 427T(B) LT | 2024-04-08 07:12 | 2024-04-08 16:07 | 8:55 | E/O | 33 KV under ground cable fault | 12 | 107 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2024-04-08 07:13 | 2024-04-08 16:05 | 8:52 | E/O | 33 kv under ground fault | 12 | 106.4 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-04-09 11:43 | 2024-04-09 14:20 | 2:37 | E/O | Due to red hot in T3(B) 33kV side B-Phase underground cable kit. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2024-04-21 09:32 | 2024-04-21 10:40 | 1:08 | E/O | Red hot problem at 33 kv Bus DS. | 25 | 28.3333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-04-18 21:05 | 2024-04-18 22:07 | 1:02 | E/O | Sirajgonj PBS-2 has taken Shutdown for 33kV Pipulbaria feeder Bus DS Emergency Red Hot Maintenance. all operations have been conducted by the instruction of ALDC, Bogura according to QF-GMD- 39 &18. | 20 | 20.6667 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-04-08 16:45 | 2024-04-08 16:55 | 0:10 | T | Due to GIS Capacitor Bank Problem (Gas Leakage) | 37 | 6.1667 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2024-04-24 18:23 | 2024-04-24 18:27 | 0:04 | T | Capacitor Bank trip due to unbalance trip | 35 | 2.3333 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) HT | 2024-04-08 16:45 | 2024-04-08 16:55 | 0:10 | T | Due to GIS Capacitor Bank Problem (Gas Leakage) | 37 | 6.1667 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2024-04-24 18:23 | 2024-04-24 18:27 | 0:04 | T | Capacitor bank CB unbalance trip | 35 | 2.3333 | Power interruption
|  |  | Total : | 39:03 |  | Unserved Energy: |  | 570.4333
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 631:54 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: April 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur 132/33kV Grid Sub-Station | Tongi-2 | 2024-04-25 10:09 | 2024-04-25 12:45 | 2:36 | T | Tripped showing E/F | 80 | 208 | Power interruption
Netrakona 132/33kV Grid Sub-Station | Mymensingh-Netrokona Ckt-1 | 2024-04-12 11:47 | 2024-04-12 12:15 | 0:28 | T | Trip forbE/F | 50 | 23.3333 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-04-29 08:49 | 2024-04-29 09:21 | 0:32 | T | 0.3km (y Phase & B Phase) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2024-04-17 17:51 | 2024-04-17 18:05 | 0:14 | T | Tripped showing Distance,Phase-C relays. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-04-20 09:58 | 2024-04-20 10:11 | 0:13 | T | Tripped showing Distance,Phase-C relays. | 0 | 0 | No interruption
|  |  | Total : | 4:03 |  | Unserved Energy: |  | 231.3333
Dhaka (South) Grid Circle :
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-04-18 12:04 | 2024-04-18 12:15 | 0:11 | T | Tripped showing Optimho: Z1, CN. relays. | 164 | 30.0667 | Power interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-04-17 19:58 | 2024-04-17 20:29 | 0:31 | T | Raining & Storm | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-04-18 11:39 | 2024-04-18 16:16 | 4:37 | T | Trip | 85 | 392.4167 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-04-16 15:54 | 2024-04-16 21:08 | 5:14 | T | Heavy Thundering & Storm | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-04-27 12:13 | 2024-04-27 12:52 | 0:39 | T | Trip | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2024-04-24 09:33 | 2024-04-24 12:13 | 2:40 | T | Unknown | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Bashundhara 132 kv Ckt | 2024-04-02 15:11 | 2024-04-02 21:58 | 6:47 | T | LA burst in Bashundhara side | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-2 | 2024-04-10 11:17 | 2024-04-10 13:32 | 2:15 | T | Tripped showing Protection lockout relay | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2024-04-02 15:11 | 2024-04-02 15:48 | 0:37 | T | LA burst in Bashundhara side. For this reason Power plant also trip at a time | 17 | 10.4833 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2024-04-10 11:17 | 2024-04-10 12:31 | 1:14 | T | DIR. O/C and E/F relay. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-01 | 2024-04-19 16:54 | 2024-04-19 17:04 | 0:10 | T | Unknown | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-04-12 08:28 | 2024-04-12 12:53 | 4:25 | T | unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-02 09:03 | 2024-04-02 09:21 | 0:18 | T | Unknown. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-14 06:46 | 2024-04-14 06:46 | 0:00 | T | Unknown. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-14 08:55 | 2024-04-19 12:55 | 124:00 | E/O | XLPE Cable fault (puncture) in Basundhara grid SS. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-22 13:55 | 2024-04-22 14:14 | 0:19 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-25 12:05 | 2024-04-25 12:23 | 0:18 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-29 11:29 | 2024-04-29 14:37 | 3:08 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-29 16:03 | 2024-04-29 22:02 | 5:59 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-04-19 03:56 | 2024-04-19 04:15 | 0:19 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-04-19 08:03 | 2024-04-19 08:14 | 0:11 | T | Unknown. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-04-23 13:17 | 2024-04-23 13:25 | 0:08 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-04-29 11:33 | 2024-04-29 11:37 | 0:04 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2024-04-03 11:52 | 2024-04-03 11:59 | 0:07 | E/O | Communication Works | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2024-04-15 03:15 | 2024-04-15 04:17 | 1:02 | T | trip due to Ullon ckt-2 trip | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-02 | 2024-04-15 03:15 | 2024-04-15 04:10 | 0:55 | T | N/A | 0 | 0 | No interruption
SevenRings 132/11kV Sub-Station | Seven Circle | 2024-04-19 11:08 | 2024-04-19 13:37 | 2:29 | T | After checking the transmission by SCBL the line side found to be ok. | 7 | 17.3833 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-04-30 06:36 | 2024-04-30 12:51 | 6:15 | E/O | Red hot Line DS B Ph | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-04-13 16:22 | 2024-04-13 16:40 | 0:18 | E/O | Emergency maintenance work by BPML-1 at 33kv outgoing side. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-04-22 09:42 | 2024-04-22 11:45 | 2:03 | E/O | Red hot maintenance by Bashundhara | 7 | 14.35 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-04-10 07:02 | 2024-04-10 07:08 | 0:06 | T | showing line distance operated trip | 0 | 0 | No interruption
|  |  | Total : | 177:19 |  | Unserved Energy: |  | 464.7
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | AKSML Ckt | 2024-04-11 10:32 | 2024-04-11 10:49 | 0:17 | T | Tripping | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2024-04-23 10:39 | 2024-04-23 14:53 | 4:14 | E/O | sparking | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2024-04-30 13:35 | 2024-04-30 15:11 | 1:36 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-04-22 23:34 | 2024-04-23 02:20 | 2:46 | E/O | spark | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-04-30 11:26 | 2024-04-30 13:32 | 2:06 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | KSRM | 2024-04-17 09:32 | 2024-04-17 14:41 | 5:09 | E/O | maintenance work needed in transmission line | 30 | 154.5 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | KSRM | 2024-04-17 12:52 | 2024-04-17 14:41 | 1:49 | E/O | maintenance work needed in transmission line | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-04-18 04:18 | 2024-04-18 07:13 | 2:55 | T | Tripping | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 2024-04-07 13:14 | 2024-04-07 13:21 | 0:07 | T | Stormy Weather | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2024-04-18 06:56 | 2024-04-18 08:38 | 1:42 | T | Tripping | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-04-15 10:26 | 2024-04-23 17:37 | 199:11 | E/O | NLDC | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2024-04-25 06:57 | 2024-04-25 10:58 | 4:01 | E/O | For Red hot repare | 0 | 0 | No interruption
|  |  | Total : | 225:53 |  | Unserved Energy: |  | 154.5
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | Sylhet-Fenchugang -T -Branibazar-2 | 2024-04-04 02:03 | 2024-04-04 02:20 | 0:17 | T | Tripping | 28 | 7.9333 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-04-18 03:02 | 2024-04-18 08:14 | 5:12 | T | Zone-01 R-phase,Y-phase,B-phase trip fault distance-47.18km | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-04-18 03:02 | 2024-04-18 08:14 | 5:12 | T | Zone-01 Y-phase,B-phase trip fault distance-46.46 km | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2024-04-17 18:55 | 2024-04-17 19:28 | 0:33 | T | Thunder storm | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2024-04-21 05:31 | 2024-04-21 05:57 | 0:26 | T | Tripping | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Chowddagram-1 | 2024-04-20 19:30 | 2024-04-20 19:36 | 0:06 | T | None | 96 | 9.6 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | Chowddagram-2 | 2024-04-20 19:30 | 2024-04-20 19:36 | 0:06 | T | None | 96 | 9.6 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-04-16 17:30 | 2024-04-16 17:57 | 0:27 | T | Bed Weather & Raining. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-04-05 23:32 | 2024-04-06 00:03 | 0:31 | T | Bad Rainy Weather | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | SPCL 86 MW | 2024-04-05 23:16 | 2024-04-05 23:20 | 0:04 | T | None | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | SPCL 86 MW | 2024-04-14 23:47 | 2024-04-15 00:49 | 1:02 | T | Madabpur-01 and pran 33 kv feeder Trip under Tr-04 Transformer | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | SPCL 86 MW | 2024-04-17 18:55 | 2024-04-17 19:02 | 0:07 | T | bad weather | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | SPCL 86 MW | 2024-04-17 19:31 | 2024-04-17 19:40 | 0:09 | T | Tripping | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-04-03 03:00 | 2024-04-03 03:11 | 0:11 | T | wind and thunder | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-04-07 12:03 | 2024-04-07 12:06 | 0:03 | T | Stormy weather | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-04-19 16:10 | 2024-04-19 16:39 | 0:29 | T | Fault | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2024-04-19 16:10 | 2024-04-19 16:39 | 0:29 | T | Fault | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-04-16 19:21 | 2024-04-16 19:31 | 0:10 | T | Chattak end ckt1 & 2 | 4 | 0.66667 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-04-30 16:58 | 2024-04-30 17:18 | 0:20 | T | Sylhet bad Weather | 30 | 10 | Power interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-04-04 02:03 | 2024-04-04 02:20 | 0:17 | T | Tripped showing REC650,REL670 relay | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-04-04 02:03 | 2024-04-04 02:20 | 0:17 | T | Tripped showing REC650,REL670 relay | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | 150MW GT PS | 2024-04-04 02:02 | 2024-04-04 05:38 | 3:36 | T | Tripped showing Not operate. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-04-04 23:30 | 2024-04-05 00:10 | 0:40 | T | Tripping | 34 | 22.6667 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-04-16 19:19 | 2024-04-16 20:36 | 1:17 | T | Tripped showing Zone-1, A&B Phase. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-04-30 16:58 | 2024-04-30 17:18 | 0:20 | T | Tripping | 29 | 9.6667 | Power interruption
|  |  | Total : | 22:21 |  | Unserved Energy: |  | 70.1333
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-04-07 10:04 | 2024-04-07 10:31 | 0:27 | T | Thunderstorm | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-04-07 10:08 | 2024-04-07 15:08 | 5:00 | T | Bat weather condition. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-04-07 15:37 | 2024-04-07 21:12 | 5:35 | T | Tripped showing Distance relay zone A.88 relay | 8 | 44.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-04-17 15:15 | 2024-04-17 15:18 | 0:03 | T | Unknown | 42 | 2.1 | Power interruption
Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2024-04-11 12:19 | 2024-04-11 15:40 | 3:21 | T | Tripped showing REL 670 relays. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Gopalgonj CKT-1 | 2024-04-17 17:50 | 2024-04-17 20:12 | 2:22 | T | Over Voltage | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Gopalgonj CKT-2 | 2024-04-17 17:50 | 2024-04-17 20:12 | 2:22 | T | Over Voltage | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2024-04-16 17:54 | 2024-04-16 21:53 | 3:59 | T | Strom & Havy Rain | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-04-06 06:05 | 2024-04-06 10:11 | 4:06 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-04-06 10:21 | 2024-04-06 12:12 | 1:51 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Gallamari Ckt-1 | 2024-04-15 08:02 | 2024-04-15 13:53 | 5:51 | T | Tripped showing REL 670 relays. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Gallamari Ckt-1 | 2024-04-16 18:54 | 2024-04-16 19:42 | 0:48 | E/O | According to ALDC Instruction. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Gallamari Ckt-2 | 2024-04-15 08:02 | 2024-04-15 13:54 | 5:52 | T | Tripped showing BBP Trip, BFP Trip. relays. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-1 | 2024-04-15 08:02 | 2024-04-15 10:10 | 2:08 | T | Tripped showing BBP Trip, BFP Trip. relays. | 127 | 270.9333 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | Khulna Central Ckt-2 | 2024-04-15 08:02 | 2024-04-15 10:13 | 2:11 | T | Tripped showing BBP Trip, BFP Trip. relays. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-1 | 2024-04-15 08:02 | 2024-04-15 10:02 | 2:00 | T | Tripped showing BBP Trip, BFP Trip. relays. | 56 | 112 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2024-04-15 08:02 | 2024-04-15 10:14 | 2:12 | T | Tripped showing BBP Trip, BFP Trip. relays. | 0 | 0 | No interruption
|  |  | Total : | 50:08 |  | Unserved Energy: |  | 429.7
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2024-04-27 11:00 | 2024-04-27 21:32 | 10:32 | E/O | Shutdown is taken from Baharampur end | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | GTG (NW) | 2024-04-15 12:23 | 2024-04-15 17:59 | 5:36 | T | Problem of Protection panel of GTG (NW) Xfr. | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 2 | 2024-04-21 11:04 | 2024-04-21 11:52 | 0:48 | T | O/C, ZONE-1 ,67.50Km | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Pabna | 2024-04-22 12:08 | 2024-04-22 13:50 | 1:42 | E/O | Redhot maintenance work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2024-04-16 15:25 | 2024-04-16 17:22 | 1:57 | T | Tripped showing Z1 (143km), VT fail, SOTF relays | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2024-04-15 09:51 | 2024-04-15 11:50 | 1:59 | T | Tripped showing Lock out 86 relays. | 90 | 178.5 | Power interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. - 2 | 2024-04-24 11:03 | 2024-04-24 12:43 | 1:40 | E/O | Kite flying on wire in Jhenaidah circuit -2. | 0 | 0 | No interruption
|  |  | Total : | 24:14 |  | Unserved Energy: |  | 178.5
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2024-04-14 12:26 | 2024-04-17 19:27 | 79:01 | E/O | As per instructions of NLDC. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2024-04-27 03:19 | 2024-04-27 09:41 | 6:22 | E/O | As per instruction of ALDC, Bogura. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-2 | 2024-04-14 12:26 | 2024-04-17 19:27 | 79:01 | E/O | As per instructions of NLDC. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Baropukuria 230 KV Ckt-2 | 2024-04-29 08:49 | 2024-04-29 10:31 | 1:42 | T | Distance Protection Trip. | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | Thakurgaon-1 | 2024-04-08 07:11 | 2024-04-08 07:20 | 0:09 | T | T-3 incomming side 33 kv under ground cable fault | 35 | 5.25 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-1 | 2024-04-28 08:56 | 2024-04-28 10:59 | 2:03 | E/O | Red hot at different point | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-2 | 2024-04-28 06:20 | 2024-04-28 08:52 | 2:32 | E/O | Red hot maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2024-04-27 11:10 | 2024-04-27 16:58 | 5:48 | E/O | Maintenances Work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Teesta Solar-1 | 2024-04-29 08:51 | 2024-04-29 09:42 | 0:51 | T | Under Voltage & Under Frequency. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2024-04-07 16:04 | 2024-04-15 00:23 | 176:19 | E/O | Due to low voltage Sherpur CKT-1 & Sherpur CKT-2 CB open as per instruction of SDE,NLDC,Dhaka. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2024-04-07 16:04 | 2024-04-15 00:24 | 176:20 | E/O | Due to low voltage Sherpur CKT-1 & Sherpur CKT-2 CB open as per instruction of SDE,NLDC,Dhaka. | 0 | 0 | No interruption
|  |  | Total : | 530:08 |  | Unserved Energy: |  | 5.25
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1034:06 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-2 (415T2) LT | 2024-04-26 06:51 | 2024-04-26 12:21 | 5:30 | S/O | Main body oil leakage | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132 kv Busbar-2 | 2024-04-05 06:02 | 2024-04-05 10:35 | 4:33 | S/O | 132 KV bus jumper temperature high | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 LT | 2024-04-05 05:19 | 2024-04-05 10:56 | 5:37 | S/O | Due to various point temperature high. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-04-18 06:29 | 2024-04-18 09:49 | 3:20 | S/O | Red-hot maintenance | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-04-04 06:23 | 2024-04-04 10:51 | 4:28 | S/O | 33kv extension bus DS work | 30 | 134 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-04-22 06:08 | 2024-04-22 07:36 | 1:28 | S/O | Auxiliary Transformer-1 Oil leakage maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-04-05 07:15 | 2024-04-05 09:49 | 2:34 | S/O | Shutdown taken by Tangail PBS due to 33kV Gorai feeder bus DS to 33kV bus Y phase loop changing work. | 110 | 282.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-04-21 06:42 | 2024-04-21 06:42 | 0:00 | S/O | 33 KV bus DS red hot maintenance. | 40 | 0 | Power interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2024-04-18 09:41 | 2024-04-18 10:07 | 0:26 | S/O | Gas pressure checking | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | BUS-B | 2024-04-04 14:42 | 2024-04-04 15:45 | 1:03 | D/W | Due to project work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2024-04-04 12:59 | 2024-04-04 14:31 | 1:32 | D/W | Due to project work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Bus-A | 2024-04-27 08:59 | 2024-04-27 08:59 | 0:00 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) LT | 2024-04-19 15:55 | 2024-04-19 21:58 | 6:03 | S/O | For 132kv T2&T3 Parallel Operation. | 50 | 302.5 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-04-27 10:15 | 2024-04-27 11:53 | 1:38 | S/O | Due to project work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2024-04-19 15:50 | 2024-04-19 16:22 | 0:32 | S/O | due to T3 Transformer load Shear. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2024-04-05 05:34 | 2024-04-05 08:05 | 2:31 | S/O | Redhot maintenance | 30 | 75.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-04-09 09:29 | 2024-04-09 11:16 | 1:47 | S/O | Red hot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-04-16 10:35 | 2024-04-16 19:11 | 8:36 | S/O | Due to project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2024-04-06 09:01 | 2024-04-06 11:55 | 2:54 | S/O | Red hot Maintenance. | 20 | 58 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-04-09 11:34 | 2024-04-09 15:08 | 3:34 | S/O | Due to maint.work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-04-27 11:58 | 2024-04-27 13:20 | 1:22 | S/O | Red hot Maintenance. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-04-27 08:50 | 2024-04-27 11:52 | 3:02 | S/O | Red hot Maintenance. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Reserve Bus | 2024-04-22 06:28 | 2024-04-22 08:35 | 2:07 | S/O | Red Hot Maintenance work | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-04-28 10:46 | 2024-04-28 16:06 | 5:20 | D/W | for NLDC Intregration from 400kv GNDP project | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) HT | 2024-04-29 11:34 | 2024-04-29 15:48 | 4:14 | D/W | 400KV GNDP Project For NLDC Intregration | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2024-04-27 06:08 | 2024-04-27 08:42 | 2:34 | S/O | High temperature maintenance of T3-HV bush(Y ph),LV bus(B ph), 33kV bus DS(RYB ph) | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-04-06 09:25 | 2024-04-06 16:05 | 6:40 | S/O | 132kV Main Bus-I DS installation work of T-4 by G2G Project. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 LT | 2024-04-24 10:45 | 2024-04-24 12:50 | 2:05 | S/O | Energy meter change | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-04-24 12:54 | 2024-04-24 13:50 | 0:56 | S/O | Energy meter change | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-04-05 08:45 | 2024-04-05 17:50 | 9:05 | S/O | For T-4 transformer installation work. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132 kV BUS-1 | 2024-04-25 09:42 | 2024-04-25 09:42 | 0:00 | S/O | cleaning bird's nest | 0 | 0 | No interruption
|  |  | Total : | 95:31 |  | Unserved Energy: |  | 852.3333
Dhaka (South) Grid Circle : | [9 empty] | 39.3333
Hasnabad 132/33kV Grid Substation | 33kv Main Bus | 2024-04-02 10:58 | 2024-04-02 13:36 | 2:38 | S/O | Pangaon feeder Red hot | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Reserve Bus | 2024-04-20 08:32 | 2024-04-20 10:20 | 1:48 | S/O | Due to maint.work | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 HT | 2024-04-30 05:38 | 2024-04-30 06:51 | 1:13 | S/O | Due to maint.work of 33 kVBus | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2024-04-30 06:58 | 2024-04-30 08:01 | 1:03 | S/O | Due to Hotspot Maintenance Work at 33 side | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 132 kV Busbar-2 | 2024-04-19 07:42 | 2024-04-19 12:19 | 4:37 | D/W | capacity upgradation | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2024-04-20 07:38 | 2024-04-20 08:15 | 0:37 | D/W | Dismental Auto Tx.-3 230 kV side by CCCE. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | 230kV Busbar-2 | 2024-04-22 07:35 | 2024-04-22 11:58 | 4:23 | D/W | Dismental old Auto Tx.-3 at 230 kV side. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 2024-04-19 07:40 | 2024-04-19 12:28 | 4:48 | D/W | Due to maint.work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV MI Cement HT | 2024-04-22 09:45 | 2024-04-22 23:48 | 14:03 | S/O | due to CT and PT Replacement work. | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV MI Cement HT | 2024-04-23 10:00 | 2024-04-23 20:20 | 10:20 | S/O | Maintenance work | 4.7 | 48.5667 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV Bus A | 2024-04-24 07:42 | 2024-04-24 09:58 | 2:16 | D/W | T-3 Loop connection with Bus-A work done by G2G project | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV Bus B | 2024-04-24 06:17 | 2024-04-24 07:32 | 1:15 | D/W | T-3 Loop connection with Bus-B work done by G2G project | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 LT | 2024-04-26 07:14 | 2024-04-26 09:15 | 2:01 | S/O | Corrective maintenance work. | 10 | 20.1667 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | T-2 HT | 2024-04-26 09:22 | 2024-04-26 10:36 | 1:14 | S/O | Corrective maintenance due to abnormal thermal issue in different point | 0 | 0 | No interruption
|  |  | Total : | 52:16 |  | Unserved Energy: |  | 68.7333
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | Main BUS | 2024-04-04 07:09 | 2024-04-04 09:36 | 2:27 | D/W | Loop conductor and BUS DS connection of Tr-02 Bay | 60 | 147 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2024-04-05 10:35 | 2024-04-05 11:18 | 0:43 | D/W | Relay Works. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-04-07 14:15 | 2024-04-07 15:04 | 0:49 | S/O | Shutdown taken By Satkania PDB for Bus Isolator | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-04-17 06:24 | 2024-04-17 07:50 | 1:26 | S/O | REDHOT maintenance by Satkania BPDB | 58 | 83.1333 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 HT | 2024-04-19 07:00 | 2024-04-19 18:14 | 11:14 | S/O | MT-02 WTI, OTI, Radiator, Water flowing works | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2024-04-29 07:15 | 2024-04-29 13:12 | 5:57 | S/O | Tan delta test | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | 33 KV BUS-1 | 2024-04-29 10:46 | 2024-04-29 13:59 | 3:13 | S/O | 33 KV Bus DS maintainance. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2024-04-25 07:20 | 2024-04-25 15:36 | 8:16 | S/O | Oil leakage maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2024-04-30 09:45 | 2024-04-30 12:34 | 2:49 | S/O | Inspection of Transformer-01 by Energypac. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-04-30 15:41 | 2024-04-30 16:57 | 1:16 | S/O | For red hot maintenance by BPDB. | 0 | 0 | No interruption
|  |  | Total : | 38:10 |  |  |  | 230.1333
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 402T HT | 2024-04-09 08:10 | 2024-04-09 11:19 | 3:09 | S/O | R-phase 33kv D.S terminal hot spot maintenance | 15 | 47.25 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-04-19 07:30 | 2024-04-19 08:30 | 1:00 | S/O | Do | 10 | 10 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-04-21 06:40 | 2024-04-21 08:15 | 1:35 | S/O | Red hot maintenance work of T-1 x-former 33 kv DS | 10 | 15.8333 | Power interruption
Chandpur 132/33kV Grid Sub-Station | Bus-B | 2024-04-25 08:26 | 2024-04-25 10:30 | 2:04 | S/O | Red Hot maintenance | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-3 LT | 2024-04-04 07:46 | 2024-04-04 10:15 | 2:29 | S/O | 33KV Companyganj PBS Shutdown For Red Hot | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-04-22 07:58 | 2024-04-22 10:30 | 2:32 | S/O | 33 KV Feeder Red Hot Maintenance By BPDB | 15 | 38 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 LT | 2024-04-18 07:20 | 2024-04-18 09:21 | 2:01 | S/O | 33 KV Bus coupler & Red Hot Maintenance By PBS | 30 | 60.5 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 HT | 2024-04-05 21:54 | 2024-04-05 22:19 | 0:25 | S/O | Shifted from Bus-01 to Bus-02 in Bd grid. | 35 | 14.5833 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 HT | 2024-04-27 07:35 | 2024-04-27 10:39 | 3:04 | S/O | Do to maint.work | 20 | 61.3333 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 HT | 2024-04-27 18:02 | 2024-04-27 18:03 | 0:01 | S/O | Do to maint.work | 35 | 0.58333 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-04-04 09:37 | 2024-04-04 16:14 | 6:37 | S/O | Project Works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-1 | 2024-04-05 09:31 | 2024-04-05 12:25 | 2:54 | D/W | G2G project work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2024-04-27 09:30 | 2024-04-27 17:05 | 7:35 | D/W | G2G Project Work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-04-04 09:23 | 2024-04-04 16:50 | 7:27 | S/O | Project works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2024-04-05 09:16 | 2024-04-05 14:24 | 5:08 | D/W | G2G project work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-04-26 07:49 | 2024-04-26 10:32 | 2:43 | D/W | G2G Project Work. | 5 | 13.5833 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-04-27 08:55 | 2024-04-27 16:46 | 7:51 | D/W | G2G Project Work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-04-06 08:29 | 2024-04-06 09:44 | 1:15 | S/O | For BPDB maintenance Work. | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | TR-2 LT | 2024-04-16 06:05 | 2024-04-16 09:25 | 3:20 | S/O | Do to maint.work | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2024-04-06 08:27 | 2024-04-06 09:33 | 1:06 | S/O | 33 KV bus maintenance | 10 | 11 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 HT | 2024-04-05 08:40 | 2024-04-05 11:00 | 2:20 | S/O | Maintenance at transformer Bay | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-04-12 22:50 | 2024-04-13 00:44 | 1:54 | S/O | Bus D/S 989B Red Hot Maintenance. Load flow by TR-04 and TR-06. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-04-17 06:49 | 2024-04-17 08:51 | 2:02 | S/O | Load flow by TR-04 and TR-06. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2024-04-25 06:06 | 2024-04-25 07:25 | 1:19 | S/O | Corrective Maintenance of TR-04 HT Bushing. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 LT | 2024-04-01 00:41 | 2024-04-01 03:06 | 2:25 | S/O | work of PDB | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-04-01 00:41 | 2024-04-01 03:06 | 2:25 | S/O | work of PDB | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-04-01 08:26 | 2024-04-01 08:44 | 0:18 | S/O | work of PDB | 5 | 1.5 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-04-02 12:22 | 2024-04-02 13:12 | 0:50 | D/W | 33 KV Botteshwar feeder Bus to DS Loop Maintenance Purpose. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 LT | 2024-04-25 08:19 | 2024-04-25 10:34 | 2:15 | S/O | work of PDB | 6 | 13.5 | Power interruption
|  |  | Total : | 80:04 |  | Unserved Energy: |  | 287.6667
Khulna Grid Circle :
Barguna 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-04-22 12:38 | 2024-04-22 12:43 | 0:05 | S/O | Auxiliary Transformer-1 ,R-Phase Fuse Change. | 8 | 0.66667 | Power interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-04-22 12:38 | 2024-04-22 12:43 | 0:05 | S/O | Auxiliary Transformer-1 ,R-Phase Fuse Change. | 8 | 0.66667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2024-04-06 06:37 | 2024-04-06 10:05 | 3:28 | S/O | Emergency work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2024-04-06 10:05 | 2024-04-06 11:19 | 1:14 | S/O | 33 kV Babiganj feeder source DS red hot repair by PBS | 7 | 8.6333 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-04-25 06:27 | 2024-04-25 09:55 | 3:28 | S/O | 33 kv busbar maintenance | 24 | 83.2 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-04-06 07:11 | 2024-04-06 09:28 | 2:17 | S/O | 33 kV Rahmatpur (Uzirpur) feeder source DS red hot repair | 9 | 20.55 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-04-25 06:27 | 2024-04-25 09:56 | 3:29 | S/O | 33kv busbar maintenance | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-04-03 05:48 | 2024-04-03 09:30 | 3:42 | D/W | EEGBPSB Project work. | 45 | 166.5 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-04-03 05:49 | 2024-04-03 09:50 | 4:01 | D/W | EEGBPSB Project work. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-04-20 07:17 | 2024-04-20 09:18 | 2:01 | S/O | 33kV Busbar Maintenance | 20 | 40.3333 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-04-21 07:46 | 2024-04-21 08:53 | 1:07 | S/O | Hotspots maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-04-25 06:33 | 2024-04-25 09:32 | 2:59 | S/O | Maintenance | 40 | 119.3333 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-04-20 07:02 | 2024-04-20 16:50 | 9:48 | S/O | 33kV Underground Cable Replace | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-04-25 06:30 | 2024-04-25 09:42 | 3:12 | S/O | Maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-04-24 10:12 | 2024-04-24 21:42 | 11:30 | S/O | Due to maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-04-25 08:59 | 2024-04-25 21:34 | 12:35 | S/O | Due to maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-04-28 11:54 | 2024-04-28 17:34 | 5:40 | S/O | Due to maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-04-29 08:31 | 2024-04-29 21:13 | 12:42 | S/O | Due to maintenance work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-04-30 08:02 | 2024-04-30 21:34 | 13:32 | S/O | Due to maintenance work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-04-27 08:52 | 2024-04-27 16:04 | 7:12 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-04-23 10:15 | 2024-04-23 19:40 | 9:25 | D/W | Rupsha 800 MW Line Project Works. CRM and Hipot Test. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-04-24 09:58 | 2024-04-24 16:58 | 7:00 | D/W | NWPGCL 800MW PP Project Work. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2024-04-23 06:03 | 2024-04-23 09:15 | 3:12 | S/O | High temperature maintenance. | 9 | 28.8 | Power interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2024-04-22 07:30 | 2024-04-22 09:29 | 1:59 | S/O | 33 KV bus section -1 (N1,N3), bus section-2 (N5) 's disconnecting blade (bottom nut) redhot maintenance work. | 30 | 59.5 | Power interruption
Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2024-04-22 07:10 | 2024-04-22 08:46 | 1:36 | S/O | 33 KV bus section -1 (N1,N3), bus section-2 (N5) 's disconnecting blade (bottom nut) redhot maintenance work. | 26 | 41.6 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-04-06 11:00 | 2024-04-06 12:14 | 1:14 | S/O | 33kV BUS Section Shutdown due to REB-1 High Temperature maintenance. | 16 | 19.7333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-04-27 16:09 | 2024-04-27 18:05 | 1:56 | S/O | 33KV T-2 Busbar S/D due to REB-1 high temperature maintenance. | 25 | 48.3333 | Power interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 HT | 2024-04-01 09:13 | 2024-04-01 10:26 | 1:13 | S/O | Disk insulator change by Silicon coating | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 HT | 2024-04-01 09:13 | 2024-04-06 15:45 | 126:32 | S/O | Disk insulator changes by Silicon coating. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 HT | 2024-04-13 10:53 | 2024-04-13 17:56 | 7:03 | D/W | oil leakage | 0 | 0 | No interruption
|  |  | Total : | 265:17 |  | Unserved Energy : |  | 637.85
HVDC Grid Circle
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 HT | 2024-04-13 09:22 | 2024-04-13 10:42 | 1:20 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-04-21 06:09 | 2024-04-21 08:26 | 2:17 | S/O | Red hot maintenance at T-1 33kv overhead line yoke clamp b phase | 25 | 57.0833 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 HT | 2024-04-22 07:07 | 2024-04-22 09:28 | 2:21 | S/O | Due to maint.work | 25 | 58.75 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 HT | 2024-04-26 07:06 | 2024-04-26 10:05 | 2:59 | S/O | Maintenance of 33 kv DS post insulator in T-3(A+B). | 10 | 29.8333 | Power interruption
|  |  | Total : | 8:57 |  | Unserved Energy : |  | 145.6667
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-04-02 08:14 | 2024-04-02 11:40 | 3:26 | S/O | High temperature maintenance. | 45 | 154.5 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2024-04-06 08:18 | 2024-04-06 10:36 | 2:18 | S/O | 33 KV Incomer-2 Red Hot Maintenance | 8 | 18.4 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-04-20 07:40 | 2024-04-20 09:43 | 2:03 | S/O | Maintenance Work | 20 | 41 | Power interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2024-04-22 07:25 | 2024-04-22 18:23 | 10:58 | D/W | T#04 Transformer Bus Loop Connection | 0 | 0 | Power interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-04-23 07:18 | 2024-04-23 18:15 | 10:57 | D/W | T#04 Transformer Commissioning work. | 0 | 0 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-04-24 06:45 | 2024-04-24 09:07 | 2:22 | S/O | Red hot maintanence. | 10 | 23.6667 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | 132kV Main Bus | 2024-04-01 06:22 | 2024-04-01 08:12 | 1:50 | S/O | Due to Thakurgaon-Panchagarh circuit-02 upgration work under PGNS project. | 28 | 51.3333 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | 132kV Main Bus | 2024-04-01 16:05 | 2024-04-01 17:38 | 1:33 | S/O | Thakurgaon -2 new circuits bay connects for 132 kv main bus under PGNS Project | 40 | 62 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | T-1(407T) LT | 2024-04-04 07:00 | 2024-04-04 09:34 | 2:34 | S/O | capacitir bank DS canection | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer HT | 2024-04-06 14:41 | 2024-04-06 15:25 | 0:44 | S/O | Oil Leakage remove work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 HT | 2024-04-03 11:16 | 2024-04-03 15:31 | 4:15 | S/O | SAS WITNESS TEST | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 LT | 2024-04-02 09:54 | 2024-04-02 11:39 | 1:45 | S/O | SAS Witness | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-04-01 11:48 | 2024-04-01 14:21 | 2:33 | S/O | SAS witness | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-04-03 16:38 | 2024-04-03 17:14 | 0:36 | S/O | Sas work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-04-04 10:00 | 2024-04-04 14:22 | 4:22 | S/O | Sas work. | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | HV 400 KV BUS | 2024-04-03 11:02 | 2024-04-03 18:08 | 7:06 | S/O | SAS witness test | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | HV 400 KV BUS | 2024-04-04 10:25 | 2024-04-04 14:15 | 3:50 | S/O | Sas work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2024-04-06 07:01 | 2024-04-06 08:26 | 1:25 | S/O | Maintenance work. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-04-06 11:06 | 2024-04-06 12:34 | 1:28 | S/O | 33 KV Side maintenance and cleaning | 40 | 58.6667 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2024-04-06 08:59 | 2024-04-06 11:06 | 2:07 | S/O | Maintenance work. | 19 | 40.2167 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) LT | 2024-04-05 08:58 | 2024-04-05 10:53 | 1:55 | S/O | Maintenance work. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 33 kV BUS | 2024-04-05 09:05 | 2024-04-05 10:53 | 1:48 | S/O | Maintenance work. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2024-04-02 12:02 | 2024-04-02 13:26 | 1:24 | S/O | High temperature maintenance work at 33 kv ckt breaker (Y-phase) of T-4 transformer. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-04-20 11:21 | 2024-04-20 13:10 | 1:49 | S/O | 33 kV capacitor bank Bus DS Connection | 15 | 27.25 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) LT | 2024-04-19 05:58 | 2024-04-19 11:12 | 5:14 | S/O | 33kV bus coupler rearrange | 7 | 36.6333 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) LT | 2024-04-20 06:02 | 2024-04-20 10:51 | 4:49 | S/O | 33 kV Bus coupler rearrange | 14 | 67.4333 | Power interruption
|  |  | Total : | 85:11 |  | Unserved Energy : |  | 581.1
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 625:26 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:April 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-04-07 22:50 | 2024-04-08 12:58 | 14:08 | S/O | Project work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-02 | 2024-04-07 22:50 | 2024-04-08 12:58 | 14:08 | S/O | Project work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-02 | 2024-04-17 06:29 | 2024-04-17 10:12 | 3:43 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-04-05 05:43 | 2024-04-05 09:29 | 3:46 | S/O | None | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2024-04-05 05:44 | 2024-04-05 10:03 | 4:19 | S/O | Due to maint.work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-04-09 06:08 | 2024-04-09 10:06 | 3:58 | S/O | Red hot maintenance at the clamp of Bus PT(Ghorasal end) | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-04-02 06:15 | 2024-04-02 23:50 | 17:35 | S/O | Insulator replacement work. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-04-04 13:17 | 2024-04-04 16:28 | 3:11 | D/W | 132 kV bus extension work by G2G project | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-04-27 09:02 | 2024-04-27 09:51 | 0:49 | S/O | Due to maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2024-04-04 14:52 | 2024-04-04 16:14 | 1:22 | D/W | Due to project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-04-09 11:35 | 2024-04-09 15:08 | 3:33 | S/O | Due to project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-04-27 08:52 | 2024-04-27 11:50 | 2:58 | S/O | Red hot Maintenance. | 30 | 89 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-04-09 09:29 | 2024-04-09 11:16 | 1:47 | S/O | Red hot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-04-16 10:35 | 2024-04-16 19:11 | 8:36 | S/O | Due to maint.work | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Bus-coupler(E-06) | 2024-04-30 11:33 | 2024-04-30 12:48 | 1:15 | D/W | NLDC Intregation S/D taken by 400 kv GNDP Project. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-04-29 12:35 | 2024-04-29 16:55 | 4:20 | D/W | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-04-30 09:32 | 2024-04-30 16:46 | 7:14 | D/W | AR modification. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-04-20 07:25 | 2024-04-20 12:15 | 4:50 | S/O | 33kv H Pole cutting. | 90 | 435 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-04-24 11:01 | 2024-04-24 12:56 | 1:55 | S/O | Temperature maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-04-05 09:42 | 2024-04-05 19:37 | 9:55 | D/W | Tower height extension work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2024-04-06 10:01 | 2024-04-06 16:54 | 6:53 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 120:15 |  | Unserved Energy: |  | 524
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | Haripur | 2024-04-29 05:51 | 2024-04-29 07:18 | 1:27 | S/O | Haripur Line Equipment Red Hot Maintenance. | 150 | 217.5 | Power interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-04-06 08:39 | 2024-04-06 10:40 | 2:01 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-1 | 2024-04-20 08:20 | 2024-04-20 10:16 | 1:56 | S/O | From other end. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2024-04-13 07:00 | 2024-04-13 20:31 | 13:31 | S/O | Work on Another Side | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-04-12 08:26 | 2024-04-12 12:01 | 3:35 | S/O | Another side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-04-12 13:08 | 2024-04-12 21:39 | 8:31 | S/O | Another side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-04-07 05:47 | 2024-04-07 05:55 | 0:08 | S/O | Load shifting from 132kV main bus to reserve bus at Haripur S/S. | 115 | 15.3333 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-04-16 06:11 | 2024-04-16 11:38 | 5:27 | S/O | beacuse of Shampur-Megnaghat Circuit Sutdown due to this reason Aminbazar1 &2 circuit going to Shutdown according to NLDC instruction. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-04-19 06:58 | 2024-04-19 08:45 | 1:47 | S/O | Meghnaghat- shaympur line work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2024-04-16 06:11 | 2024-04-16 11:38 | 5:27 | S/O | beacuse of Shampur-Megnaghat Circuit Sutdown due to this reason Aminbazar1 &2 circuit going to Shutdown according to NLDC instruction. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2024-04-19 06:58 | 2024-04-19 08:45 | 1:47 | S/O | Meghnaghat- shaympur line work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-04-19 08:44 | 2024-04-19 16:48 | 8:04 | S/O | Meghnaghat- shaympur line Shut down. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-2 | 2024-04-19 08:44 | 2024-04-19 16:48 | 8:04 | S/O | Meghnaghat- shaympur line Shut down. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Bashundhara 132 kv Ckt | 2024-04-24 08:50 | 2024-04-24 13:57 | 5:07 | S/O | LA REPLACE | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-04-06 08:38 | 2024-04-06 10:42 | 2:04 | S/O | Main bus DS Red phase fingering work | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-04-16 05:48 | 2024-04-16 05:54 | 0:06 | S/O | Corrective maintenance work | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-04-16 06:13 | 2024-04-16 10:29 | 4:16 | S/O | Corrective maintenance work done | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-04-19 07:41 | 2024-04-19 16:46 | 9:05 | S/O | Due to high temperature at some point corrective maintenance is required. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-04-26 06:54 | 2024-04-26 16:13 | 9:19 | S/O | Tree Trimming By Gulshan SS | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Shyampur old-2(E10) | 2024-04-16 09:36 | 2024-04-16 12:11 | 2:35 | S/O | Maintenance work at Shyampur old end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-04-29 08:25 | 2024-04-29 11:01 | 2:36 | S/O | Oil leakage check in unit Transformer-2 | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2024-04-27 06:07 | 2024-04-27 08:23 | 2:16 | S/O | Shutdown taken by Daudkandi Grid S/S. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2024-04-27 06:07 | 2024-04-27 08:23 | 2:16 | S/O | Shutdown taken by Daudkandi Grid S/S. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | TCCL | 2024-04-28 11:10 | 2024-04-28 14:56 | 3:46 | S/O | 132 kv TCCLline bay CB SF6 gas corrective maintenance | 0 | 0 | No interruption
|  |  | Total : | 105:11 |  | Unserved Energy: |  | 232.8333
Chattogram Grid Circle :
Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2024-04-12 07:52 | 2024-04-12 17:29 | 9:37 | S/O | Maintenance work at transmission line tower | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-04-13 08:15 | 2024-04-13 17:32 | 9:17 | S/O | Maintenance work in transmission line | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2024-04-28 10:41 | 2024-04-28 16:15 | 5:34 | D/W | Request from modunaghat SS and order of NLDC | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2024-04-17 07:58 | 2024-04-17 08:45 | 0:47 | S/O | SD taken by Matarbari | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2024-04-19 07:23 | 2024-04-19 08:04 | 0:41 | S/O | Due to clean the Bird Nest. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-04-05 05:49 | 2024-04-05 16:08 | 10:19 | D/W | Lilo connection at anandabazar end | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2024-04-14 09:36 | 2024-04-14 13:29 | 3:53 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Baraulia Circuit-2 | 2024-04-08 06:08 | 2024-04-08 07:12 | 1:04 | S/O | Line isolator(223S) y-ph line side T-clamp red hot maintenance. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-2(Rampur) | 2024-04-25 06:59 | 2024-04-25 10:57 | 3:58 | S/O | Red Hot Maintenance at Rampur End. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Chandraghona-1 | 2024-04-28 14:20 | 2024-04-28 16:15 | 1:55 | D/W | Due to maint.work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-04-05 06:08 | 2024-04-05 16:30 | 10:22 | D/W | ESPNER project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-04-05 06:05 | 2024-04-05 16:07 | 10:02 | D/W | ESPNER project work | 0 | 0 | No interruption
|  |  | Total : | 67:29 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-04-01 07:22 | 2024-04-01 14:35 | 7:13 | S/O | Due to maint.work | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-04-02 06:05 | 2024-04-02 11:51 | 5:46 | S/O | Meintenance | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-II | 2024-04-02 12:09 | 2024-04-02 16:55 | 4:46 | S/O | Due to maint.work | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibiyana-III (Back feed) | 2024-04-13 11:10 | 2024-04-16 11:57 | 72:47 | S/O | Annual maintenance bibi 3 End | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 2024-04-03 09:58 | 2024-04-03 12:10 | 2:12 | S/O | Relay testing by SPMD,Cumilla. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2024-04-03 12:30 | 2024-04-03 14:39 | 2:09 | S/O | Relay Testing by SPMD, Cumilla. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Kachua Ckt-1 | 2024-04-26 07:28 | 2024-04-26 16:20 | 8:52 | S/O | Kachua grid 230 KV line charging | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Kachua Ckt-2 | 2024-04-26 07:28 | 2024-04-26 16:20 | 8:52 | S/O | Kachua 230 KV line charging | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2024-04-22 06:38 | 2024-04-22 10:28 | 3:50 | S/O | Red Hot Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2024-04-04 09:57 | 2024-04-04 16:29 | 6:32 | S/O | Project Works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-04-02 10:42 | 2024-04-02 12:20 | 1:38 | S/O | Biyanibazar 132/33kv ss maintenance work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Barayerhat Ckt | 2024-04-15 19:52 | 2024-04-15 19:52 | 0:00 | S/O | According to NLDC order. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2024-04-15 19:52 | 2024-04-15 19:52 | 0:00 | S/O | According to NLDC order | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | SPCL 86 MW | 2024-04-17 19:41 | 2024-04-17 19:41 | 0:00 | S/O | Due to remove fault. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-04-01 09:38 | 2024-04-01 11:43 | 2:05 | D/W | Energy meter installation | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-04-29 10:26 | 2024-04-29 19:39 | 9:13 | D/W | for Chahatak-Sunamganj ckt-2 SAS integration work. | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-04-30 12:35 | 2024-04-30 21:18 | 8:43 | D/W | Due to project work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-04-02 10:43 | 2024-04-02 12:21 | 1:38 | S/O | Energy meter installation at Biyanibazar S/S | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-04-02 10:43 | 2024-04-02 12:21 | 1:38 | S/O | Energy meter installation at Biyanibazar S/S | 0 | 0 | No interruption
|  |  | Total : | 147:54 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-04-13 10:29 | 2024-04-13 11:52 | 1:23 | S/O | Due to maint.work | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-04-08 08:57 | 2024-04-08 12:21 | 3:24 | S/O | S/d taken by bhandaria end. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-04-17 15:19 | 2024-04-17 15:45 | 0:26 | S/O | For fault finding at line. | 42 | 18.2 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-04-03 04:59 | 2024-04-03 09:28 | 4:29 | D/W | EEGBPSP project work | 45 | 201.75 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-04-06 05:38 | 2024-04-06 06:32 | 0:54 | S/O | Shut down taken by Barisal 132/33 kv grid ss. | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-04-21 08:47 | 2024-04-21 20:20 | 11:33 | S/O | Shut Down from Barishal end | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2024-04-29 08:45 | 2024-04-29 18:27 | 9:42 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2024-04-25 09:31 | 2024-04-25 13:06 | 3:35 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2024-04-27 07:33 | 2024-04-27 23:50 | 16:17 | S/O | Maintenance at Madaripur 132kV end. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-04-24 07:30 | 2024-04-24 18:55 | 11:25 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-04-25 06:00 | 2024-04-25 19:10 | 13:10 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-04-26 06:03 | 2024-04-26 18:54 | 12:51 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-1 | 2024-04-27 06:10 | 2024-04-27 19:22 | 13:12 | S/O | Maintenance at Payra-end | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-04-28 06:45 | 2024-04-28 20:21 | 13:36 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-04-29 05:45 | 2024-04-29 17:19 | 11:34 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-04-30 06:05 | 2024-04-30 15:59 | 9:54 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2024-04-27 08:15 | 2024-04-27 18:57 | 10:42 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2024-04-21 09:28 | 2024-04-25 16:33 | 103:05 | D/W | Due to project work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2024-04-27 07:20 | 2024-04-27 07:20 | 0:00 | S/O | TCS Relay Installation | 0 | 0 | No interruption
Payra 400kV Sub-Station | Line-1 (Gopalganj) | 2024-04-24 07:30 | 2024-04-26 18:52 | 59:22 | S/O | NLDC requirement | 0 | 0 | No interruption
Payra 400kV Sub-Station | Line-1 (Gopalganj) | 2024-04-27 05:57 | 2024-04-27 19:22 | 13:25 | S/O | Due to maint.work | 0 | 0 | No interruption
Payra 400kV Sub-Station | Line-2 (Gopalganj) | 2024-04-28 06:24 | 2024-04-29 17:17 | 34:53 | S/O | Due to maint.work | 0 | 0 | No interruption
Payra 400kV Sub-Station | Line-2 (Gopalganj) | 2024-04-30 06:05 | 2024-04-30 15:58 | 9:53 | S/O | Cleaning work required by PGCB | 0 | 0 | No interruption
|  |  | Total : | 368:45 |  | Unserved Energy: |  | 219.95
HVDC Grid Circle :
BIPTC | Baharampur-4 | 2024-04-28 10:19 | 2024-04-29 00:37 | 14:18 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 14:18 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Amnura 132/33kV Grid Sub-Station | Amnura - Chapai Nawabganj | 2024-04-23 07:24 | 2024-04-23 10:59 | 3:35 | S/O | Due to maintenance. Work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | PS 230 KV Ckt1 | 2024-04-17 08:50 | 2024-04-17 08:57 | 0:07 | S/O | P/S unite 01 Sync | 160 | 18.6667 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2024-04-06 11:01 | 2024-04-06 11:27 | 0:26 | S/O | For Red Hot Mainteance | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2024-04-02 11:53 | 2024-04-02 12:22 | 0:29 | S/O | Rohanpur End Project work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2024-04-02 12:24 | 2024-04-02 15:11 | 2:47 | S/O | Rahanpur end project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-04-01 15:24 | 2024-04-01 16:10 | 0:46 | D/W | Project work at Rohanpur end | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-04-01 14:24 | 2024-04-01 15:23 | 0:59 | D/W | Project work at Rahonpur end By ALDC Bogura. | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | Thakurgaon-1 | 2024-04-01 06:20 | 2024-04-01 08:15 | 1:55 | S/O | Due to Thakurgaon-Panchagarh circuit-02 upgration work under PGNS project. | 28 | 53.6667 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | Panchagar CKT-1 | 2024-04-01 16:05 | 2024-04-01 17:40 | 1:35 | S/O | For Project Work. | 35 | 55.4167 | Power interruption
|  |  | Total : | 12:39 |  | Unserved Energy: |  | 127.75
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 836:31 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April 2024
| Area | Previous Month (March' 2024) |  |  |  | Current Month (April '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 50 | 20 | 125 | 195 | 24 | 12 | 52 | 88
2 | Dhaka (South) Grid Circle. | 58 | 14 | 65 | 137 | 31 | 10 | 38 | 79
3 | Chattogram Grid Circle. | 30 | 9 | 46 | 85 | 8 | 11 | 22 | 41
4 | Cumilla Grid Circle. | 18 | 16 | 75 | 109 | 31 | 6 | 48 | 85
5 | Khulna Grid Circle. | 16 | 13 | 52 | 81 | 38 | 15 | 53 | 106
6 | HVDC Grid Circle | 5 | 6 | 22 | 33 | 7 | 6 | 5 | 18
7 | Bogura Grid Circle. | 19 | 16 | 42 | 77 | 12 | 18 | 35 | 65
8 | Others
9 | Total | 196 | 94 | 427 | 717 | 151 | 78 | 253 | 482
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April 2024
| Area | Previous Month (March' 2024) |  |  |  | Current Month (April '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 952.8 | 466.94 | 3790.47 | 5210.21 | 1051.09 | 752.9 | 1376.3 | 3180.29
2 | Dhaka (South) Grid Circle. | 1129.95 | 150.75 | 125.03 | 1405.73 | 472.35 | 78.48 | 301.56 | 852.39
3 | Chattogram Grid Circle. | 574.04 | 32.82 | 1331.45 | 1938.31 | 33.6 | 190.43 | 230.13 | 454.16
4 | Cumilla Grid Circle. | 73.07 | 40.5 | 281.33 | 394.9 | 81.96 | 241.17 | 287.67 | 610.8
5 | Khulna Grid Circle. | 237.7 | 231.58 | 893.38 | 1362.66 | 3091.34 | 197.54 | 857.8 | 4146.68
6 | HVDC Grid Circle | 35.07 | 47.43 | 1642.9 | 1725.4 | 192.93 | 191.67 | 145.67 | 530.27
7 | Bogura Grid Circle. | 638.92 | 69.88 | 1231.48 | 1940.28 | 73.22 | 502.46 | 708.85 | 1284.53
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 3641.55 | 1039.9 | 9296.04 | 13977.49 | 4996.49 | 2154.65 | 3907.98 | 11059.12
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 21 | 5 | 26 | 7 | 9 | 10 | 2425
2 | Dhaka (South) | 5031.6 | 3 | 2 | 5 | 1 | 1 | 3 | 154.86
3 | Chattogram | 2042 | 5 | 2 | 7 | 3 |  | 4 | 299.66
4 | Khulna | 2434 | 28 | 13 | 41 | 16 | 5 | 20 | 3497.03
5 | HVDC | 5954.3 | 4 | 3 | 7 | 2 |  | 5 | 351.77
6 | Bogura | 3145.6 | 18 | 11 | 29 | 9 |  | 20 | 1151.53
7 | Cumilla | 2981 | 6 | 12 | 18 | 4 | 2 | 12 | 540.67
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 8420.52
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.84%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.97%
4 | Khulna | 99.62%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.94% | [6 empty] | Information Management Division
7 | Cumilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 | 2 | 4 | 1 |  | 3 | 755.33
2 | Dhaka (South) | 990.29 | - | 5 | 2 | 7 | 2 | 1 | 4 | 697.53
3 | Chattogram | 917 | - | 1 | - | 1 | - | - | 1 | 154.5
4 | Khulna | 1238.4 | - | 4 | 2 | 6 | 2 | - | 4 | 649.65
5 | HVDC | 1325 | - | 1 | - | 1 | - | - | 1 | 178.5
6 | Bogura | 1803.3 | - | 1 | 3 | 4 | 2 |  | 2 | 133
7 | Cumilla | 1648.16 | - | 7 | - | - | 6 | 1 |  | 70.13
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 2638.64
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.74%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-04-01 | 16 | - | 12 | 26hr08 min | 1 | 5hr09 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Ashuganj 230/132/33kV Sub-Station | 1 | 49:52 | 598.4
Kabirpur 132/33kV Grid Sub-Station | 2 | 2:24 | 132.5
Kishoreganj 132/33kV Grid Sub-Station | 4 | 16:37 | 181.83
Kodda 132/33kV Grid Sub-Station | 5 | 4:42 | 185.93
Mirzapur 132/33kV GIS Grid Sub-Station | 2 | 0:18 | 7.5
Sreepur 230/132/33kV Grid Sub-Station | 1 | 0:27 | 29.25
Tangail 132/33kV Grid Sub-Station | 3 | 2:47 | 114.25
Tongi 230/132/33kV Grid Sub-Station | 3 | 1:42 | 323
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:36 | 208
Netrakona 132/33kV Grid Sub-Station | 1 | 0:28 | 23.3333
Jamalpur 132/33kV Grid Sub-Station | 1 | 4:28 | 134
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:34 | 282.3333
Kishoreganj 132/33kV Grid Sub-Station | 1 | 6:03 | 302.5
Kodda 132/33kV Grid Sub-Station | 1 | 2:31 | 75.5
Manikganj 132/33kV Grid Sub-Station | 2 | 5:52 | 147
Tangail 132/33kV Grid Sub-Station | 1 | 4:50 | 435
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:22 | 22
Sonargaon 132/33kV Grid Sub-Station | 2 | 2:48 | 64.13
Haripur 230/132kV Grid Sub-Station | 2 | 4:48 | 422.48
Madanganj 132/33kV Grid Sub-Station | 1 | 0:37 | 10.4833
SevenRings 132/11kV Sub-Station | 1 | 2:29 | 17.3833
Sonargaon 132/33kV Grid Sub-Station | 1 | 2:03 | 14.35
Shitalakhya 132/33kV Grid Sub-Station | 1 | 10:20 | 48.5667
Siddhirganj 132/33kV Grid Sub-Station | 1 | 2:01 | 20.1667
Bhulta 132/33kV Grid Sub-Station | 1 | 1:27 | 217.5
Haripur 230/132kV Grid Sub-Station | 1 | 0:08 | 15.3333
Bakulia 132/33kV Grid Sub-Station | 1 | 0:25 | 5
Khagrachori 132/33kV Grid Sub-Station | 2 | 3:31 | 30.93
Madunaghat 132/33kV Grid Sub-Station | 1 | 0:28 | 20.5333
Rampur 230/132/33 kV GIS Grid Sub-Station | 1 | 0:28 | 13.0667
Baroaulia 132/33kV Grid Sub-Station | 1 | 5:09 | 154.5
Dohazari 132/33kV Grid Sub-Station | 2 | 3:53 | 230.13
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 0:02 | 2
Chowmuhani 132/33kV Grid Sub-Station | 1 | 1:04 | 26.6667
Cumilla(N) 230/132/33kV Grid Sub-Station | 2 | 1:47 | 53.33
Daudkandi 132/33kV Grid Sub-Station | 2 | 3:02 | 171
Beanibazar 132/33kV Grid Sub-Station | 1 | 0:17 | 7.9333
Cumilla(S) 132/33kV Grid Sub-Station | 2 | 0:12 | 19.2
Sunamganj 132/33kV Grid Sub-Station | 2 | 0:30 | 10.67
Sylhet 132/33kV Grid Sub-Station | 2 | 1:00 | 32.33
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 3:09 | 47.25
Chandpur 132/33kV Grid Sub-Station | 2 | 2:35 | 25.83
Cumilla(N) 230/132/33kV Grid Sub-Station | 2 | 4:33 | 98.5
Cumilla(S) 132/33kV Grid Sub-Station | 3 | 3:30 | 76.5
Fenchuganj 230/132/33kV Grid Sub-Station | 1 | 2:43 | 13.5833
Ramganj 132/33kV Grid Sub-Station | 1 | 1:06 | 11
Sylhet 132/33kV Grid Sub-Station | 2 | 2:33 | 15
Bagerhat 132/33kV Grid Sub-Station | 2 | 0:57 | 14.25
Barishal 132/33kV Grid Sub-Station | 9 | 2:57 | 196.37
Bhandaria 132/33kV Grid Sub-Station | 1 | 0:11 | 7.3333
Gopalganj 132/33kV Grid Sub-Station | 2 | 4:43 | 67.2
Khulna (C) 132/33kV Grid Sub-Station | 6 | 37:48 | 1346.18
Khulna(S) 230/132kV Grid Sub-Station | 3 | 9:40 | 1093.78
Mongla 132/33kV Grid Sub-Station | 1 | 0:32 | 9.0667
Noapara 132/33kV Grid Sub-Station | 2 | 0:48 | 14.67
Shariatpur 132/33kV Grid Sub-Station | 2 | 5:31 | 110.33
Barishal 132/33kV Grid Sub-Station | 2 | 5:38 | 46.77
Khulna(S) 230/132kV Grid Sub-Station | 2 | 4:08 | 382.93
Barguna 132/33kV Grid Sub-Station | 2 | 1:10 | 1.33
Barishal 230/132kV Grid Sub-Station | 3 | 6:59 | 112.38
Bhandaria 132/33kV Grid Sub-Station | 1 | 3:42 | 166.5
Faridpur 132/33kV Grid Sub-Station | 2 | 5:00 | 159.67
Madaripur 132/33kV Grid Sub-Station | 1 | 3:12 | 28.8
Narail 132/33kV Grid Sub-Station | 2 | 3:35 | 101.1
Noapara 132/33kV Grid Sub-Station | 2 | 3:10 | 68.07
Barishal 132/33kV Grid Sub-Station | 1 | 0:26 | 18.2
Bhandaria 132/33kV Grid Sub-Station | 1 | 4:29 | 201.75
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:49 | 109
Kushtia 132/33kV Grid Sub-Station | 2 | 0:13 | 14.43
Pabna 132/33kV Grid Sub-Station | 1 | 4:08 | 82.6667
Jashore 132/33kV Grid Sub-Station | 1 | 1:59 | 178.5
Kushtia 132/33kV Grid Sub-Station | 1 | 2:17 | 57.0833
Pabna 132/33kV Grid Sub-Station | 2 | 5:20 | 88.58
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 5:04 | 146.93
Jaldhaka 132/33kV Grid Sub-Station | 3 | 5:12 | 48.8
Kurigram 132/33kV Grid Sub-Station | 1 | 3:56 | 39.3333
Naogaon 132/33kV Grid Sub-Station | 3 | 1:19 | 44.47
Niamatpur 132/33kV Grid Sub-Station | 1 | 0:30 | 11.5
Panchagarh 132/33kV Grid Sub-Station | 2 | 17:47 | 213.4
Sirajganj 132/33kV Grid Sub-Station | 2 | 2:10 | 49
Thakurgaon 132/33kV Grid Sub-Station | 4 | 0:28 | 17
Panchagarh 132/33kV Grid Sub-Station | 1 | 0:09 | 5.25
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 5:44 | 172.9
Bogura 132/33kV Grid Sub-Station | 1 | 2:03 | 41
Naogaon 132/33kV Grid Sub-Station | 1 | 2:22 | 23.6667
Panchagarh 132/33kV Grid Sub-Station | 2 | 3:23 | 113.33
Rajshahi 132/33kV Grid Sub-Station | 2 | 3:35 | 98.88
Thakurgaon 132/33kV Grid Sub-Station | 3 | 11:52 | 131.32
Barapukuria 230/132/33kV Grid Sub-Station | 1 | 0:07 | 18.6667
Panchagarh 132/33kV Grid Sub-Station | 1 | 1:55 | 53.6667
Thakurgaon 132/33kV Grid Sub-Station | 1 | 1:35 | 55.4167
Total Unserved energy : | 163 | 366:44 | 11059.1433
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April 2024
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2024-04-30 15:00 | 50
2 | Agargaon 230/132kV Grid Sub-Station | 2024-04-21 13:00 | 129
3 | Banani 132/33kV Grid Sub-Station | 2024-04-30 14:00 | 69.8
4 | Bangabhaban 132/33kV Grid Sub-Station | 2024-04-16 10:00 | 23
5 | Bashundhara 132/33kV Grid Sub-Station | 2024-04-28 16:00 | 224
6 | BashundharaCement 132/33kV Sub-Station | 2024-04-28 19:30 | 21
7 | Bhulta 132/33kV Grid Sub-Station | 2024-04-01 22:00 | 257
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2024-04-30 17:00 | 179
9 | Charsaidpur 132/33kV Sub-Station | 2024-04-05 10:00 | 47
10 | Dhaka University 132/33kV Grid Sub-Station | 2024-04-30 13:00 | 46
11 | Dhamrai 132/33kV Grid Sub-Station | 2024-04-22 06:00 | 136
12 | Dhanmondi 132/33kV Grid Sub-Station | 2024-04-21 13:00 | 182
13 | Fatullah 132/33kV Grid Sub-Station | 2024-04-30 16:00 | 75
14 | Ghorashal 230/132/33kV Sub-Station | 2024-04-25 21:00 | 88
15 | Gulshan 132/33kV Grid Sub-Station | 2024-04-30 16:00 | 162
16 | HaripurSBU 132/33kV Sub-Station | 2024-04-30 23:00 | 174
17 | Hasnabad 132/33kV Grid Substation | 2024-04-29 21:00 | 103
18 | Joydebpur 132/33kV Grid Sub-Station | 2024-04-28 20:00 | 230
19 | Kabirpur 132/33kV Grid Sub-Station | 2024-04-21 18:00 | 320
20 | Kallyanpur 132/33kV Grid Sub-Station | 2024-04-28 22:00 | 135
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2024-04-30 16:00 | 57
22 | Kazla 132/33kV Grid Sub-Station | 2024-04-29 12:00 | 115
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2024-04-29 19:00 | 92
24 | Kodda 132/33kV Grid Sub-Station | 2024-04-22 21:00 | 315
25 | Lalbag 132/33kV Grid Sub-Station | 2024-04-30 17:00 | 101
26 | Madanganj 132/33kV Grid Sub-Station | 2024-04-18 15:00 | 48
27 | Madartek 132/33kV Grid Sub-Station | 2024-04-30 19:00 | 109.01
28 | Manikganj 132/33kV Grid Sub-Station | 2024-04-24 20:00 | 148
29 | Maniknagar 132/33kV Grid Sub-Station | 2024-04-30 16:00 | 100
30 | Matuail 132/33kV Grid Sub-Station | 2024-04-25 12:00 | 80
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2024-04-30 17:00 | 135
32 | Mirpur 132/33kV Grid Sub-Station | 2024-04-30 17:00 | 184
33 | MI_Cement 132/33kV Grid Sub-Station | 2024-04-03 10:00 | 12.4
34 | Mogbazar 132/33kV Grid Sub-Station | 2024-04-28 15:00 | 167.1
35 | Motijheel 132/33kV Grid Sub-Station | 2024-04-30 16:00 | 71
36 | Munshiganj 132/33kV Grid Sub-Station | 2024-04-30 23:00 | 124
37 | Narinda 132/33kV Grid Sub-Station | 2024-04-30 17:00 | 91
38 | Narshingdi 132/33kV Grid Sub-Station | 2024-04-26 19:00 | 181
39 | Nawabganj 132/33kV Grid Sub-Station | 2024-04-28 21:00 | 72.4
40 | New Tongi 132/33kV Grid Sub-Station | 2024-04-24 16:00 | 43.8
41 | Postogola 132/33kV Grid Sub-Station | 2024-04-30 17:00 | 67
42 | Purbachal 132/33kV Grid Sub-Station | 2024-04-28 20:00 | 26
43 | Rahim Steel 132/33kV Sub-Station | 2024-04-04 16:00 | 53
44 | Rajendrapur 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 116
45 | Satmasjid 132/33kV Grid Sub-Station | 2024-04-28 19:00 | 142
46 | Savar 132/33kV Grid Sub-Station | 2024-04-29 19:30 | 223
47 | SevenRings 132/11kV Sub-Station | 2024-04-22 15:00 | 21.06
48 | ShahCement 132/33kV Grid Sub-Station | 2024-04-04 23:00 | 36
49 | Shitalakhya 132/33kV Grid Sub-Station | 2024-04-29 16:00 | 118.3
50 | Shyampur 132/33kV Grid Sub-Station | 2024-04-04 12:00 | 188
51 | Siddhirganj 132/33kV Grid Sub-Station | 2024-04-28 16:00 | 136
52 | Sonargaon 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 112
53 | Sreepur 230/132/33kV Grid Sub-Station | 2024-04-03 07:00 | 69
54 | Srinagar 132/33kV Grid Sub-Station | 2024-04-06 21:00 | 82.6
55 | Tongi 230/132/33kV Grid Sub-Station | 2024-04-29 16:00 | 171
56 | Ullon 132/33kV Grid Sub-Station | 2024-04-27 19:00 | 70
57 | Uttara 132/33kV Grid Sub-Station | 2024-04-30 17:00 | 120
58 | UttaraNew 132/33kV Grid Sub-Station | 2024-04-22 23:00 | 74
59 | Zigatola 132/33kV Grid Sub-Station | 2024-04-30 16:00 | 110
60 | Agrabad 132/33kV Grid Sub-Station | 2024-04-29 18:00 | 94
61 | AKS 132/33kV Grid Sub-Station | 2024-04-03 06:00 | 16
62 | AKSML 230/33kV Grid Sub-Station | 2024-04-05 15:00 | 111
63 | Bakulia 132/33kV Grid Sub-Station | 2024-04-29 18:00 | 120
64 | Baroaulia 132/33kV Grid Sub-Station | 2024-04-30 11:00 | 85
65 | Baroirhat 132/33kV Grid Sub-Station | 2024-04-28 22:00 | 70
66 | BSRM 230/33kV Grid Sub-Station | 2024-04-22 20:00 | 177
67 | Chandraghona 132/33kV Grid Sub-Station | 2024-04-17 18:30 | 36
68 | Coxsbazar 132/33kV Grid Sub-Station | 2024-04-14 19:30 | 146
69 | Dohazari 132/33kV Grid Sub-Station | 2024-04-10 19:00 | 110
70 | GPH 230/33kV Grid Sub-Station | 2024-04-04 17:00 | 99
71 | Halishahar 132/33kV Grid Sub-Station | 2024-04-21 15:00 | 105
72 | Hathazari 230/132/33kV Grid Sub-Station | 2024-04-30 19:30 | 87
73 | Juldah 132/33kV Grid Sub-Station | 2024-04-04 12:00 | 23
74 | Kalurghat 132/33kV Grid Sub-Station | 2024-04-30 15:00 | 40
75 | Khagrachori 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 38
76 | Khulshi 132/33kV Grid Sub-Station | 2024-04-22 20:00 | 213
77 | KSRM 132/33kV Grid Sub-Station | 2024-04-18 07:00 | 50
78 | Madunaghat 132/33kV Grid Sub-Station | 2024-04-15 18:30 | 64
79 | Matarbari 132/33kV Sub-Station | 2024-04-30 20:00 | 52
80 | Mirsorai 230/33kV Grid Sub-Station | 2024-04-25 16:00 | 12
81 | Modern Steel 132/11kV Grid Sub-Station | 2024-04-06 15:00 | 0.3
82 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2024-04-04 19:00 | 41
83 | Rangamati 132/33kV Grid Sub-Station | 2024-04-22 19:00 | 20
84 | Shahmirpur 132/33kV Grid Sub-Station | 2024-04-25 | 63
85 | Shikalbaha 132/33kV Sub-Station | 2024-04-04 21:00 | 37
86 | Sholosohor 132/33kV Grid Sub-Station | 2024-04-27 19:00 | 47
87 | SSM 132/33kV Grid Sub-Station | 2024-04-24 05:00 | 17
88 | TK chemical 132kV Grid Sub-Station | 2024-04-22 22:00 | 35
89 | Ashuganj 230/132/33kV Sub-Station | 2024-04-30 19:30 | 99.5
90 | Brahmanbaria 132/33kV Grid Sub-Station | 2024-04-30 22:00 | 208
91 | Chandpur 132/33kV Grid Sub-Station | 2024-04-22 22:00 | 86
92 | Chauddagram 132/33kV Grid Sub-Station | 2024-04-22 22:00 | 89
93 | Chowmuhani 132/33kV Grid Sub-Station | 2024-04-22 21:00 | 253
94 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2024-04-22 20:00 | 211
95 | Cumilla(S) 132/33kV Grid Sub-Station | 2024-04-29 19:30 | 196
96 | Daudkandi 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 167
97 | Feni 132/33kV Grid Sub-Station | 2024-04-23 21:00 | 136
98 | Kachua 132/33kV Grid Sub-Station | 2024-04-14 21:00 | 98
99 | PHP 132/33kV Sub-Station | 2024-04-20 06:00 | 11
100 | Ramganj 132/33kV Grid Sub-Station | 2024-04-15 23:00 | 122
101 | Bhaluka 132/33kV Grid Sub-Station | 2024-04-08 09:00 | 136
102 | Ghatail 132/33kV Grid Sub-Station | 2024-04-20 21:00 | 70
103 | Jamalpur 132/33kV Grid Sub-Station | 2024-04-01 20:00 | 176
104 | Kishoreganj 132/33kV Grid Sub-Station | 2024-04-09 22:00 | 152
105 | Mirzapur 132/33kV GIS Grid Sub-Station | 2024-04-18 19:30 | 60
106 | Mymensingh 132/33kV Grid Sub-Station | 2024-04-24 06:00 | 254
107 | Netrakona 132/33kV Grid Sub-Station | 2024-04-13 19:00 | 152
108 | Sherpur 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 176
109 | Tangail 132/33kV Grid Sub-Station | 2024-04-05 21:00 | 258
110 | Beanibazar 132/33kV Grid Sub-Station | 2024-04-25 20:00 | 76
111 | Chhatak 132/33kV Grid Sub-Station | 2024-04-17 19:00 | 39
112 | Fenchuganj 230/132/33kV Grid Sub-Station | 2024-04-27 20:00 | 46
113 | Kulaura 132/33kV Grid Sub-Station | 2024-04-06 21:00 | 54
114 | Shahjibazar 132/33kV Grid Sub-Station | 2024-04-24 21:00 | 143
115 | Sreemongol 132/33kV Grid Sub-Station | 2024-04-27 23:00 | 84
116 | Sunamganj 132/33kV Grid Sub-Station | 2024-04-23 20:00 | 60
117 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2024-04-25 02:00 | 72
118 | Sylhet 132/33kV Grid Sub-Station | 2024-04-27 18:30 | 138
119 | Bagerhat 132/33kV Grid Sub-Station | 2024-04-28 23:00 | 105
120 | Benapole 132/33kV Grid Sub-Station | 2024-04-05 13:00 | 88
121 | Bheramara(GK) 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 77
122 | Chuadanga 132/33kV Grid Sub-Station | 2024-04-04 21:00 | 122
123 | Faridpur 132/33kV Grid Sub-Station | 2024-04-27 23:00 | 190
124 | Goalpara 132/33kV Grid Sub-Station | 2024-04-03 19:00 | 44
125 | Gollamari 132/33kV Grid Sub-Station | 2024-04-25 19:30 | 100
126 | Gopalganj 132/33kV Grid Sub-Station | 2024-04-30 23:00 | 127
127 | Jashore 132/33kV Grid Sub-Station | 2024-04-17 19:00 | 170
128 | Jhenaidah 132/33kV Grid Sub-Station | 2024-04-17 19:00 | 160
129 | Khulna (C) 132/33kV Grid Sub-Station | 2024-04-28 19:00 | 101
130 | Kushtia 132/33kV Grid Sub-Station | 2024-04-27 19:00 | 166
131 | Madaripur 132/33kV Grid Sub-Station | 2024-04-30 | 134
132 | Magura 132/33kV Grid Sub-Station | 2024-04-27 19:00 | 80
133 | Mongla 132/33kV Grid Sub-Station | 2024-04-02 11:00 | 51
134 | Narail 132/33kV Grid Sub-Station | 2024-04-17 19:00 | 68
135 | Noapara 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 55
136 | Rajbari 132/33kV Grid Sub-Station | 2024-04-20 21:00 | 90
137 | Satkhira 132/33kV Grid Sub-Station | 2024-04-16 22:00 | 152
138 | Shariatpur 132/33kV Grid Sub-Station | 2024-04-28 22:00 | 100
139 | Barguna 132/33kV Grid Sub-Station | 2024-04-03 19:30 | 24
140 | Barishal 132/33kV Grid Sub-Station | 2024-04-29 23:00 | 131
141 | Barishal 230/132kV Grid Sub-Station | 2024-04-28 22:00 | 114
142 | Bhandaria 132/33kV Grid Sub-Station | 2024-04-30 22:00 | 60
143 | Borhanuddin 230/33kV Grid Sub-Station | 2024-04-15 22:00 | 96
144 | Patuakhali 132/33kV Grid Sub-Station | 2024-04-30 23:00 | 99.9
145 | Payra 400/132/33kV Grid Sub-Station | 2024-04-16 23:00 | 30
146 | Amnura 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 104
147 | Bhangura 132/33kV Grid Sub-Station | 2024-04-20 22:00 | 54
148 | Bog-Sherpur 132/33kV Grid Sub-Station | 2024-04-21 21:00 | 80
149 | Bogura 132/33kV Grid Sub-Station | 2024-04-29 20:00 | 221
150 | Chapai 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 92
151 | Ishurdi 132/33kV Grid Sub-Station | 2024-04-30 19:30 | 95
152 | Joypurhat 132/33kV Grid Sub-Station | 2024-04-15 21:00 | 83
153 | Mahasthangarh 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 94
154 | Naogaon 132/33kV Grid Sub-Station | 2024-04-21 21:00 | 168
155 | Natore 132/33kV Grid Sub-Station | 2024-04-24 21:00 | 186
156 | Niamatpur 132/33kV Grid Sub-Station | 2024-04-26 19:30 | 128
157 | Pabna 132/33kV Grid Sub-Station | 2024-04-28 19:00 | 142
158 | Rajshahi 132/33kV Grid Sub-Station | 2024-04-23 23:00 | 202
159 | Rajshahi 230/132/33kV Grid Sub-Station | 2024-04-29 21:00 | 56
160 | Ruppur 132/11kV Grid Sub-Station | 2024-04-22 16:00 | 7.2
161 | Shahjadpur 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 111
162 | Sirajganj 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 150
163 | Ullahpara 132/33kV Grid Sub-Station | 2024-04-20 19:00 | 39
164 | Barapukuria 230/132/33kV Grid Sub-Station | 2024-04-30 21:00 | 88
165 | Jaldhaka 132/33kV Grid Sub-Station | 2024-04-15 19:30 | 96
166 | Kurigram 132/33kV Grid Sub-Station | 2024-04-09 20:00 | 79
167 | Lalmonirhat 132/33kV Grid Sub-Station | 2024-04-28 19:00 | 68
168 | Mithapukur 132/33kV Grid Sub-Station | 2024-04-20 09:00 | 73
169 | Palashbari 132/33kV Grid Sub-Station | 2024-04-18 20:00 | 148
170 | Panchagarh 132/33kV Grid Sub-Station | 2024-04-30 21:00 | 64
171 | Purbasadipur 132/33kV Grid Sub-Station | 2024-04-25 20:00 | 151
172 | Rangpur 132/33kV Grid Sub-Station | 2024-04-06 21:00 | 147
173 | Saidpur 132/33kV Grid Sub-Station | 2024-04-17 19:30 | 125
174 | Thakurgaon 132/33kV Grid Sub-Station | 2024-04-30 20:00 | 119
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5699.23 | 2024-04-28 | 20:00
Chattogram | 1457.5 | 2024-04-23 | 21:00
Cumilla | 1583 | 2024-04-22 | 21:00
Mymensingh | 1226 | 2024-04-22 | 21:00
Sylhet | 635 | 2024-04-23 | 20:00
Khulna | 2028 | 2024-04-28 | 0:00
Barishal | 531 | 2024-04-24 | 23:00
Rajshahi | 1865 | 2024-04-23 | 21:00
Rangpur | 979 | 2024-04-22 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:April 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 411 | 2024-04-11 08:00 | 370 | 2024-04-01 13:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 412 | 2024-04-11 08:00 | 372 | 2024-04-02 11:00
3 | Bibiana 400/230kV Sub-Station | 400 | 410 | 2024-04-11 09:00 | 382 | 2024-04-13 13:00
4 | BIPTC | 400 | 409 | 2024-04-12 05:00 | 386 | 2024-04-04 15:00
5 | Bogura 400/230kV Grid Sub-Station | 400 | 409 | 2024-04-29 14:00 | 343 | 2024-04-27
6 | Gopalganj 400/132kV Grid Sub-Station | 400 | 416 | 2024-04-11 08:00 | 378 | 2024-04-24 15:00
7 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 388 | 2024-04-12 05:00 | 356 | 2024-04-06 13:00
8 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 414 | 2024-04-01 21:00 | 365 | 2024-04-07 14:00
9 | Payra 400kV Sub-Station | 400 | 420 | 2024-04-11 06:00 | 403 | 2024-04-01 14:00
10 | Rahanpur 400/132kV Grid Sub-Station | 400 | 411 | 2024-04-29 18:00 | 361 | 2024-04-27 01:00
11 | Rampal 400/230kV Grid Sub-Station | 400 | 416 | 2024-04-11 08:00 | 382 | 2024-04-24 15:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 239 | 2024-04-11 08:00 | 210 | 2024-04-02 11:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 229 | 2024-04-07 13:00 | 210 | 2024-04-02 02:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 234 | 2024-04-11 09:00 | 215 | 2024-04-07 14:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 221 | 2024-04-02 15:00 | 200 | 2024-04-15 20:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 245 | 2024-04-07 11:00 | 228 | 2024-04-22 01:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 237 | 2024-04-15 21:00 | 220 | 2024-04-07 14:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 231 | 2024-04-11 09:00 | 208 | 2024-04-07 06:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 232 | 2024-04-16 19:00 | 212 | 2024-04-05 03:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 235 | 2024-04-11 09:00 | 215 | 2024-04-30 14:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 238 | 2024-04-12 15:00 | 226 | 2024-04-23 16:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 240 | 2024-04-09 01:00 | 220 | 2024-04-24 14:00
12 | Ghorashal 230kV Switching Sub-Station | 230 | 238 | 2024-04-09 06:00 | 214 | 2024-04-30 15:00
13 | GPH 230/33kV Grid Sub-Station | 230 | 228 | 2024-04-08 20:00 | 210 | 2024-04-05 03:00
14 | Haripur 230/132kV Grid Sub-Station | 230 | 240 | 2024-04-11 09:00 | 214 | 2024-04-01 12:00
15 | Hasnabad 230/132kV Grid Sub-Station | 230 | 237 | 2024-04-11 02:00 | 211 | 2024-04-01 12:00
16 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 228 | 2024-04-07 13:00 | 211 | 2024-04-05 12:00
17 | Ishurdi 230/132kV Grid Sub-Station | 230 | 237 | 2024-04-11 02:00 | 220 | 2024-04-07 14:00
18 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 232 | 2024-04-15 10:00 | 209 | 2024-04-21 19:00
19 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 239 | 2024-04-11 09:00 | 210 | 2024-04-02 11:00
20 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 239 | 2024-04-15 10:00 | 211 | 2024-04-24 15:00
21 | Maniknagar 230/132kV Grid Sub-Station | 230 | 241 | 2024-04-11 08:00 | 212 | 2024-04-30 16:00
22 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 246 | 2024-04-11 16:00 | 222 | 2024-04-02 10:00
23 | Mirsorai 230/33kV Grid Sub-Station | 230 | 235 | 2024-04-16 20:00 | 212 | 2024-04-05 04:00
24 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 240 | 2024-04-02 08:00 | 214 | 2024-04-24 12:00
25 | Rampura 230/132kV Grid Sub-Station | 230 | 240 | 2024-04-11 08:00 | 210 | 2024-04-30 15:00
26 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 237 | 2024-04-07 18:00 | 210 | 2024-04-03 07:00
27 | Shyampur 230/132kV Grid Sub-Station | 230 | 241 | 2024-04-11 08:00 | 213 | 2024-04-02 11:00
28 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 242 | 2024-04-11 11:00 | 215 | 2024-04-30 15:00
29 | Sirajgonj 230 kV Switching Station | 230 | 239 | 2024-04-11 08:00 | 225 | 2024-04-06 14:00
30 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 238 | 2024-04-11 20:00 | 218 | 2024-04-07 14:00
31 | Tongi 230/132/33kV Grid Sub-Station | 230 | 236 | 2024-04-12 15:00 | 202 | 2024-04-06 13:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-19 08:00 | 117 | 2024-04-30 14:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-07 13:00 | 119 | 2024-04-05 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 130 | 2024-04-07 13:00 | 118 | 2024-04-03 05:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 143 | 2024-04-24 01:00 | 113 | 2024-04-07 03:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 142 | 2024-04-11 09:00 | 132 | 2024-04-30 15:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-07 10:00 | 115 | 2024-04-15 09:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-07 13:00 | 120 | 2024-04-05 11:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 07:00 | 118 | 2024-04-30 15:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 06:00 | 119 | 2024-04-21 13:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-07 11:00 | 118 | 2024-04-01 22:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-01 06:00 | 114 | 2024-04-01 22:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 133 | 2024-04-30 20:00 | 120 | 2024-04-16 08:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 144 | 2024-04-25 01:00 | 113 | 2024-04-02 07:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-09 05:00 | 116 | 2024-04-06 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 139 | 2024-04-11 08:00 | 120 | 2024-04-02 11:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-01 | 121 | 2024-04-02 18:30
17 | Benapole 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-07 09:00 | 115 | 2024-04-15 13:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-16 18:00 | 116 | 2024-04-07 12:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-05 11:00 | 113 | 2024-04-02 02:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-09 05:00 | 124 | 2024-04-07 14:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-16 18:00 | 123 | 2024-04-15 13:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-11 09:00 | 113 | 2024-04-01 09:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-28 15:00 | 113 | 2024-04-22 05:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-05 17:00 | 113 | 2024-04-24 12:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-17 19:00 | 120 | 2024-04-18 15:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 141 | 2024-04-09 04:00 | 118 | 2024-04-30 15:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-04-16 19:00 | 113 | 2024-04-01
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-07 13:00 | 121 | 2024-04-03 05:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-29 14:00 | 115 | 2024-04-15 19:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 141 | 2024-04-11 09:00 | 121 | 2024-04-02 11:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-16 19:00 | 113 | 2024-04-17 12:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-01 | 122 | 2024-04-05 18:30
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-16 19:00 | 113 | 2024-04-01 05:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-09 05:00 | 113 | 2024-04-06 15:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 126 | 2024-04-04 07:00 | 113 | 2024-04-03 04:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-16 19:30 | 119 | 2024-04-02 07:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-16 17:00 | 113 | 2024-04-24 18:30
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-17 18:00 | 119 | 2024-04-30 15:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 142 | 2024-04-11 08:00 | 121 | 2024-04-06 11:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142 | 2024-04-11 08:00 | 122 | 2024-04-02 11:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 133 | 2024-04-18 09:00 | 113 | 2024-04-08 16:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-11 08:00 | 120 | 2024-04-23 18:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 08:00 | 121 | 2024-04-02 11:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-16 19:30 | 113 | 2024-04-02 06:00
45 | Ghatail 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-29 09:00 | 116 | 2024-04-30 16:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-07 10:00 | 122 | 2024-04-15 09:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-11 08:00 | 122 | 2024-04-15 13:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 05:00 | 122 | 2024-04-15 13:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-19 06:00 | 119 | 2024-04-30 15:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-07 13:00 | 119 | 2024-04-03 07:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 140 | 2024-04-11 06:00 | 121 | 2024-04-05 23:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 140 | 2024-04-11 09:00 | 123 | 2024-04-01 12:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-11 09:00 | 125 | 2024-04-21 12:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 130 | 2024-04-05 | 113 | 2024-04-03 09:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-01 18:00 | 113 | 2024-04-04 05:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 04:00 | 118 | 2024-04-15 13:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-09 06:00 | 123 | 2024-04-01 12:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-04-17 18:30 | 114 | 2024-04-15 03:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 130 | 2024-04-11 09:00 | 113 | 2024-04-03 07:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-07 13:00 | 121 | 2024-04-05 12:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-08 18:00 | 116 | 2024-04-03 12:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-16 19:00 | 113 | 2024-04-05 01:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-11 08:00 | 119 | 2024-04-01 13:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-29 11:00 | 120 | 2024-04-05 12:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-08 18:30 | 117 | 2024-04-30 15:00
66 | Kazla 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-09 08:00 | 118 | 2024-04-22 16:00
67 | Khagrachori 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-07 13:00 | 119 | 2024-04-03 07:00
68 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-09 05:00 | 118 | 2024-04-15 09:00
69 | Khulshi 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-07 13:00 | 119 | 2024-04-03 07:00
70 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-16 18:00 | 121 | 2024-04-27 12:00
71 | Kodda 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-29 10:00 | 115 | 2024-04-20 06:00
72 | KSRM 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-07 13:00 | 121 | 2024-04-03 06:00
73 | Kulaura 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-17 19:00 | 127 | 2024-04-06 23:00
74 | Kurigram 132/33kV Grid Sub-Station | 132 | 131 | 2024-04-02 13:00 | 113 | 2024-04-06 21:00
75 | Kushtia 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-09 05:00 | 123 | 2024-04-07 14:00
76 | Lalbag 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-08 18:30 | 121 | 2024-04-30 15:00
77 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 130 | 2024-04-02 13:00 | 113 | 2024-04-09 13:00
78 | Madanganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-11 08:00 | 120 | 2024-04-02 11:00
79 | Madaripur 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-17 18:00 | 125 | 2024-04-24 15:00
80 | Madartek 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 07:00 | 118 | 2024-04-30 16:00
81 | Madunaghat 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-07 13:00 | 121 | 2024-04-03 07:00
82 | Magura 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-09 04:00 | 122 | 2024-04-07 03:00
83 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-28 15:00 | 118 | 2024-04-05 18:00
84 | Manikganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-11 08:00 | 119 | 2024-04-01 09:00
85 | Maniknagar 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 05:00 | 119 | 2024-04-21 13:00
86 | Matarbari 132/33kV Sub-Station | 132 | 133 | 2024-04-26 09:00 | 113 | 2024-04-02 02:00
87 | Matuail 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-11 08:00 | 121.2 | 2024-04-02 15:00
88 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-09 07:00 | 116 | 2024-04-06 12:00
89 | Mirpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 09:00 | 120 | 2024-04-06 11:00
90 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 136 | 2024-04-05 22:00 | 122 | 2024-04-02 07:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 133 | 2024-04-12 04:00 | 114 | 2024-04-05 18:00
92 | MI_Cement 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 08:00 | 120.5 | 2024-04-02 11:00
93 | Modern Steel 132/11kV Grid Sub-Station | 132 | 133 | 2024-04-21 11:00 | 120 | 2024-04-05 12:00
94 | Mogbazar 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-19 08:00 | 116 | 2024-04-30 15:00
95 | Mongla 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-07 10:00 | 115 | 2024-04-21 19:00
96 | Motijheel 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 06:00 | 119 | 2024-04-21 13:00
97 | Munshiganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 08:00 | 120 | 2024-04-02 11:00
98 | Mymensingh 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-27 05:00 | 113 | 2024-04-07 12:00
99 | Naogaon 132/33kV Grid Sub-Station | 132 | 131 | 2024-04-11 09:00 | 113 | 2024-04-06 08:00
100 | Narail 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-09 05:00 | 121 | 2024-04-12 19:30
101 | Narshingdi 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-11 09:00 | 114 | 2024-04-03 07:00
102 | Natore 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-11 09:00 | 117 | 2024-04-21 12:00
103 | Nawabganj 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-07 18:30 | 123 | 2024-04-06 14:00
104 | Netrakona 132/33kV Grid Sub-Station | 132 | 130 | 2024-04-10 19:00 | 113 | 2024-04-02 09:00
105 | New Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-09 06:00 | 117 | 2024-04-06 12:00
106 | Niamatpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-29 14:00 | 119 | 2024-04-15 19:00
107 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-09 03:00 | 122 | 2024-04-01 12:00
108 | Pabna 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-11 09:00 | 119 | 2024-04-22 13:00
109 | Palashbari 132/33kV Grid Sub-Station | 132 | 144 | 2024-04-07 18:00 | 113 | 2024-04-04 08:00
110 | Panchagarh 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-03 19:30 | 113 | 2024-04-01 10:00
111 | Patuakhali 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-21 18:00 | 121 | 2024-04-02 22:00
112 | PHP 132/33kV Sub-Station | 132 | 138 | 2024-04-16 20:00 | 113 | 2024-04-03 02:00
113 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2024-04-11 08:00 | 122 | 2024-04-02 11:00
114 | Purbachal 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-09 07:00 | 116 | 2024-04-06 12:00
115 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 131 | 2024-04-03 20:00 | 113 | 2024-04-01 12:00
116 | Rahim Steel 132/33kV Sub-Station | 132 | 140 | 2024-04-11 06:00 | 117 | 2024-04-04 20:00
117 | Rajbari 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-11 09:00 | 123 | 2024-04-06 22:00
118 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-08 18:30 | 120 | 2024-04-01 09:00
119 | Rajshahi 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-22 18:00 | 120 | 2024-04-16 13:00
120 | Ramganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-16 19:00 | 113 | 2024-04-01 03:00
121 | Rangamati 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-07 13:00 | 119 | 2024-04-05 12:00
122 | Rangpur 132/33kV Grid Sub-Station | 132 | 131 | 2024-04-02 13:00 | 113 | 2024-04-04 08:00
123 | Ruppur 132/11kV Grid Sub-Station | 132 | 139 | 2024-04-11 07:00 | 124 | 2024-04-21 12:00
124 | Saidpur 132/33kV Grid Sub-Station | 132 | 131 | 2024-04-05 | 113 | 2024-04-05 09:00
125 | Satkhira 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-07 10:00 | 116 | 2024-04-15 13:00
126 | Satmasjid 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-09 04:00 | 119 | 2024-04-30 14:00
127 | Savar 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-11 08:00 | 119 | 2024-04-06 11:00
128 | SevenRings 132/11kV Sub-Station | 132 | 144 | 2024-04-11 08:00 | 128 | 2024-04-03 13:00
129 | ShahCement 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-11 09:00 | 121 | 2024-04-02 11:00
130 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-04-22 10:00 | 128 | 2024-04-07 14:00
131 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-17 19:30 | 120 | 2024-04-06 23:00
132 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-18 07:00 | 121 | 2024-04-03 04:00
133 | Shariatpur 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-17 18:00 | 123 | 2024-04-24 15:00
134 | Sherpur 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-27 05:00 | 113 | 2024-04-01 05:00
135 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 08:00 | 120.5 | 2024-04-02 11:00
136 | Sholosohor 132/33kV Grid Sub-Station | 132 | 137 | 2024-04-07 13:00 | 119 | 2024-04-05 12:00
137 | Shyampur 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 08:00 | 122 | 2024-04-02 11:00
138 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-11 08:00 | 122 | 2024-04-02 11:00
139 | Sirajganj 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-11 09:00 | 115 | 2024-04-19 23:00
140 | Sonargaon 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-16 17:00 | 120 | 2024-04-06 14:00
141 | Sreemongol 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-17 19:30 | 120 | 2024-04-24 18:30
142 | Srinagar 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-08 18:30 | 121 | 2024-04-30 15:00
143 | SSM 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-18 07:00 | 122 | 2024-04-05 12:00
144 | Sunamganj 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-01 | 120 | 2024-04-05 18:30
145 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 135 | 2024-04-17 21:00 | 124 | 2024-04-02 18:30
146 | Sylhet 132/33kV Grid Sub-Station | 132 | 134 | 2024-04-01 | 125 | 2024-04-02 18:30
147 | Tangail 132/33kV Grid Sub-Station | 132 | 136 | 2024-04-23 11:00 | 119 | 2024-04-07 04:00
148 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 135 | 2024-04-21 05:00 | 113 | 2024-04-01 10:00
149 | TK chemical 132kV Grid Sub-Station | 132 | 137 | 2024-04-21 14:00 | 121 | 2024-04-03 07:00
150 | Ullahpara 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-11 10:00 | 122 | 2024-04-07 14:00
151 | Ullon 132/33kV Grid Sub-Station | 132 | 138 | 2024-04-19 08:00 | 117 | 2024-04-30 15:00
152 | Uttara 132/33kV Grid Sub-Station | 132 | 140 | 2024-04-11 09:00 | 120 | 2024-04-30 15:00
153 | UttaraNew 132/33kV Grid Sub-Station | 132 | 141 | 2024-04-11 08:00 | 119 | 2024-04-02 11:00
154 | Zigatola 132/33kV Grid Sub-Station | 132 | 139 | 2024-04-07 18:30 | 121 | 2024-04-30 15:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:April 2024
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 407 | 444.2218 | 2024-04-30 16:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 407 | 444.2218 | 2024-04-30 16:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -2118 | 2120.4068 | 2024-04-21 18:30
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -266 | 289.3994 | 2024-04-30 13:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -228 | 228.0789 | 2024-04-02 15:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -219 | 219 | 2024-04-02 15:00
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 398 | 398.6076 | 2024-04-29 01:00
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 398 | 398.6076 | 2024-04-29 01:00
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 398 | 398.6076 | 2024-04-29 01:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 226 | 245.5443 | 2024-04-29 09:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 172 | 404.4008 | 2024-04-06 17:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 486 | 597.7458 | 2024-04-13 15:00
Meghnaghat 400/230kV Grid Sub-Station | ATR - 2 | 400/230 | -386 | 475.1053 | 2024-04-30 15:00
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 376 | 489.8694 | 2024-04-30 14:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -323.64 | 328.9973 | 2024-04-25 21:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -331.13 | 350.9996 | 2024-04-13 14:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 192 | 213.3378 | 2024-04-30 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -239 | 240.753 | 2024-04-30 20:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -409 | 409.011 | 2024-04-26 12:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -409 | 409.011 | 2024-04-26 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 294 | 306.3201 | 2024-04-17 07:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 294 | 306.3201 | 2024-04-17 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -170 | 193.7756 | 2024-04-02 22:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -159 | 167.9196 | 2024-04-06 04:00
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 228 | 241.6278 | 2024-04-04 13:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 234 | 250.3537 | 2024-04-03 13:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 218 | 240.2603 | 2024-04-30 17:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 218 | 240.2603 | 2024-04-30 17:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 161 | 174.0029 | 2024-04-30 18:30
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 161 | 174.0029 | 2024-04-30 18:30
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 170 | 176.6465 | 2024-04-22 14:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 284 | 308.3115 | 2024-04-15 05:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 164 | 174.631 | 2024-04-14 12:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 209 | 240.0104 | 2024-04-19 23:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 156 | 181.1077 | 2024-04-19 23:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 217 | 220.8393 | 2024-04-15 20:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 194 | 206.2426 | 2024-04-15 20:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 252 | 258.1472 | 2024-04-15 20:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 136 | 251.873 | 2024-04-06 19:30
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 242 | 243.6144 | 2024-04-11 17:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -109 | 110.3177 | 2024-04-07 07:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -109 | 110.3177 | 2024-04-07 07:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 188 | 199.5821 | 2024-04-06 05:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 188 | 199.5821 | 2024-04-06 05:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 229 | 282.2517 | 2024-04-18 08:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 156 | 221.3256 | 2024-04-27 19:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 191 | 199.905 | 2024-04-08 23:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 231 | 241.3732 | 2024-04-02 18:30
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 103 | 103 | 2024-04-25 22:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 103 | 103 | 2024-04-25 22:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 119 | 155.4381 | 2024-04-30 07:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 129 | 163.2207 | 2024-04-07 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 114 | 159.8124 | 2024-04-22 09:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 79 | 86.406 | 2024-04-02 15:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 79 | 86.406 | 2024-04-02 15:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 79 | 86.406 | 2024-04-02 15:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 133 | 134.2125 | 2024-04-19 08:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 108 | 152.7351 | 2024-04-15 06:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 133 | 134.2125 | 2024-04-19 08:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 103 | 134.8258 | 2024-04-18 19:30
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 116 | 162.6407 | 2024-04-07 07:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 114 | 150.333 | 2024-04-09 21:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 116 | 162.6407 | 2024-04-07 07:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -218 | 248.8453 | 2024-04-20 23:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -206 | 276.2101 | 2024-04-23
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 172 | 184.2281 | 2024-04-21 10:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 197 | 213.7709 | 2024-04-28 22:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2024-04-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 197 | 213.7709 | 2024-04-28 22:00 |  | 1.3301 | 195.6699
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -156 | 170.5784 | 2024-04-15 13:00 |  | -1.32 | -154.68
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -146 | 207.1835 | 2024-04-30 19:30 |  | -1.0171 | -144.9829
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -202 | 218.3873 | 2024-04-15 13:00 |  | -1.3351 | -200.6649
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 226 | 319.6123 | 2024-04-21 22:00 |  | 1.0206 | 224.9794
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 186 | 202.8719 | 2024-04-29 13:00 |  | 1.3233 | 184.6767
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -126 | 143.6558 | 2024-04-23 10:00 |  | -1.266 | -124.734
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -126 | 143.6558 | 2024-04-23 10:00 |  | -1.266 | -124.734
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2024-04-01 10:00 |  | 1.0206 | -0.020621
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 0 | 0 | 2024-04-01 |  | #DIV/0! | #DIV/0!
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 187 | 190.2472 | 2024-04-21 11:00 |  | 1.4187 | 185.5813
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 373 | 380.0763 | 2024-04-18 13:00 |  | 1.4165 | #REF! | Ashuganj(N)
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 380 | 381.9961 | 2024-04-29 13:00 |  | 1.4358
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 242 | 275.6592 | 2024-04-30 21:00 |  | 1.2671
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 242 | 275.6592 | 2024-04-30 21:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 139 | 148.7616 | 2024-04-04 12:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 139 | 148.7616 | 2024-04-04 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 135 | 136.9452 | 2024-04-07 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 135 | 136.9452 | 2024-04-07 12:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 172 | 186.0779 | 2024-04-20 18:30
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 172 | 186.0779 | 2024-04-20 18:30
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 220 | 222.4612 | 2024-04-02 18:30
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 220 | 222.4612 | 2024-04-02 18:30
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 220 | 222.4612 | 2024-04-02 18:30
423
Executive Engineer
Information Management Division
|  |  |  | LDC, PGCB, Dhaka. | [5 empty] | 270

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: April 2024 |  |  |  |  | (For Evening Peak) | [9 empty] | Month: April 2024 |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-04-01 | 13757 | 14650 | 853 | 21:00 | 130 | 90 | 130 | 150 | 173 | 70 | 40 | 0 | 70 | - | 2024-04-01 | 12049 | 12850 | 765 | 12:00 | 295 | 85 | 0 | 130 | 120 | 80 | 10 | 0 | 45 | -
2024-04-02 | 13707 | 15000 | 1235 | 21:00 | 200 | 140 | 175 | 170 | 200 | 190 | 75 | 0 | 85 | - | 2024-04-02 | 12147 | 13200 | 1006 | 12:00 | 350 | 120 | 20 | 130 | 120 | 140 | 36 | 0 | 90 | -
2024-04-03 | 13967 | 15250 | 1225 | 21:00 | 225 | 170 | 130 | 140 | 180 | 180 | 60 | 30 | 110 | - | 2024-04-03 | 12415 | 13400 | 941 | 12:00 | 285 | 123 | 0 | 114 | 158 | 164 | 46 | 0 | 51 | -
2024-04-04 | 14245 | 15500 | 1199 | 21:00 | 210 | 143 | 166 | 142 | 190 | 192 | 60 | 0 | 96 | - | 2024-04-04 | 12402 | 13700 | 1240 | 12:00 | 356 | 153 | 0 | 189 | 194 | 219 | 56 | 0 | 73 | -
2024-04-05 | 14438 | 15300 | 823 | 21:00 | 50 | 130 | 185 | 163 | 45 | 150 | 0 | 0 | 100 | - | 2024-04-05 | 12385 | 13400 | 969 | 12:00 | 220 | 130 | 0 | 160 | 156 | 180 | 23 | 0 | 100 | -
2024-04-06 | 14695 | 15700 | 960 | 21:00 | 50 | 20 | 180 | 130 | 250 | 180 | 5 | 55 | 90 | - | 2024-04-06 | 12670 | 14000 | 1270 | 12:00 | 355 | 160 | 155 | 150 | 145 | 200 | 5 | 0 | 100 | -
2024-04-07 | 13572 | 13850 | 265 | 21:00 | 0 | 0 | 0 | 50 | 0 | 115 | 0 | 0 | 100 | - | 2024-04-07 | 11881 | 14000 | 616 | 9:00 | 165 | 0 | 0 | 45 | 0 | 281 | 0 | 0 | 125 | -
2024-04-08 | 12700 | 12800 | 96 | 21:00 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | - | 2024-04-08 | 11791 | 12200 | 391 | 12:00 | 130 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 61 | -
2024-04-09 | 12729 | 12729 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-04-09 | 10541 | 10541 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-04-10 | 11948 | 11948 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-04-10 | 10049 | 10049 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-04-11 | 10929 | 10929 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-04-11 | 8894 | 8894 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-04-12 | 11762 | 11762 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-04-12 | 9637 | 9637 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-04-13 | 12653 | 12700 | 45 | 21:00 | 0 | 0 | 0 | 0 | 10 | 35 | 0 | 0 | 0 | - | 2024-04-13 | 10399 | 10399 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-04-14 | 12743 | 12880 | 131 | 21:00 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 20 | - | 2024-04-14 | 10915 | 10915 | 100 | 12:00 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | -
2024-04-15 | 14093 | 14350 | 245 | 21:00 | 0 | 88 | 7 | 0 | 0 | 65 | 0 | 0 | 85 | - | 2024-04-15 | 12011 | 12300 | 276 | 12:00 | 0 | 110 | 0 | 0 | 32 | 86 | 0 | 0 | 48 | -
2024-04-16 | 12780 | 12830 | 48 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | - | 2024-04-16 | 13091 | 13500 | 391 | 12:00 | 0 | 70 | 0 | 0 | 120 | 111 | 0 | 0 | 90 | -
2024-04-17 | 12847 | 13100 | 242 | 21:00 | 0 | 99 | 0 | 0 | 72 | 0 | 0 | 0 | 71 | - | 2024-04-17 | 13087 | 13500 | 394 | 12:00 | 14 | 95 | 0 | 0 | 100 | 120 | 0 | 0 | 65 | -
2024-04-18 | 14761 | 15080 | 305 | 21:00 | 0 | 95 | 0 | 0 | 0 | 140 | 0 | 0 | 70 | - | 2024-04-18 | 13065 | 13240 | 167 | 12:00 | 15 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 87 | -
2024-04-19 | 14308 | 14520 | 202 | 21:00 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 70 | - | 2024-04-19 | 12100 | 12420 | 270 | 12:00 | 10 | 100 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | -
2024-04-20 | 15358 | 15750 | 374 | 21:00 | 40 | 0 | 0 | 0 | 84 | 200 | 0 | 0 | 50 | - | 2024-04-20 | 13325 | 13800 | 454 | 12:00 | 104 | 0 | 0 | 0 | 100 | 250 | 0 | 0 | 0 | -
2024-04-21 | 15666 | 16000 | 319 | 21:00 | 20 | 0 | 0 | 0 | 49 | 150 | 0 | 0 | 100 | - | 2024-04-21 | 14295 | 14700 | 387 | 12:00 | 100 | 0 | 0 | 0 | 90 | 197 | 0 | 0 | 0 | -
2024-04-22 | 16233 | 16700 | 446 | 21:00 | 90 | 100 | 0 | 0 | 36 | 170 | 0 | 0 | 50 | - | 2024-04-22 | 14062 | 14800 | 705 | 12:00 | 220 | 125 | 0 | 0 | 110 | 250 | 0 | 0 | 0 | -
2024-04-23 | 15947 | 16720 | 738 | 21:00 | 124 | 128 | 0 | 0 | 90 | 300 | 0 | 0 | 96 | - | 2024-04-23 | 13971 | 14875 | 863 | 12:00 | 318 | 170 | 0 | 35 | 90 | 250 | 0 | 0 | 0 | -
2024-04-24 | 15936 | 16774 | 800 | 21:00 | 120 | 105 | 0 | 0 | 90 | 350 | 0 | 0 | 135 | - | 2024-04-24 | 14140 | 15000 | 821 | 12:00 | 200 | 150 | 0 | 0 | 100 | 271 | 0 | 0 | 100 | -
2024-04-25 | 15784 | 16750 | 923 | 19:30 | 160 | 170 | 0 | 120 | 80 | 200 | 0 | 0 | 193 | - | 2024-04-25 | 14197 | 15150 | 910 | 12:00 | 240 | 130 | 0 | 0 | 110 | 310 | 0 | 0 | 120 | -
2024-04-26 | 15550 | 15870 | 306 | 21:00 | 0 | 0 | 0 | 0 | 45 | 145 | 0 | 0 | 116 | - | 2024-04-26 | 13837 | 14180 | 328 | 12:00 | 55 | 0 | 0 | 0 | 75 | 180 | 0 | 0 | 18 | -
2024-04-27 | 15810 | 16750 | 898 | 20:00 | 100 | 130 | 0 | 110 | 200 | 238 | 0 | 0 | 120 | - | 2024-04-27 | 13673 | 14400 | 694 | 12:00 | 140 | 140 | 0 | 0 | 104 | 210 | 0 | 0 | 100 | -
2024-04-28 | 15816 | 17150 | 1274 | 21:00 | 190 | 214 | 0 | 190 | 240 | 260 | 0 | 0 | 180 | - | 2024-04-28 | 13453 | 15150 | 1621 | 11:00 | 470 | 170 | 0 | 265 | 258 | 258 | 25 | 0 | 175 | -
2024-04-29 | 15595 | 17200 | 1533 | 21:00 | 360 | 165 | 132 | 182 | 245 | 275 | 44 | 0 | 130 |  | 2024-04-29 | 13036 | 15800 | 2640 | 12:00 | 775 | 223 | 172 | 305 | 327 | 506 | 60 | 0 | 272
2024-04-30 | 16477 | 17000 | 499 | 21:00 | 140 | 20 | 15 | 0 | 20 | 220 | 0 | 0 | 84 |  | 2024-04-30 | 14301 | 16100 | 1718 | 12:00 | 493 | 260 | 0 | 160 | 300 | 300 | 55 | 0 | 150
| Max. L/S | - | 1537 | -
| Min. L/S | - | 54 | -
| No. of Days | - | 31 | -
| Average L/S |  | 21566
|  | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:April 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16477 | 2024-04-30 | 21:00
2 | Maximum Day Peak Genaration | MW | 14301 | 2024-04-30 | 12:00
3 | Maximum Evening Peak Demand | MW | 17200 | 2024-04-29 | 21:00
4 | Minimum Generation | MW | 8472 | 2024-04-11 | 6:00
5 | Average of the daily evening peak Genaration | MW | 14226.8667 | - | -
6 | Average of the daily day peak Genaration | MW | 12460.6333 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1533 | 2024-04-29 | 21:00
8 | Minimum load shed | MW | 0 | 2024-04-12 | 21:00
9 | Total nos. of load shed days | Day | 26 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 532.8 | - | -
11 | Total Generation | MkWh | 9235.7434 | - | -
12 | Total Generation by BPDB | MkWh | 2294.259 | % of total Gen. | 24.84%
13 | Total Generation by IPP | MkWh | 2636.5971 | '' | 28.55%
14 | A) Total Generation by Generation Companies | MkWh | 2587.4548 | '' | 28.02%
| B) Total Generation by REB | MkWh | 104.2242 | " | 1.128%
| C) Total Generation by RENTAL | MkWh | 150.1603 | " | 1.626%
| D) Total Imported from India (BIPTC) | MkWh | 600.5796 | " | 6.503%
| E) Total Imported from Tripura, India (A.C) | MkWh | 862.4684 | " | 9.338%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4724.5177 | % of total Gen. | 51.15%
| B) Oil | MkWh | 1014.37 | '' | 10.98%
| C) Hydro | MkWh | 22.8768 | '' | 0.2477%
| D) Solar | MkWh | 95.9778 | '' | 1.039%
| E) Coal | MkWh | 2693.0479 | '' | 29.16%
| F) BIPTC (Import from India) | MkWh | 600.5796 | '' | 6.503%
| G) A.C (Import from Tripura, India) | MkWh | 76.1338 | '' | 0.8243%
| H) Wind | MkWh | 8.2392 | '' | 0.08921%
16 | Maximun of the daily total Generation . | MkWh | 350.0203 | 2024-04-24
17 | Monthly Load factor | % | 73.8657 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 50702.547 | - | -
| A) Gas | M.Taka | 13795.2627 | - | -
| B) Liquid fuel | M.Taka | 16877.8983 | - | -
| C) Coal | M.Taka | 16846.5243 | - | -
| D) BIPTC (Import from India) | M.Taka | 2521.2737 | - | -
| E) Tripura(Import from India) | M.Taka | 661.588 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1991.8155 | 2024-04-23
| A) Gas | M.Taka | 516.0143 | 2024-04-11
| B) Liquid fuel | M.Taka | 848.3202 | 2024-04-22
| C) Coal | M.Taka | 729.6378 | 2024-04-16
| D) BIPTC (Import from India) | M.Taka | 101.8324 | 2024-04-17
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.4898
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.5664
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.2 | 30/04/2024 | 06:00
b) | Actual | FT (MSL) | 74.11 | 30/04/2024 | 6:00
22 | Peak Genaration of April 2023 | MW | 15648 | 2023-04-19 | 21:00
23 | Peak Demand of April 2023 | MW | 16221 | 2023-04-30 | 19:30
24 | Maximum peak Generation recorded upto 30/04/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 30/04/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/03/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:April 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [13 empty] | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 | [25 empty] | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | [25 empty] | √ | √ | √ | √ | √
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | [25 empty] | √ | √ | √ | √ | √
9 | Meghnaghat CCPP(Summit) | IPP | 335 | [19 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
10 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | √ | √ | √ | √ | √ |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable |  | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant