## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-19 | Wednesday
|  | Date (day): | 2024-06-19 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14564.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16012 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-18 | 2024-06-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 138 | 0 | 0 | 0 | 180 |  | under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 61 | 50 | 70 | 38
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 321 | 382 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 80
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 265 | 300 | 300 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 64 | 64 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 70 | 85 |  | 15 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 321 | 320 | 320
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 82 | 85 |  | 17 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 100 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 16 | 16 | 33 | 33 |  | 47 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 8 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 8 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 270 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 91 | 96 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 52 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 55 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 72 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 2 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 305 | 500 | 584 | 584 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 1815 | 2303 | 3551 | 3867 | 769 | 859
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 18 | 32 |  | fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 115 | 115 | 115 | 115 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 226 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 51 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 71 | 48 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 35 | 45 | 55 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 31 | 40 | 40
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 0 | 18 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 35 | 35 | 81 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 384 | 501 | 612 | 612 |  | 612 | Unit-2 shut down
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 13 | 26 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 0 | 0 | 0 | 0 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 17 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 817 | 1012 | 1663 | 1810 | 992 | 993
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 0 | 140 | 140 |  | 71 | ST Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 305 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 305 | 280 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 285 | 325 | 300 | 330 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 37 | 10 | 37 |  | 8 | engine problem
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 10 | 52 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 83 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 40 | 20 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150 |  | 0
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 85 | 86 |  | 77 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 77 | 17 | 100 | 100 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 74 | 146 | 144
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 8 | 50 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 11 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 17 | 0 | 114 | 0
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 77 | 42 | 85 | 28 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 86 | 96 | 34 | 115
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1512 | 1624 | 1658 | 2088 | 378 | 181
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 160 | 165 | 150 | 160 | 42 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 8 | 97 | 120 | 80 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 35 | 68 | 80 | 35 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 6 | 12 | 10 |  | Fuel shortage
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 35 | 35
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 160 | 220 | 407.6 | 407 | 42 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 29 | 30 | 30 | 30 |  | 40 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 50 | 50 | 52
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 39 | 39 | 39 |  | 11 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 0 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 61 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 260 | 260 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 235 | 240 | 320 | 350
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 310 | 320 | 330 | 350
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1089 | 1221 | 1371 | 1423 | 231 | 448
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 924 | 922 | 944 | 944
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 20 | 98
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 260 | 355 | 360 | 380 | 30 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 73 | 32 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 60 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 365 | 455 | 500 | 500 |  | 617 | Unit-2 shut down
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1609 | 1765 | 2053 | 2135 | 644 | 666
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 10 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 900 | 1100 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 110 | 110 | 110 |  | 110 | GT-2 under maint
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 200 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 960 | 1442 | 1690 | 1946 | 115 | 174
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 15 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 45
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 158 | 155 | 160 | 50 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 161 | 160 | 160 | 60 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 260 | 347 | 350 | 380 | 34 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36 | 14 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 5 | 8 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 94 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 821 | 1060 | 748 | 748 |  |  | Unit-2 shut down
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1366 | 1770 | 1728 | 1938 | 601 | 90
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 170 | 170 | 170 |  | 104 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 70 | 113
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 72 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 2 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 162 | 276 | 443 | 398 | 40 | 274
| Total |  |  |  |  | 27515 | 26364 | 9490 | 11633 | 14564.6 | 16012 | 3812 | 3685
A. |  | 2024-06-18 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 12671 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9490 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11633 | MW
3 | Day peak Generation : |  |  | 9490 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11261.25 | MW
4 | Evening peak Generation : |  |  | 11633 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 258.648 | MKWHr | By Solar | 1.0942 | MKWHr
| By Gas : | 146.2685 | MKWHr |  | By Oil: | 13.4054 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 70.6547 | MKWHr |  | By Hydro: | 2.644 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.55536 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3812 | MW | Dhaka | 3318.45 | 3318.45 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3685 | MW | Chittagong | 920 | 920 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7497 | MW | Khulna | 1876 | 1876 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1064.82 | MMCFD |  |  | Rajshahi | 1468.8 | 1468.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 425049401.69 | ii) Oil : | Taka | 242935606.21 | Comilla | 1248 | 1248 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 486479279.43 | Total | Taka | 1154464287.33 | Mymensingh | 914 | 914 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2805 | MKWHr. | Sylhet | 363 | 363 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 296 | MW (W to E) at | 21:00 | hrs | Barisal | 510 | 510 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 178 | MW at | 24:00 | hrs | Rangpur | 643 | 643 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0°C |  |  | Total | 11261.25 | 11261.25 |  | 0
B. |  | 2024-06-19 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16012 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 3512 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 255.1575 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9072 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3018 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7242 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.32 |  | (b) Today: | 82.48 |  | (c) Rule Curve: |  | 80.86
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-06-18 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 190 | 180 | 0 | 22 | 0 | 404 | 0 |  | 0 | 450 | 272 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 6 | 8 | 8 | 0 | 0 | 75 | 37 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 39 | 34 | 0 | 35 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 216 | 0 | 85 | 37 | 10 | 0 | 5 | 0 | 0 | 50 | 0 | 0 | 32 | 6 | 90 | 201 | 0 | 0 | 0 | 29 | 58 | 53 | 36 | 163 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 95 | 0 | 24 | 132 | 0 | 237 | 65 | 0 | 0 | 0 | 15 | 0 | 0 | 34 | 48 | 25 | 300 | 51 | 0 | 0 | 17 | 0 | 0 | 0 | 105 | 0 | 260 | 0 | 0 | 590 | 25 | 0 | 570 | 0 | 0 |  | 921 | 0 | 340 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 327 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1160 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 368 | 0 | 250 | 1217 | 0 | 0 | 0 |  | 6945 | 5726 | 12671 | 4288 | 921 | 2440 | 0 | 925 | 3745 | 112 | 0 | 125 | 90 | 0 | 25 | 66 | 82.27
2:00 | 0 | 0 | 190 | 180 | 0 | 22 | 0 | 405 | 0 |  | 0 | 450 | 270 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 8 | 0 | 0 | 75 | 37 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 31 | 34 | 0 | 38 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 216 | 0 | 85 | 37 | 10 | 0 | 5 | 0 | 0 | 50 | 0 | 0 | 32 | 6 | 86 | 201 | 0 | 0 | 0 | 29 | 58 | 53 | 36 | 163 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 78 | 0 | 24 | 68 | 0 | 237 | 65 | 0 | 0 | 0 | 15 | 0 | 0 | 34 | 36 | 25 | 300 | 24 | 0 | 0 | 17 | 0 | 0 | 0 | 115 | 0 | 260 | 0 | 0 | 590 | 21 | 0 | 570 | 0 | 0 |  | 920 | 0 | 345 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 315 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 367 | 0 | 216 | 1124 | 0 | 0 | 0 |  | 6803 | 5335 | 12138 | 4271 | 920 | 2426 | 0 | 744 | 3457 | 112 | 0 | 101 | 86 | 0 | 21 | 59 | 82.28
3:00 | 0 | 0 | 190 | 180 | 0 | 22 | 0 | 405 | 0 |  | 0 | 450 | 275 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 31 | 34 | 0 | 38 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 215 | 0 | 85 | 37 | 10 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 32 | 6 | 84 | 200 | 0 | 0 | 0 | 29 | 58 | 53 | 36 | 163 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 45 | 0 | 24 | 68 | 0 | 237 | 65 | 0 | 0 | 0 | 15 | 0 | 0 | 34 | 37 | 25 | 300 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 260 | 0 | 0 | 591 | 27 | 0 | 570 | 0 | 0 |  | 920 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 150 | 1018 | 0 | 0 | 0 |  | 6748 | 4982 | 11730 | 4269 | 920 | 2451 | 0 | 610 | 3189 | 115 | 0 | 65 | 84 | 0 | 27 | 57 | 82.29
4:00 | 0 | 0 | 190 | 180 | 0 | 22 | 0 | 405 | 0 |  | 0 | 450 | 276 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 31 | 34 | 0 | 37 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 215 | 0 | 86 | 37 | 10 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 32 | 6 | 85 | 200 | 0 | 0 | 0 | 29 | 58 | 53 | 33 | 163 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 24 | 0 | 24 | 68 | 0 | 237 | 65 | 0 | 0 | 0 | 15 | 0 | 0 | 34 | 37 | 25 | 300 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 104 | 0 | 260 | 0 | 0 | 590 | 21 | 0 | 570 | 0 | 0 |  | 920 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 150 | 934 | 0 | 0 | 0 |  | 6718 | 4755 | 11473 | 4269 | 920 | 2442 | 0 | 572 | 2984 | 115 | 0 | 65 | 85 | 0 | 21 | 59 | 82.3
5:00 | 0 | 0 | 190 | 180 | 0 | 22 | 0 | 405 | 0 |  | 0 | 450 | 240 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 30 | 34 | 0 | 37 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 218 | 0 | 86 | 37 | 10 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 32 | 6 | 82 | 200 | 0 | 0 | 0 | 29 | 58 | 53 | 36 | 163 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 17 | 0 | 24 | 68 | 0 | 237 | 65 | 0 | 0 | 0 | 15 | 0 | 0 | 34 | 37 | 25 | 294 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 103 | 0 | 260 | 0 | 0 | 590 | 14 | 0 | 570 | 0 | 0 |  | 922 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 214 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 150 | 856 | 0 | 0 | 0 |  | 6663 | 4629 | 11292 | 4261 | 922 | 2375 | 0 | 564 | 2895 | 115 | 0 | 64 | 82 | 0 | 14 | 55 | 82.31
6:00 | 0 | 0 | 140 | 180 | 0 | 22 | 0 | 376 | 0 |  | 0 | 380 | 250 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 4 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 217 | 0 | 85 | 37 | 10 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 32 | 6 | 78 | 140 | 0 | 0 | 0 | 29 | 58 | 53 | 36 | 163 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 55 | 0 | 17 | 1 | 24 | 68 | 0 | 237 | 45 | 0 | 0 | 0 | 15 | 0 | 0 | 34 | 37 | 25 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 104 | 0 | 260 | 0 | 0 | 480 | 23 | 0 | 450 | 0 | 3 |  | 922 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 180 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 378 | 0 | 150 | 822 | 0 | 0 | 0 |  | 6107 | 4366 | 10473 | 3987 | 922 | 2157 | 0 | 487 | 2690 | 115 | 0 | 4 | 78 | 10 | 23 | 54 | 82.32
7:00 | 0 | 0 | 140 | 180 | 0 | 22 | 0 | 350 | 0 |  | 0 | 320 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 186 | 0 | 85 | 37 | 10 | 0 | 5 | 0 | 0 | 51 | 0 | 0 | 32 | 6 | 74 | 159 | 0 | 0 | 0 | 29 | 58 | 50 | 10 | 130 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 4 | 12 | 68 | 0 | 237 | 24 | 0 | 0 | 1 | 0 | 0 | 0 | 34 | 37 | 12 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 99 | 0 | 285 | 0 | 0 | 400 | 32 | 0 | 400 | 0 | 16 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 367 | 0 | 150 | 822 | 0 | 0 | 0 |  | 5770 | 4295 | 10065 | 3934 | 923 | 2014 | 0 | 374 | 2559 | 115 | 0 | 0 | 74 | 40 | 32 | 43 | 82.33
8:00 | 0 | 0 | 140 | 180 | 0 | 22 | 0 | 326 | 0 |  | 0 | 300 | 272 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 186 | 0 | 85 | 36 | 10 | 0 | 5 | 0 | 0 | 50 | 0 | 0 | 32 | 0 | 72 | 160 | 0 | 0 | 0 | 29 | 58 | 50 | 10 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 12 | 68 | 0 | 237 | 8 | 0 | 0 | 2 | 0 | 0 | 0 | 34 | 37 | 12 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 84 | 0 | 285 | 0 | 0 | 370 | 22 | 0 | 350 | 0 | 27 |  | 925 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 160 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 180 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 363 | 0 | 150 | 822 | 2 | 0 | 0 |  | 5568 | 4123 | 9691 | 3833 | 925 | 1900 | 0 | 325 | 2445 | 115 | 0 | 0 | 72 | 54 | 22 | 0 | 82.34
9:00 | 0 | 0 | 138 | 180 | 0 | 22 | 0 | 321 | 0 |  | 0 | 300 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 186 | 0 | 85 | 36 | 10 | 0 | 5 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 70 | 160 | 0 | 0 | 0 | 29 | 58 | 25 | 10 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 68 | 0 | 235 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 34 | 38 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 86 | 0 | 285 | 0 | 0 | 384 | 13 | 0 | 305 | 0 | 17 |  | 924 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 365 | 0 | 150 | 821 | 2 | 0 | 0 |  | 5393 | 4097 | 9490 | 3785 | 924 | 1814 | 0 | 253 | 2420 | 115 | 0 | 0 | 70 | 96 | 13 | 0 | 82.35
10:00 | 0 | 0 | 120 | 180 | 0 | 0 | 0 | 288 | 0 |  | 0 | 300 | 295 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 39 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 191 | 0 | 85 | 5 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 66 | 160 | 0 | 0 | 0 | 29 | 58 | 5 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 69 | 0 | 235 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 36 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 85 | 0 | 250 | 0 | 0 | 332 | 20 | 0 | 255 | 0 | 27 |  | 926 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 133 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 361 | 0 | 150 | 823 | 6 | 0 | 0 |  | 5086 | 3980 | 9066 | 3591 | 926 | 1729 | 0 | 223 | 2326 | 114 | 0 | 0 | 66 | 71 | 20 | 0 | 82.36
11:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 269 | 0 |  | 0 | 300 | 290 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 186 | 0 | 85 | 5 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 24 | 6 | 68 | 160 | 0 | 0 | 0 | 30 | 58 | 5 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 100 | 0 | 235 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 37 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 86 | 0 | 250 | 0 | 0 | 332 | 19 | 0 | 255 | 0 | 14 |  | 925 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 1 | 47 | 0 | 0 | 0 | 362 | 2 | 150 | 825 | 11 | 0 | 0 |  | 5008 | 4018 | 9026 | 3476 | 925 | 1745 | 0 | 256 | 2329 | 113 | 0 | 0 | 68 | 95 | 19 | 0 | 82.34
12:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 270 | 0 |  | 0 | 300 | 307 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 8 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 320 | 305 | 207 | 0 | 85 | 5 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 68 | 160 | 0 | 0 | 1 | 30 | 58 | 5 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 100 | 0 | 236 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 37 | 0 | 310 | 0 | 3 | 0 | 0 | 0 | 0 | 11 | 74 | 0 | 250 | 0 | 0 | 330 | 20 | 0 | 250 | 0 | 9 |  | 924 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 180 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 362 | 8 | 150 | 824 | 43 | 0 | 0 |  | 5130 | 4111 | 9241 | 3578 | 924 | 1817 | 0 | 244 | 2326 | 113 | 0 | 0 | 68 | 151 | 20 | 0 | 82.35
13:00 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 291 | 0 |  | 0 | 350 | 303 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 8 | 8 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 315 | 305 | 206 | 26 | 85 | 5 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 72 | 160 | 0 | 0 | 1 | 30 | 58 | 5 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 100 | 0 | 239 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 36 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 6 | 54 | 0 | 310 | 0 | 0 | 391 | 12 | 0 | 250 | 0 | 32 |  | 922 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 570 | 110 | 0 | 0 | 1 | 63 | 0 | 0 | 0 | 406 | 5 | 170 | 822 | 43 | 0 | 0 |  | 5323 | 4356 | 9679 | 3834 | 922 | 1809 | 0 | 223 | 2519 | 113 | 0 | 0 | 72 | 175 | 12 | 0 | 82.35
14:00 | 0 | 0 | 0 | 180 | 0 | 19 | 0 | 300 | 0 |  | 0 | 350 | 296 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 7 | 8 | 8 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 300 | 270 | 173 | 55 | 85 | 0 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 74 | 191 | 0 | 0 | 0 | 30 | 58 | 5 | 18 | 163 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 100 | 0 | 239 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 40 | 0 | 310 | 0 | 7 | 0 | 0 | 0 | 0 | 17 | 53 | 0 | 315 | 0 | 0 | 500 | 21 | 0 | 400 | 0 | 19 |  | 922 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 190 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 600 | 110 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 413 | 6 | 170 | 821 | 30 | 0 | 0 |  | 5642 | 4530 | 10172 | 3889 | 922 | 2111 | 0 | 226 | 2674 | 113 | 0 | 0 | 74 | 142 | 21 | 0 | 82.34
15:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 300 | 0 |  | 0 | 350 | 300 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 8 | 8 | 0 | 0 | 75 | 39 | 0 | 0 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 0 | 0 | 0 | 255 | 275 | 173 | 55 | 85 | 0 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 74 | 174 | 0 | 0 | 0 | 30 | 58 | 5 | 33 | 163 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 100 | 0 | 239 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 17 | 47 | 0 | 310 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 53 | 0 | 300 | 0 | 0 | 500 | 20 | 0 | 400 | 0 | 21 |  | 922 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 580 | 110 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 410 | 4 | 170 | 821 | 36 | 0 | 0 |  | 5602 | 4456 | 10058 | 3754 | 922 | 2125 | 0 | 250 | 2651 | 114 | 0 | 0 | 74 | 148 | 20 | 25.785 | 82.37
16:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 355 | 0 |  | 0 | 400 | 253 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 8 | 0 | 0 | 75 | 39 | 0 | 0 | 1 | 205 | 0 | 0 | 0 |  | 0 | 7 | 0 | 0 | 37 | 0 | 0 | 34 | 0 | 0 | 0 | 255 | 275 | 0 | 55 | 86 | 10 | 3 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 64 | 174 | 0 | 0 | 0 | 30 | 58 | 5 | 33 | 163 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 0 | 239 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 57 | 0 | 310 | 0 | 6 | 0 | 0 | 0 | 0 | 9 | 52 | 0 | 300 | 0 | 0 | 500 | 38 | 0 | 400 | 0 | 6 |  | 922 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 178 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 580 | 110 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 412 | 8 | 170 | 822 | 14 | 0 | 0 |  | 5579 | 4351 | 9930 | 3684 | 922 | 2092 | 0 | 280 | 2654 | 114 | 0 | 7 | 64 | 75 | 38 | 66.85 | 82.37
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 384 | 0 |  | 0 | 350 | 266 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 39 | 0 | 0 | 8 | 205 | 0 | 0 | 0 |  | 0 | 65 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 0 | 0 | 280 | 270 | 0 | 55 | 85 | 10 | 3 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 32 | 0 | 42 | 174 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 100 | 0 | 240 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 65 | 0 | 310 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 52 | 0 | 250 | 0 | 0 | 500 | 26 | 0 | 300 | 0 | 6 |  | 921 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 157 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 550 | 110 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 412 | 3 | 170 | 823 | 6 | 0 | 0 |  | 5332 | 4235 | 9567 | 3607 | 921 | 1825 | 0 | 298 | 2625 | 114 | 0 | 65 | 42 | 44 | 26 | 0 | 82.38
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 303 | 0 |  | 0 | 300 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 0 | 70 | 0 | 0 | 38 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 280 | 0 | 8 | 85 | 10 | 3 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 32 | 0 | 58 | 174 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 68 | 0 | 240 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 74 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 52 | 0 | 250 | 0 | 0 | 453 | 40 | 0 | 250 | 0 | 0 |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 158 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 530 | 110 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 363 | 0 | 140 | 823 | 3 | 0 | 0 |  | 5103 | 3991 | 9094 | 3439 | 922 | 1664 | 0 | 298 | 2479 | 115 | 0 | 70 | 58 | 9 | 40 | 0 | 82.38
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 356 | 0 |  | 0 | 350 | 288 | 0 | 0 | 6 | 250 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 1 | 71 | 51 | 0 | 35 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 0 | 8 | 86 | 28 | 7 | 0 | 0 | 0 | 15 | 33 | 0 | 0 | 32 | 6 | 72 | 173 | 0 | 0 | 0 | 30 | 58 | 44 | 22 | 163 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 24 | 0 | 10 | 68 | 0 | 240 | 16 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 75 | 12 | 320 | 17 | 0 | 0 | 2 | 0 | 2 | 0 | 76 | 0 | 285 | 0 | 0 | 463 | 20 | 0 | 450 | 0 | 0 |  | 921 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 158 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 333 | 5 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 560 | 110 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 445 | 0 | 203 | 1012 | 0 | 0 | 0 |  | 5835 | 4658 | 10493 | 3580 | 921 | 2094 | 0 | 638 | 2853 | 115 | 0 | 200 | 72 | 0 | 20 | 0 | 82.39
19:30 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 356 | 0 |  | 0 | 350 | 257 | 0 | 0 | 15 | 250 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 8 | 71 | 51 | 0 | 35 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 295 | 0 | 55 | 85 | 34 | 40 | 0 | 5 | 0 | 15 | 8 | 0 | 0 | 32 | 6 | 70 | 162 | 0 | 0 | 0 | 30 | 58 | 50 | 36 | 163 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 80 | 0 | 12 | 68 | 0 | 240 | 27 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 75 | 12 | 320 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 85 | 0 | 320 | 0 | 0 | 491 | 24 | 0 | 450 | 0 | 0 |  | 922 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 156 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 290 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 860 | 110 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 506 | 0 | 250 | 1149 | 0 | 0 | 0 |  | 6196 | 5191 | 11387 | 3670 | 922 | 2155 | 0 | 784 | 3426 | 115 | 0 | 221 | 70 | 0 | 24 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 56 | 0 | 356 | 0 |  | 0 | 350 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 10 | 71 | 51 | 0 | 16 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 300 | 0 | 55 | 85 | 37 | 45 | 0 | 20 | 0 | 0 | 8 | 0 | 0 | 32 | 6 | 70 | 165 | 0 | 0 | 0 | 30 | 58 | 50 | 33 | 163 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 72 | 0 | 0 | 68 | 0 | 240 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 77 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 325 | 0 | 0 | 500 | 24 | 0 | 450 | 0 | 0 |  | 923 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 156 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 327 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 870 | 110 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 510 | 0 | 250 | 1162 | 0 | 0 | 0 |  | 6105 | 5265 | 11370 | 3692 | 923 | 2246 | 0 | 648 | 3462 | 115 | 0 | 190 | 70 | 0 | 24 | 0 | 82.39
21:00 | 0 | 0 | 0 | 180 | 0 | 61 | 0 | 382 | 0 |  | 0 | 420 | 300 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 12 | 71 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 305 | 305 | 0 | 83 | 85 | 37 | 52 | 0 | 40 | 0 | 0 | 8 | 0 | 0 | 32 | 11 | 74 | 165 | 0 | 0 | 0 | 30 | 58 | 50 | 39 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 91 | 0 | 0 | 77 | 0 | 240 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 77 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 325 | 0 | 0 | 501 | 26 | 0 | 500 | 0 | 0 |  | 922 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 158 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 347 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 900 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 455 | 0 | 200 | 1060 | 0 | 0 | 0 |  | 6380 | 5253 | 11633 | 3923 | 922 | 2466 | 0 | 664 | 3286 | 115 | 0 | 157 | 74 | 0 | 26 | 0 | 82.39
22:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 404 | 0 |  | 0 | 420 | 302 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 227 | 0 | 0 | 0 |  | 12 | 73 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 310 | 310 | 54 | 83 | 86 | 37 | 50 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 74 | 165 | 0 | 0 | 0 | 30 | 58 | 50 | 39 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 79 | 0 | 0 | 99 | 0 | 240 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 77 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 327 | 0 | 0 | 501 | 17 | 0 | 500 | 0 | 0 |  | 923 | 0 | 360 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 158 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 347 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 900 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 453 | 0 | 200 | 1067 | 0 | 0 | 0 |  | 6528 | 5266 | 11794 | 3977 | 923 | 2502 | 0 | 736 | 3291 | 115 | 0 | 159 | 74 | 0 | 17 | 0 | 82.4
23:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 404 | 0 |  | 0 | 450 | 297 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 40 | 39 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 12 | 73 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 320 | 315 | 115 | 8 | 86 | 34 | 44 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 72 | 162 | 0 | 0 | 0 | 30 | 58 | 50 | 39 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 85 | 0 | 0 | 102 | 0 | 240 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 77 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 230 | 0 | 0 | 477 | 23 | 0 | 584 | 0 | 0 |  | 925 | 0 | 365 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 178 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 940 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 508 | 0 | 230 | 949 | 0 | 0 | 0 |  | 6483 | 5396 | 11879 | 4000 | 925 | 2598 | 0 | 749 | 3274 | 79 | 0 | 159 | 72 | 0 | 23 | 0 | 82.41
24:00 | 0 | 0 | 0 | 180 | 0 | 65 | 0 | 404 | 0 |  | 0 | 450 | 305 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 40 | 38 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 12 | 73 | 34 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 330 | 330 | 102 | 8 | 86 | 37 | 30 | 0 | 43 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 76 | 162 | 0 | 0 | 0 | 30 | 58 | 50 | 34 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 85 | 0 | 0 | 45 | 0 | 240 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 77 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 230 | 0 | 0 | 519 | 21 | 0 | 584 | 0 | 0 |  | 925 | 0 | 380 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 183 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 414 | 27 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1040 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 507 | 0 | 230 | 753 | 0 | 0 | 0 |  | 6482 | 5337 | 11819 | 4029 | 925 | 2598 | 0 | 714 | 3219 | 78 | 0 | 159 | 76 | 0 | 21 | 0 | 82.42
KWH | 0 | 0 | 1726000 | 4079250 | 0 | 616818 | 0 | 8553600 | 0 |  | 0 | 9132500 | 6714327 | 0 | 0 | 23281 | 6527403 | 0 | 0 | 0 | 6624 | 160800 | 0 | 0 | 0 | 0 | 0 | 18050 | 19680 | 0 | 265800 | 151920 | 198600 | 198300 | 0 | 0 | 1704000 | 940000 | 0 | 0 | 69537 | 5063222 | 0 | 0 | 0 |  | 68160 | 726328 | 388904 | 0 | 419520 | 0 | 0 | 1047360 | 0 | 0 | 0 | 7495300 | 6846000 | 3336000 | 518545 | 2030710 | 597816 | 345600 | 0 | 254882 | 0 | 11952 | 791837 | 0 | 0 | 666100 | 124600 | 1724160 | 4088640 | 0 | 0 | 2600 | 705000 | 1387200 | 778200 | 569160 | 3641318 | 0 | 1206624 | 0 | 0 | 0 | 0 | 0 | 0 | 6543000 | 0 | 22896 | 0 | 10036 | 0 | 0 | 458400 | 0 | 756144 | 94770 | 184320 | 2050080 | 0 | 5722000 | 657600 | 18240 | 0 | 19160 | 122945 | 0 | 0 | 598500 | 1248240 | 192000 | 7363900 | 121920 | 32880 | 0 | 110400 | 0 | 13320 | 83811 | 2074560 | 0 | 6762300 | 0 | 0 | 11421817 | 555360 | 0 | 10207272 | 0 | 188600 |  | 22301818 | 0 | 7784064 | 0 | 182400 | 0 | 0 | 0 | 0 | 0 | 40875 | 2689000 | 235499 | 583200 | 0 | 0 | 0 | 0 | 0 | 10720 | 0 | 0 | 0 | 0 | 292460 | 0 | 0 | 165960 | 0 | 0 | 3987000 | 0 | 0 | 4350836 | 0 | 4108264 | 0 | 0 | 0 | 0 | 0 | 7614673 | 190560 | 0 | 0 | 0 | 280003 | 0 | 7888 | 0 | 19396800 | 3832009 | 0 | 0 | 6540 | 444240 | 503808 | 0 | 0 | 10000000 | 33474 | 4363600 | 21485454 | 180190 | 0 | 0 |  | 143576699 | 115071335 | 258648034 | 94217305 | 22301818 | 52051163 | 0 | 11814240 | 70654671 | 2644000 | 0 | 1591164 | 1724160 | 1094153 | 555360 | 0
Fuel Cost | 0 | 0 | 7404540 | 18152662.5 | 0 | 2356244.76 | 0 | 24634368 | 0 |  | 0 | 29041350 | 22962998.34 | 0 | 0 | 410211.22 | 19908579.15 | 0 | 0 | 0 | 118900.8 | 3122736 | 0 | 0 | 0 | 0 | 0 | 284468 | 359947.2 | 0 | 199350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1317030.78 | 16151678.18 | 0 | 0 | 0 |  | 1198934.4 | 12790636.08 | 6965270.64 | 0 | 8210006.4 | 0 | 0 | 0 | 0 | 0 | 0 | 20911887 | 20948760 | 11075520 | 1737125.75 | 6559193.3 | 2014639.92 | 1513728 | 0 | 1022076.82 | 0 | 214060.32 | 14300576.22 | 0 | 0 | 2477892 | 93450 | 11310489.6 | 12715670.4 | 0 | 0 | 0 | 2749500 | 5174256 | 3540810 | 2589678 | 12453307.56 | 0 | 6696763.2 | 0 | 0 | 0 | 0 | 0 | 0 | 20217870 | 0 | 17400.96 | 0 | 204734.4 | 0 | 0 | 8805864 | 0 | 13315695.84 | 0 | 3282739.2 | 35568888 | 0 | 15163300 | 12533856 | 342182.4 | 0 | 0 | 2010150.75 | 0 | 0 | 11437335 | 24228338.4 | 3419520 | 19587974 | 2081174.4 | 0 | 0 | 1852512 | 0 | 238028.4 | 0 | 37383571.2 | 0 | 20084031 | 0 | 0 | 79610064.49 | 0 | 0 | 0 | 0 | 0 |  | 62668108.58 | 0 | 22962988.8 | 0 | 3164640 | 0 | 0 | 0 | 0 | 0 | 727575 | 8497240 | 1116265.26 | 10054368 | 0 | 0 | 0 | 0 | 0 | 180203.2 | 0 | 0 | 0 | 0 | 5237958.6 | 0 | 0 | 125631.72 | 0 | 0 | 33650280 | 0 | 0 | 14357758.8 | 0 | 13680519.12 | 0 | 0 | 0 | 0 | 0 | 22234845.16 | 3254764.8 | 0 | 0 | 0 | 5577659.76 | 0 | 0 | 0 | 125691264 | 11917547.99 | 0 | 0 | 0 | 0 | 8741068.8 | 0 | 0 | 73000000 | 0 | 32508820 | 142018850.94 | 0 | 0 | 0 |  | 627074526.98 | 601368358.53 | 1228442885.51 | 292345554.05 | 62668108.58 | 132703847.64 | 0 | 214424741.37 | 486479279.43 | 0 | 0 | 28510864.84 | 11310489.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 138 | 180 | 0 | 22 | 0 | 321 | 0 |  | 0 | 300 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 186 | 0 | 85 | 36 | 10 | 0 | 5 | 0 | 0 | 16 | 0 | 0 | 32 | 6 | 70 | 160 | 0 | 0 | 0 | 29 | 58 | 25 | 10 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 68 | 0 | 235 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 34 | 38 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 86 | 0 | 285 | 0 | 0 | 384 | 13 | 0 | 305 | 0 | 17 |  | 924 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 160 | 0 | 0 | 130 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 180 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 365 | 0 | 150 | 821 | 2 | 0 | 0 |  | 9490 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 61 | 0 | 382 | 0 |  | 0 | 420 | 300 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 226 | 0 | 0 | 0 | 0 | 12 | 71 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 305 | 305 | 0 | 83 | 85 | 37 | 52 | 0 | 40 | 0 | 0 | 8 | 0 | 0 | 32 | 11 | 74 | 165 | 0 | 0 | 0 | 30 | 58 | 50 | 39 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 91 | 0 | 0 | 77 | 0 | 240 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 77 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 325 | 0 | 0 | 501 | 26 | 0 | 500 | 0 | 0 |  | 922 | 0 | 355 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 158 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 347 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 900 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 455 | 0 | 200 | 1060 | 0 | 0 | 0 |  | 11633 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 400 | 0 |  | 0 | 450 | 300 | 80 | 64 | 55 | 320 | 0 | 0 | 85 | 85 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 64 | 51 | 45 | 38 | 18 | 0 | 40 | 0 | 0 | 0 | 300 | 300 | 140 | 0 | 86 | 37 | 0 | 0 | 51 | 0 | 40 | 52 | 0 | 0 | 32 | 12 | 144 | 160 | 0 | 0 | 0 | 30 | 58 | 52 | 39 | 163 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 300 | 0 | 0 | 120 | 0 | 149 | 0 | 25 | 100 | 150 | 350 | 80 | 52 | 100 | 0 | 52 | 35 | 110 | 114 | 85 | 25 | 350 | 70 | 0 | 162 | 35 | 0 | 35 | 0 | 115 | 35 | 330 | 163 | 0 | 612 | 40 | 0 | 584 | 0 |  |  | 944 | 0 | 380 | 0 | 98 | 0 | 0 | 0 | 40 | 60 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 90 | 35 | 0 | 45 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 380 | 73 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 110 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 500 | 0 | 307 | 748 | 0 | 0 |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 50 | 0 | 400 | 0 | 0 | 0 | 450 | 300 | 50 | 64 | 55 | 320 | 0 | 0 | 70 | 82 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 75 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 48 | 34 | 35 | 18 | 6 | 0 | 40 | 0 | 0 |  | 300 | 280 | 140 | 0 | 85 | 10 | 0 | 0 | 20 | 0 | 40 | 50 | 0 | 0 | 32 | 12 | 146 | 150 | 0 | 0 | 1.6 | 30 | 58 | 50 | 39 | 163 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 270 | 0 | 0 | 97 | 0 | 96 | 20 | 25 | 17 | 150 | 320 | 68 | 52 | 51 | 5 | 52 | 35 | 110 | 0 | 42 | 25 | 330 | 55 | 50 | 72 | 35 | 0 | 35 | 35 | 34 | 35 | 300 | 54 | 0 | 612 | 40 | 0 | 584 | 0 | 70 |  | 944 | 0 | 360 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 16 | 0 | 0 | 0 | 32 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 155 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 94 | 0 | 70 | 0 | 8 | 113 | 1100 | 110 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 307 | 748 | 130 | 0 | [5 empty] | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 300 | 0 | 0 | 0 | 350 | 275 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 125 | 0 | 85 | 37 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 52 | 166 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 303 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 250 | 0 | 0 | 430 | 0 | 0 | 350 | 0 | 2 | 0 | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 157 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 110 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 409 | 1 | 150 | 476 | 3 | 0 | 0 | 0 |  |  |  | 146268468 | 22301818 | 0 | 70654671 | 13405404 | 1724160 | 1094153 | 555360 | 2644000 |  |  | 258648034
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [8 empty] | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [10 empty] | 146.2685 | 22.3018 | 0 | 70.6547 | 13.4054 | 1.7242 | 1.0942 | 0.55536 | 2.644
| Minimum Generation |  | 9490 | 9:00
| Highest Generation |  | 12671 | 1:00 |  |  |  |  | 4500 | [124 empty] | 0 | [72 empty] | 258.648
| Day Peak Generation |  | 9490 | 9:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 11633 | 21:00 |  |  |  |  | 10500 | [197 empty] | 202699852
| HVDC Max Flow |  | 926 | 10:00 | [202 empty] | 202.6999
| HVDC EvPeak Flow |  | 922 | 21:00
| Load factor L.F |  | 85.05% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-19
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9490 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 9072
Evening Peak Generation : |  |  | 11633 | MW Hour : | 21:00 | Available Max Generation : |  | 16012
E.P. Demand (at gen end) : |  |  | 11633 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12500
Maximum Generation : |  |  | 12671 | MW Hour : | 1:00 | Reserve(Generation end) |  | 3512
Total Gen. (MKWH) : |  |  | 258.648 | System Load Factor : | 85.05% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 178 | MW at | 24:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-19
Actual : |  | 82.48 | Ft.(MSL) , | Rule curve : | 80.86 | Ft.( MSL )
Gas Consumed : |  | Total = | 1064.82 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 425049401.69
: |  |  | Coal : | 486479279.43 | Oil : | 242935606.21 | Total : | 1154464287.33
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5310.1633 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1463.5928 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2051.5561 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1784.4161 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1467.6227 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1092.2058 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 611.5045 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 510.265 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 997.9738 |  |  | 0 | 0%
Total |  | 0 |  | 15289.3002 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:13 | Dohazari 132/33kV S/S Power Transformer -T-2 LT is restored.
| 08:13 | Dohazari 132/33kV S/S Power Transformer -T-2 HT is restored.
09:38 | 17:22 | Bogura-Sirajganj 230 kV Ckt-2 Forced S/D from Sirajgonj 230 end Due to Emergency Maintenance Work.
10:11 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 11:04 | Mymensingh-Netrokona 132kV Ckt-1 is restored.
11:31 | 12:20 | Chandpur 132/33kV S/S 402T LT Forced S/D Due to 33 Kv bus coupler clamp connector red Hot maintenance work by PDB authority. | [5 empty] | 15 MW load interrup.
11:57 | 12:16 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing Secondary Distance Protection
A-Phase Auto Reclosed Relay(Red Led) Earth Fault Protection(Yellow LED) relays.
15:01 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
15:09 | 16:46 | Sylhet (South) S/S Trafo-1 LT Forced S/D Due to red hot maintenance at 33 kv feeder. | [5 empty] | 1.5 MW load interrup.
15:10 | 16:45 | Sylhet (South) S/S Trafo-1 HT Forced S/D Due to red hot
maimtenance at 33 kv feeder
15:22 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
17:04 | 21:01 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Tripped showing CONTROL PANEL relays Due to TRIP.
17:04 | 21:01 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Tripped.
| 21:55 | Ashuganj CCPP 225 MW Synchronized
22:06 | 22:37 | Hathazari-Kaptai 132kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing Simens relays Due to rain, Thunderstome. | [5 empty] | 8 MW load interrup in
22:06 | 22:37 | Hathazari-Kaptai 132kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing Simens relays. | [5 empty] | Hathazari 230/132/33 kV end.
22:24 | 23:29 | Madanganj 132/33kV S/S GT-2 LT Forced S/D
22:26 | 23:15 | Madanganj 132/33kV S/S GT-2 HT Forced S/D
01:30 | 01:44 | Kurigram-Rangpur 132kV Ckt-1 Tripped from Rangpur 132/33kV end showing Distance protection p443 relays Due to R phase
Y phase zone 1 Block air signal show.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 1726000 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4079250
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 61 | 616818
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 382 | 8553600
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9132500 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6714327 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 23281 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 321 | 6527403 | Machine problem.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 6624 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 160800 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 18050 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 19680 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 16 | 417720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 198600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 198300 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 10036 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 91 | 756144 | Low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 18240 | Reserve
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 121920 | Reserve
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 83811
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Reserve
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 500 | 10207272
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0
| Dhaka area Total |  |  |  | 5634 | 2303 | 49590376
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 69537 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 94770
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 115 | 2644000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 226 | 5063222
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Reserve
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 726328
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 388904 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 184320 | Reserve
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 1047360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 419520 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19160
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 122945 | Reserve
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 192000 | Reserve
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 110400 | Reserve
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 501 | 11421817
| Cox's Bazar Wind |  | IPP | 66 | 60 | 26 | 555360 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 0 | 0
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 188600
| Chattogram area Total |  |  |  | 4457 | 1012 | 23248243
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 0 | 3336000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7495300 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6846000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 325 | 6762300 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 597816 | Machine problem.
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 52 | 345600
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 83 | 518545 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 40 | 254882
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 11952 | Reserve
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2030710 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 77 | 2050080 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 74 | 1724160
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 32 | 666100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 791837 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 11 | 124600 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 598500 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 1248240 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 2074560 | Fuel shortage
| Cumilla Area Total |  |  |  | 2875 | 1624 | 37477182
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 165 | 4088640 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 2600
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 8 | 458400 | Low demand
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 35 | 657600 | Low demand
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 32880
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 68160 | Engine problem
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 13320 | Reserve
| Mymensingh Area Total |  |  |  | 646 | 220 | 5321600
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 705000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1387200 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3641318
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 778200
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 569160 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 22896 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1206624
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Reserve
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6543000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 240 | 5722000
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7363900
| Sylhet Area Total |  |  |  | 2331 | 1221 | 27939298
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22301818
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 182400 | Low demand
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 7784064 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 40875 | Reserve
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 190560 | Low demand
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 444240
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 455 | 10000000
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1765 | 40943957
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 583200
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 235499
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2689000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 19396800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 3832009
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 4363600
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 0
| Barisal Area Total |  |  |  | 2236 | 1442 | 31100108
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 158 | 4350836 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 161 | 4108264
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 347 | 7614673 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 292460 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 165960 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 10720 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 6540
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1060 | 21485454
| Rajshahi Area Total |  |  |  | 3381 | 1770 | 38034907
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 3987000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 280003 | Low demand
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 7888
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 503808 | Low demand
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 33474
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 180190
| Rangpur Area Total |  |  |  | 950 | 276 | 4992363
| Total |  |  |  | 26364 | 11633 | 258648034
| Eastern Grid Total |  |  |  | 15943 | 6380 | 143576699
| Western Grid Total |  |  |  | 10421 | 5253 | 115071335
| National Grid Total |  |  |  | 26364 | 11633 | 258648034
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-06-18
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
| (a) ENTIRE EASTERN GRID: |  | 9700.03 | MW | (b) ENTIRE WESTERN GRID: |  | 4958.43 | MW
| i) Dhaka area |  |  | 5397.37 |  | MW | i) Khulna area | 1988.8 | MW
| ii) Chattogram area |  |  | 1379.4 |  | MW | ii) Barishal area | 511.4 | MW
| iii) Cumilla area |  |  | 1432 |  | MW | iii) Rajshahi area | 1743.6 | MW
| iv) Mymensingh area |  |  | 1010 |  | MW | iv) Rangpur area | 916 | MW
| v) Sylhet area |  |  | 692 |  | MW
|  | System Total Demand at Evening Peak Hour (a + b) = |  |  | 14658.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
| AKS | 0 | 00:00 | 67 | Jamalpur | 128 | 04:00 | 133 | Rahim | 0 | 00:00
| AKSML | 2 | 08:00 | 68 | Jashore | 151 | 00:00 | 134 | Rajbari | 88 | 00:00
| Aftabnagar | 34 | 00:00 | 69 | Jhenaidah | 146 | 23:00 | 135 | Rajendrapur | 84 | 01:00
| Agargaon | 92 | 00:00 | 70 | Joydebpur | 96 | 00:00 | 136 | Rajshahi | 139 | 00:00
| Agrabad | 82 | 00:00 | 71 | Joypurhat | 65 | 00:00 | 137 | Rajshahi-230 | 84 | 23:00
| Amnura | 78 | 21:00 | 72 | Juldah | 15 | 00:00 | 138 | Ramganj | 122 | 22:00
| Ashuganj | 67 | 00:00 | 73 | KSRM | 3.01 | 12:00 | 139 | Rampur | 28 | 00:00
| BIPTC | N/A | N/A | 74 | Kabirpur | 141 | 23:00 | 140 | Rangamati | 14 | 04:00
| BSRM | 2.5 | 19:00 | 75 | Kachua | 99 | 21:00 | 141 | Rangpur | 111 | 00:00
| Bagerhat | 100 | 23:00 | 76 | Kallyanpur | 102 | 00:00 | 142 | Ruppur | 4.8 | 09:00
| Bakulia | 79 | 00:00 | 77 | Kalurghat | 20 | 00:00 | 143 | SSM | 0 | 00:00
| Banani | 20.6 | 21:00 | 78 | Kamrangirchar | 29 | 00:00 | 144 | Saidpur | 80 | 00:00
| Bangabhaban | 3 | 00:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 145 | 02:00
| Barapukuria | 55 | 00:00 | 80 | Kazla | 74 | 18:30 | 146 | Satmasjid | 98 | 00:00
| Barguna | 26 | 00:00 | 81 | Keranigonj | 70 | 00:00 | 147 | Savar | 108 | 23:00
| Barishal | 123 | 23:00 | 82 | Khagrachori | 30 | 00:00 | 148 | SevenRings | 0.75 | 10:00
| Barishal-230 | 122 | 23:00 | 83 | Khulna | 66 | 23:00 | 149 | ShahCement | 2 | 08:00
| Baroaulia | 44 | 15:00 | 84 | Khulshi | 117 | 19:00 | 150 | Shahjadpur | 87 | 00:00
| Baroirhat | 74 | 00:00 | 85 | Kishoreganj | 158 | 01:00 | 151 | Shahjibazar | 101 | 00:00
| Bashundhara | 128 | 00:00 | 86 | Kodda | 130 | 21:00 | 152 | Shahmirpur | 44 | 00:00
| BashundharaCement | 0 | 00:00 | 87 | Kulaura | 42 | 00:00 | 153 | Shariatpur | 106 | 00:00
| Beanibazar | 52 | 18:30 | 88 | Kurigram | 52 | 00:00 | 154 | Sherpur | 126 | 00:00
| Benapole | 71 | 00:00 | 89 | Kushtia | 144 | 23:00 | 155 | Shikalbaha | 24 | 00:00
| Bhaluka | 102 | 00:00 | 90 | Lalbag | 37 | 01:00 | 156 | Shikalbaha-230 | N/A | N/A
| Bhandaria | 66 | 22:00 | 91 | Lalmonirhat | 42 | 00:00 | 157 | Shitalakhya | 61 | 01:00
| Bhangura | 44 | 00:00 | 92 | MI_Cement | 0.9 | 20:00 | 158 | Sholosohor | 35 | 19:30
| Bheramara(GK) | 77 | 23:00 | 93 | Madanganj | 20 | 00:00 | 159 | Shyampur | 48 | 00:00
| Bhulta | 110 | 21:00 | 94 | Madaripur | 136 | 00:00 | 160 | Siddhirganj | 78 | 00:00
| Bog-Sherpur | 58 | 00:00 | 95 | Madartek | 82.95 | 00:00 | 161 | Sirajganj | 116 | 00:00
| Bogura | 145 | 00:00 | 96 | Madunaghat | 56 | 19:00 | 162 | Sonargaon | 58 | 00:00
| Borhanuddin | 90 | 04:00 | 97 | Magura | 77 | 00:00 | 163 | Sreemongol | 62 | 00:00
| Brahmanbaria | 194 | 02:00 | 98 | Mahasthangarh | 82 | 00:00 | 164 | Sreepur | 36 | 00:00
| Cantonment | 110 | 00:00 | 99 | Manikganj | 109 | 22:00 | 165 | Srinagar | 54.45 | 00:00
| Chandpur | 88 | 00:00 | 100 | Maniknagar | 56 | 00:00 | 166 | Sunamganj | 42 | 00:00
| Chandraghona | 37 | 01:00 | 101 | Matarbari | 50 | 22:00 | 167 | Sylhet | 50 | 17:00
| Chapai | 73 | 00:00 | 102 | Matuail | 36 | 00:00 | 168 | Sylhet-132 | 72 | 22:00
| Charsaidpur | 4 | 00:00 | 103 | Millgate | 63 | 00:00 | 169 | TK | 36.7 | 00:00
| Chauddagram | 77 | 00:00 | 104 | Mirpur | 125 | 00:00 | 170 | Tangail | 202 | 00:00
| Chhatak | 20 | 00:00 | 105 | Mirsorai | 5 | 02:00 | 171 | Thakurgaon | 91 | 00:00
| Chowmuhani | 234 | 00:00 | 106 | Mirzapur | 36 | 00:00 | 172 | Tongi | 75 | 00:00
| Chuadanga | 114 | 02:00 | 107 | Mithapukur | 54 | 00:00 | 173 | Ullahpara | 27 | 00:00
| Coxsbazar | 119 | 21:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 56 | 00:00
| Cumilla(N) | 171 | 00:00 | 109 | Mogbazar | 82.4 | 00:00 | 175 | Uttara | 63 | 00:00
| Cumilla(S) | 178 | 00:00 | 110 | Mongla | 18 | 19:30 | 176 | UttaraNew | 57 | 00:00
| Daudkandi | 154 | 00:00 | 111 | Motijheel | 30 | 00:00 | 177 | Zigatola | 76 | 00:00
| Dhaka | 18 | 00:00 | 112 | Munshiganj | 112 | 23:00
| Dhamrai | 86 | 00:00 | 113 | Mymensingh | 200 | 01:00
| Dhanmondi | 73.8 | 00:00 | 114 | Naogaon | 138 | 01:00
| Dohazari | 110 | 00:00 | 115 | Narail | 69 | 00:00
| Faridpur | 181 | 23:00 | 116 | Narinda | 42 | 00:00
| Fatullah | 46 | 00:00 | 117 | Narshingdi | 147 | 00:00
| Fenchuganj | 34 | 00:00 | 118 | Natore | 162 | 01:00
| Feni | 117 | 00:00 | 119 | Nawabganj | 68.4 | 23:00
| GPH | 10 | 19:30 | 120 | Netrakona | 120 | 00:00
| Ghatail | 64 | 00:00 | 121 | New | 24.8 | 00:00
| Ghorashal | 49 | 03:00 | 122 | Niamatpur | 88 | 00:00
| Goalpara | 38 | 23:00 | 123 | Noapara | 46 | 00:00
| Gollamari | 90 | 00:00 | 124 | PHP | 3 | 12:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 393 | 18:30 | 283 | 03:00 | Kaliakoir | 391 | 18:30 | 378 | 00:00
| Ashuganj | 405 | 7:00 | 392 | 20:00 | Madunaghat_I | 404 | 06:00 | 391 | 15:00
| Bhulta | 406 | 06:00 | 327 | 16:00 | Meghnaghat | 388 | 17:00 | 376 | 00:00
| Bibiana | 405 | 18:30 | 394 | 02:00 | Payra | 413 | 18:30 | 401 | 00:00
| BIPTC | 403 | 06:00 | 393 | 16:00 | Rahanpur | 413 | 08:00 | 392 | 00:00
| Bogura | 408 | 08:00 | 382 | 00:00 | Rampal | 403 | 18:00 | 383 | 00:00
| Gopalganj | 402 | 18:30 | 383 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 234 | 18:00 | 225 | 00:00 | Hasnabad | 237 | 17:00 | 226 | 00:00
| AKSML | 233 | 18:00 | 215 | 13:00 | Hathazari | 232 | 18:00 | 218 | 00:00
| Aminbazar | 234 | 17:00 | 225 | 00:00 | Ishurdi | 237 | 18:30 | 224 | 22:00
| Ashuganj | 240 | 17:00 | 229 | 00:00 | Jhenaidah | 226 | 18:30 | 210 | 00:00
| Ashuganj-400 | 235 | 6:00 | 227 | 19:00 | Kaliakoir | 236 | 18:30 | 226 | 00:00
| Baghabari | 234 | 17:00 | 223 | 00:00 | Keranigonj | 235 | 18:00 | 225 | 00:00
| Barapukuria | 225 | 05:00 | 210 | 00:00 | Khulna(S) | 231 | 18:30 | 214 | 00:00
| Barapukuria-230 | 225 | 05:00 | 210 | 00:00 | Madunaghat_I | 234 | 17:00 | 220 | 00:00
| Barishal | 236 | 18:30 | 227 | 00:00 | Maniknagar | 236 | 17:00 | 229 | 00:00
| Bheramara | 239 | 02:00 | 223 | 22:00 | Meghnaghat | 243 | 17:00 | 235 | 00:00
| Bhulta | 237 | 17:00 | 230 | 00:00 | Meghnaghat-400 | 239 | 17:00 | 231 | 00:00
| Bibiana | 233 | 18:30 | 224 | 02:00 | Mirsorai | 234 | 18:00 | 221 | 00:00
| BIPTC | 239 | 08:00 | 222 | 22:00 | Rajshahi | 234 | 08:00 | 219 | 22:00
| Bogura | 230 | 07:00 | 215 | 00:00 | Rampal | 229 | 09:00 | 215 | 00:00
| Bogura-400 | 230 | 07:00 | 216 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 239 | 08:00 | 232 | 00:00 | Rampura | 235 | 18:00 | 227 | 00:00
| BSRM | 234 | 18:00 | 221 | 13:00 | Shikalbaha | 229 | 18:00 | 215 | 14:00
| Cumilla(N) | 235 | 18:00 | 224 | 01:00 | Shyampur | 236 | 17:00 | 227 | 00:00
| Fenchuganj | 238 | 18:00 | 229 | 01:00 | Siddhirganj | 238 | 17:00 | 226 | 10:00
| Ghorashal | 235 | 00:00 | 234 | 18:30 | Sirajgonj | 239 | 07:00 | 231 | 00:00
| Ghorashal-230 | 236 | 17:00 | 228 | 00:00 | Sreepur | 235 | 09:00 | 225 | 02:00
| GPH | 232 | 18:00 | 218 | 13:00 | Tongi | 236 | 18:30 | 226 | 00:00
| Haripur | 236 | 18:00 | 228 | 00:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 07:00 | 131 | 00:00 | Kushtia | 135 | 18:00 | 126 | 00:00
| Agargaon | 137 | 18:00 | 130 | 00:00 | Lalbag | 134 | 17:00 | 129 | 00:00
| Agrabad | 134 | 19:30 | 124 | 13:00 | Lalmonirhat | 132 | 07:00 | 121 | 19:30
| AKS | 131 | 18:00 | 123 | 13:00 | Madanganj | 135 | 17:00 | 130 | 00:00
| Aminbazar | 137 | 17:00 | 132 | 14:00 | Madaripur | 131 | 08:00 | 123 | 00:00
| Amnura | 134 | 06:00 | 119 | 00:00 | Madartek | 135 | 08:00 | 131 | 00:00
| Ashuganj | 140 | 08:00 | 135 | 00:00 | Madunaghat | 136 | 18:00 | 126 | 13:00
| Bagerhat | 132 | 18:00 | 115 | 23:00 | Magura | 136 | 09:00 | 122 | 23:00
| Bakulia | 135 | 19:30 | 126 | 13:00 | Mahasthangarh | 133 | 08:00 | 121 | 00:00
| Banani | 135 | 06:00 | 130 | 00:00 | Manikganj | 130 | 18:30 | 124 | 02:00
| Bangabhaban | 134 | 08:00 | 130 | 00:00 | Maniknagar | 134 | 08:00 | 130 | 00:00
| Barapukuria | 142 | 05:00 | 128 | 19:30 | Matarbari | 124 | 18:00 | 111 | 00:00
| Barguna | 132 | 10:00 | 124 | 00:00 | Matuail | 136.1 | 18:00 | 131 | 00:00
| Barishal | 134 | 11:00 | 124 | 00:00 | Millgate | 136 | 19:30 | 129 | 00:00
| Barishal-230 | 134 | 18:30 | 125 | 00:00 | Mirpur | 135 | 18:30 | 129 | 00:00
| Baroaulia | 136 | 18:00 | 126 | 10:00 | Mirzapur | 131 | 18:00 | 124 | 00:00
| Baroirhat | 132 | 18:00 | 116 | 13:00 | Mithapukur | 133 | 08:00 | 122 | 00:00
| Bashundhara | 136 | 17:00 | 129 | 01:00 | MI_Cement | 138 | 19:00 | 131 | 00:00
| BashundharaCement | 135 | 18:00 | 125 | 17:00 | Modern | 135 | 18:00 | 124 | 13:00
| Beanibazar | 132 | 03:00 | 118 | 00:00 | Mogbazar | 138 | 16:00 | 132 | 00:00
| Benapole | 133 | 18:00 | 116 | 23:00 | Mongla | 131 | 09:00 | 116 | 23:00
| Bhaluka | 133 | 09:00 | 123 | 00:00 | Motijheel | 134 | 08:00 | 130 | 00:00
| Bhandaria | 129 | 18:30 | 115 | 00:00 | Munshiganj | 136 | 18:00 | 130 | 00:00
| Bhangura | 136 | 05:00 | 128 | 00:00 | Mymensingh | 133 | 07:00 | 118 | 01:00
| Bheramara | 136 | 08:00 | 130 | 00:00 | Naogaon | 130 | 18:30 | 118 | 00:00
| Bheramara(GK) | 136 | 18:00 | 129 | 23:00 | Narail | 138 | 18:30 | 122 | 23:00
| Bhulta | 130 | 17:00 | 124 | 00:00 | Narinda | 134 | 08:00 | 130 | 00:00
| Bog-Sherpur | 133 | 18:30 | 123 | 00:00 | Narshingdi | 132 | 18:00 | 123 | 00:00
| Bogura | 134 | 18:00 | 124 | 00:00 | Natore | 133 | 08:00 | 124 | 00:00
| Bogura-230 | 134 | 07:00 | 124 | 00:00 | Nawabganj | 133 | 06:00 | 128 | 00:00
| Brahmanbaria | 137 | 16:00 | 121 | 00:00 | Netrakona | 132 | 08:00 | 121 | 00:00
| Cantonment | 136 | 17:00 | 130 | 00:00 | New | 136 | 17:00 | 130 | 00:00
| Chandpur | 131 | 18:00 | 118 | 13:00 | Niamatpur | 135 | 18:30 | 125 | 00:00
| Chandraghona | 136 | 18:00 | 127 | 00:00 | Noapara | 135 | 18:00 | 120 | 23:00
| Chapai | 131 | 18:00 | 120 | 00:00 | Pabna | 135 | 08:00 | 126 | 00:00
| Charsaidpur | 136 | 17:00 | 130 | 00:00 | Palashbari | 131 | 07:00 | 118 | 00:00
| Chauddagram | 134 | 18:00 | 119 | 00:00 | Panchagarh | 137 | 03:00 | 121 | 15:00
| Chhatak | 131 | 10:00 | 118 | 00:00 | Patuakhali | 133 | 11:00 | 125 | 00:00
| Chowmuhani | 127 | 18:00 | 113 | 13:00 | Payra | 135 | 17:00 | 130 | 00:00
| Chuadanga | 130 | 18:00 | 113 | 23:00 | PHP | 133 | 18:00 | 116 | 01:00
| Coxsbazar | 124 | 07:00 | 113 | 00:00 | Postogola | 138 | 18:00 | 133 | 00:00
| Cumilla(N) | 136 | 18:00 | 126 | 00:00 | Purbachal | 136 | 18:00 | 129 | 00:00
| Cumilla(S) | 135 | 18:00 | 124 | 00:00 | Purbasadipur | 133 | 06:00 | 122 | 15:00
| Daudkandi | 133 | 17:00 | 122 | 00:00 | Rahanpur | 136 | 08:00 | 128 | 00:00
| Dhaka | 135 | 06:00 | 131 | 00:00 | Rahim | 136 | 18:00 | 131 | 00:00
| Dhamrai | 139 | 17:00 | 132 | 00:00 | Rajbari | 131 | 18:30 | 120 | 00:00
| Dhanmondi | 136 | 18:00 | 131.8 | 00:00 | Rajendrapur | 133 | 20:00 | 124 | 03:00
| Dohazari | 132 | 18:00 | 122 | 00:00 | Rajshahi | 133 | 08:00 | 125 | 00:00
| Faridpur | 130 | 07:00 | 122 | 00:00 | Rajshahi-230 | 134 | 08:00 | 113 | 00:00
| Fatullah | 137 | 17:00 | 132 | 00:00 | Ramganj | 126 | 18:00 | 111 | 13:00
| Fenchuganj | 136 | 09:00 | 126 | 00:00 | Rampur | 135 | 18:00 | 125 | 14:00
| Feni | 132 | 18:00 | 115 | 13:00 | Rampura | 135 | 06:00 | 131 | 00:00
| Ghatail | 130 | 17:00 | 119 | 01:00 | Rangamati | 135 | 18:00 | 124 | 00:00
| Ghorashal | 141 | 08:00 | 137 | 00:00 | Rangpur | 146 | 05:00 | 120 | 00:00
| Goalpara | 136 | 18:30 | 123 | 01:00 | Ruppur | 137 | 05:00 | 130 | 00:00
| Gollamari | 136 | 18:30 | 124 | 00:00 | Saidpur | 134 | 04:00 | 122 | 19:30
| Gopalganj | 132 | 18:00 | 121 | 00:00 | Satkhira | 131 | 18:00 | 121 | 22:00
| Gopalganj-400 | 133 | 18:00 | 125 | 00:00 | Satmasjid | 136 | 09:00 | 130 | 00:00
| Gulshan | 135 | 18:00 | 130 | 00:00 | Savar | 135 | 18:00 | 129 | 00:00
| Halishahar | 135 | 18:00 | 126 | 12:00 | SevenRings | 142 | 17:00 | 136 | 00:00
| Haripur | 136 | 17:00 | 131 | 00:00 | ShahCement | 136 | 17:00 | 130 | 00:00
| HaripurSBU | 136 | 18:00 | 131 | 00:00 | Shahjadpur | 140 | 07:00 | 133 | 00:00
| Hasnabad | 138 | 16:00 | 133 | 00:00 | Shahjibazar | 134 | 13:00 | 125 | 05:00
| Hathazari | 137 | 18:00 | 127 | 00:00 | Shahmirpur | 136 | 18:00 | 126 | 13:00
| Ishurdi | 138 | 18:30 | 130 | 22:00 | Shariatpur | 131 | 09:00 | 119 | 00:00
| Jaldhaka | 137 | 04:00 | 121 | 19:30 | Sherpur | 130 | 06:00 | 116 | 01:00
| Jamalpur | 132 | 06:00 | 121 | 00:00 | Shikalbaha | 125 | 18:00 | 116 | 13:00
| Jashore | 134 | 18:00 | 118 | 23:00 | Shikalbaha-230 | 137 | 18:00 | 127 | 14:00
| Jhenaidah | 138 | 18:30 | 124 | 23:00 | Shitalakhya | 136 | 18:00 | 131 | 00:00
| Jhenaidah-230 | 138 | 18:30 | 125 | 00:00 | Sholosohor | 135 | 18:00 | 125 | 13:00
| Joydebpur | 139 | 17:00 | 132 | 00:00 | Shyampur | 135 | 01:00 | 134 | 00:00
| Joypurhat | 129 | 18:30 | 115 | 00:00 | Shyampur-230 | 137 | 17:00 | 130 | 03:00
| Juldah | 135 | 18:00 | 126 | 17:00 | Siddhirganj | 136 | 18:00 | 131 | 00:00
| Kabirpur | 135 | 17:00 | 127 | 00:00 | Sirajganj | 134 | 18:30 | 124 | 00:00
| Kachua | 131 | 18:00 | 120 | 12:00 | Sonargaon | 135 | 18:30 | 129 | 22:00
| Kaliakoir | 141 | 17:00 | 123 | 04:00 | Sreemongol | 133 | 15:00 | 121 | 00:00
| Kallyanpur | 134 | 08:00 | 128 | 00:00 | Sreepur | 134 | 10:00 | 127 | 01:00
| Kalurghat | 136 | 18:00 | 126 | 01:00 | Srinagar | 134 | 18:00 | 128 | 00:00
| Kamrangirchar | 135 | 18:30 | 128 | 00:00 | SSM | 140 | 18:00 | 128 | 02:00
| Kaptai | 135 | 6:00 | 130 | 19:00 | Sunamganj | 131 | 09:00 | 112 | 01:00
| Kazla | 134 | 08:00 | 130 | 00:00 | Sylhet | 130 | 09:00 | 120 | 00:00
| Keranigonj | 135 | 18:00 | 129 | 00:00 | Sylhet-132 | 131 | 09:00 | 121 | 00:00
| Khagrachori | 136 | 18:00 | 125 | 00:00 | Tangail | 130 | 16:00 | 119 | 00:00
| Khulna | 135 | 18:00 | 121 | 23:00 | Thakurgaon | 133 | 03:00 | 120 | 15:00
| Khulna(S) | 136 | 18:00 | 124 | 00:00 | TK | 137 | 18:30 | 125 | 13:00
| Khulshi | 134 | 18:00 | 124 | 13:00 | Tongi | 137 | 17:00 | 131 | 00:00
| Kishoreganj | 135 | 10:00 | 124 | 00:00 | Ullahpara | 137 | 18:00 | 127 | 00:00
| Kodda | 138 | 17:00 | 125 | 05:00 | Ullon | 135 | 17:00 | 131 | 00:00
| KSRM | 135 | 17:00 | 126 | 12:00 | Uttara | 136 | 17:00 | 129 | 00:00
| Kulaura | 133 | 16:00 | 125 | 00:00 | UttaraNew | 136 | 18:00 | 128 | 00:00
| Kurigram | 144 | 05:00 | 120 | 00:00 | Zigatola | 135 | 18:00 | 128 | 00:00

## L-Curve
Date | 2024-06-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 178 | 6482 | 5337 | 11819 |  |  |  | QF-LDC-11
0:30 | 267 | 6713.5 | 5531.5 | 12245 | Date: | 2024-06-18
1:00 | 356 | 6945 | 5726 | 12671
1:30 | 381 | 6874 | 5530.5 | 12404.5
2:00 | 406 | 6803 | 5335 | 12138
2:30 | 404 | 6775.5 | 5158.5 | 11934 | [5 empty] | Gen. at Eve. Peak | 11633 | 11633 MW (21:00 )
3:00 | 402 | 6748 | 4982 | 11730 | [6 empty] | 21:00
3:30 | 399 | 6733 | 4868.5 | 11601.5 | [5 empty] | Gen. at Day Peak | 9490 | 9490 MW (09:00 )
4:00 | 396 | 6718 | 4755 | 11473 | [6 empty] | 9:00
4:30 | 414 | 6690.5 | 4692 | 11382.5 | [5 empty] | Highest Generation | 12671
5:00 | 432 | 6663 | 4629 | 11292 | [6 empty] | 1:00
5:30 | 472 | 6385 | 4497.5 | 10882.5
6:00 | 512 | 6107 | 4366 | 10473
6:30 | 496 | 5938.5 | 4330.5 | 10269
7:00 | 480 | 5770 | 4295 | 10065
7:30 | 471 | 5669 | 4209 | 9878
8:00 | 462 | 5568 | 4123 | 9691
8:30 | 474 | 5480.5 | 4110 | 9590.5
9:00 | 486 | 5393 | 4097 | 9490
9:30 | 488 | 5239.5 | 4038.5 | 9278
10:00 | 490 | 5086 | 3980 | 9066
10:30 | 531 | 5047 | 3999 | 9046
11:00 | 572 | 5008 | 4018 | 9026
11:30 | 558 | 5069 | 4064.5 | 9133.5
12:00 | 544 | 5130 | 4111 | 9241
12:30 | 561 | 5226.5 | 4233.5 | 9460
13:00 | 578 | 5323 | 4356 | 9679
13:30 | 541 | 5482.5 | 4443 | 9925.5
14:00 | 504 | 5642 | 4530 | 10172
14:30 | 486 | 5622 | 4493 | 10115
15:00 | 468 | 5602 | 4456 | 10058
15:30 | 439 | 5590.5 | 4403.5 | 9994
16:00 | 410 | 5579 | 4351 | 9930
16:30 | 458 | 5455.5 | 4293 | 9748.5
17:00 | 506 | 5332 | 4235 | 9567
17:30 | 507 | 5217.5 | 4113 | 9330.5
18:00 | 508 | 5103 | 3991 | 9094
18:30 | 549 | 5469 | 4324.5 | 9793.5
19:00 | 590 | 5835 | 4658 | 10493
19:30 | 340 | 6196 | 5191 | 11387
20:00 | 350 | 6105 | 5265 | 11370 |  |  |  | Executive Engineer
20:30 | 323 | 6242.5 | 5259 | 11501.5 |  |  |  | Network Operation Division
21:00 | 296 | 6380 | 5253 | 11633
21:30 | 287 | 6454 | 5259.5 | 11713.5
22:00 | 278 | 6528 | 5266 | 11794 |  |  |  |  | Page 6 of 7
22:30 | 289 | 6505.5 | 5331 | 11836.5
23:00 | 300 | 6483 | 5396 | 11879
23:30 | 239 | 6482.5 | 5366.5 | 11849
24:00 | 178 | 6482 | 5337 | 11819
11633 MW (21:00 )
9490 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-18 |  | Energy |  | 258648034
[15 empty] | 2024-06-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4029 | 925 | 2598 | 0 | 714 | 3219 | 78 | 0 | 159 | 76 | 0 | 21 | 0
0:30 | 4158.5 | 923 | 2519 | 0 | 819.5 | 3482 | 95 | 0 | 142 | 83 | 0 | 23 | 33 |  |  | Date: | 43999
1:00 | 4288 | 921 | 2440 | 0 | 925 | 3745 | 112 | 0 | 125 | 90 | 0 | 25 | 66
1:30 | 4279.5 | 920.5 | 2433 | 0 | 834.5 | 3601 | 112 | 0 | 113 | 88 | 0 | 23 | 62.5 | [9 empty] | Total Energy | 258.648 | 258.648 | Total Energy Gen 258.648 MKWHr Energy Not Served 0.466 MKWHr Energy Requirement 259.114 MKWHr
2:00 | 4271 | 920 | 2426 | 0 | 744 | 3457 | 112 | 0 | 101 | 86 | 0 | 21 | 59 | [9 empty] | Energy not Served | 0.46621 | 0.46621
2:30 | 4270 | 920 | 2438.5 | 0 | 677 | 3323 | 113.5 | 0 | 83 | 85 | 0 | 24 | 58 | [9 empty] | Energy Requirement | 259.1142 | 259.1142
3:00 | 4269 | 920 | 2451 | 0 | 610 | 3189 | 115 | 0 | 65 | 84 | 0 | 27 | 57
3:30 | 4269 | 920 | 2446.5 | 0 | 591 | 3086.5 | 115 | 0 | 65 | 84.5 | 0 | 24 | 58 | [8 empty] | Shortage
4:00 | 4269 | 920 | 2442 | 0 | 572 | 2984 | 115 | 0 | 65 | 85 | 0 | 21 | 59
4:30 | 4265 | 921 | 2408.5 | 0 | 568 | 2939.5 | 115 | 0 | 64.5 | 83.5 | 0 | 17.5 | 57
5:00 | 4261 | 922 | 2375 | 0 | 564 | 2895 | 115 | 0 | 64 | 82 | 0 | 14 | 55
5:30 | 4124 | 922 | 2266 | 0 | 525.5 | 2792.5 | 115 | 0 | 34 | 80 | 5 | 18.5 | 54.5
6:00 | 3987 | 922 | 2157 | 0 | 487 | 2690 | 115 | 0 | 4 | 78 | 10 | 23 | 54
6:30 | 3960.5 | 922.5 | 2085.5 | 0 | 430.5 | 2624.5 | 115 | 0 | 2 | 76 | 25 | 27.5 | 48.5 | [7 empty] | Coal
7:00 | 3934 | 923 | 2014 | 0 | 374 | 2559 | 115 | 0 | 0 | 74 | 40 | 32 | 43
7:30 | 3883.5 | 924 | 1957 | 0 | 349.5 | 2502 | 115 | 0 | 0 | 73 | 47 | 27 | 21.5 | [6 empty] | Oil
8:00 | 3833 | 925 | 1900 | 0 | 325 | 2445 | 115 | 0 | 0 | 72 | 54 | 22 | 0
8:30 | 3809 | 924.5 | 1857 | 0 | 289 | 2432.5 | 115 | 0 | 0 | 71 | 75 | 17.5 | 0
9:00 | 3785 | 924 | 1814 | 0 | 253 | 2420 | 115 | 0 | 0 | 70 | 96 | 13 | 0
9:30 | 3688 | 925 | 1771.5 | 0 | 238 | 2373 | 114.5 | 0 | 0 | 68 | 83.5 | 16.5 | 0
10:00 | 3591 | 926 | 1729 | 0 | 223 | 2326 | 114 | 0 | 0 | 66 | 71 | 20 | 0
10:30 | 3533.5 | 925.5 | 1737 | 0 | 239.5 | 2327.5 | 113.5 | 0 | 0 | 67 | 83 | 19.5 | 0
11:00 | 3476 | 925 | 1745 | 0 | 256 | 2329 | 113 | 0 | 0 | 68 | 95 | 19 | 0
11:30 | 3527 | 924.5 | 1781 | 0 | 250 | 2327.5 | 113 | 0 | 0 | 68 | 123 | 19.5 | 0
12:00 | 3578 | 924 | 1817 | 0 | 244 | 2326 | 113 | 0 | 0 | 68 | 151 | 20 | 0
12:30 | 3706 | 923 | 1813 | 0 | 233.5 | 2422.5 | 113 | 0 | 0 | 70 | 163 | 16 | 0
13:00 | 3834 | 922 | 1809 | 0 | 223 | 2519 | 113 | 0 | 0 | 72 | 175 | 12 | 0
13:30 | 3834 | 922 | 1809 | 0 | 223 | 2519 | 113 | 0 | 0 | 72 | 175 | 12 | 0
14:00 | 3834 | 922 | 1809 | 0 | 223 | 2519 | 113 | 0 | 0 | 72 | 175 | 12 | 0
14:30 | 3794 | 922 | 1967 | 0 | 236.5 | 2585 | 113.5 | 0 | 0 | 73 | 161.5 | 16 | 12.8925
15:00 | 3754 | 922 | 2125 | 0 | 250 | 2651 | 114 | 0 | 0 | 74 | 148 | 20 | 25.785
15:30 | 3719 | 922 | 2108.5 | 0 | 265 | 2652.5 | 114 | 0 | 3.5 | 69 | 111.5 | 29 | 46.3175
16:00 | 3684 | 922 | 2092 | 0 | 280 | 2654 | 114 | 0 | 7 | 64 | 75 | 38 | 66.85
16:30 | 3645.5 | 921.5 | 1958.5 | 0 | 289 | 2639.5 | 114 | 0 | 36 | 53 | 59.5 | 32 | 33.425
17:00 | 3607 | 921 | 1825 | 0 | 298 | 2625 | 114 | 0 | 65 | 42 | 44 | 26 | 0
17:30 | 3523 | 921.5 | 1744.5 | 0 | 298 | 2552 | 114.5 | 0 | 67.5 | 50 | 26.5 | 33 | 0
18:00 | 3439 | 922 | 1664 | 0 | 298 | 2479 | 115 | 0 | 70 | 58 | 9 | 40 | 0
18:30 | 3509.5 | 921.5 | 1879 | 0 | 468 | 2666 | 115 | 0 | 135 | 65 | 4.5 | 30 | 0
19:00 | 3580 | 921 | 2094 | 0 | 638 | 2853 | 115 | 0 | 200 | 72 | 0 | 20 | 0
19:30 | 3670 | 922 | 2155 | 0 | 784 | 3426 | 115 | 0 | 221 | 70 | 0 | 24 | 0
20:00 | 3692 | 923 | 2246 | 0 | 648 | 3462 | 115 | 0 | 190 | 70 | 0 | 24 | 0
20:30 | 3807.5 | 922.5 | 2356 | 0 | 656 | 3374 | 115 | 0 | 173.5 | 72 | 0 | 25 | 0
21:00 | 3923 | 922 | 2466 | 0 | 664 | 3286 | 115 | 0 | 157 | 74 | 0 | 26 | 0
21:30 | 3950 | 922.5 | 2484 | 0 | 700 | 3288.5 | 115 | 0 | 158 | 74 | 0 | 21.5 | 0
22:00 | 3977 | 923 | 2502 | 0 | 736 | 3291 | 115 | 0 | 159 | 74 | 0 | 17 | 0
22:30 | 3988.5 | 924 | 2550 | 0 | 742.5 | 3282.5 | 97 | 0 | 159 | 73 | 0 | 20 | 0
23:00 | 4000 | 925 | 2598 | 0 | 749 | 3274 | 79 | 0 | 159 | 72 | 0 | 23 | 0
23:30 | 4014.5 | 925 | 2598 | 0 | 731.5 | 3246.5 | 78.5 | 0 | 159 | 74 | 0 | 22 | 0 |  |  | Max Temp. in Dhaka |  | 32.0°C
24:00 | 4029 | 925 | 2598 | 0 | 714 | 3219 | 78 | 0 | 159 | 76 | 0 | 21 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 258.648 MKWHr Energy Not Served 0.466 MKWHr Energy Requirement 259.114 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 1704000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 37 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 38 | 38 | 38 | 38 | 39 | 39 | 39 | 40 |  | 40 | 40 | 40 | 40 | 40 | 39 | 38 | 940000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [15 empty] | 1 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 69537
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 8 | 13 | 3 | 5 | 10 | 11 | 15 | 11 | 8 | 3 | 1 | [8 empty] | 94770
6 | Sikalbaha 225MW CCPP (Gas) | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 221 | 220 | 219 | 216 | 216 | 216 | 205 | 205 | 205 | 205 | 217 |  | 220 | 221 | 224 | 226 | 227 | 224 | 225 | 5063222
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 34 | 4 | [13 empty] | 51 | 51 | 51 | 34 | 34 | 34 | 34 | 388904
12 | Hathazari 100 MW peaking PP | 39 | 31 | 31 | 31 | 30 | 0 | [9 empty] | 7 | 65 | 70 |  | 71 | 71 | 71 | 71 | 73 | 73 | 73 | 726328
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [19 empty] | 15 | 15 |  |  |  |  | 0 | 11952
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 240 | 240 | 240 | 280 | 280 | 250 |  | 250 | 250 | 250 | 321 | 321 | 322 | 323 | 6527403
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 10036
19 | Ashuganj 195 MW PP (APSCL-United) | [12 empty] | 26 | 55 | 55 | 55 | 55 | 8 |  | 8 | 55 | 55 | 83 | 83 | 8 | 8 | 518545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 190 | 190 | 190 | 190 | 190 | 140 | 140 | 140 | 138 | 120 | [15 empty] | 0 | 1726000
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4079250
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 590 | 590 | 591 | 590 | 590 | 480 | 400 | 370 | 384 | 332 | 332 | 330 | 391 | 500 | 500 | 500 | 500 | 453 |  | 463 | 491 | 500 | 501 | 501 | 477 | 519 | 11421817
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 5 | 5 | 5 | 5 | 0 | 0 | 10 | 10 | 10 |  | 28 | 34 | 37 | 37 | 37 | 34 | 37 | 597816
33 | Ashuganj 225 MW CCPP | 216 | 216 | 215 | 215 | 218 | 217 | 186 | 186 | 186 | 191 | 186 | 207 | 206 | 173 | 173 | [8 empty] | 54 | 115 | 102 | 3336000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 305 | 305 | 270 | 275 | 275 | 270 | 280 |  | 270 | 295 | 300 | 305 | 310 | 315 | 330 | 6846000
| Ashuganj 450 MW CCPP(North) | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 285 | 285 | 285 | 285 | 320 | 315 | 300 | 255 | 255 | 280 | 295 |  | 285 | 305 | 305 | 305 | 310 | 320 | 330 | 7495300
| Ashuganj 420 MW CCPP(East) | 260 | 260 | 260 | 260 | 260 | 260 | 285 | 285 | 285 | 250 | 250 | 250 | 310 | 315 | 300 | 300 | 250 | 250 |  | 285 | 320 | 325 | 325 | 327 | 230 | 230 | 6762300
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 7 | 40 | 45 | 52 | 50 | 44 | 30 | 345600
36 | Chandpur 150 MW CCPP | 85 | 85 | 85 | 86 | 86 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 85 | 85 |  | 86 | 85 | 85 | 85 | 86 | 86 | 86 | 2030710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 405 | 405 | 405 | 405 | 376 | 350 | 326 | 321 | 288 | 269 | 270 | 291 | 300 | 300 | 355 | 384 | 303 |  | 356 | 356 | 356 | 382 | 404 | 404 | 404 | 8553600
| Meghnaghat Unique power | 570 | 570 | 570 | 570 | 570 | 450 | 400 | 350 | 305 | 255 | 255 | 250 | 250 | 400 | 400 | 400 | 300 | 250 |  | 450 | 450 | 450 | 500 | 500 | 584 | 584 | 10207272
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 380 | 320 | 300 | 300 | 300 | 300 | 300 | 350 | 350 | 350 | 400 | 350 | 300 |  | 350 | 350 | 350 | 420 | 420 | 450 | 450 | 9132500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 201 | 201 | 200 | 200 | 200 | 140 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 191 | 174 | 174 | 174 | 174 |  | 173 | 162 | 165 | 165 | 165 | 162 | 162 | 4088640
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 7 | 12 | 6 | 4 | 0 | [8 empty] | 32880
44 | Fenchugonj CCPP Phase-1 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 705000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1387200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 56 | 56 | 56 | 56 | 56 | 61 | 61 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 57 | 57 | 61 | 61 | 61 | 61 | 1206624
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [16 empty] | 0 | 22896
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 25 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 778200
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 300 | 290 | 290 | 290 | 290 | 255 | 250 |  | 255 | 255 | 250 | 260 | 290 | 290 | 290 | 6543000
| Bibiyana South 400 MW | 300 | 300 | 300 | 300 | 294 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 300 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7363900
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 5 | 17 |  |  |  |  | 0 | 19680
59 | Tangail Palli Power Gen 22 MW | 6 | [18 empty] | 1 | 8 | 10 | 12 | 12 | 12 | 12 | 68160
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 90 | 86 | 84 | 85 | 82 | 78 | 74 | 72 | 70 | 66 | 68 | 68 | 72 | 74 | 74 | 64 | 42 | 58 |  | 72 | 70 | 70 | 74 | 74 | 72 | 76 | 1724160
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 16 | 34 | 38 | 42 |  | 42 | 42 | 42 | 31 | 31 | 31 | 42 | 1047360
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 0 |  | 0 | 666100
68 | Cumilla 25 MW PP (Summit) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 0 |  | 6 | 6 | 6 | 11 | 0 | 12 | 12 | 124600
69 | Summit Ashulia | 12 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 10 | 11 | 11 | 11 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 265800
70 | Summit Madhabdi | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 0 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 151920
71 | Maona 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 198600
72 | Rupganj 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 198300
73 | Ghorashal 108 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  |  | 19 | 42 | 42 | 12 | 12 |  | 12 | 42 | 56 | 61 | 67 | 65 | 65 | 616818
| Feni Lanka Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 598500
| Chowmuhani 113 MW | 48 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 36 | 37 | 37 | 36 | 40 | 47 | 57 | 65 | 74 |  | 75 | 75 | 77 | 77 | 77 | 77 | 77 | 1248240
| Manikgonj 162MW PP(MPGL) | [25 empty] | 0 | 0
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP
79 | Kodda 150 MW PP | 16 | [18 empty] | 16 | 32 | 32 | 16 | 16 | 16 | 16 | 160800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 50 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 33 |  | 33 | 8 | 8 | 8 | 51 | 51 | 50 | 791837
| Gazipur 100 MW PP | [19 empty] | 17 | 17 |  |  |  |  | 0 | 18240
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 3 | 4 | 1 | 4 | 1 | 2 | 1 | 1 | [9 empty] | 19160
| Jodiac Power | [25 empty] | 0 | 0
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit) | [25 empty] | 0 | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 272 | 270 | 275 | 276 | 240 | 250 | 265 | 272 | 265 | 295 | 290 | 307 | 303 | 296 | 300 | 253 | 266 | 300 |  | 288 | 257 | 285 | 300 | 302 | 297 | 305 | 6714327
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 51 | 24 | [17 empty] | 17 | 17 |  |  |  |  | 0 | 121920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima) | 36 | 36 | 36 | 33 | 36 | 36 | 10 | 10 | 10 |  |  |  |  | 18 | 33 | 33 | 5 | 5 |  | 22 | 36 | 33 | 39 | 39 | 39 | 34 | 569160
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [11 empty] | 5 | 20 | 40 | 40 | 43 | 43 | 254882
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 8 | 8 |  |  |  |  | 0 | 6624
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | 35 | 38 | 38 | 37 | 37 | 12 | 12 | 12 | 11 | [5 empty] | 17 | 37 | 38 | 38 |  | 35 | 35 | 16 |  |  |  | 0 | 419520
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 6 | 15 |  |  |  |  | 0 | 23281
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 17 |  |  |  |  | 0 | 18050
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3641318
102 | Sarishabari 3 MW Solar Plant | [7 empty] | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2600
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 55 | 55 | 55 | 55 | 55 | 55 | 8 | 8 | [9 empty] | 2 |  | 16 | 24 | 35 | 8 | 8 | 8 | 8 | 458400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 95 | 78 | 45 | 24 | 17 | 17 | 17 | [12 empty] | 24 | 80 | 72 | 91 | 79 | 85 | 85 | 756144
115 | Juldah 100 MW PP Unit-3 (Acorn) | 24 | 24 | 24 | 24 | 24 | 24 | 12 | 12 | [11 empty] | 10 | 12 |  |  |  |  | 0 | 184320
116 | Chandpur 200 MW (Desh energy) | 132 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 68 |  | 68 | 68 | 68 | 77 | 99 | 102 | 45 | 2050080
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 237 | 235 | 235 | 235 | 236 | 239 | 239 | 239 | 239 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5722000
| Jamalpur 115 MW PP (United) | 65 | 65 | 65 | 65 | 65 | 45 | 24 | 8 | [9 empty] | 2 |  | 16 | 27 | 45 | 35 | 35 | 35 | 35 | 657600
| Anwara 300 MW PP (United) | 15 | 15 | 15 | 15 | 15 | 15 | [13 empty] | 15 | 15 |  |  |  |  | 0 | 122945
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 12 | [11 empty] | 12 | 12 |  |  |  |  | 0 | 192000
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 0 | [13 empty] | 2 | 17 |  |  |  |  | 0 | 110400
| Bhairob 54.5 MW | [19 empty] | 2 | 17 |  |  |  |  | 0 | 13320
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 1 | 2 | 5 | 11 | 11 | 6 | 17 | 12 | 9 | 4 | 1 | [8 empty] | 83811
| Chandpur 115(Doreen) | 105 | 115 | 104 | 104 | 103 | 104 | 99 | 84 | 86 | 85 | 86 | 74 | 54 | 53 | 53 | 52 | 52 | 52 |  | 76 | 85 | 85 | 96 | 115 | 105 | 102 | 2074560
Kanchan Purbachal Power Generation Ltd.
| Mirsharai 150 MW (Oil) | [20 empty] | 0 |  |  |  |  | 0 | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 25 | 21 | 27 | 21 | 14 | 23 | 32 | 22 | 13 | 20 | 19 | 20 | 12 | 21 | 20 | 38 | 26 | 40 |  | 20 | 24 | 24 | 26 | 17 | 23 | 21 | 555360
| Sonagazi 75 MW Solar Plant | [5 empty] | 3 | 16 | 27 | 17 | 27 | 14 | 9 | 32 | 19 | 21 | 6 | 6 | [9 empty] | 188600
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 6945 | 6803 | 6748 | 6718 | 6663 | 6107 | 5770 | 5568 | 5393 | 5086 | 5008 | 5130 | 5323 | 5642 | 5602 | 5579 | 5332 | 5103 |  | 5835 | 6196 | 6105 | 6380 | 6528 | 6483 | 6482 | 143576699
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 32 | 32 | 16 | [16 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 182400
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 17 | [17 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 27 | 190560
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 5 | 15 | 14 | 60 | 27 | 47 | 64 | 63 | 46 | 48 | 21 | 16 | 4 | [8 empty] | 444240
131 | Rampal 1320 MW (BIFPCL) | 368 | 367 | 370 | 370 | 379 | 378 | 367 | 363 | 365 | 361 | 362 | 362 | 406 | 413 | 410 | 412 | 412 | 363 |  | 445 | 506 | 510 | 455 | 453 | 508 | 507 | 10000000
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3832009
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | [14 empty] | 48 | 48 | 64 | 96 | 96 | 110 | 110 | 583200
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 216 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 170 | 170 | 170 | 170 | 170 | 140 |  | 203 | 250 | 250 | 200 | 200 | 230 | 230 | 4363600
136 | Barisal 1 MW Solar Plant
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 124 | 124 | 126 | 126 | 126 | 100 |  | 126 | 126 | 126 | 126 | 126 | 126 | 130 | 2689000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 235499
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | [24 empty] | 0 | 40875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 921 | 920 | 920 | 920 | 922 | 922 | 923 | 925 | 924 | 926 | 925 | 924 | 922 | 922 | 922 | 922 | 921 | 922 |  | 921 | 922 | 923 | 922 | 923 | 925 | 925 | 22301818
147 | Bheramara 410 MW CCPP | 340 | 345 | 345 | 345 | 340 | 345 | 300 | 260 | 260 | 220 | 220 | 220 | 300 | 390 | 355 | 345 | 300 | 250 |  | 250 | 250 | 250 | 355 | 360 | 365 | 380 | 7784064
148 | Payra 1320 MW | 1160 | 1000 | 900 | 780 | 760 | 700 | 660 | 580 | 540 | 500 | 500 | 500 | 570 | 600 | 580 | 580 | 550 | 530 |  | 560 | 860 | 870 | 900 | 900 | 940 | 1040 | 19396800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3987000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 6540
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 214 | 214 | 160 | 160 | 150 | 130 | 133 | 140 | 140 | 154 | 190 | 176 | 178 | 157 | 158 |  | 158 | 156 | 156 | 158 | 158 | 178 | 183 | 4350836
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 197 | 170 | 170 | 170 | 170 | 150 | 150 | 150 | 150 | 140 | 140 | 140 | 190 | 172 | 163 | 162 | 159 | 150 |  | 150 | 150 | 150 | 161 | 163 | 178 | 166 | 4108264
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 327 | 315 | 335 | 328 | 294 | 296 | 311 | 270 | 260 | 260 | 260 | 300 | 300 | 350 | 348 | 294 | 296 | 250 |  | 333 | 290 | 327 | 347 | 347 | 414 | 414 | 7614673
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 165960
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | 36 | 36 | [17 empty] | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 292460
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 11 | 16 | [5 empty] | 10720
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP | 0 | 0 | [19 empty] | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | [16 empty] | 4 |  | 34 | 34 | 40 | 34 | 34 | 34 | 34 | 280003
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 |  |  |  |  | 1 | 1 | 1 | 2 | 2 | 1 | 0 | [8 empty] | 7888
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | [17 empty] | 55 | 70 | 70 | 72 | 72 | 72 | 72 | 503808
| Intraco Solar 30 MW | [7 empty] | 0 |  |  | 2 | 8 | 5 | 6 | 4 | 8 | 3 | 0 | [8 empty] | 33474
| Adani Power Jharkhanda Ltd | 1217 | 1124 | 1018 | 934 | 856 | 822 | 822 | 822 | 821 | 823 | 825 | 824 | 822 | 821 | 821 | 822 | 823 | 823 |  | 1012 | 1149 | 1162 | 1060 | 1067 | 949 | 753 | 21485454
178 | Teesta Solar Limited | [7 empty] | 2 | 2 | 6 | 11 | 43 | 43 | 30 | 36 | 14 | 6 | 3 | [8 empty] | 180190