## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-20 | Thursday
|  | Date (day): | 2024-06-20 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14615.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16048 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-19 | 2024-06-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 7 | 53 | 50 | 70 | 38
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 282 | 413 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 80
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 258 | 291 | 300 | 300 | 35 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 64 | 64 |  |  | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 25 | 50 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 70 | 85 |  | 15 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 329 | 320 | 320
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 82 | 85 |  | 17 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 100 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 17 | 15 | 33 | 33 |  | 47 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 8 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 8 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 270 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 17 | 96 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 52 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 55 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 72 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 6 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 300 | 584 | 300 | 300 | 284
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 300 | 300 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 1704 | 2318 | 3567 | 3883 | 1053 | 859
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 0 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 18 | 32 |  | fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 115 | 115 | 115 | 115 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 175 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 51 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 48 | 64 | 34 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 34 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 35 | 45 | 55 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 25 | 25 | 75 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 40 | 40
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 20 | 18 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 35 | 35 | 19 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 25 | 25 | 75 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 35 | 35 | 81 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 380 | 300 | 612 | 612 |  | 612 | Unit-2 shut down
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 40 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 0 | 0 | 0 | 0 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 6 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 769 | 807 | 1663 | 1810 | 992 | 993
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 141 | 195 | 140 | 140 |  | 71 | ST Under maint.
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 295 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 280 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 260 | 285 | 300 | 330 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 0 | 0 | 37 |  | 8 | engine problem
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 55 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 20 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150 |  | 0
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 |  | 12 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 85 | 85 | 86 |  | 77 | Machine problem
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 100 | 17 | 100 | 100 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 48 | 64 | 146 | 144
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 32 | 32
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 50 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 70 | 114 | 0
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 38 | 77 | 42 | 85 | 28 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 32 | 65 | 34 | 115
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1211 | 1642 | 1718 | 2088 | 378 | 181
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 166 | 202 | 170 | 200 | 2
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 0 | 97 | 120 | 80 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 8 | 68 | 80 | 35 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 2 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 6 | 12 | 10 |  | Fuel shortage
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 35 | 35
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 184 | 210 | 427.6 | 447 | 2 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 28 | 30 | 30 |  | 40 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 50 | 50 | 52
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 5 | 36 | 39 | 39 |  | 11 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 61 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas shortage
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 16 | 16 |  | 9 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 295 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 305 | 367 | 350 | 370
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 310 | 346 | 330 | 350
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1148 | 1404 | 1401 | 1443 | 231 | 448
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 928 | 922 | 944 | 944
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 20 | 98
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 360 | 300 | 340 | 70 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 73 | 32 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 22 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 358 | 358 | 500 | 500 |  | 617 | Unit-2 shut down
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1653 | 1640 | 1993 | 2095 | 684 | 666
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 3 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 760 | 1100 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 110 | 110 | 110 | 110 |  | 110 | GT-2 under maint
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 140 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 883 | 1150 | 1690 | 1946 | 115 | 174
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 15 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 45
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 156 | 161 | 150 | 160 | 50 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 161 | 165 | 150 | 160 | 60 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 298 | 350 | 350 | 380 | 34 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 36 | 14 |  | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 5 | 8 |  | 3 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 94 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 472 | 582 | 748 | 748 |  |  | Unit-2 shut down
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1092 | 1260 | 1713 | 1938 | 601 | 90
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 70 | 113
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 35 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 31 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 202 | 205 | 443 | 398 | 40 | 274
| Total |  |  |  |  | 27515 | 26364 | 8846 | 10636 | 14615.6 | 16048 | 4096 | 3685
A. |  | 2024-06-19 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 11550 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8846 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10636 | MW
3 | Day peak Generation : |  |  | 8846 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10232.19 | MW
4 | Evening peak Generation : |  |  | 10636 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 236.0602 | MKWHr | By Solar | 0.6687 | MKWHr
| By Gas : | 144.8631 | MKWHr |  | By Oil: | 7.2078 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 56.4089 | MKWHr |  | By Hydro: | 2.6726 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.5232 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4096 | MW | Dhaka | 2861.69 | 2861.69 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3685 | MW | Chittagong | 1243.5 | 1243.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7781 | MW | Khulna | 1412 | 1412 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1055.39 | MMCFD |  |  | Rajshahi | 1331 | 1331 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 416178544.202 | ii) Oil : | Taka | 130827511.25 | Comilla | 1127 | 1127 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 391686139.36 | Total | Taka | 938692194.812 | Mymensingh | 847 | 847 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1145.1 | MKWHr. | Sylhet | 373 | 373 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 100 | MW (W to E) at | 21:00 | hrs | Barisal | 391 | 391 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 100 | MW at | 21:00 | hrs | Rangpur | 646 | 646 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.2°C |  |  | Total | 10232.19 | 10232.19 |  | 0
B. |  | 2024-06-20 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 32.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16048 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 4048 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 245.2573 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8396 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3833 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.3325 | MKWHr. | iii) Maximum HVDC Flow : |  | 929 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.48 |  | (b) Today: | 82.87 |  | (c) Rule Curve: |  | 81.03
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-06-19 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 403 | 0 |  | 0 | 450 | 254 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 40 | 38 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 3 | 57 | 34 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 300 | 100 | 0 | 85 | 37 | 9 | 0 | 43 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 68 | 162 | 0 | 0 | 0 | 30 | 58 | 50 | 37 | 163 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 85 | 0 | 0 | 17 | 0 | 240 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 62 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 230 | 0 | 0 | 520 | 62 | 0 | 584 | 0 | 0 |  | 925 | 0 | 345 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 184 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 364 | 53 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1040 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 506 | 0 | 230 | 747 | 0 | 0 | 0 |  | 6286 | 5264 | 11550 | 3927 | 925 | 2468 | 0 | 666 | 3213 | 78 | 0 | 143 | 68 | 0 | 62 | 28.65 | 82.43
2:00 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 402 | 0 |  | 0 | 450 | 276 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 57 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 300 | 32 | 0 | 86 | 37 | 5 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 72 | 164 | 0 | 0 | 0 | 29 | 58 | 50 | 37 | 163 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 55 | 0 | 0 | 17 | 0 | 304 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 250 | 0 | 0 | 520 | 39 | 0 | 584 | 0 | 0 |  | 928 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 318 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 0 | 230 | 746 | 0 | 0 | 0 |  | 6249 | 4719 | 10968 | 3935 | 928 | 2440 | 0 | 395 | 2973 | 113 | 0 | 73 | 72 | 0 | 39 | 21.01 | 82.44
3:00 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 402 | 0 |  | 0 | 400 | 261 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 57 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 300 | 137 | 0 | 85 | 37 | 5 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 0 | 12 | 68 | 165 | 0 | 0 | 0 | 29 | 58 | 50 | 34 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 0 | 17 | 0 | 303 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 300 | 0 | 0 | 520 | 48 | 0 | 584 | 0 | 0 |  | 928 | 0 | 340 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 175 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 300 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 0 | 230 | 656 | 0 | 0 | 0 |  | 6237 | 4505 | 10742 | 4078 | 928 | 2306 | 0 | 343 | 2785 | 113 | 0 | 73 | 68 | 0 | 48 | 15.28 | 82.45
4:00 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 401 | 0 |  | 0 | 400 | 274 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 57 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 300 | 117 | 0 | 85 | 37 | 5 | 0 | 43 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 66 | 165 | 0 | 0 | 0 | 29 | 58 | 50 | 34 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 17 | 0 | 303 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 250 | 0 | 0 | 520 | 56 | 0 | 584 | 0 | 0 |  | 928 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 295 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 0 | 230 | 581 | 0 | 0 | 0 |  | 6194 | 4328 | 10522 | 4013 | 928 | 2314 | 0 | 350 | 2607 | 115 | 0 | 73 | 66 | 0 | 56 | 15.28 | 82.46
5:00 | 0 | 0 | 0 | 180 | 0 | 62 | 0 | 401 | 0 |  | 0 | 400 | 257 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 57 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 300 | 116 | 0 | 85 | 37 | 5 | 0 | 51 | 0 | 0 | 50 | 0 | 0 | 0 | 12 | 64 | 166 | 0 | 0 | 0 | 29 | 58 | 50 | 37 | 120 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 17 | 0 | 303 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 235 | 0 | 0 | 520 | 19 | 0 | 584 | 0 | 0 |  | 929 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 296 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 230 | 578 | 0 | 0 | 0 |  | 6107 | 4311 | 10418 | 4002 | 929 | 2304 | 0 | 324 | 2588 | 115 | 0 | 73 | 64 | 0 | 19 | 15.28 | 82.47
6:00 | 0 | 0 | 0 | 180 | 0 | 10 | 0 | 363 | 0 |  | 0 | 350 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 123 | 0 | 85 | 37 | 5 | 0 | 5 | 0 | 0 | 25 | 0 | 0 | 0 | 12 | 58 | 166 | 0 | 0 | 0 | 29 | 58 | 5 | 5 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 235 | 0 | 0 | 484 | 21 | 0 | 420 | 0 | 0 |  | 929 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 166 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 110 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 461 | 0 | 150 | 497 | 0 | 0 | 0 |  | 5446 | 4041 | 9487 | 3888 | 929 | 1984 | 0 | 168 | 2322 | 115 | 0 | 0 | 58 | 2 | 21 | 0 | 82.48
7:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 332 | 0 |  | 0 | 350 | 275 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 310 | 127 | 0 | 85 | 37 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 52 | 166 | 0 | 0 | 0 | 29 | 58 | 5 | 5 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 87 | 0 | 250 | 0 | 0 | 445 | 47 | 0 | 420 | 0 | 0 |  | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 155 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 110 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 406 | 0 | 150 | 476 | 0 | 0 | 0 |  | 5447 | 3868 | 9315 | 3856 | 928 | 1953 | 0 | 150 | 2207 | 115 | 0 | 0 | 52 | 7 | 47 | 0 | 82.49
8:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 300 | 0 |  | 0 | 350 | 275 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 270 | 125 | 0 | 85 | 37 | 5 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 52 | 166 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 303 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 250 | 0 | 0 | 430 | 0 | 0 | 350 | 0 | 2 |  | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 157 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 110 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 409 | 1 | 150 | 476 | 3 | 0 | 0 |  | 5193 | 3879 | 9072 | 3786 | 928 | 1877 | 0 | 95 | 2195 | 115 | 0 | 0 | 52 | 24 | 0 | 0 | 82.52
9:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 282 | 0 |  | 0 | 350 | 258 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 16 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 141 | 0 | 85 | 10 | 0 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 48 | 166 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 305 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 38 | 0 | 310 | 0 | 2 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 260 | 0 | 0 | 380 | 0 | 0 | 300 | 0 | 6 |  | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 156 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 110 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 358 | 1 | 150 | 472 | 31 | 0 | 0 |  | 5016 | 3830 | 8846 | 3726 | 928 | 1778 | 0 | 111 | 2070 | 115 | 0 | 0 | 48 | 70 | 0 | 0 | 82.55
10:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 282 | 0 |  | 0 | 300 | 293 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 16 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 270 | 121 | 0 | 85 | 0 | 0 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 48 | 166 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 307 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 41 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32 | 0 | 230 | 0 | 0 | 350 | 5 | 0 | 300 | 0 | 15 |  | 928 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 157 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 361 | 2 | 150 | 435 | 3 | 0 | 0 |  | 4939 | 3688 | 8627 | 3583 | 928 | 1800 | 0 | 131 | 1966 | 113 | 0 | 0 | 48 | 53 | 5 | 0 | 82.58
11:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 283 | 0 |  | 0 | 300 | 264 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 77 | 37 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 270 | 122 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 50 | 165 | 0 | 0 | 1 | 30 | 58 | 5 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 306 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 2 | 0 | 0 | 0 | 0 | 4 | 33 | 0 | 230 | 0 | 0 | 327 | 37 | 0 | 300 | 0 | 27 |  | 923 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 157 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 10 | 150 | 432 | 28 | 0 | 0 |  | 4937 | 3693 | 8630 | 3581 | 923 | 1775 | 0 | 129 | 1945 | 114 | 0 | 0 | 50 | 76 | 37 | 0 | 82.61
12:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 283 | 0 |  | 0 | 300 | 303 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 77 | 37 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 315 | 300 | 122 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 54 | 149 | 0 | 0 | 1 | 30 | 58 | 5 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 336 | 8 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 45 | 0 | 345 | 0 | 3 | 0 | 0 | 0 | 0 | 9 | 33 | 0 | 230 | 0 | 0 | 285 | 24 | 0 | 300 | 0 | 30 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 2 | 140 | 433 | 17 | 0 | 0 |  | 5039 | 3734 | 8773 | 3747 | 923 | 1829 | 0 | 128 | 1888 | 114 | 0 | 0 | 54 | 66 | 24 | 0 | 82.64
13:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 329 | 0 |  | 0 | 350 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 16 | 16 | 0 | 0 | 75 | 35 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 275 | 142 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 50 | 150 | 0 | 0 | 0 | 30 | 58 | 19 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1 | 0 | 17 | 0 | 306 | 8 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 4 | 0 | 0 | 0 | 0 | 18 | 41 | 0 | 260 | 0 | 0 | 350 | 30 | 0 | 350 | 0 | 71 |  | 923 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 166 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 357 | 3 | 140 | 432 | 40 | 0 | 0 |  | 5273 | 3882 | 9155 | 3880 | 923 | 1942 | 0 | 129 | 1949 | 110 | 0 | 0 | 50 | 142 | 30 | 0 | 82.66
14:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 350 | 0 |  | 0 | 350 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 75 | 35 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 142 | 0 | 85 | 0 | 0 | 0 | 3 | 0 | 0 | 8 | 0 | 0 | 0 | 10 | 36 | 148 | 0 | 0 | 0 | 30 | 58 | 30 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 4 | 0 | 17 | 0 | 307 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 38 | 0 | 320 | 0 | 2 | 0 | 0 | 0 | 0 | 6 | 65 | 0 | 285 | 0 | 0 | 350 | 12 | 0 | 350 | 0 | 8 |  | 922 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 177 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 500 | 110 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 358 | 2 | 140 | 431 | 30 | 0 | 0 |  | 5229 | 3850 | 9079 | 3885 | 922 | 1956 | 0 | 152 | 1949 | 110 | 0 | 0 | 36 | 57 | 12 | 0 | 82.61
15:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 337 | 0 |  | 0 | 300 | 270 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 75 | 38 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 144 | 0 | 85 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 162 | 0 | 0 | 0 | 28 | 58 | 30 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 17 | 0 | 306 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 320 | 0 | 3 | 0 | 0 | 0 | 0 | 8 | 40 | 0 | 285 | 0 | 0 | 350 | 4 | 0 | 320 | 0 | 11 |  | 923 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 156 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 110 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 360 | 1 | 140 | 434 | 16 | 0 | 0 |  | 5007 | 3764 | 8771 | 3806 | 923 | 1802 | 0 | 99 | 1954 | 113 | 0 | 0 | 26 | 44 | 4 | 0 | 82.7
16:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 300 | 0 |  | 0 | 300 | 278 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 75 | 39 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 40 | 0 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 171 | 0 | 0 | 0 | 28 | 58 | 30 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 17 | 0 | 306 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 320 | 0 | 2 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 285 | 0 | 0 | 350 | 6 | 0 | 260 | 0 | 4 |  | 923 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 157 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 110 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 356 | 0 | 140 | 430 | 12 | 0 | 0 |  | 4794 | 3645 | 8439 | 3631 | 923 | 1691 | 0 | 59 | 1946 | 114 | 0 | 0 | 40 | 29 | 6 | 0 | 82.72
17:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 300 | 0 |  | 0 | 300 | 243 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 180 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 52 | 0 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 141 | 0 | 0 | 0 | 28 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 306 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 4 | 16 | 0 | 250 | 0 | 0 | 320 | 0 | 0 | 255 | 0 | 3 |  | 923 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 110 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 358 | 0 | 140 | 432 | 3 | 0 | 0 |  | 4632 | 3561 | 8193 | 3464 | 923 | 1637 | 0 | 59 | 1920 | 115 | 0 | 0 | 50 | 25 | 0 | 0 | 82.74
18:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 282 | 0 |  | 0 | 300 | 244 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 16 | 0 | 0 | 76 | 40 | 0 | 0 | 0 | 188 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 66 | 0 | 85 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52 | 141 | 0 | 0 | 0 | 22 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 303 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 19 | 0 | 305 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 16 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 255 | 0 | 1 |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 358 | 0 | 140 | 431 | 2 | 0 | 0 |  | 4569 | 3489 | 8058 | 3384 | 922 | 1633 | 0 | 64 | 1879 | 116 | 0 | 0 | 52 | 8 | 0 | 0 | 82.75
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 362 | 0 |  | 0 | 340 | 312 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 345 | 335 | 212 | 0 | 85 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 62 | 201 | 0 | 0 | 0 | 28 | 58 | 30 | 30 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 8 | 40 | 0 | 368 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 34 | 71 | 12 | 370 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 49 | 0 | 320 | 0 | 0 | 270 | 4 | 0 | 350 | 0 | 0 |  | 922 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 148 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 360 | 0 | 141 | 513 | 0 | 0 | 0 |  | 5651 | 3694 | 9345 | 4047 | 922 | 1954 | 0 | 269 | 1972 | 115 | 0 | 0 | 62 | 0 | 4 | 0 | 82.78
19:30 | 0 | 0 | 0 | 180 | 0 | 36 | 0 | 412 | 0 |  | 0 | 420 | 260 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 8 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 186 | 11 | 85 | 0 | 0 | 0 | 18 | 0 | 0 | 1 | 0 | 0 | 0 | 12 | 58 | 202 | 0 | 0 | 0 | 28 | 58 | 40 | 39 | 163 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 100 | 0 | 307 | 8 | 0 | 34 | 0 | 16 | 0 | 0 | 70 | 77 | 25 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 75 | 0 | 390 | 17 | 0 | 270 | 12 | 0 | 400 | 0 | 0 |  | 921 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 163 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 358 | 0 | 140 | 608 | 0 | 0 | 0 |  | 5967 | 4216 | 10183 | 4075 | 921 | 2209 | 0 | 507 | 2269 | 115 | 0 | 17 | 58 | 0 | 12 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 407 | 0 |  | 0 | 420 | 278 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 6 | 174 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 187 | 55 | 85 | 0 | 0 | 0 | 21 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 62 | 202 | 0 | 0 | 0 | 28 | 58 | 49 | 39 | 163 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 84 | 0 | 306 | 8 | 0 | 27 | 0 | 16 | 0 | 0 | 70 | 76 | 25 | 310 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 68 | 0 | 285 | 17 | 0 | 270 | 20 | 0 | 390 | 0 | 0 |  | 921 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 359 | 0 | 140 | 618 | 0 | 0 | 0 |  | 5953 | 4206 | 10159 | 3973 | 921 | 2232 | 0 | 492 | 2327 | 115 | 0 | 17 | 62 | 0 | 20 | 0 | 82.77
21:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 413 | 0 |  | 0 | 420 | 291 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 17 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 280 | 195 | 55 | 85 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 64 | 202 | 0 | 0 | 0 | 28 | 58 | 50 | 36 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 100 | 0 | 367 | 8 | 0 | 17 | 0 | 15 | 0 | 0 | 70 | 77 | 25 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 300 | 40 | 0 | 584 | 0 | 0 |  | 922 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 358 | 0 | 140 | 582 | 0 | 0 | 0 |  | 6381 | 4255 | 10636 | 4160 | 922 | 2510 | 0 | 515 | 2310 | 115 | 0 | 0 | 64 | 0 | 40 | 0 | 82.78
22:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 403 | 0 |  | 0 | 420 | 290 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 17 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 275 | 195 | 55 | 87 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 64 | 203 | 0 | 0 | 0 | 28 | 58 | 50 | 39 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 100 | 0 | 370 | 8 | 0 | 17 | 0 | 15 | 0 | 0 | 70 | 77 | 25 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 300 | 42 | 0 | 584 | 40 | 0 |  | 921 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 110 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 360 | 0 | 140 | 587 | 0 | 0 | 0 |  | 6411 | 4300 | 10711 | 4149 | 921 | 2554 | 0 | 549 | 2317 | 115 | 0 | 0 | 64 | 0 | 42 | 0 | 82.79
23:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 401 | 0 |  | 0 | 420 | 295 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 8 | 16 | 0 | 0 | 75 | 40 | 0 | 0 | 11 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 42 | 0 | 0 | 0 | 300 | 290 | 200 | 55 | 87 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 68 | 203 | 0 | 0 | 0 | 28 | 58 | 50 | 39 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 100 | 0 | 380 | 24 | 0 | 0 | 0 | 15 | 0 | 0 | 70 | 77 | 25 | 352 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 65 | 0 | 297 | 0 | 0 | 300 | 35 | 0 | 584 | 65 | 0 |  | 922 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 165 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 110 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 358 | 0 | 140 | 580 | 0 | 0 | 0 |  | 6505 | 4309 | 10814 | 4233 | 922 | 2592 | 0 | 541 | 2308 | 115 | 0 | 0 | 68 | 0 | 35 | 0 | 82.8
24:00 | 0 | 0 | 0 | 180 | 0 | 60 | 0 | 401 | 0 |  | 0 | 420 | 298 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 8 | 16 | 0 | 0 | 75 | 38 | 0 | 0 | 8 | 175 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 280 | 195 | 55 | 87 | 0 | 0 | 0 | 51 | 0 | 0 | 23 | 0 | 0 | 0 | 12 | 68 | 203 | 0 | 0 | 0 | 28 | 58 | 50 | 36 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 65 | 0 | 371 | 24 | 0 | 0 | 0 | 15 | 0 | 0 | 114 | 78 | 25 | 345 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 90 | 0 | 285 | 0 | 0 | 300 | 36 | 0 | 584 | 64 | 0 |  | 922 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 110 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 359 | 0 | 140 | 580 | 0 | 0 | 0 |  | 6503 | 4306 | 10809 | 4174 | 922 | 2596 | 0 | 591 | 2309 | 113 | 0 | 0 | 68 | 0 | 36 | 0 | 82.81
KWH | 0 | 0 | 0 | 4315500 | 0 | 709863 | 0 | 8485200 | 0 |  | 0 | 9072500 | 6664815 | 0 | 0 | 0 | 7144639 | 0 | 0 | 0 | 0 | 84960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253800 | 162360 | 205600 | 297700 | 0 | 0 | 1728600 | 944000 | 0 | 0 | 60678 | 5064596 | 0 | 0 | 0 |  | 30960 | 324624 | 40592 | 0 | 87360 | 0 | 0 | 1079520 | 0 | 0 | 0 | 7457800 | 6837000 | 3137000 | 234181 | 2046370 | 321768 | 48000 | 0 | 571162 | 0 | 0 | 430584 | 0 | 0 | 0 | 233800 | 1332480 | 3927360 | 0 | 0 | 1600 | 677000 | 1385640 | 671400 | 475416 | 3357164 | 0 | 1240896 | 0 | 0 | 0 | 0 | 0 | 0 | 7086000 | 0 | 0 | 0 | 0 | 0 | 0 | 48000 | 0 | 395280 | 16065 | 116160 | 817440 | 0 | 7532000 | 322800 | 0 | 80290 | 15360 | 85309 | 0 | 0 | 448020 | 1122240 | 126720 | 7831900 | 0 | 28090 | 0 | 86564 | 0 | 0 | 79300 | 1471680 | 0 | 6472000 | 8364 | 0 | 9185453 | 523200 | 0 | 10106363 | 99723 | 190482 |  | 22383272 | 0 | 8181216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2592000 | 168036 | 281568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55606 | 0 | 0 | 138456 | 0 | 0 | 4114000 | 0 | 0 | 4108991 | 0 | 4153736 | 0 | 0 | 0 | 0 | 0 | 7739709 | 233280 | 0 | 0 | 0 | 46723 | 0 | 7459 | 0 | 16841100 | 2574955 | 0 | 0 | 5400 | 64800 | 402048 | 0 | 0 | 9941818 | 23839 | 3949100 | 12377455 | 236310 | 0 | 0 |  | 135439291 | 100620877 | 236060168 | 94204328 | 22383272 | 50658807 | 0 | 6693704 | 56408926 | 2672600 | 0 | 514146 | 1332480 | 668705 | 523200 | 0
Fuel Cost | 0 | 0 | 0 | 19203975 | 0 | 2711676.66 | 0 | 24437376 | 0 |  | 0 | 28850550 | 22793667.3 | 0 | 0 | 0 | 21791148.95 | 0 | 0 | 0 | 0 | 1649923.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1149241.32 | 16156061.24 | 0 | 0 | 0 |  | 544586.4 | 5716628.64 | 727002.72 | 0 | 1709635.2 | 0 | 0 | 0 | 0 | 0 | 0 | 20807262 | 20921220 | 10414840 | 784506.35 | 6609775.1 | 1084358.16 | 210240 | 0 | 2290359.62 | 0 | 0 | 7776347.04 | 0 | 0 | 0 | 175350 | 8741068.8 | 12214089.6 | 0 | 0 | 0 | 2640300 | 5168437.2 | 3054870 | 2163142.8 | 11481500.88 | 0 | 6886972.8 | 0 | 0 | 0 | 0 | 0 | 0 | 21895740 | 0 | 0 | 0 | 0 | 0 | 0 | 922080 | 0 | 6960880.8 | 0 | 2068809.6 | 14182584 | 0 | 19959800 | 6152568 | 0 | 1440402.6 | 0 | 1394802.15 | 0 | 0 | 8561662.2 | 21782678.4 | 2256883.2 | 20832854 | 0 | 0 | 0 | 1452543.92 | 0 | 0 | 0 | 26519673.6 | 0 | 19221840 | 117765.12 | 0 | 64022607.41 | 0 | 0 | 0 | 0 | 0 |  | 62896994.32 | 0 | 24134587.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8190720 | 796490.64 | 4854232.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 995903.46 | 0 | 0 | 104811.192 | 0 | 0 | 34722160 | 0 | 0 | 13559670.3 | 0 | 13831940.88 | 0 | 0 | 0 | 0 | 0 | 22599950.28 | 3984422.4 | 0 | 0 | 0 | 930722.16 | 0 | 0 | 0 | 109130328 | 8008110.05 | 0 | 0 | 0 | 0 | 6975532.8 | 0 | 0 | 72575271.4 | 0 | 29420795 | 81814977.55 | 0 | 0 | 0 |  | 510802637.98 | 499527619.952 | 1010330257.932 | 288537739.622 | 62896994.32 | 127640804.58 | 0 | 121620288.11 | 391686139.36 | 0 | 0 | 9207223.14 | 8741068.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 7 | 0 | 282 | 0 |  | 0 | 350 | 258 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 6 | 8 | 16 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 141 | 0 | 85 | 10 | 0 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 48 | 166 | 0 | 0 | 0 | 30 | 58 | 5 | 5 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 305 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 38 | 0 | 310 | 0 | 2 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 260 | 0 | 0 | 380 | 0 | 0 | 300 | 0 | 6 |  | 928 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 156 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 110 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 358 | 1 | 150 | 472 | 31 | 0 | 0 |  | 8846 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 413 | 0 |  | 0 | 420 | 291 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 6 | 8 | 8 | 0 | 0 | 75 | 40 | 0 | 0 | 17 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 280 | 195 | 55 | 85 | 0 | 0 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 64 | 202 | 0 | 0 | 0 | 28 | 58 | 50 | 36 | 163 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 24 | 100 | 0 | 367 | 8 | 0 | 17 | 0 | 15 | 0 | 0 | 70 | 77 | 25 | 346 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 300 | 40 | 0 | 584 | 0 | 0 |  | 922 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 110 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 358 | 0 | 140 | 582 | 0 | 0 | 0 |  | 10636 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 400 | 0 |  | 0 | 450 | 300 | 80 | 64 | 55 | 320 | 0 | 0 | 85 | 85 | 150 | 25 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 75 | 40 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 64 | 51 | 45 | 38 | 18 | 0 | 40 | 0 | 0 | 0 | 300 | 300 | 140 | 0 | 86 | 37 | 0 | 0 | 51 | 0 | 40 | 52 | 0 | 0 | 32 | 12 | 144 | 200 | 0 | 0 | 0 | 30 | 58 | 52 | 39 | 163 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 300 | 0 | 0 | 120 | 0 | 149 | 0 | 25 | 100 | 150 | 370 | 80 | 52 | 100 | 0 | 52 | 35 | 110 | 114 | 85 | 25 | 350 | 70 | 0 | 162 | 35 | 0 | 35 | 0 | 115 | 35 | 330 | 163 | 0 | 612 | 40 | 0 | 300 | 300 |  |  | 944 | 0 | 340 | 0 | 98 | 0 | 0 | 0 | 40 | 60 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 90 | 35 | 0 | 45 | 0 | 36 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 380 | 73 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 110 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 500 | 0 | 307 | 748 | 0 | 0 |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 50 | 0 | 400 | 0 | 0 | 0 | 450 | 300 | 50 | 64 | 55 | 320 | 0 | 0 | 70 | 82 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 18 | 15 | 33 | 33 | 8 | 0 | 75 | 40 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 48 | 34 | 35 | 18 | 6 | 0 | 40 | 0 | 0 |  | 300 | 280 | 140 | 0 | 85 | 0 | 0 | 0 | 20 | 0 | 40 | 50 | 0 | 0 | 32 | 12 | 146 | 170 | 0 | 0 | 1.6 | 30 | 58 | 50 | 39 | 163 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 16 | 5 | 0 | 270 | 0 | 0 | 97 | 0 | 96 | 20 | 25 | 17 | 150 | 350 | 68 | 52 | 51 | 5 | 52 | 35 | 110 | 70 | 42 | 25 | 330 | 55 | 50 | 72 | 35 | 0 | 35 | 35 | 34 | 35 | 300 | 54 | 0 | 612 | 40 | 0 | 300 | 300 | 70 |  | 944 | 0 | 300 | 0 | 20 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 16 | 0 | 0 | 0 | 32 | 0 | 50 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 94 | 0 | 70 | 0 | 8 | 113 | 1100 | 110 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 307 | 748 | 130 | 0 | [5 empty] | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 300 | 244 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 8 | 16 | 0 | 0 | 75 | 40 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 300 | 105 | 140 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 12 | 56 | 171 | 0 | 0 | 0 | 28 | 58 | 0 | 0 | 120 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 17 | 0 | 334 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 34 | 38 | 0 | 325 | 0 | 18 | 0 | 0 | 0 | 0 | 5 | 16 | 0 | 230 | 0 | 0 | 270 | 8 | 0 | 280 | 250 | 11 | 0 | 926 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 110 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 358 | 1 | 140 | 422 | 2 | 0 | 0 | 0 |  |  |  | 144863135 | 22383272 | 0 | 56408926 | 7207850 | 1332480 | 668705 | 523200 | 2672600 |  |  | 236060168
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [8 empty] | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 | [10 empty] | 144.8631 | 22.3833 | 0 | 56.4089 | 7.2078 | 1.3325 | 0.6687 | 0.5232 | 2.6726
| Minimum Generation |  | 8846 | 9:00
| Highest Generation |  | 11550 | 1:00 |  |  |  |  | 4500 | [124 empty] | 0 | [72 empty] | 236.0602
| Day Peak Generation |  | 8846 | 9:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 10636 | 21:00 |  |  |  |  | 10500 | [197 empty] | 202699852
| HVDC Max Flow |  | 929 | 5:00 | [202 empty] | 202.6999
| HVDC EvPeak Flow |  | 922 | 21:00
| Load factor L.F |  | 85.16% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-20
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8846 | MW Hour : | 9:00 | Min. Gen. at | 8:00 | 8396
Evening Peak Generation : |  |  | 10636 | MW Hour : | 21:00 | Available Max Generation : |  | 16048
E.P. Demand (at gen end) : |  |  | 10636 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000
Maximum Generation : |  |  | 11550 | MW Hour : | 1:00 | Reserve(Generation end) |  | 4048
Total Gen. (MKWH) : |  |  | 236.0602 | System Load Factor : | 85.16% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 100 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-20
Actual : |  | 82.87 | Ft.(MSL) , | Rule curve : | 81.03 | Ft.( MSL )
Gas Consumed : |  | Total = | 1055.39 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 416178544.202
: |  |  | Coal : | 391686139.36 | Oil : | 130827511.25 | Total : | 938692194.812
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5310.1633 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1463.5928 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 2051.5561 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1784.4161 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1467.6227 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1092.2058 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 611.5045 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 510.265 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 997.9738 |  |  | 0 | 0%
Total |  | 0 |  | 15289.3002 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:33 | 08:52 | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Tripped showing 86.1 & 86.2 Master Relay relays Due to unknown.
08:34 | 08:55 | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Tripped showing Distance Relay relays Due to Thundering.
08:50 | 15:38 | Bogura-Sirajganj 230 kV Ckt-2 Forced S/D from Bogura 230/132kV end Due to Forced Shutdown and from Sirajgonj 230
end Due to Emergency Maintenance Work.
09:04 | 11:43 | BIPTC S/S 20DF41 Tripped showing 20DF41 Filter. relays.
09:38 | 11:32 | Jaldhaka 132/33kV S/S 33 KV BUS Forced S/D Due to Red Hot at 33kv Bus Coupler D/S-2. | [5 empty] | 10 MW load interrup.
09:38 | 11:31 | Jaldhaka 132/33kV S/S 416T-2 LT Forced S/D Due to Red Hot at 33kv Bus Coupler D/S-2.
09:38 |  | Jaldhaka 132/33kv T-2 with 33kv bus section S/D for redhot maintenance.
| 11:15 | Khulna (C) S/S TR-1 425T HT is restored.
| 11:18 | Khulna (C) S/S TR-1 425T LT is restored.
11:18 | 11:37 | Halishahar-Julda 132kV Ckt-1 Forced S/D from Juldah 132/33kV end Due to s/d and from Halishahar 132/33kV end
Due to Remove bird's nest from gantry structure
11:25 | 12:12 | Ashuganj 230/132/33kV S/S SHUNT REACTOR-2 Tripped showing E/F relays Due to TRIPPED.
11:32 |  | Jaldhaka 132/33kv T-2 with 33kv bus section Syn.
12:15 | 12:37 | Baroirhat-Feni 132 kV Ckt-2 Tripped from Baroirhat 132/33kV end showing Distance relay relays Due to Distance trip Phase B
13:46 | 15:36 | Madunaghat-Meghnaghat 400kV Ckt-2 Tripped from Meghnaghat 400/230kV end showing RED670 SIPROTEC JSD5 SIPROTEC &SJ85 | [5 empty] | 50 MW load interrup in
|  | relays Due to Heavy Rain Fail with Storm | [5 empty] | Meghnaghat 400/132 kV end.
15:13 | 15:24 | Chandraghona 132/33kV S/S TR-01(406T) LT Tripped showing REF630 relays Due to 33 KV Feeder Failt | [5 empty] | 29 MW load interrup.
16:09 | 16:12 | Chandraghona 132/33kV S/S TR-01(406T) LT Tripped showing REF630 relays Due to 33 KV feeder fault | [5 empty] | 24 MW load interrup.
17:11 | 21:09 | Gopalganj 132/33kV S/S T1 LT Tripped showing O/c relays Due to O/C. | [5 empty] | 14 MW load interrup.
17:56 | 21:07 | Gopalganj 132/33kV S/S T1 HT Forced S/D Due to 33 kv bus section -1 s/d
20:54 | 21:18 | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Tripped showing Distance relay relays Due to Zone-1, R-phase,general trip.
21:07 | 23:25 | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bagerhat 132/33kV end Due to OCB clamp R phase red hot maintenance work. | [5 empty] | 40 MW load interrup in
Bagerhat 132/33 kV end.
02:54 | 03:18 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Tripped from Purbasadipur 132/33kV end showing QUADRAMHO SHPM101 relays.
03:21 | 06:18 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Tripped from Purbasadipur 132/33kV end showing QUADRAMHO relays.
05:56 |  | Ashuganj 450 MW CCPP(South) Tripped with remarks:- GT
| 06:58 | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
07:04 |  | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to 33 kV REB-3 wire change. | [5 empty] | 35 Mw load interrup.
07:04 |  | Gopalganj 132/33kV S/S T2 HT Scheduled S/D Due to 33 kV REB-3 wire change
.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 53 | 709863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 413 | 8485200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9072500 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 291 | 6664815 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 329 | 7144639
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 84960 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 15 | 416160 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 205600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 297700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 395280 | Low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 0 | Reserve
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 79300
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Reserve
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 584 | 10106363
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 99723
| Dhaka area Total |  |  |  | 5634 | 2318 | 48077603
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 60678 | Low demand
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 16065
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 115 | 2672600 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 175 | 5064596
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 80290 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 324624 | Reserve
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 40592 | Reserve
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 116160 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1079520
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 20 | 87360 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 15360
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 85309 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 126720 | Reserve
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 86564 | Low demand
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 8364 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 300 | 9185453
| Cox's Bazar Wind |  | IPP | 66 | 60 | 40 | 523200 | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 0 | 0
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 190482
| Chattogram area Total |  |  |  | 4457 | 807 | 19763937
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 195 | 3137000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7457800 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6837000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 6472000 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 321768 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 0 | 48000 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 234181 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 571162
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2046370 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 817440 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 64 | 1332480
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 430584 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 233800 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 448020 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 77 | 1122240 | Low demand
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 65 | 1471680 | Low demand
| Cumilla Area Total |  |  |  | 2875 | 1642 | 32981525
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 202 | 3927360
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 1600
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 0 | 48000 | Reserve
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 8 | 322800 | Low demand
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 28090
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 30960 | Reserve
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 646 | 210 | 4358810
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 677000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1385640 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3357164
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 671400
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 36 | 475416 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1240896
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 0 | Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Reserve
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7086000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 7532000
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 7831900
| Sylhet Area Total |  |  |  | 2331 | 1404 | 30257416
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22383272
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8181216 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 233280 | Reserve
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 64800
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 358 | 9941818
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1640 | 40804386
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 281568 | Reserve
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 168036
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2592000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 760 | 16841100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 2574955 | GT-2 Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 3949100 | Low demand
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 0
| Barisal Area Total |  |  |  | 2236 | 1150 | 26406759
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 161 | 4108991 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 165 | 4153736
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 350 | 7739709 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 55606 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 2 | 138456 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 5400
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 582 | 12377455
| Rajshahi Area Total |  |  |  | 3381 | 1260 | 28579353
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4114000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 46723 | Reserve
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 7459
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 35 | 402048 | Low demand
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 23839
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 236310
| Rangpur Area Total |  |  |  | 950 | 205 | 4830379
| Total |  |  |  | 26364 | 10636 | 236060168
| Eastern Grid Total |  |  |  | 15943 | 6381 | 135439291
| Western Grid Total |  |  |  | 10421 | 4255 | 100620877
| National Grid Total |  |  |  | 26364 | 10636 | 236060168
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2024-06-19
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
| (a) ENTIRE EASTERN GRID: |  | 9700.03 | MW | (b) ENTIRE WESTERN GRID: |  | 4958.43 | MW
| i) Dhaka area |  |  | 5397.37 |  | MW | i) Khulna area | 1988.8 | MW
| ii) Chattogram area |  |  | 1379.4 |  | MW | ii) Barishal area | 511.4 | MW
| iii) Cumilla area |  |  | 1432 |  | MW | iii) Rajshahi area | 1743.6 | MW
| iv) Mymensingh area |  |  | 1010 |  | MW | iv) Rangpur area | 916 | MW
| v) Sylhet area |  |  | 692 |  | MW
|  | System Total Demand at Evening Peak Hour (a + b) = |  |  | 14658.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 103 | 01:00 | 133 | Rahim | 0 | 00:00
2 | AKSML | 4 | 10:00 | 68 | Jashore | 151 | 00:00 | 134 | Rajbari | 88 | 00:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jhenaidah | 144 | 00:00 | 135 | Rajendrapur | 72 | 00:00
4 | Agargaon | 90 | 10:00 | 70 | Joydebpur | 83 | 23:00 | 136 | Rajshahi | 134 | 00:00
5 | Agrabad | 80 | 13:00 | 71 | Joypurhat | 57 | 00:00 | 137 | Rajshahi-230 | 82 | 00:00
6 | Amnura | 78 | 01:00 | 72 | Juldah | 14 | 23:00 | 138 | Ramganj | 112 | 00:00
7 | Ashuganj | 61 | 23:00 | 73 | KSRM | 11 | 10:00 | 139 | Rampur | 28 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 133 | 23:00 | 140 | Rangamati | 15 | 19:00
9 | BSRM | 182 | 14:00 | 75 | Kachua | 90 | 00:00 | 141 | Rangpur | 101 | 21:00
10 | Bagerhat | 98 | 01:00 | 76 | Kallyanpur | 93 | 00:00 | 142 | Ruppur | 7 | 11:00
11 | Bakulia | 70 | 00:00 | 77 | Kalurghat | 20 | 00:00 | 143 | SSM | 0 | 00:00
12 | Banani | 25.4 | 10:00 | 78 | Kamrangirchar | 26 | 00:00 | 144 | Saidpur | 69 | 20:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 148 | 03:00
14 | Barapukuria | 52 | 23:00 | 80 | Kazla | 70 | 00:00 | 146 | Satmasjid | 88 | 00:00
15 | Barguna | 28 | 00:00 | 81 | Keranigonj | 66 | 00:00 | 147 | Savar | 105 | 02:00
16 | Barishal | 120 | 00:00 | 82 | Khagrachori | 28 | 19:30 | 148 | SevenRings | 0.81 | 23:00
17 | Barishal-230 | 122 | 01:00 | 83 | Khulna | 64 | 00:00 | 149 | ShahCement | 2 | 10:00
18 | Baroaulia | 54 | 22:00 | 84 | Khulshi | 144 | 18:30 | 150 | Shahjadpur | 86 | 00:00
19 | Baroirhat | 64 | 23:00 | 85 | Kishoreganj | 134 | 00:00 | 151 | Shahjibazar | 70 | 22:00
20 | Bashundhara | 117 | 00:00 | 86 | Kodda | 125 | 00:00 | 152 | Shahmirpur | 43 | 23:00
21 | BashundharaCement | 0 | 00:00 | 87 | Kulaura | 36 | 19:00 | 153 | Shariatpur | 103 | 00:00
22 | Beanibazar | 55 | 21:00 | 88 | Kurigram | 44 | 17:00 | 154 | Sherpur | 100 | 00:00
23 | Benapole | 72 | 01:00 | 89 | Kushtia | 144 | 00:00 | 155 | Shikalbaha | 25 | 21:00
24 | Bhaluka | 84 | 00:00 | 90 | Lalbag | 35 | 01:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 63 | 04:00 | 91 | Lalmonirhat | 38 | 21:00 | 157 | Shitalakhya | 53.5 | 01:00
26 | Bhangura | 42 | 00:00 | 92 | MI_Cement | 1 | 10:00 | 158 | Sholosohor | 33 | 00:00
27 | Bheramara(GK) | 76 | 00:00 | 93 | Madanganj | 19 | 00:00 | 159 | Shyampur | 46 | 00:00
28 | Bhulta | 108 | 00:00 | 94 | Madaripur | 131 | 00:00 | 160 | Siddhirganj | 68 | 00:00
29 | Bog-Sherpur | 56 | 17:00 | 95 | Madartek | 71.3 | 00:00 | 161 | Sirajganj | 102 | 00:00
30 | Bogura | 136 | 05:00 | 96 | Madunaghat | 49 | 00:00 | 162 | Sonargaon | 48 | 00:00
31 | Borhanuddin | 90 | 01:00 | 97 | Magura | 76 | 00:00 | 163 | Sreemongol | 51 | 00:00
32 | Brahmanbaria | 149 | 00:00 | 98 | Mahasthangarh | 72 | 00:00 | 164 | Sreepur | 34 | 00:00
33 | Cantonment | 97 | 00:00 | 99 | Manikganj | 102 | 01:00 | 165 | Srinagar | 52 | 01:00
34 | Chandpur | 74 | 00:00 | 100 | Maniknagar | 60 | 10:00 | 166 | Sunamganj | 32 | 23:00
35 | Chandraghona | 34 | 21:00 | 101 | Matarbari | 42 | 19:30 | 167 | Sylhet | 28 | 19:30
36 | Chapai | 73 | 00:00 | 102 | Matuail | 32 | 00:00 | 168 | Sylhet-132 | 73 | 22:00
37 | Charsaidpur | 4 | 00:00 | 103 | Millgate | 55 | 00:00 | 169 | TK | 33 | 00:00
38 | Chauddagram | 68 | 00:00 | 104 | Mirpur | 110.5 | 00:00 | 170 | Tangail | 178 | 01:00
39 | Chhatak | 18 | 17:00 | 105 | Mirsorai | 3 | 00:00 | 171 | Thakurgaon | 75 | 20:00
40 | Chowmuhani | 220 | 00:00 | 106 | Mirzapur | 34 | 00:00 | 172 | Tongi | 72 | 22:00
41 | Chuadanga | 113 | 02:00 | 107 | Mithapukur | 46 | 22:00 | 173 | Ullahpara | 28 | 23:00
42 | Coxsbazar | 110 | 00:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 49 | 00:00
43 | Cumilla(N) | 134 | 01:00 | 109 | Mogbazar | 84.9 | 10:00 | 175 | Uttara | 54 | 13:00
44 | Cumilla(S) | 148 | 00:00 | 110 | Mongla | 22 | 10:00 | 176 | UttaraNew | 40 | 00:00
45 | Daudkandi | 126 | 00:00 | 111 | Motijheel | 27 | 00:00 | 177 | Zigatola | 69 | 00:00
46 | Dhaka | 24 | 11:00 | 112 | Munshiganj | 106 | 00:00
47 | Dhamrai | 84 | 01:00 | 113 | Mymensingh | 161 | 21:00
48 | Dhanmondi | 88 | 11:00 | 114 | Naogaon | 130 | 00:00
49 | Dohazari | 96 | 19:30 | 115 | Narail | 68 | 00:00
50 | Faridpur | 179 | 01:00 | 116 | Narinda | 40 | 00:00
51 | Fatullah | 43 | 00:00 | 117 | Narshingdi | 131 | 00:00
52 | Fenchuganj | 29 | 14:00 | 118 | Natore | 163 | 00:00
53 | Feni | 96 | 23:00 | 119 | Nawabganj | 65.6 | 00:00
54 | GPH | 75 | 22:00 | 120 | Netrakona | 106 | 20:00
55 | Ghatail | 56 | 00:00 | 121 | New | 21.1 | 00:00
56 | Ghorashal | 50 | 19:30 | 122 | Niamatpur | 84 | 00:00
57 | Goalpara | 40 | 01:00 | 123 | Noapara | 46 | 00:00
58 | Gollamari | 90 | 01:00 | 124 | PHP | 9 | 12:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-19 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 395 | 11:00 | 382 | 00:00 | Kaliakoir | 392 | 11:00 | 380 | 02:00
| Ashuganj | 408 | 12:00 | 398 | 23:00 | Madunaghat_I | 399 | 02:00 | 394 | 10:00
| Bhulta | 411 | 18:00 | 396 | 00:00 | Meghnaghat | 390 | 16:00 | 379 | 00:00
| Bibiana | 406 | 09:00 | 397 | 00:00 | Payra | 415 | 11:00 | 404 | 00:00
| BIPTC | 403 | 06:00 | 394 | 00:00 | Rahanpur | 414 | 18:00 | 398 | 00:00
| Bogura | 409 | 18:30 | 393 | 00:00 | Rampal | 407 | 17:00 | 387 | 00:00
| Gopalganj | 406 | 18:00 | 387 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 09:00 | 228 | 00:00 | Hasnabad | 237 | 18:00 | 229 | 00:00
| AKSML | 228 | 02:00 | 219 | 23:00 | Hathazari | 228 | 03:00 | 223 | 19:00
| Aminbazar | 237 | 16:00 | 229 | 00:00 | Ishurdi | 237 | 08:00 | 225 | 00:00
| Ashuganj | 240 | 09:00 | 230 | 01:00 | Jhenaidah | 229 | 17:00 | 211 | 00:00
| Ashuganj-400 | 235 | 8:00 | 227 | 13:00 | Kaliakoir | 238 | 18:00 | 230 | 00:00
| Baghabari | 235 | 17:00 | 225 | 00:00 | Keranigonj | 236 | 11:00 | 228 | 00:00
| Barapukuria | 223 | 05:00 | 211 | 21:00 | Khulna(S) | 233 | 17:00 | 215 | 00:00
| Barapukuria-230 | 225 | 11:00 | 215 | 22:00 | Madunaghat_I | 231 | 08:00 | 227 | 02:00
| Barishal | 241 | 16:00 | 230 | 02:00 | Maniknagar | 238 | 18:00 | 231 | 00:00
| Bheramara | 235 | 08:00 | 223 | 00:00 | Meghnaghat | 243 | 07:00 | 238 | 00:00
| Bhulta | 239 | 16:00 | 230 | 00:00 | Meghnaghat-400 | 239 | 09:00 | 225 | 01:00
| Bibiana | 233 | 05:00 | 227 | 01:00 | Mirsorai | 229 | 01:00 | 219 | 18:30
| BIPTC | 237 | 08:00 | 223 | 00:00 | Rajshahi | 233 | 07:00 | 219 | 22:00
| Bogura | 231 | 18:00 | 221 | 00:00 | Rampal | 233 | 16:00 | 215 | 00:00
| Bogura-400 | 230 | 18:30 | 221 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 243 | 12:00 | 233 | 02:00 | Rampura | 237 | 18:00 | 230 | 00:00
| BSRM | 230 | 03:00 | 219 | 19:00 | Shikalbaha | 226 | 02:00 | 218 | 18:30
| Cumilla(N) | 234 | 18:00 | 226 | 00:00 | Shyampur | 237 | 09:00 | 230 | 00:00
| Fenchuganj | 238 | 09:00 | 232 | 00:00 | Siddhirganj | 239 | 11:00 | 233 | 00:00
| Ghorashal | 240 | 07:00 | 235 | 00:00 | Sirajgonj | 241 | 09:00 | 233 | 00:00
| Ghorashal-230 | 237 | 09:00 | 230 | 00:00 | Sreepur | 238 | 09:00 | 228 | 00:00
| GPH | 228 | 01:00 | 215 | 19:00 | Tongi | 237 | 09:00 | 230 | 00:00
| Haripur | 237 | 11:00 | 231 | 00:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 07:00 | 132 | 00:00 | Kushtia | 137 | 17:00 | 126 | 00:00
| Agargaon | 138 | 17:00 | 135 | 12:00 | Lalbag | 136 | 11:00 | 131 | 00:00
| Agrabad | 134 | 07:00 | 126 | 19:00 | Lalmonirhat | 132 | 05:00 | 115 | 21:00
| AKS | 130 | 00:00 | 124 | 18:30 | Madanganj | 136 | 08:00 | 132 | 00:00
| Aminbazar | 138 | 15:00 | 130 | 00:00 | Madaripur | 136 | 18:00 | 123 | 09:00
| Amnura | 135 | 17:00 | 120 | 00:00 | Madartek | 136 | 07:00 | 131 | 00:00
| Ashuganj | 140 | 06:00 | 137 | 00:00 | Madunaghat | 134 | 05:00 | 126 | 19:00
| Bagerhat | 137 | 16:00 | 114 | 00:00 | Magura | 137 | 17:00 | 122 | 00:00
| Bakulia | 134 | 09:00 | 127 | 19:00 | Mahasthangarh | 133 | 17:00 | 124 | 00:00
| Banani | 136 | 17:00 | 132 | 00:00 | Manikganj | 132 | 11:00 | 126 | 00:00
| Bangabhaban | 136 | 18:00 | 131 | 00:00 | Maniknagar | 135 | 05:00 | 132 | 00:00
| Barapukuria | 134 | 05:00 | 124 | 21:00 | Matarbari | 133 | 01:00 | 111 | 19:00
| Barguna | 136 | 13:00 | 125 | 00:00 | Matuail | 137 | 11:00 | 132 | 00:00
| Barishal | 137 | 12:00 | 113 | 00:00 | Millgate | 138 | 17:00 | 131 | 00:00
| Barishal-230 | 137 | 11:00 | 129 | 02:00 | Mirpur | 137 | 11:00 | 132 | 00:00
| Baroaulia | 133 | 06:00 | 125 | 19:00 | Mirzapur | 133 | 10:00 | 126 | 00:00
| Baroirhat | 131 | 09:00 | 120 | 19:00 | Mithapukur | 132 | 05:00 | 121 | 21:00
| Bashundhara | 137 | 07:00 | 131 | 00:00 | MI_Cement | 138 | 03:00 | 134 | 00:00
| BashundharaCement | 136 | 08:00 | 132 | 00:00 | Modern | 134 | 01:00 | 129 | 12:00
| Beanibazar | 131 | 07:00 | 122 | 00:00 | Mogbazar | 138 | 18:00 | 135 | 00:00
| Benapole | 136 | 18:00 | 117 | 00:00 | Mongla | 137 | 16:00 | 131 | 00:00
| Bhaluka | 135 | 09:00 | 126 | 00:00 | Motijheel | 136 | 18:00 | 131 | 00:00
| Bhandaria | 136 | 16:00 | 109 | 00:00 | Munshiganj | 137 | 18:00 | 131 | 00:00
| Bhangura | 138 | 17:00 | 129 | 00:00 | Mymensingh | 133 | 07:00 | 123 | 00:00
| Bheramara | 136 | 08:00 | 130 | 00:00 | Naogaon | 131 | 17:00 | 121 | 00:00
| Bheramara(GK) | 137 | 18:00 | 130 | 00:00 | Narail | 139 | 16:00 | 122 | 00:00
| Bhulta | 130 | 11:00 | 122 | 00:00 | Narinda | 135 | 5:00 | 132 | 24:00
| Bog-Sherpur | 134 | 17:00 | 125 | 00:00 | Narshingdi | 133 | 10:00 | 124 | 00:00
| Bogura | 135 | 17:00 | 127 | 00:00 | Natore | 134 | 17:00 | 125 | 00:00
| Bogura-230 | 135 | 17:00 | 128 | 00:00 | Nawabganj | 135 | 11:00 | 129 | 00:00
| Brahmanbaria | 136 | 11:00 | 126 | 00:00 | Netrakona | 132 | 09:00 | 124 | 00:00
| Cantonment | 138 | 18:00 | 132 | 00:00 | New | 138 | 17:00 | 132 | 00:00
| Chandpur | 130 | 20:00 | 118 | 00:00 | Niamatpur | 136 | 18:00 | 129 | 00:00
| Chandraghona | 135 | 09:00 | 126 | 19:00 | Noapara | 139 | 18:00 | 121 | 00:00
| Chapai | 133 | 18:00 | 124 | 00:00 | Pabna | 136 | 08:00 | 127 | 00:00
| Charsaidpur | 137 | 11:00 | 132 | 00:00 | Palashbari | 129 | 06:00 | 118 | 21:00
| Chauddagram | 130 | 09:00 | 120 | 00:00 | Panchagarh | 135 | 01:00 | 119 | 12:00
| Chhatak | 133 | 08:00 | 123 | 01:00 | Patuakhali | 135 | 13:00 | 126 | 03:00
| Chowmuhani | 124 | 19:30 | 112 | 00:00 | Payra | 136 | 10:00 | 131 | 00:00
| Chuadanga | 134 | 18:00 | 113 | 00:00 | PHP | 128 | 09:00 | 118 | 00:00
| Coxsbazar | 132 | 03:00 | 113 | 19:00 | Postogola | 140 | 18:00 | 134 | 00:00
| Cumilla(N) | 136 | 09:00 | 127 | 00:00 | Purbachal | 137 | 18:00 | 132 | 00:00
| Cumilla(S) | 133 | 09:00 | 126 | 00:00 | Purbasadipur | 130 | 02:00 | 117 | 21:00
| Daudkandi | 133 | 14:00 | 119 | 00:00 | Rahanpur | 137 | 18:00 | 130 | 00:00
| Dhaka | 136 | 05:00 | 132 | 00:00 | Rahim | 137 | 17:00 | 132 | 00:00
| Dhamrai | 141 | 17:00 | 136 | 01:00 | Rajbari | 134 | 17:00 | 122 | 00:00
| Dhanmondi | 137 | 02:00 | 133 | 00:00 | Rajendrapur | 134 | 11:00 | 127 | 03:00
| Dohazari | 132 | 10:00 | 120 | 19:00 | Rajshahi | 134 | 17:00 | 125 | 00:00
| Faridpur | 134 | 17:00 | 123 | 00:00 | Rajshahi-230 | 134 | 07:00 | 117 | 00:00
| Fatullah | 138 | 09:00 | 134 | 00:00 | Ramganj | 126 | 20:00 | 112 | 00:00
| Fenchuganj | 136 | 09:00 | 130 | 00:00 | Rampur | 134 | 02:00 | 124 | 19:00
| Feni | 126 | 09:00 | 117 | 01:00 | Rampura | 136 | 06:00 | 132 | 00:00
| Ghatail | 132 | 11:00 | 123 | 00:00 | Rangamati | 134 | 09:00 | 125 | 19:00
| Ghorashal | 142 | 07:00 | 137 | 00:00 | Rangpur | 132 | 03:00 | 116 | 21:00
| Goalpara | 139 | 18:00 | 134 | 13:00 | Ruppur | 137 | 08:00 | 130 | 00:00
| Gollamari | 139 | 18:00 | 124 | 00:00 | Saidpur | 135 | 05:00 | 119 | 21:00
| Gopalganj | 136 | 18:00 | 122 | 00:00 | Satkhira | 137 | 18:00 | 114 | 00:00
| Gopalganj-400 | 136 | 18:00 | 127 | 00:00 | Satmasjid | 138 | 18:30 | 132 | 00:00
| Gulshan | 136 | 18:00 | 132 | 00:00 | Savar | 136 | 09:00 | 131 | 00:00
| Halishahar | 134 | 01:00 | 125 | 19:00 | SevenRings | 142 | 09:00 | 137 | 00:00
| Haripur | 137 | 17:00 | 132 | 00:00 | ShahCement | 137 | 15:00 | 132 | 00:00
| HaripurSBU | 137 | 17:00 | 132 | 00:00 | Shahjadpur | 140 | 07:00 | 134 | 00:00
| Hasnabad | 138 | 07:00 | 135 | 00:00 | Shahjibazar | 135 | 11:00 | 126 | 00:00
| Hathazari | 134 | 01:00 | 128 | 19:00 | Shahmirpur | 134 | 05:00 | 127 | 19:00
| Ishurdi | 138 | 08:00 | 131 | 00:00 | Shariatpur | 135 | 16:00 | 122 | 00:00
| Jaldhaka | 133 | 05:00 | 116 | 21:00 | Sherpur | 129 | 13:00 | 117 | 00:00
| Jamalpur | 130 | 11:00 | 120 | 22:00 | Shikalbaha | 125 | 07:00 | 116 | 19:00
| Jashore | 137 | 18:00 | 118 | 00:00 | Shikalbaha-230 | 135 | 02:00 | 130 | 18:30
| Jhenaidah | 140 | 17:00 | 125 | 00:00 | Shitalakhya | 138 | 03:00 | 134 | 00:00
| Jhenaidah-230 | 140 | 17:00 | 126 | 00:00 | Sholosohor | 133 | 01:00 | 125 | 19:00
| Joydebpur | 143 | 16:00 | 134 | 00:00 | Shyampur | 136 | 11:00 | 134 | 00:00
| Joypurhat | 131 | 16:00 | 119 | 00:00 | Shyampur-230 | 138 | 09:00 | 133 | 00:00
| Juldah | 133 | 00:00 | 127 | 19:00 | Siddhirganj | 138 | 18:00 | 133 | 00:00
| Kabirpur | 137 | 17:00 | 130 | 00:00 | Sirajganj | 136 | 17:00 | 126 | 00:00
| Kachua | 130 | 18:00 | 119 | 00:00 | Sonargaon | 135 | 11:00 | 129 | 00:00
| Kaliakoir | 142 | 16:00 | 131 | 00:00 | Sreemongol | 132 | 10:00 | 126 | 00:00
| Kallyanpur | 135 | 09:00 | 130 | 00:00 | Sreepur | 136 | 09:00 | 128 | 00:00
| Kalurghat | 135 | 09:00 | 127 | 16:00 | Srinagar | 136 | 17:00 | 130 | 00:00
| Kamrangirchar | 137 | 18:00 | 130 | 00:00 | SSM | 138 | 11:00 | 130 | 19:00
| Kaptai | 133 | 9:00 | 129 | 19:00 | Sunamganj | 132 | 09:00 | 123 | 18:30
| Kazla | 135 | 08:00 | 132 | 00:00 | Sylhet | 133 | 09:00 | 125 | 00:00
| Keranigonj | 136 | 11:00 | 131 | 00:00 | Sylhet-132 | 132 | 09:00 | 126 | 00:00
| Khagrachori | 133 | 08:00 | 124 | 19:00 | Tangail | 132 | 15:00 | 124 | 00:00
| Khulna | 138 | 18:00 | 122 | 00:00 | Thakurgaon | 134 | 01:00 | 117 | 13:00
| Khulna(S) | 138 | 11:00 | 125 | 00:00 | TK | 134 | 07:00 | 126 | 19:00
| Khulshi | 132 | 01:00 | 124 | 19:00 | Tongi | 139 | 09:00 | 133 | 00:00
| Kishoreganj | 136 | 09:00 | 126 | 00:00 | Ullahpara | 138 | 17:00 | 129 | 00:00
| Kodda | 139 | 09:00 | 126 | 02:00 | Ullon | 136 | 07:00 | 132 | 00:00
| KSRM | 133 | 01:00 | 126 | 19:00 | Uttara | 138 | 18:00 | 132 | 00:00
| Kulaura | 134 | 10:00 | 129 | 19:00 | UttaraNew | 138 | 18:00 | 132 | 00:00
| Kurigram | 132 | 03:00 | 116 | 21:00 | Zigatola | 136 | 17:00 | 131 | 00:00

## L-Curve
Date | 2024-06-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 110 | 6503 | 4306 | 10809 |  |  |  | QF-LDC-11
0:30 | 145 | 6394.5 | 4785 | 11179.5 | Date: | 2024-06-19
1:00 | 180 | 6286 | 5264 | 11550
1:30 | 169 | 6267.5 | 4991.5 | 11259
2:00 | 158 | 6249 | 4719 | 10968
2:30 | 153 | 6243 | 4612 | 10855 | [5 empty] | Gen. at Eve. Peak | 10636 | 10636 MW (21:00 )
3:00 | 148 | 6237 | 4505 | 10742 | [6 empty] | 21:00
3:30 | 145 | 6215.5 | 4416.5 | 10632 | [5 empty] | Gen. at Day Peak | 8846 | 8846 MW (09:00 )
4:00 | 142 | 6194 | 4328 | 10522 | [6 empty] | 9:00
4:30 | 147 | 6150.5 | 4319.5 | 10470 | [5 empty] | Highest Generation | 11550
5:00 | 152 | 6107 | 4311 | 10418 | [6 empty] | 1:00
5:30 | 170 | 5776.5 | 4176 | 9952.5
6:00 | 188 | 5446 | 4041 | 9487
6:30 | 179 | 5446.5 | 3954.5 | 9401
7:00 | 170 | 5447 | 3868 | 9315
7:30 | 218 | 5320 | 3873.5 | 9193.5
8:00 | 266 | 5193 | 3879 | 9072
8:30 | 246 | 5104.5 | 3854.5 | 8959
9:00 | 226 | 5016 | 3830 | 8846
9:30 | 261 | 4977.5 | 3759 | 8736.5
10:00 | 296 | 4939 | 3688 | 8627
10:30 | 241 | 4938 | 3690.5 | 8628.5
11:00 | 186 | 4937 | 3693 | 8630
11:30 | 250 | 4988 | 3713.5 | 8701.5
12:00 | 314 | 5039 | 3734 | 8773
12:30 | 258 | 5156 | 3808 | 8964
13:00 | 202 | 5273 | 3882 | 9155
13:30 | 195 | 5251 | 3866 | 9117
14:00 | 188 | 5229 | 3850 | 9079
14:30 | 200 | 5118 | 3807 | 8925
15:00 | 212 | 5007 | 3764 | 8771
15:30 | 266 | 4900.5 | 3704.5 | 8605
16:00 | 320 | 4794 | 3645 | 8439
16:30 | 378 | 4713 | 3603 | 8316
17:00 | 436 | 4632 | 3561 | 8193
17:30 | 449 | 4600.5 | 3525 | 8125.5
18:00 | 462 | 4569 | 3489 | 8058
18:30 | 378 | 5110 | 3591.5 | 8701.5
19:00 | 294 | 5651 | 3694 | 9345
19:30 | 272 | 5967 | 4216 | 10183
20:00 | 188 | 5953 | 4206 | 10159 |  |  |  | Executive Engineer
20:30 | 144 | 6167 | 4230.5 | 10397.5 |  |  |  | Network Operation Division
21:00 | 100 | 6381 | 4255 | 10636
21:30 | 113 | 6396 | 4277.5 | 10673.5
22:00 | 126 | 6411 | 4300 | 10711 |  |  |  |  | Page 6 of 7
22:30 | 126 | 6458 | 4304.5 | 10762.5
23:00 | 126 | 6505 | 4309 | 10814
23:30 | 118 | 6504 | 4307.5 | 10811.5
24:00 | 110 | 6503 | 4306 | 10809
10636 MW (21:00 )
8846 MW (09:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-19 |  | Energy |  | 236060168
[15 empty] | 2024-06-19 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4174 | 922 | 2596 | 0 | 591 | 2309 | 113 | 0 | 0 | 68 | 0 | 36 | 0
0:30 | 4050.5 | 923.5 | 2532 | 0 | 628.5 | 2761 | 95.5 | 0 | 71.5 | 68 | 0 | 49 | 14.325 |  |  | Date: | 44000
1:00 | 3927 | 925 | 2468 | 0 | 666 | 3213 | 78 | 0 | 143 | 68 | 0 | 62 | 28.65
1:30 | 3931 | 926.5 | 2454 | 0 | 530.5 | 3093 | 95.5 | 0 | 108 | 70 | 0 | 50.5 | 24.83 | [9 empty] | Total Energy | 236.0602 | 236.0602 | Total Energy Gen 236.060 MKWHr Energy Not Served 0.092 MKWHr Energy Requirement 236.152 MKWHr
2:00 | 3935 | 928 | 2440 | 0 | 395 | 2973 | 113 | 0 | 73 | 72 | 0 | 39 | 21.01 | [9 empty] | Energy not Served | 0.09168 | 0.09168
2:30 | 4006.5 | 928 | 2373 | 0 | 369 | 2879 | 113 | 0 | 73 | 70 | 0 | 43.5 | 18.145 | [9 empty] | Energy Requirement | 236.1518 | 236.1518
3:00 | 4078 | 928 | 2306 | 0 | 343 | 2785 | 113 | 0 | 73 | 68 | 0 | 48 | 15.28
3:30 | 4045.5 | 928 | 2310 | 0 | 346.5 | 2696 | 114 | 0 | 73 | 67 | 0 | 52 | 15.28 | [8 empty] | Shortage
4:00 | 4013 | 928 | 2314 | 0 | 350 | 2607 | 115 | 0 | 73 | 66 | 0 | 56 | 15.28
4:30 | 4007.5 | 928.5 | 2309 | 0 | 337 | 2597.5 | 115 | 0 | 73 | 65 | 0 | 37.5 | 15.28
5:00 | 4002 | 929 | 2304 | 0 | 324 | 2588 | 115 | 0 | 73 | 64 | 0 | 19 | 15.28
5:30 | 3945 | 929 | 2144 | 0 | 246 | 2455 | 115 | 0 | 36.5 | 61 | 1 | 20 | 7.64
6:00 | 3888 | 929 | 1984 | 0 | 168 | 2322 | 115 | 0 | 0 | 58 | 2 | 21 | 0
6:30 | 3872 | 928.5 | 1968.5 | 0 | 159 | 2264.5 | 115 | 0 | 0 | 55 | 4.5 | 34 | 0 | [7 empty] | Coal
7:00 | 3856 | 928 | 1953 | 0 | 150 | 2207 | 115 | 0 | 0 | 52 | 7 | 47 | 0
7:30 | 3821 | 928 | 1915 | 0 | 122.5 | 2201 | 115 | 0 | 0 | 52 | 15.5 | 23.5 | 0 | [6 empty] | Oil
8:00 | 3786 | 928 | 1877 | 0 | 95 | 2195 | 115 | 0 | 0 | 52 | 24 | 0 | 0
8:30 | 3756 | 928 | 1827.5 | 0 | 103 | 2132.5 | 115 | 0 | 0 | 50 | 47 | 0 | 0
9:00 | 3726 | 928 | 1778 | 0 | 111 | 2070 | 115 | 0 | 0 | 48 | 70 | 0 | 0
9:30 | 3654.5 | 928 | 1789 | 0 | 121 | 2018 | 114 | 0 | 0 | 48 | 61.5 | 2.5 | 0
10:00 | 3583 | 928 | 1800 | 0 | 131 | 1966 | 113 | 0 | 0 | 48 | 53 | 5 | 0
10:30 | 3582 | 925.5 | 1787.5 | 0 | 130 | 1955.5 | 113.5 | 0 | 0 | 49 | 64.5 | 21 | 0
11:00 | 3581 | 923 | 1775 | 0 | 129 | 1945 | 114 | 0 | 0 | 50 | 76 | 37 | 0
11:30 | 3664 | 923 | 1802 | 0 | 128.5 | 1916.5 | 114 | 0 | 0 | 52 | 71 | 30.5 | 0
12:00 | 3747 | 923 | 1829 | 0 | 128 | 1888 | 114 | 0 | 0 | 54 | 66 | 24 | 0
12:30 | 3813.5 | 923 | 1885.5 | 0 | 128.5 | 1918.5 | 112 | 0 | 0 | 52 | 104 | 27 | 0
13:00 | 3880 | 923 | 1942 | 0 | 129 | 1949 | 110 | 0 | 0 | 50 | 142 | 30 | 0
13:30 | 3880 | 923 | 1942 | 0 | 129 | 1949 | 110 | 0 | 0 | 50 | 142 | 30 | 0
14:00 | 3880 | 923 | 1942 | 0 | 129 | 1949 | 110 | 0 | 0 | 50 | 142 | 30 | 0
14:30 | 3843 | 923 | 1872 | 0 | 114 | 1951.5 | 111.5 | 0 | 0 | 38 | 93 | 17 | 0
15:00 | 3806 | 923 | 1802 | 0 | 99 | 1954 | 113 | 0 | 0 | 26 | 44 | 4 | 0
15:30 | 3718.5 | 923 | 1746.5 | 0 | 79 | 1950 | 113.5 | 0 | 0 | 33 | 36.5 | 5 | 0
16:00 | 3631 | 923 | 1691 | 0 | 59 | 1946 | 114 | 0 | 0 | 40 | 29 | 6 | 0
16:30 | 3547.5 | 923 | 1664 | 0 | 59 | 1933 | 114.5 | 0 | 0 | 45 | 27 | 3 | 0
17:00 | 3464 | 923 | 1637 | 0 | 59 | 1920 | 115 | 0 | 0 | 50 | 25 | 0 | 0
17:30 | 3424 | 922.5 | 1635 | 0 | 61.5 | 1899.5 | 115.5 | 0 | 0 | 51 | 16.5 | 0 | 0
18:00 | 3384 | 922 | 1633 | 0 | 64 | 1879 | 116 | 0 | 0 | 52 | 8 | 0 | 0
18:30 | 3715.5 | 922 | 1793.5 | 0 | 166.5 | 1925.5 | 115.5 | 0 | 0 | 57 | 4 | 2 | 0
19:00 | 4047 | 922 | 1954 | 0 | 269 | 1972 | 115 | 0 | 0 | 62 | 0 | 4 | 0
19:30 | 4075 | 921 | 2209 | 0 | 507 | 2269 | 115 | 0 | 17 | 58 | 0 | 12 | 0
20:00 | 3973 | 921 | 2232 | 0 | 492 | 2327 | 115 | 0 | 17 | 62 | 0 | 20 | 0
20:30 | 4066.5 | 921.5 | 2371 | 0 | 503.5 | 2318.5 | 115 | 0 | 8.5 | 63 | 0 | 30 | 0
21:00 | 4160 | 922 | 2510 | 0 | 515 | 2310 | 115 | 0 | 0 | 64 | 0 | 40 | 0
21:30 | 4154.5 | 921.5 | 2532 | 0 | 532 | 2313.5 | 115 | 0 | 0 | 64 | 0 | 41 | 0
22:00 | 4149 | 921 | 2554 | 0 | 549 | 2317 | 115 | 0 | 0 | 64 | 0 | 42 | 0
22:30 | 4191 | 921.5 | 2573 | 0 | 545 | 2312.5 | 115 | 0 | 0 | 66 | 0 | 38.5 | 0
23:00 | 4233 | 922 | 2592 | 0 | 541 | 2308 | 115 | 0 | 0 | 68 | 0 | 35 | 0
23:30 | 4203.5 | 922 | 2594 | 0 | 566 | 2308.5 | 114 | 0 | 0 | 68 | 0 | 35.5 | 0 |  |  | Max Temp. in Dhaka |  | 30.2°C
24:00 | 4174 | 922 | 2596 | 0 | 591 | 2309 | 113 | 0 | 0 | 68 | 0 | 36 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 236.060 MKWHr Energy Not Served 0.092 MKWHr Energy Requirement 236.152 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 77 | 77 | 75 | 75 | 75 | 75 | 75 | 76 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1728600
2 | Karnaphuli Hydro PP Unit-4 & 5 | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 37 | 37 | 35 | 35 | 38 | 39 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 944000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [20 empty] | 8 | 6 | 17 | 17 | 11 | 8 | 60678
| Teknaf 20MW PP (Solartech) | [7 empty] | 0 |  | 0 | 0 | 0 | 1 | 4 | 3 | 4 | 2 | 0 | [8 empty] | 16065
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 225 | 225 | 222 | 222 | 222 | 222 | 222 | 180 | 188 |  | 175 | 175 | 174 | 175 | 175 | 175 | 175 | 5064596
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 0 | [23 empty] | 0 | 40592
12 | Hathazari 100 MW peaking PP | 57 | 57 | 57 | 57 | 57 | 0 | [20 empty] | 324624
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [20 empty] | 34 | 27 | 17 | 17 |  | 0 | 80290
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [25 empty] | 0 | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 321 | 321 | 319 | 319 | 322 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 250 |  | 312 | 326 | 331 | 329 | 328 | 328 | 328 | 7144639
18 | Kodda 300 MW PP Unit-2 (Summit) | [25 empty] | 0 | 0
19 | Ashuganj 195 MW PP (APSCL-United) | 0 | [19 empty] | 11 | 55 | 55 | 55 | 55 | 55 | 234181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 520 | 520 | 520 | 520 | 520 | 484 | 445 | 430 | 380 | 350 | 327 | 285 | 350 | 350 | 350 | 350 | 320 | 280 |  | 270 | 270 | 270 | 300 | 300 | 300 | 300 | 9185453
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 10 | 0 | [15 empty] | 0 | 321768
33 | Ashuganj 225 MW CCPP | 100 | 32 | 137 | 117 | 116 | 123 | 127 | 125 | 141 | 121 | 122 | 122 | 142 | 142 | 144 | 40 | 52 | 66 |  | 212 | 186 | 187 | 195 | 195 | 200 | 195 | 3137000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 270 | 310 | 270 | 270 | 270 | 270 | 300 | 275 | 270 | 270 | 270 | 270 | 240 |  | 335 | 270 | 270 | 280 | 275 | 290 | 280 | 6837000
| Ashuganj 450 MW CCPP(North) | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 285 | 285 | 285 | 315 | 290 | 285 | 285 | 285 | 285 | 280 |  | 345 | 285 | 285 | 295 | 290 | 300 | 290 | 7457800
| Ashuganj 420 MW CCPP(East) | 230 | 250 | 300 | 250 | 235 | 235 | 250 | 250 | 260 | 230 | 230 | 230 | 260 | 285 | 285 | 285 | 250 | 280 |  | 320 | 390 | 285 | 285 | 285 | 297 | 285 | 6472000
35 | Ashuganj 55 MW PP (Precision) | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [17 empty] | 0 | 48000
36 | Chandpur 150 MW CCPP | 85 | 86 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 90 | 90 | 85 |  | 85 | 85 | 85 | 85 | 87 | 87 | 87 | 2046370
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 403 | 402 | 402 | 401 | 401 | 363 | 332 | 300 | 282 | 282 | 283 | 283 | 329 | 350 | 337 | 300 | 300 | 282 |  | 362 | 412 | 407 | 413 | 403 | 401 | 401 | 8485200
| Meghnaghat Unique power | 584 | 584 | 584 | 584 | 584 | 420 | 420 | 350 | 300 | 300 | 300 | 300 | 350 | 350 | 320 | 260 | 255 | 255 |  | 350 | 400 | 390 | 584 | 584 | 584 | 584 | 10106363
| Summit Meghanghat-2 589 MW(Gas) | [23 empty] | 40 | 65 | 64 | 99723
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 350 | 350 | 300 | 300 | 300 | 300 |  | 340 | 420 | 420 | 420 | 420 | 420 | 420 | 9072500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 162 | 164 | 165 | 165 | 166 | 166 | 166 | 166 | 166 | 166 | 165 | 149 | 150 | 148 | 162 | 171 | 141 | 141 |  | 201 | 202 | 202 | 202 | 203 | 203 | 203 | 3927360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 0 | 0 | 2 | 0 | 2 | 3 | 4 | 2 | 3 | 2 | 8 | 2 | [8 empty] | 28090
44 | Fenchugonj CCPP Phase-1 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 22 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 677000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1385640
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 61 | 61 | 62 | 61 | 61 | 61 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 62 | 62 | 61 | 61 | 61 | 61 | 1240896
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | [25 empty] | 0 | 0
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 19 | 30 | 30 | 30 | 5 | 5 |  | 30 | 40 | 49 | 50 | 50 | 50 | 50 | 671400
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 285 | 285 | 280 | 270 | 290 | 290 | 275 | 270 | 290 | 300 | 300 | 305 | 280 | 280 | 290 | 300 |  | 295 | 275 | 300 | 295 | 290 | 300 | 305 | 7086000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 310 | 320 | 320 | 345 | 320 | 320 | 320 | 320 | 320 | 305 |  | 370 | 310 | 310 | 346 | 346 | 352 | 345 | 7831900
58 | Nababganj 55 MW PP (Southern power ) | [25 empty] | 0 | 0
59 | Tangail Palli Power Gen 22 MW | 3 | 6 | 6 | 6 | 6 | 0 | [19 empty] | 0 | 30960
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 68 | 72 | 68 | 66 | 64 | 58 | 52 | 52 | 48 | 48 | 50 | 54 | 50 | 36 | 26 | 40 | 50 | 52 |  | 62 | 58 | 62 | 64 | 64 | 68 | 68 | 1332480
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 30 | 30 | 30 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1079520
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 10 | 10 |  | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 233800
69 | Summit Ashulia | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 253800
70 | Summit Madhabdi | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 162360
71 | Maona 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 205600
72 | Rupganj 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 297700
73 | Ghorashal 108 MW PP (Regent) | 62 | 62 | 62 | 62 | 62 | 10 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 36 | 42 | 53 | 60 | 60 | 60 | 709863
| Feni Lanka Power | 17 | 17 | 17 | 0 | [13 empty] | 4 |  | 34 | 70 | 70 | 70 | 70 | 70 | 114 | 448020
| Chowmuhani 113 MW | 62 | 38 | 38 | 38 | 38 | 39 | 38 | 38 | 38 | 41 | 38 | 45 | 38 | 38 | 34 | 18 | 18 | 19 |  | 71 | 77 | 76 | 77 | 77 | 77 | 78 | 1122240
| Manikgonj 162MW PP(MPGL) | [25 empty] | 0 | 0
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 0 | [19 empty] | 0 | 84960
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 50 | 51 | 51 | 50 | 50 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 1 | 10 | 8 | 8 | 8 | 23 | 430584
| Gazipur 100 MW PP | [25 empty] | 0 | 0
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 3 | 1 |  |  | 0 | [9 empty] | 15360
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [25 empty] | 0 | 0
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 254 | 276 | 261 | 274 | 257 | 285 | 275 | 275 | 258 | 293 | 264 | 303 | 295 | 285 | 270 | 278 | 243 | 244 |  | 312 | 260 | 278 | 291 | 290 | 295 | 298 | 6664815
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [25 empty] | 0 | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima) | 37 | 37 | 34 | 34 | 37 | 5 | 5 | 5 | 5 | 5 |  |  |  | 5 | 5 | 5 | 5 | 5 |  | 30 | 39 | 39 | 36 | 39 | 39 | 36 | 475416
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 51 | 5 | 5 | 5 | 5 | 5 |  |  |  | 3 | 5 | 5 | 5 | 5 |  | 8 | 18 | 21 | 51 | 51 | 51 | 51 | 571162
94 | Gagnagar 102 MW PP (Digital Power) | [25 empty] | 0 | 0
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | [21 empty] | 9 | 20 | 19 | 18 | 19 | 87360
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3357164
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1600
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 8 | 8 | 8 | 8 | 8 | 0 | [19 empty] | 0 | 48000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 85 | 55 | 19 | 17 | 17 | 0 |  |  |  | 17 | 17 | 17 | 17 | 16 | [5 empty] | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 395280
115 | Juldah 100 MW PP Unit-3 (Acorn) | [19 empty] | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 116160
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 40 | 100 | 84 | 100 | 100 | 100 | 65 | 817440
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 240 | 304 | 303 | 303 | 303 | 303 | 303 | 303 | 305 | 307 | 306 | 336 | 306 | 307 | 306 | 306 | 306 | 303 |  | 368 | 307 | 306 | 367 | 370 | 380 | 371 | 7532000
| Jamalpur 115 MW PP (United) | 35 | 35 | 16 | 16 | 16 | 0 |  |  | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 322800
| Anwara 300 MW PP (United) | [12 empty] | 0 | [6 empty] | 5 | 16 | 16 | 15 | 15 | 15 | 15 | 85309
| Juldah unit-2 (Acorn) | [19 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 126720
| Anlima Energy Ltd. | [19 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 | 86564
| Bhairob 54.5 MW | [25 empty] | 0 | 0
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 6 | 6 | 10 | 4 | 9 | 18 | 6 | 8 | 4 | 4 | 2 | [8 empty] | 79300
| Chandpur 115(Doreen) | 89 | 85 | 88 | 115 | 89 | 87 | 87 | 32 | 32 | 32 | 33 | 33 | 41 | 65 | 40 | 16 | 16 | 16 |  | 49 | 75 | 68 | 65 | 65 | 65 | 90 | 1471680
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | [20 empty] | 17 | 17 |  |  |  | 0 | 8364
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 62 | 39 | 48 | 56 | 19 | 21 | 47 | 0 | 0 | 5 | 37 | 24 | 30 | 12 | 4 | 6 | 0 | 0 |  | 4 | 12 | 20 | 40 | 42 | 35 | 36 | 523200
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 0 | 2 | 6 | 15 | 27 | 30 | 71 | 8 | 11 | 4 | 3 | 1 | [8 empty] | 190482
Matarbari 2*600 MW (CPGCL)
120 | Eastern Zone Total | 6286 | 6249 | 6237 | 6194 | 6107 | 5446 | 5447 | 5193 | 5016 | 4939 | 4937 | 5039 | 5273 | 5229 | 5007 | 4794 | 4632 | 4569 |  | 5651 | 5967 | 5953 | 6381 | 6411 | 6505 | 6503 | 135439291
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 31 | 16 | 16 | 16 | 16 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 35 | 35 | 35 | 35 | 0 | [19 empty] | 0 | 233280
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 4 | 11 | 22 | 21 |  |  | 1 | 1 | 1 | 2 | 4 | 1 | [8 empty] | 64800
131 | Rampal 1320 MW (BIFPCL) | 506 | 507 | 509 | 506 | 510 | 461 | 406 | 409 | 358 | 361 | 366 | 360 | 357 | 358 | 360 | 356 | 358 | 358 |  | 360 | 358 | 359 | 358 | 360 | 358 | 359 | 9941818
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2574955
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 32 | 32 | 32 | 32 | 0 | [19 empty] | 0 | 281568
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 230 | 230 | 230 | 230 | 230 | 150 | 150 | 150 | 150 | 150 | 150 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 141 | 140 | 140 | 140 | 140 | 140 | 140 | 3949100
136 | Barisal 1 MW Solar Plant
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 126 | 126 | 126 | 126 | 126 | 126 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 130 | 80 | 80 | 80 |  | 80 | 126 | 130 | 130 | 130 | 130 | 130 | 2592000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 6 | 3 | 7 | 2 | 6 | 3 | 5 | 4 | 4 | 5 | 10 |  | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 168036
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 925 | 928 | 928 | 928 | 929 | 929 | 928 | 928 | 928 | 928 | 923 | 923 | 923 | 922 | 923 | 923 | 923 | 922 |  | 922 | 921 | 921 | 922 | 921 | 922 | 922 | 22383272
147 | Bheramara 410 MW CCPP | 345 | 345 | 340 | 345 | 345 | 345 | 345 | 345 | 345 | 250 | 250 | 300 | 345 | 345 | 345 | 345 | 300 | 250 |  | 250 | 345 | 345 | 360 | 365 | 375 | 360 | 8181216
148 | Payra 1320 MW | 1040 | 800 | 700 | 600 | 580 | 560 | 560 | 560 | 540 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 |  | 540 | 730 | 770 | 760 | 760 | 760 | 760 | 16841100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 148 | 163 | 170 | 170 | 170 | 170 | 170 | 4114000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 5400
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 184 | 176 | 175 | 176 | 176 | 166 | 155 | 157 | 156 | 157 | 157 | 161 | 166 | 177 | 156 | 157 | 140 | 140 |  | 140 | 140 | 140 | 161 | 161 | 165 | 170 | 4108991
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 163 | 162 | 160 | 160 | 160 | 160 | 160 | 161 | 161 | 161 | 161 | 177 | 210 | 177 | 159 | 160 | 140 | 140 |  | 140 | 140 | 140 | 165 | 164 | 169 | 173 | 4153736
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 364 | 318 | 300 | 295 | 296 | 347 | 316 | 307 | 298 | 348 | 347 | 348 | 346 | 344 | 309 | 250 | 250 | 230 |  | 300 | 386 | 314 | 350 | 350 | 348 | 348 | 7739709
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 138456
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | 36 | 0 | [24 empty] | 55606
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [25 empty] | 0 | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 0 | [23 empty] | 0 | 46723
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 7459
178 | Energypac Power Venture Thakurgaon Ltd. | 72 | 0 | [17 empty] | 35 | 35 | 35 | 35 | 70 | 70 | 72 | 402048
| Intraco Solar 30 MW | [6 empty] | 0 | 1 | 1 | 2 | 10 | 2 | 3 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 23839
| Adani Power Jharkhanda Ltd | 747 | 746 | 656 | 581 | 578 | 497 | 476 | 476 | 472 | 435 | 432 | 433 | 432 | 431 | 434 | 430 | 432 | 431 |  | 513 | 608 | 618 | 582 | 587 | 580 | 580 | 12377455
178 | Teesta Solar Limited | [7 empty] | 3 | 31 | 3 | 28 | 17 | 40 | 30 | 16 | 12 | 3 | 2 | [8 empty] | 236310