## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-06-27 | Thursday
|  | Date (day): | 2024-06-27 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13951.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14691 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-06-26 | 2024-06-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 398 | 397 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 370 | 400 | 400 | 50 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 29 | 16 | 34 |  | 20 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 149 | 135 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 80 | 68 | 68 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 |  | 0
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 12 |  | 63 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 41 | 52 | 40 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 293 | 277 | 280 | 320 | 15 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 82 | 24 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 21 | 29 | 31 | 31 |  | 49 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 7 | 8 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 12 | 14 | 14 |  | 19 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 260 | 278 | 263 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 132 | 135 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 72 | 52 | 72 | 33 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 53 | 17 | 52 | 52 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 8 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 2440 | 2678 | 2532 | 2854 | 1506 | 1171
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 20 | 20 | 30 |  | fuel shortage
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 149 | 126 | 110 | 145 | 85 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 212 | 221 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 68 | 68 | 68 | 68 | 37 |  | Fuel Shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 67 | 67 | 54 | 72 | 26 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 85 | 85 | 68 | 68 |  | 34 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 25 | 35 | 25 | 25 | 75 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 62 | 24 | 24 | 76 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 12 | 5 | 10
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 25 | 23 | 25 | 32 | 76 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 69 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 40 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 110 | 110 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 62 | 50 | 62 | 38 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 27 | 53 | 17 | 72 | 44 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 490 | 429 | 612 | 612 |  | 612 | Unit-2 shut down
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 1 | 9 | 40 | 40 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 470 | 469 | 570 | 570 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 80 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 2045 | 2136 | 2281 | 2436 | 923 | 976
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 212 | 210 | 210
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 280 | 280 | 280 | 80 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 250 | 280 | 280 | 80 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 230 | 230 | 170 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 15 | 5 | 5 | 40 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 13 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 52 | 140 | 55 | 135 |  | 15 | Engine problem
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 36 | 36 | 36 |  | 16 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 40 | 50 | 50 | 113 |  | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 76 | 86 | 146 | 142
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 32 | 32 |  |  | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 42 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 50 | 114 |  | 0
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 37 | 76 | 36 | 75 | 38 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 106 | 90 | 115
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1422 | 1712 | 1605 | 1836 | 954 | 44
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 5 | 17 | 7 | 15 | 187 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 111 | 143 | 116 | 145 | 55 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 88 | 68 | 85 | 30 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 37 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 4 | 12 | 12 | 10 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 10 | 18 | 35 | 35
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 244 | 270 | 289.6 | 292 | 187 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 28 | 28 | 28 | 28 |  | 42 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 68 | 68 | 68 | 68 |  | 22 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 52 | 50 | 52
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 39 | 39 | 39 |  | 11 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 56 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 106 | 202 | 205 | 205 |  | 26
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 8 | 18 | 18 |  | 7 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 380 | 367 | 365 | 365 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 365 | 340 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1567 | 1615 | 1648 | 1650 | 20 | 447
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 920 | 918 | 927 | 927
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 48 | 16 | 98 |  | 17 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 15 | 41 | 30 | 45 |  | 9 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 33 | 64 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 250 | 250 | 250 | 160 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 32 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 14 | 55 | 36 | 53 | 52 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 21 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 811 | 856 | 850 | 850 | 384 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 2078 | 2264 | 2291 | 2323 | 1178 | 75
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 96 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 9 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 610 | 622 | 622 | 622 |  | 622 | Unit-1 Under maint
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 185 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 35 | 17 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 200 | 200 | 200 | 107 |  | Coal shortage
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1213 | 1313 | 1309 | 1327 | 222 | 686
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 32 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 35 | 35 | 35 | 35 |  |  | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 38 | 40 | 36 | 45 |  |  | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint.
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 201 | 207 | 200 | 200 | 20 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 377 | 400 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 373 | 370 | 370 | 370 |  | 748 | Unit-2 shut down
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1292 | 1377 | 1360 | 1465 | 463 | 1071
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 54 | 61 | 60 | 60 |  | 25 | machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 190 | 220 | 200 | 220 |  | 54 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 113 | 113 | 113
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 95 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 1 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 205 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 680 | 509 | 636 | 508 | 40 | 164
| Total |  |  |  |  | 27515 | 26364 | 12981 | 13874 | 13951.6 | 14691 | 5493 | 4634
A. |  | 2024-06-26 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 13874 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12476 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15400 | MW
3 | Day peak Generation : |  |  | 12981 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14705.71 | MW
4 | Evening peak Generation : |  |  | 13874 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1457 | MW
5 | Total Energy Generation : |  | 314.2261 | MKWHr | By Solar | 3.1333 | MKWHr
| By Gas : | 131.0211 | MKWHr |  | By Oil: | 74.1916 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 78.0774 | MKWHr |  | By Hydro: | 3.427 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.18336 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5493 | MW | Dhaka | 5247.01 | 4897.01 |  | 350 |  | 18:00 |  | 1174.65
|  |  | For Plants S/D or M/C prob = |  |  | 4634 | MW | Chittagong | 1337.5 | 1217.5 |  | 120 |  | 19:00 |  | 1371
|  |  | Total = |  |  | 10127 | MW | Khulna | 1928 | 1648 |  | 280 |  | 19:30 |  | 1510.81
7 | Total Gas Supplied : |  |  | 970.71 | MMCFD |  |  | Rajshahi | 1583.2 | 1433.2 |  | 150 |  | 20:00 |  | 1541.37
8 | Fuel Cost : | i) Gas : | Taka | 401646359.984 | ii) Oil : | Taka | 1367457001.32 | Comilla | 1359 | 1199 |  | 160 |  | 21:00 |  | 1457.33
|  | iii) Coal : | Taka | 543799596.97 | Total | Taka | 2312902958.274 | Mymensingh | 1150 | 1060 |  | 90 |  | 22:00 |  | 1470.7
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 3488.1 | MKWHr. | Sylhet | 627 | 507 |  | 120 |  | 23:00 |  | 1686.53
| ii) During Peak Demand : |  |  | 110 | MW (W to E) at | 21:00 | hrs | Barisal | 474 | 404 |  | 70 |  | 24:00 |  | 1799.22
| iii) Maximum : |  |  | 110 | MW at | 21:00 | hrs | Rangpur | 1000 | 883 |  | 117
10 | Maximum Temperature in Dhaka was |  |  |  | 32.0°C |  |  | Total | 14705.71 | 13248.71 |  | 1457
B. |  | 2024-06-27 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 37.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 1230 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14691 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14500 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 362.377 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12300 | MW at | 8:00 | 350 | 120 | 150 | 150 | 140 | 120 | 60 | 40 | 100
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.232 | MKWHr. | ii) HVDC Flow at Peak Time |  | 918 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9603 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.78 |  | (b) Today: | 82.52 |  | (c) Rule Curve: |  | 82.92
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-06-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 |  | 0 | 400 | 148 | 27 | 80 | 55 | 303 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 15 | 23 | 12 | 8 | 0 | 78 | 70 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 9 | 46 | 85 | 25 | 0 | 6 | 0 | 9 | 0 | 0 | 0 | 325 | 240 | 211 | 0 | 40 | 0 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 94 | 25 | 0 | 0 | 0 | 28 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 20 | 0 | 0 | 0 | 320 | 20 | 0 | 0 | 278 | 0 | 0 | 112 | 0 | 117 | 0 | 24 | 17 | 66 | 404 | 71 | 17 | 68 | 0 | 69 | 54 | 110 | 17 | 37 | 25 | 370 | 17 | 0 | 162 | 72 | 0 | 36 | 0 | 115 | 35 | 230 | 36 | 0 | 490 | 0 | 471 | 0 | 0 | 0 |  | 919 | 0 | 240 | 0 | 48 | 0 | 0 | 0 | 24 | 56 | 8 | 126 | 10 | 71 | 0 | 0 | 0 | 0 | 5 | 52 | 35 | 0 | 36 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 184 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 817 | 0 | 200 | 373 | 0 | 0 | 0 |  | 7710 | 5144 | 12854 | 3720 | 919 | 1791 | 0 | 2585 | 3167 | 148 | 0 | 430 | 94 | 0 | 0 | 2240.43 | 82.88
2:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 149 | 24 | 80 | 55 | 304 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 15 | 23 | 12 | 8 | 0 | 80 | 70 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 46 | 85 | 25 | 21 | 6 | 0 | 15 | 0 | 0 | 0 | 310 | 240 | 212 | 0 | 40 | 0 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 86 | 24 | 0 | 0 | 0 | 28 | 68 | 53 | 39 | 163 | 0 | 59 | 0 | 0 | 20 | 0 | 0 | 0 | 320 | 20 | 2 | 0 | 263 | 0 | 0 | 112 | 0 | 128 | 0 | 24 | 17 | 100 | 402 | 69 | 17 | 68 | 0 | 69 | 54 | 110 | 17 | 37 | 25 | 367 | 17 | 0 | 162 | 72 | 0 | 36 | 0 | 105 | 35 | 230 | 17 | 0 | 490 | 2 | 470 | 0 | 0 | 0 |  | 920 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 20 | 51 | 0 | 126 | 10 | 32 | 0 | 0 | 0 | 0 | 5 | 0 | 35 | 0 | 36 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 180 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 815 | 0 | 200 | 374 | 0 | 0 | 0 |  | 7698 | 4999 | 12697 | 3702 | 920 | 1794 | 0 | 2545 | 3164 | 150 | 0 | 334 | 86 | 0 | 2 | 2199.365 | 82.86
3:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 146 | 25 | 80 | 55 | 304 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 23 | 12 | 8 | 0 | 79 | 70 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 12 | 46 | 85 | 25 | 25 | 6 | 0 | 16 | 0 | 0 | 0 | 315 | 240 | 210 | 0 | 40 | 0 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 92 | 23 | 0 | 0 | 0 | 28 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 30 | 0 | 0 | 0 | 325 | 20 | 2 | 0 | 268 | 0 | 0 | 112 | 0 | 129 | 0 | 24 | 17 | 105 | 390 | 69 | 17 | 68 | 0 | 53 | 54 | 110 | 17 | 37 | 25 | 374 | 17 | 0 | 162 | 55 | 0 | 36 | 0 | 105 | 35 | 230 | 17 | 0 | 490 | 1 | 471 | 0 | 0 | 0 |  | 920 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 20 | 47 | 0 | 126 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 186 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 818 | 0 | 200 | 373 | 0 | 0 | 0 |  | 7695 | 4982 | 12677 | 3708 | 920 | 1802 | 0 | 2512 | 3168 | 149 | 0 | 325 | 92 | 0 | 1 | 2122.965 | 82.84
4:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 |  | 0 | 400 | 149 | 25 | 80 | 55 | 296 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 23 | 12 | 8 | 0 | 77 | 67 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 12 | 46 | 85 | 25 | 25 | 6 | 0 | 20 | 0 | 0 | 0 | 315 | 240 | 210 | 0 | 45 | 0 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 92 | 22 | 0 | 0 | 0 | 27 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 30 | 0 | 0 | 0 | 320 | 20 | 2 | 0 | 276 | 0 | 0 | 112 | 0 | 130 | 0 | 24 | 17 | 107 | 403 | 68 | 17 | 68 | 0 | 52 | 54 | 110 | 17 | 37 | 25 | 370 | 17 | 0 | 162 | 22 | 0 | 36 | 0 | 91 | 35 | 230 | 17 | 0 | 490 | 1 | 470 | 0 | 0 | 0 |  | 920 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 20 | 47 | 0 | 126 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 22 | 0 | 0 | 8 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 185 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 817 | 0 | 200 | 375 | 0 | 0 | 0 |  | 7657 | 4988 | 12645 | 3717 | 920 | 1804 | 0 | 2474 | 3168 | 144 | 0 | 325 | 92 | 0 | 1 | 2058.025 | 82.82
5:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 146 | 24 | 80 | 55 | 296 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 23 | 12 | 8 | 0 | 76 | 64 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 46 | 85 | 25 | 25 | 6 | 0 | 25 | 0 | 0 | 0 | 300 | 240 | 214 | 0 | 50 | 0 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 90 | 22 | 0 | 0 | 0 | 27 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 30 | 0 | 0 | 0 | 315 | 20 | 2 | 0 | 268 | 0 | 0 | 112 | 0 | 132 | 0 | 24 | 17 | 98 | 370 | 68 | 17 | 68 | 0 | 52 | 54 | 110 | 17 | 37 | 25 | 340 | 17 | 0 | 162 | 17 | 0 | 36 | 0 | 84 | 35 | 230 | 17 | 0 | 490 | 2 | 468 | 0 | 0 | 0 |  | 920 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 20 | 43 | 0 | 126 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 22 | 0 | 0 | 8 | 35 | 0 | 194 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 186 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 812 | 0 | 200 | 373 | 0 | 0 | 0 |  | 7555 | 5013 | 12568 | 3653 | 920 | 1802 | 0 | 2446 | 3194 | 140 | 0 | 321 | 90 | 0 | 2 | 2036.06 | 82.8
6:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 402 | 0 |  | 0 | 400 | 146 | 25 | 80 | 55 | 294 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 23 | 12 | 8 | 0 | 76 | 64 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 46 | 85 | 25 | 24 | 6 | 0 | 25 | 0 | 0 | 0 | 285 | 240 | 216 | 0 | 50 | 0 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 84 | 20 | 0 | 0 | 0 | 28 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 55 | 0 | 0 | 0 | 300 | 20 | 2 | 0 | 268 | 0 | 0 | 111 | 0 | 131 | 1 | 24 | 17 | 103 | 365 | 68 | 17 | 68 | 0 | 52 | 54 | 110 | 17 | 37 | 25 | 340 | 17 | 2 | 162 | 17 | 0 | 36 | 2 | 85 | 35 | 230 | 17 | 0 | 490 | 1 | 470 | 0 | 0 | 4 |  | 921 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 20 | 46 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 56 | 0 | 196 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 622 | 185 | 0 | 17 | 0 | 3 | 115 | 0 | 0 | 819 | 2 | 200 | 374 | 23 | 0 | 0 |  | 7550 | 4926 | 12476 | 3615 | 921 | 1722 | 0 | 2427 | 3227 | 140 | 0 | 302 | 84 | 37 | 1 | 1837.42 | 82.78
7:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 135 | 24 | 80 | 55 | 294 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 15 | 15 | 23 | 12 | 8 | 0 | 76 | 64 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 46 | 85 | 25 | 25 | 6 | 0 | 15 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 36 | 19 | 0 | 0 | 0 | 28 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 62 | 0 | 0 | 0 | 300 | 16 | 2 | 0 | 278 | 0 | 0 | 111 | 0 | 131 | 4 | 24 | 17 | 105 | 365 | 68 | 17 | 68 | 1 | 52 | 54 | 102 | 17 | 37 | 25 | 340 | 17 | 8 | 162 | 17 | 0 | 19 | 6 | 85 | 35 | 250 | 17 | 0 | 490 | 1 | 472 | 0 | 0 | 12 |  | 920 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 15 | 46 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 54 | 0 | 192 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 622 | 187 | 0 | 17 | 1 | 16 | 115 | 0 | 0 | 819 | 5 | 200 | 375 | 55 | 0 | 0 |  | 7519 | 4973 | 12492 | 3638 | 920 | 1714 | 0 | 2414 | 3224 | 140 | 0 | 297 | 36 | 108 | 1 | 1631.14 | 82.76
8:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 140 | 25 | 80 | 55 | 298 | 0 | 0 | 10 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 15 | 23 | 12 | 8 | 0 | 76 | 66 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 38 | 85 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 0 | 12 | 44 | 17 | 0 | 0 | 1 | 28 | 68 | 53 | 39 | 163 | 0 | 60 | 0 | 0 | 72 | 0 | 0 | 0 | 290 | 16 | 2 | 0 | 276 | 0 | 0 | 111 | 0 | 132 | 6 | 24 | 17 | 70 | 367 | 68 | 17 | 68 | 2 | 52 | 54 | 107 | 17 | 37 | 25 | 340 | 17 | 13 | 162 | 17 | 0 | 18 | 17 | 86 | 35 | 250 | 17 | 0 | 490 | 0 | 470 | 0 | 0 | 29 |  | 921 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 15 | 44 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 0 | 0 | 0 | 8 | 55 | 0 | 194 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 600 | 186 | 0 | 17 | 2 | 45 | 95 | 0 | 0 | 817 | 17 | 200 | 371 | 96 | 0 | 0 |  | 7520 | 5015 | 12535 | 3658 | 921 | 1693 | 0 | 2365 | 3197 | 142 | 0 | 287 | 44 | 228 | 0 | 1303.575 | 82.74
9:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 143 | 24 | 80 | 55 | 292 | 0 | 0 | 27 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 15 | 0 | 12 | 8 | 0 | 77 | 68 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 38 | 80 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 50 | 0 | 0 | 0 | 43 | 0 | 36 | 34 | 0 | 0 | 0 | 12 | 76 | 11 | 0 | 0 | 1 | 28 | 68 | 50 | 39 | 163 | 0 | 60 | 0 | 0 | 72 | 0 | 0 | 0 | 305 | 16 | 2 | 0 | 281 | 0 | 0 | 111 | 0 | 132 | 10 | 24 | 17 | 53 | 367 | 68 | 52 | 68 | 3 | 52 | 54 | 110 | 44 | 37 | 25 | 350 | 17 | 13 | 162 | 17 | 0 | 18 | 19 | 55 | 35 | 250 | 17 | 0 | 490 | 0 | 470 | 0 | 0 | 33 |  | 920 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 15 | 42 | 0 | 130 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 194 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 600 | 150 | 0 | 17 | 4 | 58 | 95 | 0 | 0 | 814 | 11 | 200 | 374 | 138 | 0 | 0 |  | 7598 | 5126 | 12724 | 3675 | 920 | 1736 | 0 | 2412 | 3196 | 145 | 0 | 274 | 76 | 290 | 0 | 1314.08 | 82.73
10:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 393 | 0 |  | 0 | 420 | 136 | 17 | 80 | 55 | 289 | 0 | 0 | 41 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 15 | 23 | 12 | 8 | 0 | 78 | 68 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 43 | 85 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 217 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 36 | 34 | 0 | 0 | 0 | 0 | 74 | 11 | 0 | 0 | 2 | 28 | 68 | 50 | 36 | 120 | 0 | 60 | 0 | 0 | 96 | 0 | 0 | 0 | 295 | 16 | 2 | 0 | 276 | 0 | 0 | 111 | 0 | 130 | 12 | 24 | 17 | 50 | 367 | 68 | 52 | 68 | 4 | 52 | 41 | 110 | 52 | 37 | 25 | 340 | 13 | 9 | 162 | 17 | 0 | 18 | 18 | 49 | 35 | 250 | 54 | 0 | 490 | 3 | 562 | 0 | 0 | 52 |  | 920 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 15 | 34 | 0 | 130 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 196 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 113 | 0 | 113 | 0 | 1 | 113 | 600 | 148 | 0 | 35 | 4 | 53 | 95 | 0 | 0 | 812 | 9 | 200 | 374 | 180 | 0 | 0 |  | 7726 | 5143 | 12869 | 3724 | 920 | 1607 | 0 | 2450 | 3288 | 146 | 0 | 313 | 74 | 344 | 3 | 1271.105 | 82.72
11:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 370 | 0 |  | 0 | 420 | 150 | 17 | 80 | 55 | 293 | 0 | 0 | 41 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 0 | 12 | 8 | 0 | 78 | 69 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 12 | 60 | 85 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 305 | 250 | 209 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 29 | 34 | 0 | 0 | 0 | 12 | 74 | 10 | 0 | 0 | 2 | 28 | 68 | 50 | 36 | 120 | 0 | 59 | 0 | 0 | 106 | 0 | 0 | 0 | 295 | 16 | 2 | 0 | 278 | 0 | 0 | 111 | 0 | 119 | 10 | 24 | 17 | 52 | 393 | 67 | 52 | 68 | 3 | 52 | 46 | 110 | 52 | 37 | 25 | 320 | 17 | 25 | 162 | 17 | 0 | 0 | 20 | 49 | 35 | 250 | 54 | 0 | 493 | 9 | 470 | 0 | 0 | 43 |  | 919 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 15 | 34 | 0 | 126 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 196 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 113 | 0 | 108 | 0 | 1 | 113 | 600 | 146 | 0 | 35 | 5 | 36 | 95 | 0 | 0 | 812 | 11 | 200 | 374 | 200 | 0 | 0 |  | 7656 | 5086 | 12742 | 3686 | 919 | 1569 | 0 | 2444 | 3199 | 147 | 0 | 339 | 74 | 356 | 9 | 1153.64 | 82.71
12:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 398 | 0 |  | 0 | 420 | 149 | 17 | 80 | 55 | 293 | 0 | 0 | 41 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 6 | 15 | 7 | 12 | 8 | 0 | 79 | 70 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 12 | 67 | 85 | 25 | 25 | 6 | 0 | 2 | 0 | 0 | 0 | 290 | 250 | 206 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 29 | 34 | 0 | 0 | 0 | 12 | 76 | 5 | 0 | 0 | 2 | 28 | 68 | 50 | 36 | 163 | 0 | 59 | 0 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 2 | 0 | 260 | 0 | 0 | 111 | 0 | 132 | 13 | 24 | 17 | 52 | 380 | 67 | 52 | 68 | 3 | 69 | 40 | 110 | 52 | 37 | 25 | 365 | 17 | 37 | 162 | 27 | 0 | 10 | 8 | 49 | 17 | 230 | 54 | 0 | 490 | 1 | 470 | 0 | 0 | 80 |  | 920 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 15 | 33 | 8 | 126 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 190 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 14 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 610 | 185 | 0 | 35 | 3 | 21 | 115 | 0 | 0 | 811 | 1 | 200 | 373 | 205 | 0 | 0 |  | 7718 | 5263 | 12981 | 3668 | 920 | 1781 | 0 | 2444 | 3198 | 149 | 0 | 369 | 76 | 375 | 1 | 973.145 | 82.7
13:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 403 | 0 |  | 0 | 420 | 142 | 23 | 64 | 55 | 284 | 0 | 0 | 41 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 80 | 70 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 8 | 67 | 85 | 25 | 25 | 6 | 0 | 2 | 0 | 0 | 0 | 280 | 250 | 210 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 29 | 34 | 0 | 0 | 0 | 12 | 70 | 5 | 0 | 0 | 0 | 28 | 68 | 53 | 36 | 163 | 0 | 59 | 0 | 0 | 107 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 250 | 0 | 0 | 111 | 0 | 132 | 20 | 24 | 17 | 52 | 367 | 67 | 52 | 68 | 2 | 69 | 47 | 110 | 52 | 37 | 25 | 340 | 23 | 48 | 162 | 35 | 0 | 18 | 4 | 50 | 24 | 230 | 54 | 0 | 494 | 6 | 470 | 0 | 0 | 79 |  | 920 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 17 | 32 | 8 | 126 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 193 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 37 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 622 | 186 | 0 | 35 | 5 | 79 | 115 | 0 | 0 | 810 | 2 | 200 | 374 | 181 | 0 | 0 |  | 7726 | 5339 | 13065 | 3641 | 920 | 1778 | 0 | 2497 | 3217 | 150 | 0 | 362 | 70 | 424 | 6 | 1083.925 | 82.69
14:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 403 | 0 |  | 0 | 410 | 142 | 21 | 64 | 55 | 284 | 0 | 0 | 41 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 80 | 70 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 6 | 67 | 85 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 250 | 213 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 36 | 34 | 0 | 0 | 0 | 12 | 80 | 5 | 0 | 0 | 1 | 27 | 68 | 50 | 35 | 163 | 0 | 61 | 0 | 0 | 106 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 260 | 0 | 0 | 111 | 0 | 132 | 16 | 24 | 17 | 52 | 368 | 68 | 52 | 68 | 3 | 52 | 54 | 110 | 52 | 37 | 25 | 340 | 50 | 48 | 162 | 35 | 0 | 18 | 15 | 52 | 17 | 230 | 54 | 0 | 492 | 7 | 470 | 0 | 0 | 16 |  | 920 | 0 | 245 | 0 | 16 | 0 | 0 | 0 | 20 | 28 | 8 | 126 | 9 | 48 | 0 | 0 | 0 | 0 | 4 | 0 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 2 | 56 | 0 | 196 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 622 | 186 | 0 | 35 | 0 | 72 | 115 | 0 | 0 | 812 | 15 | 200 | 372 | 172 | 0 | 0 |  | 7701 | 5358 | 13059 | 3645 | 920 | 1752 | 0 | 2550 | 3220 | 150 | 0 | 372 | 80 | 363 | 7 | 1185.155 | 82.71
15:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 410 | 143 | 18 | 52 | 55 | 283 | 0 | 0 | 41 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 79 | 70 | 0 | 0 | 5 | 215 | 0 | 0 | 0 |  | 6 | 67 | 85 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 280 | 250 | 210 | 0 | 40 | 0 | 0 | 0 | 43 | 0 | 28 | 34 | 0 | 0 | 0 | 12 | 78 | 11 | 0 | 0 | 1 | 27 | 68 | 46 | 35 | 163 | 0 | 60 | 0 | 0 | 121 | 0 | 0 | 0 | 305 | 0 | 5 | 0 | 263 | 0 | 0 | 111 | 0 | 132 | 4 | 24 | 17 | 52 | 367 | 68 | 52 | 68 | 2 | 52 | 54 | 110 | 52 | 37 | 25 | 340 | 53 | 35 | 162 | 35 | 0 | 18 | 24 | 60 | 17 | 230 | 17 | 0 | 493 | 9 | 470 | 0 | 0 | 0 |  | 919 | 0 | 240 | 0 | 15 | 0 | 0 | 0 | 20 | 30 | 8 | 126 | 9 | 64 | 0 | 0 | 0 | 0 | 5 | 0 | 35 | 0 | 37 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 195 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 0 | 113 | 0 | 6 | 113 | 622 | 108 | 0 | 35 | 1 | 21 | 115 | 0 | 0 | 812 | 25 | 200 | 374 | 156 | 0 | 0 |  | 7657 | 5247 | 12904 | 3652 | 919 | 1676 | 0 | 2589 | 3220 | 149 | 0 | 337 | 78 | 275 | 9 | 1333.18 | 82.67
16:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 148 | 23 | 52 | 40 | 284 | 0 | 0 | 41 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 76 | 68 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 6 | 67 | 85 | 25 | 25 | 6 | 0 | 0 | 0 | 0 | 0 | 300 | 250 | 204 | 0 | 40 | 0 | 0 | 0 | 43 | 0 | 28 | 34 | 0 | 0 | 0 | 12 | 94 | 11 | 0 | 0 | 1 | 27 | 68 | 49 | 35 | 163 | 0 | 54 | 0 | 0 | 129 | 0 | 0 | 0 | 300 | 8 | 2 | 0 | 255 | 0 | 0 | 111 | 0 | 124 | 7 | 24 | 17 | 53 | 375 | 68 | 52 | 68 | 1 | 52 | 54 | 110 | 52 | 37 | 50 | 340 | 50 | 16 | 162 | 35 | 0 | 18 | 15 | 50 | 17 | 230 | 17 | 0 | 495 | 8 | 470 | 0 | 0 | 8 |  | 919 | 0 | 240 | 0 | 15 | 0 | 0 | 0 | 20 | 32 | 8 | 126 | 9 | 64 | 0 | 0 | 0 | 0 | 5 | 0 | 35 | 0 | 37 | 0 | 0 | 0 | 0 | 2 | 56 | 0 | 200 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 0 | 113 | 0 | 4 | 113 | 600 | 108 | 0 | 35 | 1 | 27 | 115 | 0 | 0 | 808 | 17 | 200 | 374 | 145 | 0 | 0 |  | 7680 | 5213 | 12893 | 3680 | 919 | 1669 | 0 | 2579 | 3203 | 144 | 0 | 355 | 94 | 242 | 8 | 1343.685 | 82.66
17:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 402 | 0 |  | 0 | 400 | 144 | 33 | 63 | 40 | 284 | 0 | 0 | 41 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 75 | 65 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 67 | 85 | 25 | 24 | 9 | 0 | 2 | 0 | 0 | 0 | 300 | 240 | 211 | 0 | 40 | 0 | 0 | 0 | 10 | 0 | 36 | 34 | 0 | 0 | 0 | 12 | 88 | 11 | 0 | 0 | 0 | 27 | 68 | 5 | 5 | 163 | 0 | 55 | 0 | 0 | 179 | 0 | 0 | 0 | 310 | 8 | 2 | 0 | 255 | 0 | 0 | 111 | 0 | 126 | 3 | 37 | 17 | 47 | 330 | 68 | 52 | 68 | 0 | 52 | 54 | 110 | 98 | 50 | 50 | 320 | 53 | 7 | 162 | 36 | 0 | 18 | 7 | 50 | 30 | 230 | 17 | 0 | 400 | 36 | 470 | 0 | 0 | 5 |  | 919 | 0 | 240 | 0 | 15 | 0 | 0 | 0 | 20 | 41 | 8 | 126 | 9 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 37 | 0 | 15 | 0 | 0 | 2 | 56 | 0 | 220 | 0 | 0 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 0 | 113 | 0 | 1 | 113 | 600 | 126 | 0 | 35 | 0 | 21 | 115 | 0 | 0 | 808 | 9 | 200 | 375 | 34 | 0 | 0 |  | 7580 | 5141 | 12721 | 3665 | 919 | 1588 | 0 | 2687 | 3129 | 140 | 0 | 382 | 88 | 87 | 36 | 1221.445 | 82.65
18:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 404 | 0 |  | 0 | 390 | 141 | 34 | 80 | 40 | 284 | 0 | 0 | 41 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 38 | 64 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 66 | 85 | 12 | 25 | 20 | 0 | 3 | 0 | 0 | 0 | 315 | 240 | 208 | 0 | 40 | 0 | 0 | 0 | 10 | 0 | 37 | 43 | 0 | 0 | 0 | 12 | 84 | 11 | 0 | 0 | 0 | 27 | 68 | 5 | 5 | 120 | 0 | 55 | 0 | 0 | 182 | 0 | 0 | 0 | 290 | 8 | 2 | 0 | 275 | 0 | 0 | 111 | 0 | 132 | 0 | 48 | 17 | 70 | 364 | 68 | 52 | 68 | 0 | 52 | 54 | 110 | 98 | 74 | 50 | 340 | 53 | 2 | 162 | 53 | 0 | 18 | 2 | 49 | 35 | 230 | 17 | 0 | 377 | 25 | 468 | 0 | 0 | 2 |  | 920 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 38 | 53 | 8 | 80 | 9 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 30 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 330 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 133 | 0 | 35 | 0 | 5 | 115 | 0 | 0 | 812 | 3 | 153 | 371 | 23 | 0 | 0 |  | 7613 | 4957 | 12570 | 3681 | 920 | 1436 | 0 | 2819 | 3041 | 102 | 0 | 425 | 84 | 37 | 25 | 1174.65 | 82.64
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1371.38 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 402 | 0 |  | 0 | 390 | 146 | 33 | 80 | 40 | 282 | 0 | 0 | 41 | 82 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 45 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 39 | 65 | 0 | 0 | 14 | 216 | 0 | 0 | 0 |  | 6 | 66 | 85 | 35 | 25 | 20 | 0 | 12 | 0 | 0 | 0 | 335 | 250 | 210 | 0 | 35 | 0 | 1 | 0 | 31 | 0 | 37 | 43 | 0 | 0 | 0 | 12 | 96 | 11 | 0 | 0 | 0 | 27 | 68 | 53 | 39 | 120 | 0 | 54 | 0 | 0 | 202 | 0 | 0 | 0 | 310 | 8 | 2 | 0 | 275 | 0 | 0 | 145 | 0 | 132 | 0 | 62 | 17 | 107 | 409 | 78 | 52 | 68 | 0 | 52 | 54 | 110 | 98 | 74 | 62 | 370 | 53 | 0 | 162 | 53 | 0 | 18 | 0 | 65 | 35 | 230 | 163 | 0 | 400 | 15 | 470 | 0 | 0 | 0 |  | 919 | 0 | 225 | 0 | 48 | 0 | 0 | 0 | 39 | 54 | 32 | 126 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 45 | 35 | 0 | 35 | 0 | 30 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 395 | 54 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 217 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 812 | 0 | 200 | 373 | 0 | 0 | 0 |  | 8304 | 5260 | 13564 | 3783 | 919 | 1724 | 0 | 3121 | 3115 | 104 | 0 | 687 | 96 | 0 | 15 | 1371 | 82.61
19:30 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 404 | 0 |  | 0 | 390 | 136 | 33 | 65 | 55 | 276 | 0 | 0 | 41 | 82 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 39 | 65 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 67 | 85 | 35 | 25 | 19 | 0 | 8 | 0 | 0 | 0 | 280 | 250 | 216 | 0 | 40 | 5 | 15 | 0 | 43 | 0 | 37 | 43 | 0 | 0 | 0 | 12 | 92 | 12 | 0 | 0 | 0 | 28 | 68 | 51 | 39 | 163 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 280 | 8 | 2 | 0 | 278 | 0 | 0 | 144 | 0 | 132 | 0 | 62 | 17 | 138 | 367 | 86 | 72 | 68 | 0 | 52 | 54 | 110 | 114 | 75 | 62 | 340 | 53 | 0 | 162 | 53 | 0 | 18 | 0 | 115 | 35 | 230 | 163 | 0 | 400 | 3 | 568 | 0 | 0 | 0 |  | 919 | 0 | 225 | 0 | 48 | 0 | 0 | 0 | 39 | 55 | 32 | 126 | 10 | 96 | 0 | 0 | 0 | 0 | 0 | 85 | 35 | 0 | 37 | 0 | 30 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 414 | 54 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 600 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 811 | 0 | 200 | 371 | 0 | 0 | 0 |  | 8443 | 5375 | 13818 | 3723 | 919 | 1769 | 0 | 3247 | 3230 | 104 | 0 | 731 | 92 | 0 | 3 | 1510.81 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 393 | 0 |  | 0 | 390 | 135 | 33 | 68 | 55 | 277 | 0 | 0 | 43 | 82 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 15 | 7 | 12 | 8 | 0 | 58 | 67 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 6 | 67 | 85 | 35 | 25 | 19 | 0 | 12 | 0 | 0 | 0 | 280 | 250 | 216 | 0 | 40 | 5 | 12 | 0 | 43 | 0 | 37 | 43 | 0 | 0 | 0 | 12 | 88 | 12 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 120 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 290 | 8 | 2 | 0 | 278 | 0 | 0 | 143 | 0 | 132 | 0 | 62 | 17 | 137 | 367 | 88 | 72 | 68 | 0 | 52 | 54 | 110 | 114 | 75 | 62 | 340 | 53 | 0 | 162 | 53 | 0 | 18 | 0 | 115 | 35 | 230 | 163 | 0 | 412 | 3 | 470 | 0 | 0 | 0 |  | 921 | 0 | 235 | 0 | 48 | 0 | 0 | 0 | 46 | 58 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 0 | 4 | 85 | 35 | 0 | 47 | 0 | 30 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 310 | 55 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 620 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 812 | 0 | 200 | 371 | 0 | 0 | 0 |  | 8355 | 5331 | 13686 | 3734 | 921 | 1633 | 0 | 3245 | 3165 | 125 | 0 | 772 | 88 | 0 | 3 | 1541.37 | 82.62
21:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 397 | 0 |  | 0 | 370 | 135 | 29 | 68 | 55 | 277 | 0 | 0 | 52 | 82 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 15 | 8 | 12 | 8 | 0 | 58 | 68 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 4 | 67 | 85 | 35 | 23 | 19 | 0 | 12 | 0 | 0 | 0 | 280 | 250 | 212 | 0 | 40 | 15 | 13 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 12 | 86 | 17 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 163 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 290 | 8 | 2 | 0 | 278 | 0 | 0 | 143 | 0 | 132 | 0 | 62 | 17 | 140 | 367 | 88 | 72 | 68 | 0 | 52 | 54 | 110 | 114 | 76 | 62 | 340 | 53 | 0 | 162 | 53 | 0 | 18 | 0 | 106 | 35 | 230 | 163 | 0 | 429 | 9 | 469 | 0 | 0 | 0 |  | 918 | 0 | 250 | 0 | 48 | 0 | 0 | 0 | 41 | 64 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 0 | 5 | 85 | 35 | 0 | 40 | 0 | 30 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 377 | 55 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 856 | 0 | 200 | 370 | 0 | 0 | 0 |  | 8411 | 5463 | 13874 | 3770 | 918 | 1724 | 0 | 3248 | 3227 | 126 | 0 | 766 | 86 | 0 | 9 | 1457.33 | 82.61
22:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 405 | 0 |  | 0 | 390 | 142 | 34 | 74 | 40 | 271 | 0 | 0 | 52 | 82 | 148 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 15 | 8 | 12 | 8 | 0 | 75 | 70 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 5 | 60 | 85 | 35 | 25 | 19 | 0 | 23 | 0 | 0 | 0 | 280 | 250 | 200 | 0 | 40 | 15 | 5 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 12 | 84 | 17 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 163 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 290 | 8 | 2 | 0 | 276 | 0 | 0 | 133 | 0 | 132 | 0 | 62 | 17 | 110 | 367 | 88 | 72 | 68 | 0 | 52 | 54 | 110 | 114 | 76 | 62 | 340 | 53 | 0 | 162 | 53 | 0 | 18 | 0 | 104 | 35 | 230 | 163 | 0 | 482 | 14 | 472 | 0 | 0 | 0 |  | 917 | 0 | 250 | 0 | 48 | 0 | 0 | 0 | 41 | 59 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 0 | 5 | 85 | 35 | 0 | 40 | 0 | 30 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 396 | 55 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 790 | 0 | 200 | 371 | 0 | 0 | 0 |  | 8435 | 5425 | 13860 | 3761 | 917 | 1773 | 0 | 3197 | 3217 | 145 | 0 | 752 | 84 | 0 | 14 | 1470.7 | 82.6
23:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 405 | 0 |  | 0 | 400 | 140 | 33 | 68 | 40 | 271 | 0 | 0 | 32 | 41 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 15 | 8 | 12 | 8 | 0 | 75 | 70 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 54 | 85 | 35 | 25 | 19 | 0 | 22 | 0 | 0 | 0 | 280 | 250 | 194 | 0 | 40 | 15 | 0 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 12 | 86 | 18 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 163 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 310 | 8 | 2 | 0 | 278 | 0 | 0 | 144 | 0 | 132 | 0 | 62 | 17 | 75 | 365 | 87 | 52 | 68 | 0 | 52 | 54 | 110 | 114 | 68 | 62 | 340 | 53 | 0 | 162 | 57 | 0 | 18 | 0 | 101 | 35 | 230 | 17 | 0 | 490 | 20 | 470 | 0 | 0 | 0 |  | 918 | 0 | 250 | 0 | 48 | 0 | 0 | 0 | 40 | 59 | 24 | 130 | 9 | 96 | 0 | 0 | 0 | 0 | 5 | 85 | 35 | 0 | 47 | 0 | 30 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 414 | 55 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 861 | 0 | 200 | 372 | 0 | 0 | 0 |  | 8187 | 5497 | 13684 | 3752 | 918 | 1812 | 0 | 3049 | 3295 | 145 | 0 | 607 | 86 | 0 | 20 | 1686.53 | 82.59
24:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 405 | 0 |  | 0 | 400 | 149 | 34 | 68 | 40 | 271 | 0 | 0 | 26 | 40 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 15 | 8 | 12 | 8 | 0 | 75 | 70 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 54 | 85 | 35 | 25 | 6 | 0 | 25 | 0 | 0 | 0 | 280 | 240 | 201 | 0 | 40 | 5 | 0 | 0 | 43 | 0 | 36 | 43 | 0 | 0 | 0 | 12 | 90 | 17 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 163 | 0 | 58 | 0 | 0 | 202 | 0 | 0 | 0 | 310 | 8 | 2 | 0 | 278 | 0 | 0 | 144 | 0 | 132 | 0 | 62 | 19 | 67 | 371 | 88 | 17 | 68 | 0 | 52 | 54 | 110 | 114 | 67 | 62 | 345 | 53 | 0 | 162 | 72 | 0 | 18 | 0 | 85 | 35 | 230 | 17 | 0 | 490 | 27 | 471 | 0 | 0 | 0 |  | 910 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 30 | 53 | 8 | 130 | 9 | 96 | 0 | 0 | 0 | 0 | 5 | 85 | 35 | 0 | 45 | 0 | 22 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 414 | 55 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 868 | 0 | 200 | 371 | 0 | 0 | 0 |  | 8100 | 5416 | 13516 | 3752 | 910 | 1824 | 0 | 2935 | 3303 | 145 | 0 | 530 | 90 | 0 | 27 | 1799.22 | 82.58
KWH | 0 | 0 | 0 | 2835000 | 0 | 0 | 0 | 9720000 | 0 |  | 0 | 9233500 | 3479273 | 608640 | 1631195 | 1241268 | 6977576 | 0 | 0 | 683366 | 657936 | 1389600 | 1000 | 0 | 0 | 0 | 1302120 | 1314939 | 1168601 | 0 | 340200 | 353520 | 320900 | 269600 | 195360 | 0 | 1791000 | 1636000 | 0 | 0 | 112449 | 5158368 | 0 | 0 | 0 |  | 220560 | 1343040 | 1994590 | 586080 | 583680 | 228480 | 0 | 253440 | 0 | 0 | 0 | 7575500 | 6039000 | 5101000 | 0 | 1027110 | 59040 | 30720 | 0 | 986708 | 0 | 833360 | 803290 | 0 | 0 | 0 | 272980 | 1960320 | 355200 | 0 | 0 | 11100 | 656000 | 1618560 | 1152600 | 865224 | 3599918 | 0 | 1396800 | 0 | 0 | 2633600 | 0 | 0 | 0 | 7462500 | 280152 | 60192 | 0 | 6501055 | 0 | 0 | 2860800 | 0 | 3130992 | 93555 | 828480 | 431040 | 1928654 | 9124000 | 1748400 | 1004160 | 1693636 | 26641 | 1352400 | 1311497 | 2690570 | 1375980 | 1160040 | 870720 | 8415400 | 797760 | 274690 | 3913920 | 952200 | 0 | 528480 | 152460 | 1860480 | 775080 | 5740400 | 1206036 | 0 | 11470908 | 183360 | 11360000 | 0 | 0 | 351064 |  | 22232000 | 0 | 6120000 | 0 | 527040 | 0 | 0 | 0 | 545280 | 1074304 | 206250 | 2831000 | 22305 | 1340064 | 0 | 0 | 0 | 0 | 31058 | 519392 | 828200 | 0 | 720000 | 0 | 294121 | 0 | 0 | 109242 | 1598792 | 0 | 4923000 | 0 | 0 | 0 | 0 | 5002200 | 0 | 0 | 0 | 0 | 0 | 9276945 | 742080 | 0 | 2732640 | 0 | 2677315 | 0 | 31553 | 2742336 | 15576000 | 4265455 | 0 | 705600 | 28260 | 450720 | 2683968 | 0 | 0 | 19680000 | 137270 | 4778200 | 8690545 | 1576000 | 0 | 0 |  | 188527013 | 125699135 | 314226148 | 90392540 | 22232000 | 40628588 | 0 | 64240801 | 78077445 | 3427000 | 0 | 9950781 | 1960320 | 3133313 | 183360 | 0
Fuel Cost | 0 | 0 | 0 | 12615750 | 0 | 0 | 0 | 27993600 | 0 |  | 0 | 29362530 | 11899113.66 | 12026726.4 | 30503346.5 | 21871142.16 | 21281606.8 | 0 | 0 | 13503312.16 | 11809951.2 | 26986032 | 18650 | 0 | 0 | 0 | 23776711.2 | 20723438.64 | 21373712.29 | 0 | 255150 | 0 | 0 | 0 | 3498897.6 | 0 | 0 | 0 | 0 | 0 | 2129784.06 | 16455193.92 | 0 | 0 | 0 |  | 3879650.4 | 23650934.4 | 35723106.9 | 11170684.8 | 11422617.6 | 3760780.8 | 0 | 0 | 0 | 0 | 0 | 21135645 | 18479340 | 16935320 | 0 | 3317565.3 | 198964.8 | 134553.6 | 0 | 3956699.08 | 0 | 14925477.6 | 14507417.4 | 0 | 0 | 0 | 204735 | 12859699.2 | 1104672 | 0 | 0 | 0 | 2558400 | 6037228.8 | 5244330 | 3936769.2 | 12311719.56 | 0 | 7752240 | 0 | 0 | 7347744 | 0 | 0 | 0 | 23059125 | 210114 | 45745.92 | 0 | 132621522 | 0 | 0 | 54955968 | 0 | 55136769.12 | 0 | 14755228.8 | 7478544 | 31977083.32 | 24178600 | 33324504 | 18838041.6 | 30383829.84 | 0 | 22111740 | 25495501.68 | 48268825.8 | 26294977.8 | 22516376.4 | 15507523.2 | 22384964 | 13617763.2 | 0 | 71585596.8 | 15977916 | 0 | 9443937.6 | 0 | 33525849.6 | 13129855.2 | 17048988 | 16980986.88 | 0 | 79952228.76 | 0 | 67024000 | 0 | 0 | 0 |  | 62471920 | 0 | 18054000 | 0 | 9144144 | 0 | 0 | 0 | 10256716.8 | 20207658.24 | 3671250 | 8945960 | 105725.7 | 23102703.36 | 0 | 0 | 0 | 0 | 569914.3 | 8730979.52 | 17624096 | 0 | 12895200 | 0 | 5267707.11 | 0 | 0 | 82696.194 | 17634675.76 | 0 | 41550120 | 0 | 0 | 0 | 0 | 16657326 | 0 | 0 | 0 | 0 | 0 | 27088679.4 | 12674726.4 | 0 | 54160924.8 | 0 | 53332114.8 | 0 | 0 | 54407946.24 | 100932480 | 13265565.05 | 0 | 13653360 | 0 | 0 | 46566844.8 | 0 | 0 | 143664000 | 0 | 35597590 | 57444502.45 | 0 | 0 | 0 |  | 1498473050.55 | 889761526.924 | 2388234577.474 | 271281549.734 | 62471920 | 130364810.25 | 0 | 1191262287.57 | 543799596.97 | 0 | 0 | 176194713.75 | 12859699.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 398 | 0 |  | 0 | 420 | 149 | 17 | 80 | 55 | 293 | 0 | 0 | 41 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 6 | 15 | 7 | 12 | 8 | 0 | 79 | 70 | 0 | 0 | 0 | 212 | 0 | 0 | 0 |  | 12 | 67 | 85 | 25 | 25 | 6 | 0 | 2 | 0 | 0 | 0 | 290 | 250 | 206 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 29 | 34 | 0 | 0 | 0 | 12 | 76 | 5 | 0 | 0 | 2 | 28 | 68 | 50 | 36 | 163 | 0 | 59 | 0 | 0 | 106 | 0 | 0 | 0 | 310 | 0 | 2 | 0 | 260 | 0 | 0 | 111 | 0 | 132 | 13 | 24 | 17 | 52 | 380 | 67 | 52 | 68 | 3 | 69 | 40 | 110 | 52 | 37 | 25 | 365 | 17 | 37 | 162 | 27 | 0 | 10 | 8 | 49 | 17 | 230 | 54 | 0 | 490 | 1 | 470 | 0 | 0 | 80 |  | 920 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 15 | 33 | 8 | 126 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 2 | 54 | 0 | 190 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 14 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 610 | 185 | 0 | 35 | 3 | 21 | 115 | 0 | 0 | 811 | 1 | 200 | 373 | 205 | 0 | 0 |  | 12981 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 397 | 0 |  | 0 | 370 | 135 | 29 | 68 | 55 | 277 | 0 | 0 | 52 | 82 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 14 | 15 | 8 | 12 | 8 | 0 | 58 | 68 | 0 | 0 | 17 | 221 | 0 | 0 | 0 | 0 | 4 | 67 | 85 | 35 | 23 | 19 | 0 | 12 | 0 | 0 | 0 | 280 | 250 | 212 | 0 | 40 | 15 | 13 | 0 | 43 | 0 | 36 | 42 | 0 | 0 | 0 | 12 | 86 | 17 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 163 | 0 | 56 | 0 | 0 | 202 | 0 | 0 | 0 | 290 | 8 | 2 | 0 | 278 | 0 | 0 | 143 | 0 | 132 | 0 | 62 | 17 | 140 | 367 | 88 | 72 | 68 | 0 | 52 | 54 | 110 | 114 | 76 | 62 | 340 | 53 | 0 | 162 | 53 | 0 | 18 | 0 | 106 | 35 | 230 | 163 | 0 | 429 | 9 | 469 | 0 | 0 | 0 |  | 918 | 0 | 250 | 0 | 48 | 0 | 0 | 0 | 41 | 64 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 0 | 5 | 85 | 35 | 0 | 40 | 0 | 30 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 377 | 55 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 856 | 0 | 200 | 370 | 0 | 0 | 0 |  | 13874 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 |  | 0 | 400 | 150 | 34 | 80 | 55 | 320 | 0 | 0 | 60 | 92 | 149 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 25 | 14 | 8 | 0 | 75 | 70 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 12 | 72 | 68 | 25 | 32 | 20 | 0 | 10 | 0 | 0 | 0 | 280 | 280 | 210 | 0 | 50 | 5 | 0 | 0 | 51 | 0 | 36 | 52 | 0 | 0 | 32 | 12 | 142 | 15 | 0 | 0 | 0 | 28 | 68 | 52 | 39 | 163 | 0 | 60 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 18 | 2 | 0 | 280 | 0 | 0 | 145 | 0 | 149 | 0 | 24 | 17 | 135 | 365 | 85 | 72 | 68 | 0 | 52 | 54 | 110 | 114 | 75 | 62 | 350 | 52 | 0 | 162 | 72 | 0 | 35 | 0 | 115 | 35 | 230 | 163 | 0 | 612 | 40 | 570 | 0 | 0 |  |  | 927 | 0 | 250 | 0 | 98 | 0 | 0 | 0 | 45 | 60 | 40 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 90 | 35 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 850 | 0 | 200 | 370 | 0 | 0 |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 400 | 150 | 16 | 68 | 55 | 280 | 0 | 0 | 40 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 25 | 14 | 8 | 0 | 40 | 70 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 12 | 54 | 68 | 25 | 25 | 20 | 0 | 5 | 0 | 0 | 0 | 280 | 280 | 210 | 0 | 50 | 5 | 0 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 32 | 12 | 146 | 7 | 0 | 0 | 1.6 | 28 | 68 | 50 | 39 | 163 | 0 | 60 | 0 | 0 | 205 | 0 | 0 | 0 | 300 | 18 | 2 | 0 | 263 | 0 | 0 | 116 | 0 | 135 | 20 | 24 | 17 | 55 | 365 | 68 | 52 | 68 | 5 | 52 | 54 | 110 | 50 | 36 | 50 | 350 | 17 | 50 | 162 | 17 | 0 | 35 | 35 | 90 | 35 | 230 | 54 | 0 | 612 | 40 | 570 | 0 | 0 | 70 |  | 927 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 30 | 50 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 32 | 0 | 50 | 35 | 0 | 36 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 400 | 36 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 622 | 220 |  | 17 | 6 | 100 | 95 | 0 | 0 | 850 | 30 | 200 | 370 | 130 | 0 | [5 empty] | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 420 | 149 | 24 | 68 | 40 | 279 | 0 | 0 | 12 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 15 | 8 | 12 | 8 | 0 | 40 | 67 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 6 | 54 | 68 | 35 | 19 | 6 | 0 | 5 | 0 | 0 | 0 | 280 | 280 | 202 | 0 | 45 | 5 | 0 | 0 | 43 | 0 | 28 | 25 | 0 | 0 | 0 | 12 | 80 | 11 | 0 | 0 | 0 | 28 | 68 | 50 | 39 | 120 | 0 | 58 | 0 | 0 | 204 | 0 | 0 | 0 | 300 | 8 | 2 | 0 | 263 | 0 | 0 | 117 | 0 | 132 | 11 | 48 | 17 | 65 | 346 | 68 | 17 | 68 | 2 | 51 | 54 | 110 | 52 | 38 | 50 | 345 | 17 | 1 | 162 | 17 | 0 | 18 | 8 | 69 | 17 | 230 | 17 | 0 | 278 | 42 | 420 | 0 | 0 | 23 | 0 | 911 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 10 | 43 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 201 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 113 | 0 | 113 | 0 | 1 | 113 | 600 | 220 | 0 | 17 | 0 | 15 | 94 | 0 | 0 | 866 | 2 | 200 | 374 | 27 | 0 | 0 | 0 |  |  |  | 131021128 | 22232000 | 0 | 78077445 | 74191582 | 1960320 | 3133313 | 183360 | 3427000 |  |  | 314226148
[8 empty] | 299430 |  |  |  | 25503 |  |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 | [8 empty] | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [8 empty] | 131.0211 | 22.232 | 0 | 78.0774 | 74.1916 | 1.9603 | 3.1333 | 0.18336 | 3.427
| Minimum Generation |  | 12476 | 6:00
| Highest Generation |  | 13874 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [72 empty] | 314.2261
| Day Peak Generation |  | 12981 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 13874 | 21:00 |  |  |  |  | 10500 | [197 empty] | 202699852
| HVDC Max Flow |  | 921 | 6:00 | [202 empty] | 202.6999
| HVDC EvPeak Flow |  | 918 | 21:00
| Load factor L.F |  | 94.37% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-06-27
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-06-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12981 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12300
Evening Peak Generation : |  |  | 13874 | MW Hour : | 21:00 | Available Max Generation : |  | 14691
E.P. Demand (at gen end) : |  |  | 15400 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16000
Maximum Generation : |  |  | 13874 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 314.2261 | System Load Factor : | 94.37% | Load Shed : |  | 1230
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 110 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-06-27
Actual : |  | 82.52 | Ft.(MSL) , | Rule curve : | 82.92 | Ft.( MSL )
Gas Consumed : |  | Total = | 970.71 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 401646359.984
: |  |  | Coal : | 543799596.97 | Oil : | 1367457001.32 | Total : | 2312902958.274
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 350 | 8400:00 | 5213.1791 |  |  | 350 | 5.076%
Chittagong Area |  | 120 | 2880:00 | 1436.3552 |  |  | 120 | 7.105%
Khulna Area |  | 280 | 6720:00 | 2013.2249 |  |  | 150 | 7.539%
Rajshahi Area |  | 150 | 3600:00 | 1750.9366 |  |  | 150 | 7.997%
Cumilla Area |  | 160 | 3840:00 | 1440.1582 |  |  | 140 | 7.713%
Mymensingh Area |  | 90 | 2160:00 | 1071.6925 |  |  | 120 | 8.111%
Sylhet Area |  | 120 | 2880:00 | 600.0987 |  |  | 60 | 7.351%
Barisal Area |  | 70 | 1680:00 | 500.6751 |  |  | 40 | 8.184%
Rangpur Area |  | 117 | 2808:00 | 979.2196 |  |  | 100 | 8.174%
Total |  | 1457 |  | 15005.5398 |  |  | 1230
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:16 | Cumilla(S) 132/33kV S/S TR-2 HT is restored.
| 08:16 | Cumilla(S) 132/33kV S/S TR-2 LT is restored.
08:20 | 20:25 | Chapai 132/33kV S/S T-3 (425T) HT Scheduled S/D.
08:20 | 20:27 | Chapai 132/33kV S/S T-3 (425T) LT Scheduled S/D.
10:26 | 10:55 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to Bus coupler red hot maintenance. | [5 empty] | 35 MW load interrup.
10:26 | 10:49 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to Bus coupler red hot maintenance.
10:26 | 10:55 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to Bus coupler red hot maintenance.
10:27 | 10:48 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to Bus coupler red hot maintenance.
10:40 | 14:06 | Barishal-Bhandaria 132 kV Ckt-1 Scheduled S/D from Barishal 132/33kV end Due to Approved by ALDC.
| 10:45 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 11:53 | Srinagar 132/33kV S/S Tr-02 HT is restored.
| 11:53 | Srinagar 132/33kV S/S Tr-02 LT is restored.
12:23 | 15:50 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Forced S/D Due to Emergency Maintenance.
12:23 | 15:51 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Forced S/D Due to Emergency Maintenance.
12:31 | 13:44 | Khulna (C) S/S TR-1 425T HT Forced S/D Due to Due to temperature rise of 33 kv loop point.
12:31 | 13:45 | Khulna (C) S/S TR-1 425T LT Forced S/D Due to Due to temperature rise of 33 kv loop point.
13:46 | 14:09 | Bhandaria 132/33kV S/S Transformer-2 LT Forced S/D Due to | [5 empty] | 37 MW load interrup.
13:46 | 14:09 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to axiliary fuse maintenance.
13:48 |  | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar 132/33kV end Due to Srinagar side
PT balast.
13:50 | 14:08 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to axiliary fuse maintenance.
13:50 | 14:07 | Bhandaria 132/33kV S/S Transformer-2 HT Forced S/D Due to axiliary fuse maintenance.
14:05 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Forced S/D from Bhandaria 132/33kV end Due to power received from Barishal by Bus coupler.
14:38 | 15:30 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Tripped showing PRD relays Due to PRD. | [5 empty] | 22 MW load interrup.
14:42 | 15:27 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Noapara 132/33kV end Due to Removing Kite from Bottom Conductor and
from Jashore 132/33kV end Due to Due to kite tying in Noapara CKT-1.
| 14:58 | AKSML-Khulshi 132kV Ckt-1 is restored.
| 18:05 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT is restored.
| 18:05 | Kabirpur - Manikganj 132kV Ckt-1 is restored.
| 18:26 | Meghnaghat-Madunaghat 400kV ckt.-1 was switched on
| 18:46 | Patuakhali 132/33kV S/S 425T (T-3) HT is restored.
| 18:47 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
| 20:27 | Chapai 132/33kV S/S T-3 (425T) LT is restored.
20:28 |  | Patuakhali 132/33kV S/S 425T (T-3) HT Forced S/D Due to T-3 33kV CB Pole problem.
20:36 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Forced S/D Due to T-3 33kV CB pole problem.
20:46 | 23:49 | Tangail 132/33kV S/S Tr-3 LT Tripped showing REF630 & RET670 relays Due to Due to T3 auxillary bus loop out. | [5 empty] | 30 MW load interup.
20:46 | 23:48 | Tangail 132/33kV S/S Tr-3 HT Tripped showing REF630 & RET670 relays Due to Due to T3 auxillary bus loop out.
06:02 |  | Halishahar 132/33kV S/S Halishahar-Khulshi-Ckt.-3 Project Work S/D Due to Lilo connection at anandabazar s/s end.
06:10 |  | Thakurgaon 132/33kV S/S T-1(422T) LT Scheduled S/D Due to T-1 Oil leakage.
06:10 |  | Thakurgaon 132/33kV S/S T-1(422T) HT Scheduled S/D Due to T-1 Oil leakage.
06:11 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Project Work S/D Due to Project work. | [5 empty] | 20 MW load interup.
06:14 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Project Work S/D Due to Project work.
06:19 |  | Rampur 230/132/33 S/S Halishahar-1 Project Work S/D
06:28 | 07:38 | Benapole 132/33kV S/S Transformer-1(406T) HT Forced S/D Due to Red Hot at Bagachara Feeder. | [5 empty] | 36 MW load interup.
06:35 |  | Kabirpur - Manikganj 132kV Ckt-1 Project Work S/D from Manikganj 132/33kV end Due to Project work. | [5 empty] | 20 MW load interup in
Manikganj 132/33 kV end.
06:50 |  | Mirpur 132/33kV S/S T1 HT Project Work S/D Due to 132kV CB Replacement Work.
06:50 |  | Mirpur 132/33kV S/S T1 LT Project Work S/D Due to 132kV CB Replacement Work.
07:17 |  | Sonargaon 132/33kV S/S Tr-1 LT Scheduled S/D Due to Y-ph CT replacement.
07:18 |  | Sonargaon 132/33kV S/S Tr-1 HT Scheduled S/D Due to Y-ph CT replacement work.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-06-26
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2835000 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 397 | 9720000
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 9233500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 29 | 608640 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 135 | 3479273 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 68 | 1631195 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1241268
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 1000 | Line S/D by PGCB.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 52 | 683366 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 277 | 6977576 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 657936 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1302120
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1389600
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1314939
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1168601
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 29 | 693720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 320900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 269600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 195360 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 6501055 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 3130992
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 72 | 1004160 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 797760 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3913920
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 152460
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 775080 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5634 | 2678 | 59999021
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 112449 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 93555
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 228480 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 126 | 3427000 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 221 | 5158368
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1693636 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 67 | 1343040 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1994590 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 35 | 586080 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 828480 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 12 | 253440
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 23 | 583680 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1352400 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1311497
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2690570
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 62 | 870720 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 952200 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 1206036
60 | SS Power I |  | SS Power | 2*612 | 1224 | 429 | 11470908 | Unit-2 under maint
| Cox's Bazar Wind |  | IPP | 66 | 60 | 9 | 183360
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 469 | 11360000
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 351064
| Chattogram area Total |  |  |  | 4457 | 2136 | 48078194
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 5101000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7575500
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 250 | 6039000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5740400 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 15 | 59040 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 13 | 30720 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 986708 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 1928654 | Engine problem
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 833360 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1027110 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 431040 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 86 | 1960320
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 803290 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 272980 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1375980
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 76 | 1160040 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 106 | 1860480 | Engine problem
| Cumilla Area Total |  |  |  | 2875 | 1712 | 37185622
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 17 | 355200 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11100
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 143 | 2860800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 1748400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 274690
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 4 | 220560 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 18 | 528480 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 270 | 5999230
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 656000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1618560 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3599918
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 52 | 1152600
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 865224 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 60192 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1396800
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 202 | 2633600 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 280152 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7462500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 9124000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8415400 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1615 | 37264946
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 918 | 22232000
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 48 | 527040 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 545280 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 64 | 1074304 | Fuel shortage
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 6120000 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 206250 | Engine problem
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 742080 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 450720
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 856 | 19680000
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 2264 | 51577674
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 1340064
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 22305
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2831000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 15576000 | Unit-1 under maint
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4265455
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 705600 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 4778200 | Coal shortage
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 0
| Barisal Area Total |  |  |  | 2236 | 1313 | 29518624
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 31058 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 828200 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 720000 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 207 | 5002200
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 377 | 9276945 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 294121 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 2 | 109242 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 519392 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2732640
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2742336
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28260
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 370 | 8690545 | Machine problem.
| Rajshahi Area Total |  |  |  | 3381 | 1377 | 30974939
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1598792 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 4923000
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2677315
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31553
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2683968
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 137270
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1576000
| Rangpur Area Total |  |  |  | 950 | 509 | 13627898
| Total |  |  |  | 26364 | 13874 | 314226148
| Eastern Grid Total |  |  |  | 15943 | 8411 | 188527013
| Western Grid Total |  |  |  | 10421 | 5463 | 125699135
| National Grid Total |  |  |  | 26364 | 13874 | 314226148
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-06-26
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8995.17 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4192.8 | MW
i) Dhaka area |  |  | 5001.97 |  | MW | i) Khulna area |  |  |  | 1645 | MW
ii) Chattogram area |  |  | 1276.9 |  | MW | ii) Barishal area |  |  |  | 408 | MW
iii) Cumilla area |  |  | 1228.3 |  | MW | iii) Rajshahi area |  |  |  | 1293.8 | MW
iv) Mymensingh area |  |  | 995 |  | MW | iv) Rangpur area |  |  |  | 846 | MW
v) Sylhet area |  |  | 493 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13187.97 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 126 | 20:00 | 133 | Rahim | 54 | 15:00
2 | AKSML | 96 | 10:00 | 68 | Jashore | 143 | 19:00 | 134 | Rajbari | 66 | 04:00
3 | Aftabnagar | 42 | 00:00 | 69 | Jhenaidah | 122 | 22:00 | 135 | Rajendrapur | 90 | 12:00
4 | Agargaon | 116 | 10:00 | 70 | Joydebpur | 163 | 10:00 | 136 | Rajshahi | 134 | 05:00
5 | Agrabad | 104 | 19:30 | 71 | Joypurhat | 60 | 03:00 | 137 | Rajshahi-230 | 84 | 13:00
6 | Amnura | 62 | 04:00 | 72 | Juldah | 22 | 01:00 | 138 | Ramganj | 100 | 17:00
7 | Ashuganj | 89 | 06:00 | 73 | KSRM | 41 | 00:00 | 139 | Rampur | 42 | 19:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 288 | 12:00 | 140 | Rangamati | 18 | 19:00
9 | BSRM | 192 | 17:00 | 75 | Kachua | 67 | 19:30 | 141 | Rangpur | 141 | 13:00
10 | Bagerhat | 90 | 23:00 | 76 | Kallyanpur | 114 | 00:00 | 142 | Ruppur | 7.6 | 15:00
11 | Bakulia | 108 | 14:00 | 77 | Kalurghat | 36 | 18:30 | 143 | SSM | 16 | 05:00
12 | Banani | 37.8 | 14:00 | 78 | Kamrangirchar | 44 | 10:00 | 144 | Saidpur | 107 | 08:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 119 | 19:00
14 | Barapukuria | 61 | 19:30 | 80 | Kazla | 108 | 01:00 | 146 | Satmasjid | 113 | 00:00
15 | Barguna | 20 | 02:00 | 81 | Keranigonj | 80 | 00:00 | 147 | Savar | 181 | 14:00
16 | Barishal | 112 | 19:00 | 82 | Khagrachori | 38 | 19:30 | 148 | SevenRings | 14.93 | 03:00
17 | Barishal-230 | 90 | 05:00 | 83 | Khulna | 75 | 15:00 | 149 | ShahCement | 16 | 00:00
18 | Baroaulia | 64 | 13:00 | 84 | Khulshi | 162 | 01:00 | 150 | Shahjadpur | 81 | 19:00
19 | Baroirhat | 57 | 22:00 | 85 | Kishoreganj | 136 | 21:00 | 151 | Shahjibazar | 110 | 21:00
20 | Bashundhara | 166 | 00:00 | 86 | Kodda | 274 | 20:00 | 152 | Shahmirpur | 55 | 18:30
21 | BashundharaCement | 12 | 13:00 | 87 | Kulaura | 42 | 23:00 | 153 | Shariatpur | 75 | 22:00
22 | Beanibazar | 66 | 18:30 | 88 | Kurigram | 62 | 13:00 | 154 | Sherpur | 126 | 23:00
23 | Benapole | 60 | 21:00 | 89 | Kushtia | 144 | 07:00 | 155 | Shikalbaha | 25 | 09:00
24 | Bhaluka | 124 | 21:00 | 90 | Lalbag | 76 | 17:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 48 | 21:00 | 91 | Lalmonirhat | 54 | 21:00 | 157 | Shitalakhya | 95.6 | 14:00
26 | Bhangura | 36 | 00:00 | 92 | MI_Cement | 17.6 | 17:00 | 158 | Sholosohor | 40 | 09:00
27 | Bheramara(GK) | 64 | 21:00 | 93 | Madanganj | 34 | 03:00 | 159 | Shyampur | 146 | 12:00
28 | Bhulta | 240 | 19:30 | 94 | Madaripur | 99 | 21:00 | 160 | Siddhirganj | 128 | 15:00
29 | Bog-Sherpur | 64 | 20:00 | 95 | Madartek | 91.04 | 00:00 | 161 | Sirajganj | 102 | 19:30
30 | Bogura | 163 | 21:00 | 96 | Madunaghat | 58 | 18:30 | 162 | Sonargaon | 87 | 07:00
31 | Borhanuddin | 88 | 23:00 | 97 | Magura | 53 | 22:00 | 163 | Sreemongol | 69 | 19:00
32 | Brahmanbaria | 153 | 21:00 | 98 | Mahasthangarh | 68 | 05:00 | 164 | Sreepur | 88 | 23:00
33 | Cantonment | 136 | 10:00 | 99 | Manikganj | 119 | 06:00 | 165 | Srinagar | 43.31 | 06:00
34 | Chandpur | 64 | 19:00 | 100 | Maniknagar | 78 | 14:00 | 166 | Sunamganj | 38 | 19:00
35 | Chandraghona | 30 | 08:00 | 101 | Matarbari | 38 | 02:00 | 167 | Sylhet | 46 | 19:30
36 | Chapai | 80 | 12:00 | 102 | Matuail | 64 | 10:00 | 168 | Sylhet-132 | 106 | 22:00
37 | Charsaidpur | 41 | 06:00 | 103 | Millgate | 127 | 15:00 | 169 | TK | 32.4 | 19:00
38 | Chauddagram | 64 | 22:00 | 104 | Mirpur | 150 | 00:00 | 170 | Tangail | 180 | 19:00
39 | Chhatak | 25 | 19:30 | 105 | Mirsorai | 5 | 15:00 | 171 | Thakurgaon | 93 | 20:00
40 | Chowmuhani | 191 | 20:00 | 106 | Mirzapur | 42 | 20:00 | 172 | Tongi | 129 | 11:00
41 | Chuadanga | 101 | 21:00 | 107 | Mithapukur | 51 | 21:00 | 173 | Ullahpara | 25 | 21:00
42 | Coxsbazar | 114 | 13:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 61 | 00:00
43 | Cumilla(N) | 136 | 14:00 | 109 | Mogbazar | 128.1 | 15:00 | 175 | Uttara | 82 | 16:00
44 | Cumilla(S) | 178 | 19:00 | 110 | Mongla | 39 | 10:00 | 176 | UttaraNew | 58 | 00:00
45 | Daudkandi | 118 | 19:00 | 111 | Motijheel | 41 | 15:00 | 177 | Zigatola | 88 | 00:00
46 | Dhaka | 40 | 13:00 | 112 | Munshiganj | 100 | 21:00
47 | Dhamrai | 128 | 11:00 | 113 | Mymensingh | 245 | 21:00
48 | Dhanmondi | 142.5 | 13:00 | 114 | Naogaon | 139 | 21:00
49 | Dohazari | 105 | 04:00 | 115 | Narail | 48 | 22:00
50 | Faridpur | 146 | 22:00 | 116 | Narinda | 67 | 13:00
51 | Fatullah | 82 | 10:00 | 117 | Narshingdi | 154 | 22:00
52 | Fenchuganj | 34 | 04:00 | 118 | Natore | 154 | 06:00
53 | Feni | 99 | 19:00 | 119 | Nawabganj | 44.4 | 06:00
54 | GPH | 3 | 00:00 | 120 | Netrakona | 115 | 19:00
55 | Ghatail | 46 | 20:00 | 121 | New | 56.5 | 11:00
56 | Ghorashal | 52 | 20:00 | 122 | Niamatpur | 80 | 22:00
57 | Goalpara | 32 | 00:00 | 123 | Noapara | 49 | 22:00
58 | Gollamari | 94 | 12:00 | 124 | PHP | 10 | 10:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-06-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 390 | 19:30 | 380 | 06:00 | Kaliakoir | 389 | 19:00 | 377 | 11:00
| Ashuganj | 405 | 17:00 | 398 | 9:00 | Madunaghat_I | 401 | 00:00 | 397 | 08:00
| Bhulta | 407 | 05:00 | 394 | 12:00 | Meghnaghat | 385 | 19:00 | 372 | 12:00
| Bibiana | 407 | 19:30 | 396 | 14:00 | Payra | 409 | 22:00 | 405 | 13:00
| BIPTC | 398 | 06:00 | 388 | 16:00 | Rahanpur | 416 | 18:00 | 406 | 11:00
| Bogura | 413 | 18:00 | 402 | 12:00 | Rampal | 403 | 19:30 | 397 | 00:00
| Gopalganj | 399 | 19:30 | 390 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 20:00 | 223 | 12:00 | Hasnabad | 233 | 19:30 | 226 | 15:00
| AKSML | 236 | 18:00 | 229 | 04:00 | Hathazari | 240 | 00:00 | 234 | 09:00
| Aminbazar | 232 | 03:00 | 224 | 12:00 | Ishurdi | 236 | 21:00 | 230 | 12:00
| Ashuganj | 237 | 19:30 | 231 | 12:00 | Jhenaidah | 226 | 00:00 | 219 | 12:00
| Ashuganj-400 | 230 | 9:00 | 226 | 13:00 | Kaliakoir | 235 | 05:00 | 228 | 10:00
| Baghabari | 234 | 18:30 | 228 | 21:00 | Keranigonj | 232 | 07:00 | 224 | 12:00
| Barapukuria | 233 | 10:00 | 218 | 22:00 | Khulna(S) | 232 | 20:00 | 224 | 11:00
| Barapukuria-230 | 220 | 11:00 | 216 | 21:00 | Madunaghat_I | 238 | 00:00 | 235 | 03:00
| Barishal | 240 | 20:00 | 235 | 02:00 | Maniknagar | 234 | 19:30 | 226 | 12:00
| Bheramara | 232 | 00:00 | 228 | 11:00 | Meghnaghat | 241 | 19:00 | 233 | 15:00
| Bhulta | 235 | 05:00 | 227 | 12:00 | Meghnaghat-400 | 237 | 18:30 | 229 | 12:00
| Bibiana | 234 | 03:00 | 227 | 14:00 | Mirsorai | 238 | 19:30 | 229 | 08:00
| BIPTC | 234 | 00:00 | 227 | 12:00 | Rajshahi | 233 | 06:00 | 228 | 12:00
| Bogura | 232 | 05:00 | 227 | 22:00 | Rampal | 231 | 19:30 | 224 | 11:00
| Bogura-400 | 232 | 06:00 | 227 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 22:00 | 237 | 05:00 | Rampura | 232 | 03:00 | 224 | 15:00
| BSRM | 239 | 19:30 | 229 | 16:00 | Shikalbaha | 237 | 19:30 | 229 | 03:00
| Cumilla(N) | 236 | 19:30 | 227 | 12:00 | Shyampur | 234 | 19:30 | 226 | 12:00
| Fenchuganj | 238 | 21:00 | 233 | 11:00 | Siddhirganj | 235 | 21:00 | 229 | 10:00
| Ghorashal | 236 | 01:00 | 234 | 00:00 | Sirajgonj | 239 | 05:00 | 236 | 11:00
| Ghorashal-230 | 234 | 20:00 | 226 | 14:00 | Sreepur | 233 | 00:00 | 228 | 15:00
| GPH | 237 | 19:30 | 231 | 12:00 | Tongi | 236 | 04:00 | 227 | 11:00
| Haripur | 233 | 00:00 | 226 | 15:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 07:00 | 128 | 14:00 | Kushtia | 135 | 00:00 | 132 | 07:00
| Agargaon | 134 | 06:00 | 129 | 10:00 | Lalbag | 133 | 07:00 | 127 | 12:00
| Agrabad | 137 | 00:00 | 125 | 04:00 | Lalmonirhat | 130 | 01:00 | 124 | 19:00
| AKS | 135 | 00:00 | 130 | 22:00 | Madanganj | 136 | 20:00 | 128 | 12:00
| Aminbazar | 136 | 03:00 | 130 | 10:00 | Madaripur | 133 | 02:00 | 130 | 07:00
| Amnura | 139 | 00:00 | 126 | 12:00 | Madartek | 135 | 05:00 | 129 | 12:00
| Ashuganj | 139 | 08:00 | 136 | 11:00 | Madunaghat | 138 | 00:00 | 134 | 23:00
| Bagerhat | 136 | 15:00 | 125 | 12:00 | Magura | 136 | 00:00 | 131 | 11:00
| Bakulia | 139 | 00:00 | 133 | 23:00 | Mahasthangarh | 134 | 02:00 | 129 | 22:00
| Banani | 135 | 05:00 | 127 | 15:00 | Manikganj | 129 | 07:00 | 121 | 12:00
| Bangabhaban | 132 | 04:00 | 125 | 12:00 | Maniknagar | 132 | 05:00 | 126 | 12:00
| Barapukuria | 135 | 02:00 | 129 | 22:00 | Matarbari | 132 | 00:00 | 123 | 22:00
| Barguna | 134 | 10:00 | 130 | 02:00 | Matuail | 134.4 | 20:00 | 128.5 | 12:00
| Barishal | 138 | 20:00 | 131 | 05:00 | Millgate | 132 | 02:00 | 127 | 10:00
| Barishal-230 | 138 | 20:00 | 133 | 02:00 | Mirpur | 134 | 20:00 | 128 | 12:00
| Baroaulia | 139 | 19:00 | 133 | 09:00 | Mirzapur | 133 | 19:30 | 127 | 03:00
| Baroirhat | 133 | 19:30 | 125 | 14:00 | Mithapukur | 133 | 01:00 | 128 | 19:00
| Bashundhara | 135 | 05:00 | 126 | 12:00 | MI_Cement | 137 | 19:30 | 129 | 12:00
| BashundharaCement | 139 | 03:00 | 128 | 12:00 | Modern | 139 | 00:00 | 133 | 23:00
| Beanibazar | 127 | 09:00 | 122 | 00:00 | Mogbazar | 136 | 03:00 | 128 | 15:00
| Benapole | 135 | 20:00 | 128 | 12:00 | Mongla | 135 | 19:30 | 125 | 12:00
| Bhaluka | 129 | 00:00 | 124 | 11:00 | Motijheel | 132 | 04:00 | 125 | 12:00
| Bhandaria | 133 | 20:00 | 121 | 11:00 | Munshiganj | 135 | 05:00 | 130 | 11:00
| Bhangura | 136 | 00:00 | 133 | 12:00 | Mymensingh | 135 | 00:00 | 118 | 13:00
| Bheramara | 135 | 00:00 | 133 | 11:00 | Naogaon | 131 | 18:00 | 125 | 11:00
| Bheramara(GK) | 138 | 01:00 | 133 | 11:00 | Narail | 136 | 05:00 | 130 | 10:00
| Bhulta | 125 | 19:30 | 118 | 12:00 | Narinda | 132 | 5:00 | 126 | 12:00
| Bog-Sherpur | 136 | 18:00 | 131 | 21:00 | Narshingdi | 127 | 06:00 | 120 | 13:00
| Bogura | 136 | 04:00 | 132 | 12:00 | Natore | 134 | 04:00 | 130 | 22:00
| Bogura-230 | 137 | 05:00 | 126 | 04:00 | Nawabganj | 133 | 07:00 | 126 | 18:00
| Brahmanbaria | 130 | 00:00 | 125 | 12:00 | Netrakona | 134 | 13:00 | 126 | 18:00
| Cantonment | 134 | 07:00 | 128 | 12:00 | New | 135 | 07:00 | 127 | 12:00
| Chandpur | 133 | 20:00 | 124 | 15:00 | Niamatpur | 137 | 18:00 | 131 | 12:00
| Chandraghona | 139 | 00:00 | 135 | 23:00 | Noapara | 138 | 19:30 | 131 | 07:00
| Chapai | 133 | 18:00 | 127 | 12:00 | Pabna | 135 | 06:00 | 131 | 12:00
| Charsaidpur | 136 | 19:30 | 130 | 12:00 | Palashbari | 131 | 02:00 | 125 | 19:00
| Chauddagram | 134 | 19:30 | 126 | 12:00 | Panchagarh | 139 | 02:00 | 122 | 19:00
| Chhatak | 129 | 06:00 | 122 | 00:00 | Patuakhali | 134 | 19:30 | 130 | 02:00
| Chowmuhani | 127 | 01:00 | 121 | 13:00 | Payra | 135 | 18:30 | 133 | 00:00
| Chuadanga | 131 | 20:00 | 124 | 12:00 | PHP | 134 | 19:30 | 125 | 12:00
| Coxsbazar | 132 | 17:00 | 122 | 23:00 | Postogola | 137 | 19:30 | 131 | 12:00
| Cumilla(N) | 137 | 19:30 | 132 | 11:00 | Purbachal | 135 | 05:00 | 126 | 12:00
| Cumilla(S) | 137 | 20:00 | 128 | 00:00 | Purbasadipur | 134 | 05:00 | 122 | 22:00
| Daudkandi | 128 | 19:00 | 121 | 15:00 | Rahanpur | 137 | 18:00 | 133 | 11:00
| Dhaka | 136 | 05:00 | 129 | 14:00 | Rahim | 134 | 22:00 | 128 | 15:00
| Dhamrai | 135 | 21:00 | 127 | 11:00 | Rajbari | 133 | 20:00 | 130 | 06:00
| Dhanmondi | 135 | 05:00 | 128 | 16:00 | Rajendrapur | 134 | 19:30 | 126 | 11:00
| Dohazari | 137 | 00:00 | 129 | 23:00 | Rajshahi | 134 | 02:00 | 131 | 11:00
| Faridpur | 133 | 19:30 | 130 | 06:00 | Rajshahi-230 | 136 | 06:00 | 120 | 12:00
| Fatullah | 136 | 19:30 | 130 | 12:00 | Ramganj | 130 | 19:30 | 121 | 11:00
| Fenchuganj | 134 | 05:00 | 130 | 02:00 | Rampur | 138 | 00:00 | 132 | 23:00
| Feni | 132 | 19:30 | 124 | 15:00 | Rampura | 135 | 03:00 | 128 | 15:00
| Ghatail | 132 | 19:30 | 124 | 19:00 | Rangamati | 138 | 00:00 | 134 | 12:00
| Ghorashal | 139 | 00:00 | 137 | 08:00 | Rangpur | 132 | 01:00 | 125 | 22:00
| Goalpara | 140 | 19:30 | 132 | 12:00 | Ruppur | 136 | 00:00 | 134 | 08:00
| Gollamari | 138 | 20:00 | 131 | 12:00 | Saidpur | 132 | 02:00 | 123 | 22:00
| Gopalganj | 134 | 18:00 | 129 | 12:00 | Satkhira | 134 | 00:00 | 127 | 12:00
| Gopalganj-400 | 133 | 18:30 | 130 | 12:00 | Satmasjid | 134 | 07:00 | 128 | 10:00
| Gulshan | 135 | 05:00 | 128 | 12:00 | Savar | 136 | 07:00 | 130 | 12:00
| Halishahar | 140 | 18:30 | 133 | 23:00 | SevenRings | 139 | 07:00 | 135 | 16:00
| Haripur | 134 | 21:00 | 128 | 15:00 | ShahCement | 136 | 19:30 | 130 | 12:00
| HaripurSBU | 133 | 19:30 | 128 | 15:00 | Shahjadpur | 141 | 04:00 | 136 | 12:00
| Hasnabad | 137 | 21:00 | 132 | 15:00 | Shahjibazar | 128 | 10:00 | 126 | 12:00
| Hathazari | 139 | 19:00 | 135 | 07:00 | Shahmirpur | 140 | 00:00 | 133 | 23:00
| Ishurdi | 137 | 00:00 | 135 | 09:00 | Shariatpur | 131 | 17:00 | 128 | 08:00
| Jaldhaka | 131 | 02:00 | 121 | 22:00 | Sherpur | 136 | 16:00 | 118 | 22:00
| Jamalpur | 140 | 19:30 | 130 | 04:00 | Shikalbaha | 129 | 00:00 | 120 | 23:00
| Jashore | 135 | 19:30 | 129 | 11:00 | Shikalbaha-230 | 141 | 00:00 | 132 | 23:00
| Jhenaidah | 138 | 19:30 | 132 | 12:00 | Shitalakhya | 137 | 19:30 | 129 | 12:00
| Jhenaidah-230 | 138 | 00:00 | 132 | 12:00 | Sholosohor | 138 | 00:00 | 132 | 23:00
| Joydebpur | 138 | 20:00 | 130 | 12:00 | Shyampur | 135 | 18:00 | 130 | 10:00
| Joypurhat | 132 | 07:00 | 123 | 14:00 | Shyampur-230 | 136 | 19:30 | 129 | 12:00
| Juldah | 140 | 00:00 | 134 | 23:00 | Siddhirganj | 135 | 19:30 | 129 | 12:00
| Kabirpur | 136 | 19:30 | 121 | 12:00 | Sirajganj | 134 | 00:00 | 130 | 21:00
| Kachua | 134 | 19:30 | 125 | 12:00 | Sonargaon | 134 | 20:00 | 126 | 12:00
| Kaliakoir | 137 | 18:30 | 130 | 10:00 | Sreemongol | 129 | 07:00 | 126 | 00:00
| Kallyanpur | 132 | 19:30 | 128 | 13:00 | Sreepur | 132 | 05:00 | 127 | 15:00
| Kalurghat | 138 | 18:30 | 134 | 23:00 | Srinagar | 134 | 03:00 | 127 | 11:00
| Kamrangirchar | 133 | 07:00 | 128 | 00:00 | SSM | 142 | 19:00 | 138 | 23:00
| Kaptai | 137 | 7:00 | 134 | 18:00 | Sunamganj | 127 | 03:00 | 122 | 00:00
| Kazla | 131 | 04:00 | 125 | 13:00 | Sylhet | 129 | 03:00 | 124 | 02:00
| Keranigonj | 133 | 05:00 | 128 | 12:00 | Sylhet-132 | 130 | 03:00 | 125 | 00:00
| Khagrachori | 137 | 00:00 | 132 | 12:00 | Tangail | 130 | 19:30 | 123 | 22:00
| Khulna | 138 | 19:30 | 130 | 12:00 | Thakurgaon | 138 | 02:00 | 124 | 22:00
| Khulna(S) | 139 | 20:00 | 132 | 11:00 | TK | 141 | 18:00 | 133 | 23:00
| Khulshi | 137 | 00:00 | 131 | 23:00 | Tongi | 135 | 04:00 | 129 | 11:00
| Kishoreganj | 131 | 07:00 | 126 | 14:00 | Ullahpara | 136 | 00:00 | 133 | 06:00
| Kodda | 136 | 19:30 | 126 | 10:00 | Ullon | 136 | 05:00 | 129 | 12:00
| KSRM | 140 | 19:00 | 134 | 05:00 | Uttara | 133 | 04:00 | 128 | 12:00
| Kulaura | 131 | 08:00 | 129 | 01:00 | UttaraNew | 133 | 02:00 | 128 | 10:00
| Kurigram | 132 | 01:00 | 125 | 22:00 | Zigatola | 133 | 19:30 | 128 | 10:00

## L-Curve
Date | 2024-06-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 284 | 8100 | 5416 | 13516 |  |  |  | QF-LDC-11
0:30 | 330 | 7905 | 5280 | 13185 | Date: | 2024-06-26
1:00 | 376 | 7710 | 5144 | 12854
1:30 | 351 | 7704 | 5071.5 | 12775.5
2:00 | 326 | 7698 | 4999 | 12697
2:30 | 314 | 7696.5 | 4990.5 | 12687 | [5 empty] | Gen. at Eve. Peak | 13874 | 13874 MW (21:00 )
3:00 | 302 | 7695 | 4982 | 12677 | [6 empty] | 21:00
3:30 | 308 | 7676 | 4985 | 12661 | [5 empty] | Gen. at Day Peak | 12981 | 12981 MW (12:00 )
4:00 | 314 | 7657 | 4988 | 12645 | [6 empty] | 12:00
4:30 | 330 | 7606 | 5000.5 | 12606.5 | [5 empty] | Highest Generation | 13874
5:00 | 346 | 7555 | 5013 | 12568 | [6 empty] | 21:00
5:30 | 349 | 7552.5 | 4969.5 | 12522
6:00 | 352 | 7550 | 4926 | 12476
6:30 | 285 | 7534.5 | 4949.5 | 12484
7:00 | 218 | 7519 | 4973 | 12492
7:30 | 312 | 7519.5 | 4994 | 12513.5
8:00 | 406 | 7520 | 5015 | 12535
8:30 | 501 | 7559 | 5070.5 | 12629.5
9:00 | 596 | 7598 | 5126 | 12724
9:30 | 640 | 7662 | 5134.5 | 12796.5
10:00 | 684 | 7726 | 5143 | 12869
10:30 | 628 | 7691 | 5114.5 | 12805.5
11:00 | 572 | 7656 | 5086 | 12742
11:30 | 606 | 7687 | 5174.5 | 12861.5
12:00 | 640 | 7718 | 5263 | 12981
12:30 | 609 | 7722 | 5301 | 13023
13:00 | 578 | 7726 | 5339 | 13065
13:30 | 629 | 7713.5 | 5348.5 | 13062
14:00 | 680 | 7701 | 5358 | 13059
14:30 | 723 | 7679 | 5302.5 | 12981.5
15:00 | 766 | 7657 | 5247 | 12904
15:30 | 776 | 7668.5 | 5230 | 12898.5
16:00 | 786 | 7680 | 5213 | 12893
16:30 | 727 | 7630 | 5177 | 12807
17:00 | 668 | 7580 | 5141 | 12721
17:30 | 536 | 7596.5 | 5049 | 12645.5
18:00 | 404 | 7613 | 4957 | 12570
18:30 | 346 | 7958.5 | 5108.5 | 13067
19:00 | 288 | 8304 | 5260 | 13564
19:30 | 278 | 8443 | 5375 | 13818
20:00 | 216 | 8355 | 5331 | 13686 |  |  |  | Executive Engineer
20:30 | 163 | 8383 | 5397 | 13780 |  |  |  | Network Operation Division
21:00 | 110 | 8411 | 5463 | 13874
21:30 | 125 | 8423 | 5444 | 13867
22:00 | 140 | 8435 | 5425 | 13860 |  |  |  |  | Page 6 of 7
22:30 | 221 | 8311 | 5461 | 13772
23:00 | 302 | 8187 | 5497 | 13684
23:30 | 293 | 8143.5 | 5456.5 | 13600
24:00 | 284 | 8100 | 5416 | 13516
13874 MW (21:00 )
12981 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-06-26 |  | Energy |  | 314226148
[15 empty] | 2024-06-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3752 | 910 | 1824 | 0 | 2935 | 3303 | 145 | 0 | 530 | 90 | 0 | 27 | 1799.22
0:30 | 3736 | 914.5 | 1807.5 | 0 | 2760 | 3235 | 146.5 | 0 | 480 | 92 | 0 | 13.5 | 2019.825 |  |  | Date: | 44007
1:00 | 3720 | 919 | 1791 | 0 | 2585 | 3167 | 148 | 0 | 430 | 94 | 0 | 0 | 2240.43
1:30 | 3711 | 919.5 | 1792.5 | 0 | 2565 | 3165.5 | 149 | 0 | 382 | 90 | 0 | 1 | 2219.8975 | [9 empty] | Total Energy | 314.2261 | 314.2261 | Total Energy Gen 314.226 MKWHr Energy Not Served 36.298 MKWHr Energy Requirement 350.524 MKWHr
2:00 | 3702 | 920 | 1794 | 0 | 2545 | 3164 | 150 | 0 | 334 | 86 | 0 | 2 | 2199.365 | [9 empty] | Energy not Served | 36.2976 | 36.2976
2:30 | 3705 | 920 | 1798 | 0 | 2528.5 | 3166 | 149.5 | 0 | 329.5 | 89 | 0 | 1.5 | 2161.165 | [9 empty] | Energy Requirement | 350.5237 | 350.5237
3:00 | 3708 | 920 | 1802 | 0 | 2512 | 3168 | 149 | 0 | 325 | 92 | 0 | 1 | 2122.965
3:30 | 3712.5 | 920 | 1803 | 0 | 2493 | 3168 | 146.5 | 0 | 325 | 92 | 0 | 1 | 2090.495 | [8 empty] | Shortage
4:00 | 3717 | 920 | 1804 | 0 | 2474 | 3168 | 144 | 0 | 325 | 92 | 0 | 1 | 2058.025
4:30 | 3685 | 920 | 1803 | 0 | 2460 | 3181 | 142 | 0 | 323 | 91 | 0 | 1.5 | 2047.0425
5:00 | 3653 | 920 | 1802 | 0 | 2446 | 3194 | 140 | 0 | 321 | 90 | 0 | 2 | 2036.06
5:30 | 3634 | 920.5 | 1762 | 0 | 2436.5 | 3210.5 | 140 | 0 | 311.5 | 87 | 18.5 | 1.5 | 1936.74
6:00 | 3615 | 921 | 1722 | 0 | 2427 | 3227 | 140 | 0 | 302 | 84 | 37 | 1 | 1837.42
6:30 | 3626.5 | 920.5 | 1718 | 0 | 2420.5 | 3225.5 | 140 | 0 | 299.5 | 60 | 72.5 | 1 | 1734.28 | [7 empty] | Coal
7:00 | 3638 | 920 | 1714 | 0 | 2414 | 3224 | 140 | 0 | 297 | 36 | 108 | 1 | 1631.14
7:30 | 3648 | 920.5 | 1703.5 | 0 | 2389.5 | 3210.5 | 141 | 0 | 292 | 40 | 168 | 0.5 | 1467.3575 | [6 empty] | Oil
8:00 | 3658 | 921 | 1693 | 0 | 2365 | 3197 | 142 | 0 | 287 | 44 | 228 | 0 | 1303.575
8:30 | 3666.5 | 920.5 | 1714.5 | 0 | 2388.5 | 3196.5 | 143.5 | 0 | 280.5 | 60 | 259 | 0 | 1308.8275
9:00 | 3675 | 920 | 1736 | 0 | 2412 | 3196 | 145 | 0 | 274 | 76 | 290 | 0 | 1314.08
9:30 | 3699.5 | 920 | 1671.5 | 0 | 2431 | 3242 | 145.5 | 0 | 293.5 | 75 | 317 | 1.5 | 1292.5925
10:00 | 3724 | 920 | 1607 | 0 | 2450 | 3288 | 146 | 0 | 313 | 74 | 344 | 3 | 1271.105
10:30 | 3705 | 919.5 | 1588 | 0 | 2447 | 3243.5 | 146.5 | 0 | 326 | 74 | 350 | 6 | 1212.3725
11:00 | 3686 | 919 | 1569 | 0 | 2444 | 3199 | 147 | 0 | 339 | 74 | 356 | 9 | 1153.64
11:30 | 3677 | 919.5 | 1675 | 0 | 2444 | 3198.5 | 148 | 0 | 354 | 75 | 365.5 | 5 | 1063.3925
12:00 | 3668 | 920 | 1781 | 0 | 2444 | 3198 | 149 | 0 | 369 | 76 | 375 | 1 | 973.145
12:30 | 3654.5 | 920 | 1779.5 | 0 | 2470.5 | 3207.5 | 149.5 | 0 | 365.5 | 73 | 399.5 | 3.5 | 1079.15
13:00 | 3641 | 920 | 1778 | 0 | 2497 | 3217 | 150 | 0 | 362 | 70 | 424 | 6 | 1185.155
13:30 | 3641 | 920 | 1778 | 0 | 2497 | 3217 | 150 | 0 | 362 | 70 | 424 | 6 | 1185.155
14:00 | 3641 | 920 | 1778 | 0 | 2497 | 3217 | 150 | 0 | 362 | 70 | 424 | 6 | 1185.155
14:30 | 3646.5 | 919.5 | 1727 | 0 | 2543 | 3218.5 | 149.5 | 0 | 349.5 | 74 | 349.5 | 7.5 | 1259.1675
15:00 | 3652 | 919 | 1676 | 0 | 2589 | 3220 | 149 | 0 | 337 | 78 | 275 | 9 | 1333.18
15:30 | 3666 | 919 | 1672.5 | 0 | 2584 | 3211.5 | 146.5 | 0 | 346 | 86 | 258.5 | 8.5 | 1338.4325
16:00 | 3680 | 919 | 1669 | 0 | 2579 | 3203 | 144 | 0 | 355 | 94 | 242 | 8 | 1343.685
16:30 | 3672.5 | 919 | 1628.5 | 0 | 2633 | 3166 | 142 | 0 | 368.5 | 91 | 164.5 | 22 | 1282.565
17:00 | 3665 | 919 | 1588 | 0 | 2687 | 3129 | 140 | 0 | 382 | 88 | 87 | 36 | 1221.445
17:30 | 3673 | 919.5 | 1512 | 0 | 2753 | 3085 | 121 | 0 | 403.5 | 86 | 62 | 30.5 | 1198.0475
18:00 | 3681 | 920 | 1436 | 0 | 2819 | 3041 | 102 | 0 | 425 | 84 | 37 | 25 | 1174.65
18:30 | 3732 | 919.5 | 1580 | 0 | 2970 | 3078 | 103 | 0 | 556 | 90 | 18.5 | 20 | 1272.825
19:00 | 3783 | 919 | 1724 | 0 | 3121 | 3115 | 104 | 0 | 687 | 96 | 0 | 15 | 1371
19:30 | 3723 | 919 | 1769 | 0 | 3247 | 3230 | 104 | 0 | 731 | 92 | 0 | 3 | 1456.185
20:00 | 3734 | 921 | 1633 | 0 | 3245 | 3165 | 125 | 0 | 772 | 88 | 0 | 3 | 1541.37
20:30 | 3752 | 919.5 | 1678.5 | 0 | 3246.5 | 3196 | 125.5 | 0 | 769 | 87 | 0 | 6 | 1499.35
21:00 | 3770 | 918 | 1724 | 0 | 3248 | 3227 | 126 | 0 | 766 | 86 | 0 | 9 | 1457.33
21:30 | 3765.5 | 917.5 | 1748.5 | 0 | 3222.5 | 3222 | 135.5 | 0 | 759 | 85 | 0 | 11.5 | 1464.015
22:00 | 3761 | 917 | 1773 | 0 | 3197 | 3217 | 145 | 0 | 752 | 84 | 0 | 14 | 1470.7
22:30 | 3756.5 | 917.5 | 1792.5 | 0 | 3123 | 3256 | 145 | 0 | 679.5 | 85 | 0 | 17 | 1578.615
23:00 | 3752 | 918 | 1812 | 0 | 3049 | 3295 | 145 | 0 | 607 | 86 | 0 | 20 | 1686.53
23:30 | 3752 | 914 | 1818 | 0 | 2992 | 3299 | 145 | 0 | 568.5 | 88 | 0 | 23.5 | 1742.875 |  |  | Max Temp. in Dhaka |  | 32.0°C
24:00 | 3752 | 910 | 1824 | 0 | 2935 | 3303 | 145 | 0 | 530 | 90 | 0 | 27 | 1799.22
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 314.226 MKWHr Energy Not Served 36.298 MKWHr Energy Requirement 350.524 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-06-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 78 | 80 | 79 | 77 | 76 | 76 | 76 | 76 | 77 | 78 | 78 | 79 | 80 | 80 | 79 | 76 | 75 | 38 |  | 39 | 39 | 58 | 58 | 75 | 75 | 75 | 1791000
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 67 | 64 | 64 | 64 | 66 | 68 | 68 | 69 | 70 | 70 | 70 | 70 | 68 | 65 | 64 |  | 65 | 65 | 67 | 68 | 70 | 70 | 70 | 1636000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [14 empty] | 5 | 8 | 8 | 8 |  | 14 | 17 | 17 | 17 | 17 | 8 | 8 | 112449
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 6 | 10 | 12 | 10 | 13 | 20 | 16 | 4 | 7 | 3 | 0 | [8 empty] | 93555
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 222 | 219 | 220 | 224 | 221 | 221 | 222 | 222 | 222 | 219 | 212 | 217 | 215 | 215 | 215 | 217 | 217 |  | 216 | 220 | 221 | 221 | 221 | 221 | 222 | 5158368
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 80 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1994590
12 | Hathazari 100 MW peaking PP | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 38 | 38 | 43 | 60 | 67 | 67 | 67 | 67 | 67 | 67 | 66 |  | 66 | 67 | 67 | 67 | 60 | 54 | 54 | 1343040
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1693636
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 29 | 29 | 29 | 36 | 28 | 28 | 36 | 37 |  | 37 | 37 | 37 | 36 | 36 | 36 | 36 | 833360
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 303 | 304 | 304 | 296 | 296 | 294 | 294 | 298 | 292 | 289 | 293 | 293 | 284 | 284 | 283 | 284 | 284 | 284 |  | 282 | 276 | 277 | 277 | 271 | 271 | 271 | 6977576
18 | Kodda 300 MW PP Unit-2 (Summit) | 278 | 263 | 268 | 276 | 268 | 268 | 278 | 276 | 281 | 276 | 278 | 260 | 250 | 260 | 263 | 255 | 255 | 275 |  | 275 | 278 | 278 | 278 | 276 | 278 | 278 | 6501055
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2835000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 490 | 493 | 490 | 494 | 492 | 493 | 495 | 400 | 377 |  | 400 | 400 | 412 | 429 | 482 | 490 | 490 | 11470908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | [20 empty] | 5 | 5 | 15 | 15 | 15 | 5 | 59040
33 | Ashuganj 225 MW CCPP | 211 | 212 | 210 | 210 | 214 | 216 | 216 | 216 | 216 | 217 | 209 | 206 | 210 | 213 | 210 | 204 | 211 | 208 |  | 210 | 216 | 216 | 212 | 200 | 194 | 201 | 5101000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 240 | 240 |  | 250 | 250 | 250 | 250 | 250 | 250 | 240 | 6039000
| Ashuganj 450 MW CCPP(North) | 325 | 310 | 315 | 315 | 300 | 285 | 280 | 280 | 280 | 280 | 305 | 290 | 280 | 280 | 280 | 300 | 300 | 315 |  | 335 | 280 | 280 | 280 | 280 | 280 | 280 | 7575500
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5740400
35 | Ashuganj 55 MW PP (Precision) | [19 empty] | 1 | 15 | 12 | 13 | 5 |  | 0 | 30720
36 | Chandpur 150 MW CCPP | 40 | 40 | 40 | 45 | 50 | 50 | 50 | 50 | 50 | 45 | 45 | 45 | 45 | 45 | 40 | 40 | 40 | 40 |  | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 1027110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 400 | 401 | 401 | 400 | 401 | 402 | 401 | 401 | 401 | 393 | 370 | 398 | 403 | 403 | 401 | 401 | 402 | 404 |  | 402 | 404 | 393 | 397 | 405 | 405 | 405 | 9720000
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 400 | 400 | 400 | 400 | 400 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 410 | 410 | 400 | 400 | 390 |  | 390 | 390 | 390 | 370 | 390 | 400 | 400 | 9233500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 25 | 24 | 23 | 22 | 22 | 20 | 19 | 17 | 11 | 11 | 10 | 5 | 5 | 5 | 11 | 11 | 11 | 11 |  | 11 | 12 | 12 | 17 | 17 | 18 | 17 | 355200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 8 | 13 | 13 | 9 | 25 | 37 | 48 | 48 | 35 | 16 | 7 | 2 | [8 empty] | 274690
44 | Fenchugonj CCPP Phase-1 | 28 | 28 | 28 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 27 |  | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 656000
45 | Fenchugonj CCPP Phase-2 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1618560
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 60 | 59 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 61 | 60 | 54 | 55 | 55 |  | 54 | 56 | 56 | 56 | 56 | 56 | 58 | 1396800
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 20 | 20 | 30 | 30 | 30 | 55 | 62 | 72 | 72 | 96 | 106 | 106 | 107 | 106 | 121 | 129 | 179 | 182 |  | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 2633600
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 60192
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 53 | 50 | 46 | 49 | 5 | 5 |  | 53 | 51 | 52 | 52 | 52 | 52 | 52 | 1152600
56 | Shahjahanulla 25 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 |  |  |  |  | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 280152
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 320 | 325 | 320 | 315 | 300 | 300 | 290 | 305 | 295 | 295 | 310 | 310 | 300 | 305 | 300 | 310 | 290 |  | 310 | 280 | 290 | 290 | 290 | 310 | 310 | 7462500
| Bibiyana South 400 MW | 370 | 367 | 374 | 370 | 340 | 340 | 340 | 340 | 350 | 340 | 320 | 365 | 340 | 340 | 340 | 340 | 320 | 340 |  | 370 | 340 | 340 | 340 | 340 | 340 | 345 | 8415400
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 17 | 35 | 55 | 55 | 55 | 55 |  | 45 | 55 | 55 | 55 | 35 | 35 | 35 | 1168601
59 | Tangail Palli Power Gen 22 MW | 9 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 8 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 4 | 5 | 6 | 6 | 220560
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 94 | 86 | 92 | 92 | 90 | 84 | 36 | 44 | 76 | 74 | 74 | 76 | 70 | 80 | 78 | 94 | 88 | 84 |  | 96 | 92 | 88 | 86 | 84 | 86 | 90 | 1960320
64 | Malancha, Ctg. EPZ (United) | 9 | 15 | 16 | 20 | 25 | 25 | 15 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 2 | 3 |  | 12 | 8 | 12 | 12 | 23 | 22 | 25 | 253440
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 272980
69 | Summit Ashulia | 15 | 15 | 16 | 16 | 16 | 16 | 15 | 14 | 14 | 14 | 13 | 6 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 340200
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 353520
71 | Maona 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 320900
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 269600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 44 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 98 | 98 |  | 98 | 114 | 114 | 114 | 114 | 114 | 114 | 1375980
| Chowmuhani 113 MW | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 50 | 74 |  | 74 | 75 | 75 | 76 | 76 | 68 | 67 | 1160040
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3913920
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 27 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 43 | 52 | 52 | 32 | 26 | 683366
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195360
79 | Kodda 150 MW PP | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 64 | 64 | 64 |  | 133 | 133 | 150 | 150 | 148 | 149 | 98 | 1389600
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 43 |  | 43 | 43 | 43 | 42 | 42 | 42 | 43 | 803290
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 72 | 72 | 72 | 72 | 52 | 17 | 1004160
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 3 | 3 | 2 | 3 | 2 | 1 | 0 | [9 empty] | 26641
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 41 | 46 | 40 | 47 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1311497
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 102 | 107 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2690570
82 | Madanganj 102 PP(Summit) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 64 | 64 | 52 | 52 | 63 | 80 |  | 80 | 65 | 68 | 68 | 74 | 68 | 68 | 1631195
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 1000
86 | Meghnaghat CCPP ( Summit) | 148 | 149 | 146 | 149 | 146 | 146 | 135 | 140 | 143 | 136 | 150 | 149 | 142 | 142 | 143 | 148 | 144 | 141 |  | 146 | 136 | 135 | 135 | 142 | 140 | 149 | 3479273
87 | Meghnaghat 100 MW(IEL) | 27 | 24 | 25 | 25 | 24 | 25 | 24 | 25 | 24 | 17 | 17 | 17 | 23 | 21 | 18 | 23 | 33 | 34 |  | 33 | 33 | 33 | 29 | 34 | 33 | 34 | 608640
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 13 | 17 | 17 | 23 | 50 | 53 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 797760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 586080
92 | Fenchuganj 44 MW (Energyprima) | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 5 | 5 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 865224
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 |  | 31 | 43 | 43 | 43 | 43 | 43 | 43 | 986708
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 82 | 82 | 82 | 82 | 82 | 41 | 40 | 657936
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 20 |  | 20 | 19 | 19 | 19 | 19 | 19 | 6 | 228480
96 | Chattogram 108 MW PP (ECPV) |  | 21 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 |  | 25 | 25 | 25 | 23 | 25 | 25 | 25 | 583680
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 |  | 40 | 55 | 55 | 55 | 40 | 40 | 40 | 1241268
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1314939
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 120 |  | 120 | 163 | 120 | 163 | 163 | 163 | 163 | 3599918
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 0 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 11100
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1302120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 112 | 112 | 112 | 112 | 112 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 |  | 145 | 144 | 143 | 143 | 133 | 144 | 144 | 2860800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 117 | 128 | 129 | 130 | 132 | 131 | 131 | 132 | 132 | 130 | 119 | 132 | 132 | 132 | 132 | 124 | 126 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3130992
115 | Juldah 100 MW PP Unit-3 (Acorn) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 37 | 48 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 828480
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 431040
117 | Ashuganj 150 MW PP (Midland) | 66 | 100 | 105 | 107 | 98 | 103 | 105 | 70 | 53 | 50 | 52 | 52 | 52 | 52 | 52 | 53 | 47 | 70 |  | 107 | 138 | 137 | 140 | 110 | 75 | 67 | 1928654
118 | Bibiyana-III 400 MW CCPP | 404 | 402 | 390 | 403 | 370 | 365 | 365 | 367 | 367 | 367 | 393 | 380 | 367 | 368 | 367 | 375 | 330 | 364 |  | 409 | 367 | 367 | 367 | 367 | 365 | 371 | 9124000
| Jamalpur 115 MW PP (United) | 71 | 69 | 69 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 68 | 68 | 68 | 68 | 68 |  | 78 | 86 | 88 | 88 | 88 | 87 | 88 | 1748400
| Anwara 300 MW PP (United) | 69 | 69 | 53 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 69 | 69 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1352400
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 50 | 50 | 50 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 870720
| Anlima Energy Ltd. | 72 | 72 | 55 | 22 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 35 | 35 | 35 | 35 | 36 | 53 |  | 53 | 53 | 53 | 53 | 53 | 57 | 72 | 952200
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 19 | 18 | 18 | 18 |  | 10 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 528480
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 6 | 17 | 19 | 18 | 20 | 8 | 4 | 15 | 24 | 15 | 7 | 2 | [8 empty] | 152460
| Chandpur 115(Doreen) | 115 | 105 | 105 | 91 | 84 | 85 | 85 | 86 | 55 | 49 | 49 | 49 | 50 | 52 | 60 | 50 | 50 | 49 |  | 65 | 115 | 115 | 106 | 104 | 101 | 85 | 1860480
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 24 | 17 | 17 | 17 | 30 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 775080
| Mirsharai 150 MW (Oil) | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 | 163 | 163 | 17 | 17 | 1206036
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | 3 | 9 | 1 | 6 | 7 | 9 | 8 | 36 | 25 |  | 15 | 3 | 3 | 9 | 14 | 20 | 27 | 183360
| Sonagazi 75 MW Solar Plant | [5 empty] | 4 | 12 | 29 | 33 | 52 | 43 | 80 | 79 | 16 | 0 | 8 | 5 | 2 | [8 empty] | 351064
| Matarbari 2*600 MW (CPGCL) | 471 | 470 | 471 | 470 | 468 | 470 | 472 | 470 | 470 | 562 | 470 | 470 | 470 | 470 | 470 | 470 | 470 | 468 |  | 470 | 568 | 470 | 469 | 472 | 470 | 471 | 11360000
120 | Eastern Zone Total | 7710 | 7698 | 7695 | 7657 | 7555 | 7550 | 7519 | 7520 | 7598 | 7726 | 7656 | 7718 | 7726 | 7701 | 7657 | 7680 | 7580 | 7613 |  | 8304 | 8443 | 8355 | 8411 | 8435 | 8187 | 8100 | 188527013
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 16 |  | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 527040
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 24 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 20 | 20 | 20 | 20 | 38 |  | 39 | 39 | 46 | 41 | 41 | 40 | 30 | 545280
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | [6 empty] | 14 | 37 | 53 | 53 | 53 | 53 | 53 |  | 54 | 54 | 55 | 55 | 55 | 55 | 55 | 742080
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 16 | 45 | 58 | 53 | 36 | 21 | 79 | 72 | 21 | 27 | 21 | 5 | [8 empty] | 450720
131 | Rampal 1320 MW (BIFPCL) | 817 | 815 | 818 | 817 | 812 | 819 | 819 | 817 | 814 | 812 | 812 | 811 | 810 | 812 | 812 | 808 | 808 | 812 |  | 812 | 811 | 812 | 856 | 790 | 861 | 868 | 19680000
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 705600
133 | Bhola Nutan Biddut BD LTD (GAS) | 184 | 180 | 186 | 185 | 186 | 185 | 187 | 186 | 150 | 148 | 146 | 185 | 186 | 186 | 108 | 108 | 126 | 133 |  | 217 | 220 | 220 | 220 | 220 | 220 | 220 | 4265455
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 71 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 64 | 64 | 64 | 64 |  | 110 | 96 | 96 | 96 | 110 | 96 | 96 | 1340064
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 153 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4778200
136 | Barisal 1 MW Solar Plant
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 126 | 126 | 126 | 126 | 126 | 80 | 80 | 80 | 130 | 130 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 80 |  | 126 | 126 | 130 | 130 | 130 | 130 | 130 | 2831000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 9 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 22305
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 24 | 8 | 206250
143 | Gopalganj 100 MW Peaking PP | 56 | 51 | 47 | 47 | 43 | 46 | 46 | 44 | 42 | 34 | 34 | 33 | 32 | 28 | 30 | 32 | 41 | 53 |  | 54 | 55 | 58 | 64 | 59 | 59 | 53 | 1074304
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 919 | 920 | 920 | 920 | 920 | 921 | 920 | 921 | 920 | 920 | 919 | 920 | 920 | 920 | 919 | 919 | 919 | 920 |  | 919 | 919 | 921 | 918 | 917 | 918 | 910 | 22232000
147 | Bheramara 410 MW CCPP | 240 | 240 | 240 | 245 | 245 | 245 | 250 | 250 | 250 | 250 | 250 | 240 | 245 | 245 | 240 | 240 | 240 | 240 |  | 225 | 225 | 235 | 250 | 250 | 250 | 250 | 6120000
148 | Payra 1320 MW | 622 | 622 | 622 | 622 | 622 | 622 | 622 | 600 | 600 | 600 | 600 | 610 | 622 | 622 | 622 | 600 | 600 | 580 |  | 580 | 600 | 620 | 622 | 622 | 622 | 622 | 15576000
149
150 | Barapukuria TPP Unit-1 |  |  |  |  | 35 | 56 | 54 | 55 | 54 | 54 | 54 | 54 | 54 | 56 | 54 | 56 | 56 | 60 |  | 60 | 60 | 60 | 61 | 60 | 60 | 61 | 1598792
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 194 | 193 | 194 | 194 | 194 | 196 | 192 | 194 | 194 | 196 | 196 | 190 | 193 | 196 | 195 | 200 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4923000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [25 empty] | 0 | 0
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 3 | 5 | 0 | 1 | 1 | 0 | 0 | [8 empty] | 28260
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 192 | 192 | 192 | 192 | 192 | 198 | 201 | 207 | 205 | 204 | 203 | 201 | 201 | 203 | 207 | 205 | 204 | 195 |  | 150 | 197 | 203 | 207 | 208 | 206 | 203 | 5002200
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 350 | 350 | 350 | 414 | 350 | 300 | 414 | 414 | 414 | 414 | 414 | 414 | 330 |  | 395 | 414 | 310 | 377 | 396 | 414 | 414 | 9276945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 5 | 5 | [11 empty] | 4 | 5 | 5 | [5 empty] | 4 | 5 | 5 | 5 | 5 | 31058
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 109242
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 828200
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 30 | 30 | 30 | 38 | 30 | 30 | 37 | 37 | 37 | 35 |  | 35 | 37 | 47 | 40 | 40 | 47 | 45 | 720000
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | 22 | 22 | [11 empty] | 15 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 22 | 294121
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | 52 | [18 empty] | 45 | 85 | 85 | 85 | 85 | 85 | 85 | 519392
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2732640
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2742336
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 107 | 107 | 107 | 107 | 113 | 108 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 105 | 113 | 113 | 113 | 107 | 2677315
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 4 | 5 | 6 | 4 | 1 | 0 | [8 empty] | 31553
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 95 | 95 | 95 | 95 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2683968
| Intraco Solar 30 MW | [5 empty] | 2 | 5 | 17 | 11 | 9 | 11 | 1 | 2 | 15 | 25 | 17 | 9 | 3 |  | 0 | [6 empty] | 137270
| Adani Power Jharkhanda Ltd | 373 | 374 | 373 | 375 | 373 | 374 | 375 | 371 | 374 | 374 | 374 | 373 | 374 | 372 | 374 | 374 | 375 | 371 |  | 373 | 371 | 371 | 370 | 371 | 372 | 371 | 8690545
178 | Teesta Solar Limited | [5 empty] | 23 | 55 | 96 | 138 | 180 | 200 | 205 | 181 | 172 | 156 | 145 | 34 | 23 | [8 empty] | 1576000