## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-05 | Friday
|  | Date (day): | 2024-07-05 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14446.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14980 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-04 | 2024-07-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 371 | 347 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 350 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 14 | 16 | 16 |  | 84 | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 144 | 149 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 80 | 82 | 80 | 82 |  | 20 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 25 | 30 | 25 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 11 | 40 | 40 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 333 | 315 | 300 | 325
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 |  | 94 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 149 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 17 | 17 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 29 | 29 | 29 |  | 51 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 8 | 16 | 16 |  | 17 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 10 | 6 | 14 | 16 |  | 17 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 210 | 263 | 270 |  | 30 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 135 | 149 | 149 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 53 | 70 | 52 | 70 | 35 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 25 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 1953 | 2395 | 2496 | 2709 | 1522 | 1348
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 10 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 48 | 6 | 48
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 164 | 166 | 166 | 166 | 64 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 226 | 223 | 220 | 222
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 51 | 51 | 54 |  | Fuel Shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 78 | 62 | 78 | 20 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 30 | 60 | 40 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 49 | 62 | 34 | 50 | 50 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 23 | 30 | 30
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 12 | 12 | 96 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 100 | 52 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 17 | 51 | 59 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 62 | 50 | 50 | 50 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 53 | 17 | 53 | 63 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 28 | 54 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 550 | 612 | 612 | 612 |  | 612 | Unit-2 shut down
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 51 | 18 | 44 | 62 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 518 | 516 | 520 | 520 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 27 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 1794 | 2072 | 2185 | 2393 | 941 | 993
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 209 | 215 | 215
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 280 | 80 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 240 | 240 | 120 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 240 | 230 | 230 | 230 | 170 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 5 | 5 | 5 | 40 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 135 | 135 |  | 15 | Engine problem
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 32 | 43 | 43 |  | 9 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 36 | 35 | 40 | 40 | 123 |  | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 34 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 76 | 146 | 142
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 25 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 16 | 17 | 16 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 56 | 88 | 50 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 55 | 91 | 46 | 91 |  | 22 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 66 | 104 | 115
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1344 | 1546 | 1648 | 1792 | 953 | 95
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 10 | 22 | 16 | 22 | 180 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 200 | 157 | 200 | 142 | 58 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 86 | 69 | 88 | 27 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 21 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 36 | 36 | 36
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 322 | 307 | 378.6 | 294 | 180 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 27 | 25 | 25 | 25 |  | 45 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 54 | 54 | 54 |  | 36 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 37 | 39 | 40 | 40 |  | 10 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 2 | 2 |  | 9 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 53 | 56 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 210 | 209 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 15 | 15 | 5 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 400 | 340 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 310 | 340 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1690 | 1558 | 1671 | 1682 | 5 | 464
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 924 | 927 | 927
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 48 | 48 | 66 | 98 | 17 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 30 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 58 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 280 | 300 | 300 | 110 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 25 | 53 | 52 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 45 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 342 | 343 | 350 | 350 | 384 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1677 | 1756 | 1856 | 1838 | 1177 | 61
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1022 | 1240 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 35 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 250 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1629 | 1866 | 1955 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 24 | 24 |  | 28 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 0 | 11 |  | 60 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 35 | 35 |  |  | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 36 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint.
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 184 | 156 | 160 | 170 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 394 | 329 | 350 | 350 | 64 |  | Gas shortage
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 5 | 89 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 60 | 95 |  | 18 | Engine problem
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1253 | 1334 | 748 | 748 |  | 748 | Unit-2 Under maint.
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 26 | 0 | 5 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1868 | 2120 | 1617 | 1713 | 557 | 1112
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 62 | 62 | 62 |  | 25
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 220 | 200 | 220 |  | 54 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 28 | 106 | 100 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 110 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 182 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 549 | 503 | 640 | 503 | 40 | 171
| Total |  |  |  |  | 27515 | 26364 | 12826 | 14123 | 14446.6 | 14980 | 5490 | 4308
A. |  | 2024-07-04 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 14123 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11302 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14250 | MW
3 | Day peak Generation : |  |  | 12826 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13666.58 | MW
4 | Evening peak Generation : |  |  | 14123 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 121 | MW
5 | Total Energy Generation : |  | 306.9529 | MKWHr | By Solar | 1.6661 | MKWHr
| By Gas : | 131.6994 | MKWHr |  | By Oil: | 42.8617 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 102.4355 | MKWHr |  | By Hydro: | 3.9416 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.6984 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5490 | MW | Dhaka | 4886.58 | 4876.58 |  | 10 |  | 18:00 |  | 123
|  |  | For Plants S/D or M/C prob = |  |  | 4308 | MW | Chittagong | 1325 | 1325 |  | 0 |  | 19:00 |  | 125.105
|  |  | Total = |  |  | 9798 | MW | Khulna | 1656.6 | 1656.6 |  | 0 |  | 19:30 |  | 80.22
7 | Total Gas Supplied : |  |  | 969.6 | MMCFD |  |  | Rajshahi | 1386.4 | 1386.4 |  | 0 |  | 20:00 |  | 61.12
8 | Fuel Cost : | i) Gas : | Taka | 404820472.622 | ii) Oil : | Taka | 784259390.59 | Comilla | 1323 | 1323 |  | 0 |  | 21:00 |  | 121
|  | iii) Coal : | Taka | 696332333.54 | Total | Taka | 1885412196.752 | Mymensingh | 1184 | 1073 |  | 111 |  | 22:00 |  | 134.655
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 8405.1 | MKWHr. | Sylhet | 556 | 556 |  | 0 |  | 23:00 |  | 155.665
| ii) During Peak Demand : |  |  | 858 | MW (W to E) at | 21:00 | hrs | Barisal | 426 | 426 |  | 0 |  | 24:00 |  | 233.02
| iii) Maximum : |  |  | 732 | MW at | 8:00 | hrs | Rangpur | 923 | 923 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.2°C |  |  | Total | 13666.58 | 13545.58 |  | 121
B. |  | 2024-07-05 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 31.2°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14980 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11300 | MW
4 | Reserve(Generation end) |  |  |  | 1480 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 293.6127 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10790 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8924 | MKWHr. | ii) HVDC Flow at Peak Time |  | 924 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7578 | MKWHr. | iii) Maximum HVDC Flow : |  | 924 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 88.28 |  | (b) Today: | 90.5 |  | (c) Rule Curve: |  | 84.64
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-07-04 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 356 | 0 |  | 0 | 350 | 135 | 9 | 82 | 25 | 329 | 0 | 0 | 13 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 14 | 15 | 16 | 10 | 0 | 0 | 85 | 74 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 72 | 85 | 0 | 12 | 39 | 0 | 27 | 0 | 0 | 0 | 290 | 240 | 210 | 8 | 30 | 20 | 5 | 0 | 43 | 0 | 36 | 50 | 0 | 0 | 0 | 16 | 74 | 18 | 0 | 0 | 0 | 26 | 60 | 53 | 40 | 120 | 0 | 56 | 0 | 0 | 212 | 15 | 0 | 0 | 275 | 12 | 5 | 0 | 145 | 0 | 0 | 111 | 0 | 139 | 0 | 50 | 17 | 10 | 388 | 68 | 17 | 34 | 0 | 68 | 0 | 17 | 98 | 58 | 50 | 310 | 17 | 0 | 35 | 57 | 0 | 17 | 0 | 101 | 17 | 230 | 17 | 0 | 552 | 40 | 517 | 0 | 0 | 0 |  | 911 | 0 | 335 | 0 | 81 | 0 | 0 | 0 | 22 | 41 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 5 | 0 | 0 | 0 | 25 | 0 | 15 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 305 | 17 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1140 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 338 | 0 | 250 | 1385 | 0 | 0 | 0 | 0 |  | 7307 | 5949 | 13256 | 3838 | 911 | 1591 | 0 | 1790 | 4463 | 159 | 0 | 390 | 74 | 0 | 40 | 309.42 | 87.88
2:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 361 | 0 |  | 0 | 350 | 132 | 9 | 82 | 25 | 329 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 14 | 15 | 16 | 10 | 0 | 0 | 85 | 74 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 72 | 68 | 0 | 12 | 39 | 0 | 27 | 0 | 0 | 0 | 290 | 240 | 217 | 0 | 30 | 20 | 5 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 0 | 16 | 72 | 18 | 0 | 0 | 0 | 27 | 60 | 53 | 40 | 120 | 0 | 56 | 0 | 0 | 212 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 130 | 0 | 0 | 111 | 0 | 133 | 0 | 50 | 17 | 10 | 388 | 68 | 17 | 34 | 0 | 69 | 0 | 17 | 98 | 46 | 50 | 310 | 17 | 0 | 35 | 38 | 0 | 17 | 0 | 100 | 17 | 230 | 17 | 0 | 552 | 31 | 515 | 0 | 0 | 0 |  | 911 | 0 | 335 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 311 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 338 | 0 | 250 | 1327 | 0 | 0 | 0 | 0 |  | 7201 | 5705 | 12906 | 3849 | 911 | 1591 | 0 | 1673 | 4363 | 159 | 0 | 257 | 72 | 0 | 31 | 299.87 | 87.96
3:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 364 | 0 |  | 0 | 350 | 130 | 8 | 82 | 25 | 329 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 15 | 16 | 10 | 0 | 0 | 85 | 74 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 72 | 17 | 0 | 12 | 0 | 0 | 27 | 0 | 0 | 0 | 290 | 240 | 218 | 0 | 30 | 20 | 5 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 0 | 16 | 70 | 18 | 0 | 0 | 0 | 27 | 60 | 53 | 40 | 120 | 0 | 56 | 0 | 0 | 211 | 15 | 0 | 0 | 275 | 12 | 5 | 0 | 30 | 0 | 0 | 111 | 0 | 132 | 0 | 50 | 17 | 0 | 388 | 68 | 17 | 0 | 0 | 52 | 0 | 0 | 98 | 46 | 50 | 310 | 17 | 0 | 0 | 20 | 0 | 17 | 0 | 102 | 17 | 230 | 0 | 0 | 550 | 25 | 517 | 0 | 0 | 0 |  | 912 | 0 | 335 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 302 | 17 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 340 | 0 | 250 | 1325 | 0 | 0 | 0 | 0 |  | 6785 | 5609 | 12394 | 3853 | 912 | 1575 | 0 | 1301 | 4343 | 159 | 0 | 156 | 70 | 0 | 25 | 311.33 | 88.04
4:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 378 | 0 |  | 0 | 350 | 142 | 9 | 38 | 25 | 330 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 15 | 16 | 10 | 0 | 0 | 85 | 76 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 8 | 17 | 0 | 12 | 0 | 0 | 29 | 0 | 0 | 0 | 290 | 240 | 217 | 0 | 35 | 20 | 5 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 0 | 16 | 68 | 18 | 0 | 0 | 0 | 27 | 60 | 53 | 40 | 120 | 0 | 56 | 0 | 0 | 211 | 15 | 0 | 0 | 285 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 148 | 0 | 50 | 17 | 0 | 388 | 68 | 17 | 0 | 0 | 52 | 0 | 0 | 98 | 46 | 50 | 310 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 101 | 17 | 230 | 0 | 0 | 540 | 18 | 516 | 0 | 0 | 0 |  | 910 | 0 | 335 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 342 | 17 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 339 | 0 | 250 | 1197 | 0 | 0 | 0 | 0 |  | 6689 | 5357 | 12046 | 3870 | 910 | 1639 | 0 | 1139 | 4164 | 161 | 0 | 77 | 68 | 0 | 18 | 271.22 | 88.12
5:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 389 | 0 |  | 0 | 350 | 129 | 8 | 9 | 25 | 330 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 15 | 16 | 10 | 0 | 0 | 85 | 76 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 12 | 0 | 0 | 29 | 0 | 0 | 0 | 290 | 240 | 218 | 0 | 40 | 20 | 5 | 0 | 43 | 0 | 36 | 25 | 0 | 0 | 0 | 16 | 68 | 18 | 0 | 0 | 0 | 27 | 60 | 53 | 40 | 120 | 0 | 56 | 0 | 0 | 213 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 149 | 0 | 50 | 17 | 0 | 388 | 68 | 17 | 0 | 0 | 30 | 0 | 0 | 98 | 46 | 50 | 310 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 100 | 17 | 230 | 0 | 0 | 503 | 30 | 517 | 0 | 0 | 0 |  | 911 | 0 | 345 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 301 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 340 | 0 | 250 | 1207 | 0 | 0 | 0 | 0 |  | 6616 | 5278 | 11894 | 3899 | 911 | 1589 | 0 | 1048 | 4119 | 161 | 0 | 69 | 68 | 0 | 30 | 244.48 | 88.2
6:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 402 | 0 |  | 0 | 350 | 138 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 14 | 15 | 16 | 10 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 290 | 240 | 217 | 0 | 40 | 20 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 64 | 20 | 0 | 0 | 0 | 27 | 60 | 53 | 40 | 120 | 0 | 56 | 0 | 0 | 213 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 149 | 1 | 0 | 17 | 0 | 388 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 46 | 0 | 310 | 17 | 2 | 0 | 0 | 0 | 17 | 0 | 90 | 17 | 300 | 0 | 0 | 495 | 26 | 518 | 0 | 0 | 2 |  | 911 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 220 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 340 | 1 | 250 | 1016 | 4 | 0 | 0 | 1 |  | 6332 | 4970 | 11302 | 3978 | 911 | 1601 | 0 | 638 | 3891 | 165 | 0 | 16 | 64 | 11 | 26 | 189.09 | 88.28
7:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 405 | 0 |  | 0 | 350 | 143 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 14 | 15 | 16 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 320 | 310 | 190 | 0 | 40 | 20 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 64 | 20 | 0 | 0 | 0 | 27 | 60 | 50 | 37 | 120 | 0 | 56 | 0 | 0 | 213 | 15 | 0 | 0 | 295 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 149 | 2 | 0 | 17 | 0 | 400 | 65 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 46 | 0 | 310 | 0 | 11 | 0 | 0 | 0 | 17 | 0 | 82 | 17 | 240 | 0 | 0 | 450 | 30 | 517 | 0 | 0 | 4 |  | 910 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 341 | 1 | 250 | 1011 | 20 | 0 | 0 | 3 |  | 6345 | 4987 | 11332 | 4009 | 910 | 1604 | 0 | 638 | 3852 | 166 | 0 | 16 | 64 | 40 | 30 | 184.315 | 88.36
8:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 401 | 0 |  | 0 | 350 | 150 | 0 | 3 | 0 | 326 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 2 | 0 | 55 | 0 | 14 | 15 | 16 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 295 | 240 | 203 | 0 | 40 | 20 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 70 | 16 | 0 | 0 | 0 | 27 | 59 | 50 | 40 | 120 | 0 | 55 | 0 | 0 | 214 | 15 | 0 | 0 | 305 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 149 | 5 | 0 | 17 | 0 | 403 | 68 | 17 | 0 | 1 | 0 | 0 | 0 | 34 | 45 | 0 | 330 | 0 | 5 | 0 | 0 | 0 | 17 | 3 | 80 | 17 | 240 | 0 | 0 | 450 | 30 | 518 | 0 | 0 | 3 |  | 917 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1000 | 180 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 343 | 3 | 250 | 1015 | 50 | 0 | 0 | 4 |  | 6292 | 5061 | 11353 | 3949 | 917 | 1605 | 0 | 651 | 3859 | 166 | 0 | 16 | 70 | 86 | 30 | 159.485 | 88.46
9:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 396 | 0 |  | 0 | 350 | 152 | 0 | 45 | 15 | 324 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 26 | 0 | 55 | 0 | 14 | 15 | 16 | 10 | 8 | 0 | 92 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 196 | 0 | 39 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 74 | 16 | 0 | 0 | 0 | 27 | 58 | 50 | 40 | 120 | 0 | 55 | 0 | 0 | 215 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 38 | 0 | 0 | 163 | 0 | 149 | 4 | 0 | 17 | 0 | 403 | 68 | 17 | 0 | 2 | 0 | 0 | 0 | 34 | 45 | 0 | 336 | 0 | 8 | 0 | 0 | 0 | 17 | 5 | 67 | 17 | 240 | 0 | 0 | 450 | 17 | 517 | 0 | 0 | 25 |  | 917 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1000 | 180 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 340 | 14 | 250 | 1086 | 102 | 0 | 0 | 4 |  | 6429 | 5194 | 11623 | 3917 | 917 | 1605 | 0 | 803 | 3926 | 172 | 0 | 16 | 74 | 172 | 17 | 102.185 | 88.56
10:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 379 | 0 |  | 0 | 350 | 149 | 3 | 70 | 25 | 324 | 0 | 0 | 3 | 8 | 16 | 0 | 0 | 0 | 0 | 31 | 17 | 55 | 0 | 14 | 15 | 16 | 10 | 16 | 0 | 86 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 78 | 12 | 0 | 0 | 0 | 27 | 58 | 50 | 37 | 163 | 0 | 55 | 0 | 0 | 213 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 45 | 0 | 0 | 200 | 0 | 149 | 9 | 10 | 17 | 0 | 402 | 68 | 53 | 0 | 1 | 15 | 0 | 0 | 34 | 45 | 12 | 350 | 9 | 11 | 0 | 6 | 0 | 17 | 11 | 49 | 17 | 240 | 0 | 0 | 500 | 24 | 520 | 0 | 0 | 40 |  | 917 | 0 | 340 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 59 | 0 | 220 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1000 | 220 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 343 | 25 | 250 | 1113 | 103 | 0 | 0 | 2 |  | 6742 | 5355 | 12097 | 3931 | 917 | 1748 | 0 | 1001 | 4005 | 166 | 0 | 16 | 78 | 209 | 24 | 41 | 88.66
11:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 376 | 0 |  | 0 | 350 | 129 | 8 | 80 | 25 | 334 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 0 | 15 | 16 | 10 | 16 | 0 | 86 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 76 | 12 | 0 | 0 | 2 | 27 | 58 | 50 | 37 | 163 | 0 | 55 | 0 | 0 | 213 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 45 | 0 | 0 | 200 | 0 | 149 | 20 | 49 | 22 | 0 | 404 | 68 | 53 | 0 | 2 | 100 | 0 | 0 | 34 | 47 | 48 | 350 | 17 | 20 | 0 | 17 | 0 | 17 | 35 | 50 | 17 | 240 | 0 | 0 | 500 | 29 | 518 | 0 | 0 | 1 |  | 917 | 0 | 337 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1010 | 220 | 0 | 0 | 1 | 40 | 0 | 0 | 0 | 343 | 21 | 250 | 1174 | 153 | 0 | 0 | 5 |  | 6924 | 5481 | 12405 | 3927 | 917 | 1674 | 0 | 1217 | 4078 | 166 | 0 | 20 | 76 | 296 | 29 | 43 | 88.76
12:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 371 | 0 |  | 0 | 350 | 144 | 9 | 80 | 25 | 333 | 0 | 0 | 11 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 13 | 15 | 16 | 10 | 16 | 0 | 86 | 78 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 36 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 82 | 10 | 0 | 0 | 0 | 27 | 58 | 50 | 37 | 163 | 0 | 53 | 0 | 0 | 210 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 45 | 0 | 0 | 200 | 0 | 135 | 10 | 49 | 17 | 0 | 400 | 68 | 53 | 0 | 2 | 100 | 0 | 0 | 56 | 55 | 50 | 350 | 17 | 21 | 25 | 17 | 0 | 17 | 27 | 49 | 17 | 240 | 28 | 0 | 550 | 51 | 518 | 0 | 0 | 27 |  | 917 | 0 | 325 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 28 | 0 | 1 | 0 | 1022 | 220 | 0 | 0 | 4 | 45 | 35 | 0 | 0 | 342 | 21 | 250 | 1253 | 182 | 0 | 0 | 26 |  | 7103 | 5723 | 12826 | 3904 | 917 | 1725 | 0 | 1351 | 4217 | 164 | 0 | 49 | 82 | 340 | 51 | 23 | 88.82
13:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 366 | 0 |  | 0 | 350 | 145 | 8 | 80 | 25 | 330 | 0 | 0 | 38 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 14 | 0 | 8 | 6 | 16 | 0 | 84 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 43 | 0 | 0 | 4 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 36 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 78 | 8 | 0 | 0 | 1 | 26 | 54 | 50 | 40 | 120 | 0 | 55 | 0 | 0 | 208 | 15 | 0 | 0 | 300 | 12 | 5 | 0 | 133 | 0 | 0 | 137 | 0 | 132 | 4 | 49 | 17 | 8 | 404 | 68 | 53 | 0 | 1 | 100 | 0 | 0 | 98 | 47 | 50 | 320 | 17 | 21 | 102 | 18 | 0 | 17 | 6 | 51 | 17 | 240 | 54 | 0 | 550 | 50 | 516 | 0 | 0 | 17 |  | 917 | 0 | 325 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 40 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 359 | 17 | 0 | 0 | 0 | 37 | 0 | 7 | 0 | 1032 | 220 | 0 | 0 | 4 | 8 | 35 | 0 | 0 | 343 | 12 | 250 | 1257 | 60 | 0 | 0 | 29 |  | 7213 | 5579 | 12792 | 3795 | 917 | 1647 | 0 | 1626 | 4229 | 164 | 0 | 116 | 78 | 141 | 50 | 151 | 88.92
14:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 367 | 0 |  | 0 | 350 | 128 | 8 | 80 | 25 | 260 | 0 | 0 | 50 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 85 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 12 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 82 | 6 | 0 | 0 | 1 | 26 | 58 | 52 | 5 | 120 | 0 | 59 | 0 | 0 | 208 | 15 | 0 | 0 | 270 | 0 | 5 | 0 | 250 | 0 | 0 | 137 | 0 | 132 | 1 | 49 | 17 | 36 | 380 | 67 | 53 | 0 | 1 | 107 | 0 | 0 | 98 | 46 | 50 | 320 | 17 | 5 | 108 | 35 | 0 | 17 | 16 | 51 | 17 | 240 | 54 | 0 | 500 | 39 | 503 | 0 | 0 | 65 |  | 917 | 0 | 320 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 40 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 302 | 17 | 0 | 0 | 0 | 34 | 0 | 6 | 0 | 1022 | 180 | 0 | 0 | 2 | 7 | 35 | 0 | 0 | 344 | 21 | 250 | 1259 | 120 | 0 | 0 | 33 |  | 7209 | 5508 | 12717 | 3657 | 917 | 1470 | 0 | 1809 | 4159 | 165 | 0 | 141 | 82 | 245 | 39 | 136.565 | 88.76
15:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 350 | 0 |  | 0 | 350 | 146 | 8 | 80 | 25 | 260 | 0 | 0 | 50 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 85 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 205 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 84 | 6 | 0 | 0 | 0 | 27 | 54 | 53 | 36 | 120 | 0 | 61 | 0 | 0 | 210 | 15 | 0 | 0 | 280 | 0 | 0 | 0 | 260 | 0 | 0 | 135 | 0 | 141 | 1 | 49 | 21 | 40 | 352 | 66 | 35 | 0 | 0 | 52 | 0 | 0 | 98 | 46 | 50 | 320 | 17 | 9 | 90 | 35 | 0 | 17 | 2 | 51 | 17 | 230 | 17 | 0 | 500 | 47 | 515 | 0 | 0 | 11 |  | 917 | 0 | 320 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 40 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 330 | 35 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1010 | 180 | 0 | 0 | 0 | 3 | 35 | 0 | 0 | 341 | 12 | 250 | 1256 | 50 | 0 | 0 | 7 |  | 7070 | 5440 | 12510 | 3605 | 917 | 1560 | 0 | 1776 | 4154 | 165 | 0 | 105 | 84 | 90 | 47 | 181.45 | 89.12
16:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 349 | 0 |  | 0 | 350 | 149 | 8 | 69 | 25 | 260 | 0 | 0 | 43 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 85 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 64 | 0 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 36 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 82 | 9 | 0 | 0 | 0 | 27 | 58 | 53 | 36 | 120 | 0 | 60 | 0 | 0 | 209 | 15 | 0 | 0 | 290 | 12 | 0 | 0 | 145 | 0 | 0 | 135 | 0 | 132 | 4 | 49 | 24 | 24 | 352 | 66 | 35 | 0 | 1 | 52 | 0 | 0 | 98 | 47 | 50 | 320 | 17 | 21 | 108 | 35 | 0 | 17 | 4 | 53 | 17 | 230 | 0 | 0 | 500 | 30 | 517 | 0 | 0 | 10 |  | 920 | 0 | 320 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 336 | 35 | 0 | 0 | 0 | 34 | 0 | 4 | 13 | 1080 | 180 | 0 | 0 | 1 | 7 | 35 | 0 | 0 | 341 | 4 | 250 | 1257 | 17 | 0 | 0 | 9 |  | 6954 | 5464 | 12418 | 3627 | 920 | 1575 | 0 | 1622 | 4227 | 165 | 0 | 88 | 82 | 73 | 30 | 192.91 | 89.22
17:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 363 | 0 |  | 0 | 350 | 142 | 11 | 34 | 25 | 324 | 0 | 0 | 16 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 63 | 0 | 0 | 12 | 0 | 0 | 14 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 34 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 74 | 12 | 0 | 0 | 0 | 27 | 54 | 53 | 36 | 163 | 0 | 59 | 0 | 0 | 208 | 15 | 0 | 0 | 300 | 12 | 2 | 0 | 145 | 0 | 0 | 137 | 0 | 132 | 1 | 60 | 17 | 24 | 376 | 67 | 35 | 0 | 0 | 52 | 0 | 0 | 52 | 56 | 50 | 320 | 0 | 9 | 108 | 35 | 0 | 0 | 0 | 55 | 32 | 230 | 0 | 0 | 400 | 39 | 519 | 0 | 0 | 8 |  | 920 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 319 | 53 | 0 | 0 | 0 | 34 | 0 | 4 | 13 | 1000 | 220 | 0 | 0 | 1 | 1 | 35 | 0 | 0 | 342 | 1 | 200 | 1156 | 8 | 0 | 0 | 3 |  | 6835 | 5271 | 12106 | 3778 | 920 | 1651 | 0 | 1456 | 3899 | 166 | 0 | 87 | 74 | 33 | 39 | 138 | 89.32
18:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 355 | 0 |  | 0 | 350 | 145 | 11 | 34 | 15 | 324 | 0 | 0 | 17 | 8 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 0 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 75 | 0 | 4 | 13 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 240 | 203 | 0 | 34 | 5 | 5 | 0 | 30 | 0 | 0 | 8 | 0 | 0 | 0 | 17 | 70 | 17 | 0 | 0 | 0 | 26 | 54 | 53 | 36 | 163 | 0 | 40 | 0 | 0 | 208 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 145 | 0 | 0 | 127 | 0 | 140 | 0 | 60 | 17 | 24 | 332 | 67 | 35 | 0 | 0 | 68 | 0 | 0 | 52 | 74 | 40 | 320 | 0 | 2 | 108 | 35 | 0 | 16 | 1 | 52 | 35 | 230 | 10 | 0 | 400 | 16 | 516 | 0 | 0 | 3 |  | 919 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 2 | 17 | 8 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 314 | 53 | 0 | 0 | 0 | 34 | 0 | 1 | 15 | 970 | 180 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 343 | 1 | 200 | 1161 | 3 | 0 | 0 | 0 |  | 6799 | 5172 | 11971 | 3648 | 919 | 1570 | 0 | 1492 | 3872 | 166 | 0 | 206 | 70 | 12 | 16 | 123 | 89.42
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 349 | 0 |  | 0 | 350 | 151 | 8 | 34 | 30 | 286 | 0 | 0 | 18 | 8 | 149 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 14 | 7 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 78 | 25 | 12 | 13 | 12 | 0 | 18 | 0 | 0 | 0 | 280 | 240 | 203 | 0 | 34 | 5 | 5 | 0 | 38 | 0 | 35 | 8 | 0 | 0 | 0 | 17 | 82 | 20 | 0 | 0 | 0 | 27 | 58 | 53 | 39 | 120 | 0 | 58 | 0 | 0 | 209 | 15 | 0 | 0 | 270 | 12 | 2 | 0 | 167 | 0 | 0 | 155 | 0 | 148 | 0 | 62 | 26 | 53 | 379 | 86 | 35 | 15 | 0 | 52 | 14 | 13 | 52 | 88 | 62 | 340 | 17 | 0 | 130 | 53 | 0 | 36 | 0 | 52 | 35 | 230 | 24 | 0 | 430 | 12 | 518 | 0 | 0 | 0 |  | 923 | 0 | 320 | 0 | 36 | 0 | 0 | 0 | 19 | 51 | 8 | 80 | 5 | 16 | 0 | 0 | 0 | 0 | 5 | 57 | 0 | 0 | 8 | 0 | 22 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 346 | 53 | 0 | 8 | 0 | 70 | 0 | 0 | 18 | 980 | 180 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 342 | 0 | 200 | 1302 | 0 | 0 | 0 | 0 |  | 7308 | 5561 | 12869 | 3691 | 923 | 1575 | 0 | 1893 | 4054 | 166 | 0 | 473 | 82 | 0 | 12 | 125.105 | 89.72
19:30 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 364 | 0 |  | 0 | 350 | 127 | 8 | 51 | 30 | 314 | 0 | 0 | 24 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 14 | 7 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 6 | 78 | 51 | 12 | 13 | 24 | 0 | 18 | 0 | 0 | 0 | 280 | 240 | 202 | 0 | 36 | 5 | 5 | 0 | 51 | 0 | 37 | 43 | 0 | 0 | 0 | 17 | 80 | 21 | 0 | 0 | 0 | 26 | 54 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 207 | 15 | 0 | 0 | 260 | 12 | 2 | 0 | 230 | 0 | 0 | 147 | 0 | 149 | 0 | 62 | 34 | 100 | 378 | 86 | 70 | 34 | 0 | 51 | 17 | 17 | 105 | 92 | 62 | 340 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 60 | 35 | 230 | 72 | 0 | 490 | 11 | 513 | 0 | 0 | 0 |  | 922 | 0 | 325 | 0 | 54 | 0 | 0 | 0 | 28 | 55 | 24 | 130 | 5 | 16 | 0 | 0 | 0 | 20 | 5 | 89 | 0 | 0 | 15 | 0 | 30 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 320 | 53 | 0 | 35 | 0 | 75 | 0 | 0 | 50 | 1150 | 220 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 343 | 0 | 250 | 1335 | 0 | 0 | 0 | 0 |  | 7850 | 6116 | 13966 | 3797 | 922 | 1611 | 0 | 2387 | 4363 | 166 | 0 | 629 | 80 | 0 | 11 | 80.22 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 359 | 0 |  | 0 | 350 | 127 | 8 | 55 | 30 | 320 | 0 | 0 | 34 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 92 | 80 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 6 | 78 | 51 | 0 | 12 | 44 | 0 | 18 | 0 | 0 | 0 | 280 | 240 | 203 | 0 | 36 | 5 | 5 | 0 | 51 | 0 | 37 | 50 | 0 | 0 | 0 | 17 | 80 | 21 | 0 | 0 | 0 | 26 | 54 | 53 | 39 | 163 | 0 | 59 | 0 | 0 | 208 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 245 | 0 | 0 | 157 | 0 | 145 | 0 | 62 | 34 | 70 | 338 | 86 | 70 | 29 | 0 | 52 | 0 | 23 | 110 | 91 | 62 | 310 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 59 | 35 | 230 | 54 | 0 | 560 | 15 | 516 | 0 | 0 | 0 |  | 922 | 0 | 280 | 0 | 48 | 0 | 0 | 0 | 48 | 70 | 24 | 130 | 6 | 16 | 0 | 0 | 0 | 24 | 8 | 89 | 0 | 0 | 22 | 0 | 30 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 295 | 53 | 0 | 40 | 0 | 101 | 0 | 0 | 50 | 1170 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 342 | 0 | 250 | 1343 | 0 | 0 | 0 | 0 |  | 7886 | 6150 | 14036 | 3692 | 922 | 1607 | 0 | 2424 | 4464 | 172 | 0 | 660 | 80 | 0 | 15 | 61.12 | 89.62
21:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 347 | 0 |  | 0 | 350 | 149 | 14 | 82 | 30 | 315 | 0 | 0 | 40 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 78 | 51 | 0 | 12 | 48 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 209 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 32 | 25 | 0 | 0 | 0 | 17 | 76 | 22 | 0 | 0 | 0 | 25 | 54 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 209 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 210 | 0 | 0 | 157 | 0 | 149 | 0 | 62 | 34 | 70 | 340 | 86 | 70 | 17 | 0 | 52 | 0 | 17 | 88 | 91 | 62 | 310 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 66 | 35 | 230 | 54 | 0 | 612 | 18 | 516 | 0 | 0 | 0 |  | 924 | 0 | 280 | 0 | 48 | 0 | 0 | 0 | 42 | 58 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 11 | 89 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 329 | 53 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 1240 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 343 | 0 | 250 | 1334 | 0 | 0 | 0 | 0 |  | 7878 | 6245 | 14123 | 3670 | 924 | 1664 | 0 | 2368 | 4577 | 166 | 0 | 660 | 76 | 0 | 18 | 121 | 89.72
22:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 352 | 0 |  | 0 | 350 | 130 | 8 | 82 | 30 | 333 | 0 | 0 | 46 | 8 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 78 | 51 | 0 | 16 | 50 | 0 | 35 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 37 | 40 | 0 | 0 | 0 | 17 | 76 | 22 | 0 | 0 | 0 | 25 | 54 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 209 | 15 | 0 | 0 | 290 | 12 | 2 | 0 | 210 | 0 | 0 | 157 | 0 | 145 | 0 | 62 | 34 | 70 | 340 | 87 | 70 | 17 | 0 | 52 | 0 | 17 | 114 | 91 | 62 | 310 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 67 | 35 | 230 | 54 | 0 | 570 | 22 | 516 | 0 | 0 | 0 |  | 841 | 0 | 280 | 0 | 64 | 0 | 0 | 0 | 42 | 44 | 8 | 80 | 10 | 40 | 0 | 0 | 0 | 24 | 10 | 89 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 298 | 53 | 0 | 66 | 0 | 106 | 0 | 0 | 92 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 343 | 0 | 250 | 1314 | 0 | 0 | 0 | 0 |  | 7861 | 6148 | 14009 | 3648 | 841 | 1593 | 0 | 2511 | 4519 | 166 | 0 | 633 | 76 | 0 | 22 | 134.655 | 89.82
23:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 319 | 0 |  | 0 | 350 | 140 | 9 | 82 | 30 | 330 | 0 | 0 | 55 | 8 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 78 | 51 | 0 | 19 | 50 | 0 | 36 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 37 | 51 | 0 | 0 | 0 | 17 | 78 | 23 | 0 | 0 | 0 | 27 | 59 | 53 | 39 | 120 | 0 | 55 | 0 | 0 | 210 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 255 | 0 | 0 | 137 | 0 | 149 | 0 | 62 | 34 | 70 | 398 | 87 | 35 | 17 | 0 | 52 | 0 | 17 | 114 | 89 | 50 | 310 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 41 | 35 | 230 | 54 | 0 | 574 | 22 | 520 | 0 | 0 | 0 |  | 841 | 0 | 280 | 0 | 80 | 0 | 0 | 0 | 42 | 43 | 8 | 80 | 10 | 48 | 0 | 0 | 0 | 24 | 10 | 89 | 0 | 0 | 40 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 332 | 53 | 0 | 70 | 0 | 106 | 0 | 0 | 95 | 1160 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 343 | 0 | 250 | 1240 | 0 | 0 | 0 | 0 |  | 7845 | 6012 | 13857 | 3675 | 841 | 1588 | 0 | 2520 | 4369 | 166 | 0 | 598 | 78 | 0 | 22 | 155.665 | 89.92
24:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 303 | 0 |  | 0 | 350 | 143 | 8 | 82 | 30 | 330 | 0 | 0 | 58 | 8 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 78 | 51 | 0 | 19 | 50 | 0 | 17 | 0 | 0 | 0 | 280 | 240 | 210 | 0 | 37 | 5 | 5 | 0 | 43 | 0 | 37 | 51 | 0 | 0 | 0 | 17 | 78 | 23 | 0 | 0 | 0 | 25 | 54 | 53 | 39 | 120 | 0 | 55 | 0 | 0 | 210 | 15 | 0 | 0 | 310 | 12 | 2 | 0 | 255 | 0 | 0 | 146 | 0 | 149 | 0 | 50 | 17 | 70 | 400 | 87 | 17 | 28 | 0 | 52 | 0 | 17 | 114 | 83 | 50 | 320 | 15 | 0 | 162 | 53 | 0 | 36 | 0 | 33 | 17 | 230 | 17 | 0 | 570 | 24 | 518 | 0 | 0 | 0 |  | 841 | 0 | 280 | 0 | 80 | 0 | 0 | 0 | 21 | 43 | 8 | 80 | 10 | 48 | 0 | 0 | 0 | 24 | 10 | 89 | 0 | 0 | 32 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 345 | 53 | 0 | 70 | 0 | 106 | 0 | 0 | 95 | 1160 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 342 | 0 | 250 | 1188 | 0 | 0 | 0 | 0 |  | 7680 | 5956 | 13636 | 3678 | 841 | 1615 | 0 | 2444 | 4310 | 166 | 0 | 480 | 78 | 0 | 24 | 233.02 | 90.02
KWH | 0 | 0 | 0 | 2835000 | 0 | 0 | 0 | 8870400 | 0 |  | 0 | 8199500 | 3385600 | 169920 | 1282381 | 576552 | 7628894 | 0 | 0 | 502694 | 178560 | 1162080 | 0 | 0 | 0 | 0 | 469800 | 792858 | 793970 | 0 | 32880 | 326160 | 293800 | 179600 | 180960 | 0 | 2037600 | 1904000 | 0 | 0 | 86472 | 5323429 | 0 | 0 | 0 |  | 147840 | 1044960 | 501430 | 13200 | 230400 | 324480 | 0 | 416640 | 0 | 0 | 0 | 7262400 | 5965000 | 5100000 | 16727 | 765840 | 274608 | 126720 | 0 | 979824 | 0 | 384928 | 496090 | 0 | 0 | 0 | 392730 | 1757760 | 360960 | 0 | 0 | 4300 | 623000 | 1287960 | 1236000 | 880344 | 3381627 | 0 | 1322688 | 0 | 0 | 5280520 | 364000 | 0 | 0 | 7035000 | 260640 | 86688 | 0 | 3126327 | 0 | 0 | 3362400 | 0 | 3452976 | 61830 | 1009920 | 532320 | 675781 | 9142000 | 1726800 | 874560 | 235018 | 13438 | 1191818 | 27290 | 170617 | 1841100 | 1428840 | 1014720 | 7831800 | 304320 | 145560 | 1612800 | 726382 | 0 | 525240 | 90542 | 1617600 | 559080 | 5821400 | 444945 | 0 | 12212726 | 698400 | 12458181 | 0 | 0 | 224145 |  | 21892363 | 0 | 8018496 | 0 | 966720 | 0 | 0 | 0 | 223200 | 334720 | 251625 | 2701000 | 193298 | 314592 | 0 | 0 | 0 | 135905 | 43558 | 531440 | 0 | 0 | 163194 | 0 | 210220 | 0 | 0 | 89586 | 1425163 | 0 | 5340000 | 0 | 0 | 0 | 0 | 4141009 | 0 | 0 | 0 | 0 | 0 | 8092655 | 595200 | 0 | 374112 | 0 | 1160563 | 0 | 29992 | 438720 | 27430100 | 5173005 | 0 | 0 | 13740 | 190800 | 1317504 | 0 | 0 | 9053000 | 144582 | 5869100 | 28647273 | 745130 | 0 | 2020 | 209520 |  | 170699290 | 136463105 | 307162395 | 92582488 | 21892363 | 39116940 | 0 | 37681122 | 102435543 | 3941600 | 0 | 5180580 | 1757760 | 1666079 | 698400 | 0
Fuel Cost | 0 | 0 | 0 | 12615750 | 0 | 0 | 0 | 25546752 | 0 |  | 0 | 26074410 | 11578752 | 3357619.2 | 23980524.7 | 10158846.24 | 23268126.7 | 0 | 0 | 9933233.44 | 3205152 | 22567593.6 | 0 | 0 | 0 | 0 | 8578548 | 12495442.08 | 14521711.3 | 0 | 24660 | 0 | 0 | 0 | 3240993.6 | 0 | 0 | 0 | 0 | 0 | 1637779.68 | 16981738.51 | 0 | 0 | 0 |  | 2600505.6 | 18401745.6 | 8980611.3 | 251592 | 4508928 | 5340940.8 | 0 | 0 | 0 | 0 | 0 | 20262096 | 18252900 | 16932000 | 56035.45 | 2473663.2 | 925428.96 | 555033.6 | 0 | 3929094.24 | 0 | 6894060.48 | 8959385.4 | 0 | 0 | 0 | 294547.5 | 11530905.6 | 1122585.6 | 0 | 0 | 0 | 2429700 | 4804090.8 | 5623800 | 4005565.2 | 11565164.34 | 0 | 7340918.4 | 0 | 0 | 14732650.8 | 2395120 | 0 | 0 | 21738150 | 195480 | 65882.88 | 0 | 63777070.8 | 0 | 0 | 64591704 | 0 | 60806907.36 | 0 | 17986675.2 | 9235752 | 11204448.98 | 24226300 | 32912808 | 16406745.6 | 4216222.92 | 0 | 19486224.3 | 530517.6 | 3060868.98 | 35183421 | 27733784.4 | 18072163.2 | 20832588 | 5194742.4 | 0 | 29498112 | 12188689.96 | 0 | 9386038.8 | 0 | 29149152 | 9470815.2 | 17289558 | 6264825.6 | 0 | 85122700.22 | 0 | 73503267.9 | 0 | 0 | 0 |  | 61517540.03 | 0 | 23654563.2 | 0 | 16772592 | 0 | 0 | 0 | 4198392 | 6296083.2 | 4478925 | 8535160 | 916232.52 | 5423566.08 | 0 | 0 | 0 | 2434058.55 | 799289.3 | 8933506.4 | 0 | 0 | 2922804.54 | 0 | 3765040.2 | 0 | 0 | 67816.602 | 15719547.89 | 0 | 45069600 | 0 | 0 | 0 | 0 | 13789559.97 | 0 | 0 | 0 | 0 | 0 | 23630552.6 | 10166016 | 0 | 7414899.84 | 0 | 23118414.96 | 0 | 0 | 8704204.8 | 177747048 | 16088045.55 | 0 | 0 | 0 | 0 | 22858694.4 | 0 | 0 | 66086900 | 0 | 43724795 | 189358474.53 | 0 | 0 | 0 | 0 |  | 1144268319.22 | 814192323.162 | 1958460642.382 | 279059637.122 | 61517540.03 | 125760835.5 | 0 | 691801379.82 | 696332333.54 | 0 | 0 | 92458010.77 | 11530905.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 371 | 0 |  | 0 | 350 | 144 | 9 | 80 | 25 | 333 | 0 | 0 | 11 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 13 | 15 | 16 | 10 | 16 | 0 | 86 | 78 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 36 | 5 | 5 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 16 | 82 | 10 | 0 | 0 | 0 | 27 | 58 | 50 | 37 | 163 | 0 | 53 | 0 | 0 | 210 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 45 | 0 | 0 | 200 | 0 | 135 | 10 | 49 | 17 | 0 | 400 | 68 | 53 | 0 | 2 | 100 | 0 | 0 | 56 | 55 | 50 | 350 | 17 | 21 | 25 | 17 | 0 | 17 | 27 | 49 | 17 | 240 | 28 | 0 | 550 | 51 | 518 | 0 | 0 | 27 |  | 917 | 0 | 325 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 28 | 0 | 1 | 0 | 1022 | 220 | 0 | 0 | 4 | 45 | 35 | 0 | 0 | 342 | 21 | 250 | 1253 | 182 | 0 | 0 | 26 |  | 12826 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 347 | 0 |  | 0 | 350 | 149 | 14 | 82 | 30 | 315 | 0 | 0 | 40 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 14 | 15 | 8 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 | 0 | 6 | 78 | 51 | 0 | 12 | 48 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 209 | 0 | 35 | 5 | 5 | 0 | 43 | 0 | 32 | 25 | 0 | 0 | 0 | 17 | 76 | 22 | 0 | 0 | 0 | 25 | 54 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 209 | 15 | 0 | 0 | 280 | 12 | 2 | 0 | 210 | 0 | 0 | 157 | 0 | 149 | 0 | 62 | 34 | 70 | 340 | 86 | 70 | 17 | 0 | 52 | 0 | 17 | 88 | 91 | 62 | 310 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 66 | 35 | 230 | 54 | 0 | 612 | 18 | 516 | 0 | 0 | 0 |  | 924 | 0 | 280 | 0 | 48 | 0 | 0 | 0 | 42 | 58 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 11 | 89 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 329 | 53 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 1240 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 343 | 0 | 250 | 1334 | 0 | 0 | 0 | 0 |  | 14123 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 150 | 16 | 82 | 30 | 325 | 0 | 0 | 60 | 8 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 14 | 15 | 16 | 16 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 78 | 51 | 60 | 12 | 48 | 0 | 30 | 0 | 0 | 0 | 280 | 240 | 215 | 8 | 40 | 5 | 5 | 0 | 43 | 0 | 43 | 52 | 0 | 0 |  | 17 | 142 | 22 | 0 | 0 | 0 | 25 | 54 | 51 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 15 | 0 | 0 | 300 | 12 | 2 | 0 | 270 | 0 | 0 | 142 | 0 | 149 | 0 | 50 | 17 | 135 | 400 | 88 | 70 | 51 | 0 | 52 | 54 | 51 | 114 | 91 | 50 | 350 | 17 | 0 | 162 | 53 | 0 | 36 | 0 | 115 | 35 | 230 | 163 | 0 | 612 | 62 | 520 | 0 | 0 |  |  | 927 | 0 | 300 | 0 | 98 | 0 | 0 | 0 | 42 | 60 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 24 | 11 | 90 | 35 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 350 | 53 | 0 | 113 | 0 | 106 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 350 | 0 | 307 | 748 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 16 | 80 | 25 | 300 | 0 | 0 | 40 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 14 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 62 | 51 | 30 | 12 | 6 | 0 | 30 | 0 | 0 | 0 | 280 | 240 | 215 | 8 | 40 | 5 | 5 | 0 | 43 | 0 | 43 | 25 | 0 | 0 |  | 16 | 146 | 16 | 0 | 0 | 1.6 | 25 | 54 | 50 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 15 | 0 | 0 | 300 | 12 | 2 | 0 | 263 | 0 | 0 | 200 | 0 | 149 | 20 | 34 | 17 | 135 | 400 | 69 | 52 | 51 | 5 | 52 | 54 | 17 | 50 | 46 | 50 | 340 | 17 | 50 | 162 | 17 | 0 | 36 | 35 | 104 | 35 | 230 | 54 | 0 | 612 | 44 | 520 | 0 | 0 | 70 |  | 927 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 30 | 50 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 24 | 0 | 50 | 35 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 62 | 0 | 200 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 350 | 25 | 0 | 113 | 0 | 100 | 0 | 8 | 60 | 1200 | 220 |  | 35 | 6 | 100 | 110 | 0 | 0 | 350 | 30 | 250 | 748 | 130 | 0 |  | 5 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 420 | 132 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 8 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 20 | 0 | 0 | 35 | 0 | 0 | 0 | 280 | 240 | 218 | 0 | 44 | 5 | 5 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 56 | 18 | 0 | 0 | 1 | 25 | 54 | 53 | 40 | 120 | 0 | 61 | 0 | 0 | 212 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 200 | 0 | 115 | 2 | 37 | 17 | 0 | 362 | 48 | 17 | 0 | 0 | 52 | 0 | 0 | 70 | 36 | 50 | 320 | 12 | 10 | 0 | 17 | 0 | 17 | 11 | 33 | 17 | 230 | 0 | 0 | 400 | 6 | 518 | 0 | 0 | 11 | 0 | 907 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 299 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 850 | 180 | 0 | 0 | 0 | 16 | 110 | 0 | 0 | 346 | 0 | 150 | 758 | 4 | 0 | 0 | 2 | 0 |  |  |  | 131699428 | 21892363 | 0 | 102435543 | 42861702 | 1757760 | 1666079 | 698400 | 3941600 |  |  | 306952875
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 131.6994 | 21.8924 | 0 | 102.4355 | 42.8617 | 1.7578 | 1.6661 | 0.6984 | 3.9416
| Minimum Generation |  | 11302 | 6:00
| Highest Generation |  | 14123 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [73 empty] | 306.9529
| Day Peak Generation |  | 12826 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 14123 | 21:00 |  |  |  |  | 10500 | [198 empty] | 202699852
| HVDC Max Flow |  | 924 | 21:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 924 | 21:00
| Load factor L.F |  | 90.62% | [167 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-05
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12826 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10790
Evening Peak Generation : |  |  | 14123 | MW Hour : | 21:00 | Available Max Generation : |  | 14980
E.P. Demand (at gen end) : |  |  | 14250 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13500
Maximum Generation : |  |  | 14123 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1480
Total Gen. (MKWH) : |  |  | 306.9529 | System Load Factor : | 90.62% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 732 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-05
Actual : |  | 90.5 | Ft.(MSL) , | Rule curve : | 84.64 | Ft.( MSL )
Gas Consumed : |  | Total = | 969.6 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 404820472.622
: |  |  | Coal : | 696332333.54 | Oil : | 784259390.59 | Total : | 1885412196.752
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 10 | 240:00 | 5213.1791 |  |  | 0 | 5.076%
Chittagong Area |  | 0 | 0:00 | 1436.3552 |  |  | 0 | 7.105%
Khulna Area |  | 0 | 0:00 | 2013.2249 |  |  | 0 | 7.539%
Rajshahi Area |  | 0 | 0:00 | 1750.9366 |  |  | 0 | 7.997%
Cumilla Area |  | 0 | 0:00 | 1440.1582 |  |  | 0 | 7.713%
Mymensingh Area |  | 111 | 2664:00 | 1071.6925 |  |  | 0 | 8.111%
Sylhet Area |  | 0 | 0:00 | 600.0987 |  |  | 0 | 7.351%
Barisal Area |  | 0 | 0:00 | 500.6751 |  |  | 0 | 8.184%
Rangpur Area |  | 0 | 0:00 | 979.2196 |  |  | 0 | 8.174%
Total |  | 121 |  | 15005.5398 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
09:10 | 11:40 | Rangpur-Saidpur 132kV Ckt-2 Forced S/D from Rangpur 132/33kV end Due to Red hot Maintenance
| 09:10 | Chowmuhani 132/33kV S/S TR3 is restored.
09:25 | 14:38 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Forced S/D Due to PRD maintenance
10:22 | 12:52 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Scheduled S/D Due to Maintenance work
11:56 |  | Bashkhali-Madunaghat 400kV ckt-1 was shutdown.
12:00 |  | Day peak Generation:12827 MW
13:09 | 18:24 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Project Work S/D Due to None
13:10 | 18:23 | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end Due to CB Open: 13:10 Line Isolator Open:
13:11 Earth S/W Close: 13:22 for Project Work
13:14 |  | Naogaon-Niyamatpur 132kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to CT, R-Phase Oil Leakage
13:18 | 13:28 | Fenchuganj-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance Realy. relays. and from
Fenchuganj 230/132/33kV end showing REC 650 and REL 670 relays Due to unknown
13:29 | 18:39 | Hasnabad-Sitalakhya 132kV Ckt-1 Scheduled S/D from Hasnabad 132/33kV end Due to Tower dismantled
13:32 | 14:49 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to Feeder name : 33 KV PDB incomer-1, (R-ph) redhot,
spark in bus section -2.
13:54 | 16:30 | Brahmanbaria 132/33kV S/S 401T HT Scheduled S/D Due to Gas leakage maintenance of Tr-1 A incoming.
13:54 | 16:30 | Brahmanbaria 132/33kV S/S 401T LT Scheduled S/D Due to Gas leakage maintenance of Tr-1 A incoming.
14:22 | 16:37 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Work by pbs. |  |  |  |  | 30.0MW load interruption.
14:23 | 16:37 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Work by pbs.
| 14:38 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
| 14:38 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
15:20 | 17:58 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Project Work S/D Due to 400 kV GNDP project.
15:21 | 17:58 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Project Work S/D Due to 400 kV GNDP project work.
15:24 | 22:22 | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Troubleshooting work by SPMD
15:25 | 22:22 | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Troubleshooting work by SPMD
15:32 | 16:50 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to Red-hot Maintenance By BPDB
21:00 |  | Evening Peak Gen. 14123 MW
21:22 | 22:19 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to Maintenance work by BPDB
05:25 | 06:25 | Rampura 230/132kV S/S Auto Transformer - 04 HT Scheduled S/D Due to New Auxiliary TX-4 connect to Auto Tx-4
05:25 | 06:25 | Rampura 230/132kV S/S Auto Transformer - 04 LT Scheduled S/D Due to New Auxiliary TX-4 connect to Auto Tx-4
07:10 |  | Bogura 230/132kV S/S 230KV Main 1 Scheduled S/D Due to BUS Upgradation
07:12 |  | Bogura 230/132kV S/S T-04 HT Scheduled S/D Due to BUS Upgradation
07:12 |  | Bogura 230/132kV S/S T-04 LT Scheduled S/D Due to BUS Upgradation
07:14 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D Due to Red hot maintanance
07:14 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D Due to Red hot maintanance
07:14 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For 33KV Bus-1 Maintenance Work by BPDB.
07:14 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For 33KV Bus-1 Maintenance Work by BPDB
07:20 |  | Mirpur 132/33kV S/S T1 LT Scheduled S/D Due to CT clamp hotspot maintenance and relay modification work
07:20 |  | Mirpur 132/33kV S/S T1 HT Scheduled S/D Due to CT clamp hotspot maintenance and relay modification work
Sub Divisional Engineer | [6 empty] | Executive Engineer
Network Operation Division | [6 empty] | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-04
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2835000 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 347 | 8870400 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8199500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 14 | 169920 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 149 | 3385600 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 1282381 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 576552 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 40 | 502694 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 7628894 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 178560 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 469800 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1162080
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 792858
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 793970 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 29 | 359040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 293800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 6 | 179600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 180960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 210 | 3126327 | High voltage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3452976
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 874560 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 304320 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1612800
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 90542
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 559080 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5634 | 2395 | 47882214
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 86472 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 61830
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 48 | 324480 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 166 | 3941600 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 5323429
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 235018 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 78 | 1044960 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 501430 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 13200 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 1009920 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 416640
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 230400 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 13438
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1191818 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 27290 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 170617 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 62 | 1014720 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 726382 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 54 | 444945 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 612 | 12212726
| Cox's Bazar Wind |  | IPP | 66 | 60 | 18 | 698400
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 516 | 12458181
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 224145
| Chattogram area Total |  |  |  | 4457 | 2072 | 42372041
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 5100000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7262400 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5965000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5821400 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 274608 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 5 | 126720 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 16727 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 979824 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 675781 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 384928 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 35 | 765840 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 532320 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 76 | 1757760
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 496090 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 392730 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1841100 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 91 | 1428840 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 66 | 1617600 | Low demand
| Cumilla Area Total |  |  |  | 2875 | 1546 | 35439668
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 22 | 360960 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4300
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 157 | 3362400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 86 | 1726800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 145560
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 147840 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 525240 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 307 | 6273100
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 25 | 623000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 54 | 1287960 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3381627
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1236000
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 880344 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 86688 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1322688
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5280520 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 364000 | Engine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 260640 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7035000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 340 | 9142000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 310 | 7831800 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1558 | 38732267
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 924 | 21892363
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 48 | 966720 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 223200
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 58 | 334720 | Low demand
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 280 | 8018496 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 251625 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 595200 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 190800
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 343 | 9053000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1756 | 41526124
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 314592 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 193298
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2701000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1240 | 27430100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5173005
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 5869100 | Low demand
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 2020
| Barisal Area Total |  |  |  | 2236 | 1866 | 41683115
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 24 | 135905 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 43558
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 163194 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 156 | 4141009
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 329 | 8092655 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 210220 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 89586 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 89 | 531440 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 374112 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 438720 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 13740
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1334 | 28647273
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 209520
| Rajshahi Area Total |  |  |  | 3381 | 2120 | 43090932
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 62 | 1425163
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5340000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1160563
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29992
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1317504
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 144582
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 745130
| Rangpur Area Total |  |  |  | 950 | 503 | 10162934
| Total |  |  |  | 26364 | 14123 | 307162395
| Eastern Grid Total |  |  |  | 15943 | 7878 | 170699290
| Western Grid Total |  |  |  | 10421 | 6245 | 136463105
| National Grid Total |  |  |  | 26364 | 14123 | 307162395
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-07-04
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8995.17 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4192.8 | MW
i) Dhaka area |  |  | 5001.97 |  | MW | i) Khulna area |  |  |  | 1645 | MW
ii) Chattogram area |  |  | 1276.9 |  | MW | ii) Barishal area |  |  |  | 408 | MW
iii) Cumilla area |  |  | 1228.3 |  | MW | iii) Rajshahi area |  |  |  | 1293.8 | MW
iv) Mymensingh area |  |  | 995 |  | MW | iv) Rangpur area |  |  |  | 846 | MW
v) Sylhet area |  |  | 493 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13187.97 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 100 | 09:00 | 133 | Rahim | 35 | 14:00
2 | AKSML | 105 | 06:00 | 68 | Jashore | 118 | 19:30 | 134 | Rajbari | 70 | 19:30
3 | Aftabnagar | 34 | 13:00 | 69 | Jhenaidah | 123 | 19:30 | 135 | Rajendrapur | 98 | 20:00
4 | Agargaon | 107 | 14:00 | 70 | Joydebpur | 183 | 14:00 | 136 | Rajshahi | 131 | 22:00
5 | Agrabad | 82 | 14:00 | 71 | Joypurhat | 60 | 22:00 | 137 | Rajshahi-230 | 69 | 21:00
6 | Amnura | 61 | 00:00 | 72 | Juldah | 15 | 00:00 | 138 | Ramganj | 110 | 00:00
7 | Ashuganj | 81 | 23:00 | 73 | KSRM | 44.5 | 07:00 | 139 | Rampur | 35 | 18:30
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 304 | 10:00 | 140 | Rangamati | 16 | 19:00
9 | BSRM | 187 | 05:00 | 75 | Kachua | 73 | 22:00 | 141 | Rangpur | 144 | 19:30
10 | Bagerhat | 81 | 00:00 | 76 | Kallyanpur | 99 | 00:00 | 142 | Ruppur | 6.6 | 11:00
11 | Bakulia | 96 | 20:00 | 77 | Kalurghat | 34 | 11:00 | 143 | SSM | 14 | 02:00
12 | Banani | 57 | 13:00 | 78 | Kamrangirchar | 54 | 13:00 | 144 | Saidpur | 99 | 19:30
13 | Bangabhaban | 18 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 119 | 00:00
14 | Barapukuria | 62 | 21:00 | 80 | Kazla | 107 | 13:00 | 146 | Satmasjid | 104 | 13:00
15 | Barguna | 20 | 00:00 | 81 | Keranigonj | 80 | 22:00 | 147 | Savar | 209 | 15:00
16 | Barishal | 104 | 12:00 | 82 | Khagrachori | 30 | 19:30 | 148 | SevenRings | 14.84 | 23:00
17 | Barishal-230 | 84 | 22:00 | 83 | Khulna | 62 | 13:00 | 149 | ShahCement | 20 | 01:00
18 | Baroaulia | 62 | 15:00 | 84 | Khulshi | 167 | 19:00 | 150 | Shahjadpur | 73 | 21:00
19 | Baroirhat | 54 | 21:00 | 85 | Kishoreganj | 148 | 20:00 | 151 | Shahjibazar | 125 | 23:00
20 | Bashundhara | 163 | 13:00 | 86 | Kodda | 288 | 21:00 | 152 | Shahmirpur | 45.5 | 18:30
21 | BashundharaCement | 12 | 10:00 | 87 | Kulaura | 54 | 22:00 | 153 | Shariatpur | 85 | 23:00
22 | Beanibazar | 73 | 22:00 | 88 | Kurigram | 56 | 22:00 | 154 | Sherpur | 146 | 22:00
23 | Benapole | 72 | 22:00 | 89 | Kushtia | 142 | 20:00 | 155 | Shikalbaha | 23 | 14:00
24 | Bhaluka | 152 | 19:30 | 90 | Lalbag | 100 | 14:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 50.5 | 22:00 | 91 | Lalmonirhat | 55 | 19:30 | 157 | Shitalakhya | 81.4 | 12:00
26 | Bhangura | 33 | 19:30 | 92 | MI_Cement | 7 | 07:00 | 158 | Sholosohor | 47 | 06:00
27 | Bheramara(GK) | 63 | 20:00 | 93 | Madanganj | 29 | 00:00 | 159 | Shyampur | 158 | 11:00
28 | Bhulta | 264 | 20:00 | 94 | Madaripur | 109 | 00:00 | 160 | Siddhirganj | 110 | 12:00
29 | Bog-Sherpur | 62 | 22:00 | 95 | Madartek | 72.58 | 00:00 | 161 | Sirajganj | 100 | 19:30
30 | Bogura | 162 | 19:30 | 96 | Madunaghat | 53 | 18:30 | 162 | Sonargaon | 101 | 11:00
31 | Borhanuddin | 86 | 00:00 | 97 | Magura | 59 | 19:30 | 163 | Sreemongol | 68 | 23:00
32 | Brahmanbaria | 160 | 00:00 | 98 | Mahasthangarh | 74 | 20:00 | 164 | Sreepur | 99 | 19:30
33 | Cantonment | 106 | 13:00 | 99 | Manikganj | 123 | 22:00 | 165 | Srinagar | 44.08 | 22:00
34 | Chandpur | 67 | 21:00 | 100 | Maniknagar | 77 | 13:00 | 166 | Sunamganj | 52 | 22:00
35 | Chandraghona | 32 | 19:00 | 101 | Matarbari | 42 | 19:00 | 167 | Sylhet | 42 | 23:00
36 | Chapai | 69 | 21:00 | 102 | Matuail | 71 | 10:00 | 168 | Sylhet-132 | 117 | 14:00
37 | Charsaidpur | 28 | 05:00 | 103 | Millgate | 126 | 15:00 | 169 | TK | 29 | 23:00
38 | Chauddagram | 69 | 00:00 | 104 | Mirpur | 133 | 14:00 | 170 | Tangail | 186 | 20:00
39 | Chhatak | 30 | 19:30 | 105 | Mirsorai | 7 | 00:00 | 171 | Thakurgaon | 104 | 00:00
40 | Chowmuhani | 221 | 22:00 | 106 | Mirzapur | 42 | 13:00 | 172 | Tongi | 108 | 11:00
41 | Chuadanga | 113 | 21:00 | 107 | Mithapukur | 54 | 19:00 | 173 | Ullahpara | 23 | 19:00
42 | Coxsbazar | 116 | 23:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 52 | 19:00
43 | Cumilla(N) | 147 | 00:00 | 109 | Mogbazar | 126.9 | 13:00 | 175 | Uttara | 76 | 13:00
44 | Cumilla(S) | 171 | 20:00 | 110 | Mongla | 36 | 11:00 | 176 | UttaraNew | 47 | 13:00
45 | Daudkandi | 157 | 21:00 | 111 | Motijheel | 36 | 12:00 | 177 | Zigatola | 82 | 23:00
46 | Dhaka | 40 | 13:00 | 112 | Munshiganj | 107 | 00:00
47 | Dhamrai | 126 | 11:00 | 113 | Mymensingh | 221 | 22:00
48 | Dhanmondi | 116 | 13:00 | 114 | Naogaon | 135 | 22:00
49 | Dohazari | 90 | 00:00 | 115 | Narail | 54 | 19:30
50 | Faridpur | 161 | 22:00 | 116 | Narinda | 72 | 13:00
51 | Fatullah | 87 | 10:00 | 117 | Narshingdi | 171 | 19:00
52 | Fenchuganj | 41 | 22:00 | 118 | Natore | 138 | 21:00
53 | Feni | 110 | 00:00 | 119 | Nawabganj | 46.2 | 22:00
54 | GPH | 92 | 10:00 | 120 | Netrakona | 106 | 22:00
55 | Ghatail | 48 | 17:00 | 121 | New | 57.1 | 12:00
56 | Ghorashal | 60 | 19:30 | 122 | Niamatpur | 77 | 22:00
57 | Goalpara | 32 | 13:00 | 123 | Noapara | 47 | 19:30
58 | Gollamari | 76 | 13:00 | 124 | PHP | 9 | 00:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-04 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 381 | 01:00 | 367 | 11:00 | Kaliakoir | 380 | 14:00 | 363 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Bhulta | 399 | 05:00 | 381 | 12:00 | Meghnaghat | 378 | 22:00 | 365 | 10:00
| Bibiana | 401 | 14:00 | 389 | 12:00 | Payra | 408 | 18:30 | 402 | 00:00
| BIPTC | 402 | 04:00 | 395 | 20:00 | Rahanpur | 406 | 18:00 | 392 | 00:00
| Bogura | 399 | 18:30 | 383 | 00:00 | Rampal | 400 | 18:30 | 386 | 12:00
| Gopalganj | 395 | 18:30 | 382 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 05:00 | 216 | 12:00 | Hasnabad | 228 | 18:00 | 219 | 12:00
| AKSML | 232 | 21:00 | 224 | 10:00 | Hathazari | 232 | 00:00 | 224 | 12:00
| Aminbazar | 226 | 20:00 | 216 | 12:00 | Ishurdi | 234 | 18:30 | 226 | 12:00
| Ashuganj | 231 | 14:00 | 222 | 12:00 | Jhenaidah | 226 | 18:30 | 216 | 12:00
| Ashuganj-400 | 231 | 14:00 | 222 | 12:00 | Kaliakoir | 228 | 14:00 | 217 | 12:00
| Baghabari | 231 | 18:30 | 223 | 11:00 | Keranigonj | 226 | 18:30 | 216 | 12:00
| Barapukuria | 219 | 18:30 | 214 | 00:00 | Khulna(S) | 230 | 18:30 | 220 | 00:00
| Barapukuria-230 | 219 | 18:30 | 214 | 00:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 239 | 18:00 | 232 | 00:00 | Maniknagar | 228 | 04:00 | 218 | 12:00
| Bheramara | 233 | 18:30 | 224 | 12:00 | Meghnaghat | 234 | 03:00 | 230 | 12:00
| Bhulta | 231 | 05:00 | 219 | 12:00 | Meghnaghat-400 | 231 | 18:30 | 222 | 12:00
| Bibiana | 230 | 18:30 | 224 | 10:00 | Mirsorai | 230 | 19:30 | 222 | 10:00
| BIPTC | 235 | 18:30 | 224 | 12:00 | Rajshahi | 233 | 18:00 | 223 | 01:00
| Bogura | 225 | 18:30 | 217 | 00:00 | Rampal | 230 | 18:30 | 219 | 12:00
| Bogura-400 | 225 | 18:00 | 218 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 241 | 06:00 | 237 | 00:00 | Rampura | 228 | 22:00 | 217 | 12:00
| BSRM | 232 | 19:30 | 221 | 10:00 | Shikalbaha | 235 | 18:30 | 225 | 10:00
| Cumilla(N) | 227 | 05:00 | 219 | 12:00 | Shyampur | 228 | 18:30 | 218 | 12:00
| Fenchuganj | 234 | 18:30 | 229 | 12:00 | Siddhirganj | 229 | 03:00 | 220 | 12:00
| Ghorashal | 230 | 00:00 | 222 | 12:00 | Sirajgonj | 237 | 19:30 | 231 | 00:00
| Ghorashal-230 | 228 | 18:30 | 218 | 12:00 | Sreepur | 228 | 18:30 | 220 | 12:00
| GPH | 233 | 19:30 | 223 | 10:00 | Tongi | 229 | 21:00 | 216 | 11:00
| Haripur | 228 | 05:00 | 218 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 133 | 03:00 | 123 | 12:00 | Kushtia | 135 | 18:00 | 130 | 00:00
| Agargaon | 131 | 02:00 | 125 | 12:00 | Lalbag | 131 | 04:00 | 124 | 12:00
| Agrabad | 132 | 00:00 | 126 | 09:00 | Lalmonirhat | 126 | 16:00 | 120 | 07:00
| AKS | 131 | 17:00 | 126 | 07:00 | Madanganj | 130 | 19:30 | 123 | 16:00
| Aminbazar | 136 | 20:00 | 128 | 11:00 | Madaripur | 130 | 10:00 | 125 | 00:00
| Amnura | 135 | 18:00 | 125 | 00:00 | Madartek | 133 | 05:00 | 124 | 12:00
| Ashuganj | 138 | 14:00 | 135 | 00:00 | Madunaghat | 135 | 20:00 | 128 | 09:00
| Bagerhat | 136 | 18:30 | 125 | 10:00 | Magura | 137 | 18:30 | 128 | 21:00
| Bakulia | 132 | 18:00 | 126 | 10:00 | Mahasthangarh | 130 | 18:00 | 124 | 01:00
| Banani | 133 | 02:00 | 123 | 12:00 | Manikganj | 130 | 05:00 | 122 | 12:00
| Bangabhaban | 129 | 04:00 | 121 | 11:00 | Maniknagar | 129 | 04:00 | 121 | 12:00
| Barapukuria | 131 | 18:30 | 125 | 11:00 | Matarbari | 130 | 08:00 | 117 | 19:00
| Barguna | 132 | 18:00 | 127 | 00:00 | Matuail | 130 | 20:00 | 124 | 12:00
| Barishal | 135 | 18:00 | 130 | 00:00 | Millgate | 134 | 02:00 | 126 | 12:00
| Barishal-230 | 136 | 18:30 | 130 | 01:00 | Mirpur | 134 | 05:00 | 125 | 11:00
| Baroaulia | 134 | 18:00 | 128 | 09:00 | Mirzapur | 131 | 18:30 | 122 | 12:00
| Baroirhat | 128 | 18:30 | 122 | 10:00 | Mithapukur | 127 | 17:00 | 122 | 18:30
| Bashundhara | 134 | 14:00 | 124 | 11:00 | MI_Cement | 132 | 20:00 | 124 | 16:00
| BashundharaCement | 130 | 19:30 | 123 | 16:00 | Modern | 133 | 18:00 | 127 | 12:00
| Beanibazar | 125 | 05:00 | 121 | 22:00 | Mogbazar | 135 | 21:00 | 125 | 10:00
| Benapole | 133 | 18:30 | 124 | 00:00 | Mongla | 135 | 18:30 | 125 | 02:00
| Bhaluka | 130 | 14:00 | 120 | 11:00 | Motijheel | 129 | 04:00 | 121 | 11:00
| Bhandaria | 131 | 17:00 | 122 | 00:00 | Munshiganj | 129 | 00:00 | 126 | 09:00
| Bhangura | 136 | 18:00 | 130 | 12:00 | Mymensingh | 134 | 14:00 | 117 | 00:00
| Bheramara | 135 | 18:00 | 131 | 12:00 | Naogaon | 129 | 18:30 | 121 | 00:00
| Bheramara(GK) | 136 | 18:30 | 131 | 12:00 | Narail | 135 | 18:00 | 128 | 00:00
| Bhulta | 123 | 19:00 | 116 | 12:00 | Narinda | 129 | 04:00 | 121 | 12:00
| Bog-Sherpur | 132 | 18:30 | 125 | 01:00 | Narshingdi | 126 | 06:00 | 113 | 12:00
| Bogura | 133 | 18:30 | 127 | 00:00 | Natore | 132 | 18:00 | 127 | 01:00
| Bogura-230 | 133 | 18:30 | 127 | 00:00 | Nawabganj | 133 | 18:00 | 125 | 12:00
| Brahmanbaria | 126 | 14:00 | 120 | 12:00 | Netrakona | 134 | 18:30 | 126 | 02:00
| Cantonment | 131 | 02:00 | 124 | 12:00 | New | 134 | 04:00 | 127 | 12:00
| Chandpur | 125 | 18:30 | 119 | 23:00 | Niamatpur | 136 | 08:00 | 129 | 00:00
| Chandraghona | 133 | 00:00 | 129 | 09:00 | Noapara | 136 | 18:30 | 128 | 11:00
| Chapai | 134 | 17:00 | 127 | 00:00 | Pabna | 134 | 18:00 | 129 | 12:00
| Charsaidpur | 131 | 19:30 | 124 | 17:00 | Palashbari | 127 | 18:00 | 121 | 19:30
| Chauddagram | 127 | 19:30 | 121 | 10:00 | Panchagarh | 130 | 02:00 | 116 | 11:00
| Chhatak | 128 | 05:00 | 123 | 00:00 | Patuakhali | 132 | 04:00 | 128 | 00:00
| Chowmuhani | 123 | 18:00 | 115 | 00:00 | Payra | 133 | 04:00 | 131 | 00:00
| Chuadanga | 132 | 18:30 | 121 | 21:00 | PHP | 127 | 18:30 | 121 | 00:00
| Coxsbazar | 124 | 15:00 | 118 | 19:00 | Postogola | 133 | 18:00 | 127 | 12:00
| Cumilla(N) | 131 | 18:30 | 125 | 12:00 | Purbachal | 133 | 02:00 | 123 | 12:00
| Cumilla(S) | 132 | 03:00 | 124 | 10:00 | Purbasadipur | 127 | 18:30 | 114 | 11:00
| Daudkandi | 126 | 18:30 | 119 | 10:00 | Rahanpur | 138 | 18:00 | 132 | 00:00
| Dhaka | 133 | 02:00 | 124 | 12:00 | Rahim | 129 | 20:00 | 124 | 12:00
| Dhamrai | 131 | 15:00 | 122 | 10:00 | Rajbari | 132 | 18:30 | 127 | 00:00
| Dhanmondi | 134 | 04:00 | 124 | 12:00 | Rajendrapur | 131 | 18:30 | 118 | 11:00
| Dohazari | 129 | 02:00 | 125 | 06:00 | Rajshahi | 133 | 18:00 | 127 | 12:00
| Faridpur | 132 | 18:30 | 126 | 00:00 | Rajshahi-230 | 134 | 18:00 | 121 | 00:00
| Fatullah | 132 | 14:00 | 126 | 12:00 | Ramganj | 121 | 07:00 | 16 | 01:00
| Fenchuganj | 132 | 06:00 | 128 | 14:00 | Rampur | 133 | 22:00 | 1 | 13:00
| Feni | 125 | 18:30 | 121 | 00:00 | Rampura | 132 | 04:00 | 123 | 12:00
| Ghatail | 132 | 18:30 | 124 | 03:00 | Rangamati | 133 | 00:00 | 128 | 10:00
| Ghorashal | 135 | 03:00 | 131 | 10:00 | Rangpur | 126 | 14:00 | 120 | 07:00
| Goalpara | 136 | 14:00 | 129 | 10:00 | Ruppur | 136 | 18:30 | 132 | 01:00
| Gollamari | 137 | 18:00 | 129 | 12:00 | Saidpur | 127 | 17:00 | 117 | 11:00
| Gopalganj | 133 | 18:30 | 126 | 12:00 | Satkhira | 134 | 18:00 | 124 | 00:00
| Gopalganj-400 | 132 | 18:00 | 127 | 01:00 | Satmasjid | 131 | 02:00 | 124 | 12:00
| Gulshan | 132 | 04:00 | 12 | 12:00 | Savar | 135 | 18:30 | 126 | 10:00
| Halishahar | 133 | 02:00 | 126 | 10:00 | SevenRings | 136 | 14:00 | 131 | 11:00
| Haripur | 129 | 20:00 | 124 | 12:00 | ShahCement | 131 | 19:30 | 124 | 17:00
| HaripurSBU | 129 | 20:00 | 124 | 12:00 | Shahjadpur | 139 | 04:00 | 134 | 12:00
| Hasnabad | 133 | 18:30 | 129 | 10:00 | Shahjibazar | 126 | 15:00 | 121 | 12:00
| Hathazari | 135 | 00:00 | 130 | 12:00 | Shahmirpur | 133 | 01:00 | 128 | 09:00
| Ishurdi | 136 | 06:00 | 132 | 12:00 | Shariatpur | 130 | 18:00 | 123 | 00:00
| Jaldhaka | 126 | 18:30 | 116 | 11:00 | Sherpur | 136 | 10:00 | 128 | 01:00
| Jamalpur | 139 | 12:00 | 130 | 02:00 | Shikalbaha | 122 | 00:00 | 116 | 09:00
| Jashore | 134 | 18:30 | 126 | 12:00 | Shikalbaha-230 | 134 | 18:30 | 127 | 09:00
| Jhenaidah | 138 | 18:30 | 130 | 00:00 | Shitalakhya | 132 | 20:00 | 124 | 16:00
| Jhenaidah-230 | 138 | 18:00 | 131 | 00:00 | Sholosohor | 133 | 18:30 | 126 | 10:00
| Joydebpur | 132 | 04:00 | 126 | 11:00 | Shyampur | 134 | 19:00 | 124 | 13:00
| Joypurhat | 128 | 18:30 | 119 | 01:00 | Shyampur-230 | 132 | 20:00 | 126 | 10:00
| Juldah | 133 | 00:00 | 128 | 07:00 | Siddhirganj | 130 | 19:30 | 124 | 12:00
| Kabirpur | 133 | 00:00 | 122 | 10:00 | Sirajganj | 132 | 18:00 | 127 | 00:00
| Kachua | 126 | 18:30 | 120 | 23:00 | Sonargaon | 127 | 21:00 | 122 | 12:00
| Kaliakoir | 132 | 14:00 | 125 | 10:00 | Sreemongol | 126 | 05:00 | 122 | 12:00
| Kallyanpur | 130 | 02:00 | -0.01 | 21:00 | Sreepur | 129 | 14:00 | 123 | 12:00
| Kalurghat | 135 | 20:00 | 128 | 10:00 | Srinagar | 132 | 18:00 | 125 | 12:00
| Kamrangirchar | 132 | 00:00 | 123 | 12:00 | SSM | 138 | 00:00 | 130 | 13:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 126 | 06:00 | 121 | 22:00
| Kazla | 129 | 06:00 | 120 | 13:00 | Sylhet | 128 | 18:00 | 125 | 00:00
| Keranigonj | 132 | 18:30 | 126 | 12:00 | Sylhet-132 | 129 | 06:00 | 127 | 00:00
| Khagrachori | 133 | 18:30 | 127 | 10:00 | Tangail | 130 | 00:00 | 122 | 12:00
| Khulna | 137 | 18:00 | 128 | 12:00 | Thakurgaon | 129 | 02:00 | 114 | 11:00
| Khulna(S) | 138 | 18:30 | 130 | 01:00 | TK | 133 | 03:00 | 127 | 10:00
| Khulshi | 132 | 22:00 | 125 | 10:00 | Tongi | 135 | 23:00 | 128 | 11:00
| Kishoreganj | 132 | 14:00 | 123 | 01:00 | Ullahpara | 133 | 07:00 | 130 | 00:00
| Kodda | 132 | 18:00 | 119 | 10:00 | Ullon | 133 | 03:00 | 123 | 12:00
| KSRM | 134 | 00:00 | 128 | 11:00 | Uttara | 135 | 06:00 | 128 | 10:00
| Kulaura | 130 | 05:00 | 13 | 04:00 | UttaraNew | 134 | 01:00 | 127 | 10:00
| Kurigram | 127 | 17:00 | 121 | 19:30 | Zigatola | 132 | 06:00 | 125 | 12:00

## L-Curve
Date | 2024-07-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 806 | 7680 | 5956 | 13636 |  |  |  | QF-LDC-11
0:30 | 878 | 7493.5 | 5952.5 | 13446 | Date: | 2024-07-04
1:00 | 950 | 7307 | 5949 | 13256
1:30 | 920 | 7254 | 5827 | 13081
2:00 | 890 | 7201 | 5705 | 12906
2:30 | 916 | 6993 | 5657 | 12650 | [5 empty] | Gen. at Eve. Peak | 14123 | 14123 MW (21:00 )
3:00 | 942 | 6785 | 5609 | 12394 | [6 empty] | 21:00
3:30 | 946 | 6737 | 5483 | 12220 | [5 empty] | Gen. at Day Peak | 12826 | 12826 MW (12:00 )
4:00 | 950 | 6689 | 5357 | 12046 | [6 empty] | 12:00
4:30 | 952 | 6652.5 | 5317.5 | 11970 | [5 empty] | Highest Generation | 14123
5:00 | 954 | 6616 | 5278 | 11894 | [6 empty] | 21:00
5:30 | 909 | 6474 | 5124 | 11598
6:00 | 864 | 6332 | 4970 | 11302
6:30 | 834 | 6338.5 | 4978.5 | 11317
7:00 | 804 | 6345 | 4987 | 11332
7:30 | 768 | 6318.5 | 5024 | 11342.5
8:00 | 732 | 6292 | 5061 | 11353
8:30 | 950 | 6360.5 | 5127.5 | 11488
9:00 | 1168 | 6429 | 5194 | 11623
9:30 | 1214 | 6585.5 | 5274.5 | 11860
10:00 | 1260 | 6742 | 5355 | 12097
10:30 | 1240 | 6833 | 5418 | 12251
11:00 | 1220 | 6924 | 5481 | 12405
11:30 | 1248 | 7013.5 | 5602 | 12615.5
12:00 | 1276 | 7103 | 5723 | 12826
12:30 | 1195 | 7158 | 5651 | 12809
13:00 | 1114 | 7213 | 5579 | 12792
13:30 | 1111 | 7211 | 5543.5 | 12754.5
14:00 | 1108 | 7209 | 5508 | 12717
14:30 | 1124 | 7139.5 | 5474 | 12613.5
15:00 | 1140 | 7070 | 5440 | 12510
15:30 | 1159 | 7012 | 5452 | 12464
16:00 | 1178 | 6954 | 5464 | 12418
16:30 | 1201 | 6894.5 | 5367.5 | 12262
17:00 | 1224 | 6835 | 5271 | 12106
17:30 | 1188 | 6817 | 5221.5 | 12038.5
18:00 | 1152 | 6799 | 5172 | 11971
18:30 | 1175 | 7053.5 | 5366.5 | 12420
19:00 | 1198 | 7308 | 5561 | 12869
19:30 | 920 | 7850 | 6116 | 13966
20:00 | 842 | 7886 | 6150 | 14036 |  |  |  | Executive Engineer
20:30 | 850 | 7882 | 6197.5 | 14079.5 |  |  |  | Network Operation Division
21:00 | 858 | 7878 | 6245 | 14123
21:30 | 837 | 7869.5 | 6196.5 | 14066
22:00 | 816 | 7861 | 6148 | 14009 |  |  |  |  | Page 6 of 7
22:30 | 823 | 7853 | 6080 | 13933
23:00 | 830 | 7845 | 6012 | 13857
23:30 | 818 | 7762.5 | 5984 | 13746.5
24:00 | 806 | 7680 | 5956 | 13636
14123 MW (21:00 )
12826 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-04 |  | Energy |  | 307162395
[15 empty] | 2024-07-04 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3678 | 841 | 1615 | 0 | 2444 | 4310 | 166 | 0 | 480 | 78 | 0 | 24 | 233.02
0:30 | 3758 | 876 | 1603 | 0 | 2117 | 4386.5 | 162.5 | 0 | 435 | 76 | 0 | 32 | 271.22 |  |  | Date: | 44015
1:00 | 3838 | 911 | 1591 | 0 | 1790 | 4463 | 159 | 0 | 390 | 74 | 0 | 40 | 309.42
1:30 | 3843.5 | 911 | 1591 | 0 | 1731.5 | 4413 | 159 | 0 | 323.5 | 73 | 0 | 35.5 | 304.645 | [9 empty] | Total Energy | 307.1624 | 307.1624 | Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
2:00 | 3849 | 911 | 1591 | 0 | 1673 | 4363 | 159 | 0 | 257 | 72 | 0 | 31 | 299.87 | [9 empty] | Energy not Served | 3.8726 | 3.8726
2:30 | 3851 | 911.5 | 1583 | 0 | 1487 | 4353 | 159 | 0 | 206.5 | 71 | 0 | 28 | 305.6 | [9 empty] | Energy Requirement | 311.035 | 311.035
3:00 | 3853 | 912 | 1575 | 0 | 1301 | 4343 | 159 | 0 | 156 | 70 | 0 | 25 | 311.33
3:30 | 3861.5 | 911 | 1607 | 0 | 1220 | 4253.5 | 160 | 0 | 116.5 | 69 | 0 | 21.5 | 291.275 | [8 empty] | Shortage
4:00 | 3870 | 910 | 1639 | 0 | 1139 | 4164 | 161 | 0 | 77 | 68 | 0 | 18 | 271.22
4:30 | 3884.5 | 910.5 | 1614 | 0 | 1093.5 | 4141.5 | 161 | 0 | 73 | 68 | 0 | 24 | 257.85
5:00 | 3899 | 911 | 1589 | 0 | 1048 | 4119 | 161 | 0 | 69 | 68 | 0 | 30 | 244.48
5:30 | 3938.5 | 911 | 1595 | 0 | 843 | 4005 | 163 | 0 | 42.5 | 66 | 5.5 | 28 | 216.785
6:00 | 3978 | 911 | 1601 | 0 | 638 | 3891 | 165 | 0 | 16 | 64 | 11 | 26 | 189.09
6:30 | 3993.5 | 910.5 | 1602.5 | 0 | 638 | 3871.5 | 165.5 | 0 | 16 | 64 | 25.5 | 28 | 186.7025 | [7 empty] | Coal
7:00 | 4009 | 910 | 1604 | 0 | 638 | 3852 | 166 | 0 | 16 | 64 | 40 | 30 | 184.315
7:30 | 3979 | 913.5 | 1604.5 | 0 | 644.5 | 3855.5 | 166 | 0 | 16 | 67 | 63 | 30 | 171.9 | [6 empty] | Oil
8:00 | 3949 | 917 | 1605 | 0 | 651 | 3859 | 166 | 0 | 16 | 70 | 86 | 30 | 159.485
8:30 | 3933 | 917 | 1605 | 0 | 727 | 3892.5 | 169 | 0 | 16 | 72 | 129 | 23.5 | 130.835
9:00 | 3917 | 917 | 1605 | 0 | 803 | 3926 | 172 | 0 | 16 | 74 | 172 | 17 | 102.185
9:30 | 3924 | 917 | 1676.5 | 0 | 902 | 3965.5 | 169 | 0 | 16 | 76 | 190.5 | 20.5 | 71.5925
10:00 | 3931 | 917 | 1748 | 0 | 1001 | 4005 | 166 | 0 | 16 | 78 | 209 | 24 | 41
10:30 | 3929 | 917 | 1711 | 0 | 1109 | 4041.5 | 166 | 0 | 18 | 77 | 252.5 | 26.5 | 42
11:00 | 3927 | 917 | 1674 | 0 | 1217 | 4078 | 166 | 0 | 20 | 76 | 296 | 29 | 43
11:30 | 3915.5 | 917 | 1699.5 | 0 | 1284 | 4147.5 | 165 | 0 | 34.5 | 79 | 318 | 40 | 33
12:00 | 3904 | 917 | 1725 | 0 | 1351 | 4217 | 164 | 0 | 49 | 82 | 340 | 51 | 23
12:30 | 3849.5 | 917 | 1686 | 0 | 1488.5 | 4223 | 164 | 0 | 82.5 | 80 | 240.5 | 50.5 | 79.7825
13:00 | 3795 | 917 | 1647 | 0 | 1626 | 4229 | 164 | 0 | 116 | 78 | 141 | 50 | 136.565
13:30 | 3795 | 917 | 1647 | 0 | 1626 | 4229 | 164 | 0 | 116 | 78 | 141 | 50 | 136.565
14:00 | 3795 | 917 | 1647 | 0 | 1626 | 4229 | 164 | 0 | 116 | 78 | 141 | 50 | 136.565
14:30 | 3700 | 917 | 1603.5 | 0 | 1701 | 4191.5 | 164.5 | 0 | 110.5 | 81 | 115.5 | 48.5 | 159.0075
15:00 | 3605 | 917 | 1560 | 0 | 1776 | 4154 | 165 | 0 | 105 | 84 | 90 | 47 | 181.45
15:30 | 3616 | 918.5 | 1567.5 | 0 | 1699 | 4190.5 | 165 | 0 | 96.5 | 83 | 81.5 | 38.5 | 187.18
16:00 | 3627 | 920 | 1575 | 0 | 1622 | 4227 | 165 | 0 | 88 | 82 | 73 | 30 | 192.91
16:30 | 3702.5 | 920 | 1613 | 0 | 1539 | 4063 | 165.5 | 0 | 87.5 | 78 | 53 | 34.5 | 165.455
17:00 | 3778 | 920 | 1651 | 0 | 1456 | 3899 | 166 | 0 | 87 | 74 | 33 | 39 | 138
17:30 | 3713 | 919.5 | 1610.5 | 0 | 1474 | 3885.5 | 166 | 0 | 146.5 | 72 | 22.5 | 27.5 | 130.5
18:00 | 3648 | 919 | 1570 | 0 | 1492 | 3872 | 166 | 0 | 206 | 70 | 12 | 16 | 123
18:30 | 3669.5 | 921 | 1572.5 | 0 | 1692.5 | 3963 | 166 | 0 | 339.5 | 76 | 6 | 14 | 124.0525
19:00 | 3691 | 923 | 1575 | 0 | 1893 | 4054 | 166 | 0 | 473 | 82 | 0 | 12 | 125.105
19:30 | 3797 | 922 | 1611 | 0 | 2387 | 4363 | 166 | 0 | 629 | 80 | 0 | 11 | 93.1125
20:00 | 3692 | 922 | 1607 | 0 | 2424 | 4464 | 172 | 0 | 660 | 80 | 0 | 15 | 61.12
20:30 | 3681 | 923 | 1635.5 | 0 | 2396 | 4520.5 | 169 | 0 | 660 | 78 | 0 | 16.5 | 91.06
21:00 | 3670 | 924 | 1664 | 0 | 2368 | 4577 | 166 | 0 | 660 | 76 | 0 | 18 | 121
21:30 | 3659 | 882.5 | 1628.5 | 0 | 2439.5 | 4548 | 166 | 0 | 646.5 | 76 | 0 | 20 | 127.8275
22:00 | 3648 | 841 | 1593 | 0 | 2511 | 4519 | 166 | 0 | 633 | 76 | 0 | 22 | 134.655
22:30 | 3661.5 | 841 | 1590.5 | 0 | 2515.5 | 4444 | 166 | 0 | 615.5 | 77 | 0 | 22 | 145.16
23:00 | 3675 | 841 | 1588 | 0 | 2520 | 4369 | 166 | 0 | 598 | 78 | 0 | 22 | 155.665
23:30 | 3676.5 | 841 | 1601.5 | 0 | 2482 | 4339.5 | 166 | 0 | 539 | 78 | 0 | 23 | 194.3425 |  |  | Max Temp. in Dhaka |  | 31.2°C
24:00 | 3678 | 841 | 1615 | 0 | 2444 | 4310 | 166 | 0 | 480 | 78 | 0 | 24 | 233.02
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.162 MKWHr Energy Not Served 3.873 MKWHr Energy Requirement 311.035 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 92 | 86 | 86 | 86 | 84 | 85 | 85 | 85 | 86 | 86 |  | 86 | 86 | 92 | 86 | 86 | 86 | 86 | 2037600
2 | Karnaphuli Hydro PP Unit-4 & 5 | 74 | 74 | 74 | 76 | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1904000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 8 | 8 |  | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 86472
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 5 | 4 | 9 | 20 | 10 | 4 | 1 | 1 | 4 | 1 | 0 | [8 empty] | 61830
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 222 | 223 | 221 | 221 | 221 | 221 | 222 | 221 | 222 | 226 | 226 | 225 | 225 | 225 | 223 | 223 | 223 |  | 222 | 223 | 223 | 223 | 224 | 222 | 223 | 5323429
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 68 | 17 | 17 | 17 | [14 empty] | 25 | 51 | 51 | 51 | 51 | 51 | 51 | 501430
12 | Hathazari 100 MW peaking PP | 72 | 72 | 72 | 8 | [8 empty] | 43 | 64 | 64 | 64 | 63 | 75 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1044960
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | [17 empty] | 15 | 34 | 29 | 17 | 17 | 17 | 28 | 235018
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 36 | 36 | 36 | [14 empty] | 35 | 37 | 37 | 32 | 37 | 37 | 37 | 384928
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 329 | 329 | 329 | 330 | 330 | 330 | 330 | 326 | 324 | 324 | 334 | 333 | 330 | 260 | 260 | 260 | 324 | 324 |  | 286 | 314 | 320 | 315 | 333 | 330 | 330 | 7628894
18 | Kodda 300 MW PP Unit-2 (Summit) | 145 | 130 | 30 | [5 empty] | 38 | 45 | 45 | 45 | 133 | 250 | 260 | 145 | 145 | 145 |  | 167 | 230 | 245 | 210 | 210 | 255 | 255 | 3126327
19 | Ashuganj 195 MW PP (APSCL-United) | 8 |  | 0 | [23 empty] | 16727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2835000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 552 | 552 | 550 | 540 | 503 | 495 | 450 | 450 | 450 | 500 | 500 | 550 | 550 | 500 | 500 | 500 | 400 | 400 |  | 430 | 490 | 560 | 612 | 570 | 574 | 570 | 12212726
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 274608
33 | Ashuganj 225 MW CCPP | 210 | 217 | 218 | 217 | 218 | 217 | 190 | 203 | 196 | 214 | 217 | 212 | 214 | 199 | 205 | 214 | 215 | 203 |  | 203 | 202 | 203 | 209 | 213 | 212 | 210 | 5100000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 310 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5965000
| Ashuganj 450 MW CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 320 | 295 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7262400
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 300 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5821400
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 126720
36 | Chandpur 150 MW CCPP | 30 | 30 | 30 | 35 | 40 | 40 | 40 | 40 | 39 | 35 | 35 | 36 | 36 | 35 | 35 | 36 | 34 | 34 |  | 34 | 36 | 36 | 35 | 35 | 35 | 37 | 765840
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 356 | 361 | 364 | 378 | 389 | 402 | 405 | 401 | 396 | 379 | 376 | 371 | 366 | 367 | 350 | 349 | 363 | 355 |  | 349 | 364 | 359 | 347 | 352 | 319 | 303 | 8870400
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8199500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 16 | 16 | 12 | 12 | 10 | 8 | 6 | 6 | 9 | 12 | 17 |  | 20 | 21 | 21 | 22 | 22 | 23 | 23 | 360960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 11 | 5 | 8 | 11 | 20 | 21 | 21 | 5 | 9 | 21 | 9 | 2 | [8 empty] | 145560
44 | Fenchugonj CCPP Phase-1 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 26 | 26 | 27 | 27 | 27 | 26 |  | 27 | 26 | 26 | 25 | 25 | 27 | 25 | 623000
45 | Fenchugonj CCPP Phase-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 58 | 58 | 58 | 58 | 54 | 58 | 54 | 58 | 54 | 54 |  | 58 | 54 | 54 | 54 | 54 | 59 | 54 | 1287960
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 53 | 55 | 59 | 61 | 60 | 59 | 40 |  | 58 | 56 | 59 | 56 | 56 | 55 | 55 | 1322688
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 212 | 211 | 211 | 213 | 213 | 213 | 214 | 215 | 213 | 213 | 210 | 208 | 208 | 210 | 209 | 208 | 208 |  | 209 | 207 | 208 | 209 | 209 | 210 | 210 | 5280520
51 | Sylhet 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 364000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 86688
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 52 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1236000
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 0 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 260640
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 275 | 285 | 290 | 280 | 295 | 305 | 310 | 310 | 290 | 310 | 300 | 270 | 280 | 290 | 300 | 280 |  | 270 | 260 | 280 | 280 | 290 | 280 | 310 | 7035000
| Bibiyana South 400 MW | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 330 | 336 | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 320 | 320 |  | 340 | 340 | 310 | 310 | 310 | 310 | 320 | 7831800
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 793970
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 147840
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 74 | 72 | 70 | 68 | 68 | 64 | 64 | 70 | 74 | 78 | 76 | 82 | 78 | 82 | 84 | 82 | 74 | 70 |  | 82 | 80 | 80 | 76 | 76 | 78 | 78 | 1757760
64 | Malancha, Ctg. EPZ (United) | 27 | 27 | 27 | 29 | 29 | 29 | 29 | 7 | 2 | 2 | 2 | 2 | 8 | 8 | 10 | 7 | 14 | 7 |  | 18 | 18 | 18 | 23 | 35 | 36 | 17 | 416640
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 392730
69 | Summit Ashulia | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 13 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 32880
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 15 | 15 | 15 | 15 | 15 |  | 7 | 7 | 15 | 15 | 15 | 15 | 15 | 326160
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 293800
72 | Rupganj 33 MW PP(Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 179600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 98 | 98 | 98 | 98 | 98 | 52 | 34 | 34 | 34 | 34 | 34 | 56 | 98 | 98 | 98 | 98 | 52 | 52 |  | 52 | 105 | 110 | 88 | 114 | 114 | 114 | 1841100
| Chowmuhani 113 MW | 58 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 45 | 47 | 55 | 47 | 46 | 46 | 47 | 56 | 74 |  | 88 | 92 | 91 | 91 | 91 | 89 | 83 | 1428840
| Manikgonj 162MW PP(MPGL) | 35 | 35 | [9 empty] | 25 | 102 | 108 | 90 | 108 | 108 | 108 |  | 130 | 162 | 162 | 162 | 162 | 162 | 162 | 1612800
77 | Siddhirganj 100 PP(Dutch Bangla) | 13 | 9 | 9 | 9 | 9 |  |  |  |  | 3 | 8 | 11 | 38 | 50 | 50 | 43 | 16 | 17 |  | 18 | 24 | 34 | 40 | 46 | 55 | 58 | 502694
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 180960
79 | Kodda 150 MW PP | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 82 |  | 149 | 149 | 149 | 149 | 132 | 100 | 48 | 1162080
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 50 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 43 | 50 | 25 | 40 | 51 | 51 | 496090
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 35 | 35 |  | 35 | 70 | 70 | 70 | 70 | 35 | 17 | 874560
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 1 | 0 | 0 | [8 empty] | 13438
| Jodiac Power | [19 empty] | 14 | 17 | [5 empty] | 27290
| Karnaphuli Power Ltd. | 17 | 17 | [17 empty] | 13 | 17 | 23 | 17 | 17 | 17 | 17 | 170617
82 | Madanganj 102 PP(Summit) | 82 | 82 | 82 | 38 | 9 |  |  | 3 | 45 | 70 | 80 | 80 | 80 | 80 | 80 | 69 | 34 | 34 |  | 34 | 51 | 55 | 82 | 82 | 82 | 82 | 1282381
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 135 | 132 | 130 | 142 | 129 | 138 | 143 | 150 | 152 | 149 | 129 | 144 | 145 | 128 | 146 | 149 | 142 | 145 |  | 151 | 127 | 127 | 149 | 130 | 140 | 143 | 3385600
87 | Meghnaghat 100 MW(IEL) | 9 | 9 | 8 | 9 | 8 |  |  |  |  | 3 | 8 | 9 | 8 | 8 | 8 | 8 | 11 | 11 |  | 8 | 8 | 8 | 14 | 8 | 9 | 8 | 169920
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 9 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 304320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [17 empty] | 4 |  | 12 | 12 | [5 empty] | 13200
92 | Fenchuganj 44 MW (Energyprima) | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 40 | 40 | 37 | 37 | 37 | 40 | 5 | 36 | 36 | 36 | 36 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 880344
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 30 |  | 38 | 51 | 51 | 43 | 43 | 43 | 43 | 979824
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178560
95 | Patenga 50MW PP (Baraka) | 39 | 39 | [17 empty] | 12 | 24 | 44 | 48 | 50 | 50 | 50 | 324480
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | 12 | [7 empty] | 4 | 12 | 12 | 12 | 12 | 13 |  | 13 | 13 | 12 | 12 | 16 | 19 | 19 | 230400
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 |  |  |  | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 15 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 576552
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 792858
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 163 | 163 |  | 120 | 163 | 163 | 163 | 120 | 120 | 120 | 3381627
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 4300
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | [5 empty] | 2 | 26 | 31 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 469800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 111 | 111 | 111 | 117 | 117 | 117 | 117 | 117 | 163 | 200 | 200 | 200 | 137 | 137 | 135 | 135 | 137 | 127 |  | 155 | 147 | 157 | 157 | 157 | 137 | 146 | 3362400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 139 | 133 | 132 | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 135 | 132 | 132 | 141 | 132 | 132 | 140 |  | 148 | 149 | 145 | 149 | 145 | 149 | 149 | 3452976
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 |  |  |  |  | 10 | 49 | 49 | 49 | 49 | 49 | 49 | 60 | 60 |  | 62 | 62 | 62 | 62 | 62 | 62 | 50 | 1009920
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 17 | 17 | 17 | 21 | 24 | 17 | 17 |  | 26 | 34 | 34 | 34 | 34 | 34 | 17 | 532320
117 | Ashuganj 150 MW PP (Midland) | 10 | 10 | [10 empty] | 8 | 36 | 40 | 24 | 24 | 24 |  | 53 | 100 | 70 | 70 | 70 | 70 | 70 | 675781
118 | Bibiyana-III 400 MW CCPP | 388 | 388 | 388 | 388 | 388 | 388 | 400 | 403 | 403 | 402 | 404 | 400 | 404 | 380 | 352 | 352 | 376 | 332 |  | 379 | 378 | 338 | 340 | 340 | 398 | 400 | 9142000
| Jamalpur 115 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 65 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 66 | 66 | 67 | 67 |  | 86 | 86 | 86 | 86 | 87 | 87 | 87 | 1726800
| Anwara 300 MW PP (United) | 68 | 69 | 52 | 52 | 30 |  |  |  |  | 15 | 100 | 100 | 100 | 107 | 52 | 52 | 52 | 68 |  | 52 | 51 | 52 | 52 | 52 | 52 | 52 | 1191818
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 |  |  |  |  | 12 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 40 |  | 62 | 62 | 62 | 62 | 62 | 50 | 50 | 1014720
| Anlima Energy Ltd. | 57 | 38 | 20 | 17 | 17 |  |  |  |  | 6 | 17 | 17 | 18 | 35 | 35 | 35 | 35 | 35 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 726382
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 16 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 525240
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 0 | 3 | 5 | 11 | 35 | 27 | 6 | 16 | 2 | 4 |  | 1 | [8 empty] | 90542
| Chandpur 115(Doreen) | 101 | 100 | 102 | 101 | 100 | 90 | 82 | 80 | 67 | 49 | 50 | 49 | 51 | 51 | 51 | 53 | 55 | 52 |  | 52 | 60 | 59 | 66 | 67 | 41 | 33 | 1617600
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 559080
| Mirsharai 150 MW (Oil) | 17 | 17 | [9 empty] | 28 | 54 | 54 | 17 |  |  | 10 |  | 24 | 72 | 54 | 54 | 54 | 54 | 17 | 444945
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 40 | 31 | 25 | 18 | 30 | 26 | 30 | 30 | 17 | 24 | 29 | 51 | 50 | 39 | 47 | 30 | 39 | 16 |  | 12 | 11 | 15 | 18 | 22 | 22 | 24 | 698400
| Sonagazi 75 MW Solar Plant | [5 empty] | 2 | 4 | 3 | 25 | 40 | 1 | 27 | 17 | 65 | 11 | 10 | 8 | 3 | [8 empty] | 224145
| Matarbari 2*600 MW (CPGCL) | 517 | 515 | 517 | 516 | 517 | 518 | 517 | 518 | 517 | 520 | 518 | 518 | 516 | 503 | 515 | 517 | 519 | 516 |  | 518 | 513 | 516 | 516 | 516 | 520 | 518 | 12458181
120 | Eastern Zone Total | 7307 | 7201 | 6785 | 6689 | 6616 | 6332 | 6345 | 6292 | 6429 | 6742 | 6924 | 7103 | 7213 | 7209 | 7070 | 6954 | 6835 | 6799 |  | 7308 | 7850 | 7886 | 7878 | 7861 | 7845 | 7680 | 170699290
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 81 | 81 | 80 | 32 | 16 |  |  |  |  | 13 | 18 | 48 | 47 | 48 | 64 | 63 | 32 | 32 |  | 36 | 54 | 48 | 48 | 64 | 80 | 80 | 966720
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 22 | [16 empty] | 2 |  | 19 | 28 | 48 | 42 | 42 | 42 | 21 | 223200
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | [7 empty] | 17 | 17 | 35 | 35 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 595200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 2 | 15 | 11 | 8 | 40 | 45 | 8 | 7 | 3 | 7 | 1 | 1 | [8 empty] | 190800
131 | Rampal 1320 MW (BIFPCL) | 338 | 338 | 340 | 339 | 340 | 340 | 341 | 343 | 340 | 343 | 343 | 342 | 343 | 344 | 341 | 341 | 342 | 343 |  | 342 | 343 | 342 | 343 | 343 | 343 | 342 | 9053000
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 180 |  | 180 | 220 | 220 | 220 | 220 | 180 | 180 | 5173005
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | [9 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 40 | 48 | 48 | 314592
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 200 | 200 |  | 200 | 250 | 250 | 250 | 250 | 250 | 250 | 5869100
136 | Barisal 1 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2020
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 80 | 130 | 80 |  | 80 | 130 | 130 | 130 | 80 | 80 | 80 | 2701000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 9 | 9 | 8 | 7 | 6 | 5 | 6 | 7 | 7 | 7 | 7 | 6 | 6 | 7 |  | 5 | 5 | 6 | 10 | 10 | 10 | 10 | 193298
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | [9 empty] | 40 | 40 | 40 | 8 | 8 | 8 |  | 8 | 24 | 24 | 8 | 8 | 8 | 8 | 251625
143 | Gopalganj 100 MW Peaking PP | 41 | [16 empty] | 17 |  | 51 | 55 | 70 | 58 | 44 | 43 | 43 | 334720
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 911 | 911 | 912 | 910 | 911 | 911 | 910 | 917 | 917 | 917 | 917 | 917 | 917 | 917 | 917 | 920 | 920 | 919 |  | 923 | 922 | 922 | 924 | 841 | 841 | 841 | 21892363
147 | Bheramara 410 MW CCPP | 335 | 335 | 335 | 335 | 345 | 340 | 345 | 350 | 350 | 340 | 337 | 325 | 325 | 320 | 320 | 320 | 320 | 320 |  | 320 | 325 | 280 | 280 | 280 | 280 | 280 | 8018496
148 | Payra 1320 MW | 1140 | 1100 | 1080 | 1040 | 1020 | 990 | 1000 | 1000 | 1000 | 1000 | 1010 | 1022 | 1032 | 1022 | 1010 | 1080 | 1000 | 970 |  | 980 | 1150 | 1170 | 1240 | 1244 | 1160 | 1160 | 27430100
149
150 | Barapukuria TPP Unit-1 | 61 | 61 | 61 | 62 | 62 | 62 | 63 | 63 | 63 | 59 | 63 | 62 | 61 | 61 | 62 | 62 | 62 | 62 |  | 62 | 62 | 63 | 62 | 62 | 62 | 62 | 1425163
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5340000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 24 | [19 empty] | 20 | 24 | 24 | 24 | 24 | 24 | 135905
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 4 | 2 | 0 | 1 | 1 | 0 | [8 empty] | 13740
| Sirajganj 68 MW Solar Park | [5 empty] | 1 | 3 | 4 | 4 | 2 | 5 | 26 | 29 | 33 | 7 | 9 | 3 | [9 empty] | 209520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 156 | 156 | 156 | 156 | 156 | 156 | 157 | 163 | 171 | 190 | 187 | 184 | 191 | 158 | 159 | 156 | 157 | 156 |  | 158 | 173 | 166 | 156 | 156 | 156 | 169 | 4141009
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 305 | 311 | 302 | 342 | 301 | 314 | 344 | 348 | 347 | 414 | 379 | 394 | 359 | 302 | 330 | 336 | 319 | 314 |  | 346 | 320 | 295 | 329 | 298 | 332 | 345 | 8092655
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 5 | [18 empty] | 5 | 5 | 8 | 11 | 10 | 10 | 10 | 43558
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 89586
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 25 | [18 empty] | 8 | 15 | 22 | 42 | 42 | 40 | 32 | 163194
168 | Santahar 50 MW Peaking PP | 15 | 16 | 15 | [14 empty] | 12 |  | 22 | 30 | 30 | 30 | 30 | 30 | 30 | 210220
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 4 | 5 | 3 | 7 | 8 | 8 | 8 | 8 |  | 57 | 89 | 89 | 89 | 89 | 89 | 89 | 531440
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 8 | 35 | 40 | 50 | 66 | 70 | 70 | 374112
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 13 | 13 | 15 |  | 18 | 50 | 50 | 50 | 92 | 95 | 95 | 438720
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 70 | 49 | 42 | 34 | [6 empty] | 28 | 37 | 34 | 34 | 34 | 34 | 34 |  | 70 | 75 | 101 | 106 | 106 | 106 | 106 | 1160563
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 7 | 6 | 2 | 4 | 4 | 1 | [8 empty] | 29992
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 70 | 50 | 35 | [6 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 70 | 110 | 115 | 115 | 115 | 115 | 115 | 1317504
| Intraco Solar 30 MW | [5 empty] | 1 | 1 | 3 | 14 | 25 | 21 | 21 | 12 | 21 | 12 | 4 | 1 | 1 |  | 0 | [6 empty] | 144582
| Adani Power Jharkhanda Ltd | 1385 | 1327 | 1325 | 1197 | 1207 | 1016 | 1011 | 1015 | 1086 | 1113 | 1174 | 1253 | 1257 | 1259 | 1256 | 1257 | 1156 | 1161 |  | 1302 | 1335 | 1343 | 1334 | 1314 | 1240 | 1188 | 28647273
178 | Teesta Solar Limited | [5 empty] | 4 | 20 | 50 | 102 | 103 | 153 | 182 | 60 | 120 | 50 | 17 | 8 | 3 | [8 empty] | 745130