## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-07 | Sunday
|  | Date (day): | 2024-07-07 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15074.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16076 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-06 | 2024-07-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage |  | 16-07-24
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 404 | 410 | 400 | 412
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 66 | 80 | 92 |  | 8 | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 146 | 141 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 45 | 82 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 25 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 13 |  | 62 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 32 | 78 | 40 | 78 | 22 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 322 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 82 | 50 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 15 | 54 | 17 | 54 | 0 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 48 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 35 | 17 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 30 | 31 | 31 |  | 49 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 17 | 16 | 16 |  | 17 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 12 | 14 | 16 |  | 17 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 138 | 300 | 270 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 96 | 128 | 100 | 100
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 34 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 52 | 71 | 72 | 72 | 32 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 54 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 2085 | 2740 | 2396 | 2862 | 1533 | 1140
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 17 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 166 | 166 | 166 | 64 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 221 | 220 | 222
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 12 | 68 | 100 | 100 | 5 |  | Fuel Shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 78 | 70 | 78 | 20 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 70 | 70 | 30 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 60 | 60 | 34 | 74 | 26 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 23 | 5 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 8 | 37 | 25 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 49 | 51 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 0 | 17
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 7 | 51 | 17 | 51 | 59 |  | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 62 | 50 | 75 | 25 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 70 | 17 | 70 | 46 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 35 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 610 | 606 | 612 | 612 |  | 612 | Unit-2 shut down
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 6 | 8 | 44 | 62 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 520 | 520 | 520 | 520 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 44 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 1926 | 2216 | 2294 | 2533 | 790 | 959
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 213 | 215 | 215 | 215
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 280 | 80 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 250 | 250 | 110 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 280 | 230 | 230 | 170 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 30 | 30 | 30 | 15 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 20 | 20 | 20 | 35 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 8 | 122 | 150 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 35 | 43 | 43 |  | 9 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 42 | 50 | 50 | 113 |  | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 82 | 146 | 142
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 44 | 25 | 52
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 0 | 16 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 70 | 70 | 114
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 84 | 46 | 92 |  | 21 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 33 | 115 | 33 | 115
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1344 | 1719 | 1672 | 1868 | 893 | 79
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 10 | 17 | 22 | 22 | 180 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 117 | 146 | 116 | 135 | 65 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 87 | 69 | 88 | 27 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 36 | 17 | 36
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 270 | 292 | 281.6 | 287 | 180 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 26 | 25 | 25 | 25 |  | 45 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 56 | 56 | 54 | 54 |  | 36 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 40 | 40 |  | 10 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 2 | 2 |  | 9 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 55 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 212 | 210 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 12 | 15 | 15 | 5 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 270 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 403 | 402 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 345 | 386 | 340 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1632 | 1659 | 1671 | 1682 | 5 | 464
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 922 | 937 | 937
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 74 | 96 | 66 | 98 | 17 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 30 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 340 | 300 | 300 | 110 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 32 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 18 | 55 | 25 | 53 | 52 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 343 | 346 | 350 | 350 | 384 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1799 | 1833 | 1866 | 1848 | 1177 | 61
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 130 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1244 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 35 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 307 | 200 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1789 | 1935 | 1955 | 2056 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 24 | 32 |  | 20 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 11 | 0 | 11 |  | 60 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 28 | 35 | 35 |  |  | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 36 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint.
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 167 | 166 | 170 | 170 | 50 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 315 | 392 | 350 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 83 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 60 | 95 |  | 18 | Engine problem
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 756 | 759 | 1400 | 1400 |  | 748 | Unit-2 Under maint.
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 47 | 0 | 5 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1292 | 1661 | 2279 | 2437 | 493 | 1104
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 61 | 61 | 62 | 62 |  | 25
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 220 | 220 | 220 |  | 54 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 20 | 70 | 100 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 110 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 120 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 471 | 466 | 660 | 503 | 40 | 171
| Total |  |  |  |  | 27515 | 26364 | 12608 | 14521 | 15074.6 | 16076 | 5226 | 4042
A. |  | 2024-07-06 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 14551 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10963 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14620 | MW
3 | Day peak Generation : |  |  | 12608 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14040.25 | MW
4 | Evening peak Generation : |  |  | 14521 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 95 | MW
5 | Total Energy Generation : |  | 306.1649 | MKWHr | By Solar | 2.6968 | MKWHr
| By Gas : | 134.4421 | MKWHr |  | By Oil: | 47.1259 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 93.5291 | MKWHr |  | By Hydro: | 4.0229 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.28416 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5226 | MW | Dhaka | 5083.45 | 5013.45 |  | 70 |  | 18:00 |  | 95
|  |  | For Plants S/D or M/C prob = |  |  | 4042 | MW | Chittagong | 1334.8 | 1334.8 |  | 0 |  | 19:00 |  | 114
|  |  | Total = |  |  | 9268 | MW | Khulna | 1731 | 1731 |  | 0 |  | 19:30 |  | 124
7 | Total Gas Supplied : |  |  | 958.79 | MMCFD |  |  | Rajshahi | 1422 | 1422 |  | 0 |  | 20:00 |  | 143
8 | Fuel Cost : | i) Gas : | Taka | 406203302.974 | ii) Oil : | Taka | 860993817.33 | Comilla | 1374 | 1359 |  | 15 |  | 21:00 |  | 95
|  | iii) Coal : | Taka | 637878477.38 | Total | Taka | 1905075597.684 | Mymensingh | 1134 | 1124 |  | 10 |  | 22:00 |  | 104.095
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 6048.9 | MKWHr. | Sylhet | 620 | 620 |  | 0 |  | 23:00 |  | 103.14
| ii) During Peak Demand : |  |  | 458 | MW (W to E) at | 21:00 | hrs | Barisal | 470 | 470 |  | 0 |  | 24:00 |  | 219
| iii) Maximum : |  |  | 412 | MW at | 20:00 | hrs | Rangpur | 871 | 871 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.7°C |  |  | Total | 14040.25 | 13945.25 |  | 95
B. |  | 2024-07-07 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.7°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16076 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13300 | MW
4 | Reserve(Generation end) |  |  |  | 1076 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 315.6122 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11993 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2255 | MKWHr. | ii) HVDC Flow at Peak Time |  | 922 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8384 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 92.02 |  | (b) Today: | 93.08 |  | (c) Rule Curve: |  | 84.96
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-07-06 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 410 | 151 | 8 | 68 | 30 | 329 | 0 | 0 | 40 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 17 | 15 | 16 | 13 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 4 | 56 | 0 | 0 | 30 | 19 | 0 | 24 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 52 | 30 | 5 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 0 | 17 | 70 | 22 | 0 | 0 | 0 | 26 | 58 | 53 | 10 | 163 | 0 | 51 | 0 | 0 | 211 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 95 | 0 | 0 | 117 | 0 | 123 | 0 | 72 | 17 | 0 | 401 | 67 | 17 | 0 | 0 | 68 | 0 | 0 | 98 | 48 | 75 | 345 | 0 | 0 | 0 | 35 | 0 | 36 | 0 | 45 | 17 | 260 | 0 | 0 | 550 | 29 | 518 | 0 | 0 | 0 |  | 917 | 0 | 300 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 356 | 17 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 345 | 0 | 307 | 768 | 0 | 0 | 0 | 0 |  | 7139 | 5507 | 12646 | 3827 | 917 | 1735 | 0 | 1696 | 4014 | 165 | 0 | 193 | 70 | 0 | 29 | 52 | 91.72
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 148 | 9 | 68 | 30 | 323 | 0 | 0 | 40 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 17 | 15 | 16 | 13 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 4 | 56 | 0 | 0 | 25 | 19 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 219 | 0 | 50 | 30 | 5 | 0 | 43 | 0 | 0 | 48 | 0 | 0 | 0 | 17 | 68 | 22 | 0 | 0 | 0 | 26 | 58 | 53 | 10 | 163 | 0 | 56 | 0 | 0 | 211 | 15 | 0 | 0 | 275 | 12 | 5 | 0 | 95 | 0 | 0 | 117 | 0 | 126 | 0 | 59 | 17 | 0 | 400 | 67 | 17 | 0 | 0 | 51 | 0 | 0 | 98 | 47 | 75 | 345 | 10 | 0 | 0 | 35 | 0 | 36 | 0 | 37 | 17 | 230 | 0 | 0 | 550 | 16 | 516 | 0 | 0 | 0 |  | 916 | 0 | 300 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 296 | 17 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 345 | 0 | 307 | 762 | 0 | 0 | 0 | 0 |  | 7068 | 5336 | 12404 | 3767 | 916 | 1685 | 0 | 1671 | 4006 | 165 | 0 | 110 | 68 | 0 | 16 | 44 | 91.78
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 430 | 147 | 8 | 68 | 30 | 330 | 0 | 0 | 40 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 17 | 15 | 16 | 13 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 56 | 0 | 0 | 25 | 19 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 51 | 30 | 5 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 17 | 68 | 23 | 0 | 0 | 0 | 25 | 58 | 53 | 10 | 120 | 0 | 54 | 0 | 0 | 212 | 15 | 0 | 0 | 275 | 12 | 5 | 0 | 95 | 0 | 0 | 117 | 0 | 114 | 0 | 50 | 17 | 0 | 400 | 67 | 17 | 0 | 0 | 51 | 0 | 0 | 98 | 47 | 75 | 345 | 17 | 0 | 0 | 18 | 0 | 36 | 0 | 36 | 17 | 230 | 0 | 0 | 550 | 9 | 516 | 0 | 0 | 0 |  | 915 | 0 | 300 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 319 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 349 | 0 | 307 | 759 | 0 | 0 | 0 | 0 |  | 6960 | 5019 | 11979 | 3770 | 915 | 1674 | 0 | 1434 | 3864 | 165 | 0 | 80 | 68 | 0 | 9 | 39 | 91.84
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 138 | 8 | 34 | 30 | 330 | 0 | 0 | 11 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 17 | 15 | 16 | 13 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 25 | 19 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 51 | 30 | 5 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 11 | 66 | 23 | 0 | 0 | 0 | 25 | 58 | 53 | 10 | 120 | 0 | 54 | 0 | 0 | 211 | 15 | 0 | 0 | 285 | 12 | 5 | 0 | 30 | 0 | 0 | 117 | 0 | 114 | 0 | 50 | 17 | 0 | 401 | 67 | 17 | 0 | 0 | 51 | 0 | 0 | 98 | 46 | 75 | 345 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 35 | 17 | 230 | 0 | 0 | 550 | 13 | 515 | 0 | 0 | 0 |  | 914 | 0 | 300 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 342 | 0 | 307 | 675 | 0 | 0 | 0 | 0 |  | 6768 | 4893 | 11661 | 3766 | 914 | 1665 | 0 | 1260 | 3772 | 165 | 0 | 40 | 66 | 0 | 13 | 0 | 91.9
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 149 | 0 | 17 | 30 | 328 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 16 | 14 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 19 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 50 | 30 | 5 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 11 | 64 | 23 | 0 | 0 | 0 | 26 | 58 | 53 | 10 | 120 | 0 | 54 | 0 | 0 | 212 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 114 | 0 | 50 | 17 | 0 | 402 | 67 | 17 | 0 | 0 | 51 | 0 | 0 | 98 | 47 | 75 | 345 | 17 | 0 | 0 | 17 | 0 | 36 | 0 | 36 | 17 | 230 | 0 | 0 | 550 | 19 | 517 | 0 | 0 | 0 |  | 914 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 250 | 676 | 0 | 0 | 0 | 0 |  | 6560 | 4710 | 11270 | 3771 | 914 | 1720 | 0 | 873 | 3720 | 165 | 0 | 24 | 64 | 0 | 19 | 0 | 91.96
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 420 | 156 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 16 | 14 | 0 | 0 | 86 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 30 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 209 | 0 | 70 | 30 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 60 | 24 | 0 | 0 | 0 | 26 | 58 | 53 | 10 | 120 | 0 | 54 | 0 | 0 | 212 | 15 | 0 | 0 | 305 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 78 | 1 | 24 | 17 | 0 | 402 | 67 | 17 | 0 | 0 | 15 | 0 | 0 | 70 | 47 | 24 | 345 | 17 | 3 | 0 | 0 | 0 | 20 | 3 | 35 | 4 | 300 | 0 | 0 | 550 | 27 | 517 | 0 | 0 | 3 |  | 914 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 345 | 0 | 200 | 681 | 1 | 0 | 0 | 0 |  | 6396 | 4567 | 10963 | 3862 | 914 | 1730 | 0 | 588 | 3576 | 166 | 0 | 24 | 60 | 16 | 27 | 0 | 92.02
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 152 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 0 | 38 | 0 | 0 | 0 | 280 | 250 | 199 | 0 | 70 | 30 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 56 | 23 | 0 | 0 | 0 | 27 | 58 | 53 | 10 | 120 | 0 | 55 | 0 | 0 | 213 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 78 | 2 | 24 | 17 | 0 | 402 | 67 | 17 | 0 | 1 | 15 | 0 | 0 | 70 | 46 | 24 | 375 | 17 | 6 | 0 | 0 | 0 | 18 | 5 | 36 | 17 | 230 | 0 | 0 | 550 | 12 | 518 | 0 | 0 | 4 |  | 920 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 220 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 343 | 0 | 200 | 679 | 7 | 0 | 0 | 4 |  | 6411 | 4567 | 10978 | 3817 | 920 | 1755 | 0 | 627 | 3563 | 166 | 0 | 24 | 56 | 38 | 12 | 0 | 92.08
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 152 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 0 | 9 | 0 | 0 | 0 | 280 | 250 | 192 | 0 | 48 | 30 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 66 | 23 | 0 | 0 | 1 | 27 | 54 | 53 | 10 | 163 | 0 | 55 | 0 | 0 | 212 | 15 | 0 | 0 | 310 | 12 | 5 | 0 | 0 | 0 | 0 | 117 | 0 | 78 | 13 | 24 | 17 | 0 | 402 | 67 | 17 | 0 | 2 | 15 | 0 | 0 | 70 | 47 | 24 | 375 | 17 | 13 | 0 | 0 | 0 | 17 | 15 | 34 | 17 | 230 | 0 | 0 | 612 | 21 | 516 | 0 | 0 | 19 |  | 919 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 1 | 17 | 0 | 0 | 0 | 343 | 1 | 200 | 678 | 32 | 0 | 0 | 14 |  | 6511 | 4674 | 11185 | 3830 | 919 | 1769 | 0 | 630 | 3632 | 166 | 0 | 24 | 66 | 128 | 21 | 0 | 92.14
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 141 | 0 | 0 | 15 | 326 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 0 | 7 | 0 | 0 | 0 | 280 | 250 | 197 | 0 | 50 | 30 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 70 | 22 | 0 | 0 | 1 | 26 | 54 | 50 | 10 | 163 | 0 | 55 | 0 | 0 | 212 | 15 | 0 | 0 | 295 | 12 | 5 | 0 | 5 | 0 | 0 | 117 | 0 | 78 | 13 | 74 | 17 | 0 | 402 | 67 | 17 | 0 | 5 | 49 | 0 | 0 | 70 | 47 | 74 | 345 | 19 | 13 | 0 | 7 | 0 | 17 | 19 | 35 | 17 | 230 | 0 | 0 | 612 | 0 | 519 | 0 | 0 | 53 |  | 919 | 0 | 370 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 220 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 1 | 64 | 35 | 0 | 0 | 342 | 5 | 250 | 680 | 44 | 0 | 0 | 11 |  | 6672 | 5063 | 11735 | 3887 | 919 | 1780 | 0 | 894 | 3766 | 166 | 0 | 24 | 70 | 229 | 0 | 38 | 92.2
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 145 | 0 | 0 | 30 | 326 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 50 | 0 | 6 | 0 | 0 | 0 | 280 | 250 | 198 | 0 | 51 | 30 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 76 | 18 | 0 | 0 | 1 | 26 | 54 | 50 | 10 | 163 | 0 | 50 | 0 | 0 | 213 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 15 | 0 | 0 | 117 | 0 | 79 | 6 | 74 | 17 | 0 | 402 | 67 | 34 | 0 | 6 | 49 | 0 | 0 | 70 | 47 | 74 | 345 | 47 | 37 | 0 | 17 | 0 | 17 | 28 | 35 | 17 | 230 | 0 | 0 | 612 | 14 | 516 | 0 | 0 | 68 |  | 920 | 0 | 375 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 395 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 3 | 85 | 35 | 0 | 0 | 341 | 17 | 250 | 686 | 50 | 0 | 0 | 38 |  | 6805 | 5142 | 11947 | 3885 | 920 | 1773 | 0 | 991 | 3767 | 166 | 0 | 16 | 76 | 339 | 14 | 79 | 92.26
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 147 | 2 | 2 | 30 | 289 | 0 | 0 | 3 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 1 | 0 | 0 | 0 | 50 | 0 | 5 | 0 | 0 | 0 | 280 | 240 | 208 | 0 | 50 | 10 | 5 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82 | 10 | 0 | 0 | 2 | 26 | 56 | 50 | 10 | 120 | 0 | 54 | 0 | 0 | 212 | 15 | 0 | 0 | 290 | 12 | 5 | 0 | 15 | 0 | 0 | 117 | 0 | 80 | 20 | 74 | 17 | 0 | 404 | 67 | 34 | 0 | 5 | 57 | 0 | 0 | 70 | 48 | 50 | 345 | 52 | 36 | 17 | 17 | 0 | 17 | 31 | 33 | 0 | 230 | 17 | 0 | 610 | 30 | 517 | 0 | 0 | 50 |  | 920 | 0 | 375 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 353 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 4 | 97 | 35 | 0 | 0 | 339 | 12 | 307 | 750 | 90 | 0 | 0 | 45 |  | 6781 | 5290 | 12071 | 3820 | 920 | 1699 | 0 | 1043 | 3885 | 166 | 0 | 34 | 82 | 392 | 30 | 114 | 92.32
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 146 | 9 | 45 | 15 | 317 | 0 | 0 | 32 | 50 | 16 | 0 | 0 | 0 | 0 | 15 | 35 | 55 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 24 | 0 | 0 | 8 | 50 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 45 | 10 | 5 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 82 | 10 | 0 | 0 | 0 | 26 | 56 | 50 | 10 | 163 | 0 | 55 | 0 | 0 | 212 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 138 | 0 | 0 | 117 | 0 | 96 | 17 | 60 | 17 | 8 | 403 | 67 | 34 | 12 | 2 | 49 | 0 | 7 | 70 | 47 | 50 | 345 | 52 | 53 | 72 | 17 | 0 | 17 | 35 | 33 | 0 | 230 | 54 | 0 | 610 | 6 | 520 | 0 | 0 | 44 |  | 919 | 0 | 375 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 315 | 18 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 1130 | 220 | 0 | 0 | 5 | 70 | 35 | 0 | 0 | 343 | 15 | 307 | 756 | 120 | 0 | 0 | 47 |  | 7257 | 5351 | 12608 | 3834 | 919 | 1698 | 0 | 1454 | 3947 | 166 | 0 | 94 | 82 | 408 | 6 | 136 | 92.38
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 |  | 0 | 380 | 148 | 13 | 68 | 15 | 280 | 0 | 0 | 56 | 81 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 15 | 0 | 16 | 2 | 8 | 0 | 86 | 76 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 1 | 40 | 0 | 0 | 24 | 50 | 0 | 11 | 0 | 0 | 0 | 280 | 240 | 208 | 0 | 42 | 10 | 5 | 0 | 43 | 0 | 30 | 16 | 0 | 0 | 0 | 5 | 80 | 10 | 0 | 0 | 2 | 27 | 58 | 50 | 10 | 120 | 0 | 40 | 0 | 0 | 213 | 12 | 0 | 0 | 300 | 12 | 5 | 0 | 195 | 0 | 0 | 117 | 0 | 98 | 19 | 60 | 17 | 24 | 400 | 65 | 34 | 44 | 5 | 52 | 0 | 17 | 70 | 45 | 50 | 370 | 52 | 13 | 72 | 17 | 0 | 17 | 1 | 33 | 0 | 230 | 54 | 0 | 612 | 6 | 520 | 0 | 0 | 75 |  | 920 | 0 | 370 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 59 | 0 | 220 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 250 | 53 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 1040 | 180 | 0 | 0 | 5 | 20 | 36 | 0 | 0 | 342 | 6 | 307 | 744 | 160 | 0 | 0 | 20 |  | 7290 | 5104 | 12394 | 3671 | 920 | 1504 | 0 | 1741 | 3844 | 162 | 0 | 140 | 80 | 326 | 6 | 120 | 92.42
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 380 | 148 | 9 | 68 | 30 | 280 | 0 | 0 | 68 | 81 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 16 | 15 | 16 | 12 | 8 | 0 | 86 | 76 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 1 | 40 | 0 | 0 | 26 | 50 | 0 | 11 | 0 | 0 | 0 | 280 | 240 | 209 | 0 | 43 | 10 | 5 | 0 | 43 | 0 | 36 | 16 | 0 | 0 | 0 | 5 | 90 | 10 | 0 | 0 | 2 | 28 | 58 | 50 | 10 | 163 | 0 | 40 | 0 | 0 | 211 | 15 | 0 | 0 | 315 | 12 | 5 | 0 | 195 | 0 | 0 | 117 | 0 | 108 | 17 | 60 | 17 | 24 | 404 | 65 | 34 | 51 | 4 | 52 | 0 | 17 | 70 | 45 | 50 | 370 | 52 | 4 | 72 | 17 | 0 | 17 | 2 | 32 | 0 | 230 | 54 | 0 | 610 | 5 | 520 | 0 | 0 | 60 |  | 920 | 0 | 365 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 1 | 11 | 36 | 0 | 0 | 345 | 12 | 307 | 748 | 116 | 0 | 0 | 14 |  | 7449 | 5329 | 12778 | 3808 | 920 | 1767 | 0 | 1787 | 3850 | 162 | 0 | 146 | 90 | 243 | 5 | 116.51 | 92.32
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 149 | 9 | 68 | 30 | 314 | 0 | 0 | 80 | 81 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 16 | 15 | 16 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 40 | 0 | 12 | 32 | 50 | 0 | 6 | 0 | 0 | 0 | 280 | 240 | 211 | 0 | 42 | 10 | 5 | 0 | 43 | 0 | 36 | 24 | 0 | 0 | 0 | 11 | 92 | 11 | 0 | 0 | 1 | 25 | 54 | 50 | 10 | 163 | 0 | 49 | 0 | 0 | 211 | 15 | 0 | 0 | 300 | 12 | 5 | 0 | 195 | 0 | 0 | 117 | 0 | 107 | 14 | 60 | 17 | 24 | 403 | 65 | 17 | 61 | 2 | 51 | 6 | 17 | 98 | 45 | 50 | 340 | 53 | 18 | 162 | 17 | 0 | 17 | 1 | 34 | 0 | 230 | 17 | 0 | 609 | 6 | 518 | 0 | 0 | 40 |  | 920 | 0 | 360 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 414 | 55 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1090 | 220 | 0 | 0 | 1 | 20 | 35 | 0 | 0 | 352 | 17 | 307 | 753 | 81 | 0 | 0 | 16 |  | 7579 | 5376 | 12955 | 3816 | 920 | 1789 | 0 | 1937 | 3909 | 166 | 0 | 109 | 92 | 211 | 6 | 157.575 | 0
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 410 | 127 | 24 | 51 | 30 | 312 | 0 | 0 | 78 | 90 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 16 | 15 | 16 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 214 | 0 | 0 | 0 |  | 4 | 40 | 0 | 12 | 10 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 40 | 10 | 5 | 0 | 43 | 0 | 35 | 48 | 0 | 0 | 0 | 11 | 86 | 12 | 0 | 0 | 0 | 25 | 54 | 53 | 10 | 163 | 0 | 55 | 0 | 0 | 211 | 12 | 0 | 0 | 290 | 12 | 5 | 0 | 195 | 0 | 0 | 117 | 0 | 123 | 0 | 25 | 17 | 24 | 402 | 65 | 17 | 85 | 1 | 50 | 17 | 17 | 88 | 44 | 50 | 340 | 53 | 10 | 162 | 25 | 0 | 17 | 3 | 47 | 0 | 230 | 17 | 0 | 604 | 6 | 520 | 0 | 0 | 34 |  | 920 | 0 | 355 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 373 | 55 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 1100 | 220 | 0 | 0 | 0 | 72 | 35 | 0 | 0 | 354 | 10 | 307 | 748 | 49 | 0 | 0 | 6 |  | 7479 | 5340 | 12819 | 3805 | 920 | 1706 | 0 | 1922 | 3914 | 166 | 0 | 108 | 86 | 186 | 6 | 144.205 | 0
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 137 | 33 | 51 | 30 | 318 | 0 | 0 | 78 | 90 | 16 | 13 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 16 | 15 | 16 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 203 | 0 | 0 | 0 |  | 6 | 61 | 0 | 12 | 27 | 32 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 40 | 10 | 5 | 0 | 43 | 0 | 35 | 48 | 0 | 0 | 0 | 0 | 74 | 12 | 0 | 0 | 0 | 25 | 54 | 53 | 10 | 163 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 270 | 12 | 5 | 0 | 195 | 0 | 0 | 117 | 0 | 123 | 4 | 60 | 17 | 24 | 403 | 65 | 17 | 85 | 0 | 51 | 17 | 23 | 88 | 55 | 50 | 340 | 53 | 3 | 162 | 35 | 0 | 17 | 5 | 47 | 12 | 230 | 17 | 0 | 606 | 13 | 520 | 0 | 0 | 21 |  | 920 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 2 | 59 | 0 | 220 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 308 | 55 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 980 | 220 | 0 | 0 | 0 | 23 | 35 | 0 | 0 | 354 | 3 | 200 | 651 | 20 | 0 | 0 | 4 |  | 7580 | 4827 | 12407 | 3788 | 920 | 1627 | 0 | 2008 | 3590 | 166 | 0 | 138 | 74 | 83 | 13 | 127.015 | 0
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 400 | 147 | 38 | 68 | 30 | 317 | 0 | 0 | 78 | 90 | 16 | 13 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 15 | 15 | 24 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 6 | 61 | 0 | 12 | 35 | 50 | 0 | 5 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 40 | 10 | 5 | 0 | 43 | 0 | 35 | 42 | 0 | 0 | 0 | 11 | 76 | 12 | 0 | 0 | 0 | 25 | 54 | 53 | 10 | 120 | 0 | 57 | 0 | 0 | 211 | 12 | 0 | 0 | 290 | 12 | 5 | 0 | 195 | 0 | 0 | 117 | 0 | 125 | 1 | 12 | 17 | 24 | 402 | 67 | 17 | 85 | 0 | 51 | 17 | 51 | 88 | 81 | 12 | 310 | 53 | 0 | 108 | 35 | 0 | 17 | 1 | 65 | 17 | 230 | 17 | 0 | 540 | 4 | 473 | 0 | 0 | 3 |  | 922 | 0 | 350 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 333 | 55 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 900 | 180 | 0 | 0 | 0 | 15 | 35 | 0 | 0 | 346 | 0 | 200 | 653 | 6 | 0 | 0 | 1 |  | 7353 | 4648 | 12001 | 3686 | 922 | 1593 | 0 | 1990 | 3393 | 166 | 0 | 144 | 76 | 27 | 4 | 95 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 150 | 43 | 68 | 45 | 317 | 0 | 0 | 78 | 90 | 147 | 13 | 0 | 0 | 0 | 6 | 55 | 35 | 0 | 15 | 15 | 24 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 4 | 78 | 33 | 30 | 38 | 50 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 211 | 0 | 42 | 10 | 7 | 0 | 43 | 0 | 35 | 50 | 0 | 0 | 0 | 11 | 86 | 17 | 0 | 0 | 0 | 28 | 58 | 53 | 10 | 163 | 0 | 52 | 0 | 0 | 212 | 12 | 0 | 0 | 290 | 12 | 5 | 0 | 200 | 0 | 0 | 146 | 0 | 128 | 0 | 30 | 17 | 40 | 404 | 87 | 17 | 90 | 0 | 51 | 18 | 51 | 88 | 81 | 62 | 375 | 53 | 0 | 162 | 52 | 0 | 20 | 0 | 87 | 17 | 230 | 163 | 0 | 580 | 3 | 495 | 0 | 0 | 0 |  | 923 | 0 | 340 | 0 | 48 | 0 | 0 | 0 | 34 | 0 | 0 | 80 | 10 | 32 | 0 | 0 | 0 | 0 | 5 | 81 | 14 | 0 | 14 | 0 | 20 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 347 | 55 | 0 | 26 | 0 | 96 | 0 | 0 | 70 | 900 | 180 | 0 | 22 | 0 | 0 | 112 | 0 | 0 | 346 | 0 | 200 | 698 | 0 | 0 | 0 | 0 |  | 8232 | 5099 | 13331 | 3787 | 923 | 1663 | 0 | 2593 | 3500 | 166 | 0 | 610 | 86 | 0 | 3 | 114 | 0
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 400 | 130 | 61 | 68 | 55 | 318 | 0 | 0 | 78 | 85 | 148 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 15 | 24 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 3 | 78 | 71 | 45 | 38 | 50 | 0 | 12 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 42 | 30 | 10 | 0 | 43 | 0 | 35 | 42 | 0 | 0 | 0 | 11 | 86 | 18 | 0 | 0 | 0 | 25 | 56 | 53 | 10 | 163 | 0 | 51 | 0 | 0 | 212 | 12 | 0 | 0 | 265 | 12 | 5 | 0 | 295 | 0 | 0 | 146 | 0 | 128 | 0 | 60 | 17 | 85 | 404 | 87 | 52 | 105 | 0 | 51 | 54 | 58 | 70 | 81 | 62 | 385 | 53 | 0 | 162 | 53 | 0 | 36 | 0 | 105 | 17 | 280 | 163 | 0 | 605 | 7 | 515 | 0 | 0 | 0 |  | 921 | 0 | 340 | 0 | 52 | 0 | 0 | 0 | 47 | 0 | 16 | 126 | 10 | 64 | 0 | 0 | 0 | 40 | 5 | 81 | 14 | 0 | 21 | 0 | 28 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 376 | 55 | 0 | 50 | 0 | 98 | 0 | 0 | 85 | 1140 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 348 | 0 | 253 | 760 | 0 | 0 | 0 | 0 |  | 8732 | 5788 | 14520 | 3969 | 921 | 1692 | 0 | 3059 | 3903 | 166 | 0 | 717 | 86 | 0 | 7 | 124 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 132 | 57 | 68 | 55 | 260 | 0 | 0 | 78 | 82 | 150 | 13 | 0 | 0 | 0 | 49 | 55 | 35 | 0 | 15 | 15 | 22 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 2 | 78 | 85 | 58 | 38 | 50 | 0 | 15 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 40 | 30 | 15 | 0 | 43 | 0 | 35 | 42 | 0 | 0 | 0 | 17 | 84 | 18 | 0 | 0 | 0 | 25 | 56 | 53 | 10 | 163 | 0 | 56 | 0 | 0 | 210 | 12 | 0 | 0 | 285 | 12 | 5 | 0 | 280 | 0 | 0 | 146 | 0 | 124 | 0 | 60 | 17 | 82 | 402 | 87 | 52 | 105 | 0 | 51 | 51 | 63 | 70 | 81 | 62 | 386 | 56 | 0 | 162 | 53 | 0 | 36 | 0 | 104 | 17 | 280 | 163 | 0 | 606 | 9 | 516 | 0 | 0 | 0 |  | 921 | 0 | 345 | 0 | 71 | 0 | 0 | 0 | 40 | 0 | 24 | 126 | 10 | 64 | 0 | 0 | 0 | 40 | 8 | 83 | 14 | 0 | 35 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 293 | 55 | 0 | 82 | 0 | 98 | 0 | 0 | 90 | 1170 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 346 | 0 | 250 | 754 | 0 | 0 | 0 | 0 |  | 8701 | 5799 | 14500 | 3906 | 921 | 1639 | 0 | 3105 | 3923 | 166 | 0 | 747 | 84 | 0 | 9 | 143 | 0
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 400 | 141 | 66 | 82 | 55 | 322 | 0 | 0 | 78 | 82 | 150 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 15 | 17 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 78 | 85 | 0 | 37 | 50 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 42 | 30 | 20 | 0 | 43 | 0 | 35 | 44 | 0 | 0 | 0 | 0 | 82 | 17 | 0 | 0 | 0 | 25 | 56 | 53 | 10 | 163 | 0 | 55 | 0 | 0 | 210 | 12 | 0 | 0 | 270 | 12 | 5 | 0 | 300 | 0 | 0 | 146 | 0 | 128 | 0 | 60 | 17 | 122 | 402 | 87 | 52 | 68 | 0 | 51 | 17 | 51 | 70 | 84 | 62 | 386 | 71 | 0 | 162 | 70 | 0 | 36 | 0 | 115 | 17 | 280 | 35 | 0 | 606 | 8 | 520 | 0 | 0 | 0 |  | 922 | 0 | 340 | 0 | 96 | 0 | 0 | 0 | 42 | 0 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 40 | 11 | 83 | 28 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 392 | 55 | 0 | 50 | 0 | 70 | 0 | 0 | 50 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 346 | 0 | 200 | 759 | 0 | 0 | 0 | 0 |  | 8626 | 5895 | 14521 | 3920 | 922 | 1745 | 0 | 3086 | 3956 | 166 | 0 | 636 | 82 | 0 | 8 | 95 | 0
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 400 | 140 | 67 | 82 | 25 | 324 | 0 | 0 | 78 | 90 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 15 | 17 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 1 | 78 | 85 | 0 | 38 | 50 | 0 | 27 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 42 | 30 | 20 | 0 | 43 | 0 | 35 | 50 | 0 | 0 | 0 | 17 | 90 | 17 | 0 | 0 | 0 | 26 | 56 | 53 | 10 | 163 | 0 | 53 | 0 | 0 | 211 | 12 | 0 | 0 | 285 | 12 | 5 | 0 | 300 | 0 | 0 | 146 | 0 | 132 | 0 | 60 | 17 | 130 | 402 | 87 | 52 | 68 | 0 | 51 | 17 | 51 | 70 | 91 | 62 | 390 | 71 | 0 | 162 | 72 | 0 | 36 | 0 | 105 | 17 | 280 | 35 | 0 | 604 | 5 | 519 | 0 | 0 | 0 |  | 921 | 0 | 340 | 0 | 96 | 0 | 0 | 0 | 37 | 0 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 33 | 10 | 83 | 28 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 392 | 55 | 0 | 50 | 0 | 70 | 0 | 0 | 50 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 345 | 0 | 200 | 757 | 0 | 0 | 0 | 0 |  | 8660 | 5891 | 14551 | 3957 | 921 | 1763 | 0 | 3078 | 3949 | 166 | 0 | 622 | 90 | 0 | 5 | 104.095 | 92.86
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 400 | 148 | 66 | 82 | 25 | 280 | 0 | 0 | 78 | 73 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 15 | 15 | 17 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 0 | 71 | 85 | 0 | 38 | 50 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 40 | 30 | 20 | 0 | 43 | 0 | 38 | 51 | 0 | 0 | 0 | 17 | 92 | 18 | 0 | 0 | 0 | 27 | 58 | 53 | 10 | 163 | 0 | 52 | 0 | 0 | 212 | 12 | 0 | 0 | 300 | 12 | 5 | 0 | 293 | 0 | 0 | 146 | 0 | 132 | 0 | 60 | 17 | 137 | 403 | 87 | 35 | 68 | 0 | 51 | 17 | 17 | 70 | 89 | 62 | 330 | 71 | 0 | 162 | 72 | 0 | 36 | 0 | 75 | 17 | 250 | 35 | 0 | 575 | 0 | 518 | 0 | 0 | 0 |  | 922 | 0 | 335 | 0 | 93 | 0 | 0 | 0 | 36 | 0 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 33 | 10 | 83 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 354 | 55 | 0 | 58 | 0 | 80 | 0 | 0 | 85 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 345 | 0 | 253 | 763 | 0 | 0 | 0 | 0 |  | 8369 | 5953 | 14322 | 3818 | 922 | 1758 | 0 | 2992 | 3979 | 166 | 0 | 595 | 92 | 0 | 0 | 103.14 | 92.91
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 420 | 133 | 66 | 82 | 25 | 280 | 0 | 0 | 78 | 74 | 82 | 13 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 15 | 15 | 17 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 2 | 69 | 85 | 0 | 38 | 50 | 0 | 38 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 41 | 30 | 20 | 0 | 43 | 0 | 38 | 51 | 0 | 0 | 0 | 17 | 90 | 18 | 0 | 0 | 0 | 26 | 54 | 53 | 10 | 163 | 0 | 53 | 0 | 0 | 211 | 12 | 0 | 0 | 300 | 12 | 5 | 0 | 281 | 0 | 0 | 146 | 0 | 132 | 0 | 47 | 17 | 137 | 402 | 87 | 17 | 68 | 0 | 51 | 17 | 17 | 70 | 84 | 62 | 320 | 71 | 0 | 162 | 72 | 0 | 36 | 0 | 68 | 17 | 250 | 17 | 0 | 600 | 7 | 516 | 0 | 0 | 0 |  | 923 | 0 | 335 | 0 | 96 | 0 | 0 | 0 | 23 | 0 | 32 | 130 | 10 | 110 | 0 | 0 | 0 | 33 | 10 | 83 | 28 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 394 | 55 | 0 | 111 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 346 | 0 | 307 | 753 | 0 | 0 | 0 | 0 |  | 8230 | 6111 | 14341 | 3792 | 923 | 1804 | 0 | 3001 | 4046 | 166 | 0 | 512 | 90 | 0 | 7 | 219 | 92.96
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9748800 | 0 |  | 0 | 9602000 | 3457193 | 532800 | 1037567 | 678264 | 7595649 | 0 | 0 | 1032960 | 1148976 | 1081920 | 92000 | 0 | 0 | 0 | 452160 | 799346 | 794234 | 0 | 391200 | 342360 | 412200 | 274900 | 142560 | 0 | 2098920 | 1924000 | 0 | 0 | 64371 | 5255741 | 0 | 0 | 0 |  | 111120 | 907776 | 429820 | 122640 | 505920 | 478080 | 0 | 554880 | 0 | 0 | 0 | 7208400 | 5955000 | 5123000 | 0 | 1099720 | 545832 | 197760 | 0 | 964940 | 0 | 413088 | 719573 | 0 | 0 | 0 | 271760 | 1838400 | 403200 | 0 | 0 | 8350 | 623000 | 1314960 | 1252800 | 300600 | 3564164 | 0 | 1262112 | 0 | 0 | 5265070 | 328000 | 0 | 0 | 7141500 | 284256 | 120960 | 0 | 3369709 | 0 | 0 | 2978400 | 0 | 2655216 | 117720 | 1197120 | 428640 | 829672 | 9646000 | 1700400 | 646080 | 950945 | 27480 | 1154182 | 227073 | 459161 | 1941420 | 1397760 | 1309440 | 8409900 | 987840 | 205410 | 1693440 | 738927 | 0 | 622800 | 146728 | 1252800 | 320040 | 6010800 | 667418 | 0 | 14078180 | 284160 | 12392727 | 0 | 0 | 472127 |  | 22225454 | 0 | 8342784 | 0 | 1506240 | 0 | 0 | 0 | 190560 | 0 | 207000 | 2606000 | 196680 | 594912 | 0 | 0 | 0 | 174016 | 44097 | 598064 | 127890 | 0 | 176694 | 0 | 233660 | 0 | 0 | 95202 | 1415127 | 0 | 5342000 | 0 | 0 | 0 | 0 | 4368918 | 0 | 0 | 0 | 0 | 0 | 8554327 | 776160 | 0 | 442464 | 0 | 989251 | 0 | 7822 | 405408 | 28552000 | 5349556 | 0 | 203400 | 27000 | 436320 | 1382400 | 0 | 0 | 8436364 | 102378 | 6240000 | 17072727 | 815690 | 0 | 4093 | 325680 |  | 177596517 | 128568338 | 306164855 | 93305724 | 22225454 | 41136400 | 0 | 42208761 | 93529125 | 4022920 | 0 | 4917113 | 1838400 | 2696798 | 284160 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28076544 | 0 |  | 0 | 30534360 | 11823600.06 | 10528128 | 19402502.9 | 11951011.68 | 23166729.45 | 0 | 0 | 20411289.6 | 20624119.2 | 21010886.4 | 1715800 | 0 | 0 | 0 | 8256441.6 | 12597692.96 | 14526539.86 | 0 | 293400 | 0 | 0 | 0 | 2553249.6 | 0 | 0 | 0 | 0 | 0 | 1219186.74 | 16765813.79 | 0 | 0 | 0 |  | 1954600.8 | 15985935.36 | 7698076.2 | 2337518.4 | 9900854.4 | 7869196.8 | 0 | 0 | 0 | 0 | 0 | 20111436 | 18222300 | 17008360 | 0 | 3552095.6 | 1839453.84 | 866188.8 | 0 | 3869409.4 | 0 | 7398406.08 | 12995488.38 | 0 | 0 | 0 | 203820 | 12059904 | 1253952 | 0 | 0 | 0 | 2429700 | 4904800.8 | 5700240 | 1367730 | 12189440.88 | 0 | 7004721.6 | 0 | 0 | 14689545.3 | 2158240 | 0 | 0 | 22067235 | 213192 | 91929.6 | 0 | 68742063.6 | 0 | 0 | 57215064 | 0 | 46758353.76 | 0 | 21320707.2 | 7436904 | 13755961.76 | 25561900 | 32409624 | 12120460.8 | 17059953.3 | 0 | 18870875.7 | 4414299.12 | 8237348.34 | 37100536.2 | 27130521.6 | 23321126.4 | 22370334 | 16862428.8 | 0 | 30973017.6 | 12399195.06 | 0 | 11129436 | 0 | 22575456 | 5421477.6 | 17852076 | 9397245.44 | 0 | 98124914.6 | 0 | 73117089.3 | 0 | 0 | 0 |  | 62453525.74 | 0 | 24611212.8 | 0 | 26133264 | 0 | 0 | 0 | 3584433.6 | 0 | 3684600 | 8234960 | 932263.2 | 10256282.88 | 0 | 0 | 0 | 3116626.56 | 809179.95 | 10053455.84 | 2721499.2 | 0 | 3164589.54 | 0 | 4184850.6 | 0 | 0 | 72067.914 | 15608850.81 | 0 | 45086480 | 0 | 0 | 0 | 0 | 14548496.94 | 0 | 0 | 0 | 0 | 0 | 24978634.84 | 13256812.8 | 0 | 8769636.48 | 0 | 19705879.92 | 0 | 0 | 8043294.72 | 185016960 | 16637119.16 | 0 | 3935790 | 0 | 0 | 23984640 | 0 | 0 | 61585457.2 | 0 | 46488000 | 112850725.47 | 0 | 0 | 0 | 0 |  | 1215079437.26 | 764509590.164 | 1979589027.424 | 275237081.634 | 62453525.74 | 130966221.34 | 0 | 774590131.76 | 637878477.38 | 0 | 0 | 86403685.57 | 12059904 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 146 | 9 | 45 | 15 | 317 | 0 | 0 | 32 | 50 | 16 | 0 | 0 | 0 | 0 | 15 | 35 | 55 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 24 | 0 | 0 | 8 | 50 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 213 | 0 | 45 | 10 | 5 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 5 | 82 | 10 | 0 | 0 | 0 | 26 | 56 | 50 | 10 | 163 | 0 | 55 | 0 | 0 | 212 | 15 | 0 | 0 | 280 | 12 | 5 | 0 | 138 | 0 | 0 | 117 | 0 | 96 | 17 | 60 | 17 | 8 | 403 | 67 | 34 | 12 | 2 | 49 | 0 | 7 | 70 | 47 | 50 | 345 | 52 | 53 | 72 | 17 | 0 | 17 | 35 | 33 | 0 | 230 | 54 | 0 | 610 | 6 | 520 | 0 | 0 | 44 |  | 919 | 0 | 375 | 0 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 315 | 18 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 1130 | 220 | 0 | 0 | 5 | 70 | 35 | 0 | 0 | 343 | 15 | 307 | 756 | 120 | 0 | 0 | 47 |  | 12608 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 400 | 141 | 66 | 82 | 55 | 322 | 0 | 0 | 78 | 82 | 150 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 15 | 17 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 | 0 | 6 | 78 | 85 | 0 | 37 | 50 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 42 | 30 | 20 | 0 | 43 | 0 | 35 | 44 | 0 | 0 | 0 | 0 | 82 | 17 | 0 | 0 | 0 | 25 | 56 | 53 | 10 | 163 | 0 | 55 | 0 | 0 | 210 | 12 | 0 | 0 | 270 | 12 | 5 | 0 | 300 | 0 | 0 | 146 | 0 | 128 | 0 | 60 | 17 | 122 | 402 | 87 | 52 | 68 | 0 | 51 | 17 | 51 | 70 | 84 | 62 | 386 | 71 | 0 | 162 | 70 | 0 | 36 | 0 | 115 | 17 | 280 | 35 | 0 | 606 | 8 | 520 | 0 | 0 | 0 |  | 922 | 0 | 340 | 0 | 96 | 0 | 0 | 0 | 42 | 0 | 32 | 130 | 10 | 96 | 0 | 0 | 0 | 40 | 11 | 83 | 28 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 392 | 55 | 0 | 50 | 0 | 70 | 0 | 0 | 50 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 346 | 0 | 200 | 759 | 0 | 0 | 0 | 0 |  | 14521 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 150 | 92 | 85 | 55 | 330 | 0 | 0 | 78 | 92 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 15 | 16 | 16 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 78 | 85 | 70 | 38 | 50 | 0 | 20 | 0 | 0 | 0 | 280 | 250 | 215 | 8 | 50 | 30 | 20 | 0 | 43 | 0 | 43 | 52 | 0 | 0 |  | 17 | 142 | 22 | 0 | 0 | 0 | 25 | 54 | 51 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 15 | 0 | 0 | 300 | 12 | 2 | 0 | 300 | 0 | 0 | 135 | 0 | 100 | 0 | 74 | 17 | 150 | 400 | 88 | 52 | 100 | 0 | 52 | 17 | 51 | 114 | 92 | 75 | 350 | 72 | 0 | 162 | 70 | 0 | 36 | 0 | 115 | 35 | 230 | 163 | 0 | 612 | 62 | 520 | 0 | 0 |  |  | 937 | 0 | 300 | 0 | 98 | 0 | 0 | 0 | 42 | 60 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 32 | 11 | 90 | 35 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 113 | 0 | 106 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 350 | 0 | 307 | 1400 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 80 | 85 | 25 | 330 | 0 | 0 | 40 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 16 | 15 | 16 | 14 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 70 | 85 | 70 | 25 | 50 | 0 | 5 | 0 | 0 | 0 | 280 | 250 | 215 | 8 | 50 | 30 | 20 | 0 | 43 | 0 | 43 | 25 | 0 | 0 |  | 16 | 146 | 22 | 0 | 0 | 1.6 | 25 | 54 | 50 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 15 | 0 | 0 | 300 | 12 | 2 | 0 | 270 | 0 | 0 | 116 | 0 | 100 | 20 | 34 | 17 | 150 | 400 | 69 | 34 | 100 | 5 | 52 | 0 | 17 | 70 | 46 | 50 | 340 | 72 | 50 | 54 | 17 | 0 | 17 | 35 | 33 | 35 | 230 | 54 | 0 | 612 | 44 | 520 | 0 | 0 | 70 |  | 937 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 30 | 50 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 24 | 0 | 50 | 35 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 350 | 25 | 0 | 113 | 0 | 100 | 0 | 8 | 60 | 1200 | 220 |  | 35 | 6 | 100 | 110 | 0 | 0 | 350 | 30 | 250 | 1400 | 130 | 0 |  | 5 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 420 | 148 | 25 | 34 | 25 | 280 | 0 | 0 | 25 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 15 | 17 | 8 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 6 | 70 | 17 | 0 | 25 | 0 | 0 | 8 | 0 | 0 | 0 | 290 | 240 | 189 | 0 | 45 | 30 | 20 | 0 | 43 | 0 | 37 | 25 | 0 | 0 | 0 | 17 | 80 | 18 | 0 | 0 | 1 | 25 | 54 | 47 | 10 | 120 | 0 | 57 | 0 | 0 | 212 | 12 | 0 | 0 | 305 | 12 | 2 | 0 | 145 | 0 | 0 | 118 | 0 | 116 | 4 | 47 | 17 | 0 | 340 | 67 | 17 | 0 | 3 | 52 | 0 | 0 | 70 | 45 | 50 | 310 | 54 | 26 | 54 | 17 | 0 | 17 | 8 | 33 | 0 | 230 | 0 | 0 | 500 | 1 | 516 | 0 | 0 | 17 | 0 | 922 | 0 | 345 | 0 | 96 | 0 | 0 | 0 | 0 | 0 | 24 | 126 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1120 | 110 | 0 | 17 | 2 | 57 | 35 | 0 | 0 | 345 | 9 | 250 | 1040 | 70 | 0 | 0 | 20 | 0 |  |  |  | 134442124 | 22225454 | 0 | 93529125 | 47125874 | 1838400 | 2696798 | 284160 | 4022920 |  |  | 306164855
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 134.4421 | 22.2255 | 0 | 93.5291 | 47.1259 | 1.8384 | 2.6968 | 0.28416 | 4.0229
| Minimum Generation |  | 10963 | 6:00
| Highest Generation |  | 14551 | 22:00 |  |  |  |  | 4500 | [124 empty] | 0 | [73 empty] | 306.1649
| Day Peak Generation |  | 12608 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 14521 | 21:00 |  |  |  |  | 10500 | [198 empty] | 202699852
| HVDC Max Flow |  | 923 | 19:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 922 | 21:00
| Load factor L.F |  | 87.67% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-07
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12608 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 11993
Evening Peak Generation : |  |  | 14521 | MW Hour : | 21:00 | Available Max Generation : |  | 16076
E.P. Demand (at gen end) : |  |  | 14620 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 14551 | MW Hour : | 22:00 | Reserve(Generation end) |  | 1076
Total Gen. (MKWH) : |  |  | 306.1649 | System Load Factor : | 87.67% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 412 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-07
Actual : |  | 93.08 | Ft.(MSL) , | Rule curve : | 84.96 | Ft.( MSL )
Gas Consumed : |  | Total = | 958.79 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 406203302.974
: |  |  | Coal : | 637878477.38 | Oil : | 860993817.33 | Total : | 1905075597.684
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 70 | 1680:00 | 5019.2107 |  |  | 0 | -8.615%
Chittagong Area |  | 0 | 0:00 | 1381.88 |  |  | 0 | -6.78%
Khulna Area |  | 0 | 0:00 | 1936.5624 |  |  | 0 | -6.388%
Rajshahi Area |  | 0 | 0:00 | 1683.9775 |  |  | 0 | -5.973%
Cumilla Area |  | 15 | 360:00 | 1385.229 |  |  | 0 | -6.23%
Mymensingh Area |  | 10 | 240:00 | 1030.6659 |  |  | 0 | -5.87%
Sylhet Area |  | 0 | 0:00 | 577.2872 |  |  | 0 | -6.558%
Barisal Area |  | 0 | 0:00 | 481.4952 |  |  | 0 | -5.804%
Rangpur Area |  | 0 | 0:00 | 941.7111 |  |  | 0 | -5.813%
Total |  | 95 |  | 14438.019 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:18 | 12:30 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to BPDB 33KV Bus side Red Hot Maintenance work |  |  |  |  | 8.0MW load interrup.
08:24 | 11:30 | Barapukuria-Rangpur 132 kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to Temperature Rise
08:30 | 18:15 | Mymensingh RPCL-Tangail 132kV Ckt-1 Project Work S/D from Ghatail 132/33kV end Due to 400KV
Boropukuria-bogura-kaliakair line Conductor Stringing.
08:30 | 18:16 | Mymensingh RPCL-Tangail 132kV Ckt-2 Project Work S/D from Ghatail 132/33kV end Due to 400KV
Boropukuria-bogura-kaliakair line Conductor Stringing.
08:30 | 18:20 | Tangail 132/33kV S/S RPCL-1 Project Work S/D Due to Project work |  |  |  |  | 55.0MW load interrup.
08:30 | 18:20 | Tangail 132/33kV S/S RPCL-2 Project Work S/D Due to Project work |  |  |  |  | 55.0MW load interrup.
| 08:41 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 08:41 | Feni 132/33kV S/S T-1(405T) LT is restored.
09:07 | 14:46 | Naogaon-Niyamatpur 132kV Ckt-1 Forced S/D from Niamatpur 132/33kV end Due to ALDC,Bogura এর নির্দেশ এ Naogoan ckt-1
এর CB Open করা হয়।
| 10:07 | Mirpur 132/33kV S/S T1 HT is restored.
| 10:09 | Mirpur 132/33kV S/S T1 LT is restored.
10:12 | 18:10 | Joydebpur 132/33kV S/S GT-4 HT Scheduled S/D Due to 132KV GT-4 Transformer 33KV GIS leakage Maintenance
| 10:24 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
| 10:25 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
12:00 |  | Day Peak Generation : 11170 W
17:02 | 17:46 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Tripped showing WTI relays Due to WTI
18:23 |  | BIPTC S/S 20DF44 Tripped showing 87R relays.
21:00 |  | Evening Peak Generation: 13229 MW.
00:17 |  | Ghorashal # 5 was shut down due to gas shortage
01:17 | 05:13 | Sunamganj 132/33kV S/S Tr-1 HT Tripped showing REL-670 relays Due to unknown |  |  |  |  | 25.0MW load interrup.
06:00 |  | Min. Gen. 10964 MW
06:25 |  | Khulshi 132/33kV S/S 405T (T1) HT Scheduled S/D Due to 33kV Out-door Bus conductor(R-phase) change by BPDB.
06:25 |  | Khulshi 132/33kV S/S 405T (T1) LT Scheduled S/D Due to 33kV Out-door Bus conductor( R-phase) change by BPDB
Sub Divisional Engineer | [6 empty] | Executive Engineer
Network Operation Division | [6 empty] | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-06
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 410 | 9748800
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9602000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 66 | 532800 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 141 | 3457193 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 1037567 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 678264
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 92000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 78 | 1032960 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7595649 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 1148976 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 452160
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1081920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 799346
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 794234 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 733560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 412200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 274900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 142560 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 3369709
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 128 | 2655216
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 646080 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 987840 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1693440
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 146728
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 320040 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5634 | 2740 | 49436142
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 64371 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 117720
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 478080
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 166 | 4022920 | Machine problem.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 221 | 5255741
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 950945 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 78 | 907776 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 429820 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 122640 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 1197120 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 554880
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 37 | 505920 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27480
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 51 | 1154182 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 227073 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 459161 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 62 | 1309440 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 70 | 738927 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 35 | 667418 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 606 | 14078180
| Cox's Bazar Wind |  | IPP | 66 | 60 | 8 | 284160
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 520 | 12392727
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 472127
| Chattogram area Total |  |  |  | 4457 | 2216 | 46418808
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 5123000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7208400
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 5955000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 280 | 6010800 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 545832 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 20 | 197760 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 964940 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 122 | 829672 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 35 | 413088 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 42 | 1099720 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 428640 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 82 | 1838400
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 44 | 719573 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 271760 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 1941420 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 84 | 1397760 | Engine problem
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1252800
| Cumilla Area Total |  |  |  | 2875 | 1719 | 36198565
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 17 | 403200 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8350
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 146 | 2978400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1700400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 205410
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 111120 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 622800 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 292 | 6029680
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 25 | 623000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 56 | 1314960 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3564164
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1252800
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 300600 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 120960 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1262112
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 210 | 5265070 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 328000 | Engine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 284256 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7141500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 9646000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 386 | 8409900 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1659 | 39513322
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 922 | 22225454
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 96 | 1506240 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 190560 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8342784 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 207000 | Engine problem
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 776160 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 436320
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 346 | 8436364 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1833 | 42120882
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 594912 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 196680
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2606000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 28552000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5349556
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 203400 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 6240000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 4093
| Barisal Area Total |  |  |  | 2236 | 1935 | 43746641
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 174016 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 11 | 44097
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 28 | 127890
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 176694 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 166 | 4368918
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 392 | 8554327 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 233660 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 95202 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 83 | 598064 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 442464 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 405408 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27000
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 759 | 17072727
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 325680
| Rajshahi Area Total |  |  |  | 3381 | 1661 | 32646147
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1415127
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5342000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 989251 | Low demand
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 7822
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1382400
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 102378
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 815690
| Rangpur Area Total |  |  |  | 950 | 466 | 10054668
| Total |  |  |  | 26364 | 14521 | 306164855
| Eastern Grid Total |  |  |  | 15943 | 8626 | 177596517
| Western Grid Total |  |  |  | 10421 | 5895 | 128568338
| National Grid Total |  |  |  | 26364 | 14521 | 306164855
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-07-06
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9451.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4494.8 | MW
i) Dhaka area |  |  | 5013.45 |  | MW | i) Khulna area |  |  |  | 1731 | MW
ii) Chattogram area |  |  | 1334.8 |  | MW | ii) Barishal area |  |  |  | 470 | MW
iii) Cumilla area |  |  | 1359 |  | MW | iii) Rajshahi area |  |  |  | 1422.8 | MW
iv) Mymensingh area |  |  | 1124 |  | MW | iv) Rangpur area |  |  |  | 871 | MW
v) Sylhet area |  |  | 620 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13946.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 119 | 22:00 | 133 | Rahim | 36 | 09:00
2 | AKSML | 124 | 12:00 | 68 | Jashore | 119 | 19:30 | 134 | Rajbari | 72 | 20:00
3 | Aftabnagar | 36 | 19:00 | 69 | Jhenaidah | 123 | 19:30 | 135 | Rajendrapur | 108 | 20:00
4 | Agargaon | 100 | 13:00 | 70 | Joydebpur | 171 | 20:00 | 136 | Rajshahi | 126 | 21:00
5 | Agrabad | 88 | 19:00 | 71 | Joypurhat | 60 | 20:00 | 137 | Rajshahi-230 | 70 | 21:00
6 | Amnura | 63 | 22:00 | 72 | Juldah | 18 | 18:30 | 138 | Ramganj | 120 | 21:00
7 | Ashuganj | 87 | 23:00 | 73 | KSRM | 38 | 19:00 | 139 | Rampur | 40 | 09:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 287 | 16:00 | 140 | Rangamati | 18 | 12:00
9 | BSRM | 177 | 06:00 | 75 | Kachua | 79 | 21:00 | 141 | Rangpur | 141 | 21:00
10 | Bagerhat | 98 | 19:30 | 76 | Kallyanpur | 108 | 15:00 | 142 | Ruppur | 4.6 | 10:00
11 | Bakulia | 94 | 19:00 | 77 | Kalurghat | 34 | 10:00 | 143 | SSM | 13 | 08:00
12 | Banani | 50.6 | 15:00 | 78 | Kamrangirchar | 52 | 18:30 | 144 | Saidpur | 94 | 15:00
13 | Bangabhaban | 9 | 12:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 134 | 22:00
14 | Barapukuria | 65 | 19:30 | 80 | Kazla | 115 | 13:00 | 146 | Satmasjid | 106 | 14:00
15 | Barguna | 22 | 21:00 | 81 | Keranigonj | 85 | 21:00 | 147 | Savar | 197 | 19:00
16 | Barishal | 113 | 21:00 | 82 | Khagrachori | 30 | 19:00 | 148 | SevenRings | 5.42 | 23:00
17 | Barishal-230 | 94 | 22:00 | 83 | Khulna | 95 | 12:00 | 149 | ShahCement | 20 | 15:00
18 | Baroaulia | 63 | 09:00 | 84 | Khulshi | 187 | 23:00 | 150 | Shahjadpur | 68 | 20:00
19 | Baroirhat | 60 | 16:00 | 85 | Kishoreganj | 154 | 20:00 | 151 | Shahjibazar | 136 | 22:00
20 | Bashundhara | 171 | 14:00 | 86 | Kodda | 292 | 20:00 | 152 | Shahmirpur | 51 | 00:00
21 | BashundharaCement | 1 | 09:00 | 87 | Kulaura | 54 | 19:00 | 153 | Shariatpur | 90 | 22:00
22 | Beanibazar | 76 | 19:00 | 88 | Kurigram | 58 | 19:00 | 154 | Sherpur | 140 | 00:00
23 | Benapole | 72 | 00:00 | 89 | Kushtia | 150 | 19:30 | 155 | Shikalbaha | 28 | 14:00
24 | Bhaluka | 130 | 11:00 | 90 | Lalbag | 101 | 17:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 50 | 19:30 | 91 | Lalmonirhat | 60 | 19:30 | 157 | Shitalakhya | 84.3 | 16:00
26 | Bhangura | 36 | 21:00 | 92 | MI_Cement | 12.5 | 16:00 | 158 | Sholosohor | 45 | 15:00
27 | Bheramara(GK) | 63 | 21:00 | 93 | Madanganj | 29 | 23:00 | 159 | Shyampur | 144 | 12:00
28 | Bhulta | 254 | 10:00 | 94 | Madaripur | 121 | 22:00 | 160 | Siddhirganj | 128 | 15:00
29 | Bog-Sherpur | 62 | 20:00 | 95 | Madartek | 78.42 | 23:00 | 161 | Sirajganj | 104 | 19:30
30 | Bogura | 157 | 21:00 | 96 | Madunaghat | 54 | 19:30 | 162 | Sonargaon | 83 | 00:00
31 | Borhanuddin | 89 | 21:00 | 97 | Magura | 58 | 19:30 | 163 | Sreemongol | 81 | 21:00
32 | Brahmanbaria | 158 | 00:00 | 98 | Mahasthangarh | 73 | 23:00 | 164 | Sreepur | 98 | 17:00
33 | Cantonment | 106 | 19:00 | 99 | Manikganj | 121 | 19:30 | 165 | Srinagar | 45.4 | 21:00
34 | Chandpur | 73 | 20:00 | 100 | Maniknagar | 64 | 13:00 | 166 | Sunamganj | 56 | 20:00
35 | Chandraghona | 37 | 19:30 | 101 | Matarbari | 44 | 19:00 | 167 | Sylhet | 42 | 19:30
36 | Chapai | 66 | 22:00 | 102 | Matuail | 70 | 16:00 | 168 | Sylhet-132 | 122 | 19:00
37 | Charsaidpur | 28 | 08:00 | 103 | Millgate | 128 | 16:00 | 169 | TK | 32 | 22:00
38 | Chauddagram | 72 | 23:00 | 104 | Mirpur | 141 | 19:30 | 170 | Tangail | 186 | 21:00
39 | Chhatak | 36 | 22:00 | 105 | Mirsorai | 8 | 15:00 | 171 | Thakurgaon | 86 | 19:30
40 | Chowmuhani | 228 | 21:00 | 106 | Mirzapur | 34 | 19:30 | 172 | Tongi | 133 | 15:00
41 | Chuadanga | 113 | 00:00 | 107 | Mithapukur | 58 | 20:00 | 173 | Ullahpara | 25 | 20:00
42 | Coxsbazar | 125 | 21:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 54 | 20:00
43 | Cumilla(N) | 161 | 19:00 | 109 | Mogbazar | 121.7 | 16:00 | 175 | Uttara | 78 | 13:00
44 | Cumilla(S) | 183 | 22:00 | 110 | Mongla | 36 | 10:00 | 176 | UttaraNew | 50 | 23:00
45 | Daudkandi | 155 | 22:00 | 111 | Motijheel | 39 | 13:00 | 177 | Zigatola | 81 | 17:00
46 | Dhaka | 32 | 12:00 | 112 | Munshiganj | 114 | 23:00
47 | Dhamrai | 134 | 22:00 | 113 | Mymensingh | 232 | 22:00
48 | Dhanmondi | 112 | 13:00 | 114 | Naogaon | 131 | 20:00
49 | Dohazari | 94 | 20:00 | 115 | Narail | 56 | 19:30
50 | Faridpur | 158 | 21:00 | 116 | Narinda | 67 | 13:00
51 | Fatullah | 88 | 17:00 | 117 | Narshingdi | 171 | 19:00
52 | Fenchuganj | 42 | 19:00 | 118 | Natore | 138 | 21:00
53 | Feni | 114 | 19:30 | 119 | Nawabganj | 48.24 | 22:00
54 | GPH | 97 | 00:00 | 120 | Netrakona | 130 | 19:30
55 | Ghatail | 60 | 23:00 | 121 | New | 57.5 | 12:00
56 | Ghorashal | 60 | 15:00 | 122 | Niamatpur | 73 | 22:00
57 | Goalpara | 36 | 21:00 | 123 | Noapara | 48 | 19:30
58 | Gollamari | 74 | 00:00 | 124 | PHP | 10 | 09:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 385 | 18:30 | 366 | 09:00 | Kaliakoir | 381 | 04:00 | 368 | 10:00
| Ashuganj | 401 | 24:00 | 397 | 23:00 | Madunaghat_I | 408 | 6:00 | 401 | 22:00
| Bhulta | 400 | 02:00 | 386 | 11:00 | Meghnaghat | 379 | 18:30 | 366 | 09:00
| Bibiana | 399 | 17:00 | 391 | 12:00 | Payra | 408 | 18:00 | 400 | 12:00
| BIPTC | 404 | 18:00 | 395 | 00:00 | Rahanpur | 412 | 18:30 | 400 | 21:00
| Bogura | 407 | 18:30 | 396 | 21:00 | Rampal | 402 | 18:30 | 387 | 00:00
| Gopalganj | 396 | 18:30 | 382 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 227 | 02:00 | 217 | 11:00 | Hasnabad | 227 | 20:00 | 219 | 09:00
| AKSML | 234 | 18:30 | 226 | 14:00 | Hathazari | 238 | 18:00 | 231 | 11:00
| Aminbazar | 226 | 19:00 | 218 | 10:00 | Ishurdi | 237 | 18:30 | 229 | 00:00
| Ashuganj | 232 | 18:30 | 224 | 15:00 | Jhenaidah | 229 | 18:30 | 217 | 00:00
| Ashuganj-400 | 233 | 7:00 | 226 | 23:00 | Kaliakoir | 230 | 20:00 | 219 | 10:00
| Baghabari | 234 | 18:30 | 226 | 01:00 | Keranigonj | 227 | 02:00 | 217 | 11:00
| Barapukuria | 222 | 18:30 | 216 | 08:00 | Khulna(S) | 232 | 18:30 | 220 | 19:30
| Barapukuria-230 | 224 | 10:00 | 217 | 19:30 | Madunaghat_I | 237 | 18:00 | 228 | 23:00
| Barishal | 240 | 18:00 | 233 | 19:30 | Maniknagar | 229 | 03:00 | 220 | 11:00
| Bheramara | 235 | 18:30 | 227 | 00:00 | Meghnaghat | 236 | 02:00 | 230 | 09:00
| Bhulta | 231 | 04:00 | 222 | 10:00 | Meghnaghat-400 | 233 | 18:30 | 224 | 09:00
| Bibiana | 229 | 17:00 | 224 | 11:00 | Mirsorai | 236 | 19:00 | 224 | 00:00
| BIPTC | 237 | 18:30 | 227 | 00:00 | Rajshahi | 235 | 17:00 | 226 | 14:00
| Bogura | 230 | 18:30 | 223 | 02:00 | Rampal | 231 | 18:00 | 221 | 00:00
| Bogura-400 | 230 | 18:30 | 223 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 18:30 | 239 | 00:00 | Rampura | 228 | 04:00 | 219 | 11:00
| BSRM | 234 | 20:00 | 225 | 08:00 | Shikalbaha | 236 | 18:30 | 229 | 03:00
| Cumilla(N) | 229 | 18:30 | 220 | 14:00 | Shyampur | 229 | 04:00 | 219 | 11:00
| Fenchuganj | 231 | 00:00 | 229 | 01:00 | Siddhirganj | 230 | 18:00 | 222 | 10:00
| Ghorashal | 230 | 00:00 | 225 | 10:00 | Sirajgonj | 238 | 18:30 | 232 | 11:00
| Ghorashal-230 | 228 | 02:00 | 220 | 10:00 | Sreepur | 229 | 05:00 | 222 | 00:00
| GPH | 235 | 18:30 | 227 | 08:00 | Tongi | 228 | 19:00 | 215 | 09:00
| Haripur | 229 | 03:00 | 222 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 04:00 | 125 | 12:00 | Kushtia | 137 | 18:30 | 131 | 00:00
| Agargaon | 133 | 04:00 | 125 | 11:00 | Lalbag | 132 | 01:00 | 125 | 11:00
| Agrabad | 134 | 20:00 | 129 | 14:00 | Lalmonirhat | 127 | 18:30 | 120 | 06:00
| AKS | 132 | 18:00 | 127 | 14:00 | Madanganj | 132 | 18:30 | 125 | 10:00
| Aminbazar | 135 | 00:00 | 127 | 09:00 | Madaripur | 131 | 18:30 | 126 | 00:00
| Amnura | 138 | 18:30 | 127 | 22:00 | Madartek | 134 | 02:00 | 125 | 14:00
| Ashuganj | 135 | 00:00 | 133 | 11:00 | Madunaghat | 134 | 18:00 | 130 | 16:00
| Bagerhat | 138 | 16:00 | 125 | 19:30 | Magura | 137 | 18:30 | 128 | 19:30
| Bakulia | 133 | 18:30 | 129 | 14:00 | Mahasthangarh | 133 | 18:30 | 126 | 00:00
| Banani | 134 | 02:00 | 124 | 15:00 | Manikganj | 130 | 04:00 | 121 | 09:00
| Bangabhaban | 130 | 02:00 | 123 | 11:00 | Maniknagar | 130 | 02:00 | 123 | 11:00
| Barapukuria | 133 | 17:00 | 128 | 04:00 | Matarbari | 123 | 12:00 | 117 | 19:00
| Barguna | 134 | 18:30 | 129 | 00:00 | Matuail | 131 | 18:00 | 125 | 10:00
| Barishal | 134 | 21:00 | 129 | 16:00 | Millgate | 133 | 02:00 | 124 | 10:00
| Barishal-230 | 136 | 18:30 | 131 | 00:00 | Mirpur | 135 | 02:00 | 126 | 10:00
| Baroaulia | 134 | 18:30 | 129 | 14:00 | Mirzapur | 130 | 18:30 | 121 | 19:30
| Baroirhat | 130 | 18:30 | 121 | 01:00 | Mithapukur | 130 | 18:30 | 124 | 07:00
| Bashundhara | 136 | 11:00 | 124 | 11:00 | MI_Cement | 133 | 18:30 | 125 | 11:00
| BashundharaCement | 132 | 18:30 | 125 | 10:00 | Modern | 134 | 18:30 | 130 | 00:00
| Beanibazar | 125 | 07:00 | 119 | 23:00 | Mogbazar | 136 | 05:00 | 126 | 12:00
| Benapole | 134 | 15:00 | 126 | 00:00 | Mongla | 136 | 16:00 | 125 | 19:30
| Bhaluka | 126 | 07:00 | 120 | 11:00 | Motijheel | 131 | 04:00 | 123 | 11:00
| Bhandaria | 132 | 18:30 | 125 | 00:00 | Munshiganj | 132 | 18:00 | 125 | 09:00
| Bhangura | 136 | 17:00 | 132 | 00:00 | Mymensingh | 134 | 16:00 | 115 | 22:00
| Bheramara | 136 | 18:00 | 132 | 00:00 | Naogaon | 131 | 18:30 | 123 | 13:00
| Bheramara(GK) | 137 | 18:30 | 132 | 00:00 | Narail | 136 | 17:00 | 127 | 19:30
| Bhulta | 123 | 18:00 | 117 | 10:00 | Narinda | 130 | 02:00 | 123 | 11:00
| Bog-Sherpur | 134 | 18:30 | 127 | 00:00 | Narshingdi | 128 | 16:00 | 114 | 11:00
| Bogura | 134 | 18:00 | 128 | 12:00 | Natore | 135 | 18:30 | 129 | 00:00
| Bogura-230 | 135 | 18:30 | 128 | 02:00 | Nawabganj | 132 | 03:00 | 125 | 11:00
| Brahmanbaria | 125 | 18:30 | 119 | 00:00 | Netrakona | 132 | 17:00 | 118 | 19:00
| Cantonment | 132 | 02:00 | 125 | 11:00 | New | 133 | 00:00 | 125 | 11:00
| Chandpur | 128 | 18:00 | 115 | 23:00 | Niamatpur | 138 | 17:00 | 133 | 22:00
| Chandraghona | 136 | 18:30 | 132 | 04:00 | Noapara | 137 | 18:00 | 128 | 01:00
| Chapai | 136 | 18:00 | 130 | 21:00 | Pabna | 135 | 17:00 | 130 | 00:00
| Charsaidpur | 133 | 18:30 | 126 | 09:00 | Palashbari | 128 | 17:00 | 121 | 21:00
| Chauddagram | 127 | 17:00 | 120 | 15:00 | Panchagarh | 132 | 18:30 | 116 | 08:00
| Chhatak | 127 | 03:00 | 121 | 22:00 | Patuakhali | 132 | 18:00 | 128 | 12:00
| Chowmuhani | 126 | 18:30 | 112 | 23:00 | Payra | 135 | 18:30 | 131 | 00:00
| Chuadanga | 135 | 18:30 | 121 | 00:00 | PHP | 131 | 18:30 | 119 | 23:00
| Coxsbazar | 123 | 07:00 | 117 | 19:00 | Postogola | 134 | 18:30 | 128 | 10:00
| Cumilla(N) | 132 | 18:00 | 125 | 14:00 | Purbachal | 134 | 01:00 | 124 | 10:00
| Cumilla(S) | 131 | 00:00 | 124 | 12:00 | Purbasadipur | 130 | 18:30 | 118 | 07:00
| Daudkandi | 130 | 18:30 | 120 | 22:00 | Rahanpur | 139 | 18:00 | 135 | 13:00
| Dhaka | 135 | 03:00 | 127 | 11:00 | Rahim | 131 | 19:00 | 126 | 09:00
| Dhamrai | 130 | 03:00 | 123 | 09:00 | Rajbari | 133 | 18:30 | 126 | 00:00
| Dhanmondi | 135 | 03:00 | 127 | 11:00 | Rajendrapur | 131 | 21:00 | 121 | 11:00
| Dohazari | 130 | 20:00 | 126 | 14:00 | Rajshahi | 135 | 18:00 | 129 | 00:00
| Faridpur | 135 | 15:00 | 127 | 00:00 | Rajshahi-230 | 136 | 18:30 | 124 | 22:00
| Fatullah | 133 | 03:00 | 126 | 11:00 | Ramganj | 126 | 18:30 | 110 | 23:00
| Fenchuganj | 130 | 06:00 | 128 | 01:00 | Rampur | 134 | 18:30 | 129 | 11:00
| Feni | 128 | 18:30 | 119 | 23:00 | Rampura | 133 | 04:00 | 126 | 10:00
| Ghatail | 130 | 16:00 | 115 | 19:30 | Rangamati | 133 | 02:00 | 130 | 15:00
| Ghorashal | 135 | 04:00 | 130 | 11:00 | Rangpur | 130 | 18:30 | 119 | 08:00
| Goalpara | 140 | 18:00 | 129 | 05:00 | Ruppur | 138 | 17:00 | 132 | 00:00
| Gollamari | 138 | 18:30 | 130 | 07:00 | Saidpur | 130 | 01:00 | 120 | 08:00
| Gopalganj | 133 | 18:00 | 127 | 00:00 | Satkhira | 134 | 18:00 | 124 | 00:00
| Gopalganj-400 | 132 | 18:00 | 127 | 12:00 | Satmasjid | 137 | 16:00 | 125 | 11:00
| Gulshan | 134 | 06:00 | 126 | 11:00 | Savar | 135 | 22:00 | 125 | 10:00
| Halishahar | 135 | 20:00 | 129 | 14:00 | SevenRings | 135 | 03:00 | 130 | 10:00
| Haripur | 131 | 19:00 | 126 | 09:00 | ShahCement | 133 | 18:30 | 126 | 09:00
| HaripurSBU | 131 | 19:00 | 126 | 09:00 | Shahjadpur | 140 | 17:00 | 136 | 00:00
| Hasnabad | 134 | 18:30 | 129 | 08:00 | Shahjibazar | 124 | 18:00 | 119 | 00:00
| Hathazari | 137 | 18:00 | 133 | 11:00 | Shahmirpur | 135 | 20:00 | 130 | 00:00
| Ishurdi | 139 | 18:30 | 134 | 00:00 | Shariatpur | 130 | 18:00 | 124 | 00:00
| Jaldhaka | 130 | 18:30 | 120 | 05:00 | Sherpur | 135 | 17:00 | 120 | 19:30
| Jamalpur | 137 | 16:00 | 122 | 19:30 | Shikalbaha | 123 | 18:00 | 118 | 11:00
| Jashore | 135 | 18:00 | 127 | 01:00 | Shikalbaha-230 | 135 | 19:30 | 130 | 02:00
| Jhenaidah | 139 | 18:00 | 131 | 00:00 | Shitalakhya | 133 | 18:30 | 125 | 11:00
| Jhenaidah-230 | 140 | 18:30 | 131 | 00:00 | Sholosohor | 134 | 20:00 | 130 | 08:00
| Joydebpur | 132 | 00:00 | 124 | 15:00 | Shyampur | 132 | 18:30 | 126 | 10:00
| Joypurhat | 131 | 18:30 | 122 | 13:00 | Shyampur-230 | 133 | 18:30 | 125 | 11:00
| Juldah | 134 | 18:30 | 131 | 11:00 | Siddhirganj | 132 | 18:30 | 126 | 10:00
| Kabirpur | 133 | 03:00 | 121 | 10:00 | Sirajganj | 134 | 18:30 | 128 | 00:00
| Kachua | 133 | 21:00 | 119 | 14:00 | Sonargaon | 128 | 03:00 | 122 | 11:00
| Kaliakoir | 133 | 18:00 | 126 | 15:00 | Sreemongol | 125 | 06:00 | 121 | 00:00
| Kallyanpur | 130 | 06:00 | 124 | 11:00 | Sreepur | 129 | 05:00 | 124 | 00:00
| Kalurghat | 134 | 20:00 | 130 | 11:00 | Srinagar | 132 | 02:00 | 126 | 10:00
| Kamrangirchar | 132 | 02:00 | 19 | 18:30 | SSM | 136 | 00:00 | 133 | 08:00
| Kaptai | 137 | 18:00 | 134 | 1:00 | Sunamganj | 126 | 05:00 | 120 | 19:00
| Kazla | 131 | 06:00 | 123 | 11:00 | Sylhet | 127 | 02:00 | 124 | 23:00
| Keranigonj | 133 | 04:00 | 126 | 11:00 | Sylhet-132 | 128 | 09:00 | 125 | 23:00
| Khagrachori | 134 | 18:30 | 130 | 14:00 | Tangail | 128 | 16:00 | 116 | 19:30
| Khulna | 137 | 18:00 | 129 | 19:30 | Thakurgaon | 134 | 18:30 | 116 | 05:00
| Khulna(S) | 138 | 18:00 | 130 | 19:30 | TK | 135 | 20:00 | 0.01 | 04:00
| Khulshi | 133 | 18:30 | 128 | 15:00 | Tongi | 134 | 04:00 | 126 | 09:00
| Kishoreganj | 128 | 04:00 | 121 | 23:00 | Ullahpara | 136 | 17:00 | 132 | 00:00
| Kodda | 132 | 19:30 | 122 | 10:00 | Ullon | 134 | 02:00 | 126 | 11:00
| KSRM | 136 | 20:00 | 130 | 11:00 | Uttara | 134 | 03:00 | 120 | 09:00
| Kulaura | 129 | 06:00 | 127 | 00:00 | UttaraNew | 134 | 01:00 | 125 | 10:00
| Kurigram | 127 | 18:30 | 118 | 05:00 | Zigatola | 132 | 03:00 | 126 | 11:00

## L-Curve
Date | 2024-07-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 690 | 8230 | 6111 | 14341 |  |  |  | QF-LDC-11
0:30 | 671 | 7684.5 | 5809 | 13493.5 | Date: | 2024-07-06
1:00 | 652 | 7139 | 5507 | 12646
1:30 | 611 | 7103.5 | 5421.5 | 12525
2:00 | 570 | 7068 | 5336 | 12404
2:30 | 551 | 7014 | 5177.5 | 12191.5 | [5 empty] | Gen. at Eve. Peak | 14521 | 14521 MW (21:00 )
3:00 | 532 | 6960 | 5019 | 11979 | [6 empty] | 21:00
3:30 | 568 | 6864 | 4956 | 11820 | [5 empty] | Gen. at Day Peak | 12608 | 12608 MW (12:00 )
4:00 | 604 | 6768 | 4893 | 11661 | [6 empty] | 12:00
4:30 | 575 | 6664 | 4801.5 | 11465.5 | [5 empty] | Highest Generation | 14551
5:00 | 546 | 6560 | 4710 | 11270 | [6 empty] | 22:00
5:30 | 585 | 6478 | 4638.5 | 11116.5
6:00 | 624 | 6396 | 4567 | 10963
6:30 | 622 | 6403.5 | 4567 | 10970.5
7:00 | 620 | 6411 | 4567 | 10978
7:30 | 685 | 6461 | 4620.5 | 11081.5
8:00 | 750 | 6511 | 4674 | 11185
8:30 | 818 | 6591.5 | 4868.5 | 11460
9:00 | 886 | 6672 | 5063 | 11735
9:30 | 931 | 6738.5 | 5102.5 | 11841
10:00 | 976 | 6805 | 5142 | 11947
10:30 | 986 | 6793 | 5216 | 12009
11:00 | 996 | 6781 | 5290 | 12071
11:30 | 911 | 7019 | 5320.5 | 12339.5
12:00 | 826 | 7257 | 5351 | 12608
12:30 | 797 | 7273.5 | 5227.5 | 12501
13:00 | 768 | 7290 | 5104 | 12394
13:30 | 841 | 7369.5 | 5216.5 | 12586
14:00 | 914 | 7449 | 5329 | 12778
14:30 | 961 | 7514 | 5352.5 | 12866.5
15:00 | 1008 | 7579 | 5376 | 12955
15:30 | 1005 | 7529 | 5358 | 12887
16:00 | 1002 | 7479 | 5340 | 12819
16:30 | 916 | 7529.5 | 5083.5 | 12613
17:00 | 830 | 7580 | 4827 | 12407
17:30 | 791 | 7466.5 | 4737.5 | 12204
18:00 | 752 | 7353 | 4648 | 12001
18:30 | 694 | 7792.5 | 4873.5 | 12666
19:00 | 636 | 8232 | 5099 | 13331
19:30 | 480 | 8732 | 5788 | 14520
20:00 | 412 | 8701 | 5799 | 14500 |  |  |  | Executive Engineer
20:30 | 435 | 8663.5 | 5847 | 14510.5 |  |  |  | Network Operation Division
21:00 | 458 | 8626 | 5895 | 14521
21:30 | 475 | 8643 | 5893 | 14536
22:00 | 492 | 8660 | 5891 | 14551 |  |  |  |  | Page 6 of 7
22:30 | 545 | 8514.5 | 5922 | 14436.5
23:00 | 598 | 8369 | 5953 | 14322
23:30 | 644 | 8299.5 | 6032 | 14331.5
24:00 | 690 | 8230 | 6111 | 14341
14521 MW (21:00 )
12608 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-06 |  | Energy |  | 306164855
[14 empty] | Date: | 2024-07-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3792 | 923 | 1804 | 0 | 3001 | 4046 | 166 | 0 | 512 | 90 | 0 | 7 | 219
0:30 | 3809.5 | 920 | 1769.5 | 0 | 2348.5 | 4030 | 165.5 | 0 | 352.5 | 80 | 0 | 18 | 135.5 |  |  | Date: | 44017
1:00 | 3827 | 917 | 1735 | 0 | 1696 | 4014 | 165 | 0 | 193 | 70 | 0 | 29 | 52
1:30 | 3797 | 916.5 | 1710 | 0 | 1683.5 | 4010 | 165 | 0 | 151.5 | 69 | 0 | 22.5 | 48 | [9 empty] | Total Energy | 306.1649 | 306.1649 | Total Energy Gen 306.165 MKWHr Energy Not Served 2.061 MKWHr Energy Requirement 308.226 MKWHr
2:00 | 3767 | 916 | 1685 | 0 | 1671 | 4006 | 165 | 0 | 110 | 68 | 0 | 16 | 44 | [9 empty] | Energy not Served | 2.0607 | 2.0607
2:30 | 3768.5 | 915.5 | 1679.5 | 0 | 1552.5 | 3935 | 165 | 0 | 95 | 68 | 0 | 12.5 | 41.5 | [9 empty] | Energy Requirement | 308.2255 | 308.2255
3:00 | 3770 | 915 | 1674 | 0 | 1434 | 3864 | 165 | 0 | 80 | 68 | 0 | 9 | 39
3:30 | 3768 | 914.5 | 1669.5 | 0 | 1347 | 3818 | 165 | 0 | 60 | 67 | 0 | 11 | 19.5 | [8 empty] | Shortage
4:00 | 3766 | 914 | 1665 | 0 | 1260 | 3772 | 165 | 0 | 40 | 66 | 0 | 13 | 0
4:30 | 3768.5 | 914 | 1692.5 | 0 | 1066.5 | 3746 | 165 | 0 | 32 | 65 | 0 | 16 | 0
5:00 | 3771 | 914 | 1720 | 0 | 873 | 3720 | 165 | 0 | 24 | 64 | 0 | 19 | 0
5:30 | 3816.5 | 914 | 1725 | 0 | 730.5 | 3648 | 165.5 | 0 | 24 | 62 | 8 | 23 | 0
6:00 | 3862 | 914 | 1730 | 0 | 588 | 3576 | 166 | 0 | 24 | 60 | 16 | 27 | 0
6:30 | 3839.5 | 917 | 1742.5 | 0 | 607.5 | 3569.5 | 166 | 0 | 24 | 58 | 27 | 19.5 | 0 | [7 empty] | Coal
7:00 | 3817 | 920 | 1755 | 0 | 627 | 3563 | 166 | 0 | 24 | 56 | 38 | 12 | 0
7:30 | 3823.5 | 919.5 | 1762 | 0 | 628.5 | 3597.5 | 166 | 0 | 24 | 61 | 83 | 16.5 | 0 | [6 empty] | Oil
8:00 | 3830 | 919 | 1769 | 0 | 630 | 3632 | 166 | 0 | 24 | 66 | 128 | 21 | 0
8:30 | 3858.5 | 919 | 1774.5 | 0 | 762 | 3699 | 166 | 0 | 24 | 68 | 178.5 | 10.5 | 19
9:00 | 3887 | 919 | 1780 | 0 | 894 | 3766 | 166 | 0 | 24 | 70 | 229 | 0 | 38
9:30 | 3886 | 919.5 | 1776.5 | 0 | 942.5 | 3766.5 | 166 | 0 | 20 | 73 | 284 | 7 | 58.5
10:00 | 3885 | 920 | 1773 | 0 | 991 | 3767 | 166 | 0 | 16 | 76 | 339 | 14 | 79
10:30 | 3852.5 | 920 | 1736 | 0 | 1017 | 3826 | 166 | 0 | 25 | 79 | 365.5 | 22 | 96.5
11:00 | 3820 | 920 | 1699 | 0 | 1043 | 3885 | 166 | 0 | 34 | 82 | 392 | 30 | 114
11:30 | 3827 | 919.5 | 1698.5 | 0 | 1248.5 | 3916 | 166 | 0 | 64 | 82 | 400 | 18 | 125
12:00 | 3834 | 919 | 1698 | 0 | 1454 | 3947 | 166 | 0 | 94 | 82 | 408 | 6 | 136
12:30 | 3752.5 | 919.5 | 1601 | 0 | 1597.5 | 3895.5 | 164 | 0 | 117 | 81 | 367 | 6 | 126.255
13:00 | 3671 | 920 | 1504 | 0 | 1741 | 3844 | 162 | 0 | 140 | 80 | 326 | 6 | 116.51
13:30 | 3671 | 920 | 1504 | 0 | 1741 | 3844 | 162 | 0 | 140 | 80 | 326 | 6 | 116.51
14:00 | 3671 | 920 | 1504 | 0 | 1741 | 3844 | 162 | 0 | 140 | 80 | 326 | 6 | 116.51
14:30 | 3743.5 | 920 | 1646.5 | 0 | 1839 | 3876.5 | 164 | 0 | 124.5 | 86 | 268.5 | 6 | 137.0425
15:00 | 3816 | 920 | 1789 | 0 | 1937 | 3909 | 166 | 0 | 109 | 92 | 211 | 6 | 157.575
15:30 | 3810.5 | 920 | 1747.5 | 0 | 1929.5 | 3911.5 | 166 | 0 | 108.5 | 89 | 198.5 | 6 | 150.89
16:00 | 3805 | 920 | 1706 | 0 | 1922 | 3914 | 166 | 0 | 108 | 86 | 186 | 6 | 144.205
16:30 | 3796.5 | 920 | 1666.5 | 0 | 1965 | 3752 | 166 | 0 | 123 | 80 | 134.5 | 9.5 | 135.61
17:00 | 3788 | 920 | 1627 | 0 | 2008 | 3590 | 166 | 0 | 138 | 74 | 83 | 13 | 127.015
17:30 | 3737 | 921 | 1610 | 0 | 1999 | 3491.5 | 166 | 0 | 141 | 75 | 55 | 8.5 | 111.0075
18:00 | 3686 | 922 | 1593 | 0 | 1990 | 3393 | 166 | 0 | 144 | 76 | 27 | 4 | 95
18:30 | 3736.5 | 922.5 | 1628 | 0 | 2291.5 | 3446.5 | 166 | 0 | 377 | 81 | 13.5 | 3.5 | 104.5
19:00 | 3787 | 923 | 1663 | 0 | 2593 | 3500 | 166 | 0 | 610 | 86 | 0 | 3 | 114
19:30 | 3969 | 921 | 1692 | 0 | 3059 | 3903 | 166 | 0 | 717 | 86 | 0 | 7 | 128.5
20:00 | 3906 | 921 | 1639 | 0 | 3105 | 3923 | 166 | 0 | 747 | 84 | 0 | 9 | 143
20:30 | 3913 | 921.5 | 1692 | 0 | 3095.5 | 3939.5 | 166 | 0 | 691.5 | 83 | 0 | 8.5 | 119
21:00 | 3920 | 922 | 1745 | 0 | 3086 | 3956 | 166 | 0 | 636 | 82 | 0 | 8 | 95
21:30 | 3938.5 | 921.5 | 1754 | 0 | 3082 | 3952.5 | 166 | 0 | 629 | 86 | 0 | 6.5 | 99.5475
22:00 | 3957 | 921 | 1763 | 0 | 3078 | 3949 | 166 | 0 | 622 | 90 | 0 | 5 | 104.095
22:30 | 3887.5 | 921.5 | 1760.5 | 0 | 3035 | 3964 | 166 | 0 | 608.5 | 91 | 0 | 2.5 | 103.6175
23:00 | 3818 | 922 | 1758 | 0 | 2992 | 3979 | 166 | 0 | 595 | 92 | 0 | 0 | 103.14
23:30 | 3805 | 922.5 | 1781 | 0 | 2996.5 | 4012.5 | 166 | 0 | 553.5 | 91 | 0 | 3.5 | 161.07 |  |  | Max Temp. in Dhaka |  | 33.7°C
24:00 | 3792 | 923 | 1804 | 0 | 3001 | 4046 | 166 | 0 | 512 | 90 | 0 | 7 | 219
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 306.165 MKWHr Energy Not Served 2.061 MKWHr Energy Requirement 308.226 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 2098920
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 76 | 76 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1924000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 64371
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 13 | 13 | 6 | 20 | 17 | 19 | 17 | 14 |  | 4 | 1 | [8 empty] | 117720
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 223 | 223 | 223 | 223 | 222 | 222 | 222 | 223 | 221 | 219 | 220 | 216 | 216 | 216 | 214 | 203 | 219 |  | 219 | 221 | 221 | 221 | 221 | 222 | 222 | 5255741
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 33 | 71 | 85 | 85 | 85 | 85 | 85 | 429820
12 | Hathazari 100 MW peaking PP | 56 | 56 | 56 | 16 | 0 | [5 empty] | 1 | 24 | 40 | 40 | 40 | 40 | 61 | 61 |  | 78 | 78 | 78 | 78 | 78 | 71 | 69 | 907776
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 12 | 44 | 51 | 61 | 85 | 85 | 85 |  | 90 | 105 | 105 | 68 | 68 | 68 | 68 | 950945
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [12 empty] | 30 | 36 | 36 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 38 | 38 | 413088
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 329 | 323 | 330 | 330 | 328 | 327 | 324 | 323 | 326 | 326 | 289 | 317 | 280 | 280 | 314 | 312 | 318 | 317 |  | 317 | 318 | 260 | 322 | 324 | 280 | 280 | 7595649
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 95 | 95 | 30 | 0 |  |  |  | 5 | 15 | 15 | 138 | 195 | 195 | 195 | 195 | 195 | 195 |  | 200 | 295 | 280 | 300 | 300 | 293 | 281 | 3369709
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 612 | 612 | 612 | 610 | 610 | 612 | 610 | 609 | 604 | 606 | 540 |  | 580 | 605 | 606 | 606 | 604 | 575 | 600 | 14078180
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 30 | 30 | 30 | 30 | 30 | 30 | 545832
33 | Ashuganj 225 MW CCPP | 216 | 219 | 217 | 217 | 216 | 209 | 199 | 192 | 197 | 198 | 208 | 213 | 208 | 209 | 211 | 214 | 213 | 212 |  | 211 | 215 | 216 | 215 | 216 | 213 | 216 | 5123000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 250 | 250 | 250 | 250 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5955000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7208400
| Ashuganj 420 MW CCPP(East) | 260 | 230 | 230 | 230 | 230 | 300 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 280 | 280 | 280 | 280 | 250 | 250 | 6010800
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 7 | 10 | 15 | 20 | 20 | 20 | 20 | 197760
36 | Chandpur 150 MW CCPP | 52 | 50 | 51 | 51 | 50 | 70 | 70 | 48 | 50 | 51 | 50 | 45 | 42 | 43 | 42 | 40 | 40 | 40 |  | 42 | 42 | 40 | 42 | 42 | 40 | 41 | 1099720
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 410 | 402 | 401 | 402 | 402 | 404 | 404 | 404 | 404 | 405 | 403 | 404 | 361 | 400 | 401 | 401 | 406 | 360 |  | 401 | 414 | 406 | 410 | 409 | 408 | 407 | 9748800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 410 | 420 | 430 | 420 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 380 | 380 | 420 | 410 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 420 | 9602000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 22 | 22 | 23 | 23 | 23 | 24 | 23 | 23 | 22 | 18 | 10 | 10 | 10 | 10 | 11 | 12 | 12 | 12 |  | 17 | 18 | 18 | 17 | 17 | 18 | 18 | 403200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 6 | 13 | 13 | 37 | 36 | 53 | 13 | 4 | 18 | 10 | 3 | 0 | [8 empty] | 205410
44 | Fenchugonj CCPP Phase-1 | 26 | 26 | 25 | 25 | 26 | 26 | 27 | 27 | 26 | 26 | 26 | 26 | 27 | 28 | 25 | 25 | 25 | 25 |  | 28 | 25 | 25 | 25 | 26 | 27 | 26 | 623000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 54 | 54 | 54 | 56 | 56 | 58 | 58 | 54 | 54 | 54 | 54 |  | 58 | 56 | 56 | 56 | 56 | 58 | 54 | 1314960
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 56 | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 50 | 54 | 55 | 40 | 40 | 49 | 55 | 56 | 57 |  | 52 | 51 | 56 | 55 | 53 | 52 | 53 | 1262112
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 211 | 211 | 212 | 211 | 212 | 212 | 213 | 212 | 212 | 213 | 212 | 212 | 213 | 211 | 211 | 211 | 211 | 211 |  | 212 | 212 | 210 | 210 | 211 | 212 | 211 | 5265070
51 | Sylhet 20 MW GTPP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 15 | 15 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 328000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120960
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1252800
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 284256
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 275 | 285 | 290 | 305 | 310 | 310 | 295 | 280 | 290 | 280 | 300 | 315 | 300 | 290 | 270 | 290 |  | 290 | 265 | 285 | 270 | 285 | 300 | 300 | 7141500
| Bibiyana South 400 MW | 345 | 345 | 345 | 345 | 345 | 345 | 375 | 375 | 345 | 345 | 345 | 345 | 370 | 370 | 340 | 340 | 340 | 310 |  | 375 | 385 | 386 | 386 | 390 | 330 | 320 | 8409900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 0 |  |  |  | 5 | 17 | 35 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  |  | 794234
59 | Tangail Palli Power Gen 22 MW | 4 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 1 | 1 | 6 | 4 | 6 | 6 |  | 4 | 3 | 2 | 6 | 1 |  | 2 | 111120
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 70 | 68 | 68 | 66 | 64 | 60 | 56 | 66 | 70 | 76 | 82 | 82 | 80 | 90 | 92 | 86 | 74 | 76 |  | 86 | 86 | 84 | 82 | 90 | 92 | 90 | 1838400
64 | Malancha, Ctg. EPZ (United) | 24 | 42 | 42 | 42 | 42 | 42 | 38 | 9 | 7 | 6 | 5 | 10 | 11 | 11 | 6 | 3 | 10 | 5 |  | 10 | 12 | 15 | 23 | 27 | 37 | 38 | 554880
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 11 | 11 | 0 | 11 |  | 11 | 11 | 17 | 0 | 17 | 17 | 17 | 271760
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 15 | 16 | 16 | 16 | 16 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 391200
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 342360
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 |  | 24 | 24 | 22 | 17 | 17 | 17 | 17 | 412200
72 | Rupganj 33 MW PP(Summit) | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 2 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 274900
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 98 | 98 | 98 | 98 | 98 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 98 | 88 | 88 | 88 |  | 88 | 70 | 70 | 70 | 70 | 70 | 70 | 1941420
| Chowmuhani 113 MW | 48 | 47 | 47 | 46 | 47 | 47 | 46 | 47 | 47 | 47 | 48 | 47 | 45 | 45 | 45 | 44 | 55 | 81 |  | 81 | 81 | 81 | 84 | 91 | 89 | 84 | 1397760
| Manikgonj 162MW PP(MPGL) | [10 empty] | 17 | 72 | 72 | 72 | 162 | 162 | 162 | 108 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 1693440
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 40 | 40 | 11 | 0 | [5 empty] | 3 | 32 | 56 | 68 | 80 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1032960
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 142560
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 147 | 148 | 150 | 150 | 149 | 132 | 82 | 1081920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 48 | 52 | 52 | 25 | 0 | [5 empty] | 16 | 16 | 16 | 24 | 48 | 48 | 42 |  | 50 | 42 | 42 | 44 | 50 | 51 | 51 | 719573
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 |  | 17 | 52 | 52 | 52 | 52 | 35 | 17 | 646080
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 5 | 6 | 5 | 2 | 5 | 4 | 2 | 1 | 0 | 0 | [8 empty] | 27480
| Jodiac Power | [14 empty] | 6 | 17 | 17 | 17 |  | 18 | 54 | 51 | 17 | 17 | 17 | 17 | 227073
| Karnaphuli Power Ltd. | [11 empty] | 7 | 17 | 17 | 17 | 17 | 23 | 51 |  | 51 | 58 | 63 | 51 | 51 | 17 | 17 | 459161
82 | Madanganj 102 PP(Summit) | 68 | 68 | 68 | 34 | 17 | 0 |  |  |  |  | 2 | 45 | 68 | 68 | 68 | 51 | 51 | 68 |  | 68 | 68 | 68 | 82 | 82 | 82 | 82 | 1037567
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 92000
86 | Meghnaghat CCPP ( Summit) | 151 | 148 | 147 | 138 | 149 | 156 | 152 | 152 | 141 | 145 | 147 | 146 | 148 | 148 | 149 | 127 | 137 | 147 |  | 150 | 130 | 132 | 141 | 140 | 148 | 133 | 3457193
87 | Meghnaghat 100 MW(IEL) | 8 | 9 | 8 | 8 | 0 | [5 empty] | 2 | 9 | 13 | 9 | 9 | 24 | 33 | 38 |  | 43 | 61 | 57 | 66 | 67 | 66 | 66 | 532800
| Meghnaghat 104 MW PP (OPCL) | 0 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 47 | 52 | 52 | 52 | 52 | 53 | 53 | 53 | 53 |  | 53 | 53 | 56 | 71 | 71 | 71 | 71 | 987840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [14 empty] | 12 | 12 | 12 | 12 |  | 30 | 45 | 58 |  |  |  |  | 122640
92 | Fenchuganj 44 MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 300600
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 964940
94 | Gagnagar 102 MW PP (Digital Power) | 40 | 40 | 16 | 8 | 0 | [5 empty] | 8 | 50 | 81 | 81 | 81 | 90 | 90 | 90 |  | 90 | 85 | 82 | 82 | 90 | 73 | 74 | 1148976
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 32 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 478080
96 | Chattogram 108 MW PP (ECPV) | 30 | 25 | 25 | 25 | 0 | [5 empty] | 0 | 8 | 24 | 26 | 32 | 10 | 27 | 35 |  | 38 | 38 | 38 | 37 | 38 | 38 | 38 | 505920
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 0 |  |  | 15 | 30 | 30 | 15 | 15 | 30 | 30 | 30 | 30 | 30 |  | 45 | 55 | 55 | 55 | 25 | 25 | 25 | 678264
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 35 | 35 | 0 |  |  |  | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 799346
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 163 | 120 | 163 | 163 | 163 | 163 | 120 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3564164
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 |  | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 8350
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 15 | 35 | 35 | 35 | 35 |  |  |  | 6 | 54 | 49 | 54 | 54 | 54 | 54 | 452160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 |  | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 2978400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 123 | 126 | 114 | 114 | 114 | 78 | 78 | 78 | 78 | 79 | 80 | 96 | 98 | 108 | 107 | 123 | 123 | 125 |  | 128 | 128 | 124 | 128 | 132 | 132 | 132 | 2655216
115 | Juldah 100 MW PP Unit-3 (Acorn) | 72 | 59 | 50 | 50 | 50 | 24 | 24 | 24 | 74 | 74 | 74 | 60 | 60 | 60 | 60 | 25 | 60 | 12 |  | 30 | 60 | 60 | 60 | 60 | 60 | 47 | 1197120
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 428640
117 | Ashuganj 150 MW PP (Midland) | [11 empty] | 8 | 24 | 24 | 24 | 24 | 24 | 24 |  | 40 | 85 | 82 | 122 | 130 | 137 | 137 | 829672
118 | Bibiyana-III 400 MW CCPP | 401 | 400 | 400 | 401 | 402 | 402 | 402 | 402 | 402 | 402 | 404 | 403 | 400 | 404 | 403 | 402 | 403 | 402 |  | 404 | 404 | 402 | 402 | 402 | 403 | 402 | 9646000
| Jamalpur 115 MW PP (United) | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 65 | 65 | 65 | 65 | 65 | 67 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1700400
| Anwara 300 MW PP (United) | 68 | 51 | 51 | 51 | 51 | 15 | 15 | 15 | 49 | 49 | 57 | 49 | 52 | 52 | 51 | 50 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1154182
| Juldah unit-2 (Acorn) | 75 | 75 | 75 | 75 | 75 | 24 | 24 | 24 | 74 | 74 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 12 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1309440
| Anlima Energy Ltd. | 35 | 35 | 18 | 17 | 17 | 0 |  |  | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 35 | 35 |  | 52 | 53 | 53 | 70 | 72 | 72 | 72 | 738927
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 20 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 36 | 36 | 36 | 36 | 36 | 36 | 622800
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 3 | 5 | 15 | 19 | 28 | 31 | 35 | 1 | 2 | 1 | 3 | 5 | 1 | [8 empty] | 146728
| Chandpur 115(Doreen) | 45 | 37 | 36 | 35 | 36 | 35 | 36 | 34 | 35 | 35 | 33 | 33 | 33 | 32 | 34 | 47 | 47 | 65 |  | 87 | 105 | 104 | 115 | 105 | 75 | 68 | 1252800
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 4 | 17 | 17 | 17 | 17 | [6 empty] | 12 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 320040
| Mirsharai 150 MW (Oil) | [10 empty] | 17 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 | 35 | 35 | 35 | 17 | 667418
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 29 | 16 | 9 | 13 | 19 | 27 | 12 | 21 | 0 | 14 | 30 | 6 | 6 | 5 | 6 | 6 | 13 | 4 |  | 3 | 7 | 9 | 8 | 5 | 0 | 7 | 284160
| Sonagazi 75 MW Solar Plant |  |  |  |  | 0 | 3 | 4 | 19 | 53 | 68 | 50 | 44 | 75 | 60 | 40 | 34 | 21 | 3 | [8 empty] | 472127
| Matarbari 2*600 MW (CPGCL) | 518 | 516 | 516 | 515 | 517 | 517 | 518 | 516 | 519 | 516 | 517 | 520 | 520 | 520 | 518 | 520 | 520 | 473 |  | 495 | 515 | 516 | 520 | 519 | 518 | 516 | 12392727
120 | Eastern Zone Total | 7139 | 7068 | 6960 | 6768 | 6560 | 6396 | 6411 | 6511 | 6672 | 6805 | 6781 | 7257 | 7290 | 7449 | 7579 | 7479 | 7580 | 7353 |  | 8232 | 8732 | 8701 | 8626 | 8660 | 8369 | 8230 | 177596517
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 96 | 96 | 97 | 97 | 0 |  |  | 5 | 48 | 47 | 47 | 74 | 80 | 79 | 79 | 84 | 49 | 48 |  | 48 | 52 | 71 | 96 | 96 | 93 | 96 | 1506240
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 34 | 47 | 40 | 42 | 37 | 36 | 23 | 190560
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 5 | 17 | 18 | 53 | 53 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 776160
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 5 | 9 | 17 | 64 | 85 | 97 | 70 | 20 | 11 | 20 | 72 | 23 | 15 | [8 empty] | 436320
131 | Rampal 1320 MW (BIFPCL) | 345 | 345 | 349 | 342 | 344 | 345 | 343 | 343 | 342 | 341 | 339 | 343 | 342 | 345 | 352 | 354 | 354 | 346 |  | 346 | 348 | 346 | 346 | 345 | 345 | 346 | 8436364
132 | United Payra Power Ltd. | [19 empty] | 22 | 35 | 35 | 35 | 35 | 35 | 35 | 203400
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 180 |  | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 5349556
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 0 | [9 empty] | 16 | 16 | 16 | 16 |  | 32 | 64 | 64 | 96 | 96 | 96 | 110 | 594912
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 307 | 307 | 307 | 307 | 250 | 200 | 200 | 200 | 250 | 250 | 307 | 307 | 307 | 307 | 307 | 307 | 200 | 200 |  | 200 | 253 | 250 | 200 | 200 | 253 | 307 | 6240000
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4093
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 126 | 126 | 126 | 126 | 126 | 80 | 126 | 126 | 126 | 126 | 80 |  | 80 | 126 | 126 | 130 | 130 | 130 | 130 | 2606000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 9 | 9 | 9 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 8 | 9 | 9 | 8 | 7 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 196680
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 24 | 24 | 8 | 8 | 0 | [15 empty] | 16 | 24 | 32 | 32 | 32 | 32 | 207000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 917 | 916 | 915 | 914 | 914 | 914 | 920 | 919 | 919 | 920 | 920 | 919 | 920 | 920 | 920 | 920 | 920 | 922 |  | 923 | 921 | 921 | 922 | 921 | 922 | 923 | 22225454
147 | Bheramara 410 MW CCPP | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 370 | 375 | 375 | 375 | 370 | 365 | 360 | 355 | 350 | 350 |  | 340 | 340 | 345 | 340 | 340 | 335 | 335 | 8342784
148 | Payra 1320 MW | 1244 | 1244 | 1100 | 1100 | 1100 | 1000 | 990 | 1000 | 1080 | 1080 | 1080 | 1130 | 1040 | 1040 | 1090 | 1100 | 980 | 900 |  | 900 | 1140 | 1170 | 1244 | 1244 | 1244 | 1244 | 28552000
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 61 | 59 | 60 | 60 | 61 | 59 | 61 |  | 61 | 62 | 61 | 61 | 60 | 61 | 60 | 1415127
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5342000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [20 empty] | 40 | 40 | 40 | 33 | 33 | 33 | 174016
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 3 | 4 | 5 | 5 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 27000
| Sirajganj 68 MW Solar Park | [6 empty] | 4 | 14 | 11 | 38 | 45 | 47 | 20 | 14 | 16 | 6 | 4 | 1 | [8 empty] | 325680
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 178 | 157 | 156 | 157 | 162 | 169 | 168 | 171 | 179 | 179 | 183 | 167 | 167 | 190 | 189 | 183 | 181 | 169 |  | 163 | 201 | 194 | 166 | 180 | 180 | 167 | 4368918
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 356 | 296 | 319 | 320 | 359 | 347 | 347 | 347 | 390 | 395 | 353 | 315 | 250 | 414 | 414 | 373 | 308 | 333 |  | 347 | 376 | 293 | 392 | 392 | 354 | 394 | 8554327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 5 | 5 | 8 | 11 | 10 | 10 | 10 | 44097
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 95202
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 14 | 14 | 14 | 28 | 28 | 28 | 28 | 127890
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 14 | 21 | 35 | 47 | 47 | 42 | 42 | 176694
168 | Santahar 50 MW Peaking PP | 30 | 30 | 0 | [13 empty] | 9 | 15 |  | 20 | 28 | 30 | 30 | 30 | 30 | 30 | 233660
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 91 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [10 empty] | 81 | 81 | 83 | 83 | 83 | 83 | 83 | 598064
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 26 | 50 | 82 | 50 | 50 | 58 | 111 | 442464
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 70 | 85 | 90 | 50 | 50 | 85 | 95 | 405408
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 106 | 0 | [8 empty] | 20 | 36 | 42 | 34 | 34 | 34 | 34 |  | 96 | 98 | 98 | 70 | 70 | 80 | 99 | 989251
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | [8 empty] | 7822
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 70 | 35 | 0 |  |  |  | 35 | 35 | 35 | 35 | 36 | 36 | 35 | 35 | 35 | 35 |  | 112 | 115 | 115 | 115 | 115 | 115 | 115 | 1382400
| Intraco Solar 30 MW | [5 empty] | 0 | 0 | 1 | 5 | 17 | 12 | 15 | 6 | 12 | 17 | 10 | 3 | 0 | [8 empty] | 102378
| Adani Power Jharkhanda Ltd | 768 | 762 | 759 | 675 | 676 | 681 | 679 | 678 | 680 | 686 | 750 | 756 | 744 | 748 | 753 | 748 | 651 | 653 |  | 698 | 760 | 754 | 759 | 757 | 763 | 753 | 17072727
178 | Teesta Solar Limited | [5 empty] | 1 | 7 | 32 | 44 | 50 | 90 | 120 | 160 | 116 | 81 | 49 | 20 | 6 | [8 empty] | 815690