## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: May 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-05-01 |  | 2024-04-01 |  | 2023-05-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 16067 | 2024-05-23 | 16477 | 2024-04-30 | 14511 | 2023-05-30 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 3651 | 2024-05-28 | 8472 | 2024-04-11 | 4959 | 2023-05-18 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16067 | 2024-05-23 | 16477 | 2024-04-30 | 14511 | 2023-05-30 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 14488 | 2024-05-16 | 14301 | 2024-04-30 | 15395 | 2023-05-08 | 14488 | 2024-05-16
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 16400 | 2024-05-23 | 17200 | 2024-04-29 | 15600 | 2023-05-31 | 17200 | 2024-04-29
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14021 |  | 14226.8667 |  | 12886.871 |  | - | -
7 | Average Generation (MW) at Day Peak | 12364.2258 |  | 12460.6333 |  | 11447.9032 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 939 | 2024-05-08 | 938 | 2024-04-14 | 961 | 2022-05-05 | 964 | 2024-03-28
|  |  | 10:30 |  | 12:30 |  | 22:30 |  | 13:30
9 | Maximum Power Import from Tripura, India (MW) | 100 | 2024-05-25 | 164 | 2024-04-04 | 180 | 2022-05-28 | 194 | 12/06/19
|  |  | 19:00 |  | 9:30 |  | 16:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 845 | 2024-05-16 | 1533 | 2024-04-29 | 1995 | 2023-05-15 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14965 | 2024-05-16 | 15595 | 2024-04-29 | 11496 | 45061 | 14965 | 2024-05-16
|  | - | 21:00 | - | 21:00 |  | 0.83333 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-05-11 | 0 | 2024-04-12 | 0 | 45047 | - | -
|  |  | 19:30 |  | 21:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13341 | 2024-05-11 | 11762 | 2024-04-12 | 11274 | 2023-05-01 | - | -
|  |  | 19:30 |  | 21:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 526 | 2024-05-02 | 2640 | 2024-04-29 | 2489 | 45062 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 14149 | 2024-05-02 | 13036 | 2024-04-29 | 10144 | 45062 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-05-11 | 0 | 2024-04-12 | 0 | 45047 | - | -
|  |  | 12:00 |  | 12:00 |  | 21:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 10559 | 2024-05-02 | 9637 | 2024-04-12 | 9578 | 45047 | - | -
|  |  | 12:00 |  | 12:00 |  | 21:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 22 |  | 26 |  | 23 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 21 |  | 25 |  | 25 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 2216.8164 |  | 2294.259 |  | 1885.6965 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 116.8801 |  | 206.7694 |  | 62.0427 |  | - | -
22 | Net Generation of BPDB (MKWH) | 2099.9364 |  | 2087.4896 |  | 1823.6538 |  | - | -
23 | Net Generation of IPP (MKWH) | 5569.5361 |  | 5224.0519 |  | 4615.9365 |  | - | -
24 | Net Generation of REB (MKWH) | 99.879 |  | 104.2242 |  | 122.5788 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 239.9743 |  | 150.1603 |  | 357.0366 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 8009.3258 |  | 7565.926 |  | 6919.2058 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4771.0602 |  | 4739.6465 |  | 4252.0612 |  | 4771.06 | May-24
27 | Energy Generation by Diesel (MKWH) | 20.5221 |  | 30.5077 |  | 161.3514 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1295.8587 |  | 990.3125 |  | 1442.64 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 22.2695 |  | 23.0087 |  | 9.6847 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 55.4311 |  | 58.4751 |  | 48.4734 |  | 57.09 | March-24
31 | Energy Generation by Coal (MKWH) | 987.5956 |  | 1047.9615 |  | 1067.0377 |  | 1047.9615 | April'24
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 646.3346 |  | 676.6991 |  | 766.1342 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 78.2556 |  | 73.8657 |  | 80.7771 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: May 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 16067 | 2024-05-23 | 21:00
Generation Period
| Dhaka | MW | 5455.11
| Chattogram | MW | 1522.5
| Cumilla | MW | 1517
| Mymensingh | MW | 1117
| Sylhet | MW | 667
a) | Total supply in East zone | MW | 10278.61
| Khulna | MW | 1897.4
| Barisal | MW | 470.2
| Rajshahi | MW | 1621.6
| Rangpur | MW | 984
b) | Total supply in West zone | MW | 4973.2
c) | Total supply in both zone ( a+b) | MW | 15251.81
Ref: | 27.21.0000.603.16.087.20.819 | Date: 23/06/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 482 | 2024-05-05 | 21:00
| b) Ishurdi end | MW | 346 | 2024-05-27 | 3:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 822 | 2024-05-23 | 15:00
| b) Ishurdi end | MW | 298 | 2024-05-05 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 4.9199
| b) Ishurdi end | MKWH | 84.926
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 82.3783
| b) Ishurdi end | MKWH | 4.7766
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 |  |  |  |  | 2.955
| a) Ashuganj end | MW | 400 | 2024-05-02 | 20:00
| b)Serajganj end | MW | 690 | 2024-05-30 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 400 | 2024-05-27 | 13:00
| b)Sirajganj end | MW | 360 | 2024-05-05 | 23:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.598
| b)Sirajganj end | MKWH | 228.92
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 222.3663
| b)Sirajganj end | MKWH | 1.622
30 | Transmission loss of EWI /NO-2 | % | 2.739'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2290 | 2024-05-25 | 11:00
|  | MW | 1402
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2035 | 2024-05-25 | 11:00
|  | MW | 1388
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 20754 | 2024-05-25 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 20718 | 2024-05-25
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 412153
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 419953.6
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | -1.8926
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ashuganj 230/132/33kV Sub-Station | 132 kv Busbar-2 | 2024-05-11 15:00 | 2024-05-11 16:12 | 1:12 | E/O | Busbar conductor string damage. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 HT | 2024-05-12 09:09 | 2024-05-12 10:34 | 1:25 | T | Tripped showing Distance-A,C-phase relays. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-05-05 01:52 | 2024-05-05 02:04 | 0:12 | T | 33kv feeder No-14 not tripped. | 38 | 7.6 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-05-25 11:58 | 2024-05-25 12:43 | 0:45 | T | Tripped showing Back-Up Protection Trip relays. | 82 | 61.5 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-05-25 13:11 | 2024-05-25 14:00 | 0:49 | T | Tripped showing Back-Up Protection Trip relays. | 95 | 77.5833 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-05-27 17:27 | 2024-05-27 19:20 | 1:53 | E/O | Shutdown taken by DPBS-1due to 33kV Nayerhat feeder's maintenance work. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-05-27 17:26 | 2024-05-27 19:13 | 1:47 | E/O | Shutdown taken by DPBS-1due to 33kV Nayerhat feeder's maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2024-05-28 00:40 | 2024-05-28 07:46 | 7:06 | T | Nothing Unusual was Observed, it was raining. Perhaps water has entered the PRD. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | BUS-B | 2024-05-05 01:56 | 2024-05-05 01:59 | 0:03 | T | Ashuganj -01 CKT Ashu side CB trip | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-05-27 15:32 | 2024-05-27 15:55 | 0:23 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) LT | 2024-05-10 17:05 | 2024-05-10 17:33 | 0:28 | E/O | PBS work | 22 | 10.2667 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-05-09 21:59 | 2024-05-09 22:53 | 0:54 | E/O | Red hot Remove PDB | 30 | 27 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2024-05-04 22:04 | 2024-05-04 22:26 | 0:22 | T | 33 kv PDB T-5 Transfer Panel burn Because Tr-2 LT side Trip . | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2024-05-06 10:48 | 2024-05-06 11:22 | 0:34 | T | E/F & O/C Trip by 33 Kv Kotiadi Fault | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2024-05-09 23:28 | 2024-05-10 19:07 | 19:39 | T | O/C, B-Phase(PBS) | 24 | 471.6 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2024-05-22 04:46 | 2024-05-22 06:51 | 2:05 | E/O | Red Hot | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-05-27 17:38 | 2024-05-27 20:39 | 3:01 | T | Both incomer 1 and 2 tripped due to flushing at the jumpering point of PT connection of Auxlary of PBS. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-05-27 21:24 | 2024-05-27 21:33 | 0:09 | E/O | S/D requested by pbs for work purpose. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-05-27 17:38 | 2024-05-27 20:43 | 3:05 | T | Both incomer 1 and 2 tripped due to flushing at the jumpering point of PT connection of Auxlary of PBS. | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-05-27 21:24 | 2024-05-27 21:33 | 0:09 | E/O | S/D requested by pbs for work purpose. | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | T2(413T) LT | 2024-05-06 13:18 | 2024-05-06 15:12 | 1:54 | E/O | Excessive heat in 33 kv side R phase. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-05-28 21:08 | 2024-05-28 21:13 | 0:05 | T | T-3 Transformer trip shown differential protection-2, REF trip. | 40 | 3.3333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-05-19 20:01 | 2024-05-19 20:11 | 0:10 | T | SPBS 33 KV feeder fault due to bad Walther. | 16 | 2.6667 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-05-28 06:41 | 2024-05-28 06:41 | 0:00 | T | PDB 33 KV Feeder Fault. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-05-19 20:01 | 2024-05-19 20:12 | 0:11 | T | SPBS 33 KV feeder fault due to bad Walther. | 16 | 2.9333 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-05-28 06:41 | 2024-05-28 06:41 | 0:00 | T | PDB 33 KV Feeder fault. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2024-05-28 19:53 | 2024-05-28 21:03 | 1:10 | E/O | 33kV Bushing Clamp (Y Phase) Red-hot of T-1 | 45 | 52.5 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2024-05-20 17:40 | 2024-05-20 17:54 | 0:14 | T | Due to 33kv kachuandanga feeder string insulator blast | 14 | 3.2667 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | 132 kV Bus-1 | 2024-05-27 17:53 | 2024-05-27 19:05 | 1:12 | E/O | Corrective Maintenance | 0 | 0 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2024-05-22 09:47 | 2024-05-22 15:02 | 5:15 | T | Over head DS post insulator is busted R-Phase | 22 | 115.5 | Power interruption
|  |  | Total : | 56:12 |  | Unserved Energy: |  | 835.75
Dhaka (South) Grid Circle :
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2024-05-27 05:07 | 2024-05-27 05:14 | 0:07 | T | 33kv Nobabganj-2 fault | 30 | 3.5 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-05-14 14:28 | 2024-05-14 14:34 | 0:06 | T | 33kv Zinzira-1 fault | 17 | 1.7 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 LT | 2024-05-27 05:07 | 2024-05-27 05:14 | 0:07 | T | Tripped showing Over current relays. | 15 | 1.75 | Power interruption
Hasnabad 132/33kV Grid Substation | 33kv Main Bus | 2024-05-27 05:07 | 2024-05-27 05:14 | 0:07 | T | 33kv Nobabganj-2 feeder fault. | 30 | 3.5 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | 33kV Bus Section-2 | 2024-05-29 19:03 | 2024-05-29 22:44 | 3:41 | E/O | Due to Konakhola feeder maintenance work by PBS | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-1 LT | 2024-05-29 04:22 | 2024-05-29 04:41 | 0:19 | T | 33kV H04 feeder over current fault | 47 | 14.8833 | Power interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2024-05-29 19:03 | 2024-05-29 22:44 | 3:41 | E/O | 33kV konakhola feeder maintenance work by PBS. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2024-05-28 18:30 | 2024-05-28 19:36 | 1:06 | T | 51 non dirrectional over current tripped. | 29 | 31.9 | Power interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 HT | 2024-05-27 10:32 | 2024-05-27 17:47 | 7:15 | T | None | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 HT | 2024-05-27 17:50 | 2024-05-28 17:42 | 23:52 | T | Tripped showing Over current relays. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 HT | 2024-05-28 17:44 | 2024-05-29 20:38 | 26:54 | E/O | 33 kv side voltage unbalance | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-05-12 15:05 | 2024-05-12 19:43 | 4:38 | T | Trip | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-05-05 23:43 | 2024-05-05 23:52 | 0:09 | T | Due to 33kV Agla Feeder fault | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-05-24 02:38 | 2024-05-24 07:34 | 4:56 | T | Due to Auxillary transformer fault. | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV MI Cement HT | 2024-05-18 03:00 | 2024-05-18 16:23 | 13:23 | E/O | 33 kV incom. PT Blast | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2024-05-27 15:40 | 2024-05-27 17:01 | 1:21 | E/O | 33 kv Anandabazar feeder raiser loop change under T2 bus section | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-03 00:46 | 2024-05-03 01:02 | 0:16 | T | PBS Norsingdi feeder phase B&C E/F | 45 | 12 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-05 11:00 | 2024-05-05 11:06 | 0:06 | T | Anondha Bazar 33 kv feeder fault, Cable fault | 30 | 3 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-12 13:10 | 2024-05-12 14:43 | 1:33 | E/O | Emergency maintenance work by PBS. New Borpa feeder underground cable heat shrink. | 40 | 62 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-18 10:08 | 2024-05-18 10:55 | 0:47 | T | Salaam Steel 33kv feeder fault | 65 | 50.9167 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-27 01:11 | 2024-05-27 01:18 | 0:07 | T | PBS 33kv Aman cement feeder fault. | 40 | 4.6667 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-27 11:14 | 2024-05-27 11:25 | 0:11 | T | Trip | 5 | 0.91667 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-27 13:07 | 2024-05-27 13:31 | 0:24 | T | 33 kv Anandabazar feeder loop fault | 3 | 1.2 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2024-05-27 13:29 | 2024-05-27 18:16 | 4:47 | E/O | à¦¬à¦¿à¦·à§Ÿ: à§©à§© à¦•à§‡à¦­à¦¿ à¦«à¦¿à¦¡à¦¾à¦°-à§ª à¦à¦° à¦¬à¦¾à¦¸ à¦†à¦‡à¦¸à§‹à¦²à§‡à¦Ÿà¦° à¦œà¦¾à¦®à§à¦ªà¦¾à¦° à¦œà¦°à§à¦°à§€ à¦¸à¦‚à¦°à¦•à§à¦·à¦£ à¦•à¦¾à¦œà§‡à¦° à¦œà¦¨à§à¦¯ à§©à§© à¦•à§‡à¦­à¦¿ à¦¬à¦¾à¦¸ à¦¸à§‡à¦•à¦¶à¦¨ à¦ à¦¸à¦¹ à§§à§©à§¨/à§©à§© à¦•à§‡à¦­à¦¿ à¦Ÿà§à¦°à¦¾à¦¨à§à¦¸à¦«à¦°à¦®à¦¾à¦° à§§ à¦¸à¦¾à¦Ÿà¦¡à¦¾à¦‰à¦¨ à¦ªà§à¦°à¦¦à¦¾à¦¨ | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 LT | 2024-05-27 10:46 | 2024-05-27 10:46 | 0:00 | T | 33KV Feeder-4 Bus Isolator Jumper Y Phase (Isolator Side) flashover and disconnect from the clamp connector. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 LT | 2024-05-27 10:46 | 2024-05-27 11:11 | 0:25 | T | 33KV Feeder-4 Bus Isolator Jumper Y Phase (Isolator Side) flashover and disconnect from the clamp connector. | 0.2 | 0.083333 | Power interruption
Ullon 132/33kV Grid Sub-Station | GT-1 LT | 2024-05-10 01:11 | 2024-05-10 01:11 | 0:00 | E/O | Strange Noise from 33KV Cable side | 0 | 0 | No interruption
|  |  | Total : | 100:18 |  | Unserved Energy: |  | 192.0167
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | 230/33 kV Transformer-1 (125/140 MVA) LT | 2024-05-06 13:21 | 2024-05-06 15:01 | 1:40 | T | Tripped showing O/C operated relays. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | T-2 (412T) HT | 2024-05-02 03:11 | 2024-05-02 03:58 | 0:47 | T | Thundering 33kv feeder Fold. | 5 | 3.9167 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | SASM HT | 2024-05-02 22:04 | 2024-05-02 23:43 | 1:39 | T | Tripped showing O/C operated relays. | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-05-28 20:07 | 2024-05-28 22:25 | 2:18 | E/O | Due to Emergency maintenance work | 20 | 46 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T HT | 2024-05-06 22:32 | 2024-05-07 00:04 | 1:32 | E/O | Post Insulator change in 33 kv feeder | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-05-05 07:44 | 2024-05-05 08:22 | 0:38 | T | Tripped showing Lockout relay K862 Trip relays. | 20 | 12.6667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-05-31 00:39 | 2024-05-31 01:02 | 0:23 | T | 33 kv keranihat feeder fault | 60 | 23 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) HT | 2024-05-16 08:59 | 2024-05-16 09:24 | 0:25 | E/O | Due to BPDB Emergency Red Hot Maintenance at 33 kV Incomer Side. | 10 | 4.1667 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2024-05-11 20:18 | 2024-05-11 23:02 | 2:44 | E/O | Redhot Maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 LT | 2024-05-25 10:09 | 2024-05-25 10:23 | 0:14 | T | None | 47 | 10.9667 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2024-05-25 10:09 | 2024-05-25 10:23 | 0:14 | T | Tripped showing special protection relays. | 15 | 3.5 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-05-06 15:10 | 2024-05-08 00:30 | 33:20 | T | PDB feeder y phase out from busbur due to flashing. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2024-05-26 17:12 | 2024-05-26 17:33 | 0:21 | T | PDB 33KV FLASHING | 17 | 5.95 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2024-05-17 16:32 | 2024-05-17 18:29 | 1:57 | E/O | Bus red hot maintenance | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2024-05-26 18:26 | 2024-05-26 18:55 | 0:29 | E/O | PDB BUS COUPLER Flashing | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-05-06 15:10 | 2024-05-06 16:35 | 1:25 | T | PDB Feeder y phase disconnected from 33kv busbar | 18 | 25.5 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-05-26 17:12 | 2024-05-26 17:33 | 0:21 | T | PDB 33kv flashing | 17 | 5.95 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-05-27 11:57 | 2024-05-27 12:45 | 0:48 | T | 33 kV old Wasa Trip | 9 | 7.2 | Power interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-02 | 2024-05-14 09:15 | 2024-05-25 11:38 | 266:23 | E/O | 903 B Bus cupler singled CB Trip circuit Fail. All are shifted to Bus-1 Bus cupler Open/ (S/D). (230kV energise by 132kV) | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 HT | 2024-05-19 15:06 | 2024-05-19 15:30 | 0:24 | E/O | A while ago due to wind, we notice a strip of wire is hanging on conductor of 132kV side of Transformer-02 on phase B. It is urgent to remove the strip as soon as possible. | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) HT | 2024-05-31 21:28 | 2024-05-31 22:43 | 1:15 | E/O | red hot | 0 | 0 | No interruption
|  |  | Total : | 319:17 |  | Unserved Energy: |  | 148.8167
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 33KV BUS-2 | 2024-05-15 17:16 | 2024-05-15 18:39 | 1:23 | E/O | For 33 kv bus section 2 red hot condition solve | 25 | 34.5833 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2024-05-04 19:50 | 2024-05-04 20:16 | 0:26 | E/O | As per NLDC's instruction. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2024-05-04 20:26 | 2024-05-04 20:45 | 0:19 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-05-04 19:50 | 2024-05-04 20:45 | 0:55 | E/O | As per NLDC's instruction. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2024-05-11 06:59 | 2024-05-11 07:15 | 0:16 | T | Tripped showing EF, Ib=1.68 KA relays. | 30 | 8 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2024-05-04 19:50 | 2024-05-04 20:45 | 0:55 | E/O | As per NLDC's instruction. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2024-05-11 06:59 | 2024-05-11 07:15 | 0:16 | T | Tripped showing EF, Ib=1.68 KA relays. | 30 | 8 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-05-06 15:07 | 2024-05-06 16:57 | 1:50 | T | Tripped showing Lockout Relay Operate relays Due to OLTC Buchhol TZ Trip. | 10 | 18.3333 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 LT | 2024-05-23 22:21 | 2024-05-23 23:38 | 1:17 | E/O | Red hot in 33 Kv incomer breaker DS. | 40 | 51.3333 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 HT | 2024-05-25 23:25 | 2024-05-26 01:04 | 1:39 | E/O | Emergency red hot maintenance. | 33 | 54.45 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1 | 2024-05-27 12:50 | 2024-05-27 13:13 | 0:23 | E/O | 33 Kv PDB Control room station supply Transformer Read Pace Loop maintenence | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2024-05-27 12:53 | 2024-05-27 13:15 | 0:22 | E/O | 33 Kv PDB Control room station supply Transformer Read Pace Loop maintenence | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3-435T HT | 2024-05-06 06:42 | 2024-05-06 07:36 | 0:54 | E/O | 33kv Datter Feeder Red hot. | 16 | 14.4 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2024-05-02 19:15 | 2024-05-02 20:40 | 1:25 | T | 33 KV Kotbari feeder fault | 15 | 21.25 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2024-05-06 20:19 | 2024-05-06 21:22 | 1:03 | T | 33KV Shankarpur PDB feeder commissioning. | 76 | 79.8 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 LT | 2024-05-24 06:28 | 2024-05-24 09:20 | 2:52 | E/O | Red hot remove 33 KV Bus Coupler-2 | 60 | 172 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2024-05-02 19:15 | 2024-05-02 19:29 | 0:14 | T | Tripped showing overcurrent relay relays. | 15 | 3.5 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2024-05-06 20:19 | 2024-05-06 21:06 | 0:47 | T | 33KV Shankarpur PDB feeder commissioning. | 76 | 59.5333 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 HT | 2024-05-29 14:44 | 2024-05-29 15:31 | 0:47 | E/O | 33 KV Bus coupler maintenance | 24 | 18.8 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 LT | 2024-05-27 10:23 | 2024-05-27 10:37 | 0:14 | T | 33KV kotbari & nangolkot feeder fault. | 30 | 7 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-05-08 01:46 | 2024-05-08 02:28 | 0:42 | E/O | PBS-3 Redhot Remove work. | 28 | 19.6 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-05-06 12:21 | 2024-05-06 12:32 | 0:11 | E/O | At Time of Chauddragram Ckt-02 Tripping Period NLDC Given Order Reduce the Sub-station Load, To Prevent Overload at Chauddragram Ckt-01. That Why T-01 open Secondary. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-05-06 13:10 | 2024-05-06 14:35 | 1:25 | T | Due to REB Ckt-01 SKY Wire Broke and Fall on line at 33KV Bus End. Definite Earth Current | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-05-06 14:38 | 2024-05-06 15:40 | 1:02 | T | Due to REB Ckt-01 Breaker Broke Out, Transformer Secondary Trip Definite Over Current. | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | TR-1 HT | 2024-05-29 15:41 | 2024-05-29 16:55 | 1:14 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2024-05-29 10:14 | 2024-05-29 10:29 | 0:15 | T | Tripped showing Differential Relay relays. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-05-19 08:40 | 2024-05-19 08:53 | 0:13 | T | PBS 33KV Feeder fault | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-05-28 01:12 | 2024-05-28 01:27 | 0:15 | T | Shaishatang feeder fault | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-05-28 05:12 | 2024-05-28 05:19 | 0:07 | T | Shaistaganj feeder fault | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB HT | 2024-05-28 08:48 | 2024-05-28 08:54 | 0:06 | T | Heavy Storm. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-1AB HT | 2024-05-28 08:55 | 2024-05-28 13:40 | 4:45 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 HT | 2024-05-30 06:25 | 2024-05-30 06:33 | 0:08 | T | Tripped showing Lock Out relays | 17 | 2.2667 | Power interruption
|  |  | Total : | 28:40 |  | Unserved Energy: |  | 572.85
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-05-08 03:45 | 2024-05-08 03:56 | 0:11 | T | Rampal feeder fault | 12 | 2.2 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-05-18 21:52 | 2024-05-18 22:02 | 0:10 | T | Incomer tripped due to 33kV Morrelgonj feeder fault. | 19 | 3.1667 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-05-20 17:21 | 2024-05-20 17:29 | 0:08 | T | 33 kv morrelgonj feeder fault | 9 | 1.2 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-05-08 03:45 | 2024-05-08 03:55 | 0:10 | T | Rampal feeder fault | 12 | 2 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-05-18 21:52 | 2024-05-18 22:03 | 0:11 | T | Incomer tripped due to 33kV Morrelgonj feeder fault. | 19 | 3.4833 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-05-20 17:21 | 2024-05-20 17:30 | 0:09 | T | 33kv morrelgonj feeder fault | 9 | 1.35 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2024-05-26 12:06 | 2024-05-26 12:53 | 0:47 | E/O | 132 kv control Panel CT connection maintenance works | 30 | 23.5 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-05-06 22:48 | 2024-05-06 22:53 | 0:05 | T | 33 kv Palashpur feeder (wzpdco) fault. | 32 | 2.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-05-26 11:41 | 2024-05-26 11:48 | 0:07 | T | Dopdapia 2, 33kv feeder (wzpdcl) | 40 | 4.6667 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-05-12 11:52 | 2024-05-12 11:55 | 0:03 | T | Wzpdcl dopdopia feeder fault. | 32 | 1.6 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-05-06 16:07 | 2024-05-06 16:39 | 0:32 | T | Due to 33KV Babuganj Feeder Fault | 3 | 1.6 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2024-05-25 20:06 | 2024-05-25 20:17 | 0:11 | T | Pbs Jhalokathi 33kv ct blast | 25 | 4.5833 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-05-29 00:36 | 2024-05-29 01:35 | 0:59 | E/O | Due to emergency maint.work | 6 | 5.9 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-05-06 16:07 | 2024-05-06 16:39 | 0:32 | T | Due to 33KV Babuganj Feeder Fault | 3 | 1.6 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2024-05-25 20:06 | 2024-05-25 20:17 | 0:11 | T | Pbs jhalokathi 33kv ct Blast | 25 | 4.5833 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2024-05-20 23:22 | 2024-05-21 00:06 | 0:44 | E/O | Bagachara feeder redhot maintenance | 25 | 18.3333 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2024-05-27 02:09 | 2024-05-27 02:16 | 0:07 | T | storm Remal | 20 | 2.3333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-05-15 11:20 | 2024-05-15 12:20 | 1:00 | E/O | Emergency work | 20 | 20 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-05-08 08:05 | 2024-05-08 08:30 | 0:25 | T | 33KV kathalia pbs feeder fault. | 4 | 1.6667 | Power interruption
Borhanuddin 230/33kV Grid Sub-Station | Tr-Load HT | 2024-05-17 19:54 | 2024-05-17 20:42 | 0:48 | E/O | Red hot Maintenance 33 kv Cable joint. | 65 | 52 | Power interruption
Borhanuddin 230/33kV Grid Sub-Station | Tr-Load HT | 2024-05-29 00:30 | 2024-05-29 02:45 | 2:15 | E/O | Red hot Maintenance. | 22 | 49.5 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 HT | 2024-05-08 06:56 | 2024-05-08 13:14 | 6:18 | E/O | Temperature high in 33 kv b phase loop. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-05-30 11:11 | 2024-05-30 12:36 | 1:25 | E/O | 33 kv clamp flashover. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-05-07 07:08 | 2024-05-07 09:44 | 2:36 | E/O | High temperature maintenance of loop joint at y phase breaker side of bus D/S | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-05-06 18:28 | 2024-05-06 20:17 | 1:49 | E/O | for over voltage | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-05-27 06:50 | 2024-05-27 12:26 | 5:36 | E/O | Instruction by incharge | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T HT | 2024-05-27 13:47 | 2024-05-27 13:50 | 0:03 | T | Tripped showing PRD relays. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-05-27 21:45 | 2024-05-27 21:56 | 0:11 | T | Due to REB-3 Feeder (50/51) & (50N/51N) Trip | 5 | 0.91667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-05-28 21:11 | 2024-05-28 21:19 | 0:08 | T | 50OC-DMT Trip, B&C Phase , (Due to Khanjahan Ali P/S Line Fault ) | 17.5 | 2.3333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-05-27 21:45 | 2024-05-27 21:56 | 0:11 | T | Due to REB-3 Feeder (50/51) & (50N/51N) Trip | 5 | 0.91667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-05-28 21:11 | 2024-05-28 21:19 | 0:08 | T | 50OC-DMT Trip, B&C Phase , (Due to Khanjahan Ali P/S Line Fault ) | 17.5 | 2.3333 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2024-05-06 21:03 | 2024-05-06 21:17 | 0:14 | T | Khepupara 33kV fault | 2 | 0.46667 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2024-05-10 10:21 | 2024-05-10 12:51 | 2:30 | E/O | Red hot fixation on 33kV BUS by PBS. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 405T (T-1) HT | 2024-05-18 17:43 | 2024-05-18 18:00 | 0:17 | T | Khepupara tripped due to fault in 33 KV feeder, after which when the said Khepupara was given trial, 132 KV and 33 KV side of T-1 transformer tripped due to earth fault | 8.5 | 2.4083 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 415T (T-2) HT | 2024-05-06 21:03 | 2024-05-06 21:27 | 0:24 | T | Khepupara 33kV fault | 2 | 0.8 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-05-27 10:17 | 2024-05-27 11:47 | 1:30 | E/O | Connecting Auxiliary Transformer fuse. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2024-05-27 10:16 | 2024-05-27 11:48 | 1:32 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 34:37 |  | Unserved Energy: |  | 218.1083
HVDC Grid Circle :
Bheramara 230/132kV Grid Sub-Station | Transformer-1 HT | 2024-05-27 15:35 | 2024-05-28 07:24 | 15:49 | E/O | voltage risen | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) HT | 2024-05-25 06:08 | 2024-05-25 07:53 | 1:45 | E/O | Red-hot maintenance of T-2 at 132kV Bushing(Y-Phase). | 30 | 52.5 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) LT | 2024-05-27 03:56 | 2024-05-27 04:10 | 0:14 | T | Due to rain & strom. | 16 | 3.7333 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T2(426T) LT | 2024-05-28 00:01 | 2024-05-28 00:20 | 0:19 | T | Due to 33kV Meherpur feeder | 16 | 5.0667 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T3 HT | 2024-05-27 03:56 | 2024-05-27 05:52 | 1:56 | T | Due to rain & strom. | 16 | 30.9333 | Power interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T3 HT | 2024-05-27 18:52 | 2024-05-27 19:14 | 0:22 | T | Due to 33kV Meherpur feeder | 0 | 0 | No interruption
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T3 HT | 2024-05-28 00:01 | 2024-05-28 00:18 | 0:17 | T | Due to 33kV Meherpur feeder | 16 | 4.5333 | Power interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-05-16 10:52 | 2024-05-16 12:35 | 1:43 | E/O | Red Hot Maintenance of 132kV 80/120MVA Transformer-3. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-05-19 08:39 | 2024-05-19 12:23 | 3:44 | E/O | Red Hot Maintenance. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-2 HT | 2024-05-09 17:45 | 2024-05-09 18:15 | 0:30 | E/O | Due to emergency maint.work | 5 | 2.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-3 HT | 2024-05-13 07:02 | 2024-05-13 08:38 | 1:36 | E/O | Red hot maintenance | 10 | 16 | Power interruption
|  |  | Total : | 28:15 |  | Unserved Energy: |  | 115.2667
Bogura Grid Circle:
Amnura 132/33kV Grid Sub-Station | T-1 (406T) LT | 2024-05-08 01:09 | 2024-05-08 01:52 | 0:43 | T | Tripped showing Over voltage relays. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2024-05-20 12:31 | 2024-05-20 13:40 | 1:09 | E/O | Red hot maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-A | 2024-05-31 08:33 | 2024-05-31 10:20 | 1:47 | E/O | T-1 132kV DS Loop Tightening work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2024-05-22 08:15 | 2024-05-22 09:23 | 1:08 | T | Rain & Thundering. | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-1 (407 T) LT | 2024-05-03 13:43 | 2024-05-03 13:58 | 0:15 | T | 33 kV Feeder CB to CT Jumper out and touch Ground | 9 | 2.25 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-2 (417 T) LT | 2024-05-03 13:43 | 2024-05-03 13:59 | 0:16 | T | 33 kV Feeder CB to CT Jumper out and touch Ground | 9 | 2.4 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2024-05-16 13:38 | 2024-05-16 18:12 | 4:34 | T | Kahalu 33kV Feeder Fault. | 25 | 114.1667 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2024-05-30 08:25 | 2024-05-30 12:37 | 4:12 | E/O | Shukhanpukur 33 kV Feeder Redhot in BUS Side. | 20 | 84 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2024-05-16 13:38 | 2024-05-16 14:06 | 0:28 | T | Kahalu 33kV Feeder Fault. | 45 | 21 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2024-05-28 23:56 | 2024-05-29 00:50 | 0:54 | E/O | Emergence 33 kv Bus DS Pirob Feeder Maintenance Work | 25 | 22.5 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | BUS SECTION-1 (33KV) | 2024-05-23 11:08 | 2024-05-23 12:20 | 1:12 | E/O | Maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2024-05-23 11:10 | 2024-05-23 12:25 | 1:15 | E/O | Maintenance work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2024-05-15 09:04 | 2024-05-15 10:54 | 1:50 | E/O | Red hot work | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2024-05-29 09:07 | 2024-05-29 10:24 | 1:17 | E/O | Red hot maintenance work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-05-02 12:30 | 2024-05-02 12:47 | 0:17 | T | Adamdhighi PBS 33 kv C Phase LA burst. | 37 | 10.4833 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-05-02 12:30 | 2024-05-02 12:41 | 0:11 | T | Adamdhighi PBS 33 kv C Phase LA burst. | 37 | 6.7833 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2024-05-22 09:52 | 2024-05-22 13:08 | 3:16 | T | Emergency tripping by hand cause of red hot. | 20 | 65.3333 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2024-05-08 21:22 | 2024-05-08 21:30 | 0:08 | T | Including 33Kv feeder trip | 26 | 3.4667 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2024-05-11 22:06 | 2024-05-11 23:18 | 1:12 | E/O | T3 bus red hot | 28 | 33.6 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2024-05-20 11:57 | 2024-05-20 12:22 | 0:25 | T | Feeder foult | 24 | 10 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) HT | 2024-05-29 06:34 | 2024-05-29 07:48 | 1:14 | E/O | Red hot | 18 | 22.2 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) LT | 2024-05-08 01:00 | 2024-05-08 01:16 | 0:16 | T | à¦¬à§ƒà¦·à§à¦Ÿà¦¿à¦° à¦•à¦¾à¦°à¦¨à§‡à¥¤ | 24 | 6.4 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-05-22 07:05 | 2024-05-22 08:18 | 1:13 | E/O | à¦¦à§‡à¦²à§à§Ÿà¦¾à¦¬à¦¾à§œà§€ à§©à§© à¦•à§‡à¦­à¦¿ à¦«à¦¿à¦¡à¦¾à¦°à§‡ à¦°à§‡à¦¡à¦¹à¦Ÿ | 5 | 6.0833 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) LT | 2024-05-05 18:15 | 2024-05-05 18:34 | 0:19 | T | Manda 33 kv feeder fault | 10 | 3.1667 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) LT | 2024-05-26 21:10 | 2024-05-26 21:13 | 0:03 | T | Rain | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T LT | 2024-05-29 12:01 | 2024-05-29 13:41 | 1:40 | E/O | Red hot maintenance | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer LT | 2024-05-10 12:14 | 2024-05-10 13:03 | 0:49 | E/O | Due to emergency maint.work | 30 | 24.5 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) HT | 2024-05-15 11:45 | 2024-05-15 12:05 | 0:20 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) HT | 2024-05-12 10:36 | 2024-05-12 11:22 | 0:46 | E/O | ATR 02 à¦à¦° à¦¬à§‡à¦•à¦¾à¦° à¦Ÿà§ à¦¸à¦¿à¦Ÿà¦¿ Y-ph à¦°à¦¾à¦‡à¦œà¦¾à¦°à§‡à¦° à¦®à¦¾à¦à§‡ à¦œà¦¿à¦†à¦‡ à¦¤à¦¾à¦° à¦…à¦ªà¦¸à¦¾à¦°à¦£ à¦à¦° à¦•à¦¾à¦œà¥¤ | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) HT | 2024-05-10 09:37 | 2024-05-11 01:20 | 15:43 | T | Due to Earth fault | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2024-05-08 22:33 | 2024-05-08 23:30 | 0:57 | E/O | PBS-1 has taken shutdown, Red Hot has become visible of 33kV Tarash Feeder BUS DS Y-phase. | 12 | 11.4 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) HT | 2024-05-20 00:42 | 2024-05-20 01:03 | 0:21 | T | Tripped showing N/A relay | 0 | 0 | No interruption
|  |  | Total : | 50:10 |  | Unserved Energy: |  | 449.7333
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 617:29 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-05-09 17:23 | 2024-05-09 19:13 | 1:50 | T |  | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-05-11 06:45 | 2024-05-11 08:49 | 2:04 | T |  | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-05-11 09:10 | 2024-05-11 11:25 | 2:15 | E/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-05-12 09:09 | 2024-05-12 11:16 | 2:07 | T | None | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-05-21 13:57 | 2024-05-21 14:46 | 0:49 | T | Distance protection C- Phase relay | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2024-05-28 03:06 | 2024-05-28 06:05 | 2:59 | T | Tripped | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2024-05-28 03:06 | 2024-05-28 06:06 | 3:00 | T | Tripped | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2024-05-30 10:44 | 2024-05-30 12:00 | 1:16 | E/O | oil filling CB B phase | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2024-05-30 15:34 | 2024-05-30 15:34 | 0:00 | T |  | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2024-05-28 03:06 | 2024-05-28 05:52 | 2:46 | T | Tripped | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh Ckt- 01 | 2024-05-05 20:51 | 2024-05-05 21:08 | 0:17 | T | Thunderouing | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Mymensingh Ckt- 02 | 2024-05-05 20:51 | 2024-05-05 21:08 | 0:17 | T | Thundering | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 01 | 2024-05-12 09:05 | 2024-05-12 09:27 | 0:22 | T | Overload | 102 | 37.4 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 01 | 2024-05-25 19:01 | 2024-05-25 19:09 | 0:08 | T | Overcurrent | 140 | 18.6667 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 02 | 2024-05-04 23:16 | 2024-05-04 23:32 | 0:16 | T | Distance R,Y,B Phase, zone-1, | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 02 | 2024-05-25 19:01 | 2024-05-25 19:09 | 0:08 | T | Over current | 140 | 18.6667 | Power interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-1 | 2024-05-12 09:06 | 2024-05-12 09:48 | 0:42 | T | overload | 17 | 11.9 | Power interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-2 | 2024-05-12 09:06 | 2024-05-12 09:49 | 0:43 | T | overload | 17 | 12.1833 | Power interruption
Ghatail 132/33kV Grid Sub-Station | Tangail-1 | 2024-05-08 03:53 | 2024-05-08 07:47 | 3:54 | E/O | For LA (R-Phase) Grounding emergency Connection. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-05-05 02:14 | 2024-05-05 03:14 | 1:00 | T | Tripped showing Distance -A relays. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kadda-1 | 2024-05-05 21:10 | 2024-05-05 23:09 | 1:59 | T | Tripped showing Distance -A relays. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-2 | 2024-05-05 21:23 | 2024-05-05 22:12 | 0:49 | T | Tripped showing Distance -A relays. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2024-05-05 21:23 | 2024-05-05 21:38 | 0:15 | T | Tripped showing Distance -A relays. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2024-05-27 13:38 | 2024-05-27 14:00 | 0:22 | T | Distance protection zone-1. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2024-05-27 15:44 | 2024-05-27 17:07 | 1:23 | T | Distance Protection Relay Operated, Zone-2, Distance 19.3km. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-05-12 09:04 | 2024-05-15 23:19 | 86:15 | T | CT Burst in Ashuganj S/S | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-05-15 23:35 | 2024-05-16 00:09 | 0:34 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-05-25 19:01 | 2024-05-25 20:19 | 1:18 | T | Dist: R,Y, Z1, 33.2 km | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-05-12 09:04 | 2024-05-12 11:12 | 2:08 | T | CT Burst in Ashuganj S/S | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-05-25 19:01 | 2024-05-25 20:43 | 1:42 | T | Dist: R,Y, Z1, 32.4 km | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-05-27 15:12 | 2024-05-27 22:50 | 7:38 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2024-05-05 18:56 | 2024-05-05 19:40 | 0:44 | T | Z1, y-phase Distance Relay 4.4km | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2024-05-27 15:44 | 2024-05-27 17:20 | 1:36 | T | O/V | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2024-05-27 17:27 | 2024-05-27 18:07 | 0:40 | T | O/V | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2024-05-27 19:04 | 2024-05-27 22:38 | 3:34 | T | O/V | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-05-27 15:15 | 2024-05-27 22:45 | 7:30 | T | O/V | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Kabirpur Ckt-1 | 2024-05-07 12:22 | 2024-05-09 16:05 | 51:43 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Kabirpur Ckt-2 | 2024-05-07 12:22 | 2024-05-07 12:55 | 0:33 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-2 | 2024-05-25 19:37 | 2024-05-25 19:57 | 0:20 | T | Without Reason | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-05-11 07:25 | 2024-05-11 07:25 | 0:00 | T | Heavy rain & Thunderstorm | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-2 | 2024-05-11 12:20 | 2024-05-11 13:30 | 1:10 | E/O | Tree trimming works | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-2 | 2024-05-05 00:10 | 2024-05-05 00:38 | 0:28 | T | Rain and heavy Thandaring | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-05-05 00:28 | 2024-05-05 00:45 | 0:17 | T | Heavy Rain and Thandaring | 0 | 0 | No interruption
Rajendrapur 132/33kV Grid Sub-Station | Kodda-1 | 2024-05-12 13:15 | 2024-05-12 15:15 | 2:00 | E/O | Due to ROW clearance of transmission line. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-05 00:15 | 2024-05-05 00:49 | 0:34 | T | Due to rain And Thunder storm | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-06 13:47 | 2024-05-06 15:05 | 1:18 | E/O | Removing Threads | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-05-12 09:05 | 2024-05-12 09:20 | 0:15 | T | Over Current | 130 | 32.5 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-05-12 09:05 | 2024-05-12 09:15 | 0:10 | T | Over Current | 130 | 21.6667 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2024-05-25 19:01 | 2024-05-25 19:08 | 0:07 | T | Dir. Over Current | 135 | 15.75 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-05-05 02:21 | 2024-05-05 02:32 | 0:11 | T | Heavy wind and storm. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-05-28 01:29 | 2024-05-28 01:31 | 0:02 | T | Thunder storm. | 60 | 2 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2024-05-27 07:55 | 2024-05-27 07:59 | 0:04 | T | Heavy wind | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2024-05-27 10:02 | 2024-05-28 01:51 | 15:49 | T | Heavy wind | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2024-05-28 11:58 | 2024-05-28 20:51 | 8:53 | E/O | Maintenance work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2024-05-05 02:14 | 2024-05-05 02:42 | 0:28 | T | Heavy wind and storm. | 50 | 23.3333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-05-05 02:09 | 2024-05-05 02:42 | 0:33 | T | Heavy storm and wind. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-05-05 21:32 | 2024-05-05 22:48 | 1:16 | T | Stormy weather. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-05-06 18:56 | 2024-05-06 20:13 | 1:17 | E/O | temperature rise | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-05-09 14:09 | 2024-05-09 14:30 | 0:21 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-05-20 19:17 | 2024-05-20 22:04 | 2:47 | E/O | Temperature minimising work | 100 | 278.3333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2024-05-27 00:51 | 2024-05-27 00:59 | 0:08 | T | Thunder storm | 0 | 0 | No interruption
|  |  | Total : | 236:04 |  | Unserved Energy: |  | 472.4
Dhaka (South) Grid Circle :
Bhulta 400/230kV Grid Sub-Station | Ashuganj-02 | 2024-05-05 07:19 | 2024-05-05 22:51 | 15:32 | E/O | Line checking to find out fault location of Ashuganj ckt 2. Ashuganj ckt 2 Y phase current zero. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-01 | 2024-05-28 01:14 | 2024-05-28 09:51 | 8:37 | E/O | S/D taken From NLDC. | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Ghorashal-02 | 2024-05-02 22:40 | 2024-05-03 01:07 | 2:27 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-05-27 14:32 | 2024-05-27 21:07 | 6:35 | T | deu to Tropical Cyclone Remal | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-1 | 2024-05-07 10:47 | 2024-05-07 11:09 | 0:22 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Shyampur-2 | 2024-05-27 17:19 | 2024-05-27 21:06 | 3:47 | T | Due to Tropical Cyclone Remal | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-05-05 17:33 | 2024-05-05 18:18 | 0:45 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-05-05 21:45 | 2024-05-06 01:34 | 3:49 | T | None | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-05-11 06:23 | 2024-05-11 10:46 | 4:23 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi Circuit-2 | 2024-05-22 14:57 | 2024-05-22 16:01 | 1:04 | E/O | Dhamrai 132 kV grid substation will carry out removal of cloth due to cloth stuck on the Ishwardi circuit-2 line. | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi circuit-1 | 2024-05-05 10:02 | 2024-05-06 02:01 | 15:59 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Ghorashal 230kV Switching Sub-Station | Ghorashal-Ishwardi circuit-1 | 2024-05-11 11:51 | 2024-05-11 12:56 | 1:05 | E/O | Due to saree hanging on the line | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-1 | 2024-05-05 05:28 | 2024-05-05 06:19 | 0:51 | T | Due to Differential earth fault at S phase rampura circuit -2 | 64 | 54.4 | Power interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2024-05-05 05:28 | 2024-05-14 08:38 | 219:10 | T | Differential earth fault at S phase | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Siddhirganj-2 | 2024-05-28 01:03 | 2024-05-28 07:44 | 6:41 | E/O | To reduce 230 KV Bus Voltage. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-05-05 02:36 | 2024-05-05 02:53 | 0:17 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bhulta | 2024-05-06 19:56 | 2024-05-06 20:14 | 0:18 | T | None | 20 | 6 | Power interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-05-27 16:17 | 2024-05-28 14:04 | 21:47 | E/O | Line DS (B phase) shaft displacement. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-05-03 01:43 | 2024-05-03 02:11 | 0:28 | T | Unknown. | 80 | 37.3333 | Power interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-05-05 02:36 | 2024-05-05 02:52 | 0:16 | T | Unknown. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-05-05 21:18 | 2024-05-05 21:30 | 0:12 | T | Heavy Thundering & Rainfall at Narsindi end. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-1 | 2024-05-05 22:46 | 2024-05-05 23:17 | 0:31 | T | Heavy Thundering & Rainfall | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2024-05-12 12:49 | 2024-05-12 16:28 | 3:39 | E/O | Emergency High Temperature maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-01 22:30 | 2024-05-01 22:52 | 0:22 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-05 22:59 | 2024-05-05 23:09 | 0:10 | T | Heavy Thundering & Rainfall | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-06 23:00 | 2024-05-06 23:09 | 0:09 | T | Distance relay. Zone 1 | 12 | 1.8 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-06 23:24 | 2024-05-07 01:38 | 2:14 | T | Rainy and Stormy Weather. | 5 | 11.1667 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-07 01:45 | 2024-05-07 11:17 | 9:32 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-19 16:47 | 2024-05-19 18:01 | 1:14 | T | Rain & Thundering | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-25 20:03 | 2024-05-25 20:23 | 0:20 | T | Unknown. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-26 18:14 | 2024-05-26 18:22 | 0:08 | T | None | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-27 09:50 | 2024-05-27 10:33 | 0:43 | T | Heavy Rainfall. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-27 14:10 | 2024-05-27 14:32 | 0:22 | T | Heavy Rainfall. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-27 14:40 | 2024-05-27 20:48 | 6:08 | T | Heavy Rainfall. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-27 20:49 | 2024-05-28 14:47 | 17:58 | T | Heavy Rainfall | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-05-05 23:41 | 2024-05-06 00:38 | 0:57 | T | Unknown | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-05-11 08:27 | 2024-05-11 09:27 | 1:00 | T | Heavy rain fall | 30 | 30 | Power interruption
Hasnabad 132/33kV Grid Substation | Fatulla (Pre-Brahmongaon) | 2024-05-27 13:57 | 2024-05-27 21:06 | 7:09 | T | Unknown | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-05-05 22:51 | 2024-05-05 23:58 | 1:07 | T | Thundering | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-05 22:35 | 2024-05-05 23:58 | 1:23 | T | Thundering | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-06 23:15 | 2024-05-06 23:28 | 0:13 | T | SOTF, 21 distance fault 3.7 km, Zone-01 trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-11 07:53 | 2024-05-11 11:52 | 3:59 | T | Thundering | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-24 14:35 | 2024-05-24 15:16 | 0:41 | E/O | According to NLDC Instruction. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-27 14:45 | 2024-05-27 19:06 | 4:21 | T | Zone 1 trip 3.7 km B-Phase Pickup SOTF trip | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Lalbagh-3 | 2024-05-05 22:41 | 2024-05-05 23:42 | 1:01 | T | Thundering | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2024-05-03 02:06 | 2024-05-03 02:30 | 0:24 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-05-05 03:28 | 2024-05-05 09:08 | 5:40 | E/O | overload control of 132 KV Haripur | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2024-05-11 08:25 | 2024-05-11 08:50 | 0:25 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2024-05-27 22:53 | 2024-05-28 12:46 | 13:53 | T | Main Protection Operated Fail | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-05-13 01:11 | 2024-05-13 01:11 | 0:00 | T | inn. E/F A phase | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-05-13 09:14 | 2024-05-13 09:14 | 0:00 | E/O | Emergency maintenance work . | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132 kV Maniknagar | 2024-05-03 00:26 | 2024-05-03 08:45 | 8:19 | T | Over Current & Earth fault | 0 | 0 | No interruption
Matuail 132/33kV Grid Sub-Station | 132 kV Maniknagar | 2024-05-27 14:14 | 2024-05-27 18:13 | 3:59 | T | Tripped | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-01 | 2024-05-08 05:07 | 2024-05-08 05:49 | 0:42 | T | Directional earth fault | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Aminbazar 400KV Ckt-1 | 2024-05-27 15:45 | 2024-05-27 15:45 | 0:00 | E/O | Emergency maintenance work . | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Madunaghat 400KV Ckt-2 | 2024-05-27 15:48 | 2024-05-27 15:48 | 0:00 | E/O | Emergency maintenance work . | 23 | 0 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-01 15:41 | 2024-05-01 16:53 | 1:12 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-05 15:13 | 2024-05-05 15:23 | 0:10 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-07 01:40 | 2024-05-07 01:50 | 0:10 | T | Unknown. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-09 13:53 | 2024-05-09 14:24 | 0:31 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 07:21 | 2024-05-27 07:28 | 0:07 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 09:11 | 2024-05-27 09:28 | 0:17 | T | Strom | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 09:56 | 2024-05-27 10:06 | 0:10 | T | Strom | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 13:25 | 2024-05-27 13:29 | 0:04 | T | Strom | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 14:09 | 2024-05-27 14:30 | 0:21 | T | Storm Remel | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 15:05 | 2024-05-27 15:10 | 0:05 | T | Storm Remel | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-27 15:22 | 2024-05-28 01:43 | 10:21 | T | Storm Remel | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-05-27 15:05 | 2024-05-27 15:16 | 0:11 | T | Storm Remel | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-05-27 23:05 | 2024-05-27 23:11 | 0:06 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2024-05-03 00:20 | 2024-05-03 02:12 | 1:52 | T | Due to heavy thunderstorm & rainfall. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-01 | 2024-05-31 06:34 | 2024-05-31 08:01 | 1:27 | E/O | Emergency maintenance work . | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-02 | 2024-05-28 16:04 | 2024-05-28 16:17 | 0:13 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-02 | 2024-05-28 16:18 | 2024-05-28 20:23 | 4:05 | T | Unknown | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-05-30 07:12 | 2024-05-30 20:09 | 12:57 | E/O | Emergency maintenance work . | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2024-05-05 22:45 | 2024-05-05 23:24 | 0:39 | T | Baishaki Rain storm | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-05-05 22:45 | 2024-05-05 23:20 | 0:35 | T | Rain storm | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2024-05-27 17:27 | 2024-05-27 17:48 | 0:21 | T | Cyclone Remal | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-05-20 10:48 | 2024-05-20 17:02 | 6:14 | E/O | Maintenances work in EGCB Ends | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-05-21 09:43 | 2024-05-21 17:09 | 7:26 | E/O | Maintenance work by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2024-05-23 09:15 | 2024-05-23 20:08 | 10:53 | E/O | Maintenance work by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-05-27 15:53 | 2024-05-27 16:03 | 0:10 | T | Cyclone Remal | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-05-27 16:09 | 2024-05-27 17:06 | 0:57 | T | Cyclone Remal | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-05-12 12:30 | 2024-05-12 16:29 | 3:59 | E/O | Maintenance work in Haripur end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-05-14 09:32 | 2024-05-14 21:30 | 11:58 | E/O | Maintenance work in Haripur end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-05-14 21:52 | 2024-05-14 22:30 | 0:38 | E/O | Maintenance work in Haripur end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-05-14 22:33 | 2024-05-15 12:12 | 13:39 | E/O | Maintenance work in Haripur end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2024-05-19 10:55 | 2024-05-19 14:48 | 3:53 | E/O | Maintenance work in Haripur end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-05-05 22:45 | 2024-05-05 23:09 | 0:24 | T | Baisaki Storm, lightning erresror. | 45 | 18 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | Matuail | 2024-05-27 17:27 | 2024-05-27 23:08 | 5:41 | T | Cyclone Remal | 13 | 73.8833 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2024-05-27 14:23 | 2024-05-27 19:52 | 5:29 | T | Cyclone Remal | 30 | 164.5 | Power interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2024-05-27 15:22 | 2024-05-27 16:31 | 1:09 | T | Over voltage | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2024-05-27 15:22 | 2024-05-27 16:32 | 1:10 | T | Over Voltage | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bashundhara Line | 2024-05-27 15:12 | 2024-05-27 18:12 | 3:00 | T | Over voltage trip | 14 | 42 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Bus-Coupler | 2024-05-11 08:20 | 2024-05-11 09:03 | 0:43 | T | Due to bed weather. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2024-05-11 08:20 | 2024-05-11 09:04 | 0:44 | T | Due to bad weather | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2024-05-05 03:00 | 2024-05-05 03:25 | 0:25 | T | Bad weather | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-05-27 15:05 | 2024-05-27 17:40 | 2:35 | T | Bad weather | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | OPSL(IEL-2) | 2024-05-29 14:20 | 2024-05-29 17:35 | 3:15 | E/O | OPSL (power plant) control panel signal displayed TC1/TC2 faulty CB gas pressure Lock out | 0 | 0 | No interruption
|  |  | Total : | 533:24 |  | Unserved Energy: |  | 439.0833
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-1 | 2024-05-03 00:11 | 2024-05-03 00:47 | 0:36 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-05-02 08:40 | 2024-05-02 10:14 | 1:34 | E/O | spark | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-05-06 13:11 | 2024-05-06 23:47 | 10:36 | T | None | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Cumilla Ckt-2 | 2024-05-22 10:55 | 2024-05-22 11:06 | 0:11 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | GPH Ispat Ckt | 2024-05-02 10:24 | 2024-05-02 10:42 | 0:18 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | GPH Ispat Ckt | 2024-05-02 16:13 | 2024-05-02 17:06 | 0:53 | E/O | Kite hanging | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-2 | 2024-05-06 13:47 | 2024-05-06 16:27 | 2:40 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-06 15:06 | 2024-05-06 16:21 | 1:15 | T | Thunder & Storm | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-06 16:25 | 2024-05-06 16:25 | 0:00 | T | Thundering | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-06 16:30 | 2024-05-06 20:47 | 4:17 | E/O | Line Maintenance Work | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-05-06 15:06 | 2024-05-06 15:06 | 0:00 | T | Thunder & Storm | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-05-06 20:30 | 2024-05-06 20:49 | 0:19 | E/O | Line Maintenance Work | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2024-05-16 08:22 | 2024-05-16 08:51 | 0:29 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-01 | 2024-05-27 13:26 | 2024-05-27 13:39 | 0:13 | E/O | Removal of a long polyethene part from C.T at Bak-Shk Ckt-01 diameter. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-02 | 2024-05-04 00:48 | 2024-05-04 01:24 | 0:36 | T | thunderstorm. | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | AKSPL | 2024-05-24 05:57 | 2024-05-24 06:14 | 0:17 | T | O/c | 92 | 26.0667 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2024-05-02 14:03 | 2024-05-02 14:14 | 0:11 | T | i) Distance Trip ii) Distance B iii) Distance G | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-05-02 14:03 | 2024-05-02 14:52 | 0:49 | T | High storm | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-2 | 2024-05-04 13:06 | 2024-05-04 16:28 | 3:22 | E/O | Work at Hathazari end | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2024-05-06 13:35 | 2024-05-06 16:08 | 2:33 | T | Stormy rain | 6 | 15.3 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2024-05-11 09:47 | 2024-05-11 10:15 | 0:28 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2024-05-17 06:47 | 2024-05-17 12:49 | 6:02 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-05-06 13:35 | 2024-05-06 16:11 | 2:36 | T | Stormy rain | 4 | 10.4 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-05-27 07:02 | 2024-05-27 07:48 | 0:46 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-05-02 14:04 | 2024-05-02 14:49 | 0:45 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-05-03 02:49 | 2024-05-03 03:20 | 0:31 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-05-19 12:36 | 2024-05-19 12:50 | 0:14 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-01 | 2024-05-05 07:44 | 2024-05-05 17:07 | 9:23 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2024-05-05 07:44 | 2024-05-05 17:15 | 9:31 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-01 | 2024-05-02 14:35 | 2024-05-02 15:13 | 0:38 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Madunaghat Ckt-02 | 2024-05-02 14:35 | 2024-05-02 15:28 | 0:53 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-1 | 2024-05-04 00:33 | 2024-05-04 00:45 | 0:12 | T | Distance relay. Zone 1 | 120 | 24 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2024-05-04 04:48 | 2024-05-04 05:05 | 0:17 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2024-05-06 22:30 | 2024-05-06 22:49 | 0:19 | T | stormy weather. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 2024-05-02 03:51 | 2024-05-02 04:13 | 0:22 | T | Distance relay. Zone 1 | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 2024-05-04 00:35 | 2024-05-04 00:43 | 0:08 | T | Storm weather | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-2 | 2024-05-27 09:36 | 2024-05-27 18:32 | 8:56 | E/O | To reduce over voltage Level | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2024-05-27 09:37 | 2024-05-27 18:37 | 9:00 | E/O | To reduce over voltage level | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | BSRM CKT-2 | 2024-05-02 10:22 | 2024-05-02 10:41 | 0:19 | T | Zone-1 Trip | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | BSRM CKT-2 | 2024-05-02 16:13 | 2024-05-02 17:06 | 0:53 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | HATHAZARI-2 | 2024-05-02 14:04 | 2024-05-02 14:26 | 0:22 | T | Zone-1 Trip | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-05-08 07:10 | 2024-05-08 08:22 | 1:12 | T | Due to stormy rain. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-05-31 05:41 | 2024-05-31 06:12 | 0:31 | T | It was raining and lightning | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-05-24 08:42 | 2024-05-24 08:58 | 0:16 | T | Distance trip. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-05-25 08:44 | 2024-05-25 08:53 | 0:09 | T | There are no reason finding till now. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-05-25 09:21 | 2024-05-25 09:27 | 0:06 | T | There are no reason finding till now. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-05-25 10:00 | 2024-05-25 10:15 | 0:15 | T | No reason find told till now | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroaulia-02 | 2024-05-06 15:11 | 2024-05-06 16:07 | 0:56 | T | thundering | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2024-05-06 13:35 | 2024-05-06 16:11 | 2:36 | T | thundering | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2024-05-05 07:44 | 2024-05-05 08:45 | 1:01 | T | Tripped showing SIEMENS relays. | 4 | 4.0667 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2024-05-05 06:08 | 2024-05-05 07:08 | 1:00 | T | Tripped showing SIEMENS relays. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2024-05-05 07:44 | 2024-05-05 09:25 | 1:41 | T | Tripped showing SIEMENS relays. | 4 | 6.7333 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | Raojan-02 | 2024-05-04 00:32 | 2024-05-04 01:12 | 0:40 | T | Distance trip. | 0 | 0 | No interruption
KSRM 132/33kV Grid Sub-Station | Baraulia Feeder | 2024-05-27 16:43 | 2024-05-27 17:08 | 0:25 | T | Earth Fault & Over current | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-1(Rampur) | 2024-05-02 14:03 | 2024-05-02 14:31 | 0:28 | T | Directional Earth Fault | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-05-08 07:10 | 2024-05-08 08:22 | 1:12 | T | Heavy Storm occured. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-05-31 05:41 | 2024-05-31 06:12 | 0:31 | T | over current | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-MSML Line | 2024-05-13 10:15 | 2024-05-13 14:34 | 4:19 | E/O | Red hot at R-ph CT side clamp | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2024-05-02 14:03 | 2024-05-02 14:12 | 0:09 | T | Distance trip. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-1 | 2024-05-04 11:58 | 2024-05-04 15:00 | 3:02 | T | None | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-05-02 23:01 | 2024-05-03 11:34 | 12:33 | T | Distance trip. | 0 | 0 | No interruption
Modern Steel 132/11kV Grid Sub-Station | Modern Bakalia Ckt 2 | 2024-05-15 22:26 | 2024-05-16 09:07 | 10:41 | E/O | Red Hot is seen at the B phase of the 132kV Modern Bakalia lineâ€™s Clamp joint just between LA and CVT. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-05-03 04:33 | 2024-05-03 04:33 | 0:00 | T | Thundering and Raining | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-05-24 08:42 | 2024-05-24 08:59 | 0:17 | T | General trip, Zone-1, B ph Trip,ZCOM/WEI Trip, Distance 11.22km | 112 | 31.7333 | Power interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-05-25 09:22 | 2024-05-25 09:28 | 0:06 | T | Zone-1, B-PH Trip, ZCOM/WEI Trip,General trip. Distance: 6.314km | 115 | 11.5 | Power interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-05-25 10:01 | 2024-05-25 10:10 | 0:09 | T | Zone-1, B-PH Trip, ZCOM/WEI Trip,General trip. Distance: 6.264km | 114 | 17.1 | Power interruption
Shikalbaha 230/132kV Grid Sub-Station | Dohazari Ckt-2 | 2024-05-12 17:14 | 2024-05-12 17:47 | 0:33 | T | Distance trip. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2024-05-02 14:02 | 2024-05-02 14:25 | 0:23 | T | Distance trip. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-2 | 2024-05-08 13:20 | 2024-05-09 12:40 | 23:20 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-2 | 2024-05-09 13:45 | 2024-05-09 13:45 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2024-05-02 07:46 | 2024-05-02 23:45 | 15:59 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2024-05-03 11:40 | 2024-05-03 11:40 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Power Plant Feeder-01(GT) | 2024-05-21 21:47 | 2024-05-22 03:00 | 5:13 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Madunaghat Ckt-1 | 2024-05-04 11:58 | 2024-05-04 15:00 | 3:02 | T | Earth fault | 0 | 0 | No interruption
|  |  | Total : | 176:29 |  | Unserved Energy: |  | 146.9
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-05-04 00:39 | 2024-05-04 00:49 | 0:10 | T |  | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-05-05 19:35 | 2024-05-05 20:29 | 0:54 | T | Distance trip. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-05-05 02:45 | 2024-05-05 03:52 | 1:07 | T | Distance trip. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-05-18 11:09 | 2024-05-18 12:36 | 1:27 | T | Zone-01, R-phase and Y-phase | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-05-18 11:09 | 2024-05-18 11:10 | 0:01 | T | Zone-01, B-phase | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2024-05-05 20:31 | 2024-05-06 09:28 | 12:57 | T | Distance trip. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-1 | 2024-05-29 19:59 | 2024-05-30 22:41 | 26:42 | E/O | instruction by NLDC SDE. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2024-05-29 19:59 | 2024-05-30 22:41 | 26:42 | E/O | instruction by NLDC SDE. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 100MW(GT) Power Plant Incomer (T4) | 2024-05-27 14:18 | 2024-05-27 15:20 | 1:02 | T | Unknown | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 2024-05-18 11:55 | 2024-05-18 12:28 | 0:33 | T | Unknown | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2024-05-27 14:18 | 2024-05-28 10:10 | 19:52 | T | Unknown | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-1 | 2024-05-11 09:47 | 2024-05-11 10:06 | 0:19 | T | Tripping happened due to 132 KV busbar problem in feni grid. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 2024-05-06 13:35 | 2024-05-06 13:47 | 0:12 | T | Heavy rainfall with hailstones & stormy weather. | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-2 | 2024-05-11 09:47 | 2024-05-11 10:07 | 0:20 | T | 132 KV Bus Problem in Feni Grid | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-05-27 10:05 | 2024-05-28 08:51 | 22:46 | E/O | Ordered By NLDC | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2024-05-27 16:21 | 2024-05-27 16:42 | 0:21 | T | Tripped | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2024-05-27 16:46 | 2024-05-27 17:54 | 1:08 | T | Tripped | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-05-27 10:05 | 2024-05-28 09:08 | 23:03 | E/O | Ordered By NLCD | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2024-05-05 03:37 | 2024-05-05 03:58 | 0:21 | T | Distance trip. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-05-02 19:12 | 2024-05-02 19:25 | 0:13 | T | Distance trip. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-05-02 19:50 | 2024-05-02 20:47 | 0:57 | T | Distance trip. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-05-25 14:27 | 2024-05-26 00:44 | 10:17 | E/O | R-phase CVT remove and installation. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2024-05-05 03:35 | 2024-05-05 04:16 | 0:41 | T | Distance trip. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2024-05-02 05:30 | 2024-05-02 08:36 | 3:06 | E/O | Sparking remove(71 & 83 No Tower) | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-05-02 23:53 | 2024-05-03 00:12 | 0:19 | T | Distance trip. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2024-05-06 09:28 | 2024-05-06 11:17 | 1:49 | E/O | Remove Kite of the Conductor | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2024-05-29 10:56 | 2024-05-29 11:21 | 0:25 | E/O | Emergency maintenance work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-1 | 2024-05-06 13:00 | 2024-05-06 18:25 | 5:25 | T | SF6 Gas Reclosing Lockout, Compressor Trouble, Distance RT Zone-01 Trip, Distance RY SOTF Trip | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-05-06 12:20 | 2024-05-06 12:28 | 0:08 | T | Due to Heavy Rainfall and Stormy Weather Cause the Tripping | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Feni-Lanka HFO PS | 2024-05-06 13:01 | 2024-05-06 17:10 | 4:09 | T | Line Differential Protection Operated, Distance Protection Operated No M Volt on line | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2024-05-06 13:35 | 2024-05-06 15:46 | 2:11 | T | Distance RY Zone-01 Trip, A/R Lockout | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Chandpur CKT-1 | 2024-05-27 14:20 | 2024-05-27 14:27 | 0:07 | T | Ramel Cyclon (Chandpur grid s/s side fault) | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-05-25 14:26 | 2024-05-26 00:31 | 10:05 | E/O | Emergency work at Cumilla North end | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2024-05-04 23:45 | 2024-05-04 23:59 | 0:14 | T | Bad weather | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-05-05 14:59 | 2024-05-05 15:09 | 0:10 | T | Triped by fault | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-05-04 23:23 | 2024-05-04 23:55 | 0:32 | T | Bad Weather | 4 | 2.1333 | Power interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-05-17 22:50 | 2024-05-17 22:58 | 0:08 | T | Thunderstorm | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-05-04 23:23 | 2024-05-04 23:55 | 0:32 | T | BAD WEATHER | 4 | 2.1333 | Power interruption
Sylhet 132/33kV Grid Sub-Station | 150MW GT PS | 2024-05-04 19:43 | 2024-05-04 23:05 | 3:22 | T | Distance trip. | 94 | 316.4667 | Power interruption
Sylhet 132/33kV Grid Sub-Station | 20 MW PP | 2024-05-04 19:43 | 2024-05-05 08:58 | 13:15 | T | Distance trip. | 15 | 198.75 | Power interruption
Sylhet 132/33kV Grid Sub-Station | 75 MW ST PS | 2024-05-04 19:43 | 2024-05-04 20:36 | 0:53 | T | Distance trip. | 58 | 51.2333 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2024-05-27 21:15 | 2024-05-27 21:23 | 0:08 | T | Distance trip. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2024-05-28 00:18 | 2024-05-28 00:22 | 0:04 | T | Distance trip. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2024-05-28 00:43 | 2024-05-28 00:46 | 0:03 | T | Distance trip. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-05-04 23:23 | 2024-05-04 23:53 | 0:30 | T | Heavy Thundering | 8 | 4 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-05-19 06:27 | 2024-05-19 12:46 | 6:19 | T | Raining | 0 | 0 | No interruption
|  |  | Total : | 205:59 |  | Unserved Energy: |  | 574.7167
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-05-27 06:38 | 2024-05-28 14:40 | 32:02 | T | Distance trip. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Orion P/S Line | 2024-05-27 16:12 | 2024-05-28 07:06 | 14:54 | E/O | Recommend of ALDC Khulna | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-05-27 04:01 | 2024-05-27 04:13 | 0:12 | T | Bad weather, Cyclone Remal | 0 | 0 | Power interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-05-27 10:58 | 2024-05-27 10:58 | 0:00 | T | Cyclone Remal | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-05-27 11:24 | 2024-05-27 11:24 | 0:00 | T | Bad weather, Cyclone Rimal. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-05-28 12:32 | 2024-05-28 15:52 | 3:20 | T | Cyclone Remal. Bad weather. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Gopalgonj CKT-1 | 2024-05-06 16:07 | 2024-05-07 09:44 | 17:37 | T | Over voltage | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Gopalgonj CKT-2 | 2024-05-06 16:07 | 2024-05-07 09:44 | 17:37 | T | Over Voltage | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-01 | 2024-05-06 20:57 | 2024-05-06 21:38 | 0:41 | T | distance 34.089km, loop L1N 1976amp | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2024-05-06 21:07 | 2024-05-06 21:22 | 0:15 | T | Distance trip. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Bagerhat | 2024-05-06 18:47 | 2024-05-06 20:17 | 1:30 | T | A Phase To Earth, Distance Trip(Zone-1), Three Phase Trip. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Bagerhat | 2024-05-27 16:01 | 2024-05-27 16:06 | 0:05 | E/O | Instraction of aldc | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2024-05-27 16:07 | 2024-05-27 16:14 | 0:07 | E/O | Instraction of ALDC | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Rampal Ckt-2 | 2024-05-29 17:03 | 2024-05-29 20:18 | 3:15 | T | Distance trip. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2024-05-06 19:59 | 2024-05-06 20:29 | 0:30 | E/O | According to ALDC instruction. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2024-05-08 02:42 | 2024-05-08 02:54 | 0:12 | T | L1 & E | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | Bagerhat-Mongla Line-1 | 2024-05-27 14:58 | 2024-05-28 07:12 | 16:14 | E/O | Request from ALDC | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 1 | 2024-05-06 18:22 | 2024-05-06 20:17 | 1:55 | T | Distance Relay Trip. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Barishal-Pautakhali 132kV Line | 2024-05-27 06:25 | 2024-05-27 07:50 | 1:25 | T | Fall a tree in line | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Barishal-Pautakhali 132kV Line | 2024-05-27 14:20 | 2024-05-27 15:44 | 1:24 | E/O | Tree | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Gopalganj Line-2 | 2024-05-29 17:03 | 2024-05-29 20:21 | 3:18 | T | Z#1 ( 25.7KM & 26.04) B & Y phase operated | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-1 (L-1) | 2024-05-27 15:18 | 2024-05-27 22:59 | 7:41 | T | à¦˜à§‚à¦°à§à¦£à¦¿à¦à¦¡à¦¼ à¦°à¦¿à¦®à¦¾à¦² à¦à¦° à¦•à¦¾à¦°à¦¨à§‡ à¦­à§‹à¦²à§à¦Ÿà§‡à¦œ à¦•à¦¨à§à¦Ÿà§à¦°à§‹à¦² à¦•à¦°à¦¾à¦° à¦œà¦¨à§à¦¯ à¦à¦²à¦¡à¦¿à¦¸à¦¿ à¦–à§à¦²à¦¨à¦¾à¦° à¦¨à¦¿à¦°à§à¦¦à§‡à¦¶à§‡ à¦Ÿà§à¦°à¦¿à¦ª à¦•à¦°à¦¿à¦¯à¦¼à§‡ à¦°à¦¾à¦–à¦¾ à¦¹à¦¯à¦¼à¥¤ | 0 | 0 | No interruption
|  |  | Total : | 124:14 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-2 | 2024-05-02 17:30 | 2024-05-02 20:20 | 2:50 | E/O | For rectification/replacement of porcelain disc insulator caused due to lightning by Grid India. | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2024-05-27 15:23 | 2024-05-28 07:16 | 15:53 | E/O | As per ALDC instruction. | 0 | 0 | No interruption
BIPTC | Rajshahi-1 | 2024-05-27 16:11 | 2024-05-28 08:54 | 16:43 | E/O | instructed by NLDC | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2024-05-03 11:07 | 2024-05-03 11:36 | 0:29 | E/O | Only line breaker shutdown for sf6 alarm | 0 | 0 | No interruption
BIPTC | Rajshahi-2 | 2024-05-27 16:11 | 2024-05-28 08:54 | 16:43 | E/O | Instructed by NLDC. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2024-05-27 10:26 | 2024-05-28 08:59 | 22:33 | E/O | Oder of ALDC | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-1 | 2024-05-27 10:28 | 2024-05-28 09:02 | 22:34 | E/O | Oder of ALDC | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Rajbari 2 | 2024-05-26 16:51 | 2024-05-26 17:25 | 0:34 | T | Distance Relay Trip. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-22 06:57 | 2024-05-22 08:41 | 1:44 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-23 01:18 | 2024-05-23 17:57 | 16:39 | E/O | for bera power station problem | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-25 12:57 | 2024-05-25 13:16 | 0:19 | E/O | Ordered by ALDC Bagura | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-26 22:36 | 2024-05-26 22:52 | 0:16 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-27 11:09 | 2024-05-27 11:35 | 0:26 | T | None | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-29 21:06 | 2024-05-29 21:12 | 0:06 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 230/132 kV T02 Incoming | 2024-05-19 15:56 | 2024-05-19 16:15 | 0:19 | E/O | bushing CT sounds abnormal in associated breaker . | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | BEN-1 | 2024-05-08 01:37 | 2024-05-08 02:05 | 0:28 | T | None | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-1 | 2024-05-20 11:42 | 2024-05-20 23:35 | 11:53 | E/O | For stability test of Khulna end | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah (New)-Khulna (South) Ckt-1 | 2024-05-27 15:24 | 2024-05-28 07:19 | 15:55 | E/O | For Reducing the Voltage | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Jhenaidah Ckt. - 2 | 2024-05-09 15:07 | 2024-05-09 19:18 | 4:11 | E/O | 132 KV JHE - MAG CKT-2 Y PHASE CONDUCTOR ARMORING. | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | 132 KV Sirajgonj Ckt-2 | 2024-05-27 16:20 | 2024-05-27 19:35 | 3:15 | E/O | Removal of trees Sirajganj Line 1 | 0 | 0 | No interruption
|  |  | Total : | 153:50 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-2 | 2024-05-02 02:56 | 2024-05-02 03:01 | 0:05 | E/O | As per instruction of ALDC, Bogura. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Confidance UN-1 | 2024-05-19 23:51 | 2024-05-20 00:26 | 0:35 | T | Stormy Rain | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Confidance UN-2 | 2024-05-27 09:54 | 2024-05-27 10:56 | 1:02 | T | Over Voltage. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2024-05-19 23:51 | 2024-05-20 00:24 | 0:33 | T | Stormy Rain | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2024-05-27 15:58 | 2024-05-28 11:49 | 19:51 | E/O | Only CB Open . | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Rahanpur 400 KV CKT-01 | 2024-05-14 08:25 | 2024-05-14 21:43 | 13:18 | E/O | As per instruction by NLDC. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2024-05-12 23:42 | 2024-05-13 | 0:18 | T | Trieed showing Zone 3 , R,Y,B relays. | 56 | 16.8 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-02 | 2024-05-18 23:08 | 2024-05-18 23:42 | 0:34 | T | Rain and Thundering | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-1 | 2024-05-19 22:10 | 2024-05-20 13:47 | 15:37 | T | Trip, Due to Thunderstorm | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2024-05-12 08:38 | 2024-05-12 09:08 | 0:30 | T | Lightning | 44 | 22 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-SPPP Ckt-1 | 2024-05-04 19:07 | 2024-05-04 21:15 | 2:08 | T | SANTAHER PPP TRANSFORMER TAP CHANERS PROBLEM. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-05-04 10:45 | 2024-05-04 10:45 | 0:00 | E/O | None | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-2 | 2024-05-20 03:34 | 2024-05-20 04:30 | 0:56 | T | Thundering | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-1 | 2024-05-03 07:19 | 2024-05-03 07:48 | 0:29 | T | Distance Trip, A/R Block. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Lalmonirhat | 2024-05-06 06:02 | 2024-05-06 09:20 | 3:18 | E/O | Maintenance Work | 28 | 92.4 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2024-05-23 23:45 | 2024-05-24 00:27 | 0:42 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2024-05-23 23:34 | 2024-05-24 00:28 | 0:54 | T | Tripped showing Distance relay. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Ullapara -1 | 2024-05-27 16:12 | 2024-05-27 19:32 | 3:20 | T | the cyclone Romal, a tree fell on the line from a distance. | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Bogura -01 | 2024-05-27 14:30 | 2024-05-27 14:52 | 0:22 | E/O | Emergency Tree Trimming | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Panchagar CKT-1 | 2024-05-20 00:42 | 2024-05-20 01:03 | 0:21 | T | N/A | 40 | 14 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-2 | 2024-05-19 23:52 | 2024-05-20 00:18 | 0:26 | T | Tripped showing Distance Relay | 0 | 0 | No interruption
|  |  | Total : | 65:19 |  | Unserved Energy: |  | 145.2
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1495:19 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2024-05-23 08:16 | 2024-05-25 19:03 | 58:47 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2024-05-29 07:39 | 2024-05-30 19:34 | 35:55 | S/O | Reconducting work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-05-22 09:22 | 2024-05-22 17:32 | 8:10 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-05-14 06:52 | 2024-05-14 07:44 | 0:52 | S/O | ATR-3 Bus-2 DS maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 HT | 2024-05-28 09:52 | 2024-05-30 19:24 | 57:32 | S/O | Reconductring Work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 HT | 2024-05-22 09:23 | 2024-05-25 18:28 | 81:05 | S/O | 132kV side jack bus conductor change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer LT | 2024-05-10 10:43 | 2024-05-10 20:01 | 9:18 | S/O | Scheduled shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2024-05-01 10:59 | 2024-05-01 13:53 | 2:54 | S/O | Hot spot removing | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2024-05-14 06:55 | 2024-05-14 08:50 | 1:55 | S/O | ATR-3 Bus-2 DS maintenance (230kV Side) | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132kv Busbar-1 | 2024-05-31 08:00 | 2024-05-31 10:52 | 2:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2024-05-31 07:40 | 2024-05-31 13:14 | 5:34 | S/O | 132kv Ghorashal ckt-2 , the wire of bus isolator-1, Y-phase is broken | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 LT | 2024-05-11 14:41 | 2024-05-11 16:28 | 1:47 | S/O | Hyundai team inspection. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 HT | 2024-05-31 06:04 | 2024-05-31 12:41 | 6:37 | S/O | 132kv Ghorashal ckt-2 , the wire of bus isolator-1 is broken | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 HT | 2024-05-09 10:27 | 2024-05-09 12:22 | 1:55 | S/O | 33kv CT temperature high. | 10 | 19.1667 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-05-13 07:25 | 2024-05-13 10:39 | 3:14 | S/O | Pbs work | 20 | 64.6667 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2024-05-25 07:31 | 2024-05-25 15:49 | 8:18 | S/O | 33kv bus section D/S replace. | 75 | 622.5 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-05-13 08:04 | 2024-05-13 09:18 | 1:14 | S/O | 33kv Dhanbari red-hot maintenance | 25 | 30.8333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-05-25 07:31 | 2024-05-25 15:47 | 8:16 | S/O | 33kv bus section D/S replace. | 75 | 620 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-05-15 06:14 | 2024-05-15 09:52 | 3:38 | S/O | 33 kv bus DS high temperature maintenance. | 70 | 254.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2024-05-06 12:30 | 2024-05-06 14:27 | 1:57 | S/O | PBS work | 100 | 195 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-05-06 12:32 | 2024-05-06 14:28 | 1:56 | S/O | PBS work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-05-24 07:44 | 2024-05-24 09:47 | 2:03 | S/O | High temperature maintenance work at 33kV circuit breaker Y-phase source side. | 60 | 123 | Power interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2024-05-23 07:14 | 2024-05-23 13:57 | 6:43 | S/O | Dirana Test & Ten delta | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2024-05-14 07:24 | 2024-05-14 08:57 | 1:33 | S/O | Red hot | 25 | 38.75 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2024-05-22 06:57 | 2024-05-22 07:32 | 0:35 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2024-05-14 05:34 | 2024-05-14 07:20 | 1:46 | S/O | Red hot maintenance | 35 | 61.8333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2024-05-16 12:30 | 2024-05-16 12:56 | 0:26 | S/O | Red hot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-05-01 09:26 | 2024-05-01 11:06 | 1:40 | S/O | Corrective maintenance of WTI & OTI | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2024-05-16 10:19 | 2024-05-16 11:34 | 1:15 | S/O | Red hot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-05-01 11:13 | 2024-05-01 12:25 | 1:12 | S/O | Corrective maintenance of WTI &OTI | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-05-16 07:04 | 2024-05-16 10:06 | 3:02 | S/O | Red hot Maintenance. | 16 | 48.5333 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) HT | 2024-05-26 21:06 | 2024-05-26 22:30 | 1:24 | S/O | PBS Feeder Repair | 15 | 21 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Bus A | 2024-05-11 08:41 | 2024-05-11 10:26 | 1:45 | S/O | For red hot maintenance works of 132kV A-Bus DS (401S) of T-3 (424T). | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2024-05-11 08:33 | 2024-05-11 10:45 | 2:12 | S/O | For red hot maintenance works of 132kV A-Bus DS (401S) of T-3 (424T). | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-05-10 07:59 | 2024-05-10 09:10 | 1:11 | S/O | G2G project work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-05-26 10:01 | 2024-05-26 17:21 | 7:20 | S/O | Installation of T-4 bay | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-05-30 10:34 | 2024-05-30 19:22 | 8:48 | S/O | For T-4 transformer installation work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-05-10 10:03 | 2024-05-10 14:15 | 4:12 | S/O | L-37 dismalting forT-4 bay installation work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-05-29 09:27 | 2024-05-29 11:08 | 1:41 | S/O | For Red hot maintenance of DPBS-1 & DPBS-3. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-05-01 09:00 | 2024-05-01 13:03 | 4:03 | S/O | Hot Spot Maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-05-18 06:39 | 2024-05-18 10:37 | 3:58 | S/O | hot spot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-05-24 12:52 | 2024-05-24 18:03 | 5:11 | D/W | Tr-4 tower beam Commissioning | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2024-05-01 07:08 | 2024-05-01 08:27 | 1:19 | S/O | Hotspot maintenance. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-05-01 09:07 | 2024-05-01 13:18 | 4:11 | S/O | Hot Spot Maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-2 HT | 2024-05-25 10:37 | 2024-05-25 13:55 | 3:18 | S/O | Tr-2 main Bus-2 Isolator 411 replacement work. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-05-28 21:14 | 2024-05-28 23:32 | 2:18 | S/O | For 33kV bushing measurement. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-05-21 11:55 | 2024-05-21 18:01 | 6:06 | D/W | Transformer-4 bay equipment installing work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-05-22 11:25 | 2024-05-23 19:00 | 31:35 | S/O | project work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-05-25 10:48 | 2024-05-25 13:45 | 2:57 | S/O | Maintenance work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-05-15 08:16 | 2024-05-15 15:52 | 7:36 | S/O | fire wall Works | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-05-16 07:28 | 2024-05-16 15:40 | 8:12 | D/W | project work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2024-05-15 08:14 | 2024-05-15 08:14 | 0:00 | S/O | Fire wall Works | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2024-05-24 08:12 | 2024-05-24 10:16 | 2:04 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 435:22 |  | Unserved Energy: |  | 2099.6167
Dhaka (South) Grid Circle : | [9 empty] | 39.3333
Dhaka University 132/33kV Grid Sub-Station | GT-2 LT | 2024-05-20 08:58 | 2024-05-20 09:08 | 0:10 | S/O | Gas Refilling | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Bus Coupler | 2024-05-03 09:55 | 2024-05-03 20:50 | 10:55 | S/O | Project work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-1 | 2024-05-18 10:43 | 2024-05-18 21:10 | 10:27 | S/O | 132kV Busbar protection works by Era construction. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Main Bus Sec-2 | 2024-05-19 10:34 | 2024-05-19 21:02 | 10:28 | D/W | Busbar Protection work by Ira Construction. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-1 | 2024-05-03 09:54 | 2024-05-03 19:58 | 10:04 | S/O | Project work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-1 | 2024-05-12 13:29 | 2024-05-12 15:55 | 2:26 | D/W | Bus Bar Protection System Upgradation Work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 132kV Reserve Bus Sec-2 | 2024-05-03 09:54 | 2024-05-03 19:58 | 10:04 | S/O | Project work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-1 HT | 2024-05-16 09:53 | 2024-05-16 21:27 | 11:34 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-2 HT | 2024-05-07 09:25 | 2024-05-07 21:03 | 11:38 | D/W | Busbar Protection Project work by Era Construction. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 HT | 2024-05-09 09:28 | 2024-05-09 19:35 | 10:07 | D/W | Bas bar Protection work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-2 | 2024-05-15 12:28 | 2024-05-15 19:46 | 7:18 | S/O | Bus PT changing work. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 HT | 2024-05-16 10:30 | 2024-05-16 12:36 | 2:06 | S/O | Temperature high at LT bushing. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 HT | 2024-05-16 15:01 | 2024-05-16 17:54 | 2:53 | S/O | 33 kv CB and main bus isolator temperature rise. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 HT | 2024-05-12 10:22 | 2024-05-12 22:02 | 11:40 | S/O | 132kV bay commissioning purpose | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 HT | 2024-05-13 15:33 | 2024-05-13 17:32 | 1:59 | S/O | 132kV side bushing to system connection. | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-05-10 08:35 | 2024-05-10 11:55 | 3:20 | S/O | Maintenance of 33kv bus for red hot in 33kv bus cupler by PBS. | 33 | 110 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-05-10 08:35 | 2024-05-10 11:55 | 3:20 | S/O | Maintenance of 33kv bus for red hot in 33kv bus cupler by PBS. | 33 | 110 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | 132 kV Main Bus-1 | 2024-05-09 12:35 | 2024-05-10 17:26 | 28:51 | S/O | Bus Coupler commissioning work | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 LT | 2024-05-03 14:42 | 2024-05-03 15:20 | 0:38 | S/O | à¦Ÿà¦¿-à§§, à§©à§©à¦•à§‡à¦­à¦¿ à¦‡à¦¨à¦•à¦¾à¦®à¦¿à¦‚ à¦¸à¦¿à¦Ÿà¦¿(R-Phase) à¦à¦° à¦²à§à¦ª à¦Ÿà¦¾à¦°à§à¦®à¦¿à¦¨à¦¾à¦² à¦ªà§Ÿà§‡à¦¨à§à¦Ÿà§‡ Oil Leakage Maintenance Work . | 40 | 25.3333 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 HT | 2024-05-25 07:16 | 2024-05-25 10:28 | 3:12 | S/O | Due to 33kv tr-1 Bus red hot maintenance by pbs dhaka-2 | 14 | 44.8 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 HT | 2024-05-28 09:42 | 2024-05-28 10:30 | 0:48 | S/O | 33kV feeder source DS redhot maintenance by Dhaka PBS-02. | 4 | 3.2 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 LT | 2024-05-05 06:54 | 2024-05-05 07:30 | 0:36 | S/O | Redhot maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2024-05-29 05:59 | 2024-05-29 07:50 | 1:51 | D/W | New auxilliary coonection | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-05-01 07:24 | 2024-05-01 18:11 | 10:47 | D/W | Auto Tx-04 all test | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | NLDC Trafo HT | 2024-05-01 07:25 | 2024-05-01 19:20 | 11:55 | D/W | Due to project work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2024-05-11 09:28 | 2024-05-11 09:28 | 0:00 | S/O | Bus coupler relay problem | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 HT | 2024-05-13 17:53 | 2024-05-13 18:37 | 0:44 | S/O | 33KV feeder fault at 33 KV side ,Aman cement feeder emergency maintenance purpose shutdown taken | 35 | 25.6667 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 LT | 2024-05-28 20:58 | 2024-05-28 23:40 | 2:42 | S/O | 33Kv Bus-A maintenance work by PBS | 20 | 54 | Power interruption
|  |  | Total : | 182:33 |  | Unserved Energy: |  | 373
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2024-05-24 21:10 | 2024-05-24 22:20 | 1:10 | S/O | Red hot maintenance works by PBS | 36 | 42 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2024-05-10 03:11 | 2024-05-10 03:11 | 0:00 | D/W | Transformer Commissioning | 56 | 0 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | Main Bus | 2024-05-03 05:37 | 2024-05-03 08:44 | 3:07 | D/W | Conductor connection in mainbus | 120 | 374 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | Main Bus | 2024-05-10 08:59 | 2024-05-10 12:41 | 3:42 | D/W | Due to project work | 80 | 296 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | T3 HT | 2024-05-10 03:26 | 2024-05-10 16:24 | 12:58 | D/W | Due to project work | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | Transformer-01(D05) HT | 2024-05-31 09:27 | 2024-05-31 11:42 | 2:15 | D/W | Removal of Ground wire for GPH 2DT25 Tower dismantling work | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | 230KV MAIN BUS-02 | 2024-05-18 07:30 | 2024-05-18 14:02 | 6:32 | S/O | Hot spot maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-01 HT | 2024-05-01 15:30 | 2024-05-01 16:58 | 1:28 | S/O | oil leakage check | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 HT | 2024-05-01 08:37 | 2024-05-01 09:39 | 1:02 | S/O | oil leakage check | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-03 HT | 2024-05-01 09:41 | 2024-05-01 10:37 | 0:56 | S/O | oil leakage check | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-03 HT | 2024-05-25 07:01 | 2024-05-25 13:22 | 6:21 | S/O | Hotspot maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-04 HT | 2024-05-01 10:43 | 2024-05-01 15:30 | 4:47 | S/O | oil leakage check | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-04 HT | 2024-05-18 12:45 | 2024-05-18 14:02 | 1:17 | S/O | Hot spot maintenance. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 HT | 2024-05-01 10:02 | 2024-05-01 11:23 | 1:21 | S/O | oil leakage check | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2024-05-07 17:28 | 2024-05-07 18:12 | 0:44 | S/O | Bpdb 33 KV feeder (incomer-1) red hot (Y-phase) maintenance | 16 | 11.7333 | Power interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) HT | 2024-05-01 05:39 | 2024-05-01 10:13 | 4:34 | D/W | Transfer Bus Isolator Dismantling | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) LT | 2024-05-01 10:15 | 2024-05-01 12:26 | 2:11 | D/W | Transfer Bus Dismantling under the ESPNCA Project | 30 | 65.5 | Power interruption
Khulshi 132/33kV Grid Sub-Station | Main Bus | 2024-05-16 05:39 | 2024-05-16 07:08 | 1:29 | S/O | Red Hot at Bus side | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Main Bus | 2024-05-24 06:00 | 2024-05-24 09:29 | 3:29 | D/W | Due to project work | 20 | 69.6667 | Power interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-02 | 2024-05-03 10:43 | 2024-05-03 16:38 | 5:55 | D/W | p/w | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | TR-1 LT | 2024-05-08 10:15 | 2024-05-08 11:45 | 1:30 | S/O | Tighten LT Bushing Nut-Bolt | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Bus-1 | 2024-05-17 06:23 | 2024-05-17 09:47 | 3:24 | D/W | G2G project work on bus coupler bay circuit breaker. | 43 | 146.2 | Power interruption
Shahmirpur 132/33kV Grid Sub-Station | Bus-1 | 2024-05-24 06:48 | 2024-05-24 09:30 | 2:42 | D/W | Due to project work | 45 | 121.5 | Power interruption
Shahmirpur 132/33kV Grid Sub-Station | Bus-1 | 2024-05-31 08:29 | 2024-05-31 11:20 | 2:51 | D/W | Due to project work | 40 | 114 | Power interruption
|  |  | Total : | 75:45 |  |  |  | 1240.6
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | 401T HT | 2024-05-20 07:04 | 2024-05-20 09:39 | 2:35 | S/O | Hot spot maintenance. | 50 | 129.1667 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-05-06 15:50 | 2024-05-06 16:56 | 1:06 | S/O | After OLTC Buchhol TZ trip, Shutdown taken by AE Chandpur Grid. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-05-30 16:16 | 2024-05-30 17:46 | 1:30 | S/O | 33kv bus coupler -1 ds red hot remove | 28 | 42 | Power interruption
Chandpur 132/33kV Grid Sub-Station | Bus-B | 2024-05-18 06:32 | 2024-05-18 14:56 | 8:24 | S/O | High temperature remove | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-05-17 09:18 | 2024-05-17 11:55 | 2:37 | S/O | 33KV Balutopa feeder redhot remove, sankarpur feeder loop connection | 30 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2024-05-25 13:32 | 2024-05-25 16:43 | 3:11 | S/O | Due to maint.work | 60 | 191 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2024-05-04 17:13 | 2024-05-04 18:28 | 1:15 | S/O | Due to maint.work | 10 | 12.5 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 HT | 2024-05-01 12:21 | 2024-05-01 12:22 | 0:01 | S/O | Shift from BD(Bus-ii) to Tripura (Bus-i) | 20 | 0.33333 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 LT | 2024-05-28 14:44 | 2024-05-28 15:23 | 0:39 | D/W | Project work | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-05-15 06:57 | 2024-05-15 09:53 | 2:56 | S/O | 132 kv CT & 33 kv CT terminal clamp connector Hot-spot Maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-05-14 06:57 | 2024-05-14 09:09 | 2:12 | S/O | 132 kv CT (B Phase) & 33 kv CT(B-Phase) terminal clamp connector Hot-spot Maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-05-31 06:25 | 2024-05-31 10:33 | 4:08 | S/O | 33 kV Bus section-2 S/D Taken by REB/PBS-Feni for PBS Feeder Red Hot Maintenance work | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2024-05-13 09:38 | 2024-05-13 10:48 | 1:10 | S/O | Red hot maintenance by PBS. In PBS feeder-1. | 24 | 28 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2024-05-23 07:46 | 2024-05-23 08:37 | 0:51 | S/O | completion of hot spot maintenance | 20 | 17 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 HT | 2024-05-23 06:18 | 2024-05-23 07:38 | 1:20 | S/O | hot spot maintenance | 20 | 26.6667 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2024-05-24 23:27 | 2024-05-25 05:40 | 6:13 | S/O | Tr-02 132 Kv Side B Phase DS Loop Red hot Maintenece | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2024-05-06 21:12 | 2024-05-06 21:55 | 0:43 | S/O | Tr-04 33 Kv Pdb Emergency bus Shutdown for red hot Maintenece work | 30 | 21.5 | Power interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Bus Bar 132 KV -2 | 2024-05-08 10:32 | 2024-05-08 15:47 | 5:15 | D/W | NLDC Witness, | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 HT | 2024-05-07 10:26 | 2024-05-07 15:19 | 4:53 | D/W | NLDC Witness | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 HT | 2024-05-04 07:42 | 2024-05-04 11:03 | 3:21 | S/O | 33 kv bus section 2 maintenance work for PDB | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-2 HT | 2024-05-09 10:12 | 2024-05-09 15:48 | 5:36 | D/W | NLDC witness for TR-2 | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2024-05-01 23:08 | 2024-05-02 00:04 | 0:56 | D/W | 33 KV Boteshwar feeder Red Hot Maintenance work Purpose. | 0 | 0 | No interruption
|  |  | Total : | 60:52 |  | Unserved Energy: |  | 468.1667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2024-05-09 06:42 | 2024-05-09 09:30 | 2:48 | S/O | 33kV Bus Bar riser conductor replace work by Bagerhat PBS. | 28 | 78.4 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2024-05-07 12:28 | 2024-05-07 14:01 | 1:33 | S/O | Pbs work | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-05-04 06:31 | 2024-05-04 09:56 | 3:25 | S/O | Bypass Insulatot & Operating Finger Maintenance of Nobogram 33 Feeder | 22 | 75.1667 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-05-15 07:28 | 2024-05-15 12:32 | 5:04 | S/O | PBS-2 Tetultola maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Bus-01 | 2024-05-07 18:09 | 2024-05-17 17:46 | 239:37 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Bus-01 | 2024-05-18 08:56 | 2024-05-18 18:29 | 9:33 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 HT | 2024-05-18 08:56 | 2024-05-18 18:24 | 9:28 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 HT | 2024-05-23 14:55 | 2024-05-23 16:23 | 1:28 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-05-16 08:52 | 2024-05-16 21:08 | 12:16 | S/O | Fire fighting Commissioning | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-01 LT | 2024-05-17 07:58 | 2024-05-17 17:46 | 9:48 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 HT | 2024-05-05 12:18 | 2024-05-05 21:12 | 8:54 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 HT | 2024-05-13 08:42 | 2024-05-13 21:17 | 12:35 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 HT | 2024-05-23 16:26 | 2024-05-23 16:59 | 0:33 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-05-06 09:06 | 2024-05-06 19:31 | 10:25 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-05-07 09:23 | 2024-05-07 19:14 | 9:51 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-05-12 09:41 | 2024-05-12 21:05 | 11:24 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-05-14 10:20 | 2024-05-14 19:57 | 9:37 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2024-05-15 08:35 | 2024-05-15 21:05 | 12:30 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2024-05-19 08:28 | 2024-05-19 20:03 | 11:35 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2024-05-20 08:51 | 2024-05-20 18:29 | 9:38 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 HT | 2024-05-23 17:16 | 2024-05-23 17:35 | 0:19 | D/W | Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-03 LT | 2024-05-21 08:46 | 2024-05-21 20:23 | 11:37 | S/O | Due to maint.work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-05-18 10:07 | 2024-05-18 22:01 | 11:54 | D/W | Due to GIS Bay Work by 800MW NWPGCL Project | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-05-20 11:48 | 2024-05-20 23:24 | 11:36 | D/W | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-05-21 10:23 | 2024-05-23 00:28 | 38:05 | D/W | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-05-23 10:55 | 2024-05-23 22:07 | 11:12 | D/W | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-05-17 09:59 | 2024-05-17 22:48 | 12:49 | D/W | Project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-2 HT | 2024-05-18 09:57 | 2024-05-18 16:41 | 6:44 | D/W | Due to GIS Bay Work by 800MW NWPGCL Project | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2024-05-02 06:18 | 2024-05-02 09:26 | 3:08 | S/O | 33 kv pbs Shibchar feeder bus ds red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 499:26 |  | Unserved Energy : |  | 153.5667
HVDC Grid Circle
Baghabari 230/132kV Grid Sub-Station | T-1 HT | 2024-05-17 06:31 | 2024-05-17 08:45 | 2:14 | S/O | Due to maint.work | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2024-05-09 07:48 | 2024-05-09 09:52 | 2:04 | S/O | Red hot maintenance | 30 | 62 | Power interruption
Kushtia 132/33kV Grid Sub-Station | 132 KV Bus-A | 2024-05-30 07:00 | 2024-05-30 18:49 | 11:49 | D/W | T-3 transformer's 132 kv loop connect with 132 kv bus bar | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | 132 KV Bus-B | 2024-05-31 09:45 | 2024-05-31 15:36 | 5:51 | D/W | Conductor loop connecting between BUS and DS | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-1 HT | 2024-05-05 10:05 | 2024-05-05 10:45 | 0:40 | S/O | Due to maint.work | 40 | 26.6667 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 HT | 2024-05-31 08:20 | 2024-05-31 12:03 | 3:43 | S/O | Due to maint.work | 30 | 111.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-2 HT | 2024-05-05 10:06 | 2024-05-05 10:46 | 0:40 | S/O | Due to maint.work | 20 | 13.3333 | Power interruption
Ruppur 132/11kV Grid Sub-Station | TR-02 HT | 2024-05-14 11:20 | 2024-05-21 17:57 | 174:37 | D/W | CB replacing 11 kv side | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | TR-02 LT | 2024-05-27 11:03 | 2024-05-27 15:48 | 4:45 | D/W | TR-2 of 11kv section maintenance by NESCO | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer -1 LT | 2024-05-25 09:23 | 2024-05-25 11:32 | 2:09 | D/W | 132 kV T-1 BKR SF6 Gas Leakage Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 208:32 |  | Unserved Energy : |  | 213.5
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T HT | 2024-05-17 06:27 | 2024-05-17 08:54 | 2:27 | S/O | Maintenance work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T LT | 2024-05-10 06:20 | 2024-05-10 12:34 | 6:14 | S/O | Maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-05-31 07:07 | 2024-05-31 09:30 | 2:23 | S/O | 33 Bus 1 Red Hot. | 35 | 83.4167 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2024-05-14 07:06 | 2024-05-14 08:27 | 1:21 | S/O | 132kv CT Red hot | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2024-05-18 07:32 | 2024-05-18 09:07 | 1:35 | S/O | Red Hot Remove Work. | 15 | 23.75 | Power interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 1 | 2024-05-04 07:23 | 2024-05-04 18:36 | 11:13 | S/O | project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 132KV Main 2 | 2024-05-06 07:33 | 2024-05-07 11:20 | 27:47 | S/O | project work for transformer T04 commissioning. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2024-05-04 07:54 | 2024-05-04 18:22 | 10:28 | S/O | project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-05-05 07:36 | 2024-05-05 18:45 | 11:09 | S/O | project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-05-07 16:10 | 2024-05-07 17:37 | 1:27 | D/W | project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-05-31 09:35 | 2024-05-31 21:58 | 12:23 | D/W | 230kV Bogura (W) Ckt.. 1 & Ckt.-2 Commissioning work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2024-05-20 07:43 | 2024-05-20 15:45 | 8:02 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-04 HT | 2024-05-31 11:20 | 2024-05-31 18:38 | 7:18 | D/W | 230kV Bogura(W) Ckt.-1 & Ckt.-2 Commissioning work. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | 230 KV BUS-A (A1-A2) | 2024-05-29 13:25 | 2024-05-29 18:48 | 5:23 | D/W | Due to DFDR commissioning | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | 230 KV BUS-B (B1-B2) | 2024-05-28 10:38 | 2024-05-30 17:40 | 55:02 | D/W | DFDR Commissioning For 230 Kv B-1 Bus. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | 400 KV BUS-01 | 2024-05-26 14:04 | 2024-05-26 17:49 | 3:45 | D/W | DFDR Commissioning | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | 400 KV BUS-02 | 2024-05-26 10:23 | 2024-05-26 13:53 | 3:30 | D/W | DFDR commissioning. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-01 HT | 2024-05-27 08:58 | 2024-05-27 19:30 | 10:32 | D/W | DFDR Commisioning work | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-01 HT | 2024-05-29 10:33 | 2024-05-29 18:50 | 8:17 | D/W | Due to DFDR and fire hydrant commissioning | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-02 HT | 2024-05-28 10:17 | 2024-05-28 18:24 | 8:07 | D/W | DFDR Commissioning For ATR-02 | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-03 HT | 2024-05-22 09:54 | 2024-05-22 21:03 | 11:09 | D/W | DFDR commissioning. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2024-05-14 00:13 | 2024-05-14 01:01 | 0:48 | S/O | Red hot maintenance | 3 | 2.4 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2024-05-14 08:40 | 2024-05-17 17:00 | 80:20 | S/O | Oil centrifuge | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-05-10 06:24 | 2024-05-10 08:03 | 1:39 | S/O | Corrective Maintenance of T-1, kv Bay | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-05-10 08:07 | 2024-05-10 13:32 | 5:25 | S/O | Corrective Maintenance of T-2, 33kv Bay | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) HT | 2024-05-31 07:19 | 2024-05-31 07:19 | 0:00 | D/W | T-4 upgradation work | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) LT | 2024-05-31 07:18 | 2024-05-31 07:18 | 0:00 | D/W | T-4 upgradation work | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) HT | 2024-05-22 07:25 | 2024-05-22 08:20 | 0:55 | S/O | Maintenance work. | 20 | 18.3333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) LT | 2024-05-10 07:35 | 2024-05-10 10:10 | 2:35 | S/O | Maintenance work. | 10 | 25.8333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) LT | 2024-05-21 07:09 | 2024-05-21 09:25 | 2:16 | S/O | due to pbs 33kv Bus DS Red Hot under T2-33kv Bus | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2024-05-10 07:35 | 2024-05-10 10:13 | 2:38 | S/O | Maintenance work. | 20 | 52.6667 | Power interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 LT | 2024-05-08 08:16 | 2024-05-08 18:40 | 10:24 | D/W | DFDR&SCADA Work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 LT | 2024-05-09 08:46 | 2024-05-09 15:51 | 7:05 | D/W | SUS witness | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-01 LT | 2024-05-21 09:11 | 2024-05-21 16:10 | 6:59 | D/W | DIRANA (DFR) TEST | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-05-11 08:50 | 2024-05-11 16:53 | 8:03 | D/W | SCADA & DFDR Pre Commissioning work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | AT-02 LT | 2024-05-12 08:28 | 2024-05-12 16:06 | 7:38 | D/W | DFDR witness | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | HV 400 KV BUS | 2024-05-16 09:02 | 2024-05-16 16:40 | 7:38 | S/O | SAS,DFDR Pre Commissioning work | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2024-05-03 07:02 | 2024-05-03 09:42 | 2:40 | S/O | Maintenance work at 33 kv CT connector(R&Y Phase). | 20 | 53.3333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | Main Bus | 2024-05-24 05:54 | 2024-05-24 08:55 | 3:01 | D/W | 68 MW Soler new 132kv bus is connected 132 KV main bus. | 100 | 301.6667 | Power interruption
|  |  | Total : | 359:36 |  | Unserved Energy : |  | 561.4
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1822:06 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:May 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kaliakoir-01 | 2024-05-08 08:36 | 2024-05-08 20:09 | 11:33 | S/O | OPGW Repair(Armer) | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-02 | 2024-05-10 06:02 | 2024-05-10 10:23 | 4:21 | D/W | Due to project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-05-11 09:29 | 2024-05-11 17:05 | 7:36 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-05-12 08:13 | 2024-05-12 17:44 | 9:31 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2024-05-14 09:19 | 2024-05-14 16:30 | 7:11 | S/O | NLDC Instruction. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2024-05-15 09:25 | 2024-05-15 16:31 | 7:06 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2024-05-16 09:14 | 2024-05-16 16:33 | 7:19 | S/O | As per instruction of NLDC | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-05-16 10:22 | 2024-05-16 18:18 | 7:56 | D/W | Circuit connection to BR Powergen end | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 02 | 2024-05-16 10:24 | 2024-05-23 12:41 | 170:17 | D/W | Circuit connection to BR Powergen end | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2024-05-27 17:43 | 2024-05-28 08:59 | 15:16 | S/O | Due to high voltage(147kv) with the permission of NLDC,SDE. | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-1 | 2024-05-10 13:40 | 2024-05-10 21:05 | 7:25 | D/W | Due to project work | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-05-01 07:07 | 2024-05-01 18:48 | 11:41 | D/W | Stringing work. | 35 | 150.5 | Power interruption 07:07 to 11:25
Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Ghorashal ckt-2 | 2024-05-10 06:24 | 2024-05-10 13:32 | 7:08 | D/W | LILO Work by project. | 20 | 142.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2024-05-10 07:58 | 2024-05-10 11:55 | 3:57 | S/O | Due to maint.work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-2 | 2024-05-10 07:59 | 2024-05-10 11:56 | 3:57 | S/O | Due to maint.work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -1 | 2024-05-24 06:47 | 2024-05-24 18:08 | 11:21 | S/O | BY NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Aminbazar -2 | 2024-05-24 06:48 | 2024-05-24 18:08 | 11:20 | S/O | By NLDC | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana1 | 2024-05-20 09:28 | 2024-05-20 12:05 | 2:37 | S/O | OPGW Wire maintenance at line. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tongi-2 | 2024-05-08 14:02 | 2024-05-08 20:08 | 6:06 | S/O | By NLDC | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-05-14 07:08 | 2024-05-14 17:57 | 10:49 | S/O | cross arm painting and jumper replacement | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2024-05-15 07:51 | 2024-05-15 17:50 | 9:59 | S/O | For maintenance work. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-05-16 07:31 | 2024-05-16 18:16 | 10:45 | S/O | Cross Arm Painting & Isolator Maintenance Work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-02 | 2024-05-17 07:44 | 2024-05-17 16:16 | 8:32 | S/O | Due to maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-05-02 09:08 | 2024-05-02 11:14 | 2:06 | S/O | Fixing high temperature at Ashuganj-2, B-Bus D/S, Y-Phase | 50 | 105 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-05-16 07:05 | 2024-05-16 08:57 | 1:52 | S/O | Red hot Maintenance. | 16 | 29.8667 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2024-05-16 12:30 | 2024-05-16 14:00 | 1:30 | S/O | Red hot maintenance | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-05-01 05:19 | 2024-05-01 07:52 | 2:33 | S/O | Hotspot maintenance work on Y Phase Line DS | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-05-03 05:52 | 2024-05-04 14:31 | 32:39 | S/O | Tower no-2 Replacement work on Amin Bazar Ckt-1. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-05-11 07:28 | 2024-05-11 07:28 | 0:00 | S/O | Deadline checking due to heavy Thunderstorm | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2024-05-11 07:29 | 2024-05-11 09:17 | 1:48 | S/O | Deadline checking due to heavy Thunderstorm | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2024-05-01 08:29 | 2024-05-02 03:05 | 18:36 | S/O | Tower No-2 of Mirpur-Aminbazar Line replacement work. (Ckt-2 shifting) | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakair-ckt-2A(E08) | 2024-05-10 05:59 | 2024-05-10 14:14 | 8:15 | D/W | Due to project work | 10 | 82.5 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakoir ckt-2B(E-09) | 2024-05-10 05:59 | 2024-05-10 14:13 | 8:14 | D/W | Due to project work | 10 | 82.3333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2024-05-11 08:34 | 2024-05-11 10:27 | 1:53 | S/O | For red hot maintenance works of 132kV A-Bus DS (401S) of T-3 (424T). | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2024-05-28 10:16 | 2024-05-28 13:10 | 2:54 | S/O | Due to maint.work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-05-01 09:30 | 2024-05-01 13:42 | 4:12 | S/O | Hot Spot Maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-05-18 06:44 | 2024-05-18 11:11 | 4:27 | S/O | hot spot maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-02 08:53 | 2024-05-02 16:30 | 7:37 | D/W | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-05 09:15 | 2024-05-05 17:32 | 8:17 | D/W | AR Modificaton | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-06 09:41 | 2024-05-06 13:35 | 3:54 | D/W | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-07 09:27 | 2024-05-07 17:21 | 7:54 | D/W | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-08 09:05 | 2024-05-08 16:28 | 7:23 | D/W | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-11 09:31 | 2024-05-11 17:05 | 7:34 | S/O | project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-05-12 08:38 | 2024-05-12 17:56 | 9:18 | S/O | Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-13 09:30 | 2024-05-13 16:41 | 7:11 | S/O | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-14 09:43 | 2024-05-14 16:32 | 6:49 | D/W | Project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-15 09:47 | 2024-05-15 16:31 | 6:44 | D/W | Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-16 09:51 | 2024-05-16 16:32 | 6:41 | S/O | Project S/D | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-19 09:41 | 2024-05-19 17:57 | 8:16 | S/O | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-22 10:07 | 2024-05-22 17:24 | 7:17 | D/W | AR Modification | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2024-05-23 09:29 | 2024-05-23 17:25 | 7:56 | S/O | Project Work | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2024-05-10 05:58 | 2024-05-10 13:12 | 7:14 | D/W | Schedule S/D for project work. | 80 | 578.6667 | Power interruption
|  |  | Total : | 554:47 |  | Unserved Energy: |  | 1171.5333
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-20 09:28 | 2024-05-20 18:58 | 9:30 | S/O | Tower erection work at Madangonj to Fatullah line. | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-22 13:03 | 2024-05-22 18:03 | 5:00 | D/W | Tower erection work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-23 07:30 | 2024-05-23 18:04 | 10:34 | D/W | Tower Erection work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-24 07:37 | 2024-05-24 17:57 | 10:20 | S/O | Shutdown for Erection work by Shyampur 230KV Substation | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-25 08:16 | 2024-05-25 18:36 | 10:20 | D/W | project work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-26 14:19 | 2024-05-26 17:11 | 2:52 | S/O | Erection work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-30 06:41 | 2024-05-30 19:51 | 13:10 | S/O | Due to maint.work | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-05-31 07:08 | 2024-05-31 20:51 | 13:43 | D/W | Erection Work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2024-05-06 11:12 | 2024-05-06 19:09 | 7:57 | S/O | Busbar Protection work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2024-05-03 14:27 | 2024-05-03 19:03 | 4:36 | S/O | High temperature junction point maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2024-05-03 06:14 | 2024-05-03 14:13 | 7:59 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-05-09 07:44 | 2024-05-09 12:18 | 4:34 | S/O | Removing polymer items from phases. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2024-05-14 09:34 | 2024-05-15 12:13 | 26:39 | S/O | For Bus bar Protection Work by ERA Construction. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2024-05-19 10:56 | 2024-05-19 14:51 | 3:55 | S/O | Isolator finger change. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-03 10:03 | 2024-05-03 18:29 | 8:26 | S/O | Another side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-05-10 09:53 | 2024-05-10 17:38 | 7:45 | S/O | From Ullon End. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-05-10 06:00 | 2024-05-10 10:22 | 4:22 | S/O | Ruppur project work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-19 08:43 | 2024-05-19 19:38 | 10:55 | S/O | Right of way work at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2024-05-20 08:15 | 2024-05-20 20:48 | 12:33 | S/O | Right of way work from hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-05-24 09:03 | 2024-05-24 11:51 | 2:48 | S/O | Shaympur Meghnaghat line work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-2 | 2024-05-18 08:44 | 2024-05-18 11:59 | 3:15 | S/O | High Temperature Maintenance work. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-2 | 2024-05-24 09:03 | 2024-05-24 11:51 | 2:48 | S/O | Shaympur Meghnaghat line work. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2024-05-02 11:17 | 2024-05-02 15:06 | 3:49 | S/O | EMS tuning for SCADA connection | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2024-05-08 10:47 | 2024-05-08 18:29 | 7:42 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2024-05-06 11:10 | 2024-05-06 19:10 | 8:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2024-05-09 16:07 | 2024-05-09 16:18 | 0:11 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-2 | 2024-05-09 08:27 | 2024-05-09 15:26 | 6:59 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-20 09:27 | 2024-05-20 18:58 | 9:31 | D/W | project work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-22 13:01 | 2024-05-22 18:04 | 5:03 | S/O | Tower erection work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-23 07:29 | 2024-05-23 18:04 | 10:35 | S/O | Tower erection work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-24 07:41 | 2024-05-24 17:59 | 10:18 | S/O | new tower erection | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-25 08:15 | 2024-05-25 18:35 | 10:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-26 14:19 | 2024-05-26 17:09 | 2:50 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-30 06:38 | 2024-05-30 19:53 | 13:15 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-05-31 07:09 | 2024-05-31 20:52 | 13:43 | S/O | Due to maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-2 | 2024-05-30 11:01 | 2024-05-30 16:44 | 5:43 | S/O | shifting of maniknagar- motijheel double circuit 132 kv XLPE cable of T T para underpass of padma Bridge Rail link project at T T para bus Stand. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Shaympur-02 | 2024-05-08 07:12 | 2024-05-08 09:57 | 2:45 | S/O | Preventive maintenance work | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Aminbazar 400KV Ckt-1 | 2024-05-04 09:46 | 2024-05-04 21:42 | 11:56 | D/W | DFDR integration | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Aminbazar 400KV Ckt-1 | 2024-05-05 09:18 | 2024-05-05 22:18 | 13:00 | D/W | Project Work S/D | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Aminbazar 400KV Ckt-2 | 2024-05-06 09:17 | 2024-05-06 17:08 | 7:51 | D/W | project work | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Aminbazar 400KV Ckt-2 | 2024-05-07 09:15 | 2024-05-07 21:17 | 12:02 | D/W | DFDR commissioning | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-19 07:24 | 2024-05-19 08:54 | 1:30 | S/O | For conductor Armaring work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2024-05-31 06:39 | 2024-05-31 11:10 | 4:31 | S/O | Due to red hot minimize at basundhara ss. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-05-01 18:21 | 2024-05-01 18:43 | 0:22 | S/O | Kite removal | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-05-10 07:30 | 2024-05-10 10:18 | 2:48 | S/O | Conductor armaring. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2024-05-05 16:40 | 2024-05-13 10:00 | 185:20 | D/W | Due to Y phase cable fault checking. | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-05-18 12:33 | 2024-05-18 21:57 | 9:24 | S/O | NLDC | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-05-31 07:12 | 2024-05-31 20:44 | 13:32 | S/O | Maintenance work | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 230 kV Meghnaghat-1(D06) | 2024-05-24 09:19 | 2024-05-24 11:39 | 2:20 | S/O | Maintenance at Meghnaghat End. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2024-05-12 10:35 | 2024-05-12 19:15 | 8:40 | S/O | Maintenance work in Haripur end. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-05-03 06:06 | 2024-05-03 21:02 | 14:56 | S/O | From Sonargaon Grid SS end CB Open Instructions to NLDC. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-05-11 10:09 | 2024-05-11 18:44 | 8:35 | S/O | Shutdown taken from Haripur-01 end. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-1 | 2024-05-23 11:10 | 2024-05-23 12:53 | 1:43 | S/O | Corrective maintenance of R phase CT | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Haripur-2 | 2024-05-03 06:06 | 2024-05-03 21:03 | 14:57 | S/O | From Sonargaon Grid SS end CB Open Instructions to NLDC. | 0 | 0 | No interruption
|  |  | Total : | 608:12 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
AKS 132/33kV Grid Sub-Station | Khulshi | 2024-05-16 05:34 | 2024-05-16 07:13 | 1:39 | S/O | Khulshi Bus Maintenance. | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | GPH Ispat Ckt | 2024-05-31 07:04 | 2024-05-31 09:53 | 2:49 | D/W | LILo work GPH ispat End. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-02 06:49 | 2024-05-02 08:30 | 1:41 | D/W | As per instruction of NLDC. Due to project work of Khulshi Grid SS | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-16 05:19 | 2024-05-16 07:11 | 1:52 | D/W | Bus shutdown at Khulshi end. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-24 05:58 | 2024-05-24 09:26 | 3:28 | D/W | 132kV Bus Shutdown at Khulshi Grid SS. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2024-05-25 05:28 | 2024-05-25 11:11 | 5:43 | D/W | project work | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2024-05-24 05:53 | 2024-05-24 06:14 | 0:21 | S/O | Khushi end bus shutdown | 48 | 16.8 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-05-03 07:14 | 2024-05-03 12:59 | 5:45 | D/W | project work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-05-03 07:15 | 2024-05-03 17:37 | 10:22 | D/W | project work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-05-30 06:10 | 2024-05-31 17:17 | 35:07 | D/W | Stringing work at LILO of korerhat 400/230/132 kv GIS S/S by ESPNER Project. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2024-05-17 07:10 | 2024-05-17 08:41 | 1:31 | S/O | SD taken by Shikalbaha GSS. | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | HATHAZARI-2 | 2024-05-31 10:14 | 2024-05-31 12:08 | 1:54 | D/W | LILO Project | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-05-16 05:14 | 2024-05-16 07:18 | 2:04 | S/O | Khulshi substation end 132 kV bus shutdown | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-05-24 05:43 | 2024-05-24 09:32 | 3:49 | S/O | Due to bus shutdown at khulshi s/s end | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-05-25 05:42 | 2024-05-25 10:20 | 4:38 | S/O | Due to bus shutdown at khulshi S/S. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroaulia-01 | 2024-05-05 08:56 | 2024-05-05 11:05 | 2:09 | S/O | Removing tin foil from line. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2024-05-30 08:33 | 2024-05-30 15:32 | 6:59 | S/O | insulator maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-01 | 2024-05-04 12:00 | 2024-05-04 13:00 | 1:00 | S/O | Maintenance work | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-AKSPL Line | 2024-05-24 05:29 | 2024-05-25 11:59 | 30:30 | D/W | SHOLOSHAHAR CKT-2 and AKSPL line interchange for GIS building work under ESPNCA project. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-MSML Line | 2024-05-02 10:42 | 2024-05-02 12:01 | 1:19 | D/W | Transfer bus dismantling work by ESPNCA | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Madunaghat CKT-2 | 2024-05-24 05:30 | 2024-05-24 05:30 | 0:00 | D/W | SHOLOSHAHAR CKT-2 and AKSPL line interchange for GIS building work under ESPNCA project | 0 | 0 | No interruption
Modern Steel 132/11kV Grid Sub-Station | Modern Khulshi Ckt 2 | 2024-05-25 05:46 | 2024-05-25 10:25 | 4:39 | D/W | Khulshi SS Project Work purpose. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-05-02 17:25 | 2024-05-02 21:22 | 3:57 | D/W | 400kv GNDP Project stability test. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-05-03 10:42 | 2024-05-03 16:49 | 6:07 | D/W | p/w | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2024-05-24 05:29 | 2024-05-24 09:32 | 4:03 | S/O | Khulshi grid busbar maintenance work. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2024-05-24 05:29 | 2024-05-24 09:32 | 4:03 | S/O | Khulshi grid busbar maintenance work. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-1 | 2024-05-17 06:12 | 2024-05-17 09:44 | 3:32 | S/O | Bus Maintenance at Shahmirpur S/S | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-1 | 2024-05-24 06:41 | 2024-05-24 09:38 | 2:57 | S/O | Bus-Shut down at Shahmirpur End. | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-1 | 2024-05-25 09:37 | 2024-05-25 09:46 | 0:09 | S/O | Maintenance work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-1 | 2024-05-31 08:14 | 2024-05-31 15:20 | 7:06 | S/O | Maintenance work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-2 | 2024-05-17 06:28 | 2024-05-17 09:45 | 3:17 | S/O | Bus Maintenance at Shahmirpur S/S | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-2 | 2024-05-24 06:28 | 2024-05-24 09:24 | 2:56 | S/O | Maintenance work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-2 | 2024-05-31 08:32 | 2024-05-31 11:22 | 2:50 | S/O | Maintenance work | 0 | 0 | No interruption
Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Khulshi Ckt-1 | 2024-05-16 05:25 | 2024-05-16 07:07 | 1:42 | S/O | Bus shutdown at Khulshi Grid | 0 | 0 | No interruption
|  |  | Total : | 171:58 |  | Unserved Energy: |  | 16.8
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | Sylhet-Fenchugang -T -Branibazar-1 | 2024-05-11 09:14 | 2024-05-11 12:02 | 2:48 | D/W | SAS system development | 30 | 84 | Power interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-I | 2024-05-20 09:30 | 2024-05-20 12:05 | 2:35 | S/O | Line Problem Kaliakoir Side | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-05-12 09:01 | 2024-05-12 13:58 | 4:57 | S/O | NLDC SDE. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-2 | 2024-05-12 09:01 | 2024-05-12 13:58 | 4:57 | S/O | NLDC SDE. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 2024-05-18 06:24 | 2024-05-18 10:38 | 4:14 | S/O | Red hot remove | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 2024-05-27 14:57 | 2024-05-27 16:40 | 1:43 | S/O | Requested to Desh Energy power plant authority | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2024-05-18 10:47 | 2024-05-18 14:53 | 4:06 | S/O | Red hot maintenance work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2024-05-11 09:20 | 2024-05-11 13:50 | 4:30 | D/W | For 230KV New Line Charge | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-01 | 2024-05-17 06:46 | 2024-05-17 12:47 | 6:01 | S/O | Feni grid 132kv BUS maintenance. | 40 | 240.6667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-05-11 09:20 | 2024-05-11 13:52 | 4:32 | D/W | For 230KV KorerHat-Chowmuhani Line Charge | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2024-05-17 06:45 | 2024-05-17 12:47 | 6:02 | S/O | Feni grid 132kv BUS maintenance. | 40 | 241.3333 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2024-05-10 06:13 | 2024-05-10 10:28 | 4:15 | D/W | Due To 230Kv Lin Jumper from 132kv Chow-ram Line-01 | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2024-05-10 06:13 | 2024-05-10 10:28 | 4:15 | D/W | Due To 230Kv Lin Jumper from 132kv Chow-ram Line-01 | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2024-05-30 06:03 | 2024-05-30 19:36 | 13:33 | D/W | Conductor Stringing | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Cumilla North-3 | 2024-05-25 19:25 | 2024-05-25 22:51 | 3:26 | S/O | Old CVT Open for Cumilla North S/S | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2024-05-30 07:51 | 2024-05-30 12:01 | 4:10 | S/O | Maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-05-11 09:19 | 2024-05-11 12:01 | 2:42 | S/O | Shutdown taken by Beanibazar Substation. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2024-05-17 06:51 | 2024-05-17 12:42 | 5:51 | S/O | 132KV Main Bus-2 Shutdown for Bus isolator hot Spot Maintenance Work. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2024-05-20 13:29 | 2024-05-20 14:49 | 1:20 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-2 | 2024-05-30 08:37 | 2024-05-30 12:15 | 3:38 | S/O | fenchuganj substation take the shutdown | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | BPDB 60 MW | 2024-05-09 10:36 | 2024-05-09 12:10 | 1:34 | S/O | Corrective red hot maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-01 | 2024-05-05 22:17 | 2024-05-06 09:30 | 11:13 | S/O | B-Baria end breaker is not closing (Pole discrepancy) | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-05-01 09:41 | 2024-05-01 20:15 | 10:34 | D/W | Project works , no L/S | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-05-02 09:07 | 2024-05-02 17:49 | 8:42 | D/W | Due to Project work | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-05-13 13:34 | 2024-05-13 23:37 | 10:03 | D/W | TRTU works | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Biyanibazar 132KV Ckt-1 | 2024-05-12 10:35 | 2024-05-12 15:03 | 4:28 | D/W | NLDC SAS Witness work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Biyanibazar 132KV Ckt-2 | 2024-05-12 10:35 | 2024-05-12 15:03 | 4:28 | D/W | NLDC SAS Witness work | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-05-11 09:20 | 2024-05-11 12:01 | 2:41 | D/W | Biyanibaza | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2024-05-13 10:44 | 2024-05-13 12:48 | 2:04 | D/W | NLDC Witness of Fenchugonj ckt-1 & 2 | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-05-11 09:20 | 2024-05-11 12:01 | 2:41 | D/W | Biyanibazar end working | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-05-13 10:44 | 2024-05-13 12:48 | 2:04 | D/W | NLDC Witness of Fenchugonj ckt- 1 & 2 | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2024-05-28 00:58 | 2024-05-28 14:47 | 13:49 | S/O | Work of chhatak end | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-05-04 20:03 | 2024-05-04 20:27 | 0:24 | S/O | OPEN for order of NLDC(299725) -Grid fail | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2024-05-14 10:42 | 2024-05-14 13:42 | 3:00 | D/W | South Surma Grid SCDA test by NLDC | 0 | 0 | No interruption
|  |  | Total : | 167:20 |  | Unserved Energy: |  | 566
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-05-02 10:09 | 2024-05-02 13:35 | 3:26 | S/O | Shutdown taken from Bhandaria grid | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gopalganj 100 MW PS | 2024-05-16 07:18 | 2024-05-16 13:07 | 5:49 | S/O | Red hot maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-2 | 2024-05-05 11:59 | 2024-05-05 19:23 | 7:24 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-1 | 2024-05-07 10:00 | 2024-05-07 13:16 | 3:16 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Gopalganj Ckt-2 | 2024-05-06 08:57 | 2024-05-06 16:56 | 7:59 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2024-05-31 08:10 | 2024-05-31 16:19 | 8:09 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Payra Ckt-2 | 2024-05-01 09:17 | 2024-05-01 13:55 | 4:38 | S/O | Maintenance at payra-End | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2024-05-04 17:32 | 2024-05-04 18:56 | 1:24 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2024-05-12 09:52 | 2024-05-12 18:13 | 8:21 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2024-05-17 09:46 | 2024-05-17 20:36 | 10:50 | D/W | Due to project work | 0 | 0 | No interruption
Payra 400kV Sub-Station | Line-2 (Gopalganj) | 2024-05-01 09:17 | 2024-05-01 13:54 | 4:37 | S/O | PGCB requires shutdown for disc cleaning purpose. | 0 | 0 | No interruption
|  |  | Total : | 65:53 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Bheramara-2 | 2024-05-02 10:51 | 2024-05-02 12:47 | 1:56 | S/O | Red hot maintenance | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-1 | 2024-05-24 06:49 | 2024-05-24 13:24 | 6:35 | D/W | RNPP project work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-2 | 2024-05-24 07:01 | 2024-05-24 13:25 | 6:24 | D/W | RNPP project work. | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2024-05-20 09:56 | 2024-05-20 12:14 | 2:18 | D/W | Loop jumper connection. | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | Kushtia -Bheramara-1 | 2024-05-31 10:28 | 2024-05-31 15:21 | 4:53 | D/W | Conductor Loop connecting Between DS and BUS | 0 | 0 | No interruption
|  |  | Total : | 22:06 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2024-05-10 06:56 | 2024-05-10 12:18 | 5:22 | D/W | Conductor stringing work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt1 | 2024-05-30 07:10 | 2024-05-30 12:46 | 5:36 | D/W | Project work. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2024-05-10 06:57 | 2024-05-10 12:19 | 5:22 | D/W | Conductor stringing work | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Bogura 230 KV Ckt2 | 2024-05-30 12:54 | 2024-05-30 17:18 | 4:24 | D/W | Project work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2024-05-24 05:54 | 2024-05-24 09:04 | 3:10 | S/O | Project work. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2024-05-24 05:56 | 2024-05-24 09:02 | 3:06 | S/O | Project work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2024-05-19 09:13 | 2024-05-19 18:34 | 9:21 | S/O | Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2024-05-07 16:01 | 2024-05-07 17:40 | 1:39 | D/W | Project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2024-05-18 08:45 | 2024-05-18 23:39 | 14:54 | S/O | SAS, DFDR, TWFL & SCADA pre- commissioning work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-1 | 2024-05-03 06:33 | 2024-05-03 06:41 | 0:08 | D/W | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-1 | 2024-05-24 07:05 | 2024-05-24 10:50 | 3:45 | S/O | Due to maint.work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-2 | 2024-05-03 06:33 | 2024-05-03 06:56 | 0:23 | D/W | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-2 | 2024-05-05 10:37 | 2024-05-05 17:13 | 6:36 | S/O | Busbar Stabllity Test &DS Connect With 230 kv Bus | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2024-05-06 10:35 | 2024-05-07 11:05 | 24:30 | D/W | Project work | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura - Rooppur 400 KV Line-1 | 2024-05-01 21:48 | 2024-05-01 21:48 | 0:00 | D/W | Line Charged on 21:16 (01.05.2024) and Line S/D for checking, ROW & Others work. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Rahanpur 400 KV CKT-01 | 2024-05-13 07:58 | 2024-05-13 21:47 | 13:49 | D/W | project work at Rahanpur SS end. | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Rahanpur 400 KV CKT-01 | 2024-05-19 08:31 | 2024-05-19 20:17 | 11:46 | S/O | DFDR Commissioning | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Rahanpur 400 KV CKT-02 | 2024-05-15 08:37 | 2024-05-15 20:13 | 11:36 | S/O | Project work at Rahanpur SubStation | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Rahanpur 400 KV CKT-02 | 2024-05-16 08:46 | 2024-05-16 16:58 | 8:12 | S/O | Project work at Rahanpur SubStation | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | Bogura-Rahanpur 400 KV CKT-02 | 2024-05-18 08:41 | 2024-05-18 23:20 | 14:39 | S/O | DFDR commissioning | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 1 | 2024-05-06 07:25 | 2024-05-06 14:48 | 7:23 | D/W | Project work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai Rahanpur ckt 2 | 2024-05-06 14:50 | 2024-05-06 17:23 | 2:33 | D/W | Project work | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Naogaon Ckt.-2 | 2024-05-25 07:06 | 2024-05-25 15:43 | 8:37 | D/W | Conductor rearrange on Tower no. 09 | 40 | 344.6667 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2024-05-04 06:16 | 2024-05-04 10:40 | 4:24 | S/O | Project work (Bogura 230KV S/S Side) | 30 | 132 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2024-05-04 06:16 | 2024-05-04 10:42 | 4:26 | S/O | Project work (Bogura 230KV S/S Side) | 30 | 133 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2024-05-25 07:06 | 2024-05-25 15:40 | 8:34 | S/O | Naogaon-Joypurhat second Ckt project works. | 40 | 342.6667 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-05-04 14:27 | 2024-05-04 17:12 | 2:45 | D/W | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-05-12 11:18 | 2024-05-12 12:16 | 0:58 | D/W | Project Work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-05-04 10:56 | 2024-05-04 14:20 | 3:24 | D/W | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-05-12 08:41 | 2024-05-12 11:11 | 2:30 | D/W | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-05-03 06:42 | 2024-05-04 06:16 | 23:34 | S/O | Due to project work | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2024-05-06 14:48 | 2024-05-06 17:17 | 2:29 | S/O | Due to maint.work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-1 | 2024-05-10 06:01 | 2024-05-10 12:49 | 6:48 | S/O | Due to maint.work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-2 | 2024-05-10 06:02 | 2024-05-10 12:50 | 6:48 | S/O | Due to maint.work | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-2 | 2024-05-15 07:09 | 2024-05-15 13:17 | 6:08 | S/O | Loop replacement because red hot | 0 | 0 | No interruption
|  |  | Total : | 239:39 |  | Unserved Energy: |  | 952.3333
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1829:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May 2024
| Area | Previous Month (April' 2024) |  |  |  | Current Month (May '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 24 | 12 | 52 | 88 | 69 | 23 | 105 | 197
2 | Dhaka (South) Grid Circle. | 31 | 10 | 38 | 79 | 94 | 31 | 82 | 207
3 | Chattogram Grid Circle. | 8 | 11 | 22 | 41 | 68 | 27 | 58 | 153
4 | Cumilla Grid Circle. | 31 | 6 | 48 | 85 | 54 | 25 | 56 | 135
5 | Khulna Grid Circle. | 38 | 15 | 53 | 106 | 39 | 20 | 40 | 99
6 | HVDC Grid Circle | 7 | 6 | 5 | 18 | 8 | 23 | 15 | 46
7 | Bogura Grid Circle. | 12 | 18 | 35 | 65 | 31 | 22 | 74 | 127
8 | Others
9 | Total | 151 | 78 | 253 | 482 | 363 | 171 | 430 | 964
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May 2024
| Area | Previous Month (April' 2024) |  |  |  | Current Month (May '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 1051.09 | 752.9 | 1376.3 | 3180.29 | 940.04 | 368.1 | 3271.15 | 4579.29
2 | Dhaka (South) Grid Circle. | 472.35 | 78.48 | 301.56 | 852.39 | 569.1 | 62 | 373 | 1004.1
3 | Chattogram Grid Circle. | 33.6 | 90.43 | 230.13 | 354.16 | 245.56 | 50.17 | 1257.4 | 1553.13
4 | Cumilla Grid Circle. | 81.96 | 241.17 | 287.67 | 610.8 | 782.4 | 365.17 | 1034.17 | 2181.74
5 | Khulna Grid Circle. | 3608.99 | 197.54 | 857.8 | 4664.33 | 48.87 | 169.23 | 153.57 | 371.67
6 | HVDC Grid Circle | 192.93 | 191.67 | 145.67 | 530.27 | 44.27 | 71 | 213.5 | 328.77
7 | Bogura Grid Circle. | 73.22 | 502.46 | 708.85 | 1284.53 | 298.26 | 296.68 | 1513.73 | 2108.67
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 5514.14 | 2054.65 | 3907.98 | 11476.77 | 2928.5 | 1382.35 | 7816.52 | 12127.37
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 12 | 12 | 24 | 6 | 3 | 15 | 2935.37
2 | Dhaka (South) | 5031.6 | 14 | 7 | 21 | 11 | 4 | 6 | 565.02
3 | Chattogram | 2042 | 11 | 9 | 20 | 6 | 4 | 10 | 1389.42
4 | Khulna | 2434 | 28 | 2 | 30 | 20 | 7 | 3 | 371.68
5 | HVDC | 5954.3 | 7 | 4 | 11 | 4 | 2 | 5 | 328.77
6 | Bogura | 3145.6 | 18 | 8 | 26 | 9 | 5 | 12 | 1011.13
7 | Cumilla | 2981 | 16 | 9 | 25 | 6 | 6 | 13 | 1041.02
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 7642.41
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.94%
4 | Khulna | 99.97%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.89% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 11 | 7 | 18 | 8 | 2 | 8 | 1643.93
2 | Dhaka (South) | 990.29 | - | 10 | - | 10 | 4 | 2 | 4 | 439.0833
3 | Chattogram | 917 | - | 9 | 1 | 10 | 6 | - | 4 | 163.7
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 4 | 4 | 8 | 3 |  | 5 | 1097.53
7 | Cumilla | 1648.16 | - | 6 | 3 | 9 | 1 | 3 | 5 | 1140.72
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 4484.9633
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.98%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2024-05-01 | 20 | - | 9 | 12hr34 min | 1 | 2hr47 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:12 | 7.6
Joydebpur 132/33kV Grid Sub-Station | 2 | 1:34 | 139.08
Kishoreganj 132/33kV Grid Sub-Station | 3 | 21:01 | 508.87
Savar 132/33kV Grid Sub-Station | 1 | 0:05 | 3.3333
Sherpur 132/33kV Grid Sub-Station | 2 | 0:21 | 5.6
Tangail 132/33kV Grid Sub-Station | 2 | 1:24 | 55.77
Tongi 230/132/33kV Grid Sub-Station | 1 | 5:15 | 115.5
Bhaluka 132/33kV Grid Sub-Station | 3 | 0:38 | 74.73
Ghatail 132/33kV Grid Sub-Station | 2 | 1:25 | 24.08
Sreepur 230/132/33kV Grid Sub-Station | 2 | 0:15 | 32.5
Sreepur 230/132/33kV Grid Sub-Station | 2 | 0:17 | 37.42
Tongi 230/132/33kV Grid Sub-Station | 3 | 3:17 | 303.67
Bhaluka 132/33kV Grid Sub-Station | 1 | 1:55 | 19.1667
Dhamrai 132/33kV Grid Sub-Station | 1 | 3:14 | 64.6667
Jamalpur 132/33kV Grid Sub-Station | 3 | 17:48 | 1273.33
Kabirpur 132/33kV Grid Sub-Station |  | 7:38 | 572.33
Kodda 132/33kV Grid Sub-Station | 2 | 3:19 | 100.58
Manikganj 132/33kV Grid Sub-Station | 1 | 3:02 | 48.5333
Mirzapur 132/33kV GIS Grid Sub-Station | 1 | 1:24 | 21
Joydebpur 132/33kV Grid Sub-Station | 2 | 18:49 | 293.17
Kishoreganj 132/33kV Grid Sub-Station | 1 | 2:06 | 105
Manikganj 132/33kV Grid Sub-Station | 1 | 1:52 | 29.8667
Mirzapur 132/33kV GIS Grid Sub-Station | 2 | 16:29 | 164.83
Tangail 132/33kV Grid Sub-Station | 2 | 7:14 | 578.6667
Hasnabad 132/33kV Grid Substation | 4 | 0:27 | 10.45
Keranigonj 230/132/33kV Grid Sub-Station | 2 | 1:25 | 46.78
Sonargaon 132/33kV Grid Sub-Station | 7 | 3:24 | 134.7
Srinagar 132/33kV Grid Sub-Station | 1 | 0:25 | 0.083333
Gulshan 132/33kV Grid Sub-Station | 1 | 0:51 | 54.4
Haripur 230/132kV Grid Sub-Station | 4 | 3:09 | 56.3
Hasnabad 132/33kV Grid Substation | 1 | 1:00 | 30
Siddhirganj 132/33kV Grid Sub-Station | 3 | 11:34 | 256.38
Sonargaon 132/33kV Grid Sub-Station | 1 | 3:00 | 42
Munshiganj 132/33kV Grid Sub-Station | 2 | 6:40 | 220
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:38 | 25.3333
Nawabganj 132/33kV Grid Sub-Station | 2 | 4:00 | 48
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:44 | 25.6667
Srinagar 132/33kV Grid Sub-Station | 1 | 2:42 | 54
Bakulia 132/33kV Grid Sub-Station | 1 | 0:47 | 3.9167
Baroaulia 132/33kV Grid Sub-Station | 1 | 2:18 | 46
Dohazari 132/33kV Grid Sub-Station | 2 | 1:01 | 35.67
Halishahar 132/33kV Grid Sub-Station | 1 | 0:25 | 4.1667
Hathazari 230/132/33kV Grid Sub-Station | 2 | 0:28 | 14.47
Kalurghat 132/33kV Grid Sub-Station | 3 | 2:07 | 37.4
Madunaghat 132/33kV Grid Sub-Station | 1 | 0:48 | 7.2
Baroaulia 132/33kV Grid Sub-Station | 3 | 5:26 | 51.77
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:12 | 24
Hathazari 230/132/33kV Grid Sub-Station | 2 | 2:42 | 10.8
Rampur 230/132/33 kV GIS Grid Sub-Station | 3 | 0:32 | 60.33
Baroirhat 132/33kV Grid Sub-Station | 1 | 1:10 | 42
Coxsbazar 132/33kV Grid Sub-Station | 2 | 6:49 | 670
Kalurghat 132/33kV Grid Sub-Station | 1 | 0:44 | 11.7333
Khulshi 132/33kV Grid Sub-Station | 2 | 5:40 | 135.17
Shahmirpur 132/33kV Grid Sub-Station | 3 | 8:57 | 381.7
Baroaulia 132/33kV Grid Sub-Station | 1 | 0:21 | 16.8
Beanibazar 132/33kV Grid Sub-Station | 1 | 1:23 | 34.5833
Brahmanbaria 132/33kV Grid Sub-Station | 2 | 0:32 | 16
Chandpur 132/33kV Grid Sub-Station | 1 | 1:50 | 18.33
Chauddagram 132/33kV Grid Sub-Station | 2 | 2:56 | 105.78
Chowmuhani 132/33kV Grid Sub-Station | 1 | 0:54 | 14.4
Cumilla(N) 230/132/33kV Grid Sub-Station | 6 | 2:52 | 354.88
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 0:14 | 7
Daudkandi 132/33kV Grid Sub-Station | 1 | 0:42 | 19.6
Sylhet 132/33kV Grid Sub-Station | 1 | 0:08 | 2.2667
Sunamganj 132/33kV Grid Sub-Station | 2 | 1:04 | 4.27
Sylhet 132/33kV Grid Sub-Station | 4 | 27:53 | 570.45
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 2:35 | 129.1667
Chandpur 132/33kV Grid Sub-Station | 1 | 1:30 | 42
Cumilla(N) 230/132/33kV Grid Sub-Station | 2 | 4:26 | 203.5
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 0:01 | 0.33333
Kulaura 132/33kV Grid Sub-Station | 1 | 1:10 | 28
Ramganj 132/33kV Grid Sub-Station | 2 | 2:11 | 43.67
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:43 | 21.5
Beanibazar 132/33kV Grid Sub-Station | 1 | 2:48 | 84
Chowmuhani 132/33kV Grid Sub-Station | 2 | 12:03 | 482
Bagerhat 132/33kV Grid Sub-Station | 7 | 1:46 | 36.9
Barishal 132/33kV Grid Sub-Station | 8 | 0:59 | 27.2
Benapole 132/33kV Grid Sub-Station | 2 | 0:51 | 20.67
Bhandaria 132/33kV Grid Sub-Station | 2 | 1:25 | 21.67
Borhanuddin 230/33kV Grid Sub-Station | 2 | 3:03 | 101.5
Noapara 132/33kV Grid Sub-Station | 4 | 0:38 | 6.5
Patuakhali 132/33kV Grid Sub-Station | 3 | 0:55 | 3.68
Bagerhat 132/33kV Grid Sub-Station | 1 | 2:48 | 78.4
Barishal 230/132kV Grid Sub-Station | 1 | 3:25 | 75.1667
Chuadanga 132/33kV Grid Sub-Station | 5 | 4:31 | 96.77
Pabna 132/33kV Grid Sub-Station | 2 | 2:06 | 18.5
Jhenaidah 132/33kV Grid Sub-Station | 1 | 2:04 | 62
Pabna 132/33kV Grid Sub-Station | 3 | 5:03 | 151.5
Joypurhat 132/33kV Grid Sub-Station | 2 | 0:31 | 4.65
Mahasthangarh 132/33kV Grid Sub-Station | 4 | 10:08 | 241.67
Naogaon 132/33kV Grid Sub-Station | 3 | 3:44 | 82.6
Natore 132/33kV Grid Sub-Station | 3 | 2:57 | 47.07
Niamatpur 132/33kV Grid Sub-Station | 4 | 3:02 | 37.85
Purbasadipur 132/33kV Grid Sub-Station | 1 | 0:49 | 24.5
Sirajganj 132/33kV Grid Sub-Station | 1 | 0:57 | 11.4
Chapai 132/33kV Grid Sub-Station | 1 | 0:18 | 16.8
Naogaon 132/33kV Grid Sub-Station | 1 | 0:30 | 22
Rangpur 132/33kV Grid Sub-Station | 1 | 3:18 | 92.4
Thakurgaon 132/33kV Grid Sub-Station | 1 | 0:21 | 14
Bogura 132/33kV Grid Sub-Station | 2 | 3:58 | 107.17
Chapai 132/33kV Grid Sub-Station | 1 | 0:48 | 2.4
Purbasadipur 132/33kV Grid Sub-Station | 3 | 6:08 | 96.83
Rajshahi 132/33kV Grid Sub-Station | 1 | 2:40 | 53.3333
Sirajganj 132/33kV Grid Sub-Station | 1 | 3:01 | 301.6667
Joypurhat 132/33kV Grid Sub-Station | 1 | 8:37 | 344.6667
Naogaon 132/33kV Grid Sub-Station | 3 | 17:24 | 607.67
Total Unserved energy : | 211 | 367:40 | 12127.3767
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: May 2024
Sl. No | name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2024-05-05 16:00 | 60
2 | Agargaon 230/132kV Grid Sub-Station | 2024-05-02 12:00 | 127
3 | Banani 132/33kV Grid Sub-Station | 2024-05-05 14:00 | 80.4
4 | Bangabhaban 132/33kV Grid Sub-Station | 2024-05-02 10:00 | 19
5 | Bashundhara 132/33kV Grid Sub-Station | 2024-05-25 15:00 | 244
6 | BashundharaCement 132/33kV Sub-Station | 2024-05-02 11:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2024-05-20 11:00 | 258
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2024-05-01 23:00 | 186
9 | Charsaidpur 132/33kV Sub-Station | 2024-05-02 16:00 | 47
10 | Dhaka University 132/33kV Grid Sub-Station | 2024-05-15 13:00 | 60
11 | Dhamrai 132/33kV Grid Sub-Station | 2024-05-16 20:00 | 138
12 | Dhanmondi 132/33kV Grid Sub-Station | 2024-05-19 13:00 | 188
13 | Fatullah 132/33kV Grid Sub-Station | 2024-05-15 16:00 | 77
14 | Ghorashal 230/132/33kV Sub-Station | 2024-05-25 12:00 | 88
15 | Gulshan 132/33kV Grid Sub-Station | 2024-05-02 13:00 | 160
16 | HaripurSBU 132/33kV Sub-Station | 2024-05-25 18:00 | 191
17 | Hasnabad 132/33kV Grid Substation | 2024-05-23 23:00 | 117
18 | Joydebpur 132/33kV Grid Sub-Station | 2024-05-15 19:30 | 215
19 | Kabirpur 132/33kV Grid Sub-Station | 2024-05-30 20:00 | 308
20 | Kallyanpur 132/33kV Grid Sub-Station | 2024-05-25 | 141
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2024-05-23 19:00 | 59.4
22 | Kazla 132/33kV Grid Sub-Station | 2024-05-25 16:00 | 132
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2024-05-02 23:00 | 91
24 | Kodda 132/33kV Grid Sub-Station | 2024-05-04 18:30 | 299
25 | Lalbag 132/33kV Grid Sub-Station | 2024-05-25 18:30 | 107
26 | Madanganj 132/33kV Grid Sub-Station | 2024-05-23 23:00 | 46
27 | Madartek 132/33kV Grid Sub-Station | 2024-05-04 23:00 | 105.66
28 | Manikganj 132/33kV Grid Sub-Station | 2024-05-01 10:00 | 148
29 | Maniknagar 132/33kV Grid Sub-Station | 2024-05-05 13:00 | 92
30 | Matuail 132/33kV Grid Sub-Station | 2024-05-23 | 85
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2024-05-25 15:00 | 139
32 | Mirpur 132/33kV Grid Sub-Station | 2024-05-25 19:00 | 179.5
33 | MI_Cement 132/33kV Grid Sub-Station | 2024-05-01 22:00 | 11.6
34 | Mogbazar 132/33kV Grid Sub-Station | 2024-05-29 15:00 | 157.8
35 | Motijheel 132/33kV Grid Sub-Station | 2024-05-02 13:00 | 61
36 | Munshiganj 132/33kV Grid Sub-Station | 2024-05-03 23:00 | 126
37 | Narinda 132/33kV Grid Sub-Station | 2024-05-02 13:00 | 82
38 | Narshingdi 132/33kV Grid Sub-Station | 2024-05-21 19:00 | 185
39 | Nawabganj 132/33kV Grid Sub-Station | 2024-05-04 22:00 | 70.8
40 | New Tongi 132/33kV Grid Sub-Station | 2024-05-15 12:00 | 64.4
41 | Postogola 132/33kV Grid Sub-Station | 2024-05-25 16:00 | 68
42 | Purbachal 132/33kV Grid Sub-Station | 2024-05-25 15:00 | 26
43 | Rahim Steel 132/33kV Sub-Station | 2024-05-25 13:00 | 54
44 | Rajendrapur 132/33kV Grid Sub-Station | 2024-05-25 19:30 | 134
45 | Satmasjid 132/33kV Grid Sub-Station | 2024-05-23 13:00 | 137
46 | Savar 132/33kV Grid Sub-Station | 2024-05-16 15:00 | 229
47 | SevenRings 132/11kV Sub-Station | 2024-05-29 23:00 | 23.44
48 | ShahCement 132/33kV Grid Sub-Station | 2024-05-17 | 35
49 | Shitalakhya 132/33kV Grid Sub-Station | 2024-05-25 16:00 | 122.2
50 | Shyampur 132/33kV Grid Sub-Station | 2024-05-22 09:00 | 188
51 | Siddhirganj 132/33kV Grid Sub-Station | 2024-05-25 16:00 | 134
52 | Sonargaon 132/33kV Grid Sub-Station | 2024-05-14 16:00 | 129
53 | Sreepur 230/132/33kV Grid Sub-Station | 2024-05-26 19:30 | 71
54 | Srinagar 132/33kV Grid Sub-Station | 2024-05-02 23:00 | 54.5
55 | Tongi 230/132/33kV Grid Sub-Station | 2024-05-25 15:00 | 154
56 | Ullon 132/33kV Grid Sub-Station | 2024-05-31 | 77
57 | Uttara 132/33kV Grid Sub-Station | 2024-05-02 15:00 | 112
58 | UttaraNew 132/33kV Grid Sub-Station | 2024-05-01 | 55
59 | Zigatola 132/33kV Grid Sub-Station | 2024-05-25 16:00 | 107
60 | Agrabad 132/33kV Grid Sub-Station | 2024-05-29 15:00 | 92
61 | AKS 132/33kV Grid Sub-Station | 2024-05-18 18:00 | 40
62 | AKSML 230/33kV Grid Sub-Station | 2024-05-10 12:00 | 120
63 | Bakulia 132/33kV Grid Sub-Station | 2024-05-23 21:00 | 115
64 | Baroaulia 132/33kV Grid Sub-Station | 2024-05-15 15:00 | 88
65 | Baroirhat 132/33kV Grid Sub-Station | 2024-05-16 19:00 | 76
66 | BSRM 230/33kV Grid Sub-Station | 2024-05-16 03:00 | 193
67 | Chandraghona 132/33kV Grid Sub-Station | 2024-05-29 20:00 | 41
68 | Coxsbazar 132/33kV Grid Sub-Station | 2024-05-01 20:00 | 145
69 | Dohazari 132/33kV Grid Sub-Station | 2024-05-01 21:00 | 111
70 | GPH 230/33kV Grid Sub-Station | 2024-05-29 12:00 | 99
71 | Halishahar 132/33kV Grid Sub-Station | 2024-05-26 14:00 | 104
72 | Hathazari 230/132/33kV Grid Sub-Station | 2024-05-23 21:00 | 93
73 | Juldah 132/33kV Grid Sub-Station | 2024-05-26 12:00 | 24
74 | Kalurghat 132/33kV Grid Sub-Station | 2024-05-16 16:00 | 42
75 | Khagrachori 132/33kV Grid Sub-Station | 2024-05-23 19:00 | 38
76 | Khulshi 132/33kV Grid Sub-Station | 2024-05-29 19:30 | 210
77 | KSRM 132/33kV Grid Sub-Station | 2024-05-05 08:00 | 52.5
78 | Madunaghat 132/33kV Grid Sub-Station | 2024-05-14 19:30 | 68
79 | Matarbari 132/33kV Sub-Station | 2024-05-18 19:00 | 52
80 | Mirsorai 230/33kV Grid Sub-Station | 2024-05-02 21:00 | 9
81 | Modern Steel 132/11kV Grid Sub-Station | 2024-05-01 | 0
82 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2024-05-24 05:00 | 49
83 | Rangamati 132/33kV Grid Sub-Station | 2024-05-16 19:00 | 21
84 | Shahmirpur 132/33kV Grid Sub-Station | 2024-05-06 15:00 | 63
85 | Shikalbaha 132/33kV Sub-Station | 2024-05-01 01:00 | 39
86 | Sholosohor 132/33kV Grid Sub-Station | 2024-05-25 09:00 | 53
87 | SSM 132/33kV Grid Sub-Station | 2024-05-06 | 16
88 | TK chemical 132kV Grid Sub-Station | 2024-05-23 21:00 | 35.5
89 | Ashuganj 230/132/33kV Sub-Station | 2024-05-13 02:00 | 119.5
90 | Brahmanbaria 132/33kV Grid Sub-Station | 2024-05-01 22:00 | 207
91 | Chandpur 132/33kV Grid Sub-Station | 2024-05-24 | 83
92 | Chauddagram 132/33kV Grid Sub-Station | 2024-05-25 | 84
93 | Chowmuhani 132/33kV Grid Sub-Station | 2024-05-05 21:00 | 253
94 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2024-05-22 21:00 | 211
95 | Cumilla(S) 132/33kV Grid Sub-Station | 2024-05-25 15:00 | 194
96 | Daudkandi 132/33kV Grid Sub-Station | 2024-05-23 21:00 | 175
97 | Feni 132/33kV Grid Sub-Station | 2024-05-01 19:00 | 138
98 | Kachua 132/33kV Grid Sub-Station | 2024-05-01 22:00 | 98
99 | PHP 132/33kV Sub-Station | 2024-05-12 18:30 | 11
100 | Ramganj 132/33kV Grid Sub-Station | 2024-05-25 22:00 | 124
101 | Bhaluka 132/33kV Grid Sub-Station | 2024-05-30 15:00 | 156
102 | Ghatail 132/33kV Grid Sub-Station | 2024-05-01 20:00 | 80
103 | Jamalpur 132/33kV Grid Sub-Station | 2024-05-01 20:00 | 150
104 | Kishoreganj 132/33kV Grid Sub-Station | 2024-05-17 23:00 | 152
105 | Mirzapur 132/33kV GIS Grid Sub-Station | 2024-05-25 12:00 | 62
106 | Mymensingh 132/33kV Grid Sub-Station | 2024-05-17 09:00 | 258
107 | Netrakona 132/33kV Grid Sub-Station | 2024-05-12 20:00 | 147
108 | Sherpur 132/33kV Grid Sub-Station | 2024-05-03 21:00 | 166
109 | Tangail 132/33kV Grid Sub-Station | 2024-05-04 19:30 | 280
110 | Beanibazar 132/33kV Grid Sub-Station | 2024-05-25 22:00 | 85
111 | Chhatak 132/33kV Grid Sub-Station | 2024-05-23 22:00 | 39
112 | Fenchuganj 230/132/33kV Grid Sub-Station | 2024-05-16 20:00 | 48
113 | Kulaura 132/33kV Grid Sub-Station | 2024-05-16 21:00 | 62
114 | Shahjibazar 132/33kV Grid Sub-Station | 2024-05-23 23:00 | 152
115 | Sreemongol 132/33kV Grid Sub-Station | 2024-05-21 22:00 | 83
116 | Sunamganj 132/33kV Grid Sub-Station | 2024-05-25 | 65
117 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 2024-05-26 19:00 | 52
118 | Sylhet 132/33kV Grid Sub-Station | 2024-05-26 19:00 | 156
119 | Bagerhat 132/33kV Grid Sub-Station | 2024-05-05 23:00 | 110
120 | Benapole 132/33kV Grid Sub-Station | 2024-05-01 | 83
121 | Bheramara(GK) 132/33kV Grid Sub-Station | 2024-05-05 21:00 | 75
122 | Chuadanga 132/33kV Grid Sub-Station | 2024-05-30 20:00 | 123
123 | Faridpur 132/33kV Grid Sub-Station | 2024-05-03 | 190
124 | Goalpara 132/33kV Grid Sub-Station | 2024-05-05 23:00 | 42
125 | Gollamari 132/33kV Grid Sub-Station | 2024-05-12 02:00 | 102
126 | Gopalganj 132/33kV Grid Sub-Station | 2024-05-01 | 125
127 | Jashore 132/33kV Grid Sub-Station | 2024-05-25 19:00 | 172
128 | Jhenaidah 132/33kV Grid Sub-Station | 2024-05-02 23:00 | 150
129 | Khulna (C) 132/33kV Grid Sub-Station | 2024-05-15 13:00 | 105
130 | Kushtia 132/33kV Grid Sub-Station | 2024-05-25 19:00 | 172
131 | Madaripur 132/33kV Grid Sub-Station | 2024-05-02 23:00 | 128
132 | Magura 132/33kV Grid Sub-Station | 2024-05-01 | 75
133 | Mongla 132/33kV Grid Sub-Station | 2024-05-16 15:00 | 47
134 | Narail 132/33kV Grid Sub-Station | 2024-05-01 23:00 | 68
135 | Noapara 132/33kV Grid Sub-Station | 2024-05-20 19:30 | 55
136 | Rajbari 132/33kV Grid Sub-Station | 2024-05-05 22:00 | 90
137 | Satkhira 132/33kV Grid Sub-Station | 2024-05-25 01:00 | 155
138 | Shariatpur 132/33kV Grid Sub-Station | 2024-05-01 23:00 | 98
139 | Barguna 132/33kV Grid Sub-Station | 2024-05-01 | 24
140 | Barishal 132/33kV Grid Sub-Station | 2024-05-01 | 128
141 | Barishal 230/132kV Grid Sub-Station | 2024-05-24 23:00 | 126
142 | Bhandaria 132/33kV Grid Sub-Station | 2024-05-05 23:00 | 60
143 | Borhanuddin 230/33kV Grid Sub-Station | 2024-05-25 01:00 | 94
144 | Patuakhali 132/33kV Grid Sub-Station | 2024-05-05 | 102.1
145 | Payra 400/132/33kV Grid Sub-Station | 2024-05-24 23:00 | 42
146 | Amnura 132/33kV Grid Sub-Station | 2024-05-01 23:00 | 99
147 | Bhangura 132/33kV Grid Sub-Station | 2024-05-01 21:00 | 54
148 | Bog-Sherpur 132/33kV Grid Sub-Station | 2024-05-02 19:30 | 78
149 | Bogura 132/33kV Grid Sub-Station | 2024-05-01 23:00 | 197
150 | Chapai 132/33kV Grid Sub-Station | 2024-05-01 22:00 | 85
151 | Ishurdi 132/33kV Grid Sub-Station | 2024-05-05 19:30 | 91
152 | Joypurhat 132/33kV Grid Sub-Station | 2024-05-02 23:00 | 84
153 | Mahasthangarh 132/33kV Grid Sub-Station | 2024-05-01 13:00 | 94
154 | Naogaon 132/33kV Grid Sub-Station | 2024-05-01 22:00 | 162
155 | Natore 132/33kV Grid Sub-Station | 2024-05-01 21:00 | 180
156 | Niamatpur 132/33kV Grid Sub-Station | 2024-05-01 22:00 | 128
157 | Pabna 132/33kV Grid Sub-Station | 2024-05-01 23:00 | 139
158 | Rajshahi 132/33kV Grid Sub-Station | 2024-05-04 21:00 | 186
159 | Rajshahi 230/132/33kV Grid Sub-Station | 2024-05-29 | 84
160 | Ruppur 132/11kV Grid Sub-Station | 2024-05-02 15:00 | 7.2
161 | Shahjadpur 132/33kV Grid Sub-Station | 2024-05-01 20:00 | 104
162 | Sirajganj 132/33kV Grid Sub-Station | 2024-05-01 20:00 | 134
163 | Ullahpara 132/33kV Grid Sub-Station | 2024-05-26 19:00 | 34
164 | Barapukuria 230/132/33kV Grid Sub-Station | 2024-05-01 12:00 | 80
165 | Jaldhaka 132/33kV Grid Sub-Station | 2024-05-01 19:30 | 94
166 | Kurigram 132/33kV Grid Sub-Station | 2024-05-03 19:30 | 70
167 | Lalmonirhat 132/33kV Grid Sub-Station | 2024-05-29 19:00 | 63
168 | Mithapukur 132/33kV Grid Sub-Station | 2024-05-01 20:00 | 70
169 | Palashbari 132/33kV Grid Sub-Station | 2024-05-01 23:00 | 142
170 | Panchagarh 132/33kV Grid Sub-Station | 2024-05-26 20:00 | 64
171 | Purbasadipur 132/33kV Grid Sub-Station | 2024-05-27 | 154
172 | Rangpur 132/33kV Grid Sub-Station | 2024-05-26 20:00 | 166
173 | Saidpur 132/33kV Grid Sub-Station | 2024-05-25 19:30 | 128
174 | Thakurgaon 132/33kV Grid Sub-Station | 2024-05-27 | 122
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: May 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5869.44 | 2024-05-25 | 19:00
Chattogram | 1601.5 | 2024-05-23 | 13:00
Cumilla | 1539 | 2024-05-01 | 22:00
Mymensingh | 1262 | 2024-05-01 | 22:00
Sylhet | 683 | 2024-05-23 | 23:00
Khulna | 2050 | 2024-05-01 | 0:00
Barishal | 535 | 2024-05-01 | 0:00
Rajshahi | 1843.8 | 2024-05-01 | 22:00
Rangpur | 1051 | 2024-05-25 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 416 | 2024-05-27 16:00 | 364 | 2024-05-25 15:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 418 | 2024-05-27 15:00 | 371 | 2024-05-25 12:00
3 | Bibiana 400/230kV Sub-Station | 400 | 425 | 2024-05-28 05:00 | 387 | 2024-05-25 11:00
4 | BIPTC | 400 | 412 | 2024-05-27 09:00 | 388 | 2024-05-15 15:00
5 | Bogura 400/230kV Grid Sub-Station | 400 | 419 | 2024-05-05 18:30 | 364 | 2024-05-24 21:00
6 | Gopalganj 400/132kV Grid Sub-Station | 400 | 418 | 2024-05-27 16:00 | 378 | 2024-05-25 15:00
7 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 422 | 2024-05-28 05:00 | 351 | 2024-05-20 10:00
8 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 425 | 2024-05-31 20:00 | 379 | 2024-05-23 15:00
9 | Payra 400kV Sub-Station | 400 | 421 | 2024-05-28 01:00 | 398 | 2024-05-25 12:00
10 | Rahanpur 400/132kV Grid Sub-Station | 400 | 422 | 2024-05-07 04:00 | 376 | 2024-05-24 21:00
11 | Rampal 400/230kV Grid Sub-Station | 400 | 417 | 2024-05-27 15:00 | 384 | 2024-05-25 13:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 245 | 2024-05-27 16:00 | 210 | 2024-05-25 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 240 | 2024-05-28 | 200 | 2024-05-15 08:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 243 | 2024-05-27 15:00 | 215 | 2024-05-24 12:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 225 | 2024-05-27 16:00 | 202 | 2024-05-01 23:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 247 | 2024-05-08 06:00 | 224 | 2024-05-16 15:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 248 | 2024-05-27 16:00 | 222 | 2024-05-05 15:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 236 | 2024-05-27 16:00 | 208 | 2024-05-01 04:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 240 | 2024-05-28 19:30 | 209 | 2024-05-22 11:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 245 | 2024-05-27 16:00 | 216 | 2024-05-25 11:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 246 | 2024-05-28 05:00 | 222 | 2024-05-16 13:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 248 | 2024-05-27 15:00 | 220 | 2024-05-01
12 | Ghorashal 230kV Switching Sub-Station | 230 | 246 | 2024-05-27 16:00 | 213 | 2024-05-25 12:00
13 | GPH 230/33kV Grid Sub-Station | 230 | 240 | 2024-05-23 23:00 | 208 | 2024-05-22 11:00
14 | Haripur 230/132kV Grid Sub-Station | 230 | 244 | 2024-05-27 15:00 | 211 | 2024-05-25 10:00
15 | Hasnabad 230/132kV Grid Sub-Station | 230 | 247 | 2024-05-27 16:00 | 212 | 2024-05-25 12:00
16 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 240 | 2024-05-27 09:00 | 212 | 2024-05-22 11:00
17 | Ishurdi 230/132kV Grid Sub-Station | 230 | 248 | 2024-05-27 16:00 | 216 | 2024-05-24 13:00
18 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 246 | 2024-05-27 16:00 | 208 | 2024-05-24 13:00
19 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 245 | 2024-05-27 16:00 | 210 | 2024-05-25 12:00
20 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 245 | 2024-05-27 16:00 | 214 | 2024-05-24 13:00
21 | Maniknagar 230/132kV Grid Sub-Station | 230 | 245 | 2024-05-27 16:00 | 212 | 2024-05-25 11:00
22 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 250 | 2024-05-27 16:00 | 220 | 2024-05-25 11:00
23 | Mirsorai 230/33kV Grid Sub-Station | 230 | 244 | 2024-05-27 17:00 | 212 | 2024-05-07 12:00
24 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 249 | 2024-05-27 16:00 | 214 | 2024-05-24 13:00
25 | Rampura 230/132kV Grid Sub-Station | 230 | 243 | 2024-05-28 01:00 | 209 | 2024-05-25 15:00
26 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 238 | 2024-05-23 21:00 | 212 | 2024-05-07 12:00
27 | Shyampur 230/132kV Grid Sub-Station | 230 | 246 | 2024-05-27 16:00 | 212 | 2024-05-25 12:00
28 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 248 | 2024-05-28 01:00 | 214 | 2024-05-25 14:00
29 | Sirajgonj 230 kV Switching Station | 230 | 246 | 2024-05-27 16:00 | 227 | 2024-05-25 11:00
30 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 245 | 2024-05-27 16:00 | 219 | 2024-05-25 13:00
31 | Tongi 230/132/33kV Grid Sub-Station | 230 | 243 | 2024-05-27 16:00 | 210 | 2024-05-19 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 07:00 | 120 | 2024-05-30 16:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-06 16:00 | 119 | 2024-05-22 11:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-06 16:00 | 119 | 2024-05-22 11:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 118 | 2024-05-24 21:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 147 | 2024-05-28 02:00 | 132 | 2024-05-25 17:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 07:00 | 115 | 2024-05-23 19:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-06 16:00 | 121 | 2024-05-22 11:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 119 | 2024-05-25 15:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 120 | 2024-05-25 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-27 13:00 | 123 | 2024-05-01
11 | Barishal 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-08 05:00 | 118 | 2024-05-03 22:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-06 16:00 | 121 | 2024-05-22 11:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 09:00 | 113 | 2024-05-01 05:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 120 | 2024-05-02 10:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 144 | 2024-05-27 16:00 | 120 | 2024-05-13 12:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-28 02:00 | 116 | 2024-05-15 19:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-06 18:30 | 116 | 2024-05-24 13:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 17:00 | 116 | 2024-05-26 13:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-19 17:00 | 114 | 2024-05-01
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 18:00 | 124 | 2024-05-24 13:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 123 | 2024-05-24 13:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-27 15:00 | 115 | 2024-05-02 10:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 120 | 2024-05-01 03:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 16:00 | 113 | 2024-05-15 19:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 23:00 | 119 | 2024-05-25 16:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 123 | 2024-05-25 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 113 | 2024-05-02 06:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 09:00 | 121 | 2024-05-22 11:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-08 04:00 | 119 | 2024-05-24 23:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 145 | 2024-05-27 16:00 | 122 | 2024-05-25 11:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-28 11:00 | 116 | 2024-05-01 11:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-28 04:00 | 117 | 2024-05-10 14:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 23:00 | 113 | 2024-05-14 22:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 147 | 2024-05-27 07:00 | 113 | 2024-05-17 19:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 136 | 2024-05-06 18:30 | 113 | 2024-05-01 20:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 19:00 | 122 | 2024-05-20 13:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 114 | 2024-05-25 11:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 16:00 | 121 | 2024-05-25 11:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-05 23:00 | 119 | 2024-05-14 11:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 122 | 2024-05-25 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-27 09:00 | 118 | 2024-05-10 23:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-08 05:00 | 121 | 2024-05-24 23:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 121 | 2024-05-25 12:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-06 14:00 | 113 | 2024-05-01 11:00
45 | Ghatail 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 15:00 | 114 | 2024-05-24 12:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 147 | 2024-05-27 07:00 | 124 | 2024-05-14 23:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 16:00 | 125 | 2024-05-07 19:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-06 18:30 | 120 | 2024-05-31 07:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 16:00 | 121 | 2024-05-25 11:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-06 16:00 | 121 | 2024-05-20 08:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 145 | 2024-05-27 15:00 | 117 | 2024-05-07 12:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 143 | 2024-05-28 02:00 | 123 | 2024-05-25 15:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 124 | 2024-05-24 13:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-30 02:00 | 113 | 2024-05-01 03:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 115 | 2024-05-01 11:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 07:00 | 120 | 2024-05-07 19:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 07:00 | 120 | 2024-05-24 13:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 147 | 2024-05-27 18:00 | 121 | 2024-05-25 16:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 16:00 | 113 | 2024-05-01 10:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-06 16:00 | 124 | 2024-05-09 11:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 117 | 2024-05-02 10:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 16:00 | 116 | 2024-05-14 23:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 16:00 | 118 | 2024-05-25 19:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 09:00 | 120 | 2024-05-22 11:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-03 18:00 | 116 | 2024-05-25 19:00
66 | Kazla 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 18:30 | 120 | 2024-05-25 12:00
67 | Khagrachori 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-06 16:00 | 119 | 2024-05-22 11:00
68 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 07:00 | 122 | 2024-05-23 19:00
69 | Khulshi 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 09:00 | 119 | 2024-05-22 11:00
70 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 118 | 2024-05-12 10:00
71 | Kodda 132/33kV Grid Sub-Station | 132 | 147 | 2024-05-27 18:00 | 117 | 2024-05-19 14:00
72 | KSRM 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 09:00 | 122 | 2024-05-23 13:00
73 | Kulaura 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-28 | 125 | 2024-05-10 20:00
74 | Kurigram 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-27 15:00 | 113 | 2024-05-01 08:00
75 | Kushtia 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 07:00 | 120 | 2024-05-24 13:00
76 | Lalbag 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-03 18:00 | 122 | 2024-05-16 13:00
77 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-27 16:00 | 113 | 2024-05-01 19:00
78 | Madanganj 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 122 | 2024-05-25 11:00
79 | Madaripur 132/33kV Grid Sub-Station | 132 | 139 | 2024-05-07 | 123 | 2024-05-25 22:00
80 | Madartek 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 16:00 | 120 | 2024-05-25 11:00
81 | Madunaghat 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 09:00 | 120 | 2024-05-22 11:00
82 | Magura 132/33kV Grid Sub-Station | 132 | 147 | 2024-05-27 07:00 | 119 | 2024-05-24 13:00
83 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 16:00 | 118 | 2024-05-01 03:00
84 | Manikganj 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-27 15:00 | 115 | 2024-05-20 10:00
85 | Maniknagar 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 120 | 2024-05-25 12:00
86 | Matarbari 132/33kV Sub-Station | 132 | 140 | 2024-05-28 04:00 | 113 | 2024-05-03 10:00
87 | Matuail 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 16:00 | 121.4 | 2024-05-25 12:00
88 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 121 | 2024-05-02 10:00
89 | Mirpur 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-05 23:00 | 118 | 2024-05-25 15:00
90 | Mirzapur 132/33kV GIS Grid Sub-Station | 132 | 140 | 2024-05-05 21:00 | 117 | 2024-05-10 11:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 139 | 2024-05-27 16:00 | 113 | 2024-05-01 23:00
92 | MI_Cement 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 121 | 2024-05-25 12:00
93 | Modern Steel 132/11kV Grid Sub-Station | 132 | 142 | 2024-05-27 09:00 | 122 | 2024-05-12 10:00
94 | Mogbazar 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-28 01:00 | 121 | 2024-05-30 16:00
95 | Mongla 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-06 19:30 | 117 | 2024-05-19 13:00
96 | Motijheel 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 120 | 2024-05-25 12:00
97 | Munshiganj 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 121 | 2024-05-30 07:00
98 | Mymensingh 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 15:00 | 113 | 2024-05-04 11:00
99 | Naogaon 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 113 | 2024-05-01 21:00
100 | Narail 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 07:00 | 119 | 2024-05-28 19:00
101 | Narshingdi 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 114 | 2024-05-25 11:00
102 | Natore 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 10:00 | 120 | 2024-05-15 19:30
103 | Nawabganj 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-03 18:00 | 122 | 2024-05-25 11:00
104 | Netrakona 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 15:00 | 113 | 2024-05-04 12:00
105 | New Tongi 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 16:00 | 122 | 2024-05-19 11:00
106 | Niamatpur 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-07 04:00 | 121 | 2024-05-01
107 | Noapara 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 07:00 | 122 | 2024-05-07 19:00
108 | Pabna 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 121 | 2024-05-24 13:00
109 | Palashbari 132/33kV Grid Sub-Station | 132 | 139 | 2024-05-27 16:00 | 113 | 2024-05-01 08:00
110 | Panchagarh 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-30 02:00 | 113 | 2024-05-01 12:00
111 | Patuakhali 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-28 | 124 | 2024-05-03 23:00
112 | PHP 132/33kV Sub-Station | 132 | 142 | 2024-05-27 17:00 | 113 | 2024-05-01 05:00
113 | Postogola 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 15:00 | 122 | 2024-05-25 11:00
114 | Purbachal 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 120 | 2024-05-19 12:00
115 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-20 04:00 | 113 | 2024-05-01 15:00
116 | Rahim Steel 132/33kV Sub-Station | 132 | 145 | 2024-05-27 15:00 | 115 | 2024-05-20 14:00
117 | Rajbari 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 119 | 2024-05-24 13:00
118 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 16:00 | 115 | 2024-05-20 11:00
119 | Rajshahi 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 10:00 | 123 | 2024-05-01 03:00
120 | Ramganj 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 16:00 | 113 | 2024-05-01 18:30
121 | Rangamati 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-27 09:00 | 121 | 2024-05-22 11:00
122 | Rangpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-27 14:00 | 115 | 2024-05-01
123 | Ruppur 132/11kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 127 | 2024-05-24 12:00
124 | Saidpur 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-30 02:00 | 115 | 2024-05-01 11:00
125 | Satkhira 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 07:00 | 116 | 2024-05-24 21:00
126 | Satmasjid 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 07:00 | 122 | 2024-05-25 15:00
127 | Savar 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-27 07:00 | 120 | 2024-05-25 12:00
128 | SevenRings 132/11kV Sub-Station | 132 | 147 | 2024-05-05 21:00 | 127 | 2024-05-25 15:00
129 | ShahCement 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 122 | 2024-05-25 11:00
130 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 16:00 | 130 | 2024-05-24 13:00
131 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-28 06:00 | 119 | 2024-05-25 16:00
132 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 143 | 2024-05-06 16:00 | 122 | 2024-05-20 08:00
133 | Shariatpur 132/33kV Grid Sub-Station | 132 | 140 | 2024-05-06 23:00 | 120 | 2024-05-24 23:00
134 | Sherpur 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 15:00 | 113 | 2024-05-01 15:00
135 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 16:00 | 121 | 2024-05-25 12:00
136 | Sholosohor 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-06 16:00 | 119 | 2024-05-22 11:00
137 | Shyampur 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 123 | 2024-05-25 15:00
138 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 123 | 2024-05-25 11:00
139 | Sirajganj 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 10:00 | 122 | 2024-05-01
140 | Sonargaon 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 16:00 | 117 | 2024-05-03 09:00
141 | Sreemongol 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-28 05:00 | 120 | 2024-05-25 17:00
142 | Srinagar 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 07:00 | 122 | 2024-05-25 11:00
143 | SSM 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-06 19:00 | 125 | 2024-05-12 05:00
144 | Sunamganj 132/33kV Grid Sub-Station | 132 | 138 | 2024-05-27 23:00 | 115 | 2024-05-13 21:00
145 | Sylhet (South) 132/33kV GIS Grid Sub-Station | 132 | 137 | 2024-05-28 03:00 | 118 | 2024-05-11 12:00
146 | Sylhet 132/33kV Grid Sub-Station | 132 | 137 | 2024-05-28 03:00 | 120 | 2024-05-10 15:00
147 | Tangail 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-27 15:00 | 113 | 2024-05-15 13:00
148 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-30 02:00 | 113 | 2024-05-01 15:00
149 | TK chemical 132kV Grid Sub-Station | 132 | 140 | 2024-05-27 09:00 | 122 | 2024-05-09 16:00
150 | Ullahpara 132/33kV Grid Sub-Station | 132 | 146 | 2024-05-27 16:00 | 125 | 2024-05-24 12:00
151 | Ullon 132/33kV Grid Sub-Station | 132 | 142 | 2024-05-28 03:00 | 121 | 2024-05-25 11:00
152 | Uttara 132/33kV Grid Sub-Station | 132 | 145 | 2024-05-27 07:00 | 118 | 2024-05-25 15:00
153 | UttaraNew 132/33kV Grid Sub-Station | 132 | 144 | 2024-05-27 07:00 | 120 | 2024-05-25 15:00
154 | Zigatola 132/33kV Grid Sub-Station | 132 | 141 | 2024-05-03 07:00 | 122 | 2024-05-25 12:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: May 2024
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 415 | 446.9687 | 2024-05-25 15:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 415 | 446.9687 | 2024-05-25 15:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -259 | 281.7836 | 2024-05-02 11:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 259 | 281.7836 | 2024-05-02 11:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -217 | 217.5178 | 2024-05-10 11:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -208 | 208.1538 | 2024-05-10 11:00
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 388 | 388.0464 | 2024-05-26 21:00
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 493 | 495.529 | 2024-05-29 17:00
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 493 | 495.529 | 2024-05-29 17:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 232 | 261.6582 | 2024-05-25 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 232 | 261.6582 | 2024-05-25 21:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 486 | 558.4093 | 2024-05-22 08:00
Meghnaghat 400/230kV Grid Sub-Station | ATR - 2 | 400/230 | -493 | 533.9232 | 2024-05-04 23:00
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | -418 | 591.1413 | 2024-05-30 01:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -377.97 | 391.0491 | 2024-05-05 23:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -374.06 | 387.0802 | 2024-05-05 23:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 278 | 282.4606 | 2024-05-25 09:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -323 | 329.8757 | 2024-05-05 21:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -289 | 296.4406 | 2024-05-16 21:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -323 | 329.8757 | 2024-05-05 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 314 | 316.1724 | 2024-05-13 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 314 | 316.1724 | 2024-05-13 21:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -102 | 112.3076 | 2024-05-05 23:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -107 | 116.8674 | 2024-05-06
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 221 | 233.3795 | 2024-05-12 13:00
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 221 | 237.5079 | 2024-05-21 14:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 180 | 254.5584 | 2024-05-19 14:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 180 | 254.5584 | 2024-05-19 14:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 161 | 174.3846 | 2024-05-28 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 161 | 174.3846 | 2024-05-28 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 166 | 181.3422 | 2024-05-28 10:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 280 | 300.8322 | 2024-05-08 06:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 192 | 194.3296 | 2024-05-03 14:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 182 | 200.4495 | 2024-05-05 21:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 170 | 187.8829 | 2024-05-17 07:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 190 | 197.2536 | 2024-05-25 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 187 | 203.7891 | 2024-05-25 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 243 | 253.4423 | 2024-05-25 19:30
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 172 | 174.7713 | 2024-05-17 20:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 172 | 174.7713 | 2024-05-17 20:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -410 | 417.9246 | 2024-05-11 13:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -112 | 112.2854 | 2024-05-24 19:30
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 186 | 194.5379 | 2024-05-01 05:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 186 | 194.5379 | 2024-05-01 05:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 255 | 266.6627 | 2024-05-02 05:00
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 225 | 232.607 | 2024-05-24 13:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 187 | 195.4942 | 2024-05-13 12:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 185 | 193.2899 | 2024-05-13 12:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 187 | 194.6407 | 2024-05-24 02:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 258 | 274.9345 | 2024-05-17 18:30
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 103 | 103 | 2024-05-13 18:30
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 103 | 103 | 2024-05-13 18:30
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 125 | 167.8362 | 2024-05-07 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 138 | 174.0115 | 2024-05-22 08:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 128 | 174.7713 | 2024-05-07 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 80 | 89 | 2024-05-22 10:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 80 | 89 | 2024-05-22 10:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 80 | 89 | 2024-05-22 10:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 99 | 146.5094 | 2024-05-17 11:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 99 | 146.5094 | 2024-05-17 11:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 99 | 146.5094 | 2024-05-17 11:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 99 | 146.5094 | 2024-05-17 11:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 102 | 133.4166 | 2024-05-24 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 102 | 133.4166 | 2024-05-24 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 102 | 133.4166 | 2024-05-24 22:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -219 | 245.5239 | 2024-05-02 23:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -219 | 245.5239 | 2024-05-02 23:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 140 | 156.5248 | 2024-05-02 18:30
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 194 | 205.5724 | 2024-05-05 19:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 128 | 136.7041 | 2024-05-25 17:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 194 | 205.5724 | 2024-05-05 19:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -155 | 168.0774 | 2024-05-18 15:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -154 | 167.547 | 2024-05-14 23:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -319 | 323.7067 | 2024-05-15
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 236 | 243.2632 | 2024-05-22 16:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 213 | 230.8463 | 2024-05-12 16:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -112 | 114.9783 | 2024-05-12 11:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -141 | 148.0068 | 2024-05-15 12:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 10 | 10 | 2024-05-17 13:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1 | 2024-05-14 06:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 174 | 227.7828 | 2024-05-05 06:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 359 | 360.5135 | 2024-05-01 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 318 | 323.6109 | 2024-05-25 15:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 233 | 271.3116 | 2024-05-04 18:30
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 276 | 285.2367 | 2024-05-31 19:30
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 145 | 157.3086 | 2024-05-22 11:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 145 | 157.3086 | 2024-05-22 11:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 148 | 196.3288 | 2024-05-30 08:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | -212 | 213.9743 | 2024-05-20 21:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 175 | 183.7417 | 2024-05-02 10:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 175 | 183.7417 | 2024-05-02 10:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 227.1255 | 2024-05-03 18:30
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 227.1255 | 2024-05-03 18:30
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 227.1255 | 2024-05-03 18:30
Executive Engineer
Information Management Division
|  |  |  | LDC, PGCB, Dhaka. |  | 270

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [14 empty] | Report on load shedding
Month: May 2024 |  |  |  |  | (For Evening Peak) | [9 empty] | Month: May 2024 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-05-01 | 15559 | 15850 | 278 | 21:00 | 70 | 0 | 9 | 0 | 30 | 115 | 0 | 0 | 54 | - | 2024-05-01 | 13007 | 13400 | 375 | 12:00 | 55 | 0 | 0 | 0 | 60 | 190 | 0 | 0 | 70 | -
2024-05-02 | 15360 | 15850 | 468 | 21:00 | 161 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 112 | - | 2024-05-02 | 14149 | 14700 | 526 | 12:00 | 200 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 5 | -
2024-05-03 | 14929 | 15075 | 139 | 21:00 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | - | 2024-05-03 | 13172 | 13580 | 390 | 12:00 | 145 | 0 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | -
2024-05-04 | 15229 | 15600 | 354 | 19:30 | 28 | 45 | 11 | 0 | 127 | 90 | 0 | 0 | 53 | - | 2024-05-04 | 13800 | 14000 | 191 | 12:00 | 100 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | -
2024-05-05 | 14353 | 14400 | 45 | 19:00 | 35 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-05 | 13207 | 13260 | 51 | 12:00 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-06 | 9522 | 9522 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-06 | 11237 | 11237 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-07 | 13638 | 13638 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-07 | 11356 | 11356 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-08 | 12781 | 12781 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-08 | 10663 | 10663 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-09 | 12487 | 12487 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-09 | 12241 | 12241 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-10 | 12787 | 12787 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-10 | 10639 | 10725 | 82 | 12:00 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | -
2024-05-11 | 13341 | 13341 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-11 | 10559 | 10559 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-12 | 14165 | 14202 | 35 | 19:30 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | - | 2024-05-12 | 12356 | 12500 | 138 | 12:00 | 48 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | -
2024-05-13 | 15019 | 15150 | 125 | 19:30 | 0 | 0 | 0 | 0 | 20 | 80 | 0 | 0 | 25 | - | 2024-05-13 | 12870 | 12905 | 33 | 12:00 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | -
2024-05-14 | 15435 | 15700 | 253 | 19:30 | 50 | 0 | 0 | 0 | 0 | 128 | 10 | 0 | 65 | - | 2024-05-14 | 13701 | 13850 | 142 | 12:00 | 102 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | -
2024-05-15 | 15687 | 16100 | 394 | 19:30 | 100 | 0 | 0 | 0 | 20 | 179 | 0 | 0 | 95 | - | 2024-05-15 | 13995 | 14200 | 196 | 12:00 | 86 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | -
2024-05-16 | 14965 | 15850 | 845 | 21:00 | 205 | 80 | 0 | 90 | 130 | 180 | 35 | 0 | 125 | - | 2024-05-16 | 14488 | 14870 | 365 | 12:00 | 210 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | -
2024-05-17 | 15498 | 15700 | 193 | 21:00 | 0 | 0 | 0 | 0 | 50 | 90 | 0 | 0 | 53 | - | 2024-05-17 | 13667 | 13770 | 88 | 12:00 | 15 | 0 | 0 | 0 | 10 | 63 | 0 | 0 | 0 | -
2024-05-18 | 14628 | 14628 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-18 | 11925 | 12030 | 100 | 12:00 | 0 | 0 | 0 | 10 | 90 | 0 | 0 | 0 | 0 | -
2024-05-19 | 14206 | 14300 | 90 | 19:30 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-19 | 13540 | 13640 | 96 | 12:00 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-20 | 14219 | 14376 | 150 | 19:30 | 100 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | - | 2024-05-20 | 12911 | 13030 | 114 | 12:00 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-21 | 15519 | 15585 | 63 | 20:00 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | - | 2024-05-21 | 13300 | 13300 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-22 | 15428 | 15550 | 117 | 21:00 | 25 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | - | 2024-05-22 | 12563 | 12640 | 74 | 12:00 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-23 | 16067 | 16400 | 318 | 21:00 | 100 | 0 | 0 | 0 | 35 | 150 | 0 | 0 | 33 | - | 2024-05-23 | 14166 | 14400 | 223 | 12:00 | 113 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | -
2024-05-24 | 15601 | 15850 | 238 | 21:00 | 0 | 0 | 0 | 0 | 35 | 145 | 18 | 0 | 40 | - | 2024-05-24 | 13454 | 13454 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-25 | 14623 | 14900 | 265 | 19:30 | 75 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | - | 2024-05-25 | 13726 | 13950 | 214 | 12:00 | 120 | 40 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | -
2024-05-26 | 13435 | 13560 | 119 | 19:30 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 69 | - | 2024-05-26 | 12667 | 13100 | 414 | 12:00 | 290 | 0 | 0 | 0 | 24 | 100 | 0 | 0 | 0 | -
2024-05-27 | 4554 | 4554 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-27 | 5323 | 5323 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-28 | 12451 | 12451 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-05-28 | 8051 | 8180 | 123 | 12:00 | 100 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-05-29 | 14585 | 14700 | 110 | 21:00 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 65 |  | 2024-05-29 | 12459 | 12459 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-05-30 | 14552 | 14600 | 46 | 21:00 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-05-30 | 12485 | 13000 | 492 | 12:00 | 220 | 100 | 95 | 0 | 77 | 0 | 0 | 0 | 0
2024-05-31 | 14028 | 14200 | 164 | 21:00 | 95 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 |  | 2024-05-31 | 11614 | 11700 | 82 | 12:00 | 72 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: May 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 16067 | 2024-05-23 | 21:00
2 | Maximum Day Peak Genaration | MW | 14488 | 2024-05-16 | 12:00
3 | Maximum Evening Peak Demand | MW | 16400 | 2024-05-23 | 21:00
4 | Minimum Generation | MW | 3651 | 2024-05-28 | 6:00
5 | Average of the daily evening peak Genaration | MW | 14021 | - | -
6 | Average of the daily day peak Genaration | MW | 12364.2258 | - | -
7 | Maximum load shed (Evening Peak) | MW | 845 | 2024-05-16 | 21:00
8 | Minimum load shed | MW | 0 | 2024-05-11 | 19:30
9 | Total nos. of load shed days | Day | 22 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 154.8333 | - | -
11 | Total Generation | MkWh | 9342.0397 | - | -
12 | Total Generation by BPDB | MkWh | 2216.8164 | % of total Gen. | 23.73%
13 | Total Generation by IPP | MkWh | 2951.6562 | '' | 31.6%
14 | A) Total Generation by Generation Companies | MkWh | 2617.8799 | '' | 28.02%
| B) Total Generation by REB | MkWh | 99.879 | " | 1.069%
| C) Total Generation by RENTAL | MkWh | 239.9743 | " | 2.569%
| D) Total Imported from India (BIPTC) | MkWh | 580.4555 | " | 6.213%
| E) Total Imported from Tripura, India (A.C) | MkWh | 635.3784 | " | 6.801%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4771.0834 | % of total Gen. | 51.07%
| B) Oil | MkWh | 1316.47 | '' | 14.09%
| C) Hydro | MkWh | 22.2695 | '' | 0.2384%
| D) Solar | MkWh | 89.3041 | '' | 0.9559%
| E) Coal | MkWh | 2487.2899 | '' | 26.62%
| F) BIPTC (Import from India) | MkWh | 580.4555 | '' | 6.213%
| G) A.C (Import from Tripura, India) | MkWh | 65.879 | '' | 0.7052%
| H) Wind | MkWh | 9.2856 | '' | 0.0994%
16 | Maximun of the daily total Generation . | MkWh | 347.857 | 2024-05-16
17 | Monthly Load factor | % | 78.2556 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 52663.0922 | - | -
| A) Gas | M.Taka | 13524.948 | - | -
| B) Liquid fuel | M.Taka | 20996.1135 | - | -
| C) Coal | M.Taka | 15203.2596 | - | -
| D) BIPTC (Import from India) | M.Taka | 2368.2586 | - | -
| E) Tripura(Import from India) | M.Taka | 570.5125 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2483.716 | 2024-05-18
| A) Gas | M.Taka | 500.9852 | 2024-05-13
| B) Liquid fuel | M.Taka | 1338.9485 | 2024-05-18
| C) Coal | M.Taka | 761.2792 | 2024-05-18
| D) BIPTC (Import from India) | M.Taka | 86.4812 | 2024-05-12
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.6372
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 5.7111
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/2024 | 06:00
b) | Actual | FT (MSL) | 79.53 | 31/05/2024 | 6:00
22 | Peak Genaration of May 2023 | MW | 14511 | 2023-05-30 | 21:00
23 | Peak Demand of May 2023 | MW | 15600 | 2023-05-31 | 21:00
24 | Maximum peak Generation recorded upto 31/05/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/05/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/05/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: May 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | [6 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | √ | √
9 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | [5 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | [11 empty] | √
10 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  |  |  | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | √ | √ | √ | √ |  |  |  |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  |  | √ | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410 | [20 empty] | √ | √ | √ | √ | √
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [6 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable |  |  |  |  | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant