## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-10 | Wednesday
|  | Date (day): | 2024-07-10 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14435.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15794 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-09 | 2024-07-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage |  | 16-07-24
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 400 | 320 | 350 | 50 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 360 | 200 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 52 | 92 | 80 | 92 |  | 8 | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 155 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 50 | 82 | 80 | 82 |  | 20 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 13 |  | 62 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 58 | 50 | 60 | 40 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 312 | 297 | 250 | 250
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 49 | 90 | 50 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 146 | 48 | 146
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 17 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 30 | 30 | 30 |  | 50 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 16 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 10 | 10 | 10 |  | 23 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 80 | 148 | 145 | 145 | 155 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 64 | 95 | 95 | 95 | 54 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 17 | 17 | 17 | 88 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 87 | 70 | 70 | 34 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 54 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 11 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 12 | 17 | 17 | 17 |  | 38 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 2051 | 2472 | 1824 | 2217 | 2091 | 1181
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 4 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 12 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 166 | 166 | 166 | 64 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 222 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 68 | 40 | 68 | 37 |  | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 71 | 71 | 70 | 71 | 27 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 68 | 85 | 85 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 70 | 58 | 50 | 58 | 42 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 49 | 62 | 34 | 52 | 48 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 15 | 5 | 15
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 28 | 38 | 32 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 52 | 69 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 92 | 73 | 92 |  | 18 | Engine problem
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 62 | 50 | 50 | 50 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 38 | 35 | 35 | 35 | 81 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 163 | 54 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 606 | 610 | 900 | 1200
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 19 | 10 | 44 | 62 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 519 | 519 | 510 | 520 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 36 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 2221 | 2466 | 2627 | 3068 | 855 | 365
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 215 | 215 | 215
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 290 | 280 | 290 | 70 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 240 | 240 | 240 | 120 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 280 | 285 | 250 | 290 | 110 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 35 | 30 | 35 | 10 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 10 | 42 | 20 | 42 | 13 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 45 | 137 | 130 | 137 |  | 13 | Engine problem
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 37 | 36 | 37 |  | 15 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 31 | 30 | 30 | 133 |  | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 74 | 90 | 100
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 33 | 33 | 33 | 33
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 88 | 70 | 88 | 26 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 46 | 94 | 46 | 94 |  | 19 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 93 | 33 | 93 |  | 22 | Engine problem
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1536 | 1779 | 1580 | 1801 | 860 | 118
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 11 | 18 | 20 | 20 | 182 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 107 | 161 | 116 | 160 | 40 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 57 | 66 | 60 | 70 | 45 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 22 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 1 | 6 | 6 | 16 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 221 | 263 | 270.6 | 273 | 182 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 27 | 0 | 0 | 0 |  | 70 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 54 | 54 | 54 | 54 |  | 36 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 50 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 39 | 40 | 40 |  | 10 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 2 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 56 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 206 | 211 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 12 | 12 | 12 | 12 | 8 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 15 | 0 | 150 | 200 | 141 |  | Gas shortage
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 392 | 402 | 400 | 400 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 371 | 390 | 340 | 390 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1394 | 1397 | 1493 | 1597 | 149 | 486
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 917 | 937 | 937
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 63 | 95 | 77 | 98 | 17 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 30 | 42 |  | 12 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 53 | 50 | 53 |  | 56 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 311 | 314 | 300 | 315 | 95 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 16 | 8 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 91 | 25 | 90 |  | 15 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 73 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 338 | 337 | 340 | 340 | 384 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1737 | 1857 | 1867 | 1883 | 1110 | 83
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 125 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1110 | 1200 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 27 | 54 | 35 | 54 | 96 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 150 | 150 | 150 | 157 |  | Coal shoratge
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1660 | 1874 | 1850 | 1918 | 253 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0 |  |  | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 36 | 42 |  | 8 | Engine problem
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 172 | 184 | 180 | 210
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 354 | 350 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 44 | 85 | 50 | 85 |  | 19 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 113 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1313 | 1503 | 1400 | 1515
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 56 | 0 | 5 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 2072 | 2479 | 2307 | 2577 | 663 | 126
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 60 | 60 | 60 |  | 25
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 200 | 200 | 200 |  | 74 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 103 | 106 | 99 | 106 |  | 7 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 52 | 94 | 90 | 94 |  | 21 | Engine problem
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 17 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 69 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 523 | 460 | 617 | 460 | 40 | 212
| Total |  |  |  |  | 27515 | 26364 | 13415 | 15047 | 14435.6 | 15794 | 6203 | 2635
A. |  | 2024-07-09 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 15047 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12564 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15450 | MW
3 | Day peak Generation : |  |  | 13415 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14767.64 | MW
4 | Evening peak Generation : |  |  | 15047 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 385 | MW
5 | Total Energy Generation : |  | 330.1629 | MKWHr | By Solar | 3.0814 | MKWHr
| By Gas : | 127.9319 | MKWHr |  | By Oil: | 62.4508 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 108.1456 | MKWHr |  | By Hydro: | 4.0136 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.42048 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6203 | MW | Dhaka | 5193.04 | 5003.04 |  | 190 |  | 18:00 |  | 275
|  |  | For Plants S/D or M/C prob = |  |  | 2635 | MW | Chittagong | 1470.9 | 1470.9 |  | 0 |  | 19:00 |  | 209.145
|  |  | Total = |  |  | 8838 | MW | Khulna | 1860.9 | 1860.9 |  | 0 |  | 19:30 |  | 473.68
7 | Total Gas Supplied : |  |  | 917.83 | MMCFD |  |  | Rajshahi | 1563.8 | 1501.8 |  | 62 |  | 20:00 |  | 403.965
8 | Fuel Cost : | i) Gas : | Taka | 387350220.51 | ii) Oil : | Taka | 1140260732.21 | Comilla | 1383 | 1365 |  | 18 |  | 21:00 |  | 384.865
|  | iii) Coal : | Taka | 731810848.84 | Total | Taka | 2259421801.56 | Mymensingh | 1185 | 1070 |  | 115 |  | 22:00 |  | 421.155
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 10241.55 | MKWHr. | Sylhet | 606 | 606 |  | 0 |  | 23:00 |  | 911.07
| ii) During Peak Demand : |  |  | 1008 | MW (W to E) at | 21:00 | hrs | Barisal | 500 | 500 |  | 0 |  | 24:00 |  | 1018.03
| iii) Maximum : |  |  | 1008 | MW at | 21:00 | hrs | Rangpur | 1005 | 1005 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.1°C |  |  | Total | 14767.64 | 14382.64 |  | 385
B. |  | 2024-07-10 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15794 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14300 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 346.6853 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12664 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2394 | MKWHr. | ii) HVDC Flow at Peak Time |  | 917 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8797 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.96 |  | (b) Today: | 94.42 |  | (c) Rule Curve: |  | 85.44

## YesterdayGen
2024-07-09 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 420 | 138 | 24 | 82 | 15 | 322 | 0 | 0 | 50 | 24 | 82 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 15 | 15 | 16 | 12 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 72 | 78 | 80 | 28 | 26 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 37 | 34 | 0 | 0 | 0 | 17 | 82 | 22 | 0 | 0 | 0 | 30 | 54 | 50 | 40 | 163 | 0 | 59 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 2 | 0 | 47 | 0 | 0 | 117 | 0 | 97 | 0 | 49 | 17 | 113 | 402 | 67 | 17 | 51 | 0 | 55 | 54 | 92 | 17 | 52 | 50 | 346 | 34 | 0 | 54 | 53 | 0 | 36 | 0 | 50 | 17 | 280 | 17 | 0 | 605 | 11 | 520 | 0 | 0 | 0 |  | 919 | 0 | 305 | 0 | 94 | 0 | 0 | 0 | 20 | 41 | 32 | 126 | 10 | 16 | 0 | 0 | 0 | 32 | 0 | 56 | 0 | 0 | 25 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 86 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 303 | 54 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1222 | 220 | 0 | 27 | 0 | 0 | 35 | 0 | 0 | 341 | 0 | 200 | 1503 | 0 | 0 | 0 | 0 |  | 7413 | 6473 | 13886 | 3966 | 919 | 1434 | 0 | 2168 | 4651 | 165 | 0 | 490 | 82 | 0 | 11 | 968.37 | 93.81
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 420 | 135 | 25 | 82 | 15 | 326 | 0 | 0 | 50 | 24 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 15 | 15 | 16 | 12 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 72 | 85 | 80 | 25 | 26 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 42 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 82 | 22 | 0 | 0 | 0 | 27 | 54 | 50 | 40 | 163 | 0 | 59 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 2 | 0 | 47 | 0 | 0 | 117 | 0 | 97 | 0 | 49 | 17 | 140 | 402 | 67 | 17 | 51 | 0 | 65 | 54 | 92 | 17 | 46 | 50 | 346 | 34 | 0 | 54 | 37 | 0 | 36 | 0 | 48 | 17 | 280 | 17 | 0 | 604 | 20 | 516 | 0 | 0 | 0 |  | 918 | 0 | 305 | 0 | 95 | 0 | 0 | 0 | 20 | 38 | 32 | 126 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 132 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 305 | 54 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1222 | 220 | 0 | 27 | 0 | 0 | 35 | 0 | 0 | 340 | 0 | 200 | 1509 | 0 | 0 | 0 | 0 |  | 7366 | 6460 | 13826 | 4016 | 918 | 1433 | 0 | 2161 | 4651 | 165 | 0 | 380 | 82 | 0 | 20 | 662.77 | 93.84
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 420 | 138 | 25 | 82 | 15 | 327 | 0 | 0 | 50 | 24 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 15 | 15 | 16 | 12 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 72 | 85 | 80 | 25 | 26 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 42 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 82 | 22 | 0 | 0 | 0 | 27 | 54 | 50 | 40 | 163 | 0 | 59 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 2 | 0 | 47 | 0 | 0 | 117 | 0 | 97 | 0 | 49 | 17 | 142 | 402 | 67 | 17 | 51 | 0 | 69 | 54 | 92 | 17 | 47 | 50 | 346 | 17 | 0 | 17 | 53 | 0 | 36 | 0 | 32 | 0 | 280 | 17 | 0 | 605 | 20 | 517 | 0 | 0 | 0 |  | 919 | 0 | 300 | 0 | 95 | 0 | 0 | 0 | 20 | 38 | 32 | 126 | 9 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 0 | 30 | 0 | 0 | 5 | 59 | 0 | 200 | 0 | 0 | 214 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 322 | 54 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1120 | 220 | 0 | 27 | 0 | 0 | 35 | 0 | 0 | 336 | 0 | 200 | 1414 | 0 | 0 | 0 | 0 |  | 7324 | 6352 | 13676 | 4092 | 919 | 1452 | 0 | 2115 | 4451 | 165 | 0 | 380 | 82 | 0 | 20 | 452.67 | 93.87
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 420 | 141 | 24 | 82 | 15 | 327 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 15 | 15 | 16 | 12 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 72 | 85 | 80 | 25 | 26 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 42 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 76 | 23 | 0 | 0 | 0 | 27 | 54 | 50 | 40 | 163 | 0 | 59 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 2 | 0 | 47 | 0 | 0 | 117 | 0 | 97 | 0 | 49 | 17 | 140 | 401 | 67 | 17 | 51 | 0 | 69 | 54 | 92 | 17 | 47 | 50 | 346 | 17 | 0 | 17 | 53 | 0 | 36 | 0 | 33 | 0 | 280 | 17 | 0 | 600 | 6 | 516 | 0 | 0 | 0 |  | 920 | 0 | 300 | 0 | 95 | 0 | 0 | 0 | 20 | 38 | 32 | 126 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 200 | 0 | 0 | 214 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 330 | 54 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 1080 | 220 | 0 | 27 | 0 | 0 | 35 | 0 | 0 | 338 | 0 | 200 | 1415 | 0 | 0 | 0 | 0 |  | 7282 | 6162 | 13444 | 4084 | 920 | 1464 | 0 | 1987 | 4408 | 165 | 0 | 334 | 76 | 0 | 6 | 435.48 | 93.9
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 420 | 143 | 25 | 70 | 23 | 327 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 15 | 15 | 16 | 12 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 72 | 85 | 80 | 25 | 26 | 0 | 38 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 76 | 23 | 0 | 0 | 0 | 27 | 54 | 50 | 39 | 163 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 2 | 0 | 47 | 0 | 0 | 117 | 0 | 89 | 0 | 48 | 17 | 137 | 403 | 68 | 17 | 51 | 0 | 69 | 54 | 81 | 17 | 47 | 50 | 346 | 17 | 0 | 17 | 53 | 0 | 36 | 0 | 33 | 0 | 280 | 17 | 0 | 557 | 5 | 518 | 0 | 0 | 0 |  | 920 | 0 | 300 | 0 | 79 | 0 | 0 | 0 | 20 | 38 | 32 | 126 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 200 | 0 | 0 | 214 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 342 | 54 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 1060 | 220 | 0 | 27 | 0 | 0 | 35 | 0 | 0 | 340 | 0 | 200 | 1315 | 0 | 0 | 0 | 0 |  | 7216 | 5981 | 13197 | 4048 | 920 | 1478 | 0 | 1946 | 4250 | 165 | 0 | 309 | 76 | 0 | 5 | 432.615 | 93.93
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 |  | 0 | 450 | 139 | 25 | 70 | 30 | 260 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 15 | 15 | 16 | 7 | 0 | 0 | 85 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 72 | 85 | 80 | 25 | 26 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 42 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 70 | 23 | 0 | 0 | 0 | 27 | 54 | 50 | 39 | 120 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 47 | 0 | 0 | 117 | 0 | 93 | 0 | 48 | 17 | 135 | 401 | 67 | 17 | 51 | 0 | 69 | 54 | 78 | 17 | 47 | 50 | 310 | 17 | 1 | 17 | 53 | 0 | 20 | 0 | 32 | 0 | 330 | 17 | 0 | 468 | 20 | 517 | 0 | 0 | 3 |  | 919 | 0 | 300 | 0 | 79 | 0 | 0 | 0 | 20 | 38 | 32 | 126 | 9 | 16 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 17 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 980 | 220 | 0 | 27 | 0 | 2 | 35 | 0 | 0 | 341 | 1 | 200 | 1315 | 7 | 0 | 0 | 3 |  | 7032 | 5721 | 12753 | 3828 | 919 | 1447 | 0 | 1897 | 4081 | 165 | 0 | 309 | 70 | 17 | 20 | 350.485 | 93.96
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 138 | 25 | 57 | 30 | 260 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 15 | 15 | 16 | 0 | 8 | 0 | 85 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 72 | 85 | 80 | 27 | 26 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 58 | 20 | 0 | 0 | 0 | 27 | 54 | 50 | 39 | 120 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 47 | 0 | 0 | 117 | 0 | 81 | 1 | 48 | 17 | 85 | 403 | 67 | 17 | 51 | 0 | 69 | 54 | 72 | 17 | 46 | 50 | 310 | 17 | 8 | 17 | 53 | 0 | 17 | 6 | 33 | 0 | 280 | 17 | 0 | 452 | 5 | 515 | 0 | 0 | 5 |  | 920 | 0 | 300 | 0 | 79 | 0 | 0 | 0 | 20 | 38 | 32 | 126 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 17 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 1000 | 220 | 0 | 27 | 1 | 16 | 35 | 0 | 0 | 340 | 2 | 200 | 1317 | 40 | 0 | 0 | 14 |  | 6794 | 5774 | 12568 | 3730 | 920 | 1442 | 0 | 1787 | 4083 | 165 | 0 | 285 | 58 | 93 | 5 | 317.06 | 93.99
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 148 | 25 | 66 | 30 | 260 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 15 | 15 | 16 | 7 | 8 | 0 | 85 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 72 | 85 | 70 | 32 | 26 | 0 | 5 | 0 | 0 | 0 | 300 | 250 | 217 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 66 | 20 | 0 | 0 | 1 | 27 | 54 | 50 | 39 | 120 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 47 | 0 | 0 | 117 | 0 | 97 | 4 | 36 | 17 | 50 | 352 | 66 | 17 | 51 | 1 | 52 | 54 | 73 | 17 | 47 | 50 | 310 | 17 | 11 | 17 | 53 | 0 | 17 | 11 | 32 | 0 | 240 | 17 | 0 | 455 | 15 | 518 | 0 | 0 | 19 |  | 919 | 0 | 300 | 0 | 77 | 0 | 0 | 0 | 2 | 0 | 32 | 126 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 200 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 339 | 17 | 0 | 50 | 0 | 98 | 0 | 0 | 50 | 980 | 220 | 0 | 27 | 2 | 53 | 35 | 0 | 0 | 340 | 4 | 200 | 1322 | 102 | 0 | 0 | 22 |  | 6745 | 5819 | 12564 | 3683 | 919 | 1432 | 0 | 1751 | 4074 | 165 | 0 | 229 | 66 | 230 | 15 | 311.33 | 94.02
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 |  | 0 | 450 | 138 | 25 | 66 | 30 | 260 | 0 | 0 | 50 | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 2 | 0 | 15 | 15 | 16 | 7 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 72 | 76 | 70 | 26 | 26 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 0 | 66 | 17 | 0 | 0 | 1 | 27 | 55 | 50 | 36 | 163 | 0 | 58 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 47 | 0 | 0 | 108 | 0 | 82 | 6 | 25 | 17 | 50 | 403 | 65 | 17 | 51 | 3 | 52 | 54 | 73 | 17 | 52 | 50 | 310 | 17 | 29 | 17 | 53 | 0 | 17 | 15 | 44 | 0 | 240 | 17 | 0 | 510 | 17 | 518 | 0 | 0 | 26 |  | 918 | 0 | 305 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 32 | 126 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 17 | 0 | 50 | 0 | 84 | 0 | 0 | 50 | 990 | 220 | 0 | 27 | 2 | 51 | 35 | 0 | 0 | 339 | 4 | 200 | 1319 | 73 | 0 | 0 | 21 |  | 6870 | 5852 | 12722 | 3717 | 918 | 1519 | 0 | 1714 | 4156 | 166 | 0 | 218 | 66 | 231 | 17 | 284.59 | 94.05
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 151 | 32 | 66 | 30 | 320 | 0 | 0 | 50 | 32 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 16 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 72 | 85 | 70 | 25 | 26 | 0 | 2 | 0 | 0 | 0 | 310 | 270 | 213 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 78 | 16 | 0 | 0 | 1 | 27 | 56 | 47 | 36 | 163 | 0 | 57 | 0 | 0 | 206 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 45 | 0 | 0 | 117 | 0 | 80 | 9 | 25 | 17 | 50 | 404 | 65 | 35 | 51 | 2 | 52 | 54 | 73 | 17 | 46 | 50 | 371 | 17 | 28 | 72 | 53 | 0 | 17 | 20 | 49 | 0 | 270 | 54 | 0 | 553 | 4 | 517 | 0 | 0 | 49 |  | 919 | 0 | 305 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 32 | 126 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 220 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 50 | 0 | 84 | 0 | 2 | 50 | 990 | 220 | 0 | 27 | 3 | 65 | 35 | 0 | 0 | 342 | 13 | 150 | 1319 | 115 | 0 | 0 | 26 |  | 7378 | 5783 | 13161 | 3928 | 919 | 1479 | 0 | 1824 | 4150 | 166 | 0 | 280 | 78 | 333 | 4 | 419.245 | 94.08
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 140 | 46 | 50 | 30 | 320 | 0 | 0 | 50 | 49 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 71 | 68 | 70 | 25 | 30 | 0 | 2 | 0 | 0 | 0 | 280 | 275 | 213 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 80 | 11 | 0 | 0 | 2 | 27 | 54 | 46 | 36 | 163 | 0 | 57 | 0 | 0 | 208 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 57 | 0 | 0 | 116 | 0 | 71 | 16 | 36 | 17 | 52 | 404 | 65 | 35 | 51 | 4 | 52 | 54 | 60 | 17 | 47 | 50 | 346 | 17 | 20 | 90 | 53 | 0 | 17 | 18 | 49 | 0 | 300 | 54 | 0 | 601 | 4 | 518 | 0 | 0 | 32 |  | 919 | 0 | 305 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 59 | 0 | 220 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 17 | 0 | 50 | 0 | 97 | 0 | 2 | 50 | 1090 | 220 | 0 | 27 | 6 | 54 | 48 | 0 | 0 | 338 | 22 | 150 | 1322 | 154 | 0 | 0 | 59 |  | 7406 | 5927 | 13333 | 3904 | 919 | 1438 | 0 | 1874 | 4298 | 166 | 0 | 261 | 80 | 389 | 4 | 541.485 | 94.11
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 150 | 52 | 50 | 30 | 312 | 0 | 0 | 50 | 49 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 71 | 68 | 70 | 28 | 12 | 0 | 0 | 0 | 0 | 0 | 325 | 280 | 197 | 0 | 40 | 20 | 10 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 80 | 11 | 0 | 0 | 1 | 27 | 54 | 47 | 36 | 163 | 0 | 54 | 0 | 0 | 206 | 12 | 0 | 0 | 15 | 12 | 5 | 0 | 80 | 0 | 0 | 107 | 0 | 64 | 4 | 49 | 17 | 45 | 392 | 57 | 35 | 51 | 4 | 52 | 54 | 54 | 17 | 46 | 50 | 371 | 17 | 22 | 108 | 38 | 0 | 17 | 11 | 50 | 12 | 280 | 54 | 0 | 606 | 19 | 519 | 0 | 0 | 36 |  | 919 | 0 | 311 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 17 | 0 | 35 | 0 | 103 | 0 | 2 | 50 | 1110 | 220 | 0 | 27 | 3 | 73 | 52 | 0 | 0 | 338 | 17 | 150 | 1313 | 69 | 0 | 0 | 56 |  | 7423 | 5992 | 13415 | 3914 | 919 | 1508 | 0 | 1874 | 4316 | 166 | 0 | 321 | 80 | 298 | 19 | 654.175 | 94.14
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 137 | 53 | 50 | 30 | 315 | 0 | 0 | 50 | 49 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 71 | 68 | 70 | 32 | 22 | 0 | 2 | 0 | 0 | 0 | 280 | 280 | 208 | 0 | 36 | 10 | 5 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 80 | 11 | 0 | 0 | 2 | 27 | 54 | 44 | 39 | 163 | 0 | 56 | 0 | 0 | 208 | 12 | 0 | 0 | 0 | 12 | 3 | 0 | 80 | 0 | 0 | 115 | 0 | 74 | 16 | 49 | 17 | 43 | 404 | 66 | 35 | 51 | 3 | 68 | 54 | 54 | 17 | 46 | 48 | 345 | 17 | 13 | 108 | 35 | 0 | 17 | 11 | 49 | 15 | 280 | 54 | 0 | 608 | 33 | 517 | 0 | 0 | 52 |  | 920 | 0 | 310 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 59 | 0 | 220 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 17 | 0 | 50 | 0 | 103 | 0 | 2 | 50 | 1140 | 220 | 0 | 0 | 2 | 55 | 52 | 0 | 0 | 339 | 14 | 150 | 1367 | 208 | 0 | 0 | 54 |  | 7425 | 6134 | 13559 | 3867 | 920 | 1405 | 0 | 1923 | 4400 | 166 | 0 | 333 | 80 | 432 | 33 | 707.655 | 94.16
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 138 | 50 | 50 | 30 | 316 | 0 | 0 | 54 | 49 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 70 | 51 | 70 | 31 | 40 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 211 | 0 | 36 | 10 | 5 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 86 | 9 | 0 | 0 | 2 | 27 | 55 | 47 | 39 | 163 | 0 | 57 | 0 | 0 | 208 | 12 | 0 | 0 | 0 | 12 | 3 | 0 | 80 | 0 | 0 | 110 | 0 | 73 | 17 | 49 | 17 | 43 | 404 | 66 | 17 | 51 | 0 | 69 | 54 | 54 | 17 | 46 | 50 | 345 | 17 | 11 | 108 | 35 | 0 | 17 | 18 | 49 | 17 | 230 | 54 | 0 | 610 | 44 | 517 | 0 | 0 | 7 |  | 919 | 0 | 310 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 58 | 0 | 220 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 17 | 0 | 55 | 0 | 103 | 0 | 3 | 60 | 1200 | 180 | 0 | 0 | 2 | 11 | 52 | 0 | 0 | 338 | 19 | 150 | 1370 | 143 | 0 | 0 | 63 |  | 7298 | 6003 | 13301 | 3697 | 919 | 1380 | 0 | 1943 | 4463 | 166 | 0 | 307 | 86 | 296 | 44 | 763.045 | 94.11
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 420 | 149 | 34 | 82 | 30 | 320 | 0 | 0 | 52 | 49 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 74 | 51 | 70 | 32 | 48 | 0 | 2 | 0 | 0 | 0 | 320 | 240 | 195 | 0 | 35 | 10 | 5 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 88 | 9 | 0 | 0 | 2 | 27 | 54 | 47 | 35 | 163 | 0 | 57 | 0 | 0 | 209 | 12 | 0 | 0 | 0 | 12 | 3 | 0 | 56 | 0 | 0 | 110 | 0 | 91 | 4 | 49 | 17 | 41 | 403 | 66 | 17 | 51 | 0 | 69 | 54 | 54 | 17 | 47 | 50 | 345 | 17 | 11 | 108 | 35 | 0 | 17 | 6 | 48 | 17 | 230 | 17 | 0 | 610 | 34 | 517 | 0 | 0 | 19 |  | 918 | 0 | 310 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 182 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 53 | 0 | 70 | 0 | 99 | 0 | 2 | 70 | 1244 | 180 | 0 | 0 | 1 | 37 | 54 | 0 | 0 | 336 | 27 | 150 | 1374 | 68 | 0 | 0 | 16 |  | 7295 | 5993 | 13288 | 3741 | 918 | 1390 | 0 | 2010 | 4474 | 166 | 0 | 274 | 88 | 193 | 34 | 870.96 | 94.2
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 420 | 120 | 34 | 82 | 30 | 320 | 0 | 0 | 52 | 57 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 14 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 74 | 51 | 80 | 31 | 50 | 0 | 2 | 0 | 0 | 0 | 300 | 260 | 161 | 0 | 35 | 10 | 5 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 80 | 9 | 0 | 0 | 1 | 24 | 54 | 47 | 35 | 163 | 0 | 58 | 0 | 0 | 206 | 12 | 0 | 0 | 0 | 12 | 2 | 0 | 56 | 0 | 0 | 114 | 0 | 75 | 5 | 49 | 17 | 38 | 404 | 67 | 17 | 51 | 0 | 67 | 54 | 58 | 34 | 47 | 50 | 345 | 17 | 36 | 108 | 35 | 0 | 17 | 11 | 48 | 17 | 280 | 17 | 0 | 606 | 26 | 512 | 0 | 0 | 18 |  | 918 | 0 | 309 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 8 | 108 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 194 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 71 | 0 | 80 | 0 | 95 | 0 | 2 | 90 | 1220 | 220 | 0 | 0 | 1 | 36 | 54 | 0 | 0 | 337 | 14 | 150 | 1429 | 67 | 0 | 0 | 12 |  | 7278 | 6236 | 13514 | 3782 | 918 | 1478 | 0 | 2078 | 4508 | 166 | 0 | 275 | 80 | 203 | 26 | 750.63 | 94.22
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 0 |  | 0 | 420 | 130 | 33 | 82 | 30 | 330 | 0 | 0 | 56 | 65 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 14 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 4 | 220 | 0 | 0 | 0 |  | 6 | 60 | 51 | 12 | 32 | 50 | 0 | 4 | 0 | 0 | 0 | 300 | 260 | 214 | 0 | 30 | 10 | 5 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 80 | 10 | 0 | 0 | 0 | 24 | 54 | 50 | 36 | 163 | 0 | 40 | 0 | 0 | 208 | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 114 | 0 | 87 | 1 | 49 | 17 | 36 | 404 | 67 | 17 | 51 | 1 | 67 | 54 | 72 | 34 | 65 | 50 | 345 | 17 | 11 | 162 | 35 | 0 | 17 | 8 | 49 | 17 | 280 | 17 | 0 | 608 | 32 | 517 | 0 | 0 | 12 |  | 918 | 0 | 309 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 8 | 108 | 7 | 16 | 0 | 0 | 0 | 38 | 0 | 48 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 91 | 0 | 35 | 0 | 45 | 0 | 1 | 95 | 1244 | 220 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 338 | 4 | 150 | 1413 | 27 | 0 | 0 | 3 |  | 7267 | 6110 | 13377 | 3785 | 918 | 1408 | 0 | 2025 | 4550 | 166 | 0 | 329 | 80 | 84 | 32 | 499.465 | 94.23
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 |  | 0 | 400 | 120 | 33 | 82 | 30 | 324 | 0 | 0 | 57 | 90 | 64 | 8 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 14 | 15 | 25 | 6 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 68 | 51 | 12 | 38 | 50 | 0 | 6 | 0 | 0 | 0 | 285 | 240 | 217 | 0 | 25 | 10 | 5 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 78 | 10 | 0 | 0 | 0 | 24 | 54 | 50 | 39 | 120 | 0 | 40 | 0 | 0 | 212 | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 60 | 0 | 0 | 115 | 0 | 89 | 0 | 60 | 17 | 42 | 400 | 67 | 17 | 51 | 0 | 67 | 17 | 82 | 88 | 93 | 50 | 345 | 17 | 1 | 162 | 35 | 0 | 17 | 3 | 66 | 17 | 280 | 17 | 0 | 605 | 10 | 510 | 0 | 0 | 6 |  | 918 | 0 | 310 | 0 | 93 | 0 | 0 | 0 | 25 | 4 | 8 | 126 | 7 | 16 | 0 | 0 | 0 | 38 | 0 | 48 | 0 | 0 | 6 | 0 | 15 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 91 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 1120 | 220 | 0 | 0 | 0 | 6 | 35 | 0 | 0 | 339 | 2 | 150 | 1271 | 15 | 0 | 0 | 2 |  | 7262 | 5730 | 12992 | 3726 | 918 | 1310 | 0 | 2101 | 4275 | 166 | 0 | 372 | 78 | 36 | 10 | 275 | 94.24
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 |  | 0 | 390 | 150 | 37 | 82 | 30 | 270 | 0 | 0 | 58 | 90 | 126 | 13 | 0 | 0 | 0 | 16 | 35 | 35 | 0 | 14 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 13 | 220 | 0 | 0 | 0 |  | 6 | 71 | 85 | 58 | 38 | 50 | 0 | 12 | 0 | 0 | 0 | 330 | 240 | 211 | 8 | 25 | 20 | 7 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 88 | 11 | 0 | 0 | 0 | 30 | 59 | 50 | 39 | 120 | 0 | 40 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 110 | 0 | 0 | 152 | 0 | 97 | 0 | 62 | 17 | 59 | 345 | 76 | 17 | 54 | 0 | 69 | 28 | 90 | 88 | 91 | 50 | 375 | 33 | 0 | 162 | 35 | 0 | 17 | 0 | 105 | 17 | 280 | 163 | 0 | 610 | 13 | 518 | 0 | 0 | 0 |  | 917 | 0 | 310 | 0 | 95 | 0 | 0 | 0 | 42 | 31 | 8 | 130 | 10 | 50 | 0 | 0 | 0 | 40 | 4 | 85 | 0 | 0 | 27 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 91 | 0 | 51 | 0 | 84 | 0 | 0 | 110 | 1080 | 180 | 0 | 0 | 0 | 0 | 94 | 0 | 0 | 339 | 0 | 150 | 1492 | 0 | 0 | 0 | 0 |  | 7823 | 6208 | 14031 | 3703 | 917 | 1319 | 0 | 2614 | 4470 | 166 | 0 | 741 | 88 | 0 | 13 | 209.145 | 94.27
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 380 | 130 | 66 | 82 | 55 | 314 | 0 | 0 | 58 | 90 | 131 | 13 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 14 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 16 | 221 | 0 | 0 | 0 |  | 3 | 71 | 85 | 58 | 38 | 50 | 0 | 11 | 0 | 0 | 0 | 285 | 260 | 217 | 8 | 25 | 20 | 20 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 84 | 11 | 0 | 0 | 0 | 0 | 54 | 53 | 39 | 163 | 0 | 40 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 145 | 0 | 0 | 143 | 0 | 97 | 0 | 62 | 17 | 120 | 400 | 76 | 17 | 68 | 0 | 69 | 54 | 90 | 88 | 91 | 62 | 345 | 65 | 0 | 162 | 35 | 0 | 17 | 0 | 115 | 17 | 280 | 163 | 0 | 605 | 18 | 517 | 0 | 0 | 0 |  | 916 | 0 | 314 | 0 | 95 | 0 | 0 | 0 | 47 | 45 | 8 | 126 | 10 | 64 | 0 | 0 | 0 | 40 | 5 | 85 | 0 | 0 | 36 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 91 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 1180 | 220 | 0 | 10 | 0 | 0 | 94 | 0 | 0 | 338 | 0 | 150 | 1510 | 0 | 0 | 0 | 0 |  | 8227 | 6577 | 14804 | 3833 | 916 | 1435 | 0 | 2997 | 4580 | 166 | 0 | 775 | 84 | 0 | 18 | 473.68 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 |  | 0 | 380 | 123 | 69 | 82 | 55 | 307 | 0 | 0 | 58 | 90 | 132 | 13 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 14 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 223 | 0 | 0 | 0 |  | 3 | 71 | 85 | 58 | 38 | 50 | 0 | 15 | 0 | 0 | 0 | 285 | 240 | 217 | 8 | 25 | 29 | 26 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 84 | 17 | 0 | 0 | 0 | 0 | 54 | 53 | 39 | 163 | 0 | 40 | 0 | 0 | 209 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 140 | 0 | 0 | 143 | 0 | 95 | 0 | 62 | 17 | 117 | 400 | 76 | 17 | 68 | 0 | 70 | 54 | 92 | 88 | 93 | 62 | 345 | 63 | 0 | 162 | 35 | 0 | 17 | 0 | 115 | 17 | 280 | 163 | 0 | 600 | 25 | 515 | 0 | 0 | 0 |  | 917 | 0 | 313 | 0 | 95 | 0 | 0 | 0 | 42 | 53 | 8 | 126 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 85 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 91 | 0 | 113 | 0 | 100 | 0 | 0 | 113 | 1180 | 220 | 0 | 35 | 0 | 0 | 94 | 0 | 0 | 338 | 0 | 150 | 1509 | 0 | 0 | 0 | 0 |  | 8203 | 6574 | 14777 | 3799 | 917 | 1360 | 0 | 3061 | 4572 | 166 | 0 | 793 | 84 | 0 | 25 | 403.965 | 94.26
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 360 | 155 | 92 | 82 | 55 | 297 | 0 | 0 | 58 | 90 | 146 | 13 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 15 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 1 | 71 | 85 | 58 | 38 | 50 | 0 | 15 | 0 | 0 | 0 | 290 | 240 | 215 | 8 | 31 | 35 | 42 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 74 | 18 | 0 | 0 | 0 | 0 | 54 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 148 | 0 | 0 | 161 | 0 | 95 | 0 | 62 | 17 | 137 | 402 | 66 | 17 | 68 | 0 | 69 | 54 | 92 | 88 | 94 | 62 | 390 | 87 | 0 | 162 | 35 | 0 | 17 | 0 | 93 | 17 | 285 | 163 | 0 | 610 | 10 | 519 | 0 | 0 | 0 |  | 917 | 0 | 314 | 0 | 95 | 0 | 0 | 0 | 42 | 53 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 85 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 91 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1200 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 337 | 0 | 150 | 1503 | 0 | 0 | 0 | 0 |  | 8377 | 6670 | 15047 | 3890 | 917 | 1462 | 0 | 3145 | 4579 | 166 | 0 | 804 | 74 | 0 | 10 | 384.865 | 94.27
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399 | 0 |  | 0 | 350 | 151 | 98 | 82 | 15 | 283 | 0 | 0 | 44 | 90 | 132 | 13 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 0 | 71 | 85 | 58 | 38 | 50 | 0 | 8 | 0 | 0 | 0 | 295 | 240 | 179 | 8 | 31 | 36 | 45 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 88 | 18 | 0 | 0 | 0 | 0 | 54 | 53 | 39 | 163 | 0 | 50 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 147 | 0 | 0 | 153 | 0 | 95 | 0 | 62 | 17 | 135 | 400 | 67 | 17 | 68 | 0 | 70 | 54 | 92 | 88 | 100 | 62 | 383 | 87 | 0 | 108 | 35 | 0 | 17 | 0 | 87 | 11 | 290 | 163 | 0 | 610 | 10 | 517 | 0 | 0 | 0 |  | 917 | 0 | 321 | 0 | 95 | 0 | 0 | 0 | 42 | 43 | 8 | 128 | 10 | 110 | 0 | 0 | 0 | 40 | 5 | 85 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 91 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1230 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 338 | 0 | 150 | 1501 | 0 | 0 | 0 | 0 |  | 8164 | 6745 | 14909 | 3836 | 917 | 1504 | 0 | 3007 | 4606 | 166 | 0 | 775 | 88 | 0 | 10 | 421.155 | 94.28
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 360 | 132 | 98 | 82 | 15 | 302 | 0 | 0 | 41 | 90 | 132 | 13 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 15 | 15 | 25 | 11 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 71 | 85 | 58 | 38 | 44 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 178 | 8 | 30 | 36 | 45 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 88 | 20 | 0 | 0 | 0 | 0 | 54 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 210 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 72 | 0 | 0 | 153 | 0 | 96 | 0 | 62 | 17 | 102 | 403 | 67 | 17 | 68 | 0 | 52 | 54 | 92 | 88 | 98 | 62 | 390 | 88 | 0 | 72 | 18 | 0 | 17 | 0 | 88 | 17 | 240 | 17 | 0 | 610 | 15 | 517 | 0 | 0 | 0 |  | 916 | 0 | 326 | 0 | 95 | 0 | 0 | 0 | 42 | 43 | 0 | 128 | 10 | 110 | 0 | 0 | 0 | 40 | 5 | 88 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 200 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302 | 91 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 360 | 0 | 150 | 1517 | 0 | 0 | 0 | 0 |  | 7751 | 6695 | 14446 | 3824 | 916 | 1355 | 0 | 2791 | 4659 | 166 | 0 | 632 | 88 | 0 | 15 | 911.07 | 94.29
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 370 | 137 | 99 | 82 | 15 | 306 | 0 | 0 | 41 | 90 | 98 | 13 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 15 | 15 | 25 | 11 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 71 | 85 | 58 | 38 | 39 | 0 | 33 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 30 | 36 | 23 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 86 | 19 | 0 | 0 | 0 | 0 | 56 | 50 | 0 | 163 | 0 | 56 | 0 | 0 | 210 | 12 | 0 | 0 | 10 | 12 | 2 | 0 | 47 | 0 | 0 | 153 | 0 | 96 | 0 | 49 | 17 | 95 | 402 | 67 | 17 | 68 | 0 | 52 | 54 | 92 | 17 | 93 | 50 | 390 | 88 | 0 | 54 | 17 | 0 | 32 | 0 | 88 | 17 | 240 | 17 | 0 | 600 | 18 | 517 | 0 | 0 | 0 |  | 918 | 0 | 326 | 0 | 95 | 0 | 0 | 0 | 27 | 43 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 40 | 5 | 88 | 0 | 0 | 42 | 0 | 22 | 0 | 0 | 8 | 60 | 0 | 200 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 90 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 338 | 0 | 150 | 1511 | 0 | 0 | 0 | 0 |  | 7593 | 6641 | 14234 | 3869 | 918 | 1451 | 0 | 2531 | 4620 | 166 | 0 | 575 | 86 | 0 | 18 | 1018.03 | 94.3
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9403200 | 0 |  | 0 | 9116500 | 3381585 | 1076160 | 1616478 | 676630 | 7354149 | 0 | 0 | 1181760 | 1215360 | 1440000 | 79000 | 0 | 0 | 0 | 608040 | 672822 | 665415 | 0 | 370200 | 355320 | 486900 | 224900 | 145440 | 0 | 2089620 | 1924000 | 0 | 0 | 93475 | 5291562 | 0 | 0 | 0 |  | 121200 | 1681872 | 1760231 | 1519320 | 751680 | 859680 | 0 | 407520 | 0 | 0 | 0 | 7419100 | 6145000 | 5077000 | 33454 | 844110 | 609408 | 339840 | 0 | 952551 | 0 | 872768 | 789509 | 0 | 0 | 0 | 374730 | 1879680 | 372480 | 0 | 0 | 13280 | 504000 | 1304040 | 1193400 | 885168 | 3616854 | 0 | 1284000 | 0 | 0 | 5242450 | 292000 | 0 | 0 | 0 | 272736 | 78624 | 0 | 1663527 | 0 | 0 | 2983200 | 0 | 2129328 | 88965 | 1155840 | 415200 | 2034036 | 9565000 | 1604400 | 487680 | 1373309 | 19477 | 1525527 | 1286327 | 1901050 | 872100 | 1487640 | 1256640 | 8428700 | 792960 | 205250 | 1944000 | 1013673 | 0 | 540000 | 149583 | 1385280 | 257040 | 6674200 | 1147490 | 0 | 13996362 | 420480 | 12494545 | 0 | 0 | 327436 |  | 22239360 | 0 | 7502112 | 0 | 1975680 | 0 | 0 | 0 | 379680 | 533504 | 438000 | 2899000 | 198875 | 793536 | 0 | 0 | 0 | 451445 | 27444 | 813184 | 0 | 0 | 309600 | 0 | 278123 | 0 | 0 | 103140 | 1405090 | 0 | 5030000 | 16000 | 0 | 4698382 | 0 | 943073 | 0 | 0 | 0 | 0 | 0 | 8323490 | 1255200 | 0 | 1918848 | 0 | 2294908 | 0 | 20362 | 1967712 | 29196100 | 5363182 | 0 | 562800 | 30240 | 513360 | 1352064 | 0 | 0 | 8298182 | 134540 | 4113600 | 33611690 | 1234250 | 0 | 3413 | 341250 |  | 178592446 | 151570419 | 330162865 | 94119516 | 22239360 | 33812419 | 0 | 52739474 | 108145569 | 4013620 | 16000 | 9695341 | 1879680 | 3081406 | 420480 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27081216 | 0 |  | 0 | 28990470 | 11565020.7 | 21264921.6 | 30228138.6 | 11922220.6 | 22430154.45 | 0 | 0 | 23351577.6 | 21815712 | 27964800 | 1473350 | 0 | 0 | 0 | 11102810.4 | 10603674.72 | 12170440.35 | 0 | 277650 | 0 | 0 | 0 | 2604830.4 | 0 | 0 | 0 | 0 | 0 | 1770416.5 | 16880082.78 | 0 | 0 | 0 |  | 2131908 | 29617765.92 | 31525737.21 | 28958239.2 | 14710377.6 | 14150332.8 | 0 | 0 | 0 | 0 | 0 | 20699289 | 18803700 | 16855640 | 112070.9 | 2726475.3 | 2053704.96 | 1488499.2 | 0 | 3819729.51 | 0 | 15631274.88 | 14258532.54 | 0 | 0 | 0 | 281047.5 | 12330700.8 | 1158412.8 | 0 | 0 | 0 | 1965600 | 4864069.2 | 5429970 | 4027514.4 | 12369640.68 | 0 | 7126200 | 0 | 0 | 14626435.5 | 1921360 | 0 | 0 | 0 | 204552 | 59754.24 | 0 | 33935950.8 | 0 | 0 | 57307272 | 0 | 37497466.08 | 0 | 20585510.4 | 7203720 | 33724316.88 | 25347250 | 30579864 | 9148876.8 | 24637163.46 | 0 | 24942366.45 | 25006196.88 | 34104837 | 16665831 | 28875092.4 | 22380758.4 | 22420342 | 13535827.2 | 0 | 35555760 | 17009432.94 | 0 | 9649800 | 0 | 24962745.6 | 4354257.6 | 19822374 | 16156659.2 | 0 | 97554643.14 | 0 | 73717815.5 | 0 | 0 | 0 |  | 62492601.6 | 0 | 22131230.4 | 0 | 34278048 | 0 | 0 | 0 | 7141780.8 | 10035210.24 | 7796400 | 9160840 | 942667.5 | 13680560.64 | 0 | 0 | 0 | 8085379.95 | 503597.4 | 13669623.04 | 0 | 0 | 5544936 | 0 | 4981182.93 | 0 | 0 | 78076.98 | 15498142.7 | 0 | 42453200 | 894400 | 0 | 15504660.6 | 0 | 3140433.09 | 0 | 0 | 0 | 0 | 0 | 24304590.8 | 21438816 | 0 | 38031567.36 | 0 | 45714567.36 | 0 | 0 | 39039406.08 | 189190728 | 16679496.02 | 0 | 10890180 | 0 | 0 | 23458310.4 | 0 | 0 | 60576728.6 | 0 | 30646320 | 222173270.9 | 0 | 0 | 0 | 0 |  | 1334088150.57 | 1000156953.39 | 2334245103.96 | 277620550.8 | 62492601.6 | 109729669.71 | 0 | 968508384.64 | 731810848.84 | 0 | 894400 | 170857947.57 | 12330700.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 150 | 52 | 50 | 30 | 312 | 0 | 0 | 50 | 49 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 25 | 12 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 71 | 68 | 70 | 28 | 12 | 0 | 0 | 0 | 0 | 0 | 325 | 280 | 197 | 0 | 40 | 20 | 10 | 0 | 43 | 0 | 36 | 33 | 0 | 0 | 0 | 17 | 80 | 11 | 0 | 0 | 1 | 27 | 54 | 47 | 36 | 163 | 0 | 54 | 0 | 0 | 206 | 12 | 0 | 0 | 15 | 12 | 5 | 0 | 80 | 0 | 0 | 107 | 0 | 64 | 4 | 49 | 17 | 45 | 392 | 57 | 35 | 51 | 4 | 52 | 54 | 54 | 17 | 46 | 50 | 371 | 17 | 22 | 108 | 38 | 0 | 17 | 11 | 50 | 12 | 280 | 54 | 0 | 606 | 19 | 519 | 0 | 0 | 36 |  | 919 | 0 | 311 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 16 | 130 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 17 | 0 | 35 | 0 | 103 | 0 | 2 | 50 | 1110 | 220 | 0 | 27 | 3 | 73 | 52 | 0 | 0 | 338 | 17 | 150 | 1313 | 69 | 0 | 0 | 56 |  | 13415 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 360 | 155 | 92 | 82 | 55 | 297 | 0 | 0 | 58 | 90 | 146 | 13 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 15 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 0 | 1 | 71 | 85 | 58 | 38 | 50 | 0 | 15 | 0 | 0 | 0 | 290 | 240 | 215 | 8 | 31 | 35 | 42 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 74 | 18 | 0 | 0 | 0 | 0 | 54 | 53 | 39 | 163 | 0 | 56 | 0 | 0 | 211 | 12 | 0 | 0 | 0 | 12 | 5 | 0 | 148 | 0 | 0 | 161 | 0 | 95 | 0 | 62 | 17 | 137 | 402 | 66 | 17 | 68 | 0 | 69 | 54 | 92 | 88 | 94 | 62 | 390 | 87 | 0 | 162 | 35 | 0 | 17 | 0 | 93 | 17 | 285 | 163 | 0 | 610 | 10 | 519 | 0 | 0 | 0 |  | 917 | 0 | 314 | 0 | 95 | 0 | 0 | 0 | 42 | 53 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 85 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 91 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1200 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 337 | 0 | 150 | 1503 | 0 | 0 | 0 | 0 |  | 15047 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 225 | 150 | 92 | 82 | 55 | 250 | 0 | 0 | 60 | 90 | 146 | 13 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 15 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 71 | 85 | 58 | 38 | 50 | 0 | 15 | 0 | 0 | 0 | 290 | 240 | 215 | 0 | 30 | 35 | 42 | 0 | 43 | 0 | 37 | 33 | 0 | 0 |  | 17 | 100 | 20 | 0 | 0 | 0 | 0 | 54 | 51 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 12 | 0 | 0 | 200 | 12 | 5 | 0 | 145 | 0 | 0 | 160 | 0 | 95 | 0 | 52 | 17 | 137 | 400 | 70 | 17 | 68 | 0 | 52 | 54 | 92 | 88 | 94 | 50 | 390 | 70 | 0 | 162 | 35 | 0 | 17 | 0 | 93 | 17 | 290 | 163 | 0 | 1200 | 62 | 520 | 0 | 0 |  |  | 937 | 0 | 315 | 0 | 98 | 0 | 0 | 0 | 42 | 53 | 8 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 10 | 85 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 90 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 340 | 0 | 150 | 1515 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 200 | 150 | 80 | 80 | 30 | 250 | 0 | 0 | 50 | 50 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 15 | 15 | 16 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 70 | 85 | 50 | 32 | 50 | 0 | 5 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 30 | 30 | 20 | 0 | 43 | 0 | 36 | 33 | 0 | 0 |  | 17 | 90 | 20 | 0 | 0 | 1.6 | 0 | 54 | 50 | 40 | 163 | 0 | 60 | 0 | 0 | 210 | 12 | 0 | 0 | 150 | 12 | 2 | 0 | 145 | 0 | 0 | 116 | 0 | 95 | 20 | 34 | 17 | 130 | 400 | 60 | 17 | 40 | 5 | 52 | 54 | 73 | 70 | 46 | 50 | 340 | 70 | 50 | 54 | 35 | 0 | 17 | 35 | 33 | 17 | 250 | 54 | 0 | 900 | 44 | 510 | 0 | 0 | 70 |  | 937 | 0 | 300 | 0 | 77 | 0 | 0 | 0 | 30 | 50 | 8 | 125 | 10 | 110 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 25 | 0 | 113 | 0 | 99 | 0 | 8 | 113 | 1200 | 220 |  | 35 | 6 | 100 | 90 | 0 | 0 | 340 | 30 | 150 | 1400 | 130 | 0 |  | 5 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 180 | 0 | 49 | 82 | 25 | 182 | 0 | 0 | 45 | 25 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 15 | 15 | 25 | 10 | 8 | 0 | 86 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 6 | 56 | 51 | 58 | 25 | 25 | 0 | 10 | 0 | 0 | 0 | 280 | 280 | 215 | 0 | 0 | 37 | 20 | 0 | 43 | 0 | 37 | 33 | 0 | 0 | 0 | 17 | 78 | 18 | 0 | 0 | 1 | 0 | 54 | 0 | 0 | 163 | 0 | 58 | 0 | 0 | 214 | 0 | 0 | 0 | 150 | 12 | 5 | 0 | 47 | 0 | 0 | 125 | 0 | 96 | 4 | 47 | 17 | 52 | 400 | 58 | 17 | 51 | 0 | 52 | 54 | 92 | 17 | 46 | 50 | 384 | 53 | 14 | 17 | 17 | 0 | 0 | 14 | 33 | 0 | 240 | 17 | 0 | 557 | 13 | 517 | 0 | 0 | 9 | 0 | 918 | 0 | 322 | 0 | 95 | 0 | 0 | 0 | 21 | 29 | 0 | 80 | 8 | 16 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 100 | 0 | 1 | 113 | 1170 | 220 | 0 | 17 | 1 | 28 | 35 | 0 | 0 | 340 | 0 | 150 | 1370 | 20 | 0 | 0 | 14 | 0 |  |  |  | 127931935 | 22239360 | 16000 | 108145569 | 62434815 | 1879680 | 3081406 | 420480 | 4013620 |  |  | 330146865
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 127.9319 | 22.2394 | 0.016 | 108.1456 | 62.4348 | 1.8797 | 3.0814 | 0.42048 | 4.0136
| Minimum Generation |  | 12564 | 8:00
| Highest Generation |  | 15047 | 21:00 |  |  |  |  | 4500 | [124 empty] | 0 | [73 empty] | 330.1629
| Day Peak Generation |  | 13415 | 12:00 |  |  |  |  | 6000
| Evening Peak Generation |  | 15047 | 21:00 |  |  |  |  | 10500 | [198 empty] | 202699852
| HVDC Max Flow |  | 920 | 4:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 917 | 21:00
| Load factor L.F |  | 91.43% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-10
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13415 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12664
Evening Peak Generation : |  |  | 15047 | MW Hour : | 21:00 | Available Max Generation : |  | 15794
E.P. Demand (at gen end) : |  |  | 15450 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15800
Maximum Generation : |  |  | 15047 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 330.1629 | System Load Factor : | 91.43% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 1008 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-10
Actual : |  | 94.42 | Ft.(MSL) , | Rule curve : | 85.44 | Ft.( MSL )
Gas Consumed : |  | Total = | 917.83 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 387350220.51
: |  |  | Coal : | 731810848.84 | Oil : | 1140260732.21 | Total : | 2259421801.56
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 190 | 4560:00 | 5019.2107 |  |  | 0 | -8.615%
Chittagong Area |  | 0 | 0:00 | 1381.88 |  |  | 0 | -6.78%
Khulna Area |  | 0 | 0:00 | 1936.5624 |  |  | 0 | -6.388%
Rajshahi Area |  | 62 | 1488:00 | 1683.9775 |  |  | 0 | -5.973%
Cumilla Area |  | 18 | 432:00 | 1385.229 |  |  | 0 | -6.23%
Mymensingh Area |  | 115 | 2760:00 | 1030.6659 |  |  | 0 | -5.87%
Sylhet Area |  | 0 | 0:00 | 577.2872 |  |  | 0 | -6.558%
Barisal Area |  | 0 | 0:00 | 481.4952 |  |  | 0 | -5.804%
Rangpur Area |  | 0 | 0:00 | 941.7111 |  |  | 0 | -5.813%
Total |  | 385 |  | 14438.019 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:50 | Bhulta 132/33kV S/S GT1 HT is restored.
| 08:53 | Kushtia 132/33kV S/S T2 HT is restored.
| 08:54 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
| 08:54 | Kushtia 132/33kV S/S T2 LT is restored.
09:04 | 18:34 | Fenchuganj 230/132/33kV S/S TR-02 HT Project Work S/D Due to G2G Project work purpose shutdown. No loadshed occured.
09:30 | 21:36 | Meghnaghat 400/230kV S/S Meghnaghat-Summit PP 400KV Ckt-1 Project Work S/D
09:33 | 18:22 | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Project Work S/D Due to G2G project work
09:41 | 20:19 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown is taken from Berhampore end.
10:15 | 12:52 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Line maintenance
10:26 |  | Meghnaghat 450 MW CCPP (MPL) GT-1 Synchronized with remarks:- None
10:27 |  | Meghnaghat 450 MW CCPP (MPL) GT-2 Synchronized with remarks:- None
10:28 |  | Meghnaghat 450 MW CCPP (MPL) ST Synchronized with remarks:- None
10:51 | 21:16 | Aminbazar-Meghnaghat 400kV Ckt-2 Project Work S/D from Meghnaghat 400/230kV end.
10:59 |  | Fenchuganj-Fenchuganj 132 kV Ckt-2 Project Work S/D from Fenchuganj 230/132/33kV end Due to G2G Project purpose.
11:01 |  | Bibiana-II 341 MW CCPP (Summit) Synchronized with remarks:- GT
11:19 | 11:42 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance Relay & E/F Relay.
relays Due to Instantenious trip.
11:20 | 11:43 | Rampur 230/132/33 S/S Halishahar-2 Tripped showing REL670 relays.
12:00 |  | Day Peak Generation: 13415 MW.
12:38 |  | Patuakhali 132/33kV S/S UPPL (150MW) 132kV LINE Scheduled S/D Due to scada related work
12:42 |  | Bibiana-II 341 MW CCPP (Summit) Shutdown with remarks:- GT
12:58 | 15:03 | Aminbazar-Kaliakoir 230kV Ckt-2 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Line maintenance
13:14 |  | Rampur 230/132/33 S/S Halishahar-2 Tripped showing REL670 relays.
13:14 | 15:15 | Halishahar-Khulshi 132kV Ckt-2 Tripped from Halishahar 132/33kV end showing Distance Trip, Earth
Fault Trip relays Due to Instantenious trip.
13:14 |  | Rampur 230/132/33 S/S Halishahar-2 Tripped showing REL670 relays.
13:15 | 14:43 | Shahjadpur 132/33kV S/S T-3(425T) HT Forced S/D Due to Loop changing work for T-3 x-former 33kv ds-c.b
13:15 | 14:43 | Shahjadpur 132/33kV S/S T-3(425T) LT Forced S/D Due to Loop changing work for 33kv incomer D/S to C.B
13:25 | 16:09 | Haripur-Siddirganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to High temperature
maintenance. and from Siddhirganj 132/33kV end Due to Abnormal temperature issues
in Haripur Substation end (work done by Haripur Substation)
13:52 | 16:04 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Maintenance work
14:17 | 14:38 | Sirajganj 132/33kV S/S T2-(425) HT Tripped showing ( P132-) Differential trip (P632-2) relays Due to |  |  |  |  | 50.0MW load interruption.
Kamarkhanda 33 kv Feeder Fault (T1 and T2 Paralla Oparation )
| 14:40 | Sirajganj 132/33kV S/S T1-(415) HT is restored.
| 14:41 | Sirajganj 132/33kV S/S T1-(415) LT is restored.
14:53 | 14:58 | Pabna 132/33kV S/S T-3 LT Tripped showing Main Protection Relay Gen. Trip, Master Trip Relay-1&2, Backup |  |  |  |  | 30.0MW load interruption.
Protection Relay Gen. Trip. relays Due to Chatmohar 33 kv trip
14:53 | 14:58 | Pabna 132/33kV S/S T-2 LT Tripped showing E/F, O/C relays Due to Chatmohar 33 kv BKR trip |  |  |  |  | 15.0MW load interruption.
16:11 | 17:58 | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
16:58 |  | Meghnaghat CCPP(Summit) GT-1 Synchronized with remarks:- None
16:58 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:- Running on FGMO as per NLDC's Request
16:59 |  | Meghnaghat CCPP(Summit) GT-2 Ready with remarks:- Remains standby as per NLDC's request
17:01 |  | Meghnaghat CCPP(Summit) ST Synchronized with remarks:- None
21:00 |  | Evening Peak Gen. 15047 MW
| 21:16 | Aminbazar-Meghnaghat 400kV Ckt-1 is restored.
22:55 | 01:07 | Madaripur 132/33kV S/S T2-415T LT Scheduled S/D Due to 33 kv agoiljora feeder fault work. |  |  |  |  | 25.0MW load interruption.
22:57 | 01:06 | Madaripur 132/33kV S/S T2-415T HT Scheduled S/D Due to 33 kv Agoljora feeder work
23:26 |  | Bibiana-II 341 MW CCPP (Summit) Synchronized with remarks:- GT
00:28 |  | Chowmuhani 132/33kV S/S TR1-415T LT Tripped showing Instt. E/F relays Due to Tripped By Instt. E/F |  |  |  |  | 58.0MW load interruption.
00:50 |  | Chowmuhani 132/33kV S/S TR1-415T HT Forced S/D Due to 33KV Incoming R-Phase DS Defective.
01:27 | 01:41 | Jaldhaka-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance relay relays Due to Thundering |  |  |  |  | 14.0MW load interruption.
01:27 | 01:40 | Jaldhaka-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing Distance relay relays Due to Thundering
02:00 |  | Bibiana-II 341 MW CCPP (Summit) Synchronized with remarks:- ST
05:47 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- ST
05:54 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
06:00 |  | Evening Peak generation = 12,747MW
06:10 | 07:07 | Jhenaidah-Kushtia 132kV Ckt-1 Tripped from Kushtia 132/33kV end showing Distance Relay Zone - 1 Distance -
13.4 km relays. and from Jhenaidah 132/33kV end showing Distance relay relays Due to Fault
06:24 | 07:53 | Mirpur 132/33kV S/S Main Bus Project Work S/D Due to 132/33 KV T3-Power Transformer Bus bay Upgradation.
06:29 |  | Maniknagar 132/33kV S/S Transformer GT-2 HT Scheduled S/D Due to Relay change to 33Kv side
06:58 |  | Mirzapur 132/33kV S/S Transformer-02(E07) HT Scheduled S/D Due to s/d taken by pbs due to 33kv feeder loop repair. |  |  |  |  | 32.0MW load interruption.
06:58 |  | Mirzapur 132/33kV S/S Transformer-02(E07) LT Scheduled S/D Due to s/d taken by pbs due to 33kv feeder loop repair.
07:06 | 07:36 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to For T-1 suspension disc insulator change work. |  |  |  |  | 40.0MW load interruption.
07:07 | 07:35 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to For T-1 suspension disc insulator change work.
07:14 |  | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end Due to
Temperature high CT junction point
07:28 |  | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end.
07:57 |  | Meghnaghat CCPP(Summit) record a general event:- NLDC asked for CCPP shutdown due to gas pressure low.
Time:05:47/SD/ST and 05:54/SD/GT1.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-09
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 400 | 9403200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 9116500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 92 | 1076160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 155 | 3381585 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 82 | 1616478 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 676630
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 79000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 58 | 1181760 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 297 | 7354149 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 1215360 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 608040 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 1440000 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 672822 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 665415
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 725520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 486900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 10 | 224900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 145440 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 148 | 1663527 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 95 | 2129328 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 487680 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 87 | 792960 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1944000
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 149583
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 257040 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5634 | 2472 | 47493977
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 93475 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 88965
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 859680
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 166 | 4013620 | low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5291562
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1373309 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 71 | 1681872 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1760231 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 58 | 1519320 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 1155840 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 407520
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 751680 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19477
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 69 | 1525527 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1286327
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1901050 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 62 | 1256640 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 1013673 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 163 | 1147490
60 | SS Power I |  | SS Power | 2*612 | 1224 | 610 | 13996362
| Cox's Bazar Wind |  | IPP | 66 | 60 | 10 | 420480
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 519 | 12494545 | Unit-1 Tripped
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 327436
| Chattogram area Total |  |  |  | 4457 | 2466 | 54386081
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 5077000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7419100 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6145000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 6674200 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 609408 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 42 | 339840 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 33454 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 952551 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 137 | 2034036 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 872768 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 31 | 844110 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 415200 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 74 | 1879680
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 33 | 789509 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 374730 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 872100 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 1487640 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 1385280
| Cumilla Area Total |  |  |  | 2875 | 1779 | 38205606
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 18 | 372480 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13280
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 161 | 2983200 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 66 | 1604400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 205250
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 1 | 121200 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 540000 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 263 | 5839810
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 504000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 54 | 1304040 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3616854
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1193400
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 39 | 885168 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 78624 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1284000 | Machine problem.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 211 | 5242450 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 12 | 292000 | Engine problem
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 272736 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 402 | 9565000
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 390 | 8428700 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1397 | 32666972
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 917 | 22239360
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 95 | 1975680 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 379680 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 53 | 533504 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 314 | 7502112 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 438000 | Engine problem
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 91 | 1255200 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 513360
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 337 | 8298182 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1857 | 43135078
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 793536
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 198875
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2899000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 29196100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5363182
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 562800 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 4113600 | Coal shortage
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 3413
| Barisal Area Total |  |  |  | 2236 | 1874 | 43130506
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 451445 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 27444 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 309600 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 184 | 4698382 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 943073
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 354 | 8323490 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 278123 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 103140 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 813184 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1918848
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1967712
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30240
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1503 | 33611690
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 341250
| Rajshahi Area Total |  |  |  | 3381 | 2479 | 53817621
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 60 | 1405090
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 5030000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 16000
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 2294908 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 20362
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 1352064 | Fuel shortage
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 134540
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1234250
| Rangpur Area Total |  |  |  | 950 | 460 | 11487214
| Total |  |  |  | 26364 | 15047 | 330162865
| Eastern Grid Total |  |  |  | 15943 | 8377 | 178592446
| Western Grid Total |  |  |  | 10421 | 6670 | 151570419
| National Grid Total |  |  |  | 26364 | 15047 | 330162865
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-07-09
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9451.25 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4494.8 | MW
i) Dhaka area |  |  | 5013.45 |  | MW | i) Khulna area |  |  |  | 1731 | MW
ii) Chattogram area |  |  | 1334.8 |  | MW | ii) Barishal area |  |  |  | 470 | MW
iii) Cumilla area |  |  | 1359 |  | MW | iii) Rajshahi area |  |  |  | 1422.8 | MW
iv) Mymensingh area |  |  | 1124 |  | MW | iv) Rangpur area |  |  |  | 871 | MW
v) Sylhet area |  |  | 620 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13946.05 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 112 | 19:00 | 133 | Rahim | 45 | 11:00
2 | AKSML | 106.3 | 06:00 | 68 | Jashore | 152 | 21:00 | 134 | Rajbari | 80 | 19:30
3 | Aftabnagar | 38 | 13:00 | 69 | Jhenaidah | 137 | 22:00 | 135 | Rajendrapur | 96 | 01:00
4 | Agargaon | 121 | 13:00 | 70 | Joydebpur | 179 | 22:00 | 136 | Rajshahi | 136 | 23:00
5 | Agrabad | 88 | 10:00 | 71 | Joypurhat | 64 | 02:00 | 137 | Rajshahi-230 | 79 | 00:00
6 | Amnura | 73 | 19:30 | 72 | Juldah | 20 | 18:30 | 138 | Ramganj | 120 | 22:00
7 | Ashuganj | 94 | 05:00 | 73 | KSRM | 41 | 11:00 | 139 | Rampur | 43 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 262 | 23:00 | 140 | Rangamati | 18 | 19:00
9 | BSRM | 175 | 18:30 | 75 | Kachua | 80 | 20:00 | 141 | Rangpur | 152 | 21:00
10 | Bagerhat | 97 | 22:00 | 76 | Kallyanpur | 117 | 00:00 | 142 | Ruppur | 7.2 | 16:00
11 | Bakulia | 97 | 16:00 | 77 | Kalurghat | 34 | 10:00 | 143 | SSM | 15 | 19:30
12 | Banani | 56.6 | 13:00 | 78 | Kamrangirchar | 57.8 | 13:00 | 144 | Saidpur | 109 | 01:00
13 | Bangabhaban | 20 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 138 | 00:00
14 | Barapukuria | 68 | 00:00 | 80 | Kazla | 117 | 13:00 | 146 | Satmasjid | 111 | 13:00
15 | Barguna | 24 | 01:00 | 81 | Keranigonj | 74 | 13:00 | 147 | Savar | 212 | 19:30
16 | Barishal | 118 | 19:30 | 82 | Khagrachori | 34 | 21:00 | 148 | SevenRings | 16.36 | 18:30
17 | Barishal-230 | 104 | 23:00 | 83 | Khulna | 76 | 13:00 | 149 | ShahCement | 30 | 16:00
18 | Baroaulia | 68 | 09:00 | 84 | Khulshi | 200 | 16:00 | 150 | Shahjadpur | 82 | 20:00
19 | Baroirhat | 65 | 23:00 | 85 | Kishoreganj | 134 | 07:00 | 151 | Shahjibazar | 143 | 23:00
20 | Bashundhara | 183 | 12:00 | 86 | Kodda | 272 | 18:00 | 152 | Shahmirpur | 49 | 16:00
21 | BashundharaCement | 7 | 09:00 | 87 | Kulaura | 54 | 22:00 | 153 | Shariatpur | 91 | 22:00
22 | Beanibazar | 76 | 21:00 | 88 | Kurigram | 68 | 19:00 | 154 | Sherpur | 138 | 19:00
23 | Benapole | 63 | 00:00 | 89 | Kushtia | 160 | 19:30 | 155 | Shikalbaha | 24 | 19:30
24 | Bhaluka | 124 | 08:00 | 90 | Lalbag | 96 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 58 | 23:00 | 91 | Lalmonirhat | 60 | 21:00 | 157 | Shitalakhya | 88.2 | 16:00
26 | Bhangura | 39 | 20:00 | 92 | MI_Cement | 14.2 | 21:00 | 158 | Sholosohor | 44 | 09:00
27 | Bheramara(GK) | 70 | 21:00 | 93 | Madanganj | 30 | 00:00 | 159 | Shyampur | 148 | 12:00
28 | Bhulta | 228 | 16:00 | 94 | Madaripur | 114 | 02:00 | 160 | Siddhirganj | 120 | 12:00
29 | Bog-Sherpur | 64 | 02:00 | 95 | Madartek | 88.14 | 00:00 | 161 | Sirajganj | 114 | 23:00
30 | Bogura | 187 | 22:00 | 96 | Madunaghat | 58 | 19:30 | 162 | Sonargaon | 94 | 23:00
31 | Borhanuddin | 87 | 20:00 | 97 | Magura | 69 | 20:00 | 163 | Sreemongol | 74 | 23:00
32 | Brahmanbaria | 169 | 22:00 | 98 | Mahasthangarh | 78 | 01:00 | 164 | Sreepur | 102 | 19:00
33 | Cantonment | 134 | 12:00 | 99 | Manikganj | 116 | 19:00 | 165 | Srinagar | 46.12 | 22:00
34 | Chandpur | 70 | 19:00 | 100 | Maniknagar | 80 | 13:00 | 166 | Sunamganj | 59 | 23:00
35 | Chandraghona | 37 | 20:00 | 101 | Matarbari | 47 | 20:00 | 167 | Sylhet | 46 | 20:00
36 | Chapai | 81 | 01:00 | 102 | Matuail | 74 | 11:00 | 168 | Sylhet-132 | 128 | 17:00
37 | Charsaidpur | 38 | 01:00 | 103 | Millgate | 130 | 11:00 | 169 | TK | 33 | 23:00
38 | Chauddagram | 72 | 22:00 | 104 | Mirpur | 149.5 | 16:00 | 170 | Tangail | 188 | 21:00
39 | Chhatak | 33 | 23:00 | 105 | Mirsorai | 6 | 00:00 | 171 | Thakurgaon | 107 | 00:00
40 | Chowmuhani | 234 | 21:00 | 106 | Mirzapur | 42 | 21:00 | 172 | Tongi | 116 | 09:00
41 | Chuadanga | 120 | 20:00 | 107 | Mithapukur | 62 | 00:00 | 173 | Ullahpara | 27 | 00:00
42 | Coxsbazar | 127 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 62 | 23:00
43 | Cumilla(N) | 167 | 22:00 | 109 | Mogbazar | 134.6 | 12:00 | 175 | Uttara | 88 | 14:00
44 | Cumilla(S) | 187 | 22:00 | 110 | Mongla | 41 | 16:00 | 176 | UttaraNew | 57 | 00:00
45 | Daudkandi | 166 | 21:00 | 111 | Motijheel | 45 | 13:00 | 177 | Zigatola | 84 | 00:00
46 | Dhaka | 42 | 13:00 | 112 | Munshiganj | 111 | 23:00
47 | Dhamrai | 138 | 19:30 | 113 | Mymensingh | 228 | 19:30
48 | Dhanmondi | 128 | 12:00 | 114 | Naogaon | 149 | 23:00
49 | Dohazari | 101 | 22:00 | 115 | Narail | 59 | 22:00
50 | Faridpur | 178 | 22:00 | 116 | Narinda | 80 | 13:00
51 | Fatullah | 90 | 12:00 | 117 | Narshingdi | 152 | 19:00
52 | Fenchuganj | 45 | 20:00 | 118 | Natore | 161 | 23:00
53 | Feni | 113 | 19:00 | 119 | Nawabganj | 50.6 | 23:00
54 | GPH | 95 | 11:00 | 120 | Netrakona | 112 | 19:00
55 | Ghatail | 44 | 19:00 | 121 | New | 59.7 | 12:00
56 | Ghorashal | 55 | 00:00 | 122 | Niamatpur | 88 | 23:00
57 | Goalpara | 34 | 20:00 | 123 | Noapara | 50 | 21:00
58 | Gollamari | 88 | 20:00 | 124 | PHP | 10 | 09:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 387 | 07:00 | 373 | 12:00 | Kaliakoir | 381 | 19:30 | 365 | 10:00
| Ashuganj | 407 | 4:01 | 391.6 | 11:56 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bhulta | 400 | 05:00 | 386 | 12:00 | Meghnaghat | 382 | 06:00 | 372 | 09:00
| Bibiana | 398 | 18:00 | 388 | 10:00 | Payra | 410 | 06:00 | 404 | 00:00
| BIPTC | 402 | 08:00 | 391 | 16:00 | Rahanpur | 404 | 18:00 | 390 | 22:00
| Bogura | 395 | 18:00 | 380 | 22:00 | Rampal | 401 | 08:00 | 389 | 12:00
| Gopalganj | 398 | 06:00 | 387 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 06:00 | 215 | 12:00 | Haripur | 229 | 04:00 | 220 | 12:00
| AKSML | 236 | 07:00 | 227 | 16:00 | Hasnabad | 228 | 04:00 | 217 | 12:00
| Aminbazar | 227 | 05:00 | 218 | 11:00 | Hathazari | 237 | 05:00 | 230 | 17:00
| Ashuganj | 232 | 04:00 | 225 | 12:00 | Ishurdi | 235 | 18:00 | 225 | 21:00
| Ashuganj-400 | 232 | 04:00 | 225 | 12:00 | Jhenaidah | 227 | 18:00 | 213 | 21:00
| Baghabari | 229 | 06:00 | 222 | 22:00 | Kaliakoir | 226 | 06:00 | 218 | 10:00
| Barapukuria | 219 | 14:00 | 209 | 22:00 | Keranigonj | 228 | 06:00 | 216 | 12:00
| Barapukuria-230 | 219 | 14:00 | 209 | 22:00 | Khulna(S) | 232 | 18:00 | 221 | 12:00
| Barishal | 240 | 18:00 | 232 | 01:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bheramara | 234 | 18:00 | 223 | 22:00 | Maniknagar | 229 | 06:00 | 218 | 11:00
| Bhulta | 230 | 05:00 | 220 | 12:00 | Meghnaghat | 236 | 03:00 | 228 | 12:00
| Bibiana | 229 | 00:00 | 224 | 10:00 | Meghnaghat-400 | 232 | 05:00 | 224 | 11:00
| BIPTC | 235 | 18:00 | 222 | 21:00 | Mirsorai | 235 | 19:00 | 227 | 12:00
| Bogura | 223 | 18:00 | 214 | 22:00 | Rajshahi | 234 | 18:00 | 223 | 13:00
| Bogura-400 | 224 | 06:00 | 216 | 22:00 | Rampal | 230 | 18:00 | 221 | 12:00
| Borhanuddin | 242 | 18:00 | 238 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 235 | 19:30 | 227 | 10:00 | Rampura | 229 | 06:00 | 217 | 12:00
| Cumilla(N) | 229 | 18:00 | 222 | 11:00 | Shikalbaha | 240 | 19:30 | 232 | 02:00
| Faridpur | 236 | 18:00 | 229 | 12:00 | Shyampur | 230 | 06:00 | 219 | 12:00
| Fenchuganj | 234 | 18:00 | 227 | 11:00 | Siddhirganj | 229 | 00:00 | 221 | 11:00
| Ghorashal | 232 | 01:00 | 132 | 07:00 | Sirajgonj | 233 | 05:00 | 230 | 11:00
| Ghorashal-230 | 228 | 05:00 | 217 | 12:00 | Sreepur | 229 | 06:00 | 219 | 12:00
| GPH | 234 | 19:30 | 228 | 17:00 | Tongi | 225 | 04:00 | 214 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 133 | 06:00 | 124 | 12:00 | Kushtia | 136 | 18:00 | 128 | 21:00
| Agargaon | 132 | 06:00 | 124 | 12:00 | Lalbag | 133 | 06:00 | 125 | 11:00
| Agrabad | 135 | 19:30 | 130 | 16:00 | Lalmonirhat | 128 | 15:00 | 115 | 21:00
| AKS | 132 | 01:00 | 129 | 13:00 | Madanganj | 131 | 05:00 | 124 | 12:00
| Aminbazar | 137 | 03:00 | 129 | 09:00 | Madaripur | 134 | 19:00 | 129 | 22:00
| Amnura | 136 | 18:00 | 123 | 19:30 | Madartek | 134 | 06:00 | 123 | 12:00
| Ashuganj | 135 | 00:00 | 133 | 11:00 | Madunaghat | 135 | 00:00 | 132 | 17:00
| Bagerhat | 139 | 18:00 | 125 | 22:00 | Magura | 136 | 18:00 | 126 | 21:00
| Bakulia | 136 | 19:30 | 131 | 12:00 | Mahasthangarh | 129 | 09:00 | 122 | 22:00
| Banani | 133 | 05:00 | 122 | 12:00 | Manikganj | 131 | 19:30 | 121 | 10:00
| Bangabhaban | 130 | 05:00 | 120 | 13:00 | Maniknagar | 130 | 06:00 | 120 | 12:00
| Barapukuria | 131 | 14:00 | 122 | 22:00 | Matarbari | 132 | 06:00 | 117 | 19:00
| Barguna | 132 | 06:00 | 129 | 01:00 | Matuail | 130.4 | 08:00 | 124.4 | 11:00
| Barishal | 136 | 18:00 | 130 | 01:00 | Millgate | 133 | 18:00 | 121 | 10:00
| Barishal-230 | 136 | 20:00 | 131 | 01:00 | Mirpur | 134 | 01:00 | 128 | 11:00
| Baroaulia | 136 | 19:30 | 130 | 17:00 | Mirzapur | 130 | 00:00 | 123 | 03:00
| Baroirhat | 129 | 18:30 | 121 | 03:00 | Mithapukur | 130 | 01:00 | 117 | 22:00
| Bashundhara | 136 | 09:00 | 121 | 12:00 | MI_Cement | 132 | 05:00 | 126 | 10:00
| BashundharaCement | 131 | 05:00 | 124 | 12:00 | Modern | 135 | 19:30 | 132 | 01:00
| Beanibazar | 124 | 07:00 | 118 | 23:00 | Mogbazar | 135 | 04:00 | 125 | 10:00
| Benapole | 134 | 18:00 | 122 | 22:00 | Mongla | 137 | 18:00 | 126 | 12:00
| Bhaluka | 125 | 00:00 | 118 | 19:00 | Motijheel | 130 | 05:00 | 120 | 13:00
| Bhandaria | 130 | 18:00 | 124 | 01:00 | Munshiganj | 132 | 20:00 | 125 | 12:00
| Bhangura | 135 | 06:00 | 130 | 19:00 | Mymensingh | 137 | 00:00 | 115 | 19:00
| Bheramara | 135 | 18:00 | 131 | 12:00 | Naogaon | 128 | 18:30 | 119 | 22:00
| Bheramara(GK) | 136 | 18:00 | 130 | 22:00 | Narail | 135 | 18:00 | 124 | 21:00
| Bhulta | 124 | 07:00 | 118 | 12:00 | Narinda | 130 | 06:00 | 120 | 12:00
| Bog-Sherpur | 130 | 06:00 | 124 | 22:00 | Narshingdi | 122 | 01:00 | 115 | 11:00
| Bogura | 132 | 08:00 | 127 | 21:00 | Natore | 133 | 18:00 | 126 | 21:00
| Bogura-230 | 132 | 08:00 | 126 | 21:00 | Nawabganj | 132 | 06:00 | 126 | 11:00
| Brahmanbaria | 127 | 06:00 | 121 | 19:00 | Netrakona | 134 | 00:00 | 121 | 19:00
| Cantonment | 131 | 06:00 | 123 | 12:00 | New | 134 | 18:00 | 123 | 10:00
| Chandpur | 128 | 18:00 | 119 | 04:00 | Niamatpur | 135 | 18:00 | 128 | 22:00
| Chandraghona | 137 | 19:30 | 133 | 10:00 | Noapara | 137 | 05:00 | 128 | 13:00
| Chapai | 132 | 18:00 | 125 | 01:00 | Pabna | 134 | 18:00 | 128 | 13:00
| Charsaidpur | 133 | 20:00 | 126 | 10:00 | Palashbari | 126 | 11:00 | 116 | 21:00
| Chauddagram | 131 | 18:30 | 122 | 06:00 | Panchagarh | 130 | 18:30 | 116 | 22:00
| Chhatak | 126 | 07:00 | 121 | 23:00 | Patuakhali | 133 | 04:00 | 129 | 15:00
| Chowmuhani | 124 | 18:00 | 114 | 19:00 | Payra | 135 | 07:00 | 132 | 02:00
| Chuadanga | 132 | 18:00 | 117 | 22:00 | PHP | 129 | 18:00 | 119 | 04:00
| Coxsbazar | 126 | 13:00 | 117 | 05:00 | Postogola | 134 | 07:00 | 128 | 10:00
| Cumilla(N) | 132 | 18:00 | 127 | 10:00 | Purbachal | 134 | 06:00 | 121 | 11:00
| Cumilla(S) | 133 | 07:00 | 125 | 10:00 | Purbasadipur | 126 | 18:30 | 114 | 22:00
| Daudkandi | 123 | 00:00 | 117 | 19:00 | Rahanpur | 136 | 18:00 | 131 | 22:00
| Dhaka | 134 | 05:00 | 123 | 12:00 | Rahim | 131 | 04:00 | 125 | 11:00
| Dhamrai | 127 | 06:00 | 121 | 10:00 | Rajbari | 132 | 18:00 | 126 | 22:00
| Dhanmondi | 131.5 | 20:00 | 124.5 | 12:00 | Rajendrapur | 132 | 20:00 | 120 | 10:00
| Dohazari | 132 | 08:00 | 127 | 19:00 | Rajshahi | 133 | 18:00 | 127 | 22:00
| Faridpur | 131 | 18:00 | 127 | 01:00 | Rajshahi-230 | 134 | 18:00 | 119 | 00:00
| Fatullah | 133 | 06:00 | 126 | 12:00 | Ramganj | 126 | 18:30 | 115 | 08:00
| Fenchuganj | 131 | 00:00 | 128 | 03:00 | Rampur | 134 | 05:00 | 130 | 19:00
| Feni | 127 | 23:00 | 120 | 05:00 | Rampura | 133 | 03:00 | 123 | 12:00
| Ghatail | 130 | 00:00 | 117 | 19:00 | Rangamati | 135 | 19:30 | 131 | 17:00
| Ghorashal | 135 | 01:00 | 128 | 12:00 | Rangpur | 128 | 14:00 | 115 | 22:00
| Goalpara | 141 | 18:00 | 131 | 12:00 | Ruppur | 136 | 06:00 | 130 | 22:00
| Gollamari | 136 | 05:00 | 130 | 13:00 | Saidpur | 128 | 18:30 | 117 | 01:00
| Gopalganj | 134 | 18:00 | 128 | 12:00 | Satkhira | 135 | 18:00 | 123 | 22:00
| Gopalganj-400 | 133 | 18:00 | 129 | 12:00 | Satmasjid | 131 | 06:00 | 123 | 12:00
| Gulshan | 133 | 07:00 | 12 | 12:00 | Savar | 134 | 01:00 | 128 | 09:00
| Halishahar | 136 | 19:30 | 131 | 17:00 | SevenRings | 135 | 05:00 | 129 | 12:00
| Haripur | 131 | 04:00 | 125 | 11:00 | ShahCement | 133 | 20:00 | 126 | 10:00
| HaripurSBU | 131 | 04:00 | 125 | 11:00 | Shahjadpur | 137 | 03:00 | 134 | 13:00
| Hasnabad | 133 | 02:00 | 127 | 11:00 | Shahjibazar | 125 | 07:00 | 120 | 22:00
| Hathazari | 138 | 23:00 | 134 | 11:00 | Shahmirpur | 137 | 19:30 | 130 | 03:00
| Ishurdi | 137 | 18:00 | 131 | 21:00 | Shariatpur | 133 | 18:00 | 127 | 01:00
| Jaldhaka | 125 | 14:00 | 112 | 22:00 | Sherpur | 138 | 00:00 | 121 | 19:00
| Jamalpur | 138 | 00:00 | 125 | 21:00 | Shikalbaha | 124 | 07:00 | 120 | 12:00
| Jashore | 135 | 18:00 | 123 | 22:00 | Shikalbaha-230 | 138 | 19:30 | 133 | 01:00
| Jhenaidah | 138 | 18:00 | 127 | 21:00 | Shitalakhya | 132 | 05:00 | 126 | 10:00
| Jhenaidah-230 | 138 | 18:00 | 128 | 21:00 | Sholosohor | 135 | 07:00 | 131 | 17:00
| Joydebpur | 130 | 00:00 | 122 | 19:00 | Shyampur | 133 | 20:00 | 127 | 10:00
| Joypurhat | 126 | 18:30 | 117 | 22:00 | Shyampur-230 | 133 | 06:00 | 125 | 12:00
| Juldah | 137 | 19:30 | 132 | 17:00 | Siddhirganj | 131 | 06:00 | 126 | 09:00
| Kabirpur | 134 | 19:30 | 119 | 09:00 | Sirajganj | 131 | 14:00 | 125 | 21:00
| Kachua | 129 | 18:30 | 120 | 02:00 | Sonargaon | 131 | 23:00 | 123 | 11:00
| Kaliakoir | 133 | 18:30 | 124 | 10:00 | Sreemongol | 126 | 08:00 | 121 | 19:00
| Kallyanpur | 131 | 06:00 | 125 | 12:00 | Sreepur | 129 | 05:00 | 123 | 12:00
| Kalurghat | 136 | 19:30 | 131 | 17:00 | Srinagar | 132 | 04:00 | 126 | 12:00
| Kamrangirchar | 133 | 06:00 | 125 | 10:00 | SSM | 139 | 00:00 | 134 | 11:00
| Kaptai | 137 | 1:00 | 135 | 12:00 | Sunamganj | 125 | 07:00 | 118 | 23:00
| Kazla | 129 | 05:00 | 119 | 13:00 | Sylhet | 127 | 14:00 | 123 | 22:00
| Keranigonj | 133 | 06:00 | 126 | 12:00 | Sylhet-132 | 128 | 16:00 | 125 | 22:00
| Khagrachori | 134 | 06:00 | 130 | 17:00 | Tangail | 130 | 00:00 | 118 | 19:00
| Khulna | 139 | 18:00 | 129 | 22:00 | Thakurgaon | 130 | 18:30 | 115 | 22:00
| Khulna(S) | 139 | 18:00 | 131 | 12:00 | TK | 134 | 00:00 | 132 | 16:00
| Khulshi | 134 | 19:30 | 129 | 19:00 | Tongi | 132 | 04:00 | 125 | 11:00
| Kishoreganj | 127 | 00:00 | 123 | 19:00 | Ullahpara | 134 | 18:30 | 128 | 22:00
| Kodda | 132 | 18:30 | 119 | 19:00 | Ullon | 133 | 03:00 | 124 | 12:00
| KSRM | 136 | 19:30 | 132 | 05:00 | Uttara | 134 | 00:00 | 126 | 12:00
| Kulaura | 129 | 00:00 | 126 | 22:00 | UttaraNew | 134 | 00:00 | 127 | 12:00
| Kurigram | 129 | 14:00 | 113 | 21:00 | Zigatola | 132 | 06:00 | 126 | 12:00

## L-Curve
Date | 2024-07-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1362 | 7593 | 6641 | 14234 |  |  |  | QF-LDC-11
0:30 | 1268 | 7503 | 6557 | 14060 | Date: | 2024-07-09
1:00 | 1174 | 7413 | 6473 | 13886
1:30 | 1155 | 7389.5 | 6466.5 | 13856
2:00 | 1136 | 7366 | 6460 | 13826
2:30 | 1138 | 7345 | 6406 | 13751 | [5 empty] | Gen. at Eve. Peak | 15047 | 15047 MW (21:00 )
3:00 | 1140 | 7324 | 6352 | 13676 | [6 empty] | 21:00
3:30 | 1132 | 7303 | 6257 | 13560 | [5 empty] | Gen. at Day Peak | 13415 | 13415 MW (12:00 )
4:00 | 1124 | 7282 | 6162 | 13444 | [6 empty] | 12:00
4:30 | 1086 | 7249 | 6071.5 | 13320.5 | [5 empty] | Highest Generation | 15047
5:00 | 1048 | 7216 | 5981 | 13197 | [6 empty] | 21:00
5:30 | 1056 | 7124 | 5851 | 12975
6:00 | 1064 | 7032 | 5721 | 12753
6:30 | 1080 | 6913 | 5747.5 | 12660.5
7:00 | 1096 | 6794 | 5774 | 12568
7:30 | 1202 | 6769.5 | 5796.5 | 12566
8:00 | 1308 | 6745 | 5819 | 12564
8:30 | 1372 | 6807.5 | 5835.5 | 12643
9:00 | 1436 | 6870 | 5852 | 12722
9:30 | 1447 | 7124 | 5817.5 | 12941.5
10:00 | 1458 | 7378 | 5783 | 13161
10:30 | 1441 | 7392 | 5855 | 13247
11:00 | 1424 | 7406 | 5927 | 13333
11:30 | 1418 | 7414.5 | 5959.5 | 13374
12:00 | 1412 | 7423 | 5992 | 13415
12:30 | 1327 | 7424 | 6063 | 13487
13:00 | 1242 | 7425 | 6134 | 13559
13:30 | 1218 | 7361.5 | 6068.5 | 13430
14:00 | 1194 | 7298 | 6003 | 13301
14:30 | 1215 | 7296.5 | 5998 | 13294.5
15:00 | 1236 | 7295 | 5993 | 13288
15:30 | 1303 | 7286.5 | 6114.5 | 13401
16:00 | 1370 | 7278 | 6236 | 13514
16:30 | 1375 | 7272.5 | 6173 | 13445.5
17:00 | 1380 | 7267 | 6110 | 13377
17:30 | 1298 | 7264.5 | 5920 | 13184.5
18:00 | 1216 | 7262 | 5730 | 12992
18:30 | 1363 | 7542.5 | 5969 | 13511.5
19:00 | 1510 | 7823 | 6208 | 14031
19:30 | 1230 | 8227 | 6577 | 14804
20:00 | 1150 | 8203 | 6574 | 14777 |  |  |  | Executive Engineer
20:30 | 1079 | 8290 | 6622 | 14912 |  |  |  | Network Operation Division
21:00 | 1008 | 8377 | 6670 | 15047
21:30 | 1045 | 8270.5 | 6707.5 | 14978
22:00 | 1082 | 8164 | 6745 | 14909 |  |  |  |  | Page 6 of 7
22:30 | 1159 | 7957.5 | 6720 | 14677.5
23:00 | 1236 | 7751 | 6695 | 14446
23:30 | 1299 | 7672 | 6668 | 14340
24:00 | 1362 | 7593 | 6641 | 14234
15047 MW (21:00 )
13415 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-09 |  | Energy |  | 330162865
[15 empty] | 2024-07-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3869 | 918 | 1451 | 0 | 2531 | 4620 | 166 | 0 | 575 | 86 | 0 | 18 | 1018.03
0:30 | 3917.5 | 918.5 | 1442.5 | 0 | 2349.5 | 4635.5 | 165.5 | 0 | 532.5 | 84 | 0 | 14.5 | 993.2 |  |  | Date: | 44020
1:00 | 3966 | 919 | 1434 | 0 | 2168 | 4651 | 165 | 0 | 490 | 82 | 0 | 11 | 968.37
1:30 | 3991 | 918.5 | 1433.5 | 0 | 2164.5 | 4651 | 165 | 0 | 435 | 82 | 0 | 15.5 | 815.57 | [9 empty] | Total Energy | 330.1629 | 330.1629 | Total Energy Gen 330.163 MKWHr Energy Not Served 13.065 MKWHr Energy Requirement 343.228 MKWHr
2:00 | 4016 | 918 | 1433 | 0 | 2161 | 4651 | 165 | 0 | 380 | 82 | 0 | 20 | 662.77 | [9 empty] | Energy not Served | 13.0653 | 13.0653
2:30 | 4054 | 918.5 | 1442.5 | 0 | 2138 | 4551 | 165 | 0 | 380 | 82 | 0 | 20 | 557.72 | [9 empty] | Energy Requirement | 343.2281 | 343.2281
3:00 | 4092 | 919 | 1452 | 0 | 2115 | 4451 | 165 | 0 | 380 | 82 | 0 | 20 | 452.67
3:30 | 4088 | 919.5 | 1458 | 0 | 2051 | 4429.5 | 165 | 0 | 357 | 79 | 0 | 13 | 444.075 | [8 empty] | Shortage
4:00 | 4084 | 920 | 1464 | 0 | 1987 | 4408 | 165 | 0 | 334 | 76 | 0 | 6 | 435.48
4:30 | 4066 | 920 | 1471 | 0 | 1966.5 | 4329 | 165 | 0 | 321.5 | 76 | 0 | 5.5 | 434.0475
5:00 | 4048 | 920 | 1478 | 0 | 1946 | 4250 | 165 | 0 | 309 | 76 | 0 | 5 | 432.615
5:30 | 3938 | 919.5 | 1462.5 | 0 | 1921.5 | 4165.5 | 165 | 0 | 309 | 73 | 8.5 | 12.5 | 391.55
6:00 | 3828 | 919 | 1447 | 0 | 1897 | 4081 | 165 | 0 | 309 | 70 | 17 | 20 | 350.485
6:30 | 3779 | 919.5 | 1444.5 | 0 | 1842 | 4082 | 165 | 0 | 297 | 64 | 55 | 12.5 | 333.7725 | [7 empty] | Coal
7:00 | 3730 | 920 | 1442 | 0 | 1787 | 4083 | 165 | 0 | 285 | 58 | 93 | 5 | 317.06
7:30 | 3706.5 | 919.5 | 1437 | 0 | 1769 | 4078.5 | 165 | 0 | 257 | 62 | 161.5 | 10 | 314.195 | [6 empty] | Oil
8:00 | 3683 | 919 | 1432 | 0 | 1751 | 4074 | 165 | 0 | 229 | 66 | 230 | 15 | 311.33
8:30 | 3700 | 918.5 | 1475.5 | 0 | 1732.5 | 4115 | 165.5 | 0 | 223.5 | 66 | 230.5 | 16 | 297.96
9:00 | 3717 | 918 | 1519 | 0 | 1714 | 4156 | 166 | 0 | 218 | 66 | 231 | 17 | 284.59
9:30 | 3822.5 | 918.5 | 1499 | 0 | 1769 | 4153 | 166 | 0 | 249 | 72 | 282 | 10.5 | 351.9175
10:00 | 3928 | 919 | 1479 | 0 | 1824 | 4150 | 166 | 0 | 280 | 78 | 333 | 4 | 419.245
10:30 | 3916 | 919 | 1458.5 | 0 | 1849 | 4224 | 166 | 0 | 270.5 | 79 | 361 | 4 | 480.365
11:00 | 3904 | 919 | 1438 | 0 | 1874 | 4298 | 166 | 0 | 261 | 80 | 389 | 4 | 541.485
11:30 | 3909 | 919 | 1473 | 0 | 1874 | 4307 | 166 | 0 | 291 | 80 | 343.5 | 11.5 | 597.83
12:00 | 3914 | 919 | 1508 | 0 | 1874 | 4316 | 166 | 0 | 321 | 80 | 298 | 19 | 654.175
12:30 | 3890.5 | 919.5 | 1456.5 | 0 | 1898.5 | 4358 | 166 | 0 | 327 | 80 | 365 | 26 | 708.61
13:00 | 3867 | 920 | 1405 | 0 | 1923 | 4400 | 166 | 0 | 333 | 80 | 432 | 33 | 763.045
13:30 | 3867 | 920 | 1405 | 0 | 1923 | 4400 | 166 | 0 | 333 | 80 | 432 | 33 | 763.045
14:00 | 3867 | 920 | 1405 | 0 | 1923 | 4400 | 166 | 0 | 333 | 80 | 432 | 33 | 763.045
14:30 | 3804 | 919 | 1397.5 | 0 | 1966.5 | 4437 | 166 | 0 | 303.5 | 84 | 312.5 | 33.5 | 817.0025
15:00 | 3741 | 918 | 1390 | 0 | 2010 | 4474 | 166 | 0 | 274 | 88 | 193 | 34 | 870.96
15:30 | 3761.5 | 918 | 1434 | 0 | 2044 | 4491 | 166 | 0 | 274.5 | 84 | 198 | 30 | 810.795
16:00 | 3782 | 918 | 1478 | 0 | 2078 | 4508 | 166 | 0 | 275 | 80 | 203 | 26 | 750.63
16:30 | 3783.5 | 918 | 1443 | 0 | 2051.5 | 4529 | 166 | 0 | 302 | 80 | 143.5 | 29 | 625.0475
17:00 | 3785 | 918 | 1408 | 0 | 2025 | 4550 | 166 | 0 | 329 | 80 | 84 | 32 | 499.465
17:30 | 3755.5 | 918 | 1359 | 0 | 2063 | 4412.5 | 166 | 0 | 350.5 | 79 | 60 | 21 | 387.2325
18:00 | 3726 | 918 | 1310 | 0 | 2101 | 4275 | 166 | 0 | 372 | 78 | 36 | 10 | 275
18:30 | 3714.5 | 917.5 | 1314.5 | 0 | 2357.5 | 4372.5 | 166 | 0 | 556.5 | 83 | 18 | 11.5 | 242.0725
19:00 | 3703 | 917 | 1319 | 0 | 2614 | 4470 | 166 | 0 | 741 | 88 | 0 | 13 | 209.145
19:30 | 3833 | 916 | 1435 | 0 | 2997 | 4580 | 166 | 0 | 775 | 84 | 0 | 18 | 306.555
20:00 | 3799 | 917 | 1360 | 0 | 3061 | 4572 | 166 | 0 | 793 | 84 | 0 | 25 | 403.965
20:30 | 3844.5 | 917 | 1411 | 0 | 3103 | 4575.5 | 166 | 0 | 798.5 | 79 | 0 | 17.5 | 394.415
21:00 | 3890 | 917 | 1462 | 0 | 3145 | 4579 | 166 | 0 | 804 | 74 | 0 | 10 | 384.865
21:30 | 3863 | 917 | 1483 | 0 | 3076 | 4592.5 | 166 | 0 | 789.5 | 81 | 0 | 10 | 403.01
22:00 | 3836 | 917 | 1504 | 0 | 3007 | 4606 | 166 | 0 | 775 | 88 | 0 | 10 | 421.155
22:30 | 3830 | 916.5 | 1429.5 | 0 | 2899 | 4632.5 | 166 | 0 | 703.5 | 88 | 0 | 12.5 | 666.1125
23:00 | 3824 | 916 | 1355 | 0 | 2791 | 4659 | 166 | 0 | 632 | 88 | 0 | 15 | 911.07
23:30 | 3846.5 | 917 | 1403 | 0 | 2661 | 4639.5 | 166 | 0 | 603.5 | 87 | 0 | 16.5 | 964.55 |  |  | Max Temp. in Dhaka |  | 33.1°C
24:00 | 3869 | 918 | 1451 | 0 | 2531 | 4620 | 166 | 0 | 575 | 86 | 0 | 18 | 1018.03
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 330.163 MKWHr Energy Not Served 13.065 MKWHr Energy Requirement 343.228 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 2089620
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1924000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 4 | 8 |  | 13 | 16 | 17 | 17 | 17 | 8 | 8 | 93475
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 4 | 6 | 9 | 16 | 4 | 16 | 17 | 4 | 5 | 1 | 0 | [8 empty] | 88965
6 | Sikalbaha 225MW CCPP (Gas) | 219 | 220 | 220 | 220 | 220 | 220 | 219 | 220 | 221 | 221 | 221 | 216 | 220 | 216 | 216 | 217 | 220 | 221 |  | 220 | 221 | 223 | 222 | 222 | 223 | 223 | 5291562
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 78 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 76 | 85 | 68 | 68 | 68 | 51 | 51 | 51 | 51 | 51 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1760231
12 | Hathazari 100 MW peaking PP | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 70 | 74 | 74 | 60 | 68 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1681872
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 54 | 68 | 68 | 68 | 68 | 68 | 68 | 1373309
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 36 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 872768
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 322 | 326 | 327 | 327 | 327 | 260 | 260 | 260 | 260 | 320 | 320 | 312 | 315 | 316 | 320 | 320 | 330 | 324 |  | 270 | 314 | 307 | 297 | 283 | 302 | 306 | 7354149
18 | Kodda 300 MW PP Unit-2 (Summit) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 45 | 57 | 80 | 80 | 80 | 56 | 56 | 42 | 60 |  | 110 | 145 | 140 | 148 | 147 | 72 | 47 | 1663527
19 | Ashuganj 195 MW PP (APSCL-United) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 |  | 33454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 605 | 604 | 605 | 600 | 557 | 468 | 452 | 455 | 510 | 553 | 601 | 606 | 608 | 610 | 610 | 606 | 608 | 605 |  | 610 | 605 | 600 | 610 | 610 | 610 | 600 | 13996362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 10 | 10 | 10 | 10 | 10 | 10 |  | 20 | 20 | 29 | 35 | 36 | 36 | 36 | 609408
33 | Ashuganj 225 MW CCPP | 217 | 217 | 216 | 215 | 216 | 216 | 216 | 217 | 214 | 213 | 213 | 197 | 208 | 211 | 195 | 161 | 214 | 217 |  | 211 | 217 | 217 | 215 | 179 | 178 | 214 | 5077000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 250 | 240 | 270 | 275 | 280 | 280 | 240 | 240 | 260 | 260 | 240 |  | 240 | 260 | 240 | 240 | 240 | 240 | 240 | 6145000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 280 | 310 | 280 | 325 | 280 | 280 | 320 | 300 | 300 | 285 |  | 330 | 285 | 285 | 290 | 295 | 280 | 280 | 7419100
| Ashuganj 420 MW CCPP(East) | 280 | 280 | 280 | 280 | 280 | 330 | 280 | 240 | 240 | 270 | 300 | 280 | 280 | 230 | 230 | 280 | 280 | 280 |  | 280 | 280 | 280 | 285 | 290 | 240 | 240 | 6674200
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 |  | 7 | 20 | 26 | 42 | 45 | 45 | 23 | 339840
36 | Chandpur 150 MW CCPP | 40 | 42 | 42 | 42 | 40 | 42 | 40 | 40 | 40 | 40 | 40 | 40 | 36 | 36 | 35 | 35 | 30 | 25 |  | 25 | 25 | 25 | 31 | 31 | 30 | 30 | 844110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 413 | 412 | 411 | 411 | 411 | 389 | 352 | 352 | 389 | 404 | 405 | 401 | 401 | 402 | 405 | 377 | 317 | 322 |  | 325 | 406 | 392 | 400 | 399 | 401 | 401 | 9403200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 420 | 420 | 420 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 420 | 420 | 420 | 420 | 420 | 420 | 400 |  | 390 | 380 | 380 | 360 | 350 | 360 | 370 | 9116500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 22 | 22 | 22 | 23 | 23 | 23 | 20 | 20 | 17 | 16 | 11 | 11 | 11 | 9 | 9 | 9 | 10 | 10 |  | 11 | 11 | 17 | 18 | 18 | 20 | 19 | 372480
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 8 | 11 | 29 | 28 | 20 | 22 | 13 | 11 | 11 | 36 | 11 | 1 | [8 empty] | 205250
44 | Fenchugonj CCPP Phase-1 | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 |  | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 504000
45 | Fenchugonj CCPP Phase-2 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 55 | 56 | 54 | 54 | 54 | 55 | 54 | 54 | 54 | 54 |  | 59 | 54 | 54 | 54 | 54 | 54 | 56 | 1304040
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 59 | 59 | 56 | 56 | 56 | 56 | 58 | 57 | 57 | 54 | 56 | 57 | 57 | 58 | 40 | 40 |  | 40 | 40 | 40 | 56 | 50 | 56 | 56 | 1284000
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 210 | 210 | 210 | 211 | 211 | 211 | 211 | 211 | 206 | 208 | 206 | 208 | 208 | 209 | 206 | 208 | 212 |  | 210 | 210 | 209 | 211 | 211 | 210 | 210 | 5242450
51 | Sylhet 20 MW GTPP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 292000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 2 |  |  |  |  | 5 | 5 | 5 | 5 | 5 | 2 | 78624
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 46 | 47 | 44 | 47 | 47 | 47 | 50 | 50 |  | 50 | 53 | 53 | 53 | 53 | 53 | 50 | 1193400
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 272736
57 | Bibiana-II 341 MW CCPP (Summit) | [11 empty] | 15 | [13 empty] | 10 | 0
| Bibiyana South 400 MW | 346 | 346 | 346 | 346 | 346 | 310 | 310 | 310 | 310 | 371 | 346 | 371 | 345 | 345 | 345 | 345 | 345 | 345 |  | 375 | 345 | 345 | 390 | 383 | 390 | 390 | 8428700
58 | Nababganj 55 MW PP (Southern power ) |  |  | 35 | 35 | 35 | 35 |  |  | 2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 55 | 55 | 55 | 35 | 17 |  | 665415
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 3 | 3 | 1 | 0 | 0 | 0 | 121200
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 82 | 82 | 76 | 76 | 70 | 58 | 66 | 66 | 78 | 80 | 80 | 80 | 86 | 88 | 80 | 80 | 78 |  | 88 | 84 | 84 | 74 | 88 | 88 | 86 | 1879680
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 37 | 37 | 38 | 37 | 37 | 5 | 2 | 2 | 2 | 0 | 2 | 2 | 2 | 2 | 4 | 6 |  | 12 | 11 | 15 | 15 | 8 | 23 | 33 | 407520
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 374730
69 | Summit Ashulia | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 |  | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 370200
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 355320
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 486900
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 7 | 0 | 7 | 7 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 6 |  | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 224900
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 17 | 872100
| Chowmuhani 113 MW | 52 | 46 | 47 | 47 | 47 | 47 | 46 | 47 | 52 | 46 | 47 | 46 | 46 | 46 | 47 | 47 | 65 | 93 |  | 91 | 91 | 93 | 94 | 100 | 98 | 93 | 1487640
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 72 | 90 | 108 | 108 | 108 | 108 | 108 | 162 | 162 |  | 162 | 162 | 162 | 162 | 108 | 72 | 54 | 1944000
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 54 | 52 | 52 | 56 | 57 |  | 58 | 58 | 58 | 58 | 44 | 41 | 41 | 1181760
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 145440
79 | Kodda 150 MW PP | 82 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 48 | 48 | 48 | 48 | 48 | 64 | 64 |  | 126 | 131 | 132 | 146 | 132 | 132 | 98 | 1440000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 789509
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 487680
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 2 | 4 | 4 | 3 |  |  | 0 | 1 | 0 | [8 empty] | 19477
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 |  | 28 | 54 | 54 | 54 | 54 | 54 | 54 | 1286327
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 92 | 81 | 78 | 72 | 73 | 73 | 73 | 60 | 54 | 54 | 54 | 54 | 58 | 72 | 82 |  | 90 | 90 | 92 | 92 | 92 | 92 | 92 | 1901050
82 | Madanganj 102 PP(Summit) | 82 | 82 | 82 | 82 | 70 | 70 | 57 | 66 | 66 | 66 | 50 | 50 | 50 | 50 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1616478
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 8 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 79000
86 | Meghnaghat CCPP ( Summit) | 138 | 135 | 138 | 141 | 143 | 139 | 138 | 148 | 138 | 151 | 140 | 150 | 137 | 138 | 149 | 120 | 130 | 120 |  | 150 | 130 | 123 | 155 | 151 | 132 | 137 | 3381585
87 | Meghnaghat 100 MW(IEL) | 24 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | 32 | 46 | 52 | 53 | 50 | 34 | 34 | 33 | 33 |  | 37 | 66 | 69 | 92 | 98 | 98 | 99 | 1076160
| Meghnaghat 104 MW PP (OPCL) | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 33 | 65 | 63 | 87 | 87 | 88 | 88 | 792960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 12 | 12 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1519320
92 | Fenchuganj 44 MW (Energyprima) | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 36 | 36 | 36 | 36 | 39 | 39 | 35 | 35 | 36 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 |  | 885168
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 952551
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 49 | 49 | 49 | 49 | 49 | 57 | 65 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1215360
95 | Patenga 50MW PP (Baraka) | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 12 | 22 | 40 | 48 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 44 | 39 | 859680
96 | Chattogram 108 MW PP (ECPV) | 28 | 25 | 25 | 25 | 25 | 25 | 27 | 32 | 26 | 25 | 25 | 28 | 32 | 31 | 32 | 31 | 32 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 751680
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 23 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 55 | 55 | 55 | 15 | 15 | 15 | 676630
100 | Manikganj 55 MW PP (Northern) | 35 | 17 |  |  |  |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 672822
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 |  | 120 | 163 | 163 | 163 | 163 | 120 | 163 | 3616854
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 13280
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 16 | 35 | 35 | 35 | 35 | 35 | 35 | 608040
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 108 | 117 | 116 | 107 | 115 | 110 | 110 | 114 | 114 | 115 |  | 152 | 143 | 143 | 161 | 153 | 153 | 153 | 2983200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 97 | 97 | 97 | 97 | 89 | 93 | 81 | 97 | 82 | 80 | 71 | 64 | 74 | 73 | 91 | 75 | 87 | 89 |  | 97 | 97 | 95 | 95 | 95 | 96 | 96 | 2129328
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 36 | 25 | 25 | 36 | 49 | 49 | 49 | 49 | 49 | 49 | 60 |  | 62 | 62 | 62 | 62 | 62 | 62 | 49 | 1155840
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 415200
117 | Ashuganj 150 MW PP (Midland) | 113 | 140 | 142 | 140 | 137 | 135 | 85 | 50 | 50 | 50 | 52 | 45 | 43 | 43 | 41 | 38 | 36 | 42 |  | 59 | 120 | 117 | 137 | 135 | 102 | 95 | 2034036
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 401 | 403 | 401 | 403 | 352 | 403 | 404 | 404 | 392 | 404 | 404 | 403 | 404 | 404 | 400 |  | 345 | 400 | 400 | 402 | 400 | 403 | 402 | 9565000
| Jamalpur 115 MW PP (United) | 67 | 67 | 67 | 67 | 68 | 67 | 67 | 66 | 65 | 65 | 65 | 57 | 66 | 66 | 66 | 67 | 67 | 67 |  | 76 | 76 | 76 | 66 | 67 | 67 | 67 | 1604400
| Anwara 300 MW PP (United) | 55 | 65 | 69 | 69 | 69 | 69 | 69 | 52 | 52 | 52 | 52 | 52 | 68 | 69 | 69 | 67 | 67 | 67 |  | 69 | 69 | 70 | 69 | 70 | 52 | 52 | 1525527
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 50 | 50 | 50 | 50 | 50 |  | 50 | 62 | 62 | 62 | 62 | 62 | 50 | 1256640
| Anlima Energy Ltd. | 53 | 37 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 38 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 18 | 17 | 1013673
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 540000
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 6 | 11 | 15 | 20 | 18 | 11 | 11 | 18 | 6 | 11 | 8 | 3 | [8 empty] | 149583
| Chandpur 115(Doreen) | 50 | 48 | 32 | 33 | 33 | 32 | 33 | 32 | 44 | 49 | 49 | 50 | 49 | 49 | 48 | 48 | 49 | 66 |  | 105 | 115 | 115 | 93 | 87 | 88 | 88 | 1385280
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | [9 empty] | 12 | 15 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 257040
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 |  | 163 | 163 | 163 | 163 | 163 | 17 | 17 | 1147490
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 11 | 20 | 20 | 6 | 5 | 20 | 5 | 15 | 17 | 4 | 4 | 19 | 33 | 44 | 34 | 26 | 32 | 10 |  | 13 | 18 | 25 | 10 | 10 | 15 | 18 | 420480
| Sonagazi 75 MW Solar Plant | [5 empty] | 3 | 5 | 19 | 26 | 49 | 32 | 36 | 52 | 7 | 19 | 18 | 12 | 6 | [8 empty] | 327436
| Matarbari 2*600 MW (CPGCL) | 520 | 516 | 517 | 516 | 518 | 517 | 515 | 518 | 518 | 517 | 518 | 519 | 517 | 517 | 517 | 512 | 517 | 510 |  | 518 | 517 | 515 | 519 | 517 | 517 | 517 | 12494545
120 | Eastern Zone Total | 7413 | 7366 | 7324 | 7282 | 7216 | 7032 | 6794 | 6745 | 6870 | 7378 | 7406 | 7423 | 7425 | 7298 | 7295 | 7278 | 7267 | 7262 |  | 7823 | 8227 | 8203 | 8377 | 8164 | 7751 | 7593 | 178592446
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 94 | 95 | 95 | 95 | 79 | 79 | 79 | 77 | 77 | 63 | 63 | 63 | 79 | 77 | 78 | 78 | 81 | 93 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1975680
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2 | [9 empty] | 25 |  | 42 | 47 | 42 | 42 | 42 | 42 | 27 | 379680
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 71 | 91 | 91 |  | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 1255200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 16 | 53 | 51 | 65 | 54 | 73 | 55 | 11 | 37 | 36 | 16 | 6 | [8 empty] | 513360
131 | Rampal 1320 MW (BIFPCL) | 341 | 340 | 336 | 338 | 340 | 341 | 340 | 340 | 339 | 342 | 338 | 338 | 339 | 338 | 336 | 337 | 338 | 339 |  | 339 | 338 | 338 | 337 | 338 | 360 | 338 | 8298182
132 | United Payra Power Ltd. | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | [8 empty] | 10 | 35 | 54 | 54 | 54 | 54 | 562800
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 220 |  | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 5363182
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 50 | 64 | 110 | 110 | 110 | 110 | 16 | 793536
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4113600
136 | Barisal 1 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 3413
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 130 | 130 | 130 | 80 | 80 | 108 | 108 | 126 |  | 130 | 126 | 126 | 130 | 128 | 128 | 130 | 2899000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 9 | 10 | 10 | 9 | 10 | 8 | 7 | 7 | 7 | 7 | 8 | 6 | 0 | 9 | 7 | 7 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 198875
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 8 | 16 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  |  | 438000
143 | Gopalganj 100 MW Peaking PP | 41 | 38 | 38 | 38 | 38 | 38 | 38 | [10 empty] | 4 |  | 31 | 45 | 53 | 53 | 43 | 43 | 43 | 533504
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 919 | 918 | 919 | 920 | 920 | 919 | 920 | 919 | 918 | 919 | 919 | 919 | 920 | 919 | 918 | 918 | 918 | 918 |  | 917 | 916 | 917 | 917 | 917 | 916 | 918 | 22239360
147 | Bheramara 410 MW CCPP | 305 | 305 | 300 | 300 | 300 | 300 | 300 | 300 | 305 | 305 | 305 | 311 | 310 | 310 | 310 | 309 | 309 | 310 |  | 310 | 314 | 313 | 314 | 321 | 326 | 326 | 7502112
148 | Payra 1320 MW | 1222 | 1222 | 1120 | 1080 | 1060 | 980 | 1000 | 980 | 990 | 990 | 1090 | 1110 | 1140 | 1200 | 1244 | 1220 | 1244 | 1120 |  | 1080 | 1180 | 1180 | 1200 | 1230 | 1244 | 1244 | 29196100
149
150 | Barapukuria TPP Unit-1 | 60 | 60 | 59 | 59 | 60 | 60 | 59 | 59 | 60 | 59 | 59 | 60 | 59 | 58 | 61 | 60 | 60 | 60 |  | 61 | 60 | 60 | 60 | 60 | 61 | 60 | 1405090
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 220 | 220 | 220 | 220 | 220 | 220 | 182 | 194 | 220 | 220 |  | 220 | 220 | 220 | 200 | 200 | 200 | 200 | 5030000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 24 | 24 | 24 | 24 | 24 | [10 empty] | 38 | 38 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 451445
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 2 | 3 | 6 | 3 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 30240
| Sirajganj 68 MW Solar Park | [5 empty] | 3 | 14 | 22 | 21 | 26 | 59 | 56 | 54 | 63 | 16 | 12 | 3 | 2 | [8 empty] | 341250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 86 | 132 | 214 | 214 | 214 | 214 | 214 | 214 | 204 | 173 | 163 | 172 | 179 | 148 | 160 | 191 | 212 | 175 |  | 162 | 190 | 182 | 184 | 180 | 190 | 193 | 4698382
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 179 | 180 | 180 | 178 | 143 | [21 empty] | 943073
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 303 | 305 | 322 | 330 | 342 | 330 | 325 | 339 | 400 | 350 | 321 | 397 | 324 | 337 | 346 | 414 | 330 | 300 |  | 310 | 358 | 280 | 354 | 414 | 302 | 392 | 8323490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 4 | 5 | 10 | 10 | 5 | 5 | 5 | 27444
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 |  |  |  |  | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 103140
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 25 | 25 | 25 | 25 | [13 empty] | 6 |  | 27 | 36 | 45 | 42 | 42 | 42 | 42 | 309600
168 | Santahar 50 MW Peaking PP | 30 | 30 | 30 | [13 empty] | 14 | 15 |  | 30 | 30 | 30 | 30 | 30 | 30 | 22 | 278123
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 56 | [10 empty] | 44 | 56 | 48 | 48 | 48 | 48 | 48 |  | 85 | 85 | 85 | 85 | 85 | 88 | 88 | 813184
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 35 | 50 | 55 | 70 | 80 | 35 | 35 |  | 51 | 113 | 113 | 113 | 113 | 113 | 113 | 1918848
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 70 | 90 | 95 | 35 |  | 110 | 113 | 113 | 113 | 113 | 113 | 113 | 1967712
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16000
175 | Saidpur 20 MW GTPP | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 98 | 84 | 84 | 97 | 103 | 103 | 103 | 99 | 95 | 45 | 34 |  | 84 | 104 | 100 | 106 | 106 | 106 | 99 | 2294908
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 1 | 1 | [8 empty] | 20362
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 48 | 52 | 52 | 52 | 54 | 54 | 54 | 35 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1352064
| Intraco Solar 30 MW | [5 empty] | 1 | 2 | 4 | 4 | 13 | 22 | 17 | 14 | 19 | 27 | 14 | 4 | 2 |  | 0 | [6 empty] | 134540
| Adani Power Jharkhanda Ltd | 1503 | 1509 | 1414 | 1415 | 1315 | 1315 | 1317 | 1322 | 1319 | 1319 | 1322 | 1313 | 1367 | 1370 | 1374 | 1429 | 1413 | 1271 |  | 1492 | 1510 | 1509 | 1503 | 1501 | 1517 | 1511 | 33611690
178 | Teesta Solar Limited | [5 empty] | 7 | 40 | 102 | 73 | 115 | 154 | 69 | 208 | 143 | 68 | 67 | 27 | 15 | [8 empty] | 1234250