## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-15 | Monday
|  | Date (day): | 2024-07-15 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14479.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15535 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-14 | 2024-07-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage |  | 16-07-24
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 402 | 403 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 23 | 8 | 8 | 8 | 92 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 280 | 281 | 280 | 280 | 55 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 82 | 68 | 65 | 82 | 20 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 13 |  | 62 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 75 | 100 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 318 | 0 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 |  | 94 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 132 | 16 | 132 |  | 17 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 30 | 30 | 30 |  | 50 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 14 | 14 | 14 | 14 |  | 19 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 10 | 11 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 97 | 155 | 45 | 150 | 150 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 79 | 96 | 95 | 100 |  | 49 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 137 | 108 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 |  | 38 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | on test
| Dhaka area Total |  |  |  |  | 6347 | 5634 | 1984 | 2117 | 1679 | 1982 | 2050 | 1310
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 196 | 196 | 185 | 196 | 34 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 220 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 34 | 34 | 105
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 69 | 70 | 70 | 28 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 46 | 46 | 46 | 54 |  | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 62 | 34 | 62 | 38 |  | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 22 | 5 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 38 | 38 | 32 | 38 | 70 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 51 | 52 | 52 | 248 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 17 | 17 | 37 |  | Fuel shortage
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 34 | 34 | 80 |  | 30 | Engine problem
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 62 | 50 | 62 | 38 |  | Fuel shortage
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 0 | 90 | 90 | 26 |  | Fuel shortage
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 145 | 35 | 145 |  | 18 | Engine problem
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 1100 | 1150 | 1100 | 1200
| Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 8 | 26 | 44 | 62 |  |  | On test.
61 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 420 | 420 | 420 | 420 |  |  | Unit-1 Under maint
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 55 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 2204 | 2701 | 2672 | 2994 | 770 | 429
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 213 | 200 | 210
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 310 | 280 | 310 | 50 |  | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 250 | 280 | 80 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 285 | 320 | 280 | 320 | 80 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 36 | 33 | 36 | 9 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 34 | 20 | 20 | 20 | 35 |  | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 43 | 51 | 51
70 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 12 | 12 | 80 | 90 |  | 60 | Engine problem
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 14 | 28 | 28 | 28 |  | 24 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 38 | 50 | 50 | 113 |  | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 120 | 100 | 120 | 80 |  | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 86 | 90 | 90 | 100
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 33 | 33 | 33 | 33
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 88 | 52 | 88 | 26 |  | Fuel shortage
79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 91 | 46 | 90 |  | 23 | Engine problem
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 115 | 49 | 115
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1592 | 1862 | 1667 | 1966 | 660 | 148
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 5 | 17 | 20 | 20 | 182 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 143 | 116 | 143 | 57 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 87 | 60 | 87 | 28 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 32 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 2 | 6 | 6 | 16 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 36 | 17 | 36
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 244 | 285 | 270.6 | 292 | 182 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 37 | 37 | 36 | 37 |  | 33 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 57 | 54 | 57 |  | 33 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 51
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 36 | 35 | 35 | 35 |  | 15 | Engine problem
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 3 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 55 | 60 | 60
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 211 | 209 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 280 | 285 | 56 |  | Gas shortage
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 403 | 366 | 340 | 360 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 377 | 345 | 320 | 345 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1696 | 1619 | 1563 | 1620 | 76 | 451
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 914 | 913 | 937 | 937
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 78 | 77 | 98 | 17 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 31 | 30 | 35 |  | 19 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 31 | 50 | 50 |  | 59 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 208 | 195 | 200 | 200 | 210 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 16 | 8 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 0 | 105 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 99 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 710 | 712 | 720 | 720 | 514 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1939 | 1993 | 2122 | 2056 | 1557 | 78
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 16
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 9 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 124 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1070 | 1230 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 35 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 180 | 307 | 230 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1603 | 1944 | 1841 | 1962 | 115 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 4 | 0 | 10 |  | 61 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0 |  | 28 | Engine problem
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 36 | 47
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 181 | 171 | 150 | 170 | 40 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 400 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 27 | 86 | 50 | 85 |  | 19 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 113 | 113 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 80 | 113 | 113 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1134 | 1131 | 1100 | 1140
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 50 | 0 | 5 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1926 | 2154 | 2027 | 2167 | 703 | 146
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 61 | 61 | 60 | 60 |  | 25
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 220 | 220 | 220 | 220 |  | 54 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 101 | 100 | 101 |  | 12 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 54 | 115 | 90 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 158 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 557 | 497 | 638 | 496 | 40 | 176
| Total |  |  |  |  | 27515 | 26364 | 13745 | 15172 | 14479.6 | 15535 | 6153 | 2802
A. |  | 2024-07-14 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 15172 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12389 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15700 | MW
3 | Day peak Generation : |  |  | 13745 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15038.21 | MW
4 | Evening peak Generation : |  |  | 15172 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 504 | MW
5 | Total Energy Generation : |  | 330.9205 | MKWHr | By Solar | 3.7629 | MKWHr
| By Gas : | 129.9034 | MKWHr |  | By Oil: | 47.2495 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 122.6421 | MKWHr |  | By Hydro: | 4.6634 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.47136 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6153 | MW | Dhaka | 5322.71 | 5137.71 |  | 185 |  | 18:00 |  | 404
|  |  | For Plants S/D or M/C prob = |  |  | 2802 | MW | Chittagong | 1429.8 | 1429.8 |  | 0 |  | 19:00 |  | 436.435
|  |  | Total = |  |  | 8955 | MW | Khulna | 1920.8 | 1920.8 |  | 0 |  | 19:30 |  | 625.525
7 | Total Gas Supplied : |  |  | 942.73 | MMCFD |  |  | Rajshahi | 1463 | 1463 |  | 0 |  | 20:00 |  | 657.04
8 | Fuel Cost : | i) Gas : | Taka | 393627780.952 | ii) Oil : | Taka | 865456126.5 | Comilla | 1432 | 1432 |  | 0 |  | 21:00 |  | 504
|  | iii) Coal : | Taka | 841674511.32 | Total | Taka | 2100758418.772 | Mymensingh | 1225 | 1045 |  | 180 |  | 22:00 |  | 544.35
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7007.55 | MKWHr. | Sylhet | 617 | 617 |  | 0 |  | 23:00 |  | 693.33
| ii) During Peak Demand : |  |  | 652 | MW (W to E) at | 21:00 | hrs | Barisal | 566.9 | 497.9 |  | 69 |  | 24:00 |  | 806.975
| iii) Maximum : |  |  | 550 | MW at | 5:00 | hrs | Rangpur | 1061 | 991 |  | 70
10 | Maximum Temperature in Dhaka was |  |  |  | 34.5°C |  |  | Total | 15038.21 | 14534.21 |  | 504
B. |  | 2024-07-15 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.5°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 440 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15535 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14500 | MW
4 | Reserve(Generation end) |  |  |  |  | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 348.9802 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12819 | MW at | 8:00 | 80 | 60 | 65 | 65 | 60 | 70 | 0 | 0 | 40
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.2473 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9805 | MKWHr. | iii) Maximum HVDC Flow : |  | 915 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.33 |  | (b) Today: | 95.23 |  | (c) Rule Curve: |  | 86.24

## YesterdayGen
2024-07-14 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 225 | 227 | 32 | 82 | 55 | 325 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 18 | 35 | 0 | 0 | 15 | 15 | 14 | 11 | 0 | 0 | 111 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 48 | 51 | 0 | 28 | 20 | 0 | 30 | 0 | 0 | 0 | 285 | 260 | 214 | 0 | 45 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 82 | 18 | 0 | 0 | 0 | 37 | 58 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 210 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 55 | 0 | 0 | 114 | 0 | 96 | 0 | 48 | 104 | 12 | 403 | 65 | 17 | 17 | 0 | 50 | 0 | 0 | 105 | 59 | 50 | 345 | 17 | 0 | 54 | 90 | 0 | 17 | 0 | 49 | 17 | 230 | 17 | 0 | 1219 | 11 | 420 | 0 | 0 | 0 |  | 915 | 0 | 198 | 0 | 79 | 0 | 0 | 0 | 15 | 41 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 32 | 5 | 0 | 0 | 0 | 35 | 0 | 22 | 0 | 0 | 8 | 60 | 0 | 220 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 1244 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 712 | 0 | 250 | 1127 | 0 | 0 | 0 | 0 |  | 7711 | 6259 | 13970 | 3747 | 915 | 1575 | 0 | 1894 | 5252 | 191 | 0 | 303 | 82 | 0 | 11 | 792.65 | 95.33
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 225 | 310 | 32 | 82 | 55 | 325 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 15 | 15 | 14 | 11 | 0 | 0 | 111 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 48 | 51 | 0 | 25 | 20 | 0 | 30 | 0 | 0 | 0 | 285 | 260 | 215 | 0 | 45 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 80 | 17 | 0 | 0 | 0 | 37 | 57 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 47 | 0 | 0 | 115 | 0 | 96 | 0 | 48 | 104 | 13 | 403 | 67 | 17 | 17 | 0 | 52 | 0 | 0 | 105 | 50 | 50 | 345 | 17 | 0 | 54 | 90 | 0 | 17 | 0 | 48 | 17 | 230 | 17 | 0 | 1220 | 8 | 420 | 0 | 0 | 0 |  | 914 | 0 | 203 | 0 | 79 | 0 | 0 | 0 | 15 | 41 | 0 | 126 | 10 | 16 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 22 | 0 | 0 | 8 | 60 | 0 | 220 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 1244 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 704 | 0 | 250 | 1130 | 0 | 0 | 0 | 0 |  | 7798 | 6249 | 14047 | 3749 | 914 | 1663 | 0 | 1896 | 5248 | 191 | 0 | 298 | 80 | 0 | 8 | 480.365 | 95.33
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 225 | 310 | 32 | 82 | 55 | 325 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 0 | 0 | 111 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 48 | 17 | 0 | 25 | 20 | 0 | 30 | 0 | 0 | 0 | 285 | 260 | 214 | 0 | 46 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 78 | 17 | 0 | 0 | 0 | 37 | 58 | 53 | 36 | 120 | 0 | 56 | 0 | 0 | 209 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 47 | 0 | 0 | 115 | 0 | 96 | 0 | 48 | 104 | 13 | 403 | 67 | 17 | 0 | 0 | 52 | 0 | 0 | 52 | 46 | 50 | 345 | 17 | 0 | 17 | 74 | 0 | 17 | 0 | 33 | 17 | 230 | 17 | 0 | 1220 | 14 | 421 | 0 | 0 | 0 |  | 915 | 0 | 203 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 70 | 0 | 105 | 0 | 0 | 70 | 1244 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 722 | 0 | 250 | 1131 | 0 | 0 | 0 | 0 |  | 7648 | 6001 | 13649 | 3757 | 915 | 1645 | 0 | 1704 | 5208 | 191 | 0 | 137 | 78 | 0 | 14 | 478.455 | 95.33
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 225 | 315 | 32 | 82 | 55 | 326 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 0 | 0 | 111 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 48 | 17 | 0 | 25 | 20 | 0 | 35 | 0 | 0 | 0 | 285 | 260 | 215 | 0 | 45 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 76 | 18 | 0 | 0 | 0 | 37 | 57 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 209 | 0 | 0 | 0 | 270 | 12 | 5 | 0 | 47 | 0 | 0 | 117 | 0 | 96 | 0 | 48 | 105 | 13 | 401 | 68 | 17 | 0 | 0 | 15 | 0 | 0 | 52 | 46 | 50 | 345 | 17 | 0 | 17 | 27 | 0 | 17 | 0 | 33 | 17 | 230 | 17 | 0 | 1184 | 14 | 421 | 0 | 0 | 0 |  | 913 | 0 | 213 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 62 | 0 | 220 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 35 | 0 | 49 | 0 | 0 | 35 | 1120 | 190 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 723 | 0 | 250 | 1126 | 0 | 0 | 0 | 0 |  | 7535 | 5774 | 13309 | 3763 | 913 | 1651 | 0 | 1458 | 5106 | 191 | 0 | 137 | 76 | 0 | 14 | 468.905 | 95.33
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 225 | 315 | 32 | 82 | 55 | 322 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 0 | 0 | 111 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 48 | 17 | 0 | 25 | 20 | 0 | 38 | 0 | 0 | 0 | 285 | 260 | 214 | 0 | 45 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 74 | 18 | 0 | 0 | 0 | 37 | 57 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 209 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 47 | 0 | 0 | 118 | 0 | 96 | 0 | 48 | 104 | 12 | 401 | 68 | 17 | 0 | 0 | 15 | 0 | 0 | 52 | 45 | 50 | 345 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 33 | 17 | 230 | 17 | 0 | 1180 | 15 | 421 | 0 | 0 | 0 |  | 914 | 0 | 212 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 220 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 35 | 1100 | 190 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 718 | 0 | 250 | 1130 | 0 | 0 | 0 | 0 |  | 7543 | 5684 | 13227 | 3755 | 914 | 1676 | 0 | 1402 | 5081 | 191 | 0 | 119 | 74 | 0 | 15 | 451.715 | 95.33
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 289 | 32 | 82 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 15 | 15 | 14 | 11 | 0 | 0 | 111 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 48 | 0 | 0 | 25 | 20 | 0 | 38 | 0 | 0 | 0 | 285 | 350 | 217 | 0 | 45 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 68 | 18 | 0 | 0 | 0 | 37 | 57 | 53 | 39 | 120 | 0 | 56 | 0 | 0 | 210 | 0 | 0 | 0 | 270 | 12 | 5 | 0 | 47 | 0 | 0 | 118 | 0 | 96 | 1 | 48 | 104 | 13 | 327 | 68 | 17 | 0 | 0 | 15 | 0 | 0 | 52 | 46 | 50 | 345 | 17 | 2 | 17 | 17 | 0 | 17 | 1 | 33 | 17 | 230 | 0 | 0 | 1178 | 15 | 421 | 0 | 0 | 5 |  | 915 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1080 | 190 | 0 | 0 | 0 | 2 | 35 | 0 | 0 | 719 | 1 | 250 | 1128 | 10 | 0 | 0 | 0 |  | 7395 | 5452 | 12847 | 3681 | 915 | 1620 | 0 | 1192 | 5058 | 191 | 0 | 85 | 68 | 22 | 15 | 337.115 | 95.33
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 225 | 290 | 28 | 82 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 14 | 11 | 2 | 0 | 111 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 24 | 20 | 0 | 33 | 0 | 0 | 0 | 280 | 265 | 213 | 0 | 50 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 18 | 64 | 18 | 0 | 0 | 0 | 37 | 57 | 52 | 39 | 120 | 0 | 58 | 0 | 0 | 211 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 47 | 0 | 0 | 117 | 0 | 83 | 2 | 12 | 51 | 13 | 328 | 68 | 17 | 0 | 1 | 15 | 0 | 0 | 52 | 47 | 12 | 345 | 17 | 11 | 0 | 17 | 0 | 17 | 6 | 33 | 17 | 230 | 0 | 0 | 1180 | 15 | 422 | 0 | 0 | 17 |  | 914 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1100 | 190 | 0 | 0 | 0 | 21 | 35 | 0 | 0 | 718 | 7 | 250 | 1133 | 15 | 0 | 0 | 8 |  | 7068 | 5528 | 12596 | 3579 | 914 | 1645 | 0 | 962 | 5085 | 191 | 0 | 53 | 64 | 88 | 15 | 242.57 | 95.33
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 225 | 287 | 31 | 65 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 111 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 25 | 20 | 0 | 10 | 0 | 0 | 0 | 285 | 270 | 184 | 0 | 51 | 37 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 17 | 72 | 11 | 0 | 0 | 1 | 37 | 58 | 22 | 39 | 120 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 270 | 12 | 5 | 0 | 47 | 0 | 0 | 117 | 0 | 96 | 4 | 12 | 51 | 13 | 328 | 68 | 17 | 0 | 3 | 15 | 0 | 0 | 52 | 46 | 12 | 310 | 17 | 16 | 0 | 17 | 0 | 17 | 15 | 34 | 17 | 290 | 0 | 0 | 1050 | 25 | 420 | 0 | 0 | 34 |  | 915 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1040 | 190 | 0 | 0 | 2 | 55 | 35 | 0 | 0 | 718 | 16 | 206 | 1128 | 26 | 0 | 0 | 26 |  | 6893 | 5496 | 12389 | 3564 | 915 | 1559 | 0 | 968 | 4844 | 191 | 0 | 53 | 72 | 198 | 25 | 249.255 | 95.33
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 225 | 308 | 32 | 74 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 111 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 28 | 20 | 0 | 6 | 0 | 0 | 0 | 280 | 270 | 189 | 0 | 51 | 33 | 15 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 17 | 76 | 10 | 0 | 0 | 1 | 38 | 57 | 22 | 39 | 120 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 66 | 0 | 0 | 117 | 0 | 96 | 17 | 12 | 51 | 13 | 328 | 68 | 17 | 0 | 4 | 15 | 0 | 0 | 52 | 46 | 12 | 316 | 17 | 38 | 0 | 17 | 0 | 17 | 19 | 49 | 17 | 285 | 0 | 0 | 1095 | 17 | 421 | 0 | 0 | 52 |  | 914 | 0 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1050 | 190 | 0 | 0 | 3 | 59 | 54 | 0 | 0 | 712 | 15 | 180 | 1130 | 13 | 0 | 0 | 30 |  | 7082 | 5492 | 12574 | 3562 | 914 | 1606 | 0 | 1034 | 4870 | 191 | 0 | 53 | 76 | 251 | 17 | 311.33 | 95.33
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 225 | 296 | 32 | 82 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 15 | 15 | 14 | 1 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 35 | 17 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 186 | 8 | 46 | 35 | 16 | 0 | 51 | 0 | 21 | 33 | 0 | 0 | 0 | 17 | 82 | 5 | 0 | 0 | 2 | 38 | 58 | 22 | 36 | 120 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 97 | 0 | 0 | 116 | 0 | 89 | 17 | 12 | 51 | 13 | 328 | 68 | 17 | 0 | 4 | 15 | 0 | 0 | 52 | 46 | 12 | 310 | 17 | 25 | 54 | 17 | 0 | 17 | 29 | 52 | 17 | 285 | 0 | 0 | 1110 | 14 | 421 | 0 | 0 | 65 |  | 914 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 15 | 0 | 34 | 0 | 0 | 35 | 1050 | 220 | 0 | 0 | 5 | 80 | 55 | 0 | 0 | 716 | 23 | 180 | 1133 | 96 | 0 | 0 | 41 |  | 7199 | 5704 | 12903 | 3535 | 914 | 1619 | 0 | 1211 | 4892 | 196 | 0 | 53 | 82 | 387 | 14 | 331.385 | 95.33
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 |  | 0 | 225 | 303 | 32 | 82 | 55 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 1 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 38 | 33 | 0 | 2 | 0 | 0 | 0 | 285 | 275 | 195 | 8 | 46 | 34 | 30 | 0 | 51 | 0 | 20 | 33 | 0 | 0 | 0 | 17 | 84 | 5 | 0 | 0 | 1 | 37 | 57 | 22 | 36 | 120 | 0 | 40 | 0 | 0 | 211 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 97 | 0 | 0 | 116 | 0 | 77 | 11 | 12 | 55 | 12 | 403 | 67 | 17 | 0 | 2 | 15 | 0 | 0 | 52 | 47 | 50 | 350 | 17 | 27 | 54 | 17 | 0 | 17 | 29 | 53 | 17 | 230 | 0 | 0 | 1100 | 14 | 422 | 0 | 0 | 64 |  | 914 | 0 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1040 | 220 | 0 | 0 | 5 | 95 | 54 | 0 | 0 | 710 | 12 | 180 | 1138 | 125 | 0 | 0 | 58 |  | 7409 | 5826 | 13235 | 3648 | 914 | 1651 | 0 | 1350 | 4870 | 196 | 0 | 79 | 84 | 429 | 14 | 348.575 | 95.33
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 225 | 280 | 23 | 82 | 55 | 313 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 10 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 38 | 33 | 0 | 4 | 0 | 0 | 0 | 285 | 270 | 186 | 8 | 40 | 35 | 34 | 0 | 51 | 0 | 14 | 33 | 0 | 0 | 0 | 17 | 86 | 5 | 0 | 0 | 1 | 37 | 57 | 50 | 36 | 163 | 0 | 55 | 0 | 0 | 211 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 97 | 0 | 0 | 116 | 0 | 79 | 18 | 12 | 85 | 12 | 403 | 67 | 17 | 0 | 5 | 15 | 0 | 0 | 52 | 47 | 50 | 377 | 17 | 32 | 137 | 17 | 0 | 17 | 33 | 52 | 17 | 285 | 0 | 0 | 1100 | 8 | 420 | 0 | 0 | 55 |  | 914 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 124 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 7 | 80 | 1070 | 220 | 0 | 0 | 3 | 99 | 54 | 0 | 0 | 710 | 23 | 180 | 1134 | 158 | 0 | 0 | 50 |  | 7720 | 6025 | 13745 | 3781 | 914 | 1784 | 0 | 1508 | 4895 | 196 | 0 | 89 | 86 | 484 | 8 | 291.275 | 95.33
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 225 | 295 | 10 | 82 | 55 | 316 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 10 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 21 | 0 | 0 | 37 | 19 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 186 | 8 | 41 | 35 | 42 | 0 | 51 | 0 | 14 | 33 | 0 | 0 | 0 | 5 | 86 | 5 | 0 | 0 | 2 | 37 | 57 | 50 | 36 | 163 | 0 | 53 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 97 | 0 | 0 | 116 | 0 | 84 | 14 | 12 | 100 | 12 | 404 | 67 | 17 | 0 | 5 | 28 | 0 | 0 | 52 | 47 | 50 | 377 | 17 | 44 | 162 | 17 | 0 | 17 | 33 | 55 | 17 | 285 | 0 | 0 | 1050 | 24 | 422 | 0 | 0 | 54 |  | 913 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 124 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 8 | 90 | 1080 | 220 | 0 | 0 | 5 | 83 | 54 | 0 | 0 | 711 | 14 | 180 | 1134 | 189 | 0 | 0 | 52 |  | 7733 | 6083 | 13816 | 3762 | 913 | 1799 | 0 | 1551 | 4857 | 196 | 0 | 125 | 86 | 503 | 24 | 319 | 95.32
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 297 | 8 | 82 | 55 | 313 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 53 | 0 | 0 | 37 | 19 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 186 | 8 | 42 | 35 | 42 | 0 | 51 | 0 | 20 | 29 | 0 | 0 | 0 | 17 | 92 | 5 | 0 | 0 | 0 | 37 | 58 | 50 | 33 | 163 | 0 | 53 | 0 | 0 | 210 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 102 | 0 | 0 | 116 | 0 | 96 | 17 | 12 | 100 | 12 | 404 | 66 | 17 | 0 | 4 | 23 | 0 | 0 | 52 | 45 | 50 | 340 | 17 | 31 | 162 | 17 | 0 | 17 | 30 | 52 | 17 | 285 | 17 | 0 | 1020 | 18 | 419 | 0 | 0 | 58 |  | 914 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 5 | 59 | 0 | 220 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 7 | 90 | 1110 | 220 | 0 | 0 | 4 | 97 | 54 | 0 | 0 | 712 | 24 | 180 | 1137 | 198 | 0 | 0 | 50 |  | 7725 | 6142 | 13867 | 3726 | 914 | 1808 | 0 | 1543 | 4857 | 196 | 0 | 193 | 92 | 520 | 18 | 318 | 95.33
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 310 | 8 | 82 | 55 | 315 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 213 | 0 | 0 | 0 |  | 3 | 53 | 17 | 0 | 38 | 19 | 0 | 2 | 0 | 0 | 0 | 315 | 305 | 194 | 0 | 40 | 10 | 27 | 0 | 51 | 0 | 20 | 22 | 0 | 0 | 0 | 17 | 92 | 7 | 0 | 0 | 1 | 37 | 57 | 49 | 35 | 163 | 0 | 50 | 0 | 0 | 206 | 0 | 0 | 0 | 315 | 12 | 5 | 0 | 80 | 0 | 0 | 114 | 0 | 78 | 14 | 30 | 100 | 7 | 396 | 66 | 17 | 0 | 2 | 49 | 0 | 0 | 52 | 44 | 50 | 365 | 17 | 39 | 162 | 30 | 0 | 17 | 23 | 53 | 17 | 270 | 17 | 0 | 1055 | 15 | 421 | 0 | 0 | 54 |  | 914 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 122 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 59 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 51 | 0 | 70 | 0 | 6 | 113 | 1200 | 220 | 0 | 0 | 4 | 70 | 54 | 0 | 0 | 709 | 25 | 200 | 1143 | 154 | 0 | 0 | 18 |  | 7811 | 6228 | 14039 | 3758 | 914 | 1817 | 0 | 1625 | 5007 | 196 | 0 | 205 | 92 | 410 | 15 | 421 | 95.32
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 283 | 8 | 82 | 55 | 315 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 53 | 17 | 0 | 38 | 32 | 0 | 2 | 0 | 0 | 0 | 280 | 270 | 211 | 0 | 40 | 10 | 10 | 0 | 51 | 0 | 20 | 22 | 0 | 0 | 0 | 17 | 90 | 8 | 0 | 0 | 1 | 37 | 55 | 52 | 32 | 163 | 0 | 54 | 0 | 0 | 209 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 52 | 0 | 0 | 114 | 0 | 78 | 10 | 49 | 100 | 7 | 389 | 66 | 17 | 0 | 2 | 52 | 0 | 0 | 52 | 44 | 50 | 340 | 17 | 29 | 162 | 53 | 0 | 17 | 16 | 48 | 17 | 270 | 17 | 0 | 1024 | 9 | 420 | 0 | 0 | 30 |  | 914 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 4 | 0 | 50 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 5 | 59 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 90 | 0 | 93 | 0 | 4 | 113 | 1244 | 180 | 0 | 0 | 2 | 24 | 54 | 0 | 0 | 711 | 16 | 200 | 1138 | 98 | 0 | 0 | 28 |  | 7632 | 6162 | 13794 | 3634 | 914 | 1727 | 0 | 1739 | 5016 | 196 | 0 | 209 | 90 | 260 | 9 | 626 | 95.32
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 285 | 8 | 82 | 55 | 312 | 0 | 0 | 8 | 8 | 32 | 12 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 53 | 34 | 0 | 38 | 40 | 0 | 4 | 0 | 0 | 0 | 280 | 270 | 182 | 0 | 40 | 10 | 10 | 0 | 51 | 0 | 28 | 29 | 0 | 0 | 0 | 17 | 86 | 8 | 0 | 0 | 0 | 37 | 56 | 52 | 32 | 163 | 0 | 54 | 0 | 0 | 209 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 62 | 0 | 0 | 114 | 0 | 87 | 3 | 49 | 100 | 8 | 363 | 66 | 17 | 0 | 1 | 49 | 0 | 0 | 88 | 73 | 50 | 340 | 17 | 14 | 162 | 30 | 0 | 18 | 9 | 49 | 17 | 240 | 17 | 0 | 950 | 19 | 420 | 0 | 0 | 6 |  | 914 | 0 | 185 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 8 | 16 | 0 | 0 | 0 | 40 | 0 | 49 | 0 | 0 | 14 | 0 | 16 | 0 | 0 | 2 | 60 | 0 | 220 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 2 | 0 | 105 | 0 | 93 | 0 | 2 | 113 | 1180 | 180 | 0 | 0 | 1 | 34 | 54 | 0 | 0 | 710 | 3 | 200 | 1145 | 58 | 0 | 0 | 14 |  | 7529 | 6054 | 13583 | 3541 | 914 | 1655 | 0 | 1859 | 4885 | 196 | 0 | 283 | 86 | 145 | 19 | 417 | 95.32
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 225 | 267 | 8 | 82 | 55 | 311 | 0 | 0 | 8 | 8 | 32 | 13 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 4 | 218 | 0 | 0 | 0 |  | 6 | 62 | 34 | 0 | 38 | 40 | 0 | 20 | 0 | 0 | 0 | 280 | 270 | 186 | 0 | 39 | 10 | 10 | 0 | 20 | 0 | 28 | 30 | 0 | 0 | 0 | 17 | 80 | 12 | 0 | 0 | 0 | 37 | 56 | 22 | 10 | 120 | 0 | 40 | 0 | 0 | 209 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 115 | 0 | 0 | 114 | 0 | 106 | 0 | 62 | 107 | 10 | 312 | 66 | 17 | 0 | 0 | 49 | 0 | 0 | 70 | 89 | 50 | 316 | 17 | 3 | 162 | 18 | 0 | 34 | 3 | 63 | 17 | 240 | 17 | 0 | 850 | 42 | 420 | 0 | 0 | 5 |  | 914 | 0 | 185 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 40 | 0 | 49 | 0 | 0 | 34 | 0 | 20 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 70 | 0 | 100 | 0 | 1 | 70 | 1000 | 180 | 0 | 14 | 0 | 10 | 90 | 0 | 0 | 773 | 1 | 150 | 1142 | 11 | 0 | 0 | 4 |  | 7293 | 5744 | 13037 | 3383 | 914 | 1464 | 0 | 1987 | 4617 | 196 | 0 | 316 | 80 | 38 | 42 | 404 | 95.32
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 |  | 0 | 225 | 306 | 9 | 82 | 55 | 312 | 0 | 0 | 9 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 69 | 51 | 12 | 38 | 50 | 0 | 14 | 0 | 0 | 0 | 295 | 285 | 208 | 8 | 41 | 10 | 10 | 0 | 30 | 0 | 28 | 31 | 0 | 0 | 0 | 17 | 92 | 12 | 0 | 0 | 0 | 37 | 58 | 52 | 35 | 120 | 0 | 55 | 0 | 0 | 209 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 137 | 0 | 0 | 143 | 0 | 98 | 0 | 62 | 122 | 10 | 346 | 86 | 17 | 8 | 0 | 49 | 8 | 9 | 88 | 89 | 50 | 365 | 17 | 0 | 162 | 26 | 0 | 36 | 0 | 70 | 17 | 240 | 17 | 0 | 964 | 27 | 423 | 0 | 0 | 0 |  | 914 | 0 | 188 | 0 | 44 | 0 | 0 | 0 | 27 | 25 | 16 | 124 | 10 | 16 | 0 | 0 | 0 | 40 | 4 | 74 | 0 | 0 | 45 | 0 | 20 | 0 | 0 | 2 | 62 | 0 | 220 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 17 | 0 | 73 | 0 | 101 | 0 | 0 | 90 | 950 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 772 | 0 | 203 | 1142 | 0 | 0 | 0 | 0 |  | 8021 | 6022 | 14043 | 3627 | 914 | 1635 | 0 | 2284 | 4736 | 196 | 0 | 532 | 92 | 0 | 27 | 436.435 | 95.31
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 225 | 270 | 8 | 82 | 55 | 315 | 0 | 0 | 9 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 76 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 69 | 51 | 46 | 38 | 50 | 0 | 14 | 0 | 0 | 0 | 280 | 270 | 213 | 8 | 39 | 10 | 20 | 0 | 43 | 0 | 28 | 31 | 0 | 0 | 0 | 17 | 94 | 12 | 0 | 0 | 0 | 37 | 57 | 53 | 35 | 163 | 0 | 55 | 0 | 0 | 209 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 145 | 0 | 0 | 143 | 0 | 97 | 0 | 62 | 120 | 10 | 372 | 86 | 17 | 17 | 0 | 49 | 17 | 34 | 88 | 90 | 62 | 345 | 17 | 0 | 162 | 60 | 0 | 36 | 0 | 115 | 17 | 310 | 114 | 0 | 1060 | 33 | 417 | 0 | 0 | 0 |  | 914 | 0 | 186 | 0 | 59 | 0 | 0 | 0 | 28 | 40 | 16 | 124 | 10 | 16 | 0 | 0 | 0 | 40 | 0 | 86 | 0 | 0 | 45 | 0 | 20 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 17 | 0 | 113 | 0 | 101 | 0 | 0 | 113 | 1160 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 773 | 0 | 262 | 1136 | 0 | 0 | 0 | 0 |  | 8461 | 6484 | 14945 | 3719 | 914 | 1752 | 0 | 2535 | 5089 | 156 | 0 | 653 | 94 | 0 | 33 | 625.525 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 282 | 8 | 82 | 55 | 317 | 0 | 0 | 9 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 69 | 51 | 46 | 38 | 50 | 0 | 17 | 0 | 0 | 0 | 280 | 270 | 212 | 8 | 39 | 20 | 20 | 0 | 43 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 90 | 12 | 0 | 0 | 0 | 37 | 57 | 53 | 35 | 163 | 0 | 55 | 0 | 0 | 209 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 145 | 0 | 0 | 143 | 0 | 102 | 0 | 62 | 120 | 10 | 372 | 87 | 17 | 34 | 0 | 49 | 17 | 27 | 88 | 90 | 62 | 345 | 17 | 0 | 162 | 67 | 0 | 36 | 0 | 100 | 17 | 285 | 145 | 0 | 1062 | 17 | 419 | 0 | 0 | 0 |  | 914 | 0 | 190 | 0 | 77 | 0 | 0 | 0 | 34 | 47 | 16 | 80 | 10 | 16 | 0 | 0 | 0 | 40 | 4 | 86 | 0 | 0 | 47 | 0 | 20 | 0 | 0 | 5 | 62 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 113 | 0 | 101 | 0 | 0 | 113 | 1190 | 180 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 732 | 0 | 270 | 1143 | 0 | 0 | 0 | 0 |  | 8514 | 6398 | 14912 | 3666 | 914 | 1666 | 0 | 2562 | 5098 | 196 | 0 | 703 | 90 | 0 | 17 | 657.04 | 95.31
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 225 | 281 | 8 | 68 | 55 | 318 | 0 | 0 | 9 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 2 | 69 | 51 | 46 | 38 | 50 | 0 | 22 | 0 | 0 | 0 | 310 | 280 | 213 | 8 | 38 | 36 | 20 | 0 | 43 | 0 | 28 | 33 | 0 | 0 | 0 | 17 | 90 | 17 | 0 | 0 | 0 | 37 | 57 | 53 | 35 | 163 | 0 | 55 | 0 | 0 | 209 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 155 | 0 | 0 | 143 | 0 | 96 | 0 | 62 | 120 | 12 | 366 | 87 | 17 | 34 | 0 | 51 | 17 | 34 | 88 | 91 | 62 | 345 | 17 | 0 | 108 | 0 | 0 | 36 | 0 | 115 | 17 | 320 | 145 | 0 | 1150 | 26 | 420 | 0 | 0 | 0 |  | 913 | 0 | 195 | 0 | 78 | 0 | 0 | 0 | 31 | 31 | 16 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 4 | 86 | 0 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 101 | 0 | 0 | 113 | 1230 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 712 | 0 | 307 | 1131 | 0 | 0 | 0 | 0 |  | 8584 | 6588 | 15172 | 3807 | 913 | 1779 | 0 | 2436 | 5231 | 196 | 0 | 694 | 90 | 0 | 26 | 504 | 95.31
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 302 | 8 | 68 | 55 | 317 | 0 | 0 | 9 | 8 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 105 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 0 | 69 | 51 | 46 | 36 | 50 | 0 | 27 | 0 | 0 | 0 | 320 | 330 | 208 | 8 | 38 | 36 | 20 | 0 | 43 | 0 | 28 | 34 | 0 | 0 | 0 | 17 | 92 | 17 | 0 | 0 | 0 | 37 | 57 | 47 | 36 | 120 | 0 | 50 | 0 | 0 | 209 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 140 | 0 | 0 | 143 | 0 | 96 | 0 | 62 | 120 | 10 | 368 | 87 | 17 | 34 | 0 | 51 | 17 | 34 | 88 | 90 | 62 | 373 | 17 | 0 | 72 | 0 | 0 | 36 | 0 | 111 | 17 | 300 | 90 | 0 | 1170 | 23 | 419 | 0 | 0 | 0 |  | 914 | 0 | 195 | 0 | 82 | 0 | 0 | 0 | 31 | 31 | 16 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 5 | 86 | 0 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 103 | 0 | 0 | 113 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 712 | 0 | 307 | 1146 | 0 | 0 | 0 | 0 |  | 8467 | 6613 | 15080 | 3830 | 914 | 1767 | 0 | 2350 | 5279 | 185 | 0 | 640 | 92 | 0 | 23 | 544.35 | 95.31
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 0 |  | 0 | 225 | 310 | 8 | 73 | 55 | 321 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 14 | 14 | 8 | 0 | 105 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 69 | 51 | 12 | 37 | 50 | 0 | 30 | 0 | 0 | 0 | 300 | 270 | 211 | 8 | 38 | 36 | 20 | 0 | 43 | 0 | 28 | 34 | 0 | 0 | 0 | 0 | 92 | 17 | 0 | 0 | 0 | 37 | 57 | 50 | 39 | 163 | 0 | 50 | 0 | 0 | 207 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 135 | 0 | 0 | 144 | 0 | 96 | 0 | 62 | 120 | 12 | 340 | 86 | 17 | 17 | 0 | 50 | 0 | 34 | 88 | 90 | 62 | 345 | 17 | 0 | 54 | 10 | 0 | 36 | 0 | 100 | 17 | 230 | 17 | 0 | 1168 | 57 | 422 | 0 | 0 | 0 |  | 914 | 0 | 195 | 0 | 85 | 0 | 0 | 0 | 21 | 31 | 16 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 15 | 87 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 103 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 712 | 0 | 307 | 1142 | 0 | 0 | 0 | 0 |  | 8173 | 6601 | 14774 | 3631 | 914 | 1832 | 0 | 2232 | 5265 | 185 | 0 | 566 | 92 | 0 | 57 | 693.33 | 95.3
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 225 | 302 | 9 | 68 | 55 | 324 | 0 | 0 | 0 | 8 | 100 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 0 | 15 | 15 | 14 | 14 | 8 | 0 | 105 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 1 | 69 | 51 | 0 | 38 | 50 | 0 | 30 | 0 | 0 | 0 | 280 | 270 | 211 | 8 | 34 | 36 | 20 | 0 | 43 | 0 | 30 | 33 | 0 | 0 | 0 | 17 | 90 | 17 | 0 | 0 | 0 | 37 | 57 | 50 | 39 | 163 | 0 | 56 | 0 | 0 | 209 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 82 | 0 | 0 | 143 | 0 | 96 | 0 | 49 | 108 | 10 | 342 | 86 | 17 | 0 | 0 | 52 | 0 | 0 | 88 | 90 | 50 | 345 | 0 | 0 | 54 | 87 | 0 | 36 | 0 | 59 | 17 | 230 | 17 | 0 | 1175 | 35 | 418 | 0 | 0 | 0 |  | 914 | 0 | 194 | 0 | 95 | 0 | 0 | 0 | 11 | 31 | 8 | 126 | 10 | 16 | 0 | 0 | 0 | 39 | 15 | 86 | 0 | 0 | 45 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 210 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 103 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 711 | 0 | 307 | 1139 | 0 | 0 | 0 | 0 |  | 7976 | 6579 | 14555 | 3653 | 914 | 1829 | 0 | 2061 | 5264 | 185 | 0 | 524 | 90 | 0 | 35 | 806.975 | 95.29
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9525600 | 0 |  | 0 | 5123000 | 6973935 | 461760 | 1739848 | 1329705 | 7442176 | 0 | 0 | 54720 | 195120 | 1100640 | 63000 | 0 | 0 | 0 | 647280 | 661675 | 669916 | 0 | 325800 | 356400 | 337680 | 267800 | 172800 | 0 | 2735444 | 1928000 | 0 | 0 | 33516 | 5005591 | 0 | 0 | 0 |  | 124320 | 1068144 | 557812 | 173640 | 794880 | 722400 | 0 | 475200 | 0 | 0 | 0 | 7360200 | 6748000 | 4933000 | 83636 | 985180 | 723960 | 472320 | 0 | 1085228 | 0 | 543632 | 764242 | 0 | 0 | 0 | 393840 | 1980480 | 274560 | 0 | 0 | 11650 | 874000 | 1374000 | 1084800 | 851976 | 3366573 | 0 | 1218144 | 0 | 0 | 5215380 | 0 | 0 | 0 | 7102000 | 287952 | 102816 | 0 | 2070000 | 0 | 0 | 2925600 | 0 | 2225952 | 117720 | 919680 | 2333280 | 272654 | 9027000 | 1704000 | 426240 | 193199 | 32762 | 870655 | 79860 | 143850 | 1639320 | 1461600 | 1106880 | 8252100 | 394560 | 311000 | 1955520 | 819218 | 0 | 559800 | 244689 | 1392960 | 432000 | 6395400 | 615563 | 0 | 26247270 | 471360 | 10152727 | 0 | 0 | 504745 |  | 20247272 | 0 | 5021568 | 0 | 915840 | 0 | 0 | 0 | 169920 | 256256 | 121875 | 2588000 | 158046 | 256320 | 0 | 0 | 0 | 391069 | 37188 | 841080 | 0 | 0 | 308800 | 0 | 313582 | 0 | 0 | 127616 | 1425163 | 0 | 5291000 | 0 | 0 | 4150455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8734981 | 108480 | 0 | 1538976 | 0 | 1673308 | 0 | 36280 | 1787136 | 29431400 | 5077459 | 0 | 232800 | 37140 | 725040 | 1875456 | 0 | 0 | 17410909 | 195028 | 5476400 | 27207273 | 1147250 | 0 | 4330 | 395250 |  | 185204535 | 145715946 | 330920481 | 89314218 | 20247272 | 40589154 | 0 | 41045841 | 122642142 | 4663444 | 0 | 6203686 | 1980480 | 3762884 | 471360 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27433728 | 0 |  | 0 | 16291140 | 23850857.7 | 9124377.6 | 32535157.6 | 23429402.1 | 22698636.8 | 0 | 0 | 1081267.2 | 3502404 | 21374428.8 | 1174950 | 0 | 0 | 0 | 11819332.8 | 10427998 | 12252763.64 | 0 | 244350 | 0 | 0 | 0 | 3094848 | 0 | 0 | 0 | 0 | 0 | 634793.04 | 15967835.29 | 0 | 0 | 0 |  | 2186788.8 | 18810015.84 | 9990412.92 | 3309578.4 | 15555801.6 | 11890704 | 0 | 0 | 0 | 0 | 0 | 20534958 | 20648880 | 16377560 | 280180.6 | 3182131.4 | 2439745.2 | 2068761.6 | 0 | 4351764.28 | 0 | 9736449.12 | 13802210.52 | 0 | 0 | 0 | 295380 | 12991948.8 | 853881.6 | 0 | 0 | 0 | 3408600 | 5125020 | 4935840 | 3876490.8 | 11513679.66 | 0 | 6760699.2 | 0 | 0 | 14550910.2 | 0 | 0 | 0 | 21945180 | 215964 | 78140.16 | 0 | 42228000 | 0 | 0 | 56200776 | 0 | 39199014.72 | 0 | 16379500.8 | 40482408 | 4520603.32 | 23921550 | 32478240 | 7996262.4 | 3465990.06 | 0 | 14235209.25 | 1552478.4 | 2580669 | 31327405.2 | 28369656 | 19713532.8 | 21950586 | 6735139.2 | 0 | 35766460.8 | 13746478.04 | 0 | 10003626 | 0 | 25101139.2 | 7318080 | 18994338 | 8667127.04 | 0 | 182943471.9 | 0 | 59901089.3 | 0 | 0 | 0 |  | 56894834.32 | 0 | 14813625.6 | 0 | 15889824 | 0 | 0 | 0 | 3196195.2 | 4820175.36 | 2169375 | 8178080 | 749138.04 | 4418956.8 | 0 | 0 | 0 | 7004045.79 | 682399.8 | 14138554.8 | 0 | 0 | 5530608 | 0 | 5616253.62 | 0 | 0 | 96605.312 | 15719547.89 | 0 | 44656040 | 0 | 0 | 13696501.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25506144.52 | 1852838.4 | 0 | 30502504.32 | 0 | 33332295.36 | 0 | 0 | 35456778.24 | 190715472 | 15790897.49 | 0 | 4504680 | 0 | 0 | 32539161.6 | 0 | 0 | 127099635.7 | 0 | 40799180 | 179840074.53 | 0 | 0 | 0 | 0 |  | 1234434778.7 | 936210423.192 | 2170645201.892 | 262467706.262 | 56894834.32 | 131160074.69 | 0 | 755889460.21 | 841674511.32 | 0 | 0 | 109566666.29 | 12991948.8 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 225 | 280 | 23 | 82 | 55 | 313 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 15 | 15 | 14 | 10 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 16 | 0 | 0 | 38 | 33 | 0 | 4 | 0 | 0 | 0 | 285 | 270 | 186 | 8 | 40 | 35 | 34 | 0 | 51 | 0 | 14 | 33 | 0 | 0 | 0 | 17 | 86 | 5 | 0 | 0 | 1 | 37 | 57 | 50 | 36 | 163 | 0 | 55 | 0 | 0 | 211 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 97 | 0 | 0 | 116 | 0 | 79 | 18 | 12 | 85 | 12 | 403 | 67 | 17 | 0 | 5 | 15 | 0 | 0 | 52 | 47 | 50 | 377 | 17 | 32 | 137 | 17 | 0 | 17 | 33 | 52 | 17 | 285 | 0 | 0 | 1100 | 8 | 420 | 0 | 0 | 55 |  | 914 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 124 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 220 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 34 | 0 | 7 | 80 | 1070 | 220 | 0 | 0 | 3 | 99 | 54 | 0 | 0 | 710 | 23 | 180 | 1134 | 158 | 0 | 0 | 50 |  | 13745 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 225 | 281 | 8 | 68 | 55 | 318 | 0 | 0 | 9 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 15 | 15 | 14 | 11 | 8 | 0 | 116 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 | 0 | 2 | 69 | 51 | 46 | 38 | 50 | 0 | 22 | 0 | 0 | 0 | 310 | 280 | 213 | 8 | 38 | 36 | 20 | 0 | 43 | 0 | 28 | 33 | 0 | 0 | 0 | 17 | 90 | 17 | 0 | 0 | 0 | 37 | 57 | 53 | 35 | 163 | 0 | 55 | 0 | 0 | 209 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 155 | 0 | 0 | 143 | 0 | 96 | 0 | 62 | 120 | 12 | 366 | 87 | 17 | 34 | 0 | 51 | 17 | 34 | 88 | 91 | 62 | 345 | 17 | 0 | 108 | 0 | 0 | 36 | 0 | 115 | 17 | 320 | 145 | 0 | 1150 | 26 | 420 | 0 | 0 | 0 |  | 913 | 0 | 195 | 0 | 78 | 0 | 0 | 0 | 31 | 31 | 16 | 126 | 10 | 16 | 0 | 0 | 0 | 40 | 4 | 86 | 0 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 220 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 113 | 0 | 101 | 0 | 0 | 113 | 1230 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 712 | 0 | 307 | 1131 | 0 | 0 | 0 | 0 |  | 15172 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 225 | 280 | 8 | 82 | 55 | 0 | 0 | 100 | 8 | 8 | 132 | 13 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 15 | 15 | 14 | 12 | 8 | 0 | 116 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 70 | 51 | 46 | 38 | 50 | 0 | 20 | 0 | 0 | 0 | 310 | 280 | 210 | 8 | 50 | 36 | 20 | 0 | 51 | 0 | 28 | 33 | 0 | 0 |  | 17 | 100 | 20 | 0 | 0 | 0 | 37 | 57 | 51 | 35 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 150 | 0 | 0 | 143 | 0 | 100 | 0 | 62 | 120 | 90 | 360 | 87 | 17 | 105 | 0 | 52 | 17 | 80 | 88 | 90 | 62 | 345 | 17 | 0 | 162 | 90 | 0 | 36 | 0 | 115 | 17 | 320 | 145 | 0 | 1200 | 62 | 420 | 0 | 0 |  |  | 937 | 0 | 200 | 0 | 98 | 0 | 0 | 0 | 35 | 50 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 40 | 10 | 85 | 0 | 0 | 47 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 113 | 0 | 101 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 720 | 0 | 307 | 1140 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 225 | 280 | 8 | 65 | 55 | 0 | 0 | 75 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 15 | 15 | 14 | 12 | 8 | 0 | 105 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 70 | 51 | 46 | 32 | 50 | 0 | 5 | 0 | 0 | 0 | 280 | 250 | 200 | 8 | 50 | 33 | 20 | 0 | 51 | 0 | 28 | 33 | 0 | 0 |  | 17 | 90 | 20 | 0 | 0 | 1.6 | 36 | 54 | 50 | 35 | 163 | 0 | 60 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 12 | 3 | 0 | 45 | 0 | 0 | 116 | 0 | 95 | 20 | 34 | 100 | 80 | 340 | 60 | 17 | 34 | 5 | 52 | 17 | 34 | 52 | 46 | 50 | 320 | 17 | 50 | 162 | 90 | 0 | 17 | 35 | 49 | 17 | 280 | 35 | 0 | 1100 | 44 | 420 | 0 | 0 | 70 |  | 937 | 0 | 200 | 0 | 77 | 0 | 0 | 0 | 30 | 50 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 113 | 0 | 100 | 0 | 8 | 113 | 1200 | 220 |  | 35 | 6 | 100 | 90 | 0 | 0 | 720 | 30 | 230 | 1100 | 130 | 0 |  | 5 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 225 | 304 | 8 | 82 | 55 | 0 | 0 | 75 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 15 | 15 | 14 | 14 | 8 | 0 | 105 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 21 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 240 | 212 | 8 | 50 | 36 | 42 | 0 | 51 | 0 | 28 | 33 | 0 | 0 | 0 | 17 | 80 | 9 | 0 | 0 | 1 | 36 | 57 | 50 | 39 | 120 | 0 | 58 | 0 | 0 | 210 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 47 | 0 | 0 | 116 | 0 | 95 | 12 | 49 | 100 | 88 | 343 | 67 | 17 | 0 | 3 | 15 | 0 | 0 | 52 | 46 | 50 | 315 | 0 | 3 | 17 | 17 | 0 | 17 | 16 | 32 | 17 | 250 | 0 | 0 | 1025 | 51 | 421 | 0 | 0 | 35 | 0 | 912 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 8 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 113 | 0 | 103 | 0 | 4 | 113 | 1040 | 180 | 0 | 0 | 1 | 14 | 35 | 0 | 0 | 724 | 13 | 234 | 1134 | 101 | 0 | 0 | 13 | 0 |  |  |  | 129903372 | 20247272 | 0 | 122642142 | 47249527 | 1980480 | 3762884 | 471360 | 4663444 |  |  | 330920481
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 129.9034 | 20.2473 | 0 | 122.6421 | 47.2495 | 1.9805 | 3.7629 | 0.47136 | 4.6634
| Minimum Generation |  | 12389 | 8:00
| Highest Generation |  | 15172 | 21:00 | [129 empty] | 0 | [73 empty] | 330.9205
| Day Peak Generation |  | 13745 | 12:00
| Evening Peak Generation |  | 15172 | 21:00 | [203 empty] | 202699852
| HVDC Max Flow |  | 915 | 1:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 913 | 21:00
| Load factor L.F |  | 90.88% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-15
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13745 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 12819
Evening Peak Generation : |  |  | 15172 | MW Hour : | 21:00 | Available Max Generation : |  | 15535
E.P. Demand (at gen end) : |  |  | 15700 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16000
Maximum Generation : |  |  | 15172 | MW Hour : | 21:00 | Reserve(Generation end)
Total Gen. (MKWH) : |  |  | 330.9205 | System Load Factor : | 90.88% | Load Shed : |  | 440
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 550 | MW at | 5:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-15
Actual : |  | 95.23 | Ft.(MSL) , | Rule curve : | 86.24 | Ft.( MSL )
Gas Consumed : |  | Total = | 942.73 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 393627780.952
: |  |  | Coal : | 841674511.32 | Oil : | 865456126.5 | Total : | 2100758418.772
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 185 | 4440:00 | 4534.2896 |  |  | 80 | -19.95%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 60 | -18.16%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 65 | -17.78%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 65 | -17.38%
Cumilla Area |  | 0 | 0:00 | 1247.9061 |  |  | 60 | -17.63%
Mymensingh Area |  | 180 | 4320:00 | 928.0993 |  |  | 70 | -17.28%
Sylhet Area |  | 0 | 0:00 | 520.2585 |  |  | 0 | -17.95%
Barisal Area |  | 69 | 1656:00 | 433.5457 |  |  | 0 | -17.21%
Rangpur Area |  | 70 | 1680:00 | 847.94 |  |  | 40 | -17.22%
Total |  | 504 |  | 13019.2171 |  |  | 440
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Remark
Time | Time
| 08:46 | Sirajganj 132/33kV S/S T1-(415) HT is restored.
| 08:46 | Sirajganj 132/33kV S/S T1-(415) LT is restored.
| 08:46 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
| 08:48 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
09:05 | 09:57 | Bhaluka 132/33kV S/S Auxiliary- 01 LT Scheduled S/D Due to Maintenance work |  |  |  |  | 30.0MW load interruption.
09:05 | 10:21 | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Maintenance work
09:06 | 10:20 | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Maintenance work
09:12 | 12:46 | Bagerhat-Goalpara 132 kV Ckt-1 Scheduled S/D from Goalpara 132/33kV end Due to To change damage meter
09:13 | 13:34 | Siddhirganj 132/33kV S/S T-2 LT Tripped showing 1) Gen Trip 2) R,Y,B phase pickup relays Due to Physical stroke |  |  |  |  | 58.0MW load interruption.
on Demra Line underground cable by Excavator under G2G project work..
09:13 | 09:53 | Siddhirganj 132/33kV S/S T-1 LT Tripped showing 1) Gen. Trip 2) R,Y,B phase pickup 3) 51/51N/50/50N relays Due to
Physical stroke on Demra Line underground cable by Excavator under G2G project work.
| 09:41 | Noapara 132/33kV S/S T-1 LT is restored.
| 09:41 | Noapara 132/33kV S/S T-1 HT is restored.
09:45 | 13:32 | Siddhirganj 132/33kV S/S T-2 HT Forced S/D Due to 33 kv DS R phase terminal damage due to Physical stroke on 33 kv
Demra Line underground cable by Excavator under G2G project work..
10:12 | 19:49 | BIPTC S/S Baharampur-4 Scheduled S/D
10:44 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:- CCPP put into FGMO as per NLDC request at 5:58 hrs
11:44 | 12:58 | Tongi 230/132/33kV S/S Tongi-Tongi 80 MW PS Forced S/D Due to 132 kV Circuit breaker maintenance work at 80 MW power
station site
12:00 |  | Day Peak Generation: 13745 MW.
| 12:08 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt is restored.
13:05 | 14:23 | Bogura 230/132kV S/S T-04 HT Scheduled S/D Due to Bus upgradetion
13:05 | 14:23 | Bogura 230/132kV S/S T-04 LT Scheduled S/D Due to Bus upgradetion
14:25 | 16:40 | Bogura 230/132kV S/S T-02 HT Scheduled S/D Due to 230kV Bus Upgradation work.
14:25 | 16:40 | Bogura 230/132kV S/S T-02 LT Scheduled S/D Due to 230kV Bus Upgradation work.
14:26 | 16:15 | Maniknagar 132/33kV S/S Kazla Ckt -2 Scheduled S/D Due to P T-(R phase) Harming Mentenance work.
16:32 | 18:15 | Madunaghat 132/33kV S/S TR-2(517T) LT Forced S/D Due to BPDB Maintenance work
16:33 | 18:14 | Madunaghat 132/33kV S/S TR-2(517T) HT Forced S/D Due to BPDB Maintenance Work
17:27 |  | Ashuganj 420 MW CCPP(East), FGMO is OFF with remarks:- 14:13 FGMO off due to low gas pressure.
19:20 | 19:47 | Fenchuganj-Kulaura 132 kV Ckt-1 Tripped from Kulaura 132/33kV end showing Distance Relay relays. |  |  |  |  | 28.0MW load interruption.
19:20 | 19:47 | Fenchuganj-Kulaura 132 kV Ckt-2 Tripped from Kulaura 132/33kV end showing Distance realy relays.
19:25 | 20:15 | Bogura 132/33kV S/S Transformer-1 LT Tripped showing Micom relays Due to T-1 33kv incoming CB Trip due to Puran
bogura-2 33kv feeder CB Blust.
19:25 | 20:15 | Bogura 132/33kV S/S Transformer-2 LT Tripped showing No Relay Signal relays Due to T-2 33kv incoming CB Trip due to |  |  |  |  | 42.0MW load interruption.
Puran bogura-2 33kv feeder CB Blust.
19:32 | 22:10 | Chowmuhani 132/33kV S/S TR3 Forced S/D Due to 123kv HT side bushing red-hot. |  |  |  |  | 30.0MW load interruption.
21:00 |  | Evening peak Generation: 15172 MW
21:24 |  | Ashuganj 420 MW CCPP(East), FGMO is ON with remarks:- At 19:27
21:57 | 23:45 | Bogura 132/33kV S/S Transformer-1 LT Forced S/D Due to Red hot (132 KV CB upper loop-B phase)
22:57 | 23:45 | Bogura 132/33kV S/S Transformer-1 HT Forced S/D Due to Red hot (132 KV CB upper loop-B phase)
23:58 | 00:25 | Bogura 132/33kV S/S Transformer-3 HT Forced S/D Due to Red hot 132KV CT (R-Phase) |  |  |  |  | 35.0MW load interruption.
23:58 | 00:25 | Bogura 132/33kV S/S Transformer-3 LT Forced S/D Due to Red hot 132KV CT (R-Phase)
05:28 |  | Bashundhara-Rampura 132 kV Ckt-1 Forced S/D from Rampura 230/132kV end Due to Line Ds 141s Maintenance
06:09 |  | Baghabari-Sirajganj 230 kV Ckt-1 Project Work S/D from Baghabari 230/132kV end Due to IDRNPP project work
06:10 |  | Baghabari-Sirajganj 230 kV Ckt-2 Project Work S/D from Baghabari 230/132kV end Due to IDRNPP project work
06:17 |  | Siddhirganj 335 MW CCPP Shutdown with remarks:- ST
06:19 |  | Halishahar 132/33kV S/S 413T(TR-2) HT Scheduled S/D Due to Due to maintenance work
06:20 |  | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Maintenance due to high temperature at various point
of switchyard equipment
06:20 |  | Sreepur 230/132/33kV S/S 230/132 kV T-1 HT Scheduled S/D Due to Maintenance due to high temperature at various point
of switchyard equipment
06:20 |  | Sreepur 230/132/33kV S/S Auxiliary Transformer - 1 HT Scheduled S/D
06:20 |  | Sreepur 230/132/33kV S/S Auxiliary Transformer - 1 LT Scheduled S/D
06:28 |  | Siddhirganj 335 MW CCPP Shutdown with remarks:- GT
06:30 |  | Sreepur 230/132/33kV S/S Sreepur-Valuka Ckt-1 Scheduled S/D Due to Maintenance due to high temperature at
various point of switchyard equipment
06:33 |  | Bhaluka 132/33kV S/S Sreepur Ckt- 01 Scheduled S/D Due to High Temperature maintenance.
06:42 |  | Sonargaon 132/33kV S/S OPSL(IEL-2) Scheduled S/D Due to Corrective maintenance work at Bus-B isolator B-phase Finger point.
06:48 |  | Chowmuhani-Feni 132 kV Ckt-2 Forced S/D from Chowmuhani 132/33kV end Due to Ordered By NLDC and from
Feni 132/33kV end Due to Maintenance work
| 06:51 | Sreepur 230/132/33kV S/S 132 kV BUS-2 is restored.
06:56 |  | Siddhirgonj 2*120 MW GTPP Synchronized with remarks:- GT-2
06:59 |  | Sreepur 230/132/33kV S/S 132 kV BUS-1 Scheduled S/D Due to Maintenance due to high temperature at various point
07:00 |  | Minimum Generation :12827 MW
07:04 |  | Halishahar 132/33kV S/S 423T(TR-3) LT Scheduled S/D Due to Due to red hot at 33 kv side shutdown taken by PDB. |  |  |  |  | 5.0MW load interruption.
07:10 |  | Sonargaon 132/33kV S/S BUS B Scheduled S/D Due to OPSL B-Bus DS corrective maintenance work.
07:20 |  | Bhaluka 132/33kV S/S Bus A Forced S/D Due to High temperature maintenance.
07:31 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Forced S/D
07:32 |  | Kabirpur - Manikganj 132kV Ckt-2 Forced S/D from Manikganj 132/33kV end.
07:32 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Forced S/D
07:58 |  | Siddhirgonj 2*120 MW GTPP Synchronized with remarks:- GT-1

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-14
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 403 | 9525600 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5123000 | GT-1 S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 461760 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 6973935 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 68 | 1739848 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1329705
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 63000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 54720 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 318 | 7442176 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 195120 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 647280
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1100640 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 661675 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 669916 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 682200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 14 | 337680 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 267800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 172800 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 155 | 2070000 | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 96 | 2225952 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 426240 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 394560 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1955520
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 244689
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432000 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5634 | 2117 | 45197816
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 33516 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 117720
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 722400
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 196 | 4663444 | Low water level
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5005591
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 193199 | Meghna bus section limitation.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 69 | 1068144 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 557812 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 46 | 173640 | Meghna bus section limitation.
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 62 | 919680 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 475200
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 38 | 794880 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 32762
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 51 | 870655 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 79860 | Meghna bus section limitation.
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 143850 | Meghna bus section limitation.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 62 | 1106880 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 819218 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 145 | 615563 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 1150 | 26247270
| Cox's Bazar Wind |  | IPP | 66 | 60 | 26 | 471360
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 420 | 10152727
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 504745
| Chattogram area Total |  |  |  | 4457 | 2701 | 55770116
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4933000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7360200 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6748000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 320 | 6395400 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 723960 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 20 | 472320 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 83636 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1085228
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 12 | 272654 | Fuel shortage
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 543632 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 38 | 985180 | Under maint.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2333280 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 1980480
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 33 | 764242 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 393840 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 1639320 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 91 | 1461600 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1392960
| Cumilla Area Total |  |  |  | 2875 | 1862 | 39568932
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 17 | 274560 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11650
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 143 | 2925600 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 87 | 1704000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 311000
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 2 | 124320 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 559800 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 285 | 5910930
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 37 | 874000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 57 | 1374000 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3366573
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1084800
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 35 | 851976 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 102816 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 55 | 1218144 | Machine problem.
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 209 | 5215380 | Machine problem.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 287952 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7102000
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 9027000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 345 | 8252100 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1619 | 38756741
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 20247272
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 78 | 915840 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 169920 | Engine problem
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 31 | 256256 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 195 | 5021568 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 121875 | Engine problem
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 108480 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 725040
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 712 | 17410909 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1993 | 44977160
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 256320
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 158046
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2588000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1230 | 29431400
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5077459
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 232800 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5476400
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 4330
| Barisal Area Total |  |  |  | 2236 | 1944 | 43224755
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 391069 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 37188 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 47 | 308800
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 171 | 4150455 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8734981
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 313582 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 127616 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 841080 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1538976
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1787136
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 37140
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1131 | 27207273
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 395250
| Rajshahi Area Total |  |  |  | 3381 | 2154 | 45870546
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1425163
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 5291000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 1673308 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 36280
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1875456
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 195028
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1147250
| Rangpur Area Total |  |  |  | 950 | 497 | 11643485
| Total |  |  |  | 26364 | 15172 | 330920481
| Eastern Grid Total |  |  |  | 15943 | 8584 | 185204535
| Western Grid Total |  |  |  | 10421 | 6588 | 145715946
| National Grid Total |  |  |  | 26364 | 15172 | 330920481
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-07-14
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9262.61 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4119.4 | MW
i) Dhaka area |  |  | 4973.61 |  | MW | i) Khulna area |  |  |  | 1765 | MW
ii) Chattogram area |  |  | 1414 |  | MW | ii) Barishal area |  |  |  | 486.5 | MW
iii) Cumilla area |  |  | 1336 |  | MW | iii) Rajshahi area |  |  |  | 1136.4 | MW
iv) Mymensingh area |  |  | 956 |  | MW | iv) Rangpur area |  |  |  | 731.5 | MW
v) Sylhet area |  |  | 583 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13382.01 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | SSS | 00:00 | 67 | Jamalpur | 102 | 22:00 | 133 | Rahim | 45 | 12:00
2 | AKSML | 8.3 | 09:00 | 68 | Jashore | 156 | 21:00 | 134 | Rajbari | 82 | 19:30
3 | Aftabnagar | 38 | 16:00 | 69 | Jhenaidah | 141 | 21:00 | 135 | Rajendrapur | 90 | 21:00
4 | Agargaon | 121 | 13:00 | 70 | Joydebpur | 161 | 20:00 | 136 | Rajshahi | 142 | 23:00
5 | Agrabad | 98 | 16:00 | 71 | Joypurhat | 64 | 22:00 | 137 | Rajshahi-230 | 79 | 00:00
6 | Amnura | 75 | 22:00 | 72 | Juldah | 25 | 00:00 | 138 | Ramganj | 120 | 22:00
7 | Ashuganj | 91 | 23:00 | 73 | KSRM | 29 | 16:00 | 139 | Rampur | 43 | 23:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 270 | 19:00 | 140 | Rangamati | 18 | 18:30
9 | BSRM | 179 | 03:00 | 75 | Kachua | 86 | 22:00 | 141 | Rangpur | 139 | 12:00
10 | Bagerhat | 99 | 23:00 | 76 | Kallyanpur | 120 | 19:30 | 142 | Ruppur | 7 | 16:00
11 | Bakulia | 105 | 16:00 | 77 | Kalurghat | 36 | 12:00 | 143 | SSM | 0 | 00:00
12 | Banani | 58 | 13:00 | 78 | Kamrangirchar | 60 | 13:00 | 144 | Saidpur | 110 | 19:30
13 | Bangabhaban | 21 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 136 | 23:00
14 | Barapukuria | 67 | 19:30 | 80 | Kazla | 107 | 00:00 | 146 | Satmasjid | 117 | 19:00
15 | Barguna | 24 | 22:00 | 81 | Keranigonj | 79 | 19:30 | 147 | Savar | 222 | 12:00
16 | Barishal | 118 | 21:00 | 82 | Khagrachori | 34 | 21:00 | 148 | SevenRings | 3.21 | 01:00
17 | Barishal-230 | 106 | 23:00 | 83 | Khulna | 79 | 00:00 | 149 | ShahCement | 20 | 04:00
18 | Baroaulia | 63 | 22:00 | 84 | Khulshi | 160 | 00:00 | 150 | Shahjadpur | 91 | 22:00
19 | Baroirhat | 58 | 21:00 | 85 | Kishoreganj | 140 | 01:00 | 151 | Shahjibazar | 145 | 21:00
20 | Bashundhara | 189 | 13:00 | 86 | Kodda | 274 | 21:00 | 152 | Shahmirpur | 57 | 17:00
21 | BashundharaCement | 7 | 02:00 | 87 | Kulaura | 56 | 19:00 | 153 | Shariatpur | 94 | 00:00
22 | Beanibazar | 86 | 21:00 | 88 | Kurigram | 64 | 22:00 | 154 | Sherpur | 128 | 21:00
23 | Benapole | 68 | 23:00 | 89 | Kushtia | 163 | 23:00 | 155 | Shikalbaha | 32 | 11:00
24 | Bhaluka | 136 | 11:00 | 90 | Lalbag | 93 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 57 | 22:00 | 91 | Lalmonirhat | 60 | 02:00 | 157 | Shitalakhya | 90.7 | 15:00
26 | Bhangura | 40 | 22:00 | 92 | MI_Cement | 17.5 | 11:00 | 158 | Sholosohor | 48 | 17:00
27 | Bheramara(GK) | 71 | 21:00 | 93 | Madanganj | 38 | 22:00 | 159 | Shyampur | 129 | 12:00
28 | Bhulta | 223 | 17:00 | 94 | Madaripur | 121 | 22:00 | 160 | Siddhirganj | 118 | 20:00
29 | Bog-Sherpur | 66 | 22:00 | 95 | Madartek | 96.49 | 23:00 | 161 | Sirajganj | 118 | 21:00
30 | Bogura | 161 | 22:00 | 96 | Madunaghat | 60 | 19:30 | 162 | Sonargaon | 93 | 16:00
31 | Borhanuddin | 87 | 00:00 | 97 | Magura | 70 | 19:30 | 163 | Sreemongol | 85 | 22:00
32 | Brahmanbaria | 176 | 20:00 | 98 | Mahasthangarh | 82 | 01:00 | 164 | Sreepur | 101 | 15:00
33 | Cantonment | 124 | 13:00 | 99 | Manikganj | 116 | 22:00 | 165 | Srinagar | 49.09 | 21:00
34 | Chandpur | 78 | 21:00 | 100 | Maniknagar | 80 | 13:00 | 166 | Sunamganj | 54 | 03:00
35 | Chandraghona | 35 | 22:00 | 101 | Matarbari | 51 | 21:00 | 167 | Sylhet | 46 | 20:00
36 | Chapai | 79 | 22:00 | 102 | Matuail | 76 | 12:00 | 168 | Sylhet-132 | 129 | 19:30
37 | Charsaidpur | 40 | 01:00 | 103 | Millgate | 133 | 16:00 | 169 | TK | 35.4 | 22:00
38 | Chauddagram | 77 | 22:00 | 104 | Mirpur | 156 | 19:30 | 170 | Tangail | 180 | 21:00
39 | Chhatak | 36 | 22:00 | 105 | Mirsorai | 10 | 00:00 | 171 | Thakurgaon | 116 | 20:00
40 | Chowmuhani | 233 | 19:00 | 106 | Mirzapur | 36 | 05:00 | 172 | Tongi | 120 | 15:00
41 | Chuadanga | 118 | 00:00 | 107 | Mithapukur | 74 | 03:00 | 173 | Ullahpara | 29 | 23:00
42 | Coxsbazar | 130 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 57 | 00:00
43 | Cumilla(N) | 165 | 19:00 | 109 | Mogbazar | 139.2 | 16:00 | 175 | Uttara | 87 | 13:00
44 | Cumilla(S) | 195 | 19:30 | 110 | Mongla | 41 | 15:00 | 176 | UttaraNew | 55 | 23:00
45 | Daudkandi | 176 | 19:30 | 111 | Motijheel | 44 | 13:00 | 177 | Zigatola | 81 | 13:00
46 | Dhaka | 42 | 13:00 | 112 | Munshiganj | 109 | 01:00
47 | Dhamrai | 138 | 19:30 | 113 | Mymensingh | 240 | 21:00
48 | Dhanmondi | 151 | 13:00 | 114 | Naogaon | 140 | 22:00
49 | Dohazari | 110 | 19:30 | 115 | Narail | 65 | 19:30
50 | Faridpur | 184 | 23:00 | 116 | Narinda | 80 | 13:00
51 | Fatullah | 90 | 16:00 | 117 | Narshingdi | 158 | 21:00
52 | Fenchuganj | 44 | 19:00 | 118 | Natore | 159 | 00:00
53 | Feni | 125 | 20:00 | 119 | Nawabganj | 53 | 22:00
54 | GPH | 76 | 15:00 | 120 | Netrakona | 101 | 22:00
55 | Ghatail | 44 | 19:30 | 121 | New | 59.5 | 12:00
56 | Ghorashal | 53 | 15:00 | 122 | Niamatpur | 86 | 22:00
57 | Goalpara | 40 | 00:00 | 123 | Noapara | 52 | 19:30
58 | Gollamari | 88 | 19:30 | 124 | PHP | 10 | 10:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 385 | 06:00 | 370 | 15:00 | Kaliakoir | 368 | 18:30 | 154 | 15:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Bhulta | 400 | 18:30 | 381 | 15:00 | Meghnaghat | 381 | 18:30 | 367 | 15:00
| Bibiana | 394 | 00:00 | 385 | 16:00 | Payra | 409 | 18:00 | 402 | 00:00
| BIPTC | 403 | 07:00 | 393 | 23:00 | Rahanpur | 410 | 18:00 | 399 | 05:00
| Bogura | 403 | 18:30 | 389 | 05:00 | Rampal | 403 | 18:30 | 391 | 00:00
| Gopalganj | 396 | 18:00 | 383 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 06:00 | 216 | 15:00 | Haripur | 227 | 04:00 | 220 | 12:00
| AKSML | 238 | 18:00 | 226 | 12:00 | Hasnabad | 228 | 04:00 | 217 | 15:00
| Aminbazar | 226 | 03:00 | 218 | 15:00 | Hathazari | 238 | 19:30 | 230 | 05:00
| Ashuganj | 231 | 05:00 | 222 | 15:00 | Ishurdi | 235 | 18:30 | 225 | 15:00
| Ashuganj-400 | 231 | 05:00 | 222 | 15:00 | Jhenaidah | 227 | 18:30 | 215 | 22:00
| Baghabari | 231 | 18:00 | 223 | 22:00 | Kaliakoir | 227 | 18:30 | 218 | 15:00
| Barapukuria | 220 | 16:00 | 212 | 03:00 | Keranigonj | 227 | 06:00 | 216 | 15:00
| Barapukuria-230 | 220 | 16:00 | 212 | 03:00 | Khulna(S) | 231 | 18:30 | 219 | 15:00
| Barishal | 234 | 18:00 | 225 | 00:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bheramara | 234 | 18:30 | 223 | 22:00 | Maniknagar | 229 | 04:00 | 218 | 15:00
| Bhulta | 229 | 05:00 | 217 | 15:00 | Meghnaghat | 233 | 04:00 | 229 | 13:00
| Bibiana | 228 | 00:00 | 221 | 12:00 | Meghnaghat-400 | 233 | 06:00 | 222 | 15:00
| BIPTC | 235 | 18:30 | 222 | 22:00 | Mirsorai | 232 | 19:30 | 223 | 12:00
| Bogura | 227 | 18:00 | 1 | 00:00 | Rajshahi | 234 | 18:30 | 221 | 22:00
| Bogura-400 | 229 | 18:30 | 219 | 05:00 | Rampal | 231 | 18:30 | 220 | 00:00
| Borhanuddin | 237 | 18:00 | 230 | 23:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 232 | 19:30 | 224 | 15:00 | Rampura | 227 | 05:00 | 217 | 16:00
| Cumilla(N) | 227 | 18:30 | 217 | 15:00 | Shikalbaha | 237 | 20:00 | 228 | 10:00
| Faridpur | 234 | 18:30 | 225 | 23:00 | Shyampur | 229 | 06:00 | 218 | 15:00
| Fenchuganj | 231 | 07:00 | 225 | 15:00 | Siddhirganj | 229 | 04:00 | 220 | 15:00
| Ghorashal | 230 | 00:00 | 220 | 15:00 | Sirajgonj | 236 | 18:00 | 230 | 22:00
| Ghorashal-230 | 227 | 06:00 | 216 | 15:00 | Sreepur | 227 | 18:00 | 220 | 15:00
| Gopalganj | 234 | 18:30 | 226 | 15:00 | Tongi | 227 | 04:00 | 212 | 15:00
| GPH | 233 | 18:00 | 226 | 15:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 06:00 | 121 | 15:00 | Kushtia | 136 | 18:30 | 128 | 01:00
| Agargaon | 132 | 06:00 | 124 | 15:00 | Lalbag | 132 | 06:00 | 124 | 15:00
| Agrabad | 135 | 18:30 | 128 | 15:00 | Lalmonirhat | 130 | 16:00 | 115 | 21:00
| AKS | 132 | 20:00 | 127 | 14:00 | Madanganj | 130 | 18:30 | 124 | 15:00
| Aminbazar | 135 | 01:00 | 130 | 01:00 | Madaripur | 132 | 09:00 | 128 | 00:00
| Amnura | 137 | 17:00 | 125 | 22:00 | Madartek | 134 | 06:00 | 123 | 15:00
| Ashuganj | 135 | 00:00 | 133 | 12:00 | Madunaghat | 136 | 00:00 | 130 | 15:00
| Bagerhat | 133 | 18:00 | 119 | 12:00 | Magura | 138 | 18:30 | 126 | 22:00
| Bakulia | 135 | 00:00 | 129 | 15:00 | Mahasthangarh | 132 | 18:00 | 123 | 04:00
| Banani | 134 | 06:00 | 121 | 15:00 | Manikganj | 133 | 06:00 | 119 | 12:00
| Bangabhaban | 128 | 05:00 | 120 | 15:00 | Maniknagar | 128 | 03:00 | 121 | 13:00
| Barapukuria | 132 | 16:00 | 124 | 03:00 | Matarbari | 125 | 18:00 | 117 | 01:00
| Barguna | 133 | 18:00 | 124 | 00:00 | Matuail | 128.7 | 18:30 | 123.5 | 15:00
| Barishal | 138 | 18:00 | 129 | 23:00 | Millgate | 130 | 03:00 | 121 | 15:00
| Barishal-230 | 139 | 18:30 | 131 | 22:00 | Mirpur | 135 | 05:00 | 126 | 15:00
| Baroaulia | 135 | 00:00 | 129 | 15:00 | Mirzapur | 127 | 18:30 | 119 | 15:00
| Baroirhat | 130 | 18:30 | 119 | 15:00 | Mithapukur | 130 | 18:00 | 119 | 04:00
| Bashundhara | 139 | 23:00 | 121 | 15:00 | MI_Cement | 130 | 03:00 | 126 | 12:00
| BashundharaCement | 130 | 18:30 | 124 | 15:00 | Modern | 135 | 00:00 | 128 | 14:00
| Beanibazar | 123 | 00:00 | 116 | 22:00 | Mogbazar | 134 | 04:00 | 124 | 12:00
| Benapole | 135 | 18:00 | 123 | 21:00 | Mongla | 133 | 18:00 | 119 | 12:00
| Bhaluka | 123 | 05:00 | 117 | 15:00 | Motijheel | 128 | 05:00 | 120 | 15:00
| Bhandaria | 133 | 18:00 | 121 | 00:00 | Munshiganj | 131 | 06:00 | 124 | 15:00
| Bhangura | 135 | 18:00 | 129 | 22:00 | Mymensingh | 131 | 09:00 | 114 | 19:00
| Bheramara | 135 | 18:00 | 130 | 22:00 | Naogaon | 130 | 18:30 | 120 | 22:00
| Bheramara(GK) | 136 | 18:30 | 130 | 15:00 | Narail | 139 | 18:30 | 128 | 01:00
| Bhulta | 121 | 02:00 | 115 | 12:00 | Narinda | 128 | 03:00 | 121 | 13:00
| Bog-Sherpur | 131 | 18:00 | 125 | 05:00 | Narshingdi | 121 | 02:00 | 113 | 15:00
| Bogura | 134 | 18:00 | 127 | 03:00 | Natore | 133 | 18:00 | 126 | 22:00
| Bogura-230 | 135 | 18:00 | 127 | 07:00 | Nawabganj | 132 | 04:00 | 125 | 15:00
| Brahmanbaria | 126 | 07:00 | 120 | 15:00 | Netrakona | 133 | 00:00 | 120 | 06:00
| Cantonment | 132 | 06:00 | 123 | 15:00 | New | 131 | 04:00 | 122 | 15:00
| Chandpur | 130 | 18:30 | 119 | 15:00 | Niamatpur | 137 | 18:00 | 131 | 22:00
| Chandraghona | 137 | 18:30 | 131 | 15:00 | Noapara | 138 | 18:30 | 126 | 00:00
| Chapai | 134 | 18:00 | 129 | 07:00 | Pabna | 134 | 18:30 | 128 | 22:00
| Charsaidpur | 131 | 04:00 | 125 | 12:00 | Palashbari | 128 | 18:00 | 118 | 22:00
| Chauddagram | 128 | 18:00 | 119 | 14:00 | Panchagarh | 132 | 18:30 | 119 | 08:00
| Chhatak | 125 | 00:00 | 119 | 19:00 | Patuakhali | 132 | 18:00 | 126 | 00:00
| Chowmuhani | 127 | 18:30 | 115 | 06:00 | Payra | 134 | 18:00 | 129 | 00:00
| Chuadanga | 132 | 18:30 | 117 | 22:00 | PHP | 130 | 18:30 | 117 | 15:00
| Coxsbazar | 127 | 00:00 | 116 | 07:00 | Postogola | 135 | 05:00 | 127 | 15:00
| Cumilla(N) | 132 | 18:30 | 124 | 15:00 | Purbachal | 134 | 05:00 | 120 | 15:00
| Cumilla(S) | 132 | 04:00 | 123 | 15:00 | Purbasadipur | 128 | 18:00 | 116 | 07:00
| Daudkandi | 126 | 00:00 | 118 | 15:00 | Rahanpur | 138 | 18:00 | 134 | 05:00
| Dhaka | 134 | 05:00 | 122 | 15:00 | Rahim | 128 | 00:00 | 116 | 13:00
| Dhamrai | 128 | 06:00 | 120 | 15:00 | Rajbari | 131 | 18:00 | 125 | 22:00
| Dhanmondi | 130 | 18:30 | 123 | 15:00 | Rajendrapur | 125 | 22:00 | 117 | 16:00
| Dohazari | 133 | 18:00 | 125 | 13:00 | Rajshahi | 134 | 18:30 | 126 | 05:00
| Faridpur | 131 | 18:30 | 126 | 00:00 | Rajshahi-230 | 134 | 18:00 | 121 | 22:00
| Fatullah | 132 | 03:00 | 125 | 15:00 | Ramganj | 126 | 18:30 | 113 | 15:00
| Fenchuganj | 130 | 07:00 | 126 | 15:00 | Rampur | 136 | 00:00 | 129 | 13:00
| Feni | 128 | 18:30 | 118 | 15:00 | Rampura | 132 | 03:00 | 122 | 16:00
| Ghatail | 128 | 09:00 | 119 | 08:00 | Rangamati | 136 | 18:30 | 130 | 11:00
| Ghorashal | 136 | 01:00 | 129 | 15:00 | Rangpur | 129 | 16:00 | 25 | 00:00
| Goalpara | 139 | 18:30 | 127 | 22:00 | Ruppur | 136 | 18:30 | 131 | 00:00
| Gollamari | 137 | 18:00 | 128 | 22:00 | Saidpur | 128 | 16:00 | 116 | 22:00
| Gopalganj | 133 | 17:00 | 126 | 15:00 | Satkhira | 134 | 18:00 | 121 | 23:00
| Gopalganj-400 | 133 | 18:00 | 128 | 00:00 | Satmasjid | 132 | 06:00 | 124 | 12:00
| Gulshan | 133 | 06:00 | 122 | 15:00 | Savar | 134 | 18:30 | 127 | 12:00
| Halishahar | 136 | 00:00 | 129 | 13:00 | SevenRings | 135 | 06:00 | 129 | 15:00
| Haripur | 128 | 00:00 | 124 | 12:00 | ShahCement | 131 | 04:00 | 125 | 12:00
| HaripurSBU | 128 | 00:00 | 124 | 12:00 | Shahjadpur | 136 | 00:00 | 135 | 09:00
| Hasnabad | 134 | 03:00 | 128 | 15:00 | Shahjibazar | 124 | 00:00 | 119 | 22:00
| Hathazari | 137 | 19:30 | 133 | 03:00 | Shahmirpur | 136 | 18:00 | 130 | 14:00
| Ishurdi | 137 | 18:00 | 131 | 22:00 | Shariatpur | 133 | 18:00 | 125 | 22:00
| Jaldhaka | 126 | 16:00 | 115 | 21:00 | Sherpur | 135 | 00:00 | 122 | 03:00
| Jamalpur | 138 | 00:00 | 125 | 03:00 | Shikalbaha | 125 | 00:00 | 118 | 15:00
| Jashore | 136 | 18:30 | 124 | 23:00 | Shikalbaha-230 | 137 | 18:30 | 130 | 15:00
| Jhenaidah | 139 | 18:30 | 128 | 22:00 | Shitalakhya | 130 | 03:00 | 126 | 12:00
| Jhenaidah-230 | 139 | 18:30 | 129 | 22:00 | Sholosohor | 135 | 00:00 | 128 | 15:00
| Joydebpur | 130 | 18:00 | 123 | 12:00 | Shyampur | 132 | 20:00 | 126 | 14:00
| Joypurhat | 127 | 18:00 | 115 | 22:00 | Shyampur-230 | 133 | 06:00 | 125 | 15:00
| Juldah | 137 | 00:00 | 130 | 13:00 | Siddhirganj | 129 | 07:00 | 124 | 15:00
| Kabirpur | 129 | 03:00 | 118 | 15:00 | Sirajganj | 132 | 18:00 | 127 | 21:00
| Kachua | 130 | 18:30 | 119 | 15:00 | Sonargaon | 130 | 03:00 | 121 | 15:00
| Kaliakoir | 130 | 07:00 | 122 | 15:00 | Sreemongol | 124 | 00:00 | 120 | 19:00
| Kallyanpur | 130 | 06:00 | 124 | 15:00 | Sreepur | 127 | 06:00 | 123 | 12:00
| Kalurghat | 136 | 18:00 | 130 | 15:00 | Srinagar | 132 | 04:00 | 125 | 15:00
| Kamrangirchar | 132 | 04:00 | 122 | 15:00 | SSM | 140 | 00:00 | 125 | 13:00
| Kaptai | 135 | 8:00 | 132 | 15:00 | Sunamganj | 124 | 07:00 | 118 | 19:00
| Kazla | 128 | 04:00 | 121 | 13:00 | Sylhet | 125 | 07:00 | 122 | 19:30
| Keranigonj | 133 | 06:00 | 126 | 15:00 | Sylhet-132 | 126 | 00:00 | 124 | 15:00
| Khagrachori | 135 | 18:00 | 129 | 15:00 | Tangail | 127 | 02:00 | 117 | 15:00
| Khulna | 137 | 18:30 | 127 | 15:00 | Thakurgaon | 133 | 18:30 | 117 | 08:00
| Khulna(S) | 138 | 18:30 | 129 | 15:00 | TK | 136 | 00:00 | 131 | 11:00
| Khulshi | 134 | 00:00 | 127 | 15:00 | Tongi | 134 | 04:00 | 124 | 15:00
| Kishoreganj | 127 | 05:00 | 121 | 15:00 | Ullahpara | 135 | 18:00 | 129 | 21:00
| Kodda | 128 | 07:00 | 117 | 16:00 | Ullon | 133 | 03:00 | 123 | 15:00
| KSRM | 136 | 18:00 | 130 | 11:00 | Uttara | 135 | 04:00 | 127 | 15:00
| Kulaura | 128 | 00:00 | 125 | 02:00 | UttaraNew | 135 | 03:00 | 127 | 15:00
| Kurigram | 129 | 18:00 | 115 | 22:00 | Zigatola | 133 | 06:00 | 126 | 15:00

## L-Curve
Date | 2024-07-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 994 | 7976 | 6579 | 14555 |  |  |  | QF-LDC-11
0:30 | 812 | 7843.5 | 6419 | 14262.5 | Date: | 2024-07-14
1:00 | 630 | 7711 | 6259 | 13970
1:30 | 616 | 7754.5 | 6254 | 14008.5
2:00 | 602 | 7798 | 6249 | 14047
2:30 | 588 | 7723 | 6125 | 13848 | [5 empty] | Gen. at Eve. Peak | 15172 | 15172 MW (21:00 )
3:00 | 574 | 7648 | 6001 | 13649 | [6 empty] | 21:00
3:30 | 563 | 7591.5 | 5887.5 | 13479 | [5 empty] | Gen. at Day Peak | 13745 | 13745 MW (12:00 )
4:00 | 552 | 7535 | 5774 | 13309 | [6 empty] | 12:00
4:30 | 551 | 7539 | 5729 | 13268 | [5 empty] | Highest Generation | 15172
5:00 | 550 | 7543 | 5684 | 13227 | [6 empty] | 21:00
5:30 | 567 | 7469 | 5568 | 13037
6:00 | 584 | 7395 | 5452 | 12847
6:30 | 617 | 7231.5 | 5490 | 12721.5
7:00 | 650 | 7068 | 5528 | 12596
7:30 | 748 | 6980.5 | 5512 | 12492.5
8:00 | 846 | 6893 | 5496 | 12389
8:30 | 865 | 6987.5 | 5494 | 12481.5
9:00 | 884 | 7082 | 5492 | 12574
9:30 | 956 | 7140.5 | 5598 | 12738.5
10:00 | 1028 | 7199 | 5704 | 12903
10:30 | 1054 | 7304 | 5765 | 13069
11:00 | 1080 | 7409 | 5826 | 13235
11:30 | 1108 | 7564.5 | 5925.5 | 13490
12:00 | 1136 | 7720 | 6025 | 13745
12:30 | 1111 | 7726.5 | 6054 | 13780.5
13:00 | 1086 | 7733 | 6083 | 13816
13:30 | 1104 | 7729 | 6112.5 | 13841.5
14:00 | 1122 | 7725 | 6142 | 13867
14:30 | 1137 | 7768 | 6185 | 13953
15:00 | 1152 | 7811 | 6228 | 14039
15:30 | 1183 | 7721.5 | 6195 | 13916.5
16:00 | 1214 | 7632 | 6162 | 13794
16:30 | 1240 | 7580.5 | 6108 | 13688.5
17:00 | 1266 | 7529 | 6054 | 13583
17:30 | 1224 | 7411 | 5899 | 13310
18:00 | 1182 | 7293 | 5744 | 13037
18:30 | 1105 | 7657 | 5883 | 13540
19:00 | 1028 | 8021 | 6022 | 14043
19:30 | 880 | 8461 | 6484 | 14945
20:00 | 792 | 8514 | 6398 | 14912 |  |  |  | Executive Engineer
20:30 | 722 | 8549 | 6493 | 15042 |  |  |  | Network Operation Division
21:00 | 652 | 8584 | 6588 | 15172
21:30 | 611 | 8525.5 | 6600.5 | 15126
22:00 | 570 | 8467 | 6613 | 15080 |  |  |  |  | Page 6 of 7
22:30 | 700 | 8320 | 6607 | 14927
23:00 | 830 | 8173 | 6601 | 14774
23:30 | 912 | 8074.5 | 6590 | 14664.5
24:00 | 994 | 7976 | 6579 | 14555
15172 MW (21:00 )
13745 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-14 |  | Energy |  | 330920481
[14 empty] | 2024-07-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3653 | 914 | 1829 | 0 | 2061 | 5264 | 185 | 0 | 524 | 90 | 0 | 35 | 806.975
0:30 | 3700 | 914.5 | 1702 | 0 | 1977.5 | 5258 | 188 | 0 | 413.5 | 86 | 0 | 23 | 799.8125 |  | Date: | 44025
1:00 | 3747 | 915 | 1575 | 0 | 1894 | 5252 | 191 | 0 | 303 | 82 | 0 | 11 | 792.65
1:30 | 3748 | 914.5 | 1619 | 0 | 1895 | 5250 | 191 | 0 | 300.5 | 81 | 0 | 9.5 | 636.5075 | [8 empty] | Total Energy | 330.9205 | 330.9205 | Total Energy Gen 330.920 MKWHr Energy Not Served 10.880 MKWHr Energy Requirement 341.800 MKWHr
2:00 | 3749 | 914 | 1663 | 0 | 1896 | 5248 | 191 | 0 | 298 | 80 | 0 | 8 | 480.365 | [8 empty] | Energy not Served | 10.8799 | 10.8799
2:30 | 3753 | 914.5 | 1654 | 0 | 1800 | 5228 | 191 | 0 | 217.5 | 79 | 0 | 11 | 479.41 | [8 empty] | Energy Requirement | 341.8004 | 341.8004
3:00 | 3757 | 915 | 1645 | 0 | 1704 | 5208 | 191 | 0 | 137 | 78 | 0 | 14 | 478.455
3:30 | 3760 | 914 | 1648 | 0 | 1581 | 5157 | 191 | 0 | 137 | 77 | 0 | 14 | 473.68 | [7 empty] | Shortage
4:00 | 3763 | 913 | 1651 | 0 | 1458 | 5106 | 191 | 0 | 137 | 76 | 0 | 14 | 468.905
4:30 | 3759 | 913.5 | 1663.5 | 0 | 1430 | 5093.5 | 191 | 0 | 128 | 75 | 0 | 14.5 | 460.31
5:00 | 3755 | 914 | 1676 | 0 | 1402 | 5081 | 191 | 0 | 119 | 74 | 0 | 15 | 451.715
5:30 | 3718 | 914.5 | 1648 | 0 | 1297 | 5069.5 | 191 | 0 | 102 | 71 | 11 | 15 | 394.415
6:00 | 3681 | 915 | 1620 | 0 | 1192 | 5058 | 191 | 0 | 85 | 68 | 22 | 15 | 337.115
6:30 | 3630 | 914.5 | 1632.5 | 0 | 1077 | 5071.5 | 191 | 0 | 69 | 66 | 55 | 15 | 289.8425 | [6 empty] | Coal
7:00 | 3579 | 914 | 1645 | 0 | 962 | 5085 | 191 | 0 | 53 | 64 | 88 | 15 | 242.57
7:30 | 3571.5 | 914.5 | 1602 | 0 | 965 | 4964.5 | 191 | 0 | 53 | 68 | 143 | 20 | 245.9125 | [5 empty] | Oil
8:00 | 3564 | 915 | 1559 | 0 | 968 | 4844 | 191 | 0 | 53 | 72 | 198 | 25 | 249.255
8:30 | 3563 | 914.5 | 1582.5 | 0 | 1001 | 4857 | 191 | 0 | 53 | 74 | 224.5 | 21 | 280.2925
9:00 | 3562 | 914 | 1606 | 0 | 1034 | 4870 | 191 | 0 | 53 | 76 | 251 | 17 | 311.33
9:30 | 3548.5 | 914 | 1612.5 | 0 | 1122.5 | 4881 | 193.5 | 0 | 53 | 79 | 319 | 15.5 | 321.3575
10:00 | 3535 | 914 | 1619 | 0 | 1211 | 4892 | 196 | 0 | 53 | 82 | 387 | 14 | 331.385
10:30 | 3591.5 | 914 | 1635 | 0 | 1280.5 | 4881 | 196 | 0 | 66 | 83 | 408 | 14 | 339.98
11:00 | 3648 | 914 | 1651 | 0 | 1350 | 4870 | 196 | 0 | 79 | 84 | 429 | 14 | 348.575
11:30 | 3714.5 | 914 | 1717.5 | 0 | 1429 | 4882.5 | 196 | 0 | 84 | 85 | 456.5 | 11 | 319.925
12:00 | 3781 | 914 | 1784 | 0 | 1508 | 4895 | 196 | 0 | 89 | 86 | 484 | 8 | 291.275
12:30 | 3771.5 | 913.5 | 1791.5 | 0 | 1529.5 | 4876 | 196 | 0 | 107 | 86 | 493.5 | 16 | 304.6375
13:00 | 3762 | 913 | 1799 | 0 | 1551 | 4857 | 196 | 0 | 125 | 86 | 503 | 24 | 318
13:30 | 3762 | 913 | 1799 | 0 | 1551 | 4857 | 196 | 0 | 125 | 86 | 503 | 24 | 318
14:00 | 3762 | 913 | 1799 | 0 | 1551 | 4857 | 196 | 0 | 125 | 86 | 503 | 24 | 318
14:30 | 3760 | 913.5 | 1808 | 0 | 1588 | 4932 | 196 | 0 | 165 | 89 | 456.5 | 19.5 | 369.5
15:00 | 3758 | 914 | 1817 | 0 | 1625 | 5007 | 196 | 0 | 205 | 92 | 410 | 15 | 421
15:30 | 3696 | 914 | 1772 | 0 | 1682 | 5011.5 | 196 | 0 | 207 | 91 | 335 | 12 | 523.5
16:00 | 3634 | 914 | 1727 | 0 | 1739 | 5016 | 196 | 0 | 209 | 90 | 260 | 9 | 626
16:30 | 3587.5 | 914 | 1691 | 0 | 1799 | 4950.5 | 196 | 0 | 246 | 88 | 202.5 | 14 | 521.5
17:00 | 3541 | 914 | 1655 | 0 | 1859 | 4885 | 196 | 0 | 283 | 86 | 145 | 19 | 417
17:30 | 3462 | 914 | 1559.5 | 0 | 1923 | 4751 | 196 | 0 | 299.5 | 83 | 91.5 | 30.5 | 410.5
18:00 | 3383 | 914 | 1464 | 0 | 1987 | 4617 | 196 | 0 | 316 | 80 | 38 | 42 | 404
18:30 | 3505 | 914 | 1549.5 | 0 | 2135.5 | 4676.5 | 196 | 0 | 424 | 86 | 19 | 34.5 | 420.2175
19:00 | 3627 | 914 | 1635 | 0 | 2284 | 4736 | 196 | 0 | 532 | 92 | 0 | 27 | 436.435
19:30 | 3719 | 914 | 1752 | 0 | 2535 | 5089 | 156 | 0 | 653 | 94 | 0 | 33 | 546.7375
20:00 | 3666 | 914 | 1666 | 0 | 2562 | 5098 | 196 | 0 | 703 | 90 | 0 | 17 | 657.04
20:30 | 3736.5 | 913.5 | 1722.5 | 0 | 2499 | 5164.5 | 196 | 0 | 698.5 | 90 | 0 | 21.5 | 580.52
21:00 | 3807 | 913 | 1779 | 0 | 2436 | 5231 | 196 | 0 | 694 | 90 | 0 | 26 | 504
21:30 | 3818.5 | 913.5 | 1773 | 0 | 2393 | 5255 | 190.5 | 0 | 667 | 91 | 0 | 24.5 | 524.175
22:00 | 3830 | 914 | 1767 | 0 | 2350 | 5279 | 185 | 0 | 640 | 92 | 0 | 23 | 544.35
22:30 | 3730.5 | 914 | 1799.5 | 0 | 2291 | 5272 | 185 | 0 | 603 | 92 | 0 | 40 | 618.84
23:00 | 3631 | 914 | 1832 | 0 | 2232 | 5265 | 185 | 0 | 566 | 92 | 0 | 57 | 693.33
23:30 | 3642 | 914 | 1830.5 | 0 | 2146.5 | 5264.5 | 185 | 0 | 545 | 91 | 0 | 46 | 750.1525 |  | Max Temp. in Dhaka |  | 34.5°C
24:00 | 3653 | 914 | 1829 | 0 | 2061 | 5264 | 185 | 0 | 524 | 90 | 0 | 35 | 806.975
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 330.920 MKWHr Energy Not Served 10.880 MKWHr Energy Requirement 341.800 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 76 | 116 | 116 | 105 | 105 | 105 | 2735444
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1928000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 4 |  | 8 | 8 | 8 | 8 | 8 |  |  | 33516
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 4 | 17 | 17 | 11 | 18 | 14 | 17 | 14 | 10 | 3 | 0 | [8 empty] | 117720
6 | Sikalbaha 225MW CCPP (Gas) | 219 | 221 | 221 | 221 | 222 | 221 | 219 | 220 | 218 | 218 | 218 | 217 | 216 | 216 | 213 | 216 | 216 | 218 |  | 218 | 218 | 220 | 220 | 218 | 218 | 220 | 5005591
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 34 | 34 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 557812
12 | Hathazari 100 MW peaking PP | 48 | 48 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 53 | 53 | 53 | 53 | 62 |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 1068144
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | [17 empty] | 8 | 17 | 34 | 34 | 34 | 17 |  | 193199
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 14 | 14 | 20 | 20 | 20 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 543632
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 325 | 325 | 325 | 326 | 322 | 280 | 280 | 280 | 280 | 280 | 280 | 313 | 316 | 313 | 315 | 315 | 312 | 311 |  | 312 | 315 | 317 | 318 | 317 | 321 | 324 | 7442176
18 | Kodda 300 MW PP Unit-2 (Summit) | 55 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 66 | 97 | 97 | 97 | 97 | 102 | 80 | 52 | 62 | 115 |  | 137 | 145 | 145 | 155 | 140 | 135 | 82 | 2070000
19 | Ashuganj 195 MW PP (APSCL-United) | [9 empty] | 8 | 8 | 8 | 8 | 8 | [5 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 83636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 1219 | 1220 | 1220 | 1184 | 1180 | 1178 | 1180 | 1050 | 1095 | 1110 | 1100 | 1100 | 1050 | 1020 | 1055 | 1024 | 950 | 850 |  | 964 | 1060 | 1062 | 1150 | 1170 | 1168 | 1175 | 26247270
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 33 | 35 | 34 | 35 | 35 | 35 | 10 | 10 | 10 | 10 |  | 10 | 10 | 20 | 36 | 36 | 36 | 36 | 723960
33 | Ashuganj 225 MW CCPP | 214 | 215 | 214 | 215 | 214 | 217 | 213 | 184 | 189 | 186 | 195 | 186 | 186 | 186 | 194 | 211 | 182 | 186 |  | 208 | 213 | 212 | 213 | 208 | 211 | 211 | 4933000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 350 | 265 | 270 | 270 | 270 | 275 | 270 | 270 | 270 | 305 | 270 | 270 | 270 |  | 285 | 270 | 270 | 280 | 330 | 270 | 270 | 6748000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 285 | 285 | 280 | 285 | 280 | 280 | 285 | 285 | 280 | 280 | 315 | 280 | 280 | 280 |  | 295 | 280 | 280 | 310 | 320 | 300 | 280 | 7360200
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 290 | 285 | 285 | 230 | 285 | 285 | 285 | 270 | 270 | 240 | 240 |  | 240 | 310 | 285 | 320 | 300 | 230 | 230 | 6395400
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 30 | 34 | 42 | 42 | 27 | 10 | 10 | 10 |  | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 472320
36 | Chandpur 150 MW CCPP | 45 | 45 | 46 | 45 | 45 | 45 | 50 | 51 | 51 | 46 | 46 | 40 | 41 | 42 | 40 | 40 | 40 | 39 |  | 41 | 39 | 39 | 38 | 38 | 38 | 34 | 985180
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 408 | 409 | 407 | 403 | 400 | 370 | 370 | 371 | 371 | 378 | 402 | 403 | 401 | 401 | 401 | 401 | 351 |  | 390 | 405 | 401 | 403 | 400 | 396 | 401 | 9525600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 5123000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 18 | 17 | 17 | 18 | 18 | 18 | 18 | 11 | 10 | 5 | 5 | 5 | 5 | 5 | 7 | 8 | 8 | 12 |  | 12 | 12 | 12 | 17 | 17 | 17 | 17 | 274560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 11 | 16 | 38 | 25 | 27 | 32 | 44 | 31 | 39 | 29 | 14 | 3 |  | 0 | [6 empty] | 311000
44 | Fenchugonj CCPP Phase-1 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 874000
45 | Fenchugonj CCPP Phase-2 | 58 | 57 | 58 | 57 | 57 | 57 | 57 | 58 | 57 | 58 | 57 | 57 | 57 | 58 | 57 | 55 | 56 | 56 |  | 58 | 57 | 57 | 57 | 57 | 57 | 57 | 1374000
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 56 | 58 | 40 | 40 | 40 | 40 | 55 | 53 | 53 | 50 | 54 | 54 | 40 |  | 55 | 55 | 55 | 55 | 50 | 50 | 56 | 1218144
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 210 | 210 | 209 | 209 | 209 | 210 | 211 | 211 | 211 | 211 | 211 | 211 | 210 | 210 | 206 | 209 | 209 | 209 |  | 209 | 209 | 209 | 209 | 209 | 207 | 209 | 5215380
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 102816
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 22 | 22 | 22 | 22 | 50 | 50 | 50 | 49 | 52 | 52 | 22 |  | 52 | 53 | 53 | 53 | 47 | 50 | 50 | 1084800
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 287952
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 275 | 270 | 300 | 270 | 300 | 270 | 300 | 290 | 295 | 290 | 280 | 290 | 315 | 305 | 295 | 280 |  | 275 | 290 | 280 | 285 | 295 | 300 | 305 | 7102000
| Bibiyana South 400 MW | 345 | 345 | 345 | 345 | 345 | 345 | 345 | 310 | 316 | 310 | 350 | 377 | 377 | 340 | 365 | 340 | 340 | 316 |  | 365 | 345 | 345 | 345 | 373 | 345 | 345 | 8252100
58 | Nababganj 55 MW PP (Southern power ) |  |  | 35 | 35 | 35 | 35 |  |  |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 669916
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 6 | 6 | 6 |  | 6 | 6 | 6 | 2 | 0 | 0 | 1 | 124320
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 80 | 78 | 76 | 74 | 68 | 64 | 72 | 76 | 82 | 84 | 86 | 86 | 92 | 92 | 90 | 86 | 80 |  | 92 | 94 | 90 | 90 | 92 | 92 | 90 | 1980480
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 35 | 38 | 38 | 33 | 10 | 6 | 5 | 2 | 4 | 5 | 5 | 2 | 2 | 4 | 20 |  | 14 | 14 | 17 | 22 | 27 | 30 | 30 | 475200
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 5 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 17 | 393840
69 | Summit Ashulia | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 325800
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 356400
71 | Maona 33 MW PP(Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 337680
72 | Rupganj 33 MW PP(Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 1 | 1 | 10 | 10 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 267800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 105 | 105 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 88 | 70 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1639320
| Chowmuhani 113 MW | 59 | 50 | 46 | 46 | 45 | 46 | 47 | 46 | 46 | 46 | 47 | 47 | 47 | 45 | 44 | 44 | 73 | 89 |  | 89 | 90 | 90 | 91 | 90 | 90 | 90 | 1461600
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 17 | 17 | 17 | 17 |  |  |  | 54 | 54 | 137 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 108 | 72 | 54 | 54 | 1955520
77 | Siddhirganj 100 PP(Dutch Bangla) | [15 empty] | 8 | 8 | 8 |  | 9 | 9 | 9 | 9 | 9 |  |  | 54720
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 172800
79 | Kodda 150 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 132 | 132 | 132 | 132 | 132 | 132 | 100 | 1100640
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 | 22 | 22 | 29 | 30 |  | 31 | 31 | 32 | 33 | 34 | 34 | 33 | 764242
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 426240
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 2 | 5 | 5 | 4 | 2 | 2 | 1 | [9 empty] | 32762
| Jodiac Power | [19 empty] | 8 | 17 | 17 | 17 | 17 |  |  | 79860
| Karnaphuli Power Ltd. | [19 empty] | 9 | 34 | 27 | 34 | 34 | 34 |  | 143850
82 | Madanganj 102 PP(Summit) | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 65 | 74 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 68 | 68 | 73 | 68 | 1739848
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [16 empty] | 12 | 13 |  | 13 | 13 | 13 | 13 |  |  |  | 63000
86 | Meghnaghat CCPP ( Summit) | 227 | 310 | 310 | 315 | 315 | 289 | 290 | 287 | 308 | 296 | 303 | 280 | 295 | 297 | 310 | 283 | 285 | 267 |  | 306 | 270 | 282 | 281 | 302 | 310 | 302 | 6973935
87 | Meghnaghat 100 MW(IEL) | 32 | 32 | 32 | 32 | 32 | 32 | 28 | 31 | 32 | 32 | 32 | 23 | 10 | 8 | 8 | 8 | 8 | 8 |  | 9 | 8 | 8 | 8 | 8 | 8 | 9 | 461760
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 394560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 12 | 46 | 46 | 46 | 46 | 12 |  | 173640
92 | Fenchuganj 44 MW (Energyprima) | 39 | 39 | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 36 | 36 | 36 | 33 | 35 | 32 | 32 | 10 |  | 35 | 35 | 35 | 35 | 36 | 39 | 39 | 851976
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 20 |  | 30 | 43 | 43 | 43 | 43 | 43 | 43 | 1085228
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 195120
95 | Patenga 50MW PP (Baraka) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 33 | 33 | 19 | 19 | 19 | 32 | 40 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 722400
96 | Chattogram 108 MW PP (ECPV) | 28 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 28 | 35 | 38 | 38 | 37 | 37 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 36 | 37 | 38 | 794880
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1329705
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | [5 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 661675
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 120 |  | 120 | 163 | 163 | 163 | 120 | 163 | 163 | 3366573
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | 0 | [8 empty] | 11650
103 | Kamalaghat 54 MW PP(Banco Energy) | 18 | 35 | 35 | 35 | 35 | 35 |  |  |  | 17 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 35 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 647280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 114 | 115 | 115 | 117 | 118 | 118 | 117 | 117 | 117 | 116 | 116 | 116 | 116 | 116 | 114 | 114 | 114 | 114 |  | 143 | 143 | 143 | 143 | 143 | 144 | 143 | 2925600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 96 | 96 | 96 | 96 | 96 | 96 | 83 | 96 | 96 | 89 | 77 | 79 | 84 | 96 | 78 | 78 | 87 | 106 |  | 98 | 97 | 102 | 96 | 96 | 96 | 96 | 2225952
115 | Juldah 100 MW PP Unit-3 (Acorn) | 48 | 48 | 48 | 48 | 48 | 48 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 49 | 49 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 49 | 919680
116 | Chandpur 200 MW (Desh energy) | 104 | 104 | 104 | 105 | 104 | 104 | 51 | 51 | 51 | 51 | 55 | 85 | 100 | 100 | 100 | 100 | 100 | 107 |  | 122 | 120 | 120 | 120 | 120 | 120 | 108 | 2333280
117 | Ashuganj 150 MW PP (Midland) | 12 | 13 | 13 | 13 | 12 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 12 | 7 | 7 | 8 | 10 |  | 10 | 10 | 10 | 12 | 10 | 12 | 10 | 272654
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 403 | 401 | 401 | 327 | 328 | 328 | 328 | 328 | 403 | 403 | 404 | 404 | 396 | 389 | 363 | 312 |  | 346 | 372 | 372 | 366 | 368 | 340 | 342 | 9027000
| Jamalpur 115 MW PP (United) | 65 | 67 | 67 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 66 | 66 | 66 | 66 | 66 |  | 86 | 86 | 87 | 87 | 87 | 86 | 86 | 1704000
| Anwara 300 MW PP (United) | 50 | 52 | 52 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 28 | 23 | 49 | 52 | 49 | 49 |  | 49 | 49 | 49 | 51 | 51 | 50 | 52 | 870655
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 12 | 12 | 12 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 62 | 62 | 62 | 62 | 62 | 50 | 1106880
| Anlima Energy Ltd. | 90 | 90 | 74 | 27 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 53 | 30 | 18 |  | 26 | 60 | 67 |  |  | 10 | 87 | 819218
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 559800
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 15 | 19 | 29 | 29 | 33 | 33 | 30 | 23 | 16 | 9 | 3 | [8 empty] | 244689
| Chandpur 115(Doreen) | 49 | 48 | 33 | 33 | 33 | 33 | 33 | 34 | 49 | 52 | 53 | 52 | 55 | 52 | 53 | 48 | 49 | 63 |  | 70 | 115 | 100 | 115 | 111 | 100 | 59 | 1392960
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432000
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | [8 empty] | 17 | 17 | 17 | 17 | 17 |  | 17 | 114 | 145 | 145 | 90 | 17 | 17 | 615563
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 11 | 8 | 14 | 14 | 15 | 15 | 15 | 25 | 17 | 14 | 14 | 8 | 24 | 18 | 15 | 9 | 19 | 42 |  | 27 | 33 | 17 | 26 | 23 | 57 | 35 | 471360
| Sonagazi 75 MW Solar Plant | [5 empty] | 5 | 17 | 34 | 52 | 65 | 64 | 55 | 54 | 58 | 54 | 30 | 6 | 5 | [8 empty] | 504745
| Matarbari 2*600 MW (CPGCL) | 420 | 420 | 421 | 421 | 421 | 421 | 422 | 420 | 421 | 421 | 422 | 420 | 422 | 419 | 421 | 420 | 420 | 420 |  | 423 | 417 | 419 | 420 | 419 | 422 | 418 | 10152727
120 | Eastern Zone Total | 7711 | 7798 | 7648 | 7535 | 7543 | 7395 | 7068 | 6893 | 7082 | 7199 | 7409 | 7720 | 7733 | 7725 | 7811 | 7632 | 7529 | 7293 |  | 8021 | 8461 | 8514 | 8584 | 8467 | 8173 | 7976 | 185204535
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 79 | 79 | 80 | 81 | 72 | [10 empty] | 16 | 31 | 31 |  | 44 | 59 | 77 | 78 | 82 | 85 | 95 | 915840
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 15 | 15 | [17 empty] | 27 | 28 | 34 | 31 | 31 | 21 | 11 | 169920
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [16 empty] | 2 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 108480
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 21 | 55 | 59 | 80 | 95 | 99 | 83 | 97 | 70 | 24 | 34 | 10 | [8 empty] | 725040
131 | Rampal 1320 MW (BIFPCL) | 712 | 704 | 722 | 723 | 718 | 719 | 718 | 718 | 712 | 716 | 710 | 710 | 711 | 712 | 709 | 711 | 710 | 773 |  | 772 | 773 | 732 | 712 | 712 | 712 | 711 | 17410909
132 | United Payra Power Ltd. | [17 empty] | 14 |  | 35 | 35 | 35 | 35 | 54 | 35 | 35 | 232800
133 | Bhola Nutan Biddut BD LTD (GAS) | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 |  | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 5077459
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | [9 empty] | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 256320
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 206 | 180 | 180 | 180 | 180 | 180 | 180 | 200 | 200 | 200 | 150 |  | 203 | 262 | 270 | 307 | 307 | 307 | 307 | 5476400
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4330
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 126 | 130 | 130 | 130 | 80 | 80 | 80 | 80 | 80 | 124 | 124 | 124 | 124 | 122 | 80 | 80 | 80 |  | 124 | 124 | 80 | 126 | 126 | 126 | 126 | 2588000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 8 | [6 empty] | 9 | 9 | 10 | 10 | 6 | 10 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 158046
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 121875
143 | Gopalganj 100 MW Peaking PP | 41 | 41 | [17 empty] | 25 | 40 | 47 | 31 | 31 | 31 | 31 | 256256
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 915 | 914 | 915 | 913 | 914 | 915 | 914 | 915 | 914 | 914 | 914 | 914 | 913 | 914 | 914 | 914 | 914 | 914 |  | 914 | 914 | 914 | 913 | 914 | 914 | 914 | 20247272
147 | Bheramara 410 MW CCPP | 198 | 203 | 203 | 213 | 212 | 215 | 226 | 225 | 226 | 228 | 216 | 208 | 209 | 200 | 190 | 185 | 185 | 185 |  | 188 | 186 | 190 | 195 | 195 | 195 | 194 | 5021568
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1120 | 1100 | 1080 | 1100 | 1040 | 1050 | 1050 | 1040 | 1070 | 1080 | 1110 | 1200 | 1244 | 1180 | 1000 |  | 950 | 1160 | 1190 | 1230 | 1244 | 1244 | 1244 | 29431400
149
150 | Barapukuria TPP Unit-1 | 60 | 60 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 60 | 61 | 60 | 59 | 59 | 59 | 60 | 62 |  | 62 | 61 | 62 | 61 | 61 | 60 | 60 | 1425163
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 210 | 210 | 5291000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 32 | 32 | [13 empty] | 4 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 391069
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 5 | 5 | 3 | 5 | 4 | 4 | 2 | 1 | 0 | [8 empty] | 37140
| Sirajganj 68 MW Solar Park | [6 empty] | 8 | 26 | 30 | 41 | 58 | 50 | 52 | 50 | 18 | 28 | 14 | 4 | [8 empty] | 395250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 174 | 174 | 174 | 173 | 174 | 176 | 180 | 183 | 185 | 185 | 183 | 181 | 176 | 173 | 171 | 170 | 167 | 140 |  | 143 | 171 | 171 | 171 | 140 | 160 | 170 | 4150455
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 414 | 414 | 414 | 414 | 414 | 350 | 300 |  | 330 | 401 | 350 | 414 | 414 | 414 | 414 | 8734981
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 5 | [18 empty] | 4 |  | 4 | 4 | 5 | 15 | 15 | 37188
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 2 | 2 |  | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 127616
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 35 | 35 | [14 empty] | 14 | 34 |  | 45 | 45 | 47 | 47 | 47 | 45 | 45 | 308800
168 | Santahar 50 MW Peaking PP | 22 | 22 | 18 | 18 | [8 empty] | 10 | 23 | 16 | 16 | 16 | 20 |  | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 313582
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 27 | 27 | 48 | 48 | 50 | 50 | 49 | 49 |  | 74 | 86 | 86 | 86 | 86 | 87 | 86 | 841080
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 70 | 35 | [5 empty] | 15 | 35 | 35 | 35 | 35 | 51 | 90 | 105 | 70 |  | 73 | 113 | 113 | 113 | 113 | 113 | 113 | 1538976
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 70 | 35 | 35 |  |  |  |  | 35 | 35 | 80 | 90 | 90 | 113 | 113 | 113 | 70 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 1787136
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 105 | 105 | 105 | 49 | 49 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 70 | 93 | 93 | 100 |  | 101 | 101 | 101 | 101 | 103 | 103 | 103 | 1673308
177 | Sympa Solar Power 8MW | [11 empty] | 7 | 8 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 36280
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 74 | 74 | 35 | 35 | 35 | 54 | 55 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 90 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1875456
| Intraco Solar 30 MW | [5 empty] | 1 | 7 | 16 | 15 | 23 | 12 | 23 | 14 | 24 | 25 | 16 | 3 | 1 |  | 0 | [6 empty] | 195028
| Adani Power Jharkhanda Ltd | 1127 | 1130 | 1131 | 1126 | 1130 | 1128 | 1133 | 1128 | 1130 | 1133 | 1138 | 1134 | 1134 | 1137 | 1143 | 1138 | 1145 | 1142 |  | 1142 | 1136 | 1143 | 1131 | 1146 | 1142 | 1139 | 27207273
178 | Teesta Solar Limited | [5 empty] | 10 | 15 | 26 | 13 | 96 | 125 | 158 | 189 | 198 | 154 | 98 | 58 | 11 | [8 empty] | 1147250