## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-23 | Tuesday
|  | Date (day): | 2024-07-23 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 16148.6 | MW |  |  | (b) At Evening Peak Hour : |  | 17535 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-22 | 2024-07-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 140 | 140 | 140 |  | 40 | Machine problem
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage |  | 16-07-24
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 352 | 408 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 24 | 24 | 76 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 308 | 304 | 300 | 300 | 35 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 17 | 17 | 85 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 80 | 78 | 100 | 100
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 332 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 82 | 90 | 12 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 32 | 130 |  | 19 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 | 20 |  | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 27 | 27 | 42 | 42 |  | 38 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 7 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 16 | 30 | 30 |  | 3 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 50 | 60 | 96 |  | 53 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 0 | 17 | 50 | 55 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 17 | 50 | 54 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 0 |  | Fuel shortage
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1531 | 1874 | 2760 | 3013 | 2021 | 1016
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 105 | 112 | 110 | 112 | 68 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 8 | 17 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 11 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 200 | 200 | 200 | 200 | 30 |  | Low water lavel
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 220 | 220
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 50 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 70 | 28 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 80 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 50 | 50 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 0 | 49 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 29 | 30 | 40
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 25 | 25 | 83 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 15 | 52 | 248 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 0 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 100 | 110 | 0 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 50 | 62 | 38 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 17 | 104 |  | 12 | Engine problem
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 35 | 108 |  | 55 | Engine problem
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 606 | 800 | 1100 | 1200
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 49 | 21 | 44 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 420 | 373 | 420 | 420
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 2 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 1641 | 1755 | 2735 | 3180 | 612 | 419
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 195 | 212 | 200 | 210
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 330 | 285 | 330 | 30 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 320 | 340 | 340 | 20 |  | Gas shortage
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 | 400 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 30 | 35 | 35 | 10 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 20 | 44 | 43 | 43 | 12 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 107 | 200 | 200
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 55 | 150
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 34 | 36 |  | 16 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 86 | 90 | 90 | 90 | 73 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 193 | 100 | 193 | 7 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 70 | 78 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 16 | 33 | 33
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 17 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 17 | 17 | 97 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 28 | 28 | 85 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 32 | 115 | 49 | 115 |  | 0
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1221 | 1621 | 1667 | 1988 | 734 | 57
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 192 | 201 | 200 | 200 | 2 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 119 | 116 | 150 | 50 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 32 | 76 | 68 | 75 | 40 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 32 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 266 | 396 | 452.6 | 442 | 2 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 36 | 35 | 35 | 35 |  | 35 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 48 | 68 | 56 |  | 34 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 33 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 213 | 0 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 323 | 323 | 335 | 330 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 330 | 378 | 330 | 380 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1379 | 1360 | 1461 | 1494 | 121 | 436
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 905 | 931 | 931
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 48 | 98 | 17 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 50 |  | 59 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 385 | 330 | 330 | 80 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 8 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 35 | 70 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 46 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 758 | 860 | 956 | 1000 | 234 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1961 | 2183 | 2420 | 2500 | 1112 | 73
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 48 | 62 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 790 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 35 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 180 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 935 | 1326 | 1861 | 1994 | 177 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 144 | 174 | 180 | 200
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 3 | 208 | 180 | 200 | 20 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 345 | 414 | 400 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 87 |  | 17 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 829 | 1066 | 1140 | 1140
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 18 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1341 | 1882 | 2171 | 2416 | 463 | 126
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 63 | 63 | 63 | 60 |  | 25
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 165 | 176 | 200 | 220 |  | 54 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 100 | 113
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 92 | 90 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 124 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 390 | 401 | 621 | 508 | 40 | 164
| Total |  |  |  |  | 28098 | 26947 | 10665 | 12798 | 16148.6 | 17535 | 5282 | 2355
A. |  | 2024-07-22 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 13218 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10608 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12820 | MW
3 | Day peak Generation : |  |  | 10665 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12279 | MW
4 | Evening peak Generation : |  |  | 12798 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 59 | MW
5 | Total Energy Generation : |  | 284.7766 | MKWHr | By Solar | 2.709 | MKWHr
| By Gas : | 142.7518 | MKWHr |  | By Oil: | 10.6731 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 97.8784 | MKWHr |  | By Hydro: | 4.8046 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.92784 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5282 | MW | Dhaka | 3857 | 3857 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2355 | MW | Chittagong | 1020 | 1020 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7637 | MW | Khulna | 1635 | 1635 |  | 0 |  | 19:30 |  | 93.59
7 | Total Gas Supplied : |  |  | 1062.77 | MMCFD |  |  | Rajshahi | 1487 | 1487 |  | 0 |  | 20:00 |  | 100.275
8 | Fuel Cost : | i) Gas : | Taka | 445979695.924 | ii) Oil : | Taka | 194575794.02 | Comilla | 1254 | 1209 |  | 45 |  | 21:00 |  | 59.21
|  | iii) Coal : | Taka | 674151214.37 | Total | Taka | 1314706704.314 | Mymensingh | 1168 | 1168 |  | 0 |  | 22:00 |  | 32.47
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 559 | 545 |  | 14 |  | 23:00 |  | 25.785
| ii) During Peak Demand : |  |  | 614 | MW (W to E) at | 21:00 | hrs | Barisal | 411 | 411 |  | 0 |  | 24:00 |  | 30
| iii) Maximum : |  |  | 614 | MW at | 21:00 | hrs | Rangpur | 888 | 888 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32°C |  |  | Total | 12279 | 12220 |  | 59
B. |  | 2024-07-23 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 17535 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  | 4335 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 284.3888 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10542 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 23.2262 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8058 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.99 |  | (b) Today: | 94.79 |  | (c) Rule Curve: |  | 87.52
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-07-22 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 288 | 0 | 0 | 15 | 330 | 0 | 140 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 15 | 16 | 0 | 0 | 120 | 80 | 105 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 310 | 345 | 185 | 195 | 90 | 37 | 41 | 0 | 43 | 0 | 0 | 25 | 0 | 0 | 0 | 17 | 88 | 200 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 85 | 0 | 0 | 120 | 0 | 323 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 17 | 0 | 0 | 0 | 950 | 30 | 420 | 0 | 0 | 0 |  | 918 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 61 | 0 | 150 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1120 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 912 | 0 | 232 | 1112 | 0 | 0 | 0 | 0 |  | 7338 | 5808 | 13146 | 4265 | 918 | 2015 | 0 | 602 | 4957 | 200 | 0 | 71 | 88 | 0 | 30 | 166.17 | 94.99
2:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 295 | 0 | 0 | 15 | 330 | 0 | 140 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 15 | 16 | 0 | 0 | 118 | 80 | 105 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 310 | 345 | 185 | 195 | 90 | 37 | 41 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 84 | 200 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 120 | 0 | 323 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 17 | 0 | 0 | 0 | 844 | 26 | 422 | 0 | 0 | 0 |  | 917 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 815 | 0 | 200 | 1017 | 0 | 0 | 0 | 0 |  | 7211 | 5573 | 12784 | 4288 | 917 | 2047 | 0 | 573 | 4619 | 198 | 0 | 32 | 84 | 0 | 26 | 139.43 | 94.99
3:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 300 | 0 | 0 | 15 | 330 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 15 | 16 | 0 | 0 | 117 | 80 | 105 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 310 | 345 | 185 | 195 | 91 | 37 | 41 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 86 | 200 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 0 | 120 | 0 | 323 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 17 | 0 | 0 | 0 | 758 | 36 | 421 | 0 | 0 | 0 |  | 917 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 817 | 0 | 200 | 948 | 0 | 0 | 0 | 0 |  | 7096 | 5403 | 12499 | 4289 | 917 | 2048 | 0 | 544 | 4366 | 197 | 0 | 16 | 86 | 0 | 36 | 125.105 | 94.99
4:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 305 | 0 | 0 | 0 | 330 | 0 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 15 | 16 | 0 | 0 | 118 | 80 | 105 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 310 | 345 | 185 | 195 | 90 | 37 | 41 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 78 | 199 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 34 | 0 | 0 | 120 | 0 | 323 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 759 | 45 | 420 | 0 | 0 | 0 |  | 917 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 990 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 777 | 0 | 197 | 918 | 0 | 0 | 0 | 0 |  | 6924 | 5324 | 12248 | 4227 | 917 | 2063 | 0 | 421 | 4283 | 198 | 0 | 16 | 78 | 0 | 45 | 106.96 | 94.99
5:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 294 | 0 | 0 | 0 | 333 | 0 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 15 | 16 | 0 | 0 | 118 | 80 | 105 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 310 | 345 | 185 | 195 | 90 | 37 | 42 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 82 | 199 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 34 | 0 | 0 | 120 | 0 | 323 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 733 | 46 | 423 | 0 | 0 | 0 |  | 916 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 900 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 765 | 0 | 150 | 912 | 0 | 0 | 0 | 0 |  | 6890 | 5164 | 12054 | 4232 | 916 | 2054 | 0 | 405 | 4105 | 198 | 0 | 16 | 82 | 0 | 46 | 91.68 | 94.99
6:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 283 | 0 | 0 | 0 | 300 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 15 | 16 | 0 | 0 | 118 | 80 | 107 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 310 | 350 | 185 | 195 | 90 | 37 | 41 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 74 | 200 | 0 | 0 | 0 | 36 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 0 | 0 | 120 | 0 | 323 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 658 | 17 | 422 | 0 | 0 | 1 |  | 917 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 160 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 680 | 180 | 0 | 0 | 0 | 2 | 35 | 0 | 0 | 766 | 0 | 150 | 816 | 5 | 0 | 0 | 2 |  | 6637 | 4782 | 11419 | 4147 | 917 | 1952 | 0 | 388 | 3714 | 198 | 0 | 0 | 74 | 12 | 17 | 0 | 94.99
7:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 363 | 0 |  | 0 | 330 | 281 | 0 | 0 | 0 | 300 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 15 | 16 | 8 | 0 | 118 | 80 | 105 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 300 | 185 | 160 | 90 | 37 | 42 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 76 | 200 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 1 | 0 | 51 | 0 | 323 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 32 | 0 | 0 | 0 | 0 | 650 | 35 | 420 | 0 | 0 | 6 |  | 917 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 160 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 580 | 180 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 767 | 6 | 150 | 823 | 25 | 0 | 0 | 2 |  | 6315 | 4605 | 10920 | 3924 | 917 | 1791 | 0 | 288 | 3612 | 198 | 0 | 0 | 76 | 79 | 35 | 0 | 94.99
8:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 330 | 268 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 15 | 16 | 8 | 0 | 118 | 80 | 104 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 270 | 187 | 108 | 90 | 36 | 41 | 0 | 10 | 0 | 0 | 19 | 0 | 0 | 0 | 15 | 66 | 200 | 0 | 0 | 1 | 35 | 56 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 2 | 0 | 40 | 0 | 323 | 58 | 0 | 0 | 2 | 0 | 0 | 0 | 17 | 9 | 0 | 346 | 0 | 17 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 0 | 0 | 0 | 638 | 45 | 421 | 0 | 0 | 12 |  | 917 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 160 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 560 | 180 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 765 | 13 | 150 | 822 | 51 | 0 | 0 | 12 |  | 6078 | 4553 | 10631 | 3810 | 917 | 1613 | 0 | 242 | 3578 | 198 | 0 | 0 | 66 | 162 | 45 | 0 | 94.99
9:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 330 | 271 | 0 | 0 | 0 | 250 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 15 | 16 | 8 | 0 | 118 | 80 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 280 | 270 | 188 | 108 | 85 | 36 | 20 | 0 | 10 | 0 | 0 | 33 | 0 | 0 | 0 | 11 | 68 | 195 | 0 | 0 | 1 | 35 | 55 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 6 | 0 | 17 | 0 | 323 | 58 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 9 | 0 | 310 | 0 | 19 | 0 | 0 | 0 | 0 | 14 | 42 | 0 | 0 | 0 | 0 | 600 | 53 | 420 | 0 | 0 | 25 |  | 917 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 140 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 41 | 0 | 4 | 0 | 560 | 180 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 764 | 11 | 150 | 824 | 109 | 0 | 0 | 22 |  | 5993 | 4615 | 10608 | 3755 | 917 | 1585 | 0 | 250 | 3521 | 198 | 0 | 0 | 68 | 261 | 53 | 0 | 94.98
10:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 300 | 294 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 16 | 8 | 0 | 118 | 80 | 104 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 270 | 187 | 78 | 85 | 36 | 20 | 0 | 10 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 70 | 193 | 0 | 0 | 1 | 35 | 55 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 6 | 0 | 36 | 0 | 323 | 57 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 9 | 0 | 310 | 0 | 28 | 0 | 0 | 0 | 0 | 10 | 49 | 0 | 0 | 0 | 0 | 600 | 38 | 424 | 0 | 0 | 23 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 140 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 560 | 180 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 765 | 20 | 150 | 821 | 88 | 0 | 0 | 8 |  | 5980 | 4509 | 10489 | 3687 | 906 | 1568 | 0 | 269 | 3522 | 198 | 0 | 0 | 70 | 231 | 38 | 0 | 94.98
11:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 300 | 280 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 16 | 8 | 0 | 120 | 80 | 100 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 270 | 188 | 78 | 85 | 35 | 20 | 0 | 10 | 0 | 0 | 33 | 0 | 0 | 0 | 14 | 68 | 193 | 0 | 0 | 1 | 35 | 56 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 9 | 0 | 60 | 0 | 323 | 32 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 52 | 0 | 0 | 0 | 0 | 29 | 49 | 0 | 0 | 0 | 0 | 602 | 50 | 423 | 0 | 0 | 20 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 138 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 0 | 0 | 0 | 0 | 41 | 0 | 3 | 0 | 540 | 180 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 761 | 38 | 150 | 829 | 140 | 0 | 0 | 49 |  | 5999 | 4594 | 10593 | 3697 | 906 | 1549 | 0 | 248 | 3506 | 200 | 0 | 0 | 68 | 369 | 50 | 0 | 94.97
12:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 300 | 308 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 16 | 8 | 0 | 120 | 80 | 105 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 305 | 300 | 195 | 78 | 86 | 35 | 20 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 70 | 192 | 0 | 0 | 2 | 36 | 57 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 11 | 0 | 68 | 0 | 323 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 606 | 49 | 420 | 0 | 0 | 2 |  | 907 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 165 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 520 | 180 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 758 | 33 | 150 | 829 | 124 | 0 | 0 | 18 |  | 6038 | 4627 | 10665 | 3780 | 907 | 1676 | 0 | 164 | 3511 | 200 | 0 | 0 | 70 | 308 | 49 | 0 | 94.97
13:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 369 | 0 |  | 0 | 350 | 298 | 0 | 0 | 0 | 280 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 16 | 8 | 0 | 115 | 80 | 105 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 300 | 184 | 66 | 86 | 35 | 28 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 2 | 74 | 191 | 0 | 0 | 2 | 36 | 25 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 310 | 11 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 13 | 0 | 68 | 0 | 323 | 32 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 44 | 0 | 0 | 0 | 0 | 33 | 32 | 0 | 0 | 0 | 0 | 657 | 59 | 420 | 0 | 0 | 19 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 168 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 580 | 180 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 763 | 39 | 150 | 925 | 153 | 0 | 0 | 56 |  | 6261 | 4841 | 11102 | 3865 | 906 | 1727 | 0 | 164 | 3726 | 195 | 0 | 0 | 74 | 386 | 59 | 0 | 94.96
14:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 350 | 267 | 0 | 0 | 0 | 280 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 16 | 8 | 0 | 120 | 80 | 103 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 305 | 300 | 188 | 66 | 90 | 32 | 40 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 2 | 78 | 192 | 0 | 0 | 1 | 35 | 25 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 280 | 11 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 8 | 0 | 81 | 0 | 323 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 22 | 42 | 0 | 0 | 0 | 0 | 699 | 50 | 416 | 0 | 0 | 12 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 169 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 660 | 180 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 764 | 33 | 150 | 916 | 162 | 0 | 0 | 50 |  | 6173 | 4936 | 11109 | 3838 | 906 | 1660 | 0 | 209 | 3837 | 200 | 0 | 0 | 78 | 331 | 50 | 0 | 94.97
15:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 320 | 291 | 0 | 0 | 0 | 280 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 14 | 16 | 8 | 0 | 118 | 80 | 104 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 285 | 300 | 190 | 68 | 90 | 35 | 39 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 76 | 195 | 0 | 0 | 1 | 35 | 20 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 295 | 11 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 11 | 0 | 100 | 0 | 323 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 16 | 0 | 0 | 0 | 0 | 10 | 49 | 0 | 0 | 0 | 0 | 700 | 52 | 421 | 0 | 0 | 40 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 179 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 640 | 180 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 764 | 28 | 150 | 825 | 43 | 0 | 0 | 21 |  | 6174 | 4747 | 10921 | 3811 | 906 | 1700 | 0 | 226 | 3742 | 198 | 0 | 0 | 76 | 210 | 52 | 0 | 94.94
16:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 320 | 267 | 0 | 0 | 0 | 280 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 14 | 16 | 0 | 0 | 118 | 80 | 101 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 300 | 190 | 68 | 90 | 32 | 20 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 70 | 200 | 0 | 0 | 1 | 35 | 20 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 290 | 11 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 100 | 0 | 323 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 20 | 0 | 0 | 0 | 0 | 7 | 49 | 0 | 0 | 0 | 0 | 700 | 48 | 421 | 0 | 0 | 19 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 180 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 640 | 180 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 764 | 6 | 150 | 821 | 81 | 0 | 0 | 13 |  | 6074 | 4744 | 10818 | 3846 | 906 | 1628 | 0 | 208 | 3738 | 198 | 0 | 0 | 70 | 176 | 48 | 0 | 94.93
17:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 318 | 0 |  | 0 | 320 | 265 | 0 | 0 | 0 | 280 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 14 | 16 | 0 | 0 | 117 | 80 | 108 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 285 | 260 | 190 | 68 | 90 | 32 | 9 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 68 | 201 | 0 | 0 | 0 | 35 | 37 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 275 | 11 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 0 | 34 | 0 | 323 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 700 | 49 | 369 | 0 | 0 | 10 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 177 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 620 | 180 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 716 | 7 | 150 | 814 | 79 | 0 | 0 | 8 |  | 5812 | 4591 | 10403 | 3805 | 906 | 1522 | 0 | 116 | 3608 | 197 | 0 | 0 | 68 | 132 | 49 | 0 | 94.93
18:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 273 | 0 |  | 0 | 270 | 246 | 0 | 0 | 0 | 230 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 14 | 16 | 0 | 0 | 120 | 80 | 107 | 0 | 0 | 193 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 285 | 240 | 190 | 68 | 90 | 30 | 5 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 11 | 62 | 155 | 0 | 0 | 0 | 35 | 37 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 260 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 323 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 6 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 0 | 0 | 700 | 45 | 371 | 0 | 0 | 3 |  | 907 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 176 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 127 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 520 | 180 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 725 | 2 | 140 | 805 | 7 | 0 | 0 | 3 |  | 5464 | 4301 | 9765 | 3532 | 907 | 1414 | 0 | 74 | 3501 | 200 | 0 | 0 | 62 | 30 | 45 | 0 | 94.91
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.85 | 0
19:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 270 | 298 | 4 | 5 | 2 | 280 | 0 | 79 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 12 | 15 | 14 | 16 | 2 | 0 | 120 | 80 | 114 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 340 | 240 | 190 | 105 | 90 | 30 | 11 | 0 | 9 | 0 | 0 | 7 | 0 | 0 | 0 | 11 | 74 | 200 | 0 | 0 | 0 | 35 | 37 | 36 | 11 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 8 | 8 | 0 | 10 | 0 | 0 | 30 | 0 | 2 | 0 | 0 | 18 | 0 | 323 | 14 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 12 | 370 | 31 | 0 | 25 | 0 | 0 | 0 | 0 | 42 | 4 | 0 | 0 | 0 | 764 | 33 | 373 | 0 | 0 | 0 |  | 905 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 174 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 394 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 560 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 858 | 0 | 158 | 1048 | 0 | 0 | 0 | 0 |  | 6005 | 5201 | 11206 | 3735 | 905 | 1801 | 0 | 402 | 3998 | 200 | 0 | 58 | 74 | 0 | 33 | 0 | 94.88
19:30 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 255 | 16 | 16 | 30 | 336 | 0 | 77 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 12 | 15 | 14 | 16 | 8 | 0 | 120 | 80 | 110 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 305 | 295 | 215 | 105 | 90 | 30 | 40 | 0 | 30 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 74 | 200 | 0 | 0 | 0 | 35 | 37 | 45 | 26 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 12 | 8 | 0 | 30 | 0 | 0 | 120 | 0 | 50 | 0 | 0 | 130 | 0 | 323 | 75 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 12 | 391 | 33 | 0 | 35 | 0 | 0 | 0 | 0 | 105 | 30 | 0 | 0 | 0 | 767 | 29 | 371 | 0 | 0 | 0 |  | 907 | 0 | 346 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 178 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 384 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 750 | 220 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 859 | 0 | 180 | 1058 | 0 | 0 | 0 | 0 |  | 6925 | 5677 | 12602 | 4101 | 907 | 2010 | 0 | 981 | 4226 | 200 | 0 | 74 | 74 | 0 | 29 | 93.59 | 0
20:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 420 | 265 | 0 | 16 | 0 | 338 | 0 | 77 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 14 | 16 | 8 | 0 | 120 | 80 | 114 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 305 | 320 | 215 | 107 | 90 | 30 | 41 | 0 | 36 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 76 | 202 | 0 | 0 | 0 | 35 | 37 | 47 | 29 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 120 | 0 | 48 | 0 | 0 | 105 | 0 | 323 | 74 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 389 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 100 | 35 | 0 | 0 | 0 | 770 | 36 | 369 | 0 | 0 | 0 |  | 906 | 0 | 347 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 178 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 384 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 760 | 220 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 861 | 0 | 180 | 1065 | 0 | 0 | 0 | 0 |  | 6808 | 5667 | 12475 | 4152 | 906 | 2024 | 0 | 803 | 4246 | 200 | 0 | 32 | 76 | 0 | 36 | 100.275 | 94.89
21:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 304 | 0 | 0 | 0 | 332 | 0 | 78 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 7 | 16 | 8 | 0 | 120 | 80 | 112 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 330 | 320 | 212 | 107 | 90 | 30 | 44 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 78 | 201 | 0 | 0 | 0 | 35 | 48 | 53 | 33 | 163 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 119 | 0 | 50 | 0 | 0 | 193 | 0 | 323 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 378 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 35 | 0 | 0 | 0 | 800 | 21 | 373 | 0 | 0 | 0 |  | 905 | 0 | 385 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 63 | 0 | 176 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 414 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 790 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 860 | 0 | 180 | 1066 | 0 | 0 | 0 | 0 |  | 7006 | 5792 | 12798 | 4259 | 905 | 2130 | 0 | 850 | 4308 | 200 | 0 | 47 | 78 | 0 | 21 | 59.21 | 94.88
22:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 420 | 314 | 0 | 0 | 0 | 333 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 14 | 16 | 8 | 0 | 120 | 80 | 111 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 335 | 320 | 213 | 108 | 90 | 30 | 44 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 78 | 201 | 0 | 0 | 0 | 35 | 68 | 53 | 33 | 163 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 110 | 0 | 50 | 0 | 0 | 155 | 0 | 335 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 380 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 35 | 0 | 0 | 0 | 800 | 29 | 373 | 0 | 0 | 0 |  | 906 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 63 | 0 | 173 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 414 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 840 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 860 | 0 | 220 | 1064 | 0 | 0 | 0 | 0 |  | 7085 | 5881 | 12966 | 4373 | 906 | 2166 | 0 | 775 | 4393 | 200 | 0 | 46 | 78 | 0 | 29 | 32.47 | 94.87
23:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 306 | 0 | 0 | 0 | 335 | 0 | 201 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 15 | 16 | 8 | 0 | 120 | 80 | 110 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 320 | 320 | 214 | 108 | 91 | 30 | 45 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 84 | 200 | 0 | 0 | 0 | 35 | 68 | 25 | 36 | 163 | 0 | 20 | 0 | 0 | 70 | 18 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 110 | 0 | 52 | 0 | 0 | 136 | 0 | 335 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 380 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 35 | 0 | 0 | 0 | 806 | 41 | 371 | 0 | 0 | 0 |  | 906 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 5 | 63 | 0 | 172 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 414 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 880 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 858 | 0 | 260 | 1066 | 0 | 0 | 0 | 0 |  | 7275 | 5943 | 13218 | 4563 | 906 | 2149 | 0 | 758 | 4476 | 200 | 0 | 41 | 84 | 0 | 41 | 25.785 | 94.86
24:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 290 | 0 | 0 | 0 | 335 | 0 | 79 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 14 | 16 | 8 | 0 | 120 | 80 | 110 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 305 | 320 | 213 | 128 | 85 | 31 | 42 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 84 | 200 | 0 | 0 | 0 | 35 | 68 | 25 | 36 | 163 | 0 | 20 | 0 | 0 | 138 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 110 | 0 | 52 | 0 | 0 | 136 | 0 | 334 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 35 | 0 | 0 | 0 | 803 | 21 | 373 | 0 | 0 | 0 |  | 907 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 5 | 63 | 0 | 173 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 414 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 960 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 858 | 0 | 260 | 1054 | 0 | 0 | 0 | 0 |  | 7137 | 5972 | 13109 | 4454 | 907 | 2144 | 0 | 714 | 4544 | 200 | 0 | 41 | 84 | 0 | 21 | 30 | 94.85
KWH | 0 | 0 | 3328812 | 0 | 0 | 0 | 0 | 9039600 | 0 |  | 0 | 8994500 | 6857513 | 22080 | 13632 | 90789 | 7171613 | 0 | 2599000 | 0 | 20448 | 256800 | 0 | 0 | 0 | 0 | 0 | 7929 | 24193 | 0 | 340200 | 425520 | 329400 | 391600 | 115200 | 0 | 2872631 | 1932000 | 2400000 | 0 | 0 | 5257138 | 0 | 0 | 0 |  | 0 | 0 | 20348 | 0 | 0 | 0 | 0 | 681120 | 0 | 0 | 0 | 7592800 | 7482000 | 4722000 | 3128000 | 2106710 | 809784 | 780960 | 0 | 693980 | 0 | 0 | 418445 | 0 | 0 | 0 | 334240 | 1805760 | 4578240 | 0 | 0 | 12000 | 829000 | 1375800 | 232200 | 174168 | 3462545 | 0 | 27648 | 0 | 0 | 3614450 | 52000 | 0 | 0 | 7088000 | 269424 | 202752 | 0 | 37636 | 0 | 0 | 1228800 | 0 | 717408 | 72090 | 0 | 2310720 | 0 | 8169000 | 1234800 | 35520 | 0 | 22719 | 32618 | 0 | 0 | 264480 | 132720 | 11520 | 8142100 | 161280 | 281720 | 51840 | 0 | 0 | 9720 | 155536 | 1326720 | 250200 | 0 | 0 | 0 | 17481816 | 927840 | 9810909 | 0 | 0 | 203445 |  | 23226181 | 0 | 7475328 | 0 | 34560 | 0 | 0 | 0 | 0 | 0 | 0 | 2391000 | 180157 | 26784 | 0 | 0 | 0 | 0 | 0 | 57456 | 0 | 0 | 0 | 0 | 100173 | 0 | 0 | 105012 | 1425163 | 0 | 4017000 | 0 | 0 | 4278000 | 0 | 0 | 0 | 0 | 0 | 1706455 | 0 | 7987272 | 78720 | 0 | 0 | 0 | 824246 | 0 | 33863 | 0 | 19701700 | 4944716 | 0 | 0 | 4140 | 380160 | 755328 | 0 | 0 | 19134546 | 197267 | 4232700 | 22074546 | 1088130 | 0 | 2895 | 255000 |  | 158058129 | 126718498 | 284776627 | 97546626 | 23226181 | 45205131 | 0 | 10238336 | 97878380 | 4804631 | 0 | 434777 | 1805760 | 2708965 | 927840 | 0
Fuel Cost | 0 | 0 | 14280603.48 | 0 | 0 | 0 | 0 | 26034048 | 0 |  | 0 | 28602510 | 23452694.46 | 436300.8 | 254918.4 | 1599702.18 | 21873419.65 | 0 | 13904650 | 0 | 367041.6 | 4987056 | 0 | 0 | 0 | 0 | 0 | 124961.04 | 442489.97 | 0 | 255150 | 0 | 0 | 0 | 2063232 | 0 | 0 | 0 | 13104000 | 0 | 0 | 16770270.22 | 0 | 0 | 0 |  | 0 | 0 | 364432.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21183912 | 22894920 | 15677040 | 10478800 | 6804673.3 | 2728972.08 | 3420604.8 | 0 | 2782859.8 | 0 | 0 | 7557116.7 | 0 | 0 | 0 | 250680 | 11845785.6 | 14238326.4 | 0 | 0 | 0 | 3233100 | 5131734 | 1056510 | 792464.4 | 11841903.9 | 0 | 153446.4 | 0 | 0 | 10084315.5 | 342160 | 0 | 0 | 21901920 | 202068 | 154091.52 | 0 | 767774.4 | 0 | 0 | 23605248 | 0 | 12633554.88 | 0 | 0 | 40090992 | 0 | 21647850 | 23535288 | 666355.2 | 0 | 0 | 533304.3 | 0 | 0 | 5054212.8 | 2576095.2 | 205171.2 | 21657986 | 2753049.6 | 0 | 948153.6 | 0 | 0 | 173696.4 | 0 | 23907494.4 | 4238388 | 0 | 0 | 0 | 121848257.52 | 0 | 57884363.1 | 0 | 0 | 0 |  | 65265568.61 | 0 | 22052217.6 | 0 | 599616 | 0 | 0 | 0 | 0 | 0 | 0 | 7555560 | 853944.18 | 461756.16 | 0 | 0 | 0 | 0 | 0 | 965835.36 | 0 | 0 | 0 | 0 | 1794098.43 | 0 | 0 | 79494.084 | 15719547.89 | 0 | 33903480 | 0 | 0 | 14117400 | 0 | 0 | 0 | 0 | 0 | 5682495.15 | 0 | 23322834.24 | 1344537.6 | 0 | 0 | 0 | 16418980.32 | 0 | 0 | 0 | 127667016 | 15378066.76 | 0 | 0 | 0 | 0 | 13104940.8 | 0 | 0 | 139682185.8 | 0 | 31533615 | 145912749.06 | 0 | 0 | 0 | 0 |  | 708402119.48 | 683415939.044 | 1391818058.524 | 302094583.384 | 65265568.61 | 143885112.54 | 0 | 186464371.55 | 674151214.37 | 0 | 0 | 8111422.47 | 11845785.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 300 | 308 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 16 | 8 | 0 | 120 | 80 | 105 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 305 | 300 | 195 | 78 | 86 | 35 | 20 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 6 | 70 | 192 | 0 | 0 | 2 | 36 | 57 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 11 | 0 | 68 | 0 | 323 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 606 | 49 | 420 | 0 | 0 | 2 |  | 907 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 165 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 520 | 180 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 758 | 33 | 150 | 829 | 124 | 0 | 0 | 18 |  | 10665 | DayPeak
Yesterday Evening Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 304 | 0 | 0 | 0 | 332 | 0 | 78 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 7 | 16 | 8 | 0 | 120 | 80 | 112 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 330 | 320 | 212 | 107 | 90 | 30 | 44 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 78 | 201 | 0 | 0 | 0 | 35 | 48 | 53 | 33 | 163 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 119 | 0 | 50 | 0 | 0 | 193 | 0 | 323 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 378 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 35 | 0 | 0 | 0 | 800 | 21 | 373 | 0 | 0 | 0 |  | 905 | 0 | 385 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 63 | 0 | 176 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 414 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 790 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 860 | 0 | 180 | 1066 | 0 | 0 | 0 | 0 |  | 12798 | EvPeak
Forecast for Evening | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 300 | 24 | 17 | 55 | 335 | 0 | 100 | 50 | 90 | 130 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 20 | 22 | 25 | 30 | 8 | 0 | 120 | 80 | 112 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 70 | 80 | 50 | 25 | 50 | 0 | 40 | 0 | 0 | 0 | 330 | 340 | 210 | 200 | 90 | 35 | 43 | 0 | 51 | 0 | 36 | 33 | 0 | 0 |  | 17 | 100 | 200 | 0 | 0 | 0 | 35 | 56 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 300 | 0 | 0 | 150 | 0 | 96 | 0 | 50 | 193 | 150 | 330 | 75 | 50 | 105 | 0 | 52 | 54 | 110 | 17 | 28 | 62 | 380 | 50 | 0 | 162 | 104 | 0 | 17 | 0 | 115 | 35 | 0 | 108 | 0 | 1200 | 60 | 420 | 0 | 0 |  |  | 931 | 0 | 330 | 0 | 98 | 0 | 0 | 0 | 40 | 50 | 16 | 130 | 10 | 48 | 0 | 0 | 0 | 40 | 0 | 87 | 28 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 220 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 1000 | 0 | 307 | 1140 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 300 | 24 | 17 | 30 | 335 | 0 | 100 | 50 | 82 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 20 | 22 | 25 | 30 | 8 | 0 | 120 | 80 | 110 | 0 | 8 | 220 |  | 0 | 0 | 0 | 0 | 16 | 51 | 50 | 25 | 50 | 0 | 30 | 0 | 0 | 0 | 285 | 340 | 200 | 200 | 90 | 35 | 43 | 0 | 51 | 0 | 34 | 33 | 0 | 0 |  | 17 | 90 | 200 | 0 | 0 | 1.6 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 300 | 0 | 0 | 116 | 0 | 60 | 20 | 49 | 100 | 55 | 335 | 68 | 17 | 50 | 5 | 15 | 0 | 100 | 17 | 28 | 50 | 330 | 17 | 50 | 162 | 17 | 0 | 17 | 35 | 49 | 17 | 0 | 35 | 0 | 1100 | 44 | 420 | 0 | 0 | 70 |  | 931 | 0 | 330 | 0 | 48 | 0 | 0 | 0 | 30 | 0 | 8 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 63 | 0 | 200 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 400 | 17 | 0 | 35 | 0 | 100 | 0 | 8 | 70 | 1200 | 220 |  | 35 | 6 | 100 | 90 | 0 | 0 | 956 | 30 | 250 | 1140 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 380 | 284 | 0 | 0 | 0 | 280 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 14 | 16 | 0 | 0 | 118 | 80 | 110 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 285 | 270 | 215 | 78 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 66 | 200 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 4 | 0 | 34 | 0 | 335 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 15 | 0 | 0 | 0 | 0 | 9 | 35 | 0 | 0 | 0 | 0 | 607 | 34 | 373 | 0 | 0 | 21 | 0 | 905 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 174 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 540 | 180 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 719 | 12 | 150 | 813 | 43 | 0 | 0 | 14 | 0 |  |  |  | 142751757 | 23226181 | 0 | 97878380 | 10673113 | 1805760 | 2708965 | 927840 | 4804631 |  |  | 284776627
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 142.7518 | 23.2262 | 0 | 97.8784 | 10.6731 | 1.8058 | 2.709 | 0.92784 | 4.8046
| Minimum Generation |  | 10608 | 9:00
| Highest Generation |  | 13218 | 23:00 | [129 empty] | 0 | [73 empty] | 284.7766
| Day Peak Generation |  | 10665 | 12:00
| Evening Peak Generation |  | 12798 | 21:00 | [203 empty] | 202699852
| HVDC Max Flow |  | 918 | 1:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 905 | 21:00
| Load factor L.F |  | 89.77% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-23
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10665 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10542
Evening Peak Generation : |  |  | 12798 | MW Hour : | 21:00 | Available Max Generation : |  | 17535
E.P. Demand (at gen end) : |  |  | 12820 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13200
Maximum Generation : |  |  | 13218 | MW Hour : | 23:00 | Reserve(Generation end) |  | 4335
Total Gen. (MKWH) : |  |  | 284.7766 | System Load Factor : | 89.77% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 614 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-23
Actual : |  | 94.79 | Ft.(MSL) , | Rule curve : | 87.52 | Ft.( MSL )
Gas Consumed : |  | Total = | 1062.77 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 445979695.924
: |  |  | Coal : | 674151214.37 | Oil : | 194575794.02 | Total : | 1314706704.314
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4533.8427 |  |  | 0 | -26.93%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | -25.31%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | -24.96%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | -24.59%
Cumilla Area |  | 45 | 1080:00 | 1247.9061 |  |  | 0 | -24.82%
Mymensingh Area |  | 0 | 0:00 | 928.0993 |  |  | 0 | -24.5%
Sylhet Area |  | 14 | 336:00 | 520.2585 |  |  | 0 | -25.11%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | -24.44%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | -24.44%
Total |  | 59 |  | 13018.7703 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Remark
Time | Time
08:33 |  | Faridpur 230/132KV T-2 TR. S/D.
10:07 |  | Mahasthangarh 132/33 KV T2 Sync
11:00 |  | Faridpur 230/132KV T-2 TR. S/D Restored.
11:22 |  | Faridpur 230/132 KV T-1 TR. S/D.
12:46 |  | Faridpur 230/132KV T-1 TR. S/D Restored.
13:06 |  | Bhandaria 132/33 KV T-1 S/D |  |  |  |  | About 34 MW power interrupt.
| 14:38 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
15:17 |  | Fenchugong 230/132 KV (225/300 MVA) AT-1 was first time switched on at 15:17 hrs.
15:57 |  | 132/33 KV T-1 TR. S/D Restore Bhandaria S/S.
6:02 | - | Barapukuria-Bogura 230 kV Ckt-2 Scheduled S/D from Bogura 230/132kV end Due to 230kV Bus Upgradation work
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-22
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 140 | 3328812
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 408 | 9039600
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8994500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 22080 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 6857513 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 13632 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 90789 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 78 | 2599000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7171613
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 20448 | Reserve
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 0 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 256800 | Low Demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 7929 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 24193 | Low Demand
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 27 | 765720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 7 | 329400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 391600 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 115200 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 37636 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 50 | 717408 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 35520 | Low Demand
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 161280 | Low Demand
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 51840 | Reserve
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 155536
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 250200 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 1874 | 41438249
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 112 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 72090
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 200 | 4804631
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5257138
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Reserve
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 20348 | Reserve
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 0 | Reserve
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 681120
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22719
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 32618 | Reserve
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 11520 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 800 | 17481816
| Cox's Bazar Wind |  | IPP | 66 | 60 | 21 | 927840
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 373 | 9810909
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 203445
| Chattogram area Total |  |  |  | 4457 | 1755 | 41726194
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 4722000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7592800 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7482000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 809784 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 44 | 780960 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 107 | 3128000
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 693980 | Engine problem
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2106710 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 193 | 2310720 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 78 | 1805760
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 418445 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 334240 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 264480 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 132720 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1326720
| Cumilla Area Total |  |  |  | 2875 | 1621 | 33909319
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 201 | 4578240 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12000
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 119 | 1228800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 76 | 1234800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 281720
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 9720 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 396 | 7345280
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 35 | 829000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 48 | 1375800 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3462545
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 232200 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 33 | 174168 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 202752 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 27648 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 3614450 | Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 52000 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 269424 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7088000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 323 | 8169000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 378 | 8142100 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1360 | 33639087
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 23226181
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 34560 | Low Demand
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 385 | 7475328 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 78720 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 380160
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 860 | 19134546 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 2183 | 50329495
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 26784 | Reserve
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 180157
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2391000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 790 | 19701700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4944716
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 180 | 4232700
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 2895
| Barisal Area Total |  |  |  | 2236 | 1326 | 31479952
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 174 | 4278000
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 208 | 1706455 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7987272
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 100173 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 105012 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 57456 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 4140
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1066 | 22074546
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 255000
| Rajshahi Area Total |  |  |  | 3381 | 1882 | 36568054
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 63 | 1425163
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 176 | 4017000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 824246
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33863
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 92 | 755328
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 197267
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1088130
| Rangpur Area Total |  |  |  | 950 | 401 | 8340997
| Total |  |  |  | 26947 | 12798 | 284776627
| Eastern Grid Total |  |  |  | 16526 | 7006 | 158058129
| Western Grid Total |  |  |  | 10421 | 5792 | 126718498
| National Grid Total |  |  |  | 26947 | 12798 | 284776627
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2024-07-22
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9239.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4956 | MW
i) Dhaka area |  |  | 5062.28 |  | MW | i) Khulna area |  |  |  | 1892 | MW
ii) Chattogram area |  |  | 1308.2 |  | MW | ii) Barishal area |  |  |  | 477 | MW
iii) Cumilla area |  |  | 1290 |  | MW | iii) Rajshahi area |  |  |  | 1631 | MW
iv) Mymensingh area |  |  | 1039 |  | MW | iv) Rangpur area |  |  |  | 956 | MW
v) Sylhet area |  |  | 540 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14195.48 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 116 | 21:00 | 133 | Rahim | 34 | 02:00
2 | AKSML | 5 | 16:00 | 68 | Jashore | 153 | 19:30 | 134 | Rajbari | 82 | 23:00
3 | Aftabnagar | 40 | 23:00 | 69 | Jhenaidah | 153 | 19:30 | 135 | Rajendrapur | 84 | 13:00
4 | Agargaon | 110 | 19:30 | 70 | Joydebpur | 171 | 20:00 | 136 | Rajshahi | 149 | 23:00
5 | Agrabad | 94 | 19:30 | 71 | Joypurhat | 66 | 20:00 | 137 | Rajshahi-230 | 83 | 23:00
6 | Amnura | 85 | 22:00 | 72 | Juldah | 26 | 13:00 | 138 | Ramganj | 106 | 18:30
7 | Ashuganj | 87 | 01:00 | 73 | KSRM | 25 | 00:00 | 139 | Rampur | 43 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 257 | 02:00 | 140 | Rangamati | 18 | 19:00
9 | BSRM | 169 | 17:00 | 75 | Kachua | 78 | 15:00 | 141 | Rangpur | 137 | 12:00
10 | Bagerhat | 98 | 22:00 | 76 | Kallyanpur | 123 | 19:30 | 142 | Ruppur | 7.2 | 15:00
11 | Bakulia | 97 | 20:00 | 77 | Kalurghat | 34 | 15:00 | 143 | SSM | 13 | 00:00
12 | Banani | 40 | 00:00 | 78 | Kamrangirchar | 57.06 | 13:00 | 144 | Saidpur | 112 | 20:00
13 | Bangabhaban | 5 | 12:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 140 | 23:00
14 | Barapukuria | 71 | 21:00 | 80 | Kazla | 113 | 12:00 | 146 | Satmasjid | 119 | 19:30
15 | Barguna | 24 | 23:00 | 81 | Keranigonj | 82 | 23:00 | 147 | Savar | 208 | 10:00
16 | Barishal | 118 | 00:00 | 82 | Khagrachori | 36 | 21:00 | 148 | SevenRings | 17.35 | 18:00
17 | Barishal-230 | 110 | 22:00 | 83 | Khulna | 71 | 19:30 | 149 | ShahCement | 12 | 04:00
18 | Baroaulia | 61 | 01:00 | 84 | Khulshi | 184 | 00:00 | 150 | Shahjadpur | 89 | 20:00
19 | Baroirhat | 72 | 23:00 | 85 | Kishoreganj | 126 | 18:30 | 151 | Shahjibazar | 116 | 17:00
20 | Bashundhara | 171 | 00:00 | 86 | Kodda | 257 | 08:00 | 152 | Shahmirpur | 49 | 19:00
21 | BashundharaCement | 7 | 01:00 | 87 | Kulaura | 52 | 19:00 | 153 | Shariatpur | 98 | 22:00
22 | Beanibazar | 70 | 13:00 | 88 | Kurigram | 100 | 19:00 | 154 | Sherpur | 132 | 22:00
23 | Benapole | 76 | 14:00 | 89 | Kushtia | 144 | 00:00 | 155 | Shikalbaha | 33 | 19:00
24 | Bhaluka | 128 | 09:00 | 90 | Lalbag | 84 | 00:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 56.5 | 23:00 | 91 | Lalmonirhat | 66 | 21:00 | 157 | Shitalakhya | 87 | 12:00
26 | Bhangura | 40 | 21:00 | 92 | MI_Cement | 14.9 | 12:00 | 158 | Sholosohor | 44 | 15:00
27 | Bheramara(GK) | 72 | 22:00 | 93 | Madanganj | 38 | 13:00 | 159 | Shyampur | 158 | 13:00
28 | Bhulta | 220 | 22:00 | 94 | Madaripur | 124 | 23:00 | 160 | Siddhirganj | 128 | 15:00
29 | Bog-Sherpur | 70 | 20:00 | 95 | Madartek | 87.72 | 00:00 | 161 | Sirajganj | 124 | 21:00
30 | Bogura | 188 | 22:00 | 96 | Madunaghat | 58 | 00:00 | 162 | Sonargaon | 95 | 19:00
31 | Borhanuddin | 86 | 00:00 | 97 | Magura | 70 | 19:30 | 163 | Sreemongol | 77 | 22:00
32 | Brahmanbaria | 166 | 19:00 | 98 | Mahasthangarh | 86 | 22:00 | 164 | Sreepur | 103 | 19:00
33 | Cantonment | 136 | 19:30 | 99 | Manikganj | 119 | 22:00 | 165 | Srinagar | 50.7 | 21:00
34 | Chandpur | 67 | 20:00 | 100 | Maniknagar | 70 | 21:00 | 166 | Sunamganj | 52 | 06:00
35 | Chandraghona | 38 | 19:30 | 101 | Matarbari | 51 | 21:00 | 167 | Sylhet | 44 | 04:00
36 | Chapai | 83 | 21:00 | 102 | Matuail | 78 | 15:00 | 168 | Sylhet-132 | 129 | 17:00
37 | Charsaidpur | 41 | 08:00 | 103 | Millgate | 130 | 15:00 | 169 | TK | 35 | 21:00
38 | Chauddagram | 74 | 19:00 | 104 | Mirpur | 161 | 19:30 | 170 | Tangail | 197 | 23:00
39 | Chhatak | 35 | 14:00 | 105 | Mirsorai | 7 | 00:00 | 171 | Thakurgaon | 113 | 20:00
40 | Chowmuhani | 221 | 19:00 | 106 | Mirzapur | 38 | 21:00 | 172 | Tongi | 115 | 11:00
41 | Chuadanga | 116 | 21:00 | 107 | Mithapukur | 68 | 18:30 | 173 | Ullahpara | 28 | 21:00
42 | Coxsbazar | 133 | 19:30 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 61 | 01:00
43 | Cumilla(N) | 168 | 05:00 | 109 | Mogbazar | 110.3 | 00:00 | 175 | Uttara | 82 | 19:30
44 | Cumilla(S) | 203 | 19:00 | 110 | Mongla | 41 | 01:00 | 176 | UttaraNew | 69 | 23:00
45 | Daudkandi | 142 | 21:00 | 111 | Motijheel | 39 | 19:00 | 177 | Zigatola | 100 | 19:30
46 | Dhaka | 24 | 12:00 | 112 | Munshiganj | 112 | 19:30
47 | Dhamrai | 136 | 18:30 | 113 | Mymensingh | 231 | 01:00
48 | Dhanmondi | 124 | 12:00 | 114 | Naogaon | 149 | 21:00
49 | Dohazari | 106 | 21:00 | 115 | Narail | 63 | 23:00
50 | Faridpur | 178 | 22:00 | 116 | Narinda | 60 | 13:00
51 | Fatullah | 90 | 12:00 | 117 | Narshingdi | 164 | 11:00
52 | Fenchuganj | 42 | 05:00 | 118 | Natore | 154 | 20:00
53 | Feni | 124 | 19:00 | 119 | Nawabganj | 53 | 21:00
54 | GPH | 2 | 01:00 | 120 | Netrakona | 103 | 20:00
55 | Ghatail | 44 | 00:00 | 121 | New | 54.1 | 12:00
56 | Ghorashal | 48 | 07:00 | 122 | Niamatpur | 97 | 21:00
57 | Goalpara | 36 | 23:00 | 123 | Noapara | 50 | 19:30
58 | Gollamari | 88 | 13:00 | 124 | PHP | 8 | 00:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 385 | 07:00 | 372 | 21:00 | Kaliakoir | 369 | 18:30 | 360 | 17:00
| Ashuganj | 408 | 7:00 | 380 | 18:00 | Madunaghat_I | 400 | 17:00 | 386 | 9:00
| Bhulta | 396 | 03:00 | 384 | 15:00 | Meghnaghat | 381 | 03:00 | 370 | 12:00
| Bibiana | 396 | 19:30 | 387 | 12:00 | Payra | 408 | 08:00 | 401 | 21:00
| BIPTC | 403 | 06:00 | 393 | 00:00 | Rahanpur | 405 | 18:30 | 396 | 21:00
| Bogura | 398 | 19:00 | 384 | 22:00 | Rampal | 400 | 08:00 | 389 | 21:00
| Gopalganj | 395 | 07:00 | 383 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 227 | 03:00 | 218 | 15:00 | Haripur | 229 | 08:00 | 222 | 12:00
| AKSML | 237 | 03:00 | 230 | 22:00 | Hasnabad | 229 | 05:00 | 222 | 02:00
| Aminbazar | 228 | 05:00 | 218 | 13:00 | Hathazari | 237 | 03:00 | 230 | 13:00
| Ashuganj | 232 | 05:00 | 227 | 15:00 | Ishurdi | 234 | 18:30 | 225 | 21:00
| Ashuganj-400 | 233 | 6:00 | 222 | 13:00 | Jhenaidah | 225 | 18:00 | 214 | 19:30
| Baghabari | 230 | 09:00 | 222 | 20:00 | Kaliakoir | 228 | 03:00 | 222 | 17:00
| Barapukuria | 219 | 14:00 | 209 | 22:00 | Keranigonj | 227 | 03:00 | 218 | 15:00
| Barapukuria-230 | 219 | 14:00 | 209 | 22:00 | Khulna(S) | 230 | 18:30 | 219 | 22:00
| Barishal | 235 | 18:00 | 223 | 22:00 | Madunaghat_I | 234 | 13:00 | 222 | 10:00
| Bheramara | 232 | 18:30 | 222 | 21:00 | Maniknagar | 229 | 04:00 | 221 | 15:00
| Bhulta | 231 | 04:00 | 223 | 15:00 | Meghnaghat | 237 | 03:00 | 230 | 14:00
| Bibiana | 228 | 19:30 | 222 | 14:00 | Meghnaghat-400 | 233 | 05:00 | 225 | 12:00
| BIPTC | 233 | 08:00 | 223 | 21:00 | Mirsorai | 233 | 08:00 | 225 | 15:00
| Bogura | 224 | 10:00 | 217 | 22:00 | Rajshahi | 232 | 08:00 | 222 | 22:00
| Bogura-400 | 225 | 10:00 | 218 | 21:00 | Rampal | 229 | 18:30 | 219 | 21:00
| Borhanuddin | 238 | 10:00 | 232 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 232 | 03:00 | 226 | 15:00 | Rampura | 229 | 04:00 | 222 | 12:00
| Cumilla(N) | 227 | 01:00 | 222 | 12:00 | Shikalbaha | 236 | 00:00 | 230 | 16:00
| Faridpur | 233 | 07:00 | 223 | 23:00 | Shyampur | 229 | 04:00 | 221 | 15:00
| Fenchuganj | 230 | 07:00 | 226 | 11:00 | Siddhirganj | 231 | 04:00 | 223 | 11:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 236 | 10:00 | 228 | 22:00
| Ghorashal-230 | 228 | 06:00 | 220 | 15:00 | Sreepur | 230 | 08:00 | 222 | 21:00
| Gopalganj | 233 | 07:00 | 225 | 23:00 | Tongi | 226 | 05:00 | 219 | 15:00
| GPH | 235 | 04:00 | 230 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 06:00 | 130 | 00:00 | Kushtia | 135 | 08:00 | 128 | 21:00
| Agargaon | 132 | 07:00 | 125 | 15:00 | Lalbag | 132 | 03:00 | 127 | 12:00
| Agrabad | 134 | 00:00 | 130 | 10:00 | Lalmonirhat | 126 | 14:00 | 112 | 21:00
| AKS | 133 | 04:00 | 129 | 09:00 | Madanganj | 132 | 05:00 | 126 | 12:00
| Aminbazar | 137 | 04:00 | 127 | 15:00 | Madaripur | 132 | 09:00 | 126 | 21:00
| Amnura | 138 | 01:00 | 122 | 22:00 | Madartek | 134 | 05:00 | 129 | 11:00
| Ashuganj | 135 | 00:00 | 134 | 01:00 | Madunaghat | 136 | 05:00 | 131 | 16:00
| Bagerhat | 132 | 18:00 | 121 | 23:00 | Magura | 136 | 10:00 | 125 | 22:00
| Bakulia | 135 | 05:00 | 131 | 11:00 | Mahasthangarh | 128 | 10:00 | 122 | 21:00
| Banani | 134 | 06:00 | 130 | 00:00 | Manikganj | 126 | 19:30 | 118 | 12:00
| Bangabhaban | 129 | 01:00 | 124 | 12:00 | Maniknagar | 129 | 05:00 | 123 | 15:00
| Barapukuria | 131 | 14:00 | 121 | 22:00 | Matarbari | 126 | 07:00 | 115 | 22:00
| Barguna | 132 | 18:00 | 125 | 23:00 | Matuail | 130 | 03:00 | 125.5 | 15:00
| Barishal | 137 | 18:30 | 130 | 23:00 | Millgate | 131 | 05:00 | 124 | 12:00
| Barishal-230 | 138 | 10:00 | 131 | 21:00 | Mirpur | 135 | 02:00 | 128 | 21:00
| Baroaulia | 137 | 06:00 | 132 | 13:00 | Mirzapur | 127 | 18:30 | 120 | 12:00
| Baroirhat | 128 | 20:00 | 122 | 12:00 | Mithapukur | 126 | 14:00 | 117 | 04:00
| Bashundhara | 134 | 08:00 | 124 | 17:00 | MI_Cement | 132 | 03:00 | 126 | 15:00
| BashundharaCement | 132 | 05:00 | 126 | 12:00 | Modern | 135 | 05:00 | 130 | 15:00
| Beanibazar | 123 | 09:00 | 116 | 14:00 | Mogbazar | 135 | 05:00 | 122 | 19:00
| Benapole | 133 | 18:00 | 122 | 23:00 | Mongla | 132 | 18:00 | 121 | 00:00
| Bhaluka | 126 | 07:00 | 120 | 01:00 | Motijheel | 130 | 07:00 | 124 | 12:00
| Bhandaria | 134 | 11:00 | 120 | 23:00 | Munshiganj | 132 | 03:00 | 126 | 12:00
| Bhangura | 135 | 07:00 | 129 | 21:00 | Mymensingh | 133 | 18:30 | 111 | 08:00
| Bheramara | 135 | 18:30 | 130 | 21:00 | Naogaon | 127 | 18:30 | 117 | 22:00
| Bheramara(GK) | 135 | 10:00 | 130 | 00:00 | Narail | 137 | 18:00 | 127 | 19:30
| Bhulta | 123 | 07:00 | 117 | 15:00 | Narinda | 129 | 05:00 | 123 | 15:00
| Bog-Sherpur | 131 | 10:00 | 124 | 22:00 | Narshingdi | 122 | 04:00 | 116 | 12:00
| Bogura | 131 | 10:00 | 126 | 03:00 | Natore | 132 | 18:30 | 126 | 21:00
| Bogura-230 | 132 | 10:00 | 126 | 22:00 | Nawabganj | 132 | 04:00 | 126 | 21:00
| Brahmanbaria | 125 | 01:00 | 120 | 17:00 | Netrakona | 133 | 18:30 | 119 | 01:00
| Cantonment | 132 | 07:00 | 124 | 15:00 | New | 131 | 05:00 | 126 | 12:00
| Chandpur | 130 | 18:30 | 119 | 15:00 | Niamatpur | 134 | 18:00 | 129 | 22:00
| Chandraghona | 137 | 05:00 | 133 | 12:00 | Noapara | 135 | 18:00 | 126 | 19:30
| Chapai | 131 | 14:00 | 125 | 22:00 | Pabna | 133 | 08:00 | 127 | 21:00
| Charsaidpur | 132 | 04:00 | 126 | 16:00 | Palashbari | 125 | 18:30 | 116 | 22:00
| Chauddagram | 128 | 00:00 | 120 | 15:00 | Panchagarh | 133 | 19:00 | 113 | 01:00
| Chhatak | 123 | 16:00 | 120 | 11:00 | Patuakhali | 133 | 10:00 | 126 | 01:00
| Chowmuhani | 125 | 00:00 | 113 | 15:00 | Payra | 134 | 18:30 | 129 | 23:00
| Chuadanga | 130 | 07:00 | 117 | 21:00 | PHP | 127 | 00:00 | 119 | 15:00
| Coxsbazar | 125 | 05:00 | 115 | 20:00 | Postogola | 134 | 04:00 | 129 | 11:00
| Cumilla(N) | 131 | 18:30 | 126 | 15:00 | Purbachal | 135 | 18:30 | 124 | 12:00
| Cumilla(S) | 130 | 05:00 | 123 | 15:00 | Purbasadipur | 126 | 19:00 | 110 | 01:00
| Daudkandi | 127 | 01:00 | 122 | 14:00 | Rahanpur | 136 | 14:00 | 132 | 21:00
| Dhaka | 133 | 02:00 | 124 | 15:00 | Rahim | 130 | 03:00 | 126 | 00:00
| Dhamrai | 129 | 02:00 | 124 | 12:00 | Rajbari | 131 | 18:30 | 125 | 21:00
| Dhanmondi | 133.5 | 03:00 | 125 | 12:00 | Rajendrapur | 128 | 19:00 | 119 | 12:00
| Dohazari | 131 | 18:00 | 125 | 12:00 | Rajshahi | 132 | 08:00 | 127 | 21:00
| Faridpur | 130 | 05:00 | 125 | 23:00 | Rajshahi-230 | 134 | 08:00 | 118 | 22:00
| Fatullah | 133 | 04:00 | 127 | 12:00 | Ramganj | 126 | 23:00 | 115 | 15:00
| Fenchuganj | 128 | 07:00 | 125 | 14:00 | Rampur | 134 | 05:00 | 130 | 11:00
| Feni | 125 | 00:00 | 119 | 15:00 | Rampura | 134 | 05:00 | 128 | 12:00
| Ghatail | 127 | 18:30 | 120 | 12:00 | Rangamati | 136 | 06:00 | 131 | 14:00
| Ghorashal | 135 | 06:00 | 130 | 00:00 | Rangpur | 127 | 15:00 | 114 | 21:00
| Goalpara | 137 | 08:00 | 129 | 22:00 | Ruppur | 136 | 02:00 | 130 | 21:00
| Gollamari | 136 | 18:00 | 128 | 22:00 | Saidpur | 126 | 14:00 | 113 | 03:00
| Gopalganj | 132 | 09:00 | 126 | 19:30 | Satkhira | 133 | 18:00 | 120 | 22:00
| Gopalganj-400 | 133 | 18:30 | 128 | 21:00 | Satmasjid | 131 | 03:00 | 124 | 15:00
| Gulshan | 133 | 04:00 | 129 | 00:00 | Savar | 135 | 01:00 | 128 | 21:00
| Halishahar | 135 | 02:00 | 130 | 13:00 | SevenRings | 135 | 07:00 | 131 | 12:00
| Haripur | 130 | 01:00 | 126 | 12:00 | ShahCement | 132 | 04:00 | 126 | 16:00
| HaripurSBU | 130 | 03:00 | 126 | 12:00 | Shahjadpur | 138 | 10:00 | 132 | 21:00
| Hasnabad | 133 | 05:00 | 129 | 12:00 | Shahjibazar | 123 | 10:00 | 119 | 17:00
| Hathazari | 138 | 03:00 | 134 | 13:00 | Shahmirpur | 135 | 00:00 | 132 | 11:00
| Ishurdi | 136 | 07:00 | 130 | 22:00 | Shariatpur | 132 | 10:00 | 124 | 22:00
| Jaldhaka | 125 | 14:00 | 109 | 22:00 | Sherpur | 138 | 18:30 | 121 | 02:00
| Jamalpur | 139 | 18:30 | 124 | 02:00 | Shikalbaha | 124 | 00:00 | 120 | 11:00
| Jashore | 134 | 10:00 | 124 | 19:30 | Shikalbaha-230 | 137 | 06:00 | 131 | 16:00
| Jhenaidah | 138 | 08:00 | 128 | 19:30 | Shitalakhya | 132 | 03:00 | 126 | 15:00
| Jhenaidah-230 | 137 | 08:00 | 128 | 21:00 | Sholosohor | 135 | 05:00 | 131 | 11:00
| Joydebpur | 132 | 19:30 | 123 | 12:00 | Shyampur | 131 | 05:00 | 127 | 11:00
| Joypurhat | 125 | 18:30 | 114 | 22:00 | Shyampur-230 | 132 | 02:00 | 127 | 12:00
| Juldah | 135 | 00:00 | 133 | 08:00 | Siddhirganj | 131 | 02:00 | 126 | 15:00
| Kabirpur | 129 | 19:00 | 123 | 06:00 | Sirajganj | 131 | 15:00 | 124 | 21:00
| Kachua | 128 | 00:00 | 120 | 14:00 | Sonargaon | 129 | 03:00 | 122 | 12:00
| Kaliakoir | 131 | 02:00 | 124 | 18:00 | Sreemongol | 124 | 19:30 | 121 | 11:00
| Kallyanpur | 130 | 03:00 | 125 | 13:00 | Sreepur | 130 | 08:00 | 124 | 21:00
| Kalurghat | 136 | 05:00 | 131 | 13:00 | Srinagar | 132 | 05:00 | 126 | 15:00
| Kamrangirchar | 133 | 06:00 | 123 | 21:00 | SSM | 140 | 01:00 | 131 | 16:00
| Kaptai | 135 | 7:00 | 131 | 18:00 | Sunamganj | 122 | 16:00 | 117 | 06:00
| Kazla | 129 | 03:00 | 123 | 12:00 | Sylhet | 124 | 07:00 | 123 | 00:00
| Keranigonj | 133 | 07:00 | 127 | 15:00 | Sylhet-132 | 125 | 08:00 | 123 | 13:00
| Khagrachori | 134 | 05:00 | 130 | 00:00 | Tangail | 127 | 18:30 | 118 | 12:00
| Khulna | 135 | 18:00 | 127 | 19:30 | Thakurgaon | 131 | 19:00 | 110 | 01:00
| Khulna(S) | 136 | 18:00 | 128 | 22:00 | TK | 135 | 00:00 | 132 | 12:00
| Khulshi | 133 | 02:00 | 129 | 13:00 | Tongi | 132 | 02:00 | 127 | 11:00
| Kishoreganj | 129 | 10:00 | 122 | 19:00 | Ullahpara | 134 | 02:00 | 123 | 13:00
| Kodda | 129 | 07:00 | 119 | 12:00 | Ullon | 135 | 04:00 | 129 | 12:00
| KSRM | 137 | 06:00 | 131 | 14:00 | Uttara | 135 | 06:00 | 129 | 12:00
| Kulaura | 127 | 09:00 | 124 | 00:00 | UttaraNew | 134 | 02:00 | 128 | 15:00
| Kurigram | 124 | 14:00 | 111 | 22:00 | Zigatola | 133 | 07:00 | 127 | 13:00

## L-Curve
Date | 2024-07-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 824 | 7137 | 5972 | 13109 |  |  |  | QF-LDC-11
0:30 | 824 | 7237.5 | 5890 | 13127.5 | Date: | 2024-07-22
1:00 | 824 | 7338 | 5808 | 13146
1:30 | 791 | 7274.5 | 5690.5 | 12965
2:00 | 758 | 7211 | 5573 | 12784
2:30 | 754 | 7153.5 | 5488 | 12641.5 | [5 empty] | Gen. at Eve. Peak | 12798 | 12798 MW (21:00 )
3:00 | 750 | 7096 | 5403 | 12499 | [6 empty] | 21:00
3:30 | 745 | 7010 | 5363.5 | 12373.5 | [5 empty] | Gen. at Day Peak | 10665 | 10665 MW (12:00 )
4:00 | 740 | 6924 | 5324 | 12248 | [6 empty] | 12:00
4:30 | 744 | 6907 | 5244 | 12151 | [5 empty] | Highest Generation | 13218
5:00 | 748 | 6890 | 5164 | 12054 | [6 empty] | 23:00
5:30 | 757 | 6763.5 | 4973 | 11736.5
6:00 | 766 | 6637 | 4782 | 11419
6:30 | 730 | 6476 | 4693.5 | 11169.5
7:00 | 694 | 6315 | 4605 | 10920
7:30 | 785 | 6196.5 | 4579 | 10775.5
8:00 | 876 | 6078 | 4553 | 10631
8:30 | 961 | 6035.5 | 4584 | 10619.5
9:00 | 1046 | 5993 | 4615 | 10608
9:30 | 1078 | 5986.5 | 4562 | 10548.5
10:00 | 1110 | 5980 | 4509 | 10489
10:30 | 1116 | 5989.5 | 4551.5 | 10541
11:00 | 1122 | 5999 | 4594 | 10593
11:30 | 1220 | 6018.5 | 4610.5 | 10629
12:00 | 1318 | 6038 | 4627 | 10665
12:30 | 1269 | 6149.5 | 4734 | 10883.5
13:00 | 1220 | 6261 | 4841 | 11102
13:30 | 1192 | 6217 | 4888.5 | 11105.5
14:00 | 1164 | 6173 | 4936 | 11109
14:30 | 1218 | 6173.5 | 4841.5 | 11015
15:00 | 1272 | 6174 | 4747 | 10921
15:30 | 1296 | 6124 | 4745.5 | 10869.5
16:00 | 1320 | 6074 | 4744 | 10818
16:30 | 1337 | 5943 | 4667.5 | 10610.5
17:00 | 1354 | 5812 | 4591 | 10403
17:30 | 1296 | 5638 | 4446 | 10084
18:00 | 1238 | 5464 | 4301 | 9765
18:30 | 1225 | 5734.5 | 4751 | 10485.5
19:00 | 1212 | 6005 | 5201 | 11206
19:30 | 780 | 6925 | 5677 | 12602
20:00 | 712 | 6808 | 5667 | 12475 |  |  |  | Executive Engineer
20:30 | 663 | 6907 | 5729.5 | 12636.5 |  |  |  | Network Operation Division
21:00 | 614 | 7006 | 5792 | 12798
21:30 | 635 | 7045.5 | 5836.5 | 12882
22:00 | 656 | 7085 | 5881 | 12966 |  |  |  |  | Page 6 of 7
22:30 | 733 | 7180 | 5912 | 13092
23:00 | 810 | 7275 | 5943 | 13218
23:30 | 817 | 7206 | 5957.5 | 13163.5
24:00 | 824 | 7137 | 5972 | 13109
12798 MW (21:00 )
10665 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-22 |  | Energy |  | 284776627
[15 empty] | 2024-07-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4454 | 907 | 2144 | 0 | 714 | 4544 | 200 | 0 | 41 | 84 | 0 | 21 | 30
0:30 | 4359.5 | 912.5 | 2079.5 | 0 | 658 | 4750.5 | 200 | 0 | 56 | 86 | 0 | 25.5 | 98.085 |  |  | Date: | 44033
1:00 | 4265 | 918 | 2015 | 0 | 602 | 4957 | 200 | 0 | 71 | 88 | 0 | 30 | 166.17
1:30 | 4276.5 | 917.5 | 2031 | 0 | 587.5 | 4788 | 199 | 0 | 51.5 | 86 | 0 | 28 | 152.8 | [9 empty] | Total Energy | 284.7766 | 284.7766 | Total Energy Gen 284.777 MKWHr Energy Not Served 0.856 MKWHr Energy Requirement 285.633 MKWHr
2:00 | 4288 | 917 | 2047 | 0 | 573 | 4619 | 198 | 0 | 32 | 84 | 0 | 26 | 139.43 | [9 empty] | Energy not Served | 0.8564 | 0.8564
2:30 | 4288.5 | 917 | 2047.5 | 0 | 558.5 | 4492.5 | 197.5 | 0 | 24 | 85 | 0 | 31 | 132.2675 | [9 empty] | Energy Requirement | 285.633 | 285.633
3:00 | 4289 | 917 | 2048 | 0 | 544 | 4366 | 197 | 0 | 16 | 86 | 0 | 36 | 125.105
3:30 | 4258 | 917 | 2055.5 | 0 | 482.5 | 4324.5 | 197.5 | 0 | 16 | 82 | 0 | 40.5 | 116.0325 | [8 empty] | Shortage
4:00 | 4227 | 917 | 2063 | 0 | 421 | 4283 | 198 | 0 | 16 | 78 | 0 | 45 | 106.96
4:30 | 4229.5 | 916.5 | 2058.5 | 0 | 413 | 4194 | 198 | 0 | 16 | 80 | 0 | 45.5 | 99.32
5:00 | 4232 | 916 | 2054 | 0 | 405 | 4105 | 198 | 0 | 16 | 82 | 0 | 46 | 91.68
5:30 | 4189.5 | 916.5 | 2003 | 0 | 396.5 | 3909.5 | 198 | 0 | 8 | 78 | 6 | 31.5 | 45.84
6:00 | 4147 | 917 | 1952 | 0 | 388 | 3714 | 198 | 0 | 0 | 74 | 12 | 17 | 0
6:30 | 4035.5 | 917 | 1871.5 | 0 | 338 | 3663 | 198 | 0 | 0 | 75 | 45.5 | 26 | 0 | [7 empty] | Coal
7:00 | 3924 | 917 | 1791 | 0 | 288 | 3612 | 198 | 0 | 0 | 76 | 79 | 35 | 0
7:30 | 3867 | 917 | 1702 | 0 | 265 | 3595 | 198 | 0 | 0 | 71 | 120.5 | 40 | 0 | [6 empty] | Oil
8:00 | 3810 | 917 | 1613 | 0 | 242 | 3578 | 198 | 0 | 0 | 66 | 162 | 45 | 0
8:30 | 3782.5 | 917 | 1599 | 0 | 246 | 3549.5 | 198 | 0 | 0 | 67 | 211.5 | 49 | 0
9:00 | 3755 | 917 | 1585 | 0 | 250 | 3521 | 198 | 0 | 0 | 68 | 261 | 53 | 0
9:30 | 3721 | 911.5 | 1576.5 | 0 | 259.5 | 3521.5 | 198 | 0 | 0 | 69 | 246 | 45.5 | 0
10:00 | 3687 | 906 | 1568 | 0 | 269 | 3522 | 198 | 0 | 0 | 70 | 231 | 38 | 0
10:30 | 3692 | 906 | 1558.5 | 0 | 258.5 | 3514 | 199 | 0 | 0 | 69 | 300 | 44 | 0
11:00 | 3697 | 906 | 1549 | 0 | 248 | 3506 | 200 | 0 | 0 | 68 | 369 | 50 | 0
11:30 | 3738.5 | 906.5 | 1612.5 | 0 | 206 | 3508.5 | 200 | 0 | 0 | 69 | 338.5 | 49.5 | 0
12:00 | 3780 | 907 | 1676 | 0 | 164 | 3511 | 200 | 0 | 0 | 70 | 308 | 49 | 0
12:30 | 3822.5 | 906.5 | 1701.5 | 0 | 164 | 3618.5 | 197.5 | 0 | 0 | 72 | 347 | 54 | 0
13:00 | 3865 | 906 | 1727 | 0 | 164 | 3726 | 195 | 0 | 0 | 74 | 386 | 59 | 0
13:30 | 3865 | 906 | 1727 | 0 | 164 | 3726 | 195 | 0 | 0 | 74 | 386 | 59 | 0
14:00 | 3865 | 906 | 1727 | 0 | 164 | 3726 | 195 | 0 | 0 | 74 | 386 | 59 | 0
14:30 | 3838 | 906 | 1713.5 | 0 | 195 | 3734 | 196.5 | 0 | 0 | 75 | 298 | 55.5 | 0
15:00 | 3811 | 906 | 1700 | 0 | 226 | 3742 | 198 | 0 | 0 | 76 | 210 | 52 | 0
15:30 | 3828.5 | 906 | 1664 | 0 | 217 | 3740 | 198 | 0 | 0 | 73 | 193 | 50 | 0
16:00 | 3846 | 906 | 1628 | 0 | 208 | 3738 | 198 | 0 | 0 | 70 | 176 | 48 | 0
16:30 | 3825.5 | 906 | 1575 | 0 | 162 | 3673 | 197.5 | 0 | 0 | 69 | 154 | 48.5 | 0
17:00 | 3805 | 906 | 1522 | 0 | 116 | 3608 | 197 | 0 | 0 | 68 | 132 | 49 | 0
17:30 | 3668.5 | 906.5 | 1468 | 0 | 95 | 3554.5 | 198.5 | 0 | 0 | 65 | 81 | 47 | 0
18:00 | 3532 | 907 | 1414 | 0 | 74 | 3501 | 200 | 0 | 0 | 62 | 30 | 45 | 0
18:30 | 3633.5 | 906 | 1607.5 | 0 | 238 | 3749.5 | 200 | 0 | 29 | 68 | 15 | 39 | 0
19:00 | 3735 | 905 | 1801 | 0 | 402 | 3998 | 200 | 0 | 58 | 74 | 0 | 33 | 0
19:30 | 4101 | 907 | 2010 | 0 | 981 | 4226 | 200 | 0 | 74 | 74 | 0 | 29 | 50.1375
20:00 | 4152 | 906 | 2024 | 0 | 803 | 4246 | 200 | 0 | 32 | 76 | 0 | 36 | 100.275
20:30 | 4205.5 | 905.5 | 2077 | 0 | 826.5 | 4277 | 200 | 0 | 39.5 | 77 | 0 | 28.5 | 79.7425
21:00 | 4259 | 905 | 2130 | 0 | 850 | 4308 | 200 | 0 | 47 | 78 | 0 | 21 | 59.21
21:30 | 4316 | 905.5 | 2148 | 0 | 812.5 | 4350.5 | 200 | 0 | 46.5 | 78 | 0 | 25 | 45.84
22:00 | 4373 | 906 | 2166 | 0 | 775 | 4393 | 200 | 0 | 46 | 78 | 0 | 29 | 32.47
22:30 | 4468 | 906 | 2157.5 | 0 | 766.5 | 4434.5 | 200 | 0 | 43.5 | 81 | 0 | 35 | 29.1275
23:00 | 4563 | 906 | 2149 | 0 | 758 | 4476 | 200 | 0 | 41 | 84 | 0 | 41 | 25.785
23:30 | 4508.5 | 906.5 | 2146.5 | 0 | 736 | 4510 | 200 | 0 | 41 | 84 | 0 | 31 | 27.8925 |  |  | Max Temp. in Dhaka |  | 32°C
24:00 | 4454 | 907 | 2144 | 0 | 714 | 4544 | 200 | 0 | 41 | 84 | 0 | 21 | 30
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 284.777 MKWHr Energy Not Served 0.856 MKWHr Energy Requirement 285.633 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 120 | 118 | 117 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 120 | 120 | 115 | 120 | 118 | 118 | 117 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2872631
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1932000
3 | Chattogram TPP-1 | 105 | 105 | 105 | 105 | 105 | 107 | 105 | 104 | 100 | 104 | 100 | 105 | 105 | 103 | 104 | 101 | 108 | 107 |  | 114 | 110 | 114 | 112 | 111 | 110 | 110 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 2 | 6 | 6 | 9 | 11 | 13 | 8 | 11 | 3 | 1 | 0 | [8 empty] | 72090
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 223 | 222 | 223 | 222 | 218 | 218 | 220 | 220 | 221 | 221 | 193 |  | 220 | 221 | 221 | 220 | 220 | 222 | 223 | 5257138
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [24 empty] | 0 | 20348
12 | Hathazari 100 MW peaking PP | [26 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [25 empty] | 0 | 0
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 140 | 140 | 140 | 80 | 80 | 80 | 80 | 80 | 79 | 80 | 80 | 80 | 140 | 75 | 75 | 79 | 78 | 78 |  | 79 | 77 | 77 | 78 | 140 | 201 | 79 | 2599000
17 | Siddhirganj 335 MW CCPP | 330 | 330 | 330 | 330 | 333 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 280 | 280 | 230 |  | 280 | 336 | 338 | 332 | 333 | 335 | 335 | 7171613
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 10 | 30 | 0 |  |  |  | 0 | 37636
19 | Ashuganj 195 MW PP (APSCL-United) | 195 | 195 | 195 | 195 | 195 | 195 | 160 | 108 | 108 | 78 | 78 | 78 | 66 | 66 | 68 | 68 | 68 | 68 |  | 105 | 105 | 107 | 107 | 108 | 108 | 128 | 3128000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 130 | 130 |  | 130 | 130 | 130 | 140 | 140 | 200 | 200 | 3328812
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 950 | 844 | 758 | 759 | 733 | 658 | 650 | 638 | 600 | 600 | 602 | 606 | 657 | 699 | 700 | 700 | 700 | 700 |  | 764 | 767 | 770 | 800 | 800 | 806 | 803 | 17481816
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 35 | 35 | 35 | 32 | 35 | 32 | 32 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 809784
33 | Ashuganj 225 MW CCPP | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 187 | 188 | 187 | 188 | 195 | 184 | 188 | 190 | 190 | 190 | 190 |  | 190 | 215 | 215 | 212 | 213 | 214 | 213 | 4722000
34 | Ashuganj 450 MW CCPP(South) | 345 | 345 | 345 | 345 | 345 | 350 | 300 | 270 | 270 | 270 | 270 | 300 | 300 | 300 | 300 | 300 | 260 | 240 |  | 240 | 295 | 320 | 320 | 320 | 320 | 320 | 7482000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 280 | 280 | 280 | 280 | 280 | 305 | 285 | 305 | 285 | 280 | 285 | 285 |  | 340 | 305 | 305 | 330 | 335 | 320 | 305 | 7592800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision) | 41 | 41 | 41 | 41 | 42 | 41 | 42 | 41 | 20 | 20 | 20 | 20 | 28 | 40 | 39 | 20 | 9 | 5 |  | 11 | 40 | 41 | 44 | 44 | 45 | 42 | 780960
36 | Chandpur 150 MW CCPP | 90 | 90 | 91 | 90 | 90 | 90 | 90 | 90 | 85 | 85 | 85 | 86 | 86 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 91 | 85 | 2106710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 409 | 408 | 408 | 409 | 409 | 401 | 363 | 351 | 352 | 352 | 352 | 352 | 369 | 403 | 351 | 352 | 318 | 273 |  | 360 | 408 | 405 | 408 | 407 | 407 | 408 | 9039600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 330 | 330 | 330 | 300 | 300 | 300 | 350 | 350 | 320 | 320 | 320 | 270 |  | 270 | 420 | 420 | 420 | 420 | 450 | 450 | 8994500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 200 | 200 | 200 | 199 | 199 | 200 | 200 | 200 | 195 | 193 | 193 | 192 | 191 | 192 | 195 | 200 | 201 | 155 |  | 200 | 200 | 202 | 201 | 201 | 200 | 200 | 4578240
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 5 | 17 | 19 | 28 | 52 | 32 | 44 | 8 | 16 | 20 | 18 | 6 |  | 0 | [6 empty] | 281720
44 | Fenchugonj CCPP Phase-1 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 829000
45 | Fenchugonj CCPP Phase-2 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 56 | 57 | 25 | 25 | 20 | 20 | 37 | 37 |  | 37 | 37 | 37 | 48 | 68 | 68 | 68 | 1375800
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | [24 empty] | 20 | 20 | 27648
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 208 | 210 | 210 | 209 | 211 | 212 | 211 | 211 | 211 | 212 | 212 | 213 | 210 | 209 | 209 | 209 | 208 | 209 | [6 empty] | 70 | 138 | 3614450
51 | Sylhet 20 MW GTPP | [22 empty] | 17 | 18 | 18 | 0 | 52000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 202752
55 | Fenchugonj 51 MW PP (Barakatullah) | [19 empty] | 36 | 45 | 47 | 53 | 53 | 25 | 25 | 232200
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 12 |  | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 269424
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 295 | 295 | 300 | 305 | 290 | 280 | 270 | 275 | 280 | 275 | 280 | 310 | 280 | 295 | 290 | 275 | 260 |  | 290 | 285 | 275 | 290 | 315 | 315 | 310 | 7088000
| Bibiyana South 400 MW | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 346 | 310 | 310 | 310 | 330 | 377 | 310 | 310 | 310 | 310 | 310 |  | 370 | 391 | 389 | 378 | 380 | 380 | 387 | 8142100
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 10 | 17 | 0 |  |  |  | 0 | 24193
59 | Tangail Palli Power Gen 22 MW | [26 empty] | 0
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 88 | 84 | 86 | 78 | 82 | 74 | 76 | 66 | 68 | 70 | 68 | 70 | 74 | 78 | 76 | 70 | 68 | 62 |  | 74 | 74 | 76 | 78 | 78 | 84 | 84 | 1805760
64 | Malancha, Ctg. EPZ (United) | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 15 | 30 | 30 | 30 | 30 | 25 | 30 | 30 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 15 | 15 | 681120
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 11 | 0 | 14 | 6 | 2 | 2 | 11 | 15 | 15 | 11 |  | 11 | 11 | 17 | 17 | 17 | 17 | 17 | 334240
69 | Summit Ashulia | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 340200
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 425520
71 | Maona 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 7 | 14 | 15 | 14 | 329400
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 391600
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 264480
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | [12 empty] | 9 | 9 | 9 | 9 | 132720
| Manikgonj 162MW PP(MPGL) | [19 empty] | 25 | 35 | 17 | 0 |  |  | 0 | 51840
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 |  |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 115200
79 | Kodda 150 MW PP | 32 | 32 | 16 | 16 | 16 | [14 empty] | 16 | 32 | 32 | 32 | 16 | 16 | 16 | 256800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 16 | 16 | 7 |  | 7 | 16 | 16 | 16 | 16 | 16 | 16 | 418445
| Gazipur 100 MW PP | 17 | 17 | [23 empty] | 0 | 35520
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 1 | 3 | 2 |  | 1 | 3 | 1 | 1 | 1 | 0 | [8 empty] | 22719
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit) | [19 empty] | 5 | 16 | 16 | 0 |  |  | 0 | 13632
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 288 | 295 | 300 | 305 | 294 | 283 | 281 | 268 | 271 | 294 | 280 | 308 | 298 | 267 | 291 | 267 | 265 | 246 |  | 298 | 255 | 265 | 304 | 314 | 306 | 290 | 6857513
87 | Meghnaghat 100 MW(IEL) | [19 empty] | 4 | 16 | 0 |  |  |  | 0 | 22080
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | [15 empty] | 31 | 33 | 17 | 17 | 17 | 15 | 0 | 161280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima) | [19 empty] | 11 | 26 | 29 | 33 | 33 | 36 | 36 | 174168
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 9 | 30 | 36 | 43 | 43 | 43 | 43 | 693980
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 16 | 8 | 0 |  |  |  | 0 | 20448
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | [5 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | [16 empty] | 2 | 30 | 0 |  |  |  | 0 | 90789
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 7929
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3462545
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 12000
103 | Kamalaghat 54 MW PP(Banco Energy) | [25 empty] | 0 | 0
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 100 | 100 | 48 | 48 | 48 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 8 | 8 | 8 | 8 |  | 30 | 120 | 120 | 119 | 110 | 110 | 110 | 1228800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 85 | 70 | 70 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 2 | 50 | 48 | 50 | 50 | 52 | 52 | 717408
115 | Juldah 100 MW PP Unit-3 (Acorn) | [25 empty] | 0
116 | Chandpur 200 MW (Desh energy) | 120 | 120 | 120 | 120 | 120 | 120 | 51 | 40 | 17 | 36 | 60 | 68 | 68 | 81 | 100 | 100 | 34 | 17 |  | 18 | 130 | 105 | 193 | 155 | 136 | 136 | 2310720
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 323 |  | 323 | 323 | 323 | 323 | 335 | 335 | 334 | 8169000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 58 | 59 | 59 | 59 | 58 | 58 | 57 | 32 | 32 | 32 | 45 | 45 | 35 | 8 | 8 |  | 14 | 75 | 74 | 76 | 77 | 77 | 77 | 1234800
| Anwara 300 MW PP (United) | [19 empty] | 10 | 15 | 15 |  |  |  | 0 | 32618
| Juldah unit-2 (Acorn) | [19 empty] | 12 | 12 | 0 |  |  |  | 0 | 11520
| Anlima Energy Ltd. | [25 empty] | 0 | 0
| Bhairob 54.5 MW | [25 empty] | 0 | 9720
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 6 | 14 | 10 | 29 | 35 | 33 | 22 | 10 | 7 | 0 | 2 | [8 empty] | 155536
| Chandpur 115(Doreen) | 53 | 48 | 36 | 33 | 33 | 33 | 32 | 32 | 42 | 49 | 49 | 32 | 32 | 42 | 49 | 49 | 50 | 34 |  | 42 | 105 | 100 | 115 | 102 | 104 | 92 | 1326720
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | [16 empty] | 4 | 30 | 35 | 35 | 35 | 35 | 35 | 250200
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 30 | 26 | 36 | 45 | 46 | 17 | 35 | 45 | 53 | 38 | 50 | 49 | 59 | 50 | 52 | 48 | 49 | 45 |  | 33 | 29 | 36 | 21 | 29 | 41 | 21 | 927840
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 6 | 12 | 25 | 23 | 20 | 2 | 19 | 12 | 40 | 19 | 10 | 3 | [8 empty] | 203445
| Matarbari 2*600 MW (CPGCL) | 420 | 422 | 421 | 420 | 423 | 422 | 420 | 421 | 420 | 424 | 423 | 420 | 420 | 416 | 421 | 421 | 369 | 371 |  | 373 | 371 | 369 | 373 | 373 | 371 | 373 | 9810909
120 | Eastern Zone Total | 7338 | 7211 | 7096 | 6924 | 6890 | 6637 | 6315 | 6078 | 5993 | 5980 | 5999 | 6038 | 6261 | 6173 | 6174 | 6074 | 5812 | 5464 |  | 6005 | 6925 | 6808 | 7006 | 7085 | 7275 | 7137 | 158058129
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [20 empty] | 16 | 16 | 16 |  |  | 0 | 34560
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [20 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 78720
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 28 | 43 | 49 | 41 | 26 | 46 | 19 | 29 | 35 | 23 | 4 | 6 | [8 empty] | 380160
131 | Rampal 1320 MW (BIFPCL) | 912 | 815 | 817 | 777 | 765 | 766 | 767 | 765 | 764 | 765 | 761 | 758 | 763 | 764 | 764 | 764 | 716 | 725 |  | 858 | 859 | 861 | 860 | 860 | 858 | 858 | 19134546
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4944716
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 0 |  |  |  | 0 | 26784
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 232 | 200 | 200 | 197 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 140 |  | 158 | 180 | 180 | 180 | 220 | 260 | 260 | 4232700
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2895
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 120 | 126 | 126 | 126 | 126 | 126 | 2391000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 9 | 10 | 10 | 8 | 0 | 6 | 6 | 6 | 6 | 5 | 5 | 7 | 7 | 6 | 6 | 6 |  | 8 | 8 | 8 | 10 | 10 | 9 | 8 | 180157
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 918 | 917 | 917 | 917 | 916 | 917 | 917 | 917 | 917 | 906 | 906 | 907 | 906 | 906 | 906 | 906 | 906 | 907 |  | 905 | 907 | 906 | 905 | 906 | 906 | 907 | 23226181
147 | Bheramara 410 MW CCPP | 347 | 349 | 349 | 349 | 349 | 347 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 180 |  | 220 | 346 | 347 | 385 | 376 | 367 | 350 | 7475328
148 | Payra 1320 MW | 1120 | 1100 | 1000 | 990 | 900 | 680 | 580 | 560 | 560 | 560 | 540 | 520 | 580 | 660 | 640 | 640 | 620 | 520 |  | 560 | 750 | 760 | 790 | 840 | 880 | 960 | 19701700
149
150 | Barapukuria TPP Unit-1 | 61 | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 63 | 62 | 63 | 63 | 63 | 63 | 63 | 62 | 62 | 64 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1425163
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 140 | 140 | 138 | 165 | 168 | 169 | 179 | 180 | 177 | 176 |  | 174 | 178 | 178 | 176 | 173 | 172 | 173 | 4017000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [14 empty] | 1 | 0 | 1 | 0 | [8 empty] | 4140
| Sirajganj 68 MW Solar Park | [5 empty] | 2 | 2 | 12 | 22 | 8 | 49 | 18 | 56 | 50 | 21 | 13 | 8 | 3 | [8 empty] | 255000
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 214 | 214 | 214 | 160 | 140 | 140 | 140 | 140 | 144 | 155 | 166 | 181 | 175 | 176 | 140 |  | 140 | 163 | 166 | 174 | 186 | 184 | 177 | 4278000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | [9 empty] | 2 | 2 | 3 | 10 | 31 | 49 | 86 | 100 | 127 |  | 168 | 176 | 183 | 208 | 209 | 209 | 210 | 1706455
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 326 | 346 | 343 | 346 | 342 | 319 | 325 | 250 | 250 | 250 | 250 | 345 | 330 | 315 | 340 | 317 | 250 | 230 |  | 394 | 384 | 384 | 414 | 414 | 414 | 414 | 7987272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 105012
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | 22 | [21 empty] | 15 | 30 | 25 | 25 | 100173
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 42 | 42 | 0 |  |  |  | 0 | 57456
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW | [25 empty] | 0 | 0
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 41 | 35 | 41 | [8 empty] | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 824246
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 4 | 3 | 3 | 5 | 7 | 3 | 3 | 2 | 3 | 1 | [8 empty] | 33863
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | [13 empty] | 72 | 99 | 112 | 92 | 92 | 92 | 75 | 755328
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 13 | 11 | 20 | 38 | 33 | 39 | 33 | 28 | 6 | 7 | 2 |  | 0 | [6 empty] | 197267
| Adani Power Jharkhanda Ltd | 1112 | 1017 | 948 | 918 | 912 | 816 | 823 | 822 | 824 | 821 | 829 | 829 | 925 | 916 | 825 | 821 | 814 | 805 |  | 1048 | 1058 | 1065 | 1066 | 1064 | 1066 | 1054 | 22074546
178 | Teesta Solar Limited | [5 empty] | 5 | 25 | 51 | 109 | 88 | 140 | 124 | 153 | 162 | 43 | 81 | 79 | 7 | [8 empty] | 1088130