## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-25 | Thursday
|  | Date (day): | 2024-07-25 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15096.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16521 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-24 | 2024-07-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Machine problem
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage |  | 16-07-24
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 401 | 377 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 340 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 24 | 24 | 24 | 76 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 302 | 126 | 300 | 300 | 35 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 34 | 17 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 12 | 57 | 50 | 57 | 43 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 272 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 82 | 82 | 82 | 20 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 132 | 32 | 132 |  | 17 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 20 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 44 | 42 | 44 |  | 36 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 24 | 24 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 30 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 295 | 200 | 300
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 94 | 90 | 94 |  | 55 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 17 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 40 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 105 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 16 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1988 | 2380 | 2449 | 2782 | 2226 | 1152
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 5 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 20 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 205 | 203 | 200 | 200 | 30 |  | Low water lavel
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 223 | 220 | 220
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 50 | 100
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 75 | 16 | 75 | 23 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 50 | 50 | 50 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 45 | 49 | 49 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 5 | 20
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 4 | 25 | 25 | 83 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 49 | 15 | 52 | 248 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 0 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 100 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 50 | 50 | 50 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 17 | 104 |  | 12 | Engine problem
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 72 | 35 | 163
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 949 | 1100 | 1100 | 1200
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 11 | 5 | 44 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 422 | 419 | 420 | 420
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 72 | 0 | 70 | 0 |  |  | On test
| Chattogram area Total |  |  |  |  | 4517 | 4457 | 2108 | 2422 | 2570 | 3062 | 731 | 393
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 213 | 210 | 210
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 280 | 290 | 300 | 60 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 280 | 280 | 300 | 60 |  | Gas shortage
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 23 | 230 | 230 | 170 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 24 | 25 | 25 | 25 | 20 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 44 | 42 | 42 | 42 | 13 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 108 | 70 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 60 | 55 | 100 |  | 50 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 34 | 36 |  | 16 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 50 | 50 | 50 | 113 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 180 | 160 | 100 | 150 | 50 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 86 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 32 | 33 | 33
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 18 | 17 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 88 | 17 | 17 | 97 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 5 | 53 | 28 | 53 | 60 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 29 | 73 | 49 | 75 | 40 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2883 | 2875 | 1475 | 1640 | 1601 | 1790 | 878 | 106
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 133 | 103 | 80 | 100 | 102 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 123 | 100 | 120 | 80 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 64 | 78 | 68 | 78 | 37 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 17 | 17 | 17
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 284 | 321 | 316.6 | 315 | 102 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 36 | 35 | 35 | 35 |  | 35 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 68 | 68 | 68 | 68 |  | 22 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 15 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 15 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 2 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 133 | 135 | 136 | 136 |  | 95 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 11 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 270 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 336 | 323 | 300 | 325 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 351 | 341 | 330 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1421 | 1379 | 1352 | 1397 | 121 | 498
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 907 | 907 | 931 | 931
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 47 | 48 | 98 | 17 |  | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 35 | 0 | 50 |  | 59 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 325 | 303 | 300 | 300 | 110 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 8 | 8 | 32 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 35 | 70 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 601 | 605 | 620 | 620 | 614 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1919 | 1962 | 2054 | 2082 | 1530 | 73
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 28 | 16 | 48 | 62 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 7 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 80 | 80 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1010 | 1200 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 180 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 35 | 35 | 115 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 200 | 250 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1607 | 1575 | 1811 | 1994 | 177 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 20 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 0 |  | 71 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 159 | 158 | 180 | 180 | 30 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 147 | 150 | 150 | 70 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 395 | 310 | 400 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 25 | 35 |  | 15 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 87 | 50 | 87 |  | 17 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 6 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1208 | 1458 | 1420 | 1450
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 65 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 2009 | 2306 | 2421 | 2661 | 543 | 121
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 60 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 152 | 170 | 173 |  | 101 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 18 | 106 | 34 | 90 | 23 |  | Fuel shortage
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 17 | 98 | 90 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 209 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 508 | 416 | 522 | 438 | 63 | 211
| Total |  |  |  |  | 28098 | 26947 | 13319 | 14401 | 15096.6 | 16521 | 6371 | 2618
A. |  | 2024-07-24 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 14605 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 11428 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14600 | MW
3 | Day peak Generation : |  |  | 13319 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13930 | MW
4 | Evening peak Generation : |  |  | 14401 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 190 | MW
5 | Total Energy Generation : |  | 315.2692 | MKWHr | By Solar | 3.2487 | MKWHr
| By Gas : | 136.7786 | MKWHr |  | By Oil: | 30.2457 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 114.2479 | MKWHr |  | By Hydro: | 6.7879 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.16896 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6371 | MW | Dhaka | 4995 | 4987 |  | 8 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2618 | MW | Chittagong | 1183 | 1183 |  | 0 |  | 19:00 |  | 75.445
|  |  | Total = |  |  | 8989 | MW | Khulna | 1691 | 1691 |  | 0 |  | 19:30 |  | 190.045
7 | Total Gas Supplied : |  |  | 1011.63 | MMCFD |  |  | Rajshahi | 1472 | 1472 |  | 0 |  | 20:00 |  | 158.53
8 | Fuel Cost : | i) Gas : | Taka | 410983370.582 | ii) Oil : | Taka | 550811369.38 | Comilla | 1313 | 1258 |  | 55 |  | 21:00 |  | 196
|  | iii) Coal : | Taka | 780333852.92 | Total | Taka | 1742128592.882 | Mymensingh | 1223 | 1116 |  | 107 |  | 22:00 |  | 186.225
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 618 | 598 |  | 20 |  | 23:00 |  | 322.79
| ii) During Peak Demand : |  |  | 780 | MW (W to E) at | 19:30 | hrs | Barisal | 473 | 473 |  | 0 |  | 24:00 |  | 390.595
| iii) Maximum : |  |  | 614 | MW at | 21:00 | hrs | Rangpur | 962 | 962 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.3°C |  |  | Total | 13930 | 13740 |  | 190
B. |  | 2024-07-25 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16521 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13900 | MW
4 | Reserve(Generation end) |  |  |  |  | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 328.1131 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12075 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.978 | MKWHr. | ii) HVDC Flow at Peak Time |  | 907 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8134 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 94.56 |  | (b) Today: | 94.35 |  | (c) Rule Curve: |  | 87.84

## YesterdayGen
2024-07-24 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 263 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 0 | 0 | 120 | 80 | 105 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 275 | 216 | 184 | 90 | 25 | 45 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 82 | 205 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 275 | 12 | 2 | 0 | 0 | 0 | 0 | 96 | 0 | 108 | 0 | 0 | 200 | 0 | 370 | 58 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 901 | 14 | 420 | 0 | 0 | 0 |  | 906 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 8 | 62 | 0 | 176 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 310 | 0 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 1230 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 786 | 0 | 307 | 1351 | 0 | 0 | 0 | 0 |  | 7138 | 6308 | 13446 | 4178 | 906 | 2013 | 0 | 768 | 5233 | 200 | 0 | 52 | 82 | 0 | 14 | 80 | 94.61
2:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 274 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 0 | 0 | 120 | 80 | 108 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 215 | 184 | 90 | 25 | 45 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 74 | 205 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 0 | 0 | 0 | 70 | 0 | 113 | 0 | 0 | 200 | 0 | 371 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 16 | 17 | 0 | 0 | 0 | 804 | 7 | 421 | 0 | 0 | 0 |  | 907 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 160 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 310 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 1244 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 625 | 0 | 307 | 1364 | 0 | 0 | 0 | 0 |  | 6924 | 6037 | 12961 | 4122 | 907 | 1978 | 0 | 686 | 4987 | 200 | 0 | 0 | 74 | 0 | 7 | 43 | 94.6
3:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 254 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 0 | 0 | 119 | 80 | 110 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 216 | 185 | 90 | 25 | 46 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 78 | 204 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 200 | 0 | 371 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 0 | 0 | 0 | 801 | 0 | 421 | 0 | 0 | 0 |  | 907 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 164 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 310 | 0 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 1200 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 624 | 0 | 250 | 1347 | 0 | 0 | 0 | 0 |  | 6819 | 5898 | 12717 | 4065 | 907 | 1960 | 0 | 639 | 4869 | 199 | 0 | 0 | 78 | 0 | 0 | 37 | 94.59
4:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 450 | 290 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 0 | 0 | 118 | 80 | 110 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 213 | 160 | 85 | 24 | 46 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 76 | 205 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 81 | 0 | 0 | 200 | 0 | 371 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 17 | 0 | 0 | 0 | 802 | 5 | 421 | 0 | 0 | 0 |  | 907 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 170 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 344 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 1080 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 630 | 0 | 250 | 1264 | 0 | 0 | 0 | 0 |  | 6711 | 5674 | 12385 | 3953 | 907 | 2026 | 0 | 541 | 4679 | 198 | 0 | 0 | 76 | 0 | 5 | 25 | 94.58
5:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 380 | 287 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 0 | 0 | 117 | 80 | 110 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 213 | 160 | 85 | 24 | 44 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 76 | 202 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 65 | 0 | 0 | 198 | 0 | 371 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 803 | 0 | 422 | 0 | 0 | 0 |  | 907 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 170 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 180 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 630 | 0 | 200 | 1263 | 0 | 0 | 0 | 0 |  | 6611 | 5477 | 12088 | 3964 | 907 | 1962 | 0 | 451 | 4531 | 197 | 0 | 0 | 76 | 0 | 0 | 0 | 94.57
6:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 357 | 0 |  | 0 | 340 | 289 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 0 | 0 | 118 | 80 | 112 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 320 | 310 | 213 | 110 | 86 | 24 | 41 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 17 | 74 | 202 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 200 | 0 | 371 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 17 | 17 | 0 | 0 | 0 | 802 | 0 | 422 | 0 | 0 | 2 |  | 907 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 172 | 0 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 557 | 1 | 200 | 1130 | 2 | 0 | 0 | 0 |  | 6452 | 5044 | 11496 | 3984 | 907 | 1808 | 0 | 370 | 4146 | 198 | 0 | 0 | 74 | 9 | 0 | 0 | 94.56
7:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 340 | 296 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 8 | 0 | 119 | 80 | 111 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 285 | 270 | 212 | 110 | 90 | 24 | 46 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 64 | 203 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 1 | 0 | 200 | 0 | 371 | 35 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 4 | 0 | 0 | 0 | 0 | 3 | 17 | 17 | 0 | 0 | 0 | 802 | 1 | 422 | 0 | 0 | 17 |  | 907 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 172 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 780 | 180 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 562 | 4 | 200 | 1117 | 10 | 0 | 0 | 6 |  | 6403 | 5054 | 11457 | 3909 | 907 | 1828 | 0 | 378 | 4117 | 199 | 0 | 0 | 64 | 54 | 1 | 0 | 94.55
8:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 340 | 0 |  | 0 | 340 | 300 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 15 | 33 | 8 | 0 | 119 | 80 | 109 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 290 | 275 | 211 | 110 | 90 | 24 | 46 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 62 | 200 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 50 | 7 | 0 | 200 | 0 | 373 | 35 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 6 | 0 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 803 | 1 | 422 | 0 | 0 | 17 |  | 907 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 135 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 780 | 180 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 562 | 7 | 200 | 1113 | 27 | 0 | 0 | 18 |  | 6370 | 5058 | 11428 | 3925 | 907 | 1763 | 0 | 382 | 4077 | 199 | 0 | 0 | 62 | 112 | 1 | 0 | 94.54
9:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 379 | 0 |  | 0 | 340 | 302 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 15 | 33 | 8 | 0 | 120 | 80 | 110 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 320 | 305 | 211 | 110 | 80 | 24 | 46 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 70 | 200 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 56 | 9 | 0 | 200 | 0 | 335 | 39 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 13 | 0 | 0 | 0 | 0 | 14 | 17 | 17 | 0 | 0 | 0 | 852 | 1 | 422 | 0 | 0 | 56 |  | 907 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 133 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 830 | 180 | 0 | 0 | 1 | 35 | 0 | 0 | 0 | 561 | 26 | 200 | 1117 | 57 | 0 | 0 | 32 |  | 6646 | 5258 | 11904 | 4119 | 907 | 1773 | 0 | 405 | 4177 | 200 | 0 | 0 | 70 | 252 | 1 | 0 | 94.53
10:00 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 380 | 302 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 17 | 32 | 8 | 0 | 120 | 80 | 113 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 300 | 285 | 211 | 110 | 75 | 24 | 44 | 0 | 35 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 72 | 167 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 78 | 3 | 0 | 195 | 0 | 335 | 58 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 53 | 0 | 0 | 0 | 0 | 5 | 16 | 17 | 0 | 0 | 0 | 900 | 4 | 420 | 0 | 0 | 35 |  | 907 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 160 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1020 | 220 | 0 | 0 | 2 | 36 | 0 | 0 | 0 | 562 | 22 | 200 | 1210 | 140 | 0 | 0 | 27 |  | 6604 | 5659 | 12263 | 3881 | 907 | 1879 | 0 | 440 | 4532 | 200 | 0 | 16 | 72 | 332 | 4 | 0 | 94.52
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 305 | 0 | 0 | 5 | 327 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 15 | 17 | 24 | 8 | 0 | 120 | 80 | 111 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 320 | 305 | 209 | 108 | 75 | 22 | 44 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 72 | 162 | 0 | 0 | 2 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 305 | 11 | 8 | 0 | 7 | 0 | 0 | 35 | 0 | 88 | 9 | 12 | 180 | 0 | 336 | 63 | 17 | 0 | 2 | 0 | 0 | 0 | 17 | 0 | 15 | 365 | 17 | 9 | 22 | 0 | 0 | 0 | 4 | 16 | 17 | 0 | 0 | 0 | 898 | 9 | 420 | 0 | 0 | 73 |  | 907 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 171 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1100 | 220 | 0 | 0 | 3 | 37 | 0 | 0 | 0 | 560 | 36 | 200 | 1210 | 149 | 0 | 0 | 48 |  | 6845 | 5823 | 12668 | 3955 | 907 | 1958 | 0 | 552 | 4620 | 200 | 0 | 16 | 72 | 379 | 9 | 30.56 | 94.51
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 302 | 0 | 0 | 15 | 325 | 0 | 0 | 12 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 20 | 0 | 24 | 15 | 20 | 24 | 8 | 0 | 125 | 80 | 110 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 320 | 208 | 108 | 70 | 24 | 44 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 82 | 133 | 0 | 0 | 1 | 36 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 315 | 11 | 8 | 0 | 30 | 0 | 0 | 35 | 0 | 105 | 5 | 45 | 180 | 0 | 336 | 64 | 17 | 17 | 2 | 0 | 0 | 0 | 17 | 5 | 50 | 351 | 40 | 51 | 105 | 0 | 0 | 0 | 16 | 29 | 0 | 0 | 0 | 0 | 949 | 11 | 422 | 0 | 0 | 72 |  | 907 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 395 | 0 | 0 | 0 | 0 | 18 | 0 | 7 | 0 | 1100 | 220 | 0 | 0 | 6 | 86 | 17 | 0 | 0 | 601 | 27 | 200 | 1208 | 209 | 0 | 0 | 65 |  | 7276 | 6043 | 13319 | 3896 | 907 | 2057 | 0 | 888 | 4710 | 205 | 0 | 16 | 82 | 547 | 11 | 58.255 | 94.51
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 298 | 6 | 17 | 30 | 328 | 0 | 0 | 30 | 41 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 0 | 24 | 15 | 24 | 24 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 67 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 295 | 305 | 210 | 108 | 50 | 24 | 43 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 80 | 133 | 0 | 0 | 3 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 310 | 11 | 8 | 0 | 140 | 0 | 0 | 35 | 0 | 105 | 1 | 49 | 180 | 0 | 335 | 61 | 52 | 17 | 2 | 15 | 0 | 3 | 17 | 9 | 50 | 340 | 50 | 17 | 126 | 0 | 0 | 7 | 20 | 33 | 0 | 100 | 17 | 0 | 1045 | 21 | 421 | 0 | 0 | 21 |  | 907 | 0 | 303 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 174 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 361 | 0 | 0 | 0 | 0 | 33 | 0 | 8 | 0 | 1100 | 220 | 0 | 0 | 6 | 91 | 35 | 0 | 0 | 608 | 35 | 250 | 1208 | 96 | 0 | 0 | 58 |  | 7421 | 6082 | 13503 | 3751 | 907 | 2017 | 0 | 1266 | 4865 | 205 | 0 | 33 | 80 | 358 | 21 | 63.985 | 0
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 450 | 305 | 18 | 17 | 30 | 325 | 0 | 0 | 47 | 41 | 16 | 0 | 0 | 0 | 0 | 14 | 35 | 55 | 0 | 23 | 15 | 24 | 24 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 78 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 285 | 275 | 212 | 108 | 50 | 24 | 41 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 80 | 101 | 0 | 0 | 2 | 36 | 67 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 295 | 11 | 8 | 0 | 240 | 0 | 0 | 43 | 0 | 115 | 4 | 49 | 180 | 0 | 335 | 66 | 52 | 17 | 4 | 15 | 0 | 17 | 17 | 9 | 50 | 340 | 52 | 36 | 144 | 8 | 0 | 17 | 19 | 33 | 0 | 30 | 17 | 0 | 1050 | 10 | 422 | 0 | 0 | 40 |  | 906 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 172 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 397 | 0 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 1100 | 180 | 0 | 0 | 3 | 16 | 35 | 0 | 0 | 610 | 8 | 250 | 1253 | 117 | 0 | 0 | 45 |  | 7471 | 6018 | 13489 | 3587 | 906 | 1960 | 0 | 1490 | 4917 | 205 | 0 | 33 | 80 | 301 | 10 | 77.355 | 94.51
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 290 | 24 | 17 | 30 | 322 | 0 | 0 | 57 | 41 | 38 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 22 | 15 | 24 | 24 | 8 | 0 | 124 | 80 | 0 | 0 | 0 | 85 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 270 | 212 | 108 | 70 | 24 | 40 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 84 | 101 | 0 | 0 | 0 | 35 | 67 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 300 | 11 | 8 | 0 | 270 | 0 | 0 | 72 | 0 | 118 | 7 | 49 | 180 | 2 | 335 | 63 | 52 | 17 | 1 | 15 | 0 | 17 | 17 | 9 | 50 | 340 | 52 | 21 | 162 | 17 | 0 | 17 | 11 | 32 | 0 | 12 | 17 | 0 | 1050 | 8 | 421 | 0 | 0 | 47 |  | 907 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 172 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 394 | 0 | 0 | 0 | 0 | 34 | 0 | 6 | 0 | 1120 | 180 | 0 | 0 | 4 | 44 | 35 | 0 | 0 | 617 | 24 | 250 | 1316 | 150 | 0 | 0 | 43 |  | 7559 | 6175 | 13734 | 3572 | 907 | 1944 | 0 | 1596 | 5006 | 204 | 0 | 55 | 84 | 358 | 8 | 82.13 | 94.49
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 |  | 0 | 450 | 282 | 24 | 17 | 15 | 333 | 0 | 0 | 50 | 41 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 22 | 21 | 24 | 24 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 213 | 108 | 50 | 24 | 38 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 62 | 115 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 280 | 11 | 8 | 0 | 210 | 0 | 0 | 90 | 0 | 131 | 4 | 49 | 180 | 10 | 323 | 68 | 52 | 17 | 1 | 15 | 0 | 17 | 17 | 9 | 50 | 340 | 17 | 23 | 126 | 17 | 0 | 17 | 7 | 35 | 3 | 6 | 17 | 0 | 1054 | 8 | 422 | 0 | 0 | 6 |  | 906 | 0 | 302 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 172 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 358 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 1100 | 180 | 0 | 0 | 3 | 31 | 35 | 0 | 0 | 619 | 20 | 208 | 1318 | 124 | 0 | 0 | 31 |  | 7527 | 6008 | 13535 | 3698 | 906 | 1877 | 0 | 1493 | 4953 | 202 | 0 | 81 | 62 | 255 | 8 | 62.075 | 94.49
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 350 | 147 | 27 | 17 | 15 | 333 | 0 | 0 | 24 | 41 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 22 | 22 | 24 | 24 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 280 | 270 | 211 | 78 | 50 | 23 | 39 | 0 | 20 | 0 | 0 | 24 | 0 | 0 | 0 | 18 | 60 | 115 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 275 | 11 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 108 | 0 | 20 | 180 | 10 | 323 | 67 | 52 | 17 | 1 | 15 | 0 | 17 | 33 | 10 | 24 | 335 | 17 | 18 | 126 | 17 | 0 | 17 | 6 | 49 | 17 | 5 | 17 | 0 | 1000 | 0 | 420 | 0 | 0 | 8 |  | 907 | 0 | 305 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 172 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 318 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 920 | 180 | 0 | 0 | 0 | 37 | 35 | 0 | 0 | 590 | 13 | 185 | 1117 | 21 | 0 | 0 | 8 |  | 7034 | 5420 | 12454 | 3691 | 907 | 1538 | 0 | 1396 | 4464 | 202 | 0 | 81 | 60 | 115 | 0 | 0 | 94.48
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 |  | 0 | 300 | 152 | 27 | 32 | 15 | 280 | 0 | 0 | 24 | 41 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 22 | 22 | 24 | 16 | 8 | 0 | 122 | 80 | 0 | 0 | 1 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 9 | 0 | 0 | 0 | 285 | 275 | 209 | 78 | 50 | 25 | 40 | 0 | 20 | 0 | 0 | 33 | 0 | 0 | 0 | 18 | 70 | 115 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 295 | 11 | 8 | 0 | 145 | 0 | 0 | 94 | 0 | 100 | 0 | 20 | 180 | 10 | 323 | 67 | 52 | 17 | 0 | 15 | 0 | 17 | 52 | 53 | 24 | 327 | 17 | 2 | 126 | 17 | 0 | 17 | 3 | 49 | 17 | 15 | 17 | 0 | 900 | 0 | 422 | 0 | 0 | 6 |  | 907 | 0 | 308 | 0 | 16 | 0 | 0 | 0 | 6 | 0 | 0 | 80 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 172 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 347 | 9 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 700 | 180 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 472 | 2 | 150 | 1117 | 12 | 0 | 0 | 3 |  | 6898 | 4919 | 11817 | 3520 | 907 | 1547 | 0 | 1455 | 3993 | 202 | 0 | 87 | 70 | 36 | 0 | 0 | 94.47
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 |  | 0 | 350 | 138 | 24 | 34 | 15 | 270 | 0 | 0 | 30 | 50 | 130 | 0 | 0 | 0 | 0 | 27 | 35 | 55 | 0 | 22 | 22 | 24 | 24 | 8 | 0 | 122 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 48 | 43 | 0 | 0 | 19 | 0 | 14 | 0 | 0 | 0 | 285 | 270 | 210 | 108 | 50 | 25 | 42 | 0 | 26 | 0 | 35 | 33 | 0 | 0 | 0 | 18 | 86 | 115 | 0 | 0 | 0 | 35 | 68 | 15 | 12 | 120 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 170 | 0 | 0 | 123 | 0 | 93 | 0 | 30 | 180 | 22 | 323 | 77 | 52 | 17 | 0 | 43 | 0 | 17 | 88 | 53 | 35 | 335 | 17 | 0 | 162 | 17 | 0 | 17 | 0 | 49 | 17 | 19 | 54 | 0 | 1045 | 2 | 423 | 0 | 0 | 0 |  | 907 | 0 | 250 | 0 | 38 | 0 | 0 | 0 | 25 | 20 | 8 | 124 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 12 | 0 | 32 | 0 | 0 | 5 | 60 | 0 | 176 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 300 | 17 | 0 | 16 | 0 | 57 | 0 | 0 | 35 | 780 | 220 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 553 | 0 | 222 | 1391 | 0 | 0 | 0 | 0 |  | 7605 | 5666 | 13271 | 3484 | 907 | 1634 | 0 | 1879 | 4650 | 202 | 0 | 427 | 86 | 0 | 2 | 75.445 | 94.44
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 340 | 126 | 24 | 34 | 55 | 272 | 0 | 0 | 57 | 82 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 22 | 22 | 24 | 24 | 8 | 0 | 123 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 75 | 51 | 0 | 4 | 19 | 0 | 10 | 0 | 0 | 0 | 280 | 280 | 213 | 70 | 50 | 25 | 42 | 0 | 51 | 0 | 36 | 32 | 0 | 0 | 0 | 18 | 86 | 103 | 0 | 0 | 0 | 35 | 68 | 15 | 15 | 163 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 295 | 0 | 0 | 123 | 0 | 94 | 0 | 49 | 160 | 60 | 323 | 78 | 52 | 51 | 0 | 49 | 0 | 17 | 88 | 53 | 50 | 341 | 17 | 0 | 162 | 17 | 0 | 17 | 0 | 73 | 17 | 23 | 72 | 0 | 1100 | 5 | 419 | 0 | 0 | 0 |  | 907 | 0 | 303 | 0 | 47 | 0 | 0 | 0 | 40 | 35 | 8 | 80 | 10 | 28 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 16 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 152 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 310 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 1010 | 180 | 0 | 17 | 0 | 0 | 98 | 0 | 0 | 605 | 0 | 250 | 1458 | 0 | 0 | 0 | 0 |  | 8142 | 6259 | 14401 | 3565 | 907 | 1602 | 0 | 2380 | 5054 | 203 | 0 | 599 | 86 | 0 | 5 | 190.045 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 |  | 0 | 340 | 142 | 25 | 34 | 50 | 270 | 0 | 0 | 57 | 82 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 22 | 22 | 24 | 24 | 8 | 0 | 125 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 56 | 51 | 0 | 13 | 19 | 0 | 18 | 0 | 0 | 0 | 280 | 280 | 210 | 53 | 50 | 25 | 43 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 18 | 80 | 103 | 0 | 0 | 0 | 35 | 68 | 15 | 15 | 163 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 210 | 0 | 0 | 123 | 0 | 94 | 0 | 49 | 170 | 50 | 323 | 78 | 52 | 17 | 0 | 15 | 0 | 17 | 88 | 53 | 50 | 341 | 17 | 0 | 162 | 17 | 0 | 17 | 0 | 70 | 17 | 48 | 35 | 0 | 1100 | 4 | 420 | 0 | 0 | 0 |  | 907 | 0 | 304 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 10 | 0 | 0 | 0 | 0 | 38 | 0 | 87 | 0 | 0 | 25 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 162 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 347 | 17 | 0 | 50 | 0 | 106 | 0 | 0 | 35 | 1020 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 613 | 0 | 250 | 1458 | 0 | 0 | 0 | 0 |  | 7956 | 6228 | 14184 | 3585 | 907 | 1647 | 0 | 2178 | 5083 | 205 | 0 | 495 | 80 | 0 | 4 | 158.53 | 94.45
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 |  | 0 | 450 | 147 | 21 | 24 | 15 | 327 | 0 | 0 | 34 | 40 | 132 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 22 | 22 | 24 | 33 | 8 | 0 | 125 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 0 | 40 | 51 | 0 | 24 | 19 | 0 | 25 | 0 | 0 | 0 | 330 | 325 | 210 | 53 | 50 | 25 | 43 | 0 | 51 | 0 | 35 | 34 | 0 | 0 | 0 | 18 | 78 | 103 | 0 | 0 | 0 | 35 | 68 | 30 | 25 | 163 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 95 | 0 | 0 | 124 | 0 | 94 | 0 | 49 | 160 | 50 | 323 | 78 | 52 | 17 | 0 | 25 | 0 | 17 | 88 | 54 | 50 | 366 | 17 | 0 | 118 | 17 | 0 | 17 | 0 | 107 | 17 | 73 | 25 | 0 | 430 | 7 | 423 | 0 | 0 | 0 |  | 907 | 0 | 395 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 126 | 10 | 0 | 0 | 0 | 0 | 39 | 4 | 87 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 172 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 414 | 17 | 0 | 50 | 0 | 110 | 0 | 0 | 95 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 617 | 0 | 293 | 1494 | 0 | 0 | 0 | 0 |  | 7435 | 6760 | 14195 | 3976 | 907 | 1936 | 0 | 2009 | 4590 | 205 | 0 | 487 | 78 | 0 | 7 | 196 | 94.44
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 142 | 7 | 17 | 15 | 328 | 0 | 0 | 9 | 16 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 23 | 22 | 24 | 33 | 8 | 0 | 125 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 0 | 40 | 51 | 0 | 12 | 19 | 0 | 21 | 0 | 0 | 0 | 310 | 300 | 211 | 53 | 50 | 25 | 45 | 0 | 51 | 0 | 35 | 25 | 0 | 0 | 0 | 18 | 88 | 104 | 0 | 0 | 0 | 35 | 68 | 30 | 30 | 163 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 165 | 0 | 0 | 124 | 0 | 94 | 0 | 49 | 160 | 50 | 323 | 78 | 52 | 51 | 0 | 90 | 0 | 42 | 88 | 52 | 50 | 346 | 17 | 0 | 159 | 47 | 0 | 17 | 0 | 90 | 17 | 91 | 108 | 0 | 330 | 14 | 422 | 0 | 0 | 0 |  | 907 | 0 | 395 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 8 | 126 | 10 | 0 | 0 | 0 | 0 | 39 | 5 | 87 | 0 | 0 | 42 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 172 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 414 | 17 | 0 | 100 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 1509 | 0 | 0 | 0 | 0 |  | 7569 | 7036 | 14605 | 3970 | 907 | 1929 | 0 | 2257 | 4666 | 205 | 0 | 569 | 88 | 0 | 14 | 186.225 | 0
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 140 | 8 | 17 | 15 | 328 | 0 | 0 | 9 | 16 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 10 | 22 | 24 | 33 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 40 | 51 | 0 | 12 | 20 | 0 | 29 | 0 | 0 | 0 | 310 | 300 | 212 | 55 | 50 | 26 | 45 | 0 | 51 | 0 | 35 | 33 | 0 | 0 | 0 | 18 | 92 | 109 | 0 | 0 | 0 | 35 | 68 | 30 | 30 | 163 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 210 | 0 | 0 | 123 | 0 | 94 | 0 | 49 | 160 | 50 | 323 | 78 | 34 | 51 | 0 | 100 | 0 | 51 | 88 | 25 | 50 | 346 | 17 | 0 | 162 | 72 | 0 | 17 | 0 | 40 | 17 | 110 | 17 | 0 | 343 | 24 | 421 | 0 | 0 | 0 |  | 906 | 0 | 397 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 128 | 10 | 0 | 0 | 0 | 0 | 39 | 8 | 87 | 0 | 0 | 42 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 172 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 414 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 619 | 0 | 297 | 1509 | 0 | 0 | 0 | 0 |  | 7517 | 7075 | 14592 | 3985 | 906 | 1932 | 0 | 2297 | 4665 | 205 | 0 | 486 | 92 | 0 | 24 | 322.79 | 0
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 142 | 7 | 17 | 15 | 330 | 0 | 0 | 9 | 16 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 23 | 22 | 24 | 33 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 40 | 51 | 0 | 13 | 20 | 0 | 34 | 0 | 0 | 0 | 310 | 305 | 212 | 55 | 50 | 26 | 45 | 0 | 51 | 0 | 35 | 33 | 0 | 0 | 0 | 18 | 94 | 100 | 0 | 0 | 0 | 35 | 68 | 30 | 30 | 163 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 210 | 0 | 0 | 123 | 0 | 94 | 0 | 24 | 130 | 50 | 323 | 78 | 17 | 51 | 0 | 100 | 0 | 51 | 70 | 9 | 25 | 346 | 17 | 0 | 162 | 72 | 0 | 17 | 0 | 17 | 17 | 130 | 17 | 0 | 500 | 7 | 422 | 0 | 0 | 0 |  | 907 | 0 | 397 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 8 | 128 | 10 | 0 | 0 | 0 | 0 | 39 | 11 | 87 | 0 | 0 | 40 | 0 | 22 | 0 | 0 | 5 | 60 | 0 | 148 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 414 | 34 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 250 | 1510 | 0 | 0 | 0 | 0 |  | 7547 | 7024 | 14571 | 4028 | 907 | 1944 | 0 | 2160 | 4752 | 205 | 0 | 474 | 94 | 0 | 7 | 390.595 | 94.41
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9280800 | 0 |  | 0 | 9510000 | 5934167 | 216000 | 228699 | 310276 | 7515149 | 0 | 16000 | 368640 | 464832 | 1079520 | 0 | 0 | 0 | 0 | 377280 | 486153 | 653434 | 0 | 447600 | 417240 | 516800 | 682400 | 149760 | 0 | 4863875 | 1924000 | 0 | 0 | 32376 | 4662952 | 0 | 0 | 0 |  | 0 | 238512 | 260633 | 0 | 75840 | 115680 | 0 | 500640 | 0 | 0 | 0 | 7474800 | 6984000 | 5146000 | 2693091 | 1617610 | 585216 | 1041120 | 0 | 991634 | 0 | 196096 | 495014 | 0 | 0 | 0 | 390240 | 1813440 | 3533760 | 0 | 0 | 12100 | 833000 | 1601400 | 136800 | 160632 | 3549109 | 0 | 10080 | 0 | 0 | 3249220 | 0 | 0 | 0 | 7185000 | 270432 | 133384 | 0 | 2463927 | 0 | 0 | 1730400 | 0 | 2226960 | 54135 | 537600 | 4398240 | 359636 | 8608000 | 1484400 | 705600 | 354618 | 22199 | 436582 | 0 | 295240 | 739860 | 406560 | 551040 | 8076700 | 341760 | 294630 | 1758240 | 328691 | 0 | 277920 | 138969 | 820800 | 359280 | 579300 | 342909 | 0 | 20296361 | 168960 | 10174540 | 0 | 0 | 385564 |  | 21978000 | 0 | 7947072 | 0 | 264000 | 0 | 0 | 0 | 35040 | 26368 | 44250 | 2395000 | 201147 | 50976 | 0 | 0 | 0 | 177670 | 20774 | 412800 | 0 | 0 | 155572 | 0 | 187281 | 0 | 0 | 142326 | 1425164 | 0 | 4071000 | 0 | 0 | 3903727 | 0 | 0 | 0 | 0 | 0 | 4267145 | 0 | 8566036 | 101760 | 0 | 460416 | 0 | 124783 | 0 | 53280 | 436800 | 27182300 | 5021895 | 0 | 8160 | 33420 | 457200 | 1070016 | 0 | 0 | 14705450 | 210329 | 5607300 | 30785803 | 1207380 | 0 | 3717 | 375750 |  | 171152057 | 144117107 | 315269164 | 91287353 | 21978000 | 45491271 | 0 | 27112499 | 114247918 | 6787875 | 0 | 3133175 | 1813440 | 3248673 | 168960 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26728704 | 0 |  | 0 | 30241800 | 20294851.14 | 4268160 | 4276671.3 | 5467063.12 | 22921204.45 | 0 | 85600 | 7284326.4 | 8343734.4 | 20964278.4 | 0 | 0 | 0 | 0 | 6889132.8 | 7661771.28 | 11951307.86 | 0 | 335700 | 0 | 0 | 0 | 2682201.6 | 0 | 0 | 0 | 0 | 0 | 613201.44 | 14874816.88 | 0 | 0 | 0 |  | 0 | 4200196.32 | 4667937.03 | 0 | 1484188.8 | 1904092.8 | 0 | 0 | 0 | 0 | 0 | 20854692 | 21371040 | 17084720 | 9021854.85 | 5224880.3 | 1972177.92 | 4560105.6 | 0 | 3976452.34 | 0 | 3512079.36 | 8939952.84 | 0 | 0 | 0 | 292680 | 11896166.4 | 10989993.6 | 0 | 0 | 0 | 3248700 | 5973222 | 622440 | 730875.6 | 12137952.78 | 0 | 55944 | 0 | 0 | 9065323.8 | 0 | 0 | 0 | 22201650 | 202824 | 101371.84 | 0 | 50264110.8 | 0 | 0 | 33240984 | 0 | 39216765.6 | 0 | 9574656 | 76309464 | 5962764.88 | 22811200 | 28292664 | 13237056 | 6361846.92 | 0 | 7138115.7 | 0 | 5296605.6 | 14138724.6 | 7891329.6 | 9814022.4 | 21484022 | 5833843.2 | 0 | 32158209.6 | 5515434.98 | 0 | 4966430.4 | 0 | 14790816 | 6086203.2 | 1720521 | 4828158.72 | 0 | 141465636.17 | 0 | 60029786 | 0 | 0 | 0 |  | 61758180 | 0 | 23443862.4 | 0 | 4580400 | 0 | 0 | 0 | 659102.4 | 495982.08 | 787650 | 7568200 | 953436.78 | 878826.24 | 0 | 0 | 0 | 3182069.7 | 381202.9 | 6939168 | 0 | 0 | 2786294.52 | 0 | 3354202.71 | 0 | 0 | 107740.782 | 15719558.92 | 0 | 34359240 | 0 | 0 | 12882299.1 | 0 | 0 | 0 | 0 | 0 | 14209592.85 | 0 | 25012825.12 | 1738060.8 | 0 | 9125445.12 | 0 | 2485677.36 | 0 | 0 | 8666112 | 176141304 | 15618093.45 | 0 | 157896 | 0 | 0 | 18564777.6 | 0 | 0 | 107349785 | 0 | 41774385 | 203494157.83 | 0 | 0 | 0 | 0 |  | 1010607410.62 | 805175528.662 | 1815782939.282 | 265611032.922 | 61758180 | 145372337.66 | 0 | 494840697.24 | 780333852.92 | 0 | 0 | 55970672.14 | 11896166.4 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 302 | 0 | 0 | 15 | 325 | 0 | 0 | 12 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 20 | 0 | 24 | 15 | 20 | 24 | 8 | 0 | 125 | 80 | 110 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 320 | 208 | 108 | 70 | 24 | 44 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 11 | 82 | 133 | 0 | 0 | 1 | 36 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 315 | 11 | 8 | 0 | 30 | 0 | 0 | 35 | 0 | 105 | 5 | 45 | 180 | 0 | 336 | 64 | 17 | 17 | 2 | 0 | 0 | 0 | 17 | 5 | 50 | 351 | 40 | 51 | 105 | 0 | 0 | 0 | 16 | 29 | 0 | 0 | 0 | 0 | 949 | 11 | 422 | 0 | 0 | 72 |  | 907 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 395 | 0 | 0 | 0 | 0 | 18 | 0 | 7 | 0 | 1100 | 220 | 0 | 0 | 6 | 86 | 17 | 0 | 0 | 601 | 27 | 200 | 1208 | 209 | 0 | 0 | 65 |  | 13319 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 340 | 126 | 24 | 34 | 55 | 272 | 0 | 0 | 57 | 82 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 22 | 22 | 24 | 24 | 8 | 0 | 123 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 | 0 | 0 | 75 | 51 | 0 | 4 | 19 | 0 | 10 | 0 | 0 | 0 | 280 | 280 | 213 | 70 | 50 | 25 | 42 | 0 | 51 | 0 | 36 | 32 | 0 | 0 | 0 | 18 | 86 | 103 | 0 | 0 | 0 | 35 | 68 | 15 | 15 | 163 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 295 | 0 | 0 | 123 | 0 | 94 | 0 | 49 | 160 | 60 | 323 | 78 | 52 | 51 | 0 | 49 | 0 | 17 | 88 | 53 | 50 | 341 | 17 | 0 | 162 | 17 | 0 | 17 | 0 | 73 | 17 | 23 | 72 | 0 | 1100 | 5 | 419 | 0 | 0 | 0 |  | 907 | 0 | 303 | 0 | 47 | 0 | 0 | 0 | 40 | 35 | 8 | 80 | 10 | 28 | 0 | 0 | 0 | 20 | 0 | 87 | 0 | 0 | 16 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 152 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 310 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 1010 | 180 | 0 | 17 | 0 | 0 | 98 | 0 | 0 | 605 | 0 | 250 | 1458 | 0 | 0 | 0 | 0 |  | 14401 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 300 | 24 | 34 | 55 | 335 | 0 | 0 | 57 | 82 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 22 | 22 | 24 | 33 | 8 | 0 | 120 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 75 | 51 | 50 | 25 | 50 | 0 | 20 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 50 | 25 | 42 | 0 | 51 | 0 | 36 | 33 | 0 | 0 |  | 18 | 100 | 100 | 0 | 0 | 0 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 300 | 0 | 0 | 120 | 0 | 94 | 0 | 50 | 150 | 100 | 325 | 78 | 52 | 100 | 0 | 52 | 54 | 110 | 17 | 53 | 50 | 350 | 17 | 0 | 162 | 104 | 0 | 17 | 0 | 75 | 35 | 230 | 163 | 0 | 1200 | 60 | 420 | 0 | 0 |  |  | 931 | 0 | 300 | 0 | 98 | 0 | 0 | 0 | 40 | 50 | 8 | 130 | 10 | 48 | 0 | 0 | 0 | 40 | 0 | 87 | 28 | 0 | 46 | 0 | 35 | 0 | 0 | 5 | 60 | 0 | 173 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 414 | 35 | 0 | 113 | 0 | 90 | 0 | 0 | 113 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1450 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 300 | 24 | 17 | 30 | 335 | 0 | 0 | 50 | 82 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 20 | 22 | 24 | 30 | 8 | 0 | 120 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 0 | 16 | 51 | 50 | 25 | 20 | 0 | 5 | 0 | 0 | 0 | 290 | 280 | 210 | 0 | 50 | 25 | 42 | 0 | 51 | 0 | 34 | 33 | 0 | 0 |  | 17 | 90 | 80 | 0 | 0 | 1.6 | 35 | 68 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 200 | 0 | 0 | 100 | 0 | 90 | 20 | 49 | 100 | 55 | 300 | 68 | 17 | 50 | 5 | 15 | 0 | 100 | 17 | 28 | 50 | 330 | 17 | 50 | 162 | 17 | 0 | 17 | 35 | 49 | 17 | 230 | 35 | 0 | 1100 | 44 | 420 | 0 | 0 | 70 |  | 931 | 0 | 300 | 0 | 48 | 0 | 0 | 0 | 30 | 0 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 400 | 17 | 0 | 35 | 0 | 34 | 0 | 8 | 70 | 1200 | 220 |  | 35 | 6 | 100 | 90 | 0 | 0 | 620 | 30 | 250 | 1420 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 360 | 143 | 7 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 22 | 24 | 33 | 8 | 0 | 123 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 280 | 270 | 212 | 0 | 50 | 14 | 42 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 72 | 63 | 0 | 0 | 1 | 35 | 68 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 295 | 12 | 3 | 0 | 0 | 0 | 0 | 95 | 0 | 95 | 1 | 24 | 51 | 0 | 323 | 58 | 17 | 17 | 3 | 15 | 0 | 17 | 17 | 9 | 25 | 346 | 17 | 10 | 0 | 17 | 0 | 17 | 13 | 16 | 17 | 230 | 0 | 0 | 576 | 11 | 424 | 0 | 0 | 18 | 0 | 907 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 173 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 351 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 1110 | 180 | 0 | 0 | 2 | 60 | 35 | 0 | 0 | 621 | 7 | 250 | 1415 | 69 | 0 | 0 | 24 | 0 |  |  |  | 136778624 | 21978000 | 0 | 114247918 | 30245674 | 1813440 | 3248673 | 168960 | 6787875 |  |  | 315269164
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 | [6 empty] | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 136.7786 | 21.978 | 0 | 114.2479 | 30.2457 | 1.8134 | 3.2487 | 0.16896 | 6.7879
| Minimum Generation |  | 11428 | 8:00
| Highest Generation |  | 14605 | 22:00 | [129 empty] | 0 | [73 empty] | 315.2692
| Day Peak Generation |  | 13319 | 12:00
| Evening Peak Generation |  | 14401 | 19:30 | [203 empty] | 202699852
| HVDC Max Flow |  | 907 | 2:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 907 | 19:30
| Load factor L.F |  | 89.94% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-25
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13319 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 12075
Evening Peak Generation : |  |  | 14401 | MW Hour : | 19:30 | Available Max Generation : |  | 16521
E.P. Demand (at gen end) : |  |  | 14600 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 15200
Maximum Generation : |  |  | 14605 | MW Hour : | 22:00 | Reserve(Generation end)
Total Gen. (MKWH) : |  |  | 315.2692 | System Load Factor : | 89.94% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 614 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-25
Actual : |  | 94.35 | Ft.(MSL) , | Rule curve : | 87.84 | Ft.( MSL )
Gas Consumed : |  | Total = | 1011.63 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 410983370.582
: |  |  | Coal : | 780333852.92 | Oil : | 550811369.38 | Total : | 1742128592.882
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 8 | 192:00 | 4533.8427 |  |  | 0 | -26.93%
Chittagong Area |  | 0 | 0:00 | 1245.692 |  |  | 0 | -25.31%
Khulna Area |  | 0 | 0:00 | 1744.9061 |  |  | 0 | -24.96%
Rajshahi Area |  | 0 | 0:00 | 1516.5797 |  |  | 0 | -24.59%
Cumilla Area |  | 55 | 1320:00 | 1247.9061 |  |  | 0 | -24.82%
Mymensingh Area |  | 107 | 2568:00 | 928.0993 |  |  | 0 | -24.5%
Sylhet Area |  | 20 | 480:00 | 520.2585 |  |  | 0 | -25.11%
Barisal Area |  | 0 | 0:00 | 433.5457 |  |  | 0 | -24.44%
Rangpur Area |  | 0 | 0:00 | 847.94 |  |  | 0 | -24.44%
Total |  | 190 |  | 13018.7703 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Remark
Time | Time
| 08:20 | Kulaura 132/33 kV T-1 scheduled shutdown withdrawn.
10:12 | 12:21 | Baroirhat 132/33kV S/S TR-1, 406T HT Forced S/D Due to Red hot maintenance work |  |  |  |  | 10.0MW load interruption.
10:34 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
10:37 | 17:17 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 Scheduled S/D from Bogura 230/132kV end Due to 1st Span Conductor
(R-Phase) place change.
10:37 |  | Bogura new - Sherpur 132kv ckt 01 S/D.
10:43 | 16:57 | Bogura 230/132kV S/S Confidance UN-1 Scheduled S/D Due to 132kV Sherpur Ckt.-1 1st Span Conductor(R-Phase)
place change.
10:43 |  | Bogura new - CPBL-1 132kv ckt S/D.
10:55 | 16:38 | Baroirhat 132/33kV S/S Bus-A Forced S/D Due to Red hot maintenance work
11:32 |  | Khulna(S) 230/132kV S/S 230 KV Main Bus 2 Forced S/D Due to Due to Gas leakage on NWPGCL new GIS230KV bay.
12:00 |  | Day Peak Gen. 13320 MW
12:24 |  | Raozan -1 was shut down due to gas shortage
12:31 |  | Ashuganj 420 MW CCPP(East) Synchronized with remarks:- GTG
| 14:40 | Bogura 230/132kV S/S 230KV Main 2 is restored.
15:12 |  | Sikalbaha 225MW ST was sync.
16:42 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2 was sd at 16:55 on 24.7.24
16:42 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT2
16:42 |  | Meghnaghat CCPP(Summit) GT-2 Shutdown with remarks:- NLDC asked for one unit shutdown
19:04 |  | Ashuganj 420 MW CCPP(East) Synchronized with remarks:- STG
19:04 |  | Ashuganj (E) CCPP ST was synch.
19:30 |  | Evening Peak Gen. 14401 MW
20:34 |  | SS Power unit-2 tripped due to cwp trip.
20:34 |  | SS Power Tripped with remarks:- unit2
20:35 |  | SS Power Synchronized with remarks:- (False)
06:05 |  | Bhulta 132/33 kv T-2 was shut down due to red hot maint. at 132 kv, R-phase, PT connector |  |  |  |  | 50MW load interruption.
06:05 | 07:27 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to Due to red hot maintenance
06:22 |  | Jaldhaka 132/33kV S/S 416T-2 LT Scheduled S/D Due to 33 KV Bus Section-02 Shutdown for maintenance work of |  |  |  |  | 30.0MW load interruption.
Debiganj-02 33 KV Feeder Source Isolator.
06:23 |  | Jaldhaka 132/33kV S/S 416T-2 HT Scheduled S/D Due to 33 KV Bus Section-02 Shutdown for maintenance work of
Debiganj-02 33 KV Feeder Source Isolator.
06:45 |  | Dhamrai 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot maintenance.
06:45 |  | Dhamrai 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot maintenance.
07:25 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to S/d taken byPbs barishal 2
07:26 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-24
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 377 | 9280800 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 9510000 | Frequency Control
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 24 | 216000 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 126 | 5934167 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 228699 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 310276
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 16000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 57 | 368640 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 272 | 7515149 | Frequency Control
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 82 | 464832 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 377280
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1079520 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 486153 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 653434
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 864840 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 516800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 682400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 149760 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 295 | 2463927
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 94 | 2226960 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 705600 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 341760 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1758240
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 138969
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 359280 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 2380 | 46649486
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 32376 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 54135
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 115680 | Fuel shortage
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 203 | 6787875
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 4662952
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 354618 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 75 | 238512 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 260633 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Low Demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 49 | 537600 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 500640
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 4 | 75840 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22199
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 49 | 436582 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 295240 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 551040 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 328691 | Fuel shortage
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 72 | 342909 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 1100 | 20296361
| Cox's Bazar Wind |  | IPP | 66 | 60 | 5 | 168960
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 419 | 10174540
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 385564
| Chattogram area Total |  |  |  | 4457 | 2422 | 46622947
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 5146000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7474800 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6984000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 23 | 579300 | synchronized process
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 25 | 585216 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 42 | 1041120 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 70 | 2693091 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 991634
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 60 | 359636 | Low Demand
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 196096
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1617610 | Gas shortage
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 160 | 4398240 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 86 | 1813440
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 32 | 495014 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 390240 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 739860 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 53 | 406560 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 820800 | Fuel shortage
| Cumilla Area Total |  |  |  | 2875 | 1640 | 36732657
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 103 | 3533760 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12100
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 123 | 1730400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1484400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 294630
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 277920 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 321 | 7333210
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 35 | 833000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 68 | 1601400 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3549109
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 15 | 136800 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 15 | 160632 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 133384 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 10080
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 3249220 | ST under maint
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 270432 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7185000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 323 | 8608000 | Machine problem.
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 341 | 8076700 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1379 | 33813757
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 907 | 21978000
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 47 | 264000 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 40 | 35040
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 35 | 26368
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 303 | 7947072 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 44250 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 101760 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 457200
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 605 | 14705450 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1962 | 45559140
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 28 | 50976 | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 201147
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2395000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1010 | 27182300
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 5021895
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 8160 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 5607300
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 3717
| Barisal Area Total |  |  |  | 2236 | 1575 | 40470495
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 20 | 177670
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 20774 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Low Demand
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 155572
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 158 | 3903727 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 147 | 4267145 | FGMO
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 310 | 8566036 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 187281 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 142326 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 412800
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 460416 | Low Demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 436800 | Low Demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33420
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1458 | 30785803
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 375750
| Rajshahi Area Total |  |  |  | 3381 | 2306 | 49925520
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 60 | 1425164
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 152 | 4071000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 124783
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 53280
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 98 | 1070016
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 210329
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1207380
| Rangpur Area Total |  |  |  | 950 | 416 | 8161952
| Total |  |  |  | 26947 | 14401 | 315269164
| Eastern Grid Total |  |  |  | 16526 | 8142 | 171152057
| Western Grid Total |  |  |  | 10421 | 6259 | 144117107
| National Grid Total |  |  |  | 26947 | 14401 | 315269164
*Data collected from respective power station over telephone.
Page- 3

## P3
Power Grid Company of Bangladesh Limited (PGCB)
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-07-2024 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 5979.8 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3335.1 | MW
i) Dhaka area |  |  | 3480.8 |  | MW | i) Khulna area |  |  |  | 1616 | MW
ii) Chattogram area |  |  | 761 |  | MW | ii) Barishal area |  |  |  | 387.5 | MW
iii) Cumilla area |  |  | 444 |  | MW | iii) Rajshahi area |  |  |  | 875.6 | MW
iv) Mymensingh area |  |  | 866 |  | MW | iv) Rangpur area |  |  |  | 456 | MW
v) Sylhet area |  |  | 428 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 9314.9 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 85.2 | 19:00 | 67 | Jamalpur | 126 | 00:00 | 133 | Rahim | 42 | 13:00
2 | AKSML | 9.6 | 16:00 | 68 | Jashore | 143 | 19:30 | 134 | Rajbari | 76 | 20:00
3 | Aftabnagar | 34 | 14:00 | 69 | Jhenaidah | 138 | 19:30 | 135 | Rajendrapur | 88 | 22:00
4 | Agargaon | 122 | 13:00 | 70 | Joydebpur | 185 | 16:00 | 136 | Rajshahi | 137 | 22:00
5 | Agrabad | 90 | 14:00 | 71 | Joypurhat | 66 | 22:00 | 137 | Rajshahi-230 | 79 | 13:00
6 | Amnura | 79 | 21:00 | 72 | Juldah | 24 | 19:00 | 138 | Ramganj | 116 | 22:00
7 | Ashuganj | 85 | 23:00 | 73 | KSRM | 27 | 13:00 | 139 | Rampur | 35 | 22:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 265 | 16:00 | 140 | Rangamati | 17 | 19:30
9 | BSRM | 186 | 22:00 | 75 | Kachua | 80 | 21:00 | 141 | Rangpur | 135 | 15:00
10 | Bagerhat | 95 | 20:00 | 76 | Kallyanpur | 120 | 19:30 | 142 | Ruppur | 7 | 15:00
11 | Bakulia | 85 | 14:00 | 77 | Kalurghat | 32 | 16:00 | 143 | SSM | 11 | 03:00
12 | Banani | 71 | 13:00 | 78 | Kamrangirchar | 52 | 13:00 | 144 | Saidpur | 110 | 19:30
13 | Bangabhaban | 24 | 13:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 135 | 23:00
14 | Barapukuria | 63 | 19:30 | 80 | Kazla | 105 | 22:00 | 146 | Satmasjid | 113 | 14:00
15 | Barguna | 22 | 22:00 | 81 | Keranigonj | 76 | 22:00 | 147 | Savar | 206 | 15:00
16 | Barishal | 114 | 13:00 | 82 | Khagrachori | 32 | 21:00 | 148 | SevenRings | 6.36 | 10:00
17 | Barishal-230 | 96 | 19:30 | 83 | Khulna | 67 | 13:00 | 149 | ShahCement | 21 | 19:30
18 | Baroaulia | 61 | 23:00 | 84 | Khulshi | 170 | 13:00 | 150 | Shahjadpur | 90 | 21:00
19 | Baroirhat | 58 | 22:00 | 85 | Kishoreganj | 156 | 19:30 | 151 | Shahjibazar | 121 | 19:00
20 | Bashundhara | 168 | 13:00 | 86 | Kodda | 280 | 19:00 | 152 | Shahmirpur | 55 | 19:00
21 | BashundharaCement | 1 | 11:00 | 87 | Kulaura | 55 | 19:00 | 153 | Shariatpur | 89 | 22:00
22 | Beanibazar | 82 | 19:30 | 88 | Kurigram | 68 | 19:00 | 154 | Sherpur | 125 | 21:00
23 | Benapole | 72 | 23:00 | 89 | Kushtia | 140 | 19:30 | 155 | Shikalbaha | 29 | 12:00
24 | Bhaluka | 126 | 17:00 | 90 | Lalbag | 82 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 51 | 19:00 | 91 | Lalmonirhat | 66 | 23:00 | 157 | Shitalakhya | 84.7 | 16:00
26 | Bhangura | 38 | 21:00 | 92 | MI_Cement | 10.5 | 17:00 | 158 | Sholosohor | 42 | 15:00
27 | Bheramara(GK) | 68 | 21:00 | 93 | Madanganj | 38 | 21:00 | 159 | Shyampur | 134 | 13:00
28 | Bhulta | 217 | 19:00 | 94 | Madaripur | 120 | 21:00 | 160 | Siddhirganj | 110 | 13:00
29 | Bog-Sherpur | 66 | 22:00 | 95 | Madartek | 82.1 | 23:00 | 161 | Sirajganj | 120 | 20:00
30 | Bogura | 175 | 21:00 | 96 | Madunaghat | 60 | 19:30 | 162 | Sonargaon | 90 | 17:00
31 | Borhanuddin | 84 | 21:00 | 97 | Magura | 71 | 20:00 | 163 | Sreemongol | 79 | 23:00
32 | Brahmanbaria | 151 | 22:00 | 98 | Mahasthangarh | 80 | 21:00 | 164 | Sreepur | 90 | 18:00
33 | Cantonment | 116 | 14:00 | 99 | Manikganj | 131 | 23:00 | 165 | Srinagar | 49.64 | 23:00
34 | Chandpur | 70 | 19:00 | 100 | Maniknagar | 64 | 12:00 | 166 | Sunamganj | 56 | 19:00
35 | Chandraghona | 31 | 19:30 | 101 | Matarbari | 45 | 21:00 | 167 | Sylhet | 44 | 21:00
36 | Chapai | 77 | 20:00 | 102 | Matuail | 72 | 15:00 | 168 | Sylhet-132 | 125 | 13:00
37 | Charsaidpur | 37 | 21:00 | 103 | Millgate | 124 | 15:00 | 169 | TK | 31 | 23:00
38 | Chauddagram | 68 | 19:00 | 104 | Mirpur | 142 | 13:00 | 170 | Tangail | 202 | 00:00
39 | Chhatak | 34 | 21:00 | 105 | Mirsorai | 10 | 22:00 | 171 | Thakurgaon | 114 | 20:00
40 | Chowmuhani | 220 | 19:30 | 106 | Mirzapur | 50 | 19:00 | 172 | Tongi | 114 | 15:00
41 | Chuadanga | 118 | 19:30 | 107 | Mithapukur | 62 | 23:00 | 173 | Ullahpara | 26 | 23:00
42 | Coxsbazar | 127 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 55 | 21:00
43 | Cumilla(N) | 130 | 19:00 | 109 | Mogbazar | 141.2 | 15:00 | 175 | Uttara | 76 | 10:00
44 | Cumilla(S) | 160 | 20:00 | 110 | Mongla | 28 | 12:00 | 176 | UttaraNew | 56 | 23:00
45 | Daudkandi | 144 | 21:00 | 111 | Motijheel | 42 | 13:00 | 177 | Zigatola | 83 | 15:00
46 | Dhaka | 42 | 13:00 | 112 | Munshiganj | 106 | 22:00
47 | Dhamrai | 122 | 15:00 | 113 | Mymensingh | 230 | 19:00
48 | Dhanmondi | 114 | 16:00 | 114 | Naogaon | 110 | 14:00
49 | Dohazari | 110 | 19:30 | 115 | Narail | 61 | 19:30
50 | Faridpur | 159 | 19:00 | 116 | Narinda | 81 | 14:00
51 | Fatullah | 86 | 12:00 | 117 | Narshingdi | 155 | 21:00
52 | Fenchuganj | 45 | 02:00 | 118 | Natore | 118 | 15:00
53 | Feni | 122 | 20:00 | 119 | Nawabganj | 51.6 | 22:00
54 | GPH | 83 | 13:00 | 120 | Netrakona | 100 | 21:00
55 | Ghatail | 66 | 19:00 | 121 | New | 53.5 | 11:00
56 | Ghorashal | 55 | 12:00 | 122 | Niamatpur | 84 | 22:00
57 | Goalpara | 34 | 13:00 | 123 | Noapara | 47 | 21:00
58 | Gollamari | 80 | 13:00 | 124 | PHP | 9 | 18:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 388 | 18:30 | 371 | 14:00 | Kaliakoir | 381 | 18:00 | 358 | 11:00
| Ashuganj | 402 | 5:00 | 379 | 11:00 | Madunaghat_I | 396 | 6:00 | 389 | 10:00
| Bhulta | 395 | 18:30 | 379 | 13:00 | Meghnaghat | 385 | 18:30 | 366 | 12:00
| Bibiana | 398 | 19:30 | 389 | 14:00 | Payra | 410 | 06:00 | 401 | 21:00
| BIPTC | 403 | 06:00 | 394 | 23:00 | Rahanpur | 406 | 18:30 | 390 | 21:00
| Bogura | 401 | 7:00 | 385 | 19:00 | Rampal | 404 | 18:30 | 386 | 12:00
| Gopalganj | 403 | 2:00 | 394 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 06:00 | 214 | 11:00 | Haripur | 230 | 05:00 | 217 | 11:00
| AKSML | 236 | 18:30 | 223 | 11:00 | Hasnabad | 228 | 05:00 | 216 | 11:00
| Aminbazar | 230 | 18:30 | 218 | 14:00 | Hathazari | 236 | 19:30 | 233 | 18:30
| Ashuganj | 236 | 18:30 | 227 | 14:00 | Ishurdi | 225 | 00:00 | 225 | 00:00
| Ashuganj-400 | 234 | 7:00 | 224 | 14:00 | Jhenaidah | 228 | 18:30 | 211 | 23:00
| Baghabari | 231 | 07:00 | 223 | 00:00 | Kaliakoir | 238 | 18:30 | 220 | 11:00
| Barapukuria | 219 | 00:00 | 208 | 23:00 | Keranigonj | 229 | 18:30 | 214 | 12:00
| Barapukuria-230 | 219 | 00:00 | 208 | 23:00 | Khulna(S) | 227 | 9:00 | 220 | 16:00
| Barishal | 235 | 18:30 | 223 | 22:00 | Madunaghat_I | 233 | 6:00 | 229 | 10:00
| Bheramara | 235 | 18:30 | 224 | 21:00 | Maniknagar | 232 | 10:00 | 226 | 21:00
| Bhulta | 234 | 18:30 | 222 | 13:00 | Meghnaghat | 234 | 18:00 | 222 | 1100
| Bibiana | 228 | 19:30 | 221 | 14:00 | Meghnaghat-400 | 232 | 10:00 | 227 | 20:00
| BIPTC | 236 | 18:30 | 222 | 23:00 | Mirsorai | 233 | 19:00 | 224 | 11:00
| Bogura | 225 | 7:00 | 215 | 19:30 | Rajshahi | 235 | 18:30 | 221 | 23:00
| Bogura-400 | 227 | 02:00 | 216 | 22:00 | Rampal | 232 | 18:30 | 217 | 23:00
| Borhanuddin | 238 | 08:00 | 230 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 234 | 19:30 | 223 | 12:00 | Rampura | 232 | 06:00 | 217 | 11:00
| Cumilla(N) | 229 | 18:30 | 218 | 11:00 | Shikalbaha | 236 | 19:00 | 233 | 20:00
| Faridpur | 234 | 18:00 | 224 | 12:00 | Shyampur | 231 | 06:00 | 217 | 11:00
| Fenchuganj | 229 | 05:00 | 224 | 02:00 | Siddhirganj | 233 | 04:00 | 220 | 11:00
| Ghorashal | 235 | 07:00 | 230 | 14:00 | Sirajgonj | 232 | 7:00 | 226 | 19:00
| Ghorashal-230 | 233 | 18:30 | 218 | 11:00 | Sreepur | 230 | 18:30 | 227 | 19:00
| Gopalganj | 234 | 2:00 | 222 | 20:00 | Tongi | 235 | 18:30 | 216 | 11:00
| GPH | 234 | 19:30 | 225 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 06:00 | 124 | 11:00 | Kushtia | 136 | 18:30 | 129 | 00:00
| Agargaon | 137 | 06:00 | 125 | 12:00 | Lalbag | 133 | 18:30 | 124 | 12:00
| Agrabad | 135 | 19:30 | 127 | 10:00 | Lalmonirhat | 125 | 17:00 | 114 | 19:30
| AKS | 132 | 01:00 | 127 | 09:00 | Madanganj | 132 | 19:00 | 122 | 11:00
| Aminbazar | 138 | 18:00 | 127 | 22:00 | Madaripur | 132 | 18:30 | 126 | 10:00
| Amnura | 134 | 22:00 | 121 | 22:00 | Madartek | 135 | 19:30 | 132 | 21:00
| Ashuganj | 138 | 06:00 | 135 | 00:00 | Madunaghat | 135 | 18:00 | 129 | 12:00
| Bagerhat | 134 | 18:30 | 119 | 23:00 | Magura | 138 | 18:00 | 126 | 22:00
| Bakulia | 136 | 21:00 | 128 | 10:00 | Mahasthangarh | 130 | 18:30 | 121 | 20:00
| Banani | 136 | 03:00 | 123 | 11:00 | Manikganj | 129 | 18:30 | 119 | 11:00
| Bangabhaban | 130 | 18:30 | 121 | 12:00 | Maniknagar | 130 | 18:30 | 122 | 11:00
| Barapukuria | 131 | 00:00 | 122 | 23:00 | Matarbari | 126 | 07:00 | 117 | 00:00
| Barguna | 132 | 18:00 | 126 | 23:00 | Matuail | 131.2 | 19:30 | 122.4 | 11:00
| Barishal | 137 | 18:00 | 130 | 22:00 | Millgate | 136 | 18:30 | 124 | 11:00
| Barishal-230 | 139 | 18:30 | 130 | 22:00 | Mirpur | 137 | 18:30 | 125 | 11:00
| Baroaulia | 136 | 22:00 | 133 | 23:00 | Mirzapur | 130 | 18:30 | 121 | 11:00
| Baroirhat | 128 | 22:00 | 120 | 10:00 | Mithapukur | 127 | 18:30 | 119 | 19:30
| Bashundhara | 136 | 06:00 | 124 | 11:00 | MI_Cement | 133.6 | 19:30 | 123 | 11:00
| BashundharaCement | 132 | 19:00 | 122 | 11:00 | Modern | 135 | 19:00 | 131 | 00:00
| Beanibazar | 118 | 17:00 | 116 | 13:00 | Mogbazar | 136 | 06:00 | 125 | 11:00
| Benapole | 135 | 18:30 | 120 | 23:00 | Mongla | 134 | 18:00 | 120 | 23:00
| Bhaluka | 127 | 18:00 | 120 | 15:00 | Motijheel | 130 | 18:30 | 121 | 12:00
| Bhandaria | 134 | 18:00 | 124 | 03:00 | Munshiganj | 132 | 19:30 | 122 | 11:00
| Bhangura | 135 | 17:00 | 130 | 20:00 | Mymensingh | 135 | 18:30 | 116 | 12:00
| Bheramara | 136 | 18:30 | 131 | 15:00 | Naogaon | 121 | 14:00 | 121 | 14:00
| Bheramara(GK) | 136 | 18:00 | 130 | 23:00 | Narail | 139 | 18:30 | 124 | 23:00
| Bhulta | 127 | 06:00 | 117 | 11:00 | Narinda | 131 | 03:00 | 120 | 11:00
| Bog-Sherpur | 128 | 17:00 | 124 | 20:00 | Narshingdi | 122 | 05:00 | 113 | 10:00
| Bogura | 132 | 18:30 | 126 | 19:30 | Natore | 128 | 15:00 | 128 | 15:00
| Bogura-230 | 133 | 18:30 | 126 | 19:30 | Nawabganj | 133 | 18:30 | 123 | 12:00
| Brahmanbaria | 128 | 18:30 | 121 | 15:00 | Netrakona | 133 | 13:00 | 120 | 23:00
| Cantonment | 137 | 07:00 | 125 | 12:00 | New | 136 | 06:00 | 125 | 11:00
| Chandpur | 130 | 19:30 | 116 | 01:00 | Niamatpur | 135 | 17:00 | 127 | 22:00
| Chandraghona | 136 | 18:30 | 131 | 10:00 | Noapara | 137 | 18:30 | 124 | 00:00
| Chapai | 134 | 06:00 | 125 | 20:00 | Pabna | 134 | 18:00 | 127 | 23:00
| Charsaidpur | 134 | 04:00 | 124 | 11:00 | Palashbari | 124 | 18:00 | 116 | 19:30
| Chauddagram | 130 | 18:00 | 119 | 15:00 | Panchagarh | 129 | 18:30 | 113 | 19:30
| Chhatak | 125 | 07:00 | 121 | 19:00 | Patuakhali | 130 | 16:00 | 127 | 21:00
| Chowmuhani | 125 | 18:00 | 114 | 01:00 | Payra | 135 | 18:30 | 131 | 01:00
| Chuadanga | 133 | 18:30 | 115 | 23:00 | PHP | 128 | 18:30 | 117 | 13:00
| Coxsbazar | 123 | 16:00 | 117 | 00:00 | Postogola | 135 | 19:00 | 131 | 23:00
| Cumilla(N) | 133 | 18:30 | 125 | 11:00 | Purbachal | 137 | 18:30 | 123 | 11:00
| Cumilla(S) | 132 | 02:00 | 124 | 10:00 | Purbasadipur | 127 | 18:00 | 113 | 23:00
| Daudkandi | 123 | 06:00 | 116 | 11:00 | Rahanpur | 138 | 06:00 | 130 | 22:00
| Dhaka | 136 | 07:00 | 124 | 12:00 | Rahim | 131 | 06:00 | 123 | 11:00
| Dhamrai | 138 | 18:30 | 127 | 15:00 | Rajbari | 132 | 18:30 | 124 | 23:00
| Dhanmondi | 131 | 18:30 | 124 | 16:00 | Rajendrapur | 129 | 03:00 | 119 | 13:00
| Dohazari | 130 | 17:00 | 124 | 12:00 | Rajshahi | 134 | 18:30 | 127 | 11:00
| Faridpur | 132 | 18:30 | 125 | 23:00 | Rajshahi-230 | 136 | 18:30 | 116 | 23:00
| Fatullah | 134 | 19:30 | 124 | 12:00 | Ramganj | 127 | 18:30 | 117 | 22:00
| Fenchuganj | 129 | 06:00 | 126 | 00:00 | Rampur | 135 | 19:30 | 129 | 11:00
| Feni | 128 | 18:00 | 120 | 01:00 | Rampura | 136 | 06:00 | 124 | 11:00
| Ghatail | 132 | 18:30 | 123 | 11:00 | Rangamati | 135 | 18:30 | 128 | 11:00
| Ghorashal | 137 | 19:30 | 129 | 12:00 | Rangpur | 126 | 03:00 | 114 | 20:00
| Goalpara | 139 | 18:00 | 126 | 00:00 | Ruppur | 137 | 18:00 | 131 | 21:00
| Gollamari | 138 | 18:30 | 127 | 22:00 | Saidpur | 127 | 17:00 | 114 | 23:00
| Gopalganj | 134 | 18:30 | 124 | 23:00 | Satkhira | 134 | 18:30 | 119 | 23:00
| Gopalganj-400 | 133 | 18:30 | 126 | 11:00 | Satmasjid | 135 | 18:00 | 125 | 12:00
| Gulshan | 134 | 04:00 | 121 | 11:00 | Savar | 137 | 18:00 | 124 | 11:00
| Halishahar | 135 | 19:30 | 130 | 15:00 | SevenRings | 138 | 18:30 | 129 | 12:00
| Haripur | 131 | 05:00 | 124 | 11:00 | ShahCement | 134 | 04:00 | 124 | 11:00
| HaripurSBU | 131 | 06:00 | 123 | 11:00 | Shahjadpur | 138 | 18:00 | 133 | 12:00
| Hasnabad | 134 | 07:00 | 126 | 12:00 | Shahjibazar | 126 | 04:00 | 119 | 11:00
| Hathazari | 138 | 18:00 | 136 | 18:30 | Shahmirpur | 135 | 18:00 | 129 | 11:00
| Ishurdi | 131 | 00:00 | 131 | 00:00 | Shariatpur | 132 | 18:00 | 123 | 23:00
| Jaldhaka | 125 | 18:30 | 113 | 19:30 | Sherpur | 135 | 18:30 | 122 | 23:00
| Jamalpur | 138 | 18:30 | 127 | 00:00 | Shikalbaha | 122 | 05:00 | 118 | 10:00
| Jashore | 136 | 18:30 | 122 | 00:00 | Shikalbaha-230 | 136 | 21:00 | 134 | 19:00
| Jhenaidah | 139 | 18:30 | 126 | 23:00 | Shitalakhya | 133.6 | 19:30 | 126 | 15:00
| Jhenaidah-230 | 139 | 18:30 | 126 | 23:00 | Sholosohor | 135 | 22:00 | 128 | 11:00
| Joydebpur | 136 | 18:30 | 125 | 12:00 | Shyampur | 133 | 06:00 | 127 | 11:00
| Joypurhat | 127 | 18:30 | 116 | 20:00 | Shyampur-230 | 133 | 06:00 | 122 | 17:00
| Juldah | 135 | 15:00 | 129 | 10:00 | Siddhirganj | 131 | 05:00 | 123 | 11:00
| Kabirpur | 134 | 06:00 | 121 | 11:00 | Sirajganj | 130 | 18:00 | 125 | 11:00
| Kachua | 132 | 18:30 | 123 | 11:00 | Sonargaon | 127 | 01:00 | 122 | 12:00
| Kaliakoir | 133 | 03:00 | 123 | 11:00 | Sreemongol | 125 | 08:00 | 120 | 13:00
| Kallyanpur | 131 | 02:00 | 123 | 11:00 | Sreepur | 129 | 18:30 | 127 | 19:00
| Kalurghat | 135 | 22:00 | 129 | 10:00 | Srinagar | 133 | 07:00 | 124 | 11:00
| Kamrangirchar | 134 | 18:30 | 124 | 13:00 | SSM | 140 | 19:30 | 131 | 10:00
| Kaptai | 133 | 8:00 | 128 | 16:00 | Sunamganj | 120 | 13:00 | 115 | 19:00
| Kazla | 131 | 04:00 | 119 | 12:00 | Sylhet | 122 | 21:00 | 120 | 22:00
| Keranigonj | 134 | 18:30 | 125 | 12:00 | Sylhet-132 | 123 | 18:00 | 120 | 13:00
| Khagrachori | 133 | 18:00 | 129 | 23:00 | Tangail | 130 | 18:30 | 121 | 11:00
| Khulna | 137 | 18:30 | 124 | 00:00 | Thakurgaon | 131 | 18:00 | 113 | 23:00
| Khulna(S) | 138 | 18:30 | 130 | 11:00 | TK | 136 | 22:00 | 133 | 23:00
| Khulshi | 134 | 19:30 | 127 | 11:00 | Tongi | 136 | 18:30 | 125 | 11:00
| Kishoreganj | 130 | 06:00 | 124 | 00:00 | Ullahpara | 135 | 18:30 | 128 | 23:00
| Kodda | 130 | 19:00 | 126 | 23:00 | Ullon | 134 | 03:00 | 121 | 11:00
| KSRM | 136 | 19:00 | 129 | 11:00 | Uttara | 136 | 06:00 | 126 | 10:00
| Kulaura | 129 | 04:00 | 127 | 00:00 | UttaraNew | 137 | 06:00 | 125 | 11:00
| Kurigram | 126 | 18:00 | 113 | 20:00 | Zigatola | 134 | 18:30 | 125 | 12:00

## L-Curve
Date | 2024-07-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 824 | 7547 | 7024 | 14571 |  |  |  | QF-LDC-11
0:30 | 824 | 7342.5 | 6666 | 14008.5 | Date: | 2024-07-24
1:00 | 824 | 7138 | 6308 | 13446
1:30 | 791 | 7031 | 6172.5 | 13203.5
2:00 | 758 | 6924 | 6037 | 12961
2:30 | 754 | 6871.5 | 5967.5 | 12839 | [5 empty] | Gen. at Eve. Peak | 14401 | 14401 MW (19:30 )
3:00 | 750 | 6819 | 5898 | 12717 | [6 empty] | 19:30
3:30 | 745 | 6765 | 5786 | 12551 | [5 empty] | Gen. at Day Peak | 13319 | 13319 MW (12:00 )
4:00 | 740 | 6711 | 5674 | 12385 | [6 empty] | 12:00
4:30 | 744 | 6661 | 5575.5 | 12236.5 | [5 empty] | Highest Generation | 14605
5:00 | 748 | 6611 | 5477 | 12088 | [6 empty] | 22:00
5:30 | 757 | 6531.5 | 5260.5 | 11792
6:00 | 766 | 6452 | 5044 | 11496
6:30 | 730 | 6427.5 | 5049 | 11476.5
7:00 | 694 | 6403 | 5054 | 11457
7:30 | 785 | 6386.5 | 5056 | 11442.5
8:00 | 876 | 6370 | 5058 | 11428
8:30 | 961 | 6508 | 5158 | 11666
9:00 | 1046 | 6646 | 5258 | 11904
9:30 | 1078 | 6625 | 5458.5 | 12083.5
10:00 | 1110 | 6604 | 5659 | 12263
10:30 | 1116 | 6724.5 | 5741 | 12465.5
11:00 | 1122 | 6845 | 5823 | 12668
11:30 | 1220 | 7060.5 | 5933 | 12993.5
12:00 | 1318 | 7276 | 6043 | 13319
12:30 | 1269 | 7348.5 | 6062.5 | 13411
13:00 | 1220 | 7421 | 6082 | 13503
13:30 | 1192 | 7446 | 6050 | 13496
14:00 | 1164 | 7471 | 6018 | 13489
14:30 | 1218 | 7515 | 6096.5 | 13611.5
15:00 | 1272 | 7559 | 6175 | 13734
15:30 | 1296 | 7543 | 6091.5 | 13634.5
16:00 | 1320 | 7527 | 6008 | 13535
16:30 | 1337 | 7280.5 | 5714 | 12994.5
17:00 | 1354 | 7034 | 5420 | 12454
17:30 | 1296 | 6966 | 5169.5 | 12135.5
18:00 | 1238 | 6898 | 4919 | 11817
18:30 | 1225 | 7251.5 | 5292.5 | 12544
19:00 | 1212 | 7605 | 5666 | 13271
19:30 | 780 | 8142 | 6259 | 14401
20:00 | 712 | 7956 | 6228 | 14184 |  |  |  | Executive Engineer
20:30 | 663 | 7695.5 | 6494 | 14189.5 |  |  |  | Network Operation Division
21:00 | 614 | 7435 | 6760 | 14195
21:30 | 635 | 7502 | 6898 | 14400
22:00 | 656 | 7569 | 7036 | 14605 |  |  |  |  | Page 6 of 7
22:30 | 733 | 7543 | 7055.5 | 14598.5
23:00 | 810 | 7517 | 7075 | 14592
23:30 | 817 | 7532 | 7049.5 | 14581.5
24:00 | 824 | 7547 | 7024 | 14571
14401 MW (19:30 )
13319 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-24 |  | Energy |  | 315269164
[15 empty] | 2024-07-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4028 | 907 | 1944 | 0 | 2160 | 4752 | 205 | 0 | 474 | 94 | 0 | 7 | 390.595
0:30 | 4103 | 906.5 | 1978.5 | 0 | 1464 | 4992.5 | 202.5 | 0 | 263 | 88 | 0 | 10.5 | 235.2975 |  |  | Date: | 44035
1:00 | 4178 | 906 | 2013 | 0 | 768 | 5233 | 200 | 0 | 52 | 82 | 0 | 14 | 80
1:30 | 4150 | 906.5 | 1995.5 | 0 | 727 | 5110 | 200 | 0 | 26 | 78 | 0 | 10.5 | 61.5 | [9 empty] | Total Energy | 315.2692 | 315.2692 | Total Energy Gen 315.269 MKWHr Energy Not Served 2.014 MKWHr Energy Requirement 317.283 MKWHr
2:00 | 4122 | 907 | 1978 | 0 | 686 | 4987 | 200 | 0 | 0 | 74 | 0 | 7 | 43 | [9 empty] | Energy not Served | 2.0137 | 2.0137
2:30 | 4093.5 | 907 | 1969 | 0 | 662.5 | 4928 | 199.5 | 0 | 0 | 76 | 0 | 3.5 | 40 | [9 empty] | Energy Requirement | 317.2829 | 317.2829
3:00 | 4065 | 907 | 1960 | 0 | 639 | 4869 | 199 | 0 | 0 | 78 | 0 | 0 | 37
3:30 | 4009 | 907 | 1993 | 0 | 590 | 4774 | 198.5 | 0 | 0 | 77 | 0 | 2.5 | 31 | [8 empty] | Shortage
4:00 | 3953 | 907 | 2026 | 0 | 541 | 4679 | 198 | 0 | 0 | 76 | 0 | 5 | 25
4:30 | 3958.5 | 907 | 1994 | 0 | 496 | 4605 | 197.5 | 0 | 0 | 76 | 0 | 2.5 | 12.5
5:00 | 3964 | 907 | 1962 | 0 | 451 | 4531 | 197 | 0 | 0 | 76 | 0 | 0 | 0
5:30 | 3974 | 907 | 1885 | 0 | 410.5 | 4338.5 | 197.5 | 0 | 0 | 75 | 4.5 | 0 | 0
6:00 | 3984 | 907 | 1808 | 0 | 370 | 4146 | 198 | 0 | 0 | 74 | 9 | 0 | 0
6:30 | 3946.5 | 907 | 1818 | 0 | 374 | 4131.5 | 198.5 | 0 | 0 | 69 | 31.5 | 0.5 | 0 | [7 empty] | Coal
7:00 | 3909 | 907 | 1828 | 0 | 378 | 4117 | 199 | 0 | 0 | 64 | 54 | 1 | 0
7:30 | 3917 | 907 | 1795.5 | 0 | 380 | 4097 | 199 | 0 | 0 | 63 | 83 | 1 | 0 | [6 empty] | Oil
8:00 | 3925 | 907 | 1763 | 0 | 382 | 4077 | 199 | 0 | 0 | 62 | 112 | 1 | 0
8:30 | 4022 | 907 | 1768 | 0 | 393.5 | 4127 | 199.5 | 0 | 0 | 66 | 182 | 1 | 0
9:00 | 4119 | 907 | 1773 | 0 | 405 | 4177 | 200 | 0 | 0 | 70 | 252 | 1 | 0
9:30 | 4000 | 907 | 1826 | 0 | 422.5 | 4354.5 | 200 | 0 | 8 | 71 | 292 | 2.5 | 0
10:00 | 3881 | 907 | 1879 | 0 | 440 | 4532 | 200 | 0 | 16 | 72 | 332 | 4 | 0
10:30 | 3918 | 907 | 1918.5 | 0 | 496 | 4576 | 200 | 0 | 16 | 72 | 355.5 | 6.5 | 15.28
11:00 | 3955 | 907 | 1958 | 0 | 552 | 4620 | 200 | 0 | 16 | 72 | 379 | 9 | 30.56
11:30 | 3925.5 | 907 | 2007.5 | 0 | 720 | 4665 | 202.5 | 0 | 16 | 77 | 463 | 10 | 44.4075
12:00 | 3896 | 907 | 2057 | 0 | 888 | 4710 | 205 | 0 | 16 | 82 | 547 | 11 | 58.255
12:30 | 3823.5 | 907 | 2037 | 0 | 1077 | 4787.5 | 205 | 0 | 24.5 | 81 | 452.5 | 16 | 67.805
13:00 | 3751 | 907 | 2017 | 0 | 1266 | 4865 | 205 | 0 | 33 | 80 | 358 | 21 | 77.355
13:30 | 3751 | 907 | 2017 | 0 | 1266 | 4865 | 205 | 0 | 33 | 80 | 358 | 21 | 77.355
14:00 | 3751 | 907 | 2017 | 0 | 1266 | 4865 | 205 | 0 | 33 | 80 | 358 | 21 | 77.355
14:30 | 3661.5 | 907 | 1980.5 | 0 | 1431 | 4935.5 | 204.5 | 0 | 44 | 82 | 358 | 14.5 | 79.7425
15:00 | 3572 | 907 | 1944 | 0 | 1596 | 5006 | 204 | 0 | 55 | 84 | 358 | 8 | 82.13
15:30 | 3635 | 906.5 | 1910.5 | 0 | 1544.5 | 4979.5 | 203 | 0 | 68 | 73 | 306.5 | 8 | 72.1025
16:00 | 3698 | 906 | 1877 | 0 | 1493 | 4953 | 202 | 0 | 81 | 62 | 255 | 8 | 62.075
16:30 | 3694.5 | 906.5 | 1707.5 | 0 | 1444.5 | 4708.5 | 202 | 0 | 81 | 61 | 185 | 4 | 31.0375
17:00 | 3691 | 907 | 1538 | 0 | 1396 | 4464 | 202 | 0 | 81 | 60 | 115 | 0 | 0
17:30 | 3605.5 | 907 | 1542.5 | 0 | 1425.5 | 4228.5 | 202 | 0 | 84 | 65 | 75.5 | 0 | 0
18:00 | 3520 | 907 | 1547 | 0 | 1455 | 3993 | 202 | 0 | 87 | 70 | 36 | 0 | 0
18:30 | 3502 | 907 | 1590.5 | 0 | 1667 | 4321.5 | 202 | 0 | 257 | 78 | 18 | 1 | 37.7225
19:00 | 3484 | 907 | 1634 | 0 | 1879 | 4650 | 202 | 0 | 427 | 86 | 0 | 2 | 75.445
19:30 | 3565 | 907 | 1602 | 0 | 2380 | 5054 | 203 | 0 | 599 | 86 | 0 | 5 | 116.9875
20:00 | 3585 | 907 | 1647 | 0 | 2178 | 5083 | 205 | 0 | 495 | 80 | 0 | 4 | 158.53
20:30 | 3780.5 | 907 | 1791.5 | 0 | 2093.5 | 4836.5 | 205 | 0 | 491 | 79 | 0 | 5.5 | 177.265
21:00 | 3976 | 907 | 1936 | 0 | 2009 | 4590 | 205 | 0 | 487 | 78 | 0 | 7 | 196
21:30 | 3973 | 907 | 1932.5 | 0 | 2133 | 4628 | 205 | 0 | 528 | 83 | 0 | 10.5 | 191.1125
22:00 | 3970 | 907 | 1929 | 0 | 2257 | 4666 | 205 | 0 | 569 | 88 | 0 | 14 | 186.225
22:30 | 3977.5 | 906.5 | 1930.5 | 0 | 2277 | 4665.5 | 205 | 0 | 527.5 | 90 | 0 | 19 | 254.5075
23:00 | 3985 | 906 | 1932 | 0 | 2297 | 4665 | 205 | 0 | 486 | 92 | 0 | 24 | 322.79
23:30 | 4006.5 | 906.5 | 1938 | 0 | 2228.5 | 4708.5 | 205 | 0 | 480 | 93 | 0 | 15.5 | 356.6925 |  |  | Max Temp. in Dhaka |  | 34.3°C
24:00 | 4028 | 907 | 1944 | 0 | 2160 | 4752 | 205 | 0 | 474 | 94 | 0 | 7 | 390.595
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 315.269 MKWHr Energy Not Served 2.014 MKWHr Energy Requirement 317.283 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 120 | 120 | 119 | 118 | 117 | 118 | 119 | 119 | 120 | 120 | 120 | 125 | 125 | 125 | 124 | 122 | 122 | 122 |  | 122 | 123 | 125 | 125 | 125 | 125 | 125 | 4863875
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1924000
3 | Chattogram TPP-1 | 105 | 108 | 110 | 110 | 110 | 112 | 111 | 109 | 110 | 113 | 111 | 110
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 8 | 8 | 8 | 8 | 8 |  |  | 32376
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 7 | 9 | 3 | 9 | 5 | 1 | 4 | 7 | 4 | 0 | 0 | [8 empty] | 54135
6 | Sikalbaha 225MW CCPP (Gas) | 222 | 222 | 221 | 221 | 222 | 221 | 220 | 221 | 221 | 221 | 218 | 218 | 67 | 78 | 85 | 220 | 222 | 221 |  | 220 | 223 | 223 | 222 | 222 | 221 | 220 | 4662952
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 260633
12 | Hathazari 100 MW peaking PP | [19 empty] | 48 | 75 | 56 | 40 | 40 | 40 | 40 | 238512
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 51 | 17 | 17 | 51 | 51 | 51 | 354618
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [19 empty] | 35 | 36 | 36 | 35 | 35 | 35 | 35 | 196096
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [26 empty] | 16000
17 | Siddhirganj 335 MW CCPP | 335 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 332 | 332 | 327 | 325 | 328 | 325 | 322 | 333 | 333 | 280 |  | 270 | 272 | 270 | 327 | 328 | 328 | 330 | 7515149
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 7 | 30 | 140 | 240 | 270 | 210 | 145 | 145 |  | 170 | 295 | 210 | 95 | 165 | 210 | 210 | 2463927
19 | Ashuganj 195 MW PP (APSCL-United) | 184 | 184 | 185 | 160 | 160 | 110 | 110 | 110 | 110 | 110 | 108 | 108 | 108 | 108 | 108 | 108 | 78 | 78 |  | 108 | 70 | 53 | 53 | 53 | 55 | 55 | 2693091
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 10
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 901 | 804 | 801 | 802 | 803 | 802 | 802 | 803 | 852 | 900 | 898 | 949 | 1045 | 1050 | 1050 | 1054 | 1000 | 900 |  | 1045 | 1100 | 1100 | 430 | 330 | 343 | 500 | 20296361
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 24 | 24 | 24 | 24 | 24 | 23 | 25 |  | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 585216
33 | Ashuganj 225 MW CCPP | 216 | 215 | 216 | 213 | 213 | 213 | 212 | 211 | 211 | 211 | 209 | 208 | 210 | 212 | 212 | 213 | 211 | 209 |  | 210 | 213 | 210 | 210 | 211 | 212 | 212 | 5146000
34 | Ashuganj 450 MW CCPP(South) | 275 | 270 | 270 | 270 | 270 | 310 | 270 | 275 | 305 | 285 | 305 | 320 | 305 | 275 | 270 | 270 | 270 | 275 |  | 270 | 280 | 280 | 325 | 300 | 300 | 305 | 6984000
| Ashuganj 450 MW CCPP(North) | 285 | 285 | 285 | 285 | 285 | 320 | 285 | 290 | 320 | 300 | 320 | 310 | 295 | 285 | 280 | 285 | 280 | 285 |  | 285 | 280 | 280 | 330 | 310 | 310 | 310 | 7474800
| Ashuganj 420 MW CCPP(East) | [12 empty] | 100 | 30 | 12 | 6 | 5 | 15 |  | 19 | 23 | 48 | 73 | 91 | 110 | 130 | 579300
35 | Ashuganj 55 MW PP (Precision) | 45 | 45 | 46 | 46 | 44 | 41 | 46 | 46 | 46 | 44 | 44 | 44 | 43 | 41 | 40 | 38 | 39 | 40 |  | 42 | 42 | 43 | 43 | 45 | 45 | 45 | 1041120
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 85 | 85 | 86 | 90 | 90 | 80 | 75 | 75 | 70 | 50 | 50 | 70 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1617610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 407 | 407 | 373 | 373 | 357 | 340 | 340 | 379 | 403 | 401 | 401 | 401 | 371 | 370 | 374 | 373 | 336 |  | 333 | 377 | 379 | 393 | 404 | 404 | 403 | 9280800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 380 | 340 | 340 | 340 | 340 | 380 | 450 | 450 | 450 | 450 | 450 | 450 | 350 | 300 |  | 350 | 340 | 340 | 450 | 450 | 450 | 450 | 9510000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 205 | 205 | 204 | 205 | 202 | 202 | 203 | 200 | 200 | 167 | 162 | 133 | 133 | 101 | 101 | 115 | 115 | 115 |  | 115 | 103 | 103 | 103 | 104 | 109 | 100 | 3533760
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 4 | 6 | 13 | 53 | 9 | 51 | 17 | 36 | 21 | 23 | 18 | 2 |  | 0 | [6 empty] | 294630
44 | Fenchugonj CCPP Phase-1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 35 | 36 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 833000
45 | Fenchugonj CCPP Phase-2 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 67 | 67 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1601400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | [26 empty] | 10080
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 |  | 133 | 135 | 137 | 136 | 136 | 136 | 136 | 3249220
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 133384
55 | Fenchugonj 51 MW PP (Barakatullah) | [19 empty] | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 136800
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 270432
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 270 | 270 | 290 | 300 | 285 | 295 | 300 | 310 | 310 | 305 | 315 | 310 | 295 | 300 | 280 | 275 | 295 |  | 280 | 270 | 270 | 305 | 300 | 295 | 300 | 7185000
| Bibiyana South 400 MW | 345 | 345 | 315 | 315 | 320 | 320 | 320 | 320 | 335 | 320 | 365 | 351 | 340 | 340 | 340 | 340 | 335 | 327 |  | 335 | 341 | 341 | 366 | 346 | 346 | 346 | 8076700
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 20 | 50 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 653434
59 | Tangail Palli Power Gen 22 MW | [26 empty] | 0
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 74 | 78 | 76 | 76 | 74 | 64 | 62 | 70 | 72 | 72 | 82 | 80 | 80 | 84 | 62 | 60 | 70 |  | 86 | 86 | 80 | 78 | 88 | 92 | 94 | 1813440
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 4 | 2 | 5 | 2 | 2 | 6 | 6 | 2 | 2 | 4 | 9 |  | 14 | 10 | 18 | 25 | 21 | 29 | 34 | 500640
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 15 | 11 | 11 | 11 | 11 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 390240
69 | Summit Ashulia | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 21 | 21 | 21 | 24 | 24 | 23 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 23 | 10 | 23 | 447600
70 | Summit Madhabdi | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 417240
71 | Maona 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 20 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 516800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 |  | 24 | 24 | 24 | 33 | 33 | 33 | 33 | 682400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 33 | 52 |  | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 739860
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | [6 empty] | 5 | 9 | 9 | 9 | 9 | 10 | 53 |  | 53 | 53 | 53 | 54 | 52 | 25 | 9 | 406560
| Manikgonj 162MW PP(MPGL) | [10 empty] | 22 | 105 | 126 | 144 | 162 | 126 | 126 | 126 |  | 162 | 162 | 162 | 118 | 159 | 162 | 162 | 1758240
77 | Siddhirganj 100 PP(Dutch Bangla) | [11 empty] | 12 | 30 | 47 | 57 | 50 | 24 | 24 |  | 30 | 57 | 57 | 34 | 9 | 9 | 9 | 368640
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 149760
79 | Kodda 150 MW PP | 32 | [8 empty] | 16 | 16 | 16 | 16 | 16 | 38 | 64 | 64 | 64 |  | 130 | 132 | 132 | 132 | 132 | 132 | 132 | 1079520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 33 |  | 33 | 32 | 25 | 34 | 25 | 33 | 33 | 495014
| Gazipur 100 MW PP | 34 | 17 | [5 empty] | 5 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 34 | 17 | 705600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 0 | 2 | 1 | 2 | 2 | 2 | 4 | 1 | 1 | 1 | 0 | [8 empty] | 22199
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | [12 empty] | 3 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 42 | 51 | 51 | 295240
82 | Madanganj 102 PP(Summit) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 32 |  | 34 | 34 | 34 | 24 | 17 | 17 | 17 | 228699
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 263 | 274 | 254 | 290 | 287 | 289 | 296 | 300 | 302 | 302 | 305 | 302 | 298 | 305 | 290 | 282 | 147 | 152 |  | 138 | 126 | 142 | 147 | 142 | 140 | 142 | 5934167
87 | Meghnaghat 100 MW(IEL) | [12 empty] | 6 | 18 | 24 | 24 | 27 | 27 |  | 24 | 24 | 25 | 21 | 7 | 8 | 7 | 216000
| Meghnaghat 104 MW PP (OPCL) | [10 empty] | 17 | 40 | 50 | 52 | 52 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 341760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44 MW (Energyprima) | [19 empty] | 12 | 15 | 15 | 25 | 30 | 30 | 30 | 160632
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 35 | 51 | 51 | 51 | 51 | 51 | 51 | 20 | 20 |  | 26 | 51 | 51 | 51 | 51 | 51 | 51 | 991634
94 | Gagnagar 102 MW PP (Digital Power) | [11 empty] | 8 | 41 | 41 | 41 | 41 | 41 | 41 |  | 50 | 82 | 82 | 40 | 16 | 16 | 16 | 464832
95 | Patenga 50MW PP (Baraka) | [17 empty] | 3 |  | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 115680
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 4 | 13 | 24 | 12 | 12 | 13 | 75840
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 5 | 15 | 30 | 30 | 30 | 15 | 15 | 15 |  | 15 | 55 | 50 | 15 | 15 | 15 | 15 | 310276
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 486153
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 163 | 163 | 120 | 120 | 120 | 120 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3549109
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 3 | 2 | 0 | 1 | 1 | 0 | [8 empty] | 12100
103 | Kamalaghat 54 MW PP(Banco Energy) | [13 empty] | 14 | 17 | 17 | 17 | 17 |  | 27 | 54 | 54 | 35 | 54 | 54 | 54 | 377280
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 96 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 43 | 72 | 90 | 95 | 94 |  | 123 | 123 | 123 | 124 | 124 | 123 | 123 | 1730400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 108 | 113 | 113 | 81 | 65 | 50 | 50 | 50 | 56 | 78 | 88 | 105 | 105 | 115 | 118 | 131 | 108 | 100 |  | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 2226960
115 | Juldah 100 MW PP Unit-3 (Acorn) | [10 empty] | 12 | 45 | 49 | 49 | 49 | 49 | 20 | 20 |  | 30 | 49 | 49 | 49 | 49 | 49 | 24 | 537600
116 | Chandpur 200 MW (Desh energy) | 200 | 200 | 200 | 200 | 198 | 200 | 200 | 200 | 200 | 195 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 160 | 170 | 160 | 160 | 160 | 130 | 4398240
117 | Ashuganj 150 MW PP (Midland) | [14 empty] | 2 | 10 | 10 | 10 |  | 22 | 60 | 50 | 50 | 50 | 50 | 50 | 359636
118 | Bibiyana-III 400 MW CCPP | 370 | 371 | 371 | 371 | 371 | 371 | 371 | 373 | 335 | 335 | 336 | 336 | 335 | 335 | 335 | 323 | 323 | 323 |  | 323 | 323 | 323 | 323 | 323 | 323 | 323 | 8608000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 58 | 58 | 35 | 35 | 35 | 39 | 58 | 63 | 64 | 61 | 66 | 63 | 68 | 67 | 67 |  | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 1484400
| Anwara 300 MW PP (United) | [12 empty] | 15 | 15 | 15 | 15 | 15 | 15 |  | 43 | 49 | 15 | 25 | 90 | 100 | 100 | 436582
| Juldah unit-2 (Acorn) | [10 empty] | 15 | 50 | 50 | 50 | 50 | 50 | 24 | 24 |  | 35 | 50 | 50 | 50 | 50 | 50 | 25 | 551040
| Anlima Energy Ltd. | [13 empty] | 8 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 47 | 72 | 72 | 328691
| Bhairob 54.5 MW | 17 | 17 | 17 | [9 empty] | 7 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 277920
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 17 | 14 | 5 | 4 | 16 | 20 | 19 | 11 | 7 | 6 | 3 | [8 empty] | 138969
| Chandpur 115(Doreen) | 17 | 16 | 17 | 16 | 17 | 17 | 17 | 16 | 17 | 16 | 16 | 29 | 33 | 33 | 32 | 35 | 49 | 49 |  | 49 | 73 | 70 | 107 | 90 | 40 | 17 | 820800
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 3 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 359280
| Mirsharai 150 MW (Oil) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 72 | 35 | 25 | 108 | 17 | 17 | 342909
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 14 | 7 | 0 | 5 | 0 | 0 | 1 | 1 | 1 | 4 | 9 | 11 | 21 | 10 | 8 | 8 | 0 | 0 |  | 2 | 5 | 4 | 7 | 14 | 24 | 7 | 168960
| Sonagazi 75 MW Solar Plant | [5 empty] | 2 | 17 | 17 | 56 | 35 | 73 | 72 | 21 | 40 | 47 | 6 | 8 | 6 | [8 empty] | 385564
| Matarbari 2*600 MW (CPGCL) | 420 | 421 | 421 | 421 | 422 | 422 | 422 | 422 | 422 | 420 | 420 | 422 | 421 | 422 | 421 | 422 | 420 | 422 |  | 423 | 419 | 420 | 423 | 422 | 421 | 422 | 10174540
120 | Eastern Zone Total | 7138 | 6924 | 6819 | 6711 | 6611 | 6452 | 6403 | 6370 | 6646 | 6604 | 6845 | 7276 | 7421 | 7471 | 7559 | 7527 | 7034 | 6898 |  | 7605 | 8142 | 7956 | 7435 | 7569 | 7517 | 7547 | 171152057
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [12 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 38 | 47 | 16 | 16 | 19 | 48 | 48 | 264000
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 6 |  | 25 | 40 | [5 empty] | 35040
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 9 |  | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 101760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 7 | 6 | 35 | 36 | 37 | 86 | 91 | 16 | 44 | 31 | 37 | 7 | [8 empty] | 457200
131 | Rampal 1320 MW (BIFPCL) | 786 | 625 | 624 | 630 | 630 | 557 | 562 | 562 | 561 | 562 | 560 | 601 | 608 | 610 | 617 | 619 | 590 | 472 |  | 553 | 605 | 613 | 617 | 621 | 619 | 618 | 14705450
132 | United Payra Power Ltd. | [20 empty] | 17 | [5 empty] | 8160
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 |  | 220 | 180 | 180 | 220 | 220 | 220 | 220 | 5021895
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 12 | 16 |  | 16 | 28 | [5 empty] | 50976
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 307 | 307 | 250 | 250 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 250 | 208 | 185 | 150 |  | 222 | 250 | 250 | 293 | 307 | 297 | 250 | 5607300
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 3717
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 120 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 126 | 126 | 124 | 124 | 126 | 80 |  | 124 | 80 | 80 | 126 | 126 | 128 | 128 | 2395000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 9 | 10 | 8 | 8 | 6 | 6 | 6 | 7 | 6 | 7 | 7 | 7 | 9 | 8 | 7 | 6 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 201147
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 44250
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 20 | 35 | [5 empty] | 26368
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 906 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 907 | 906 | 907 | 906 | 907 | 907 |  | 907 | 907 | 907 | 907 | 907 | 906 | 907 | 21978000
147 | Bheramara 410 MW CCPP | 304 | 303 | 304 | 303 | 309 | 305 | 315 | 317 | 343 | 325 | 345 | 325 | 303 | 305 | 305 | 302 | 305 | 308 |  | 250 | 303 | 304 | 395 | 395 | 397 | 397 | 7947072
148 | Payra 1320 MW | 1230 | 1244 | 1200 | 1080 | 980 | 800 | 780 | 780 | 830 | 1020 | 1100 | 1100 | 1100 | 1100 | 1120 | 1100 | 920 | 700 |  | 780 | 1010 | 1020 | 1100 | 1244 | 1244 | 1244 | 27182300
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 62 | 62 | 63 | 63 | 62 | 62 | 62 | 60 | 61 | 60 | 59 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 61 | 61 | 60 | 60 | 1425164
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 176 | 160 | 164 | 170 | 170 | 172 | 172 | 135 | 133 | 160 | 171 | 170 | 174 | 172 | 172 | 172 | 172 | 172 |  | 176 | 152 | 162 | 172 | 172 | 172 | 148 | 4071000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [20 empty] | 20 | 38 | 39 | 39 | 39 | 39 | 177670
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 3 | 1 | 2 | 3 | 6 | 6 | 3 | 4 | 3 | 0 | 0 | [8 empty] | 33420
| Sirajganj 68 MW Solar Park | [6 empty] | 6 | 18 | 32 | 27 | 48 | 65 | 58 | 45 | 43 | 31 | 8 | 3 | [8 empty] | 375750
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 157 | 168 | 154 | 147 | 148 | 144 | 145 | 145 | 159 | 156 | 159 | 159 | 179 | 176 | 177 | 172 | 172 | 140 |  | 145 | 158 | 151 | 162 | 174 | 174 | 181 | 3903727
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 162 | 174 | 159 | 147 | 151 | 148 | 148 | 155 | 171 | 167 | 172 | 171 | 197 | 190 | 183 | 178 | 178 | 169 |  | 145 | 147 | 149 | 169 | 183 | 182 | 189 | 4267145
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 310 | 310 | 310 | 344 | 347 | 340 | 347 | 347 | 347 | 346 | 347 | 395 | 361 | 397 | 394 | 358 | 318 | 347 |  | 300 | 310 | 347 | 414 | 414 | 414 | 414 | 8566036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [22 empty] | 4 | 5 | 8 | 11 | 20774
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 142326
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 12 | 16 | 25 | 46 | 42 | 42 | 40 | 155572
168 | Santahar 50 MW Peaking PP | 20 | [18 empty] | 32 | 35 | 35 | 28 | 30 | 35 | 22 | 187281
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 28 | 87 | 87 | 87 | 87 | 87 | 87 | 412800
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 16 | 35 | 50 | 50 | 100 | 113 | 113 | 460416
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 35 | 35 | 35 | 95 | 113 | 113 | 113 | 436800
173 | Rangpur 20 MW GTPP | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 107 | 100 | 104 | 56 | [7 empty] | 18 | 33 | 34 | 34 | 34 | 34 | 34 |  | 57 | 106 | 106 | 110 | 113 | 113 | 113 | 124783
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 6 | 7 | 7 | 7 | 8 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 53280
178 | Energypac Power Venture Thakurgaon Ltd. | 72 | 36 | 36 | 36 | 36 | [6 empty] | 17 | 35 | 35 | 35 | 35 | 35 |  |  | 75 | 98 | 115 | 115 | 115 | 115 | 115 | 1070016
| Intraco Solar 30 MW | [5 empty] | 1 | 4 | 7 | 26 | 22 | 36 | 27 | 35 | 8 | 24 | 20 | 13 | 2 |  | 0 | [6 empty] | 210329
| Adani Power Jharkhanda Ltd | 1351 | 1364 | 1347 | 1264 | 1263 | 1130 | 1117 | 1113 | 1117 | 1210 | 1210 | 1208 | 1208 | 1253 | 1316 | 1318 | 1117 | 1117 |  | 1391 | 1458 | 1458 | 1494 | 1509 | 1509 | 1510 | 30785803
178 | Teesta Solar Limited | [5 empty] | 2 | 10 | 27 | 57 | 140 | 149 | 209 | 96 | 117 | 150 | 124 | 21 | 12 | [8 empty] | 1207380