## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-07-31 | Wednesday
|  | Date (day): | 2024-07-31 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14487.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16160 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-07-30 | 2024-07-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Machine problem
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 352 | 356 | 350 | 350 | 50 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 6 | 12 | 15 | 16 | 84 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 151 | 150 | 152 | 183 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 51 | 85 | 85 | 85 | 17 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 25 | 55 | 30 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 17 | 17 | 17 | 17 | 83 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 328 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 49 | 8 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 132 | 64 | 132 |  | 17 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 28 | 28 | 28
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 35 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 22 | 22 |  | 11 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 6 | 6 | 6 | 6 |  | 27 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 260 | 145 | 260 |  | 40 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 80 | 118 | 100 | 118 |  | 31 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 72 | 17 | 72 | 33 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 13 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 |  | 38 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 2138 | 2513 | 2185 | 2518 | 2466 | 1149
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 17 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 3 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 47 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 198 | 200 | 200 | 200 | 30 |  | Low water lavel
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 220 | 220 | 220
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 1 | 85 | 50 | 85 |  | 20 | Engine problem
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 81 | 16 | 80 | 18 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 51 | 85 |  | 17 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 25 | 50 | 50 | 50 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 19 | 5 | 15
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 32 | 25 | 30 | 78 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 107 | 20 | 107 | 193 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 70 | 51 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 24 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 53 | 17 | 53 | 63 |  | Fuel shortage
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 108 | 17 | 163
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 990 | 592 | 612 | 612 |  |  | unit-1 under maint.
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 4 | 7 | 44 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 687 | 734 | 733 | 733
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 2173 | 2586 | 2216 | 2774 | 770 | 367
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 210 | 210 | 210
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 315 | 280 | 315 | 45 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 300 | 280 | 300 | 60 |  | Gas shortage
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 280 | 300 | 260 | 300 | 100 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 35 | 37 | 37 | 37 | 8 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 30 | 10 | 20 | 20 | 35 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 134 | 55 | 138 |  | 12 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 28 | 28 | 28 | 28 |  | 24 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 52 | 60 | 60 | 103 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 103 | 17 | 100 | 100 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 92 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 32 | 25 | 33 |  | 19 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 17 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 70 | 34 | 70 | 44 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 39 | 47 | 28 | 56 | 57 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 98 | 50 | 115
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 35 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2950 | 1509 | 1896 | 1612 | 1950 | 747 | 96
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 10 | 31 | 25 | 30 | 172 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 123 | 100 | 124 | 76 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 78 | 68 | 78 | 37 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 2 | 6 | 6 | 16 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 207 | 251 | 267.6 | 255 | 172 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 26 | 28 | 28 | 28 |  | 42 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 67 | 67 | 67 | 67 |  | 23 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 33 | 33 | 17 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 2 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 36 |  | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 136 | 136 | 136 |  | 95 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 379 | 388 | 360 | 380 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 220 | 255 | 260 | 260 |  | 123 | ST Under maint.
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1340 | 1386 | 1447 | 1467 | 73 | 629
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 916 | 782 | 915 | 915
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 62 | 32 | 64 |  | 51 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 6 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 0 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 268 | 265 | 290 | 290 | 120 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 16 | 24 | 16 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 87 | 17 | 87 | 18 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 41 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 560 | 618 | 620 | 620 | 614 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1802 | 1881 | 2020 | 2100 | 1455 | 114
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 16 | 64 | 46 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 126 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1020 | 1244 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 90 | 17 | 90 | 60 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 250 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1622 | 2004 | 1887 | 2065 | 106 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 37 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 35 | 0 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 191 | 181 | 160 | 180 | 30 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 351 | 350 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 85 | 50 | 86 |  | 18 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 39 | 113 | 70 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 60 | 55 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 6 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1409 | 1236 | 1498 | 1498
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 63 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 2184 | 2188 | 2314 | 2580 | 693 | 107
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 60 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 91 | 106 | 106 | 106
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 54 | 115 | 35 | 115 |  | 0 | Engine problem
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 200 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 600 | 451 | 539 | 451 | 40 | 214
| Total |  |  |  |  | 28098 | 26947 | 13575 | 15156 | 14487.6 | 16160 | 6522 | 2740
A. |  | 2024-07-30 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 15156 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12576 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 15750 | MW
3 | Day peak Generation : |  |  | 13575 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 15086.19 | MW
4 | Evening peak Generation : |  |  | 15156 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 567 | MW
5 | Total Energy Generation : |  | 330.7991 | MKWHr | By Solar | 3.2028 | MKWHr
| By Gas : | 126.7692 | MKWHr |  | By Oil: | 46.1424 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 125.7885 | MKWHr |  | By Hydro: | 4.8119 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.18048 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6522 | MW | Dhaka | 5189.59 | 5057.59 |  | 132 |  | 18:00 |  | 679
|  |  | For Plants S/D or M/C prob = |  |  | 2740 | MW | Chittagong | 1372.4 | 1372.4 |  | 0 |  | 19:00 |  | 688.555
|  |  | Total = |  |  | 9262 | MW | Khulna | 1870 | 1820 |  | 50 |  | 19:30 |  | 691.42
7 | Total Gas Supplied : |  |  | 942.3 | MMCFD |  |  | Rajshahi | 1717.2 | 1717.2 |  | 0 |  | 20:00 |  | 532.89
8 | Fuel Cost : | i) Gas : | Taka | 380818938.52 | ii) Oil : | Taka | 851925543.84 | Comilla | 1427 | 1372 |  | 55 |  | 21:00 |  | 567
|  | iii) Coal : | Taka | 852199347.58 | Total | Taka | 2084943829.94 | Mymensingh | 1300 | 1080 |  | 220 |  | 22:00 |  | 630.3
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7743.45 | MKWHr. | Sylhet | 649 | 634 |  | 15 |  | 23:00 |  | 1057.185
| ii) During Peak Demand : |  |  | 660 | MW (W to E) at | 21:00 | hrs | Barisal | 484 | 484 |  | 0 |  | 24:00 |  | 1370.425
| iii) Maximum : |  |  | 640 | MW at | 19:30 | hrs | Rangpur | 1077 | 982 |  | 95
10 | Maximum Temperature in Dhaka was |  |  |  | 31.4°C |  |  | Total | 15086.19 | 14519.19 |  | 567
B. |  | 2024-07-31 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.4°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 16000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16160 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14800 | MW
4 | Reserve(Generation end) |  |  |  |  | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 349.2205 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12697 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6604 | MKWHr. | ii) HVDC Flow at Peak Time |  | 782 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2435 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.02 |  | (b) Today: | 92.89 |  | (c) Rule Curve: |  | 88.83
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-07-30 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 450 | 151 | 15 | 51 | 25 | 330 | 0 | 0 | 11 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 22 | 22 | 6 | 0 | 0 | 119 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 48 | 68 | 0 | 12 | 0 | 0 | 32 | 0 | 0 | 0 | 300 | 280 | 211 | 0 | 50 | 25 | 5 | 0 | 51 | 0 | 27 | 15 | 0 | 0 | 0 | 17 | 102 | 30 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 130 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 200 | 0 | 0 | 95 | 0 | 64 | 0 | 12 | 17 | 123 | 365 | 58 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 34 | 12 | 220 | 0 | 0 | 162 | 0 | 0 | 17 | 0 | 83 | 17 | 230 | 17 | 0 | 1143 | 16 | 630 | 0 | 0 | 0 |  | 905 | 0 | 209 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 24 | 128 | 10 | 16 | 0 | 0 | 0 | 38 | 16 | 50 | 0 | 0 | 32 | 0 | 22 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 35 | 0 | 71 | 0 | 0 | 55 | 1244 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 623 | 0 | 250 | 1506 | 0 | 0 | 0 | 0 |  | 7613 | 6427 | 14040 | 3543 | 905 | 1796 | 0 | 1443 | 5626 | 199 | 0 | 410 | 102 | 0 | 16 | 1431 | 93.02
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 450 | 151 | 15 | 51 | 25 | 333 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 22 | 22 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 48 | 68 | 0 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 280 | 213 | 0 | 52 | 25 | 5 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 96 | 30 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 132 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 52 | 0 | 12 | 17 | 123 | 361 | 58 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 28 | 12 | 205 | 0 | 0 | 162 | 0 | 0 | 17 | 0 | 71 | 17 | 230 | 17 | 0 | 1150 | 16 | 628 | 0 | 0 | 0 |  | 904 | 0 | 216 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 8 | 128 | 10 | 16 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 59 | 0 | 170 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 35 | 0 | 71 | 0 | 0 | 35 | 1244 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 624 | 0 | 250 | 1518 | 0 | 0 | 0 | 0 |  | 7472 | 6288 | 13760 | 3520 | 904 | 1805 | 0 | 1320 | 5643 | 200 | 0 | 256 | 96 | 0 | 16 | 1361 | 93.02
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 |  | 0 | 450 | 153 | 15 | 51 | 25 | 333 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 22 | 24 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 48 | 51 | 0 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 280 | 213 | 0 | 51 | 25 | 5 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 98 | 31 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 52 | 0 | 12 | 17 | 125 | 348 | 58 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 28 | 12 | 205 | 0 | 0 | 162 | 0 | 0 | 17 | 0 | 72 | 17 | 230 | 17 | 0 | 1096 | 20 | 628 | 0 | 0 | 0 |  | 915 | 0 | 224 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 8 | 128 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1244 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 622 | 0 | 250 | 1508 | 0 | 0 | 0 | 0 |  | 7382 | 6282 | 13664 | 3521 | 915 | 1802 | 0 | 1322 | 5578 | 200 | 0 | 208 | 98 | 0 | 20 | 1182 | 93.02
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 |  | 0 | 450 | 152 | 15 | 51 | 25 | 330 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 22 | 24 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 48 | 34 | 0 | 12 | 0 | 0 | 35 | 0 | 0 | 0 | 290 | 280 | 212 | 0 | 70 | 25 | 5 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 100 | 31 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 52 | 0 | 12 | 17 | 120 | 355 | 58 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 28 | 12 | 215 | 0 | 0 | 162 | 0 | 0 | 17 | 0 | 69 | 17 | 230 | 17 | 0 | 1045 | 44 | 630 | 0 | 0 | 0 |  | 916 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 35 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 1244 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 565 | 0 | 250 | 1480 | 0 | 0 | 0 | 0 |  | 7374 | 6052 | 13426 | 3467 | 916 | 1750 | 0 | 1314 | 5444 | 200 | 0 | 191 | 100 | 0 | 44 | 978 | 93.02
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 151 | 15 | 51 | 25 | 330 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 14 | 22 | 24 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 285 | 280 | 213 | 0 | 70 | 35 | 10 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 100 | 32 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 52 | 0 | 12 | 17 | 120 | 349 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 29 | 12 | 210 | 0 | 0 | 162 | 0 | 0 | 17 | 0 | 37 | 17 | 230 | 0 | 0 | 1047 | 3 | 628 | 0 | 0 | 0 |  | 916 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 35 | 0 | 71 | 0 | 0 | 35 | 1244 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 562 | 0 | 291 | 1522 | 0 | 0 | 0 | 0 |  | 7204 | 6046 | 13250 | 3494 | 916 | 1765 | 0 | 1166 | 5524 | 200 | 0 | 82 | 100 | 0 | 3 | 885 | 93.02
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 154 | 15 | 51 | 25 | 333 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 14 | 22 | 24 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 50 | 35 | 25 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 100 | 32 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 51 | 0 | 12 | 17 | 10 | 328 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 12 | 180 | 0 | 2 | 162 | 0 | 0 | 17 | 1 | 35 | 17 | 260 | 0 | 0 | 950 | 3 | 628 | 0 | 0 | 0 |  | 917 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 1120 | 180 | 0 | 0 | 0 | 2 | 35 | 0 | 0 | 564 | 1 | 307 | 1510 | 2 | 0 | 0 | 0 |  | 6933 | 5758 | 12691 | 3407 | 917 | 1689 | 0 | 998 | 5309 | 200 | 0 | 60 | 100 | 8 | 3 | 846 | 93.02
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 450 | 151 | 16 | 51 | 25 | 280 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 14 | 22 | 0 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 350 | 350 | 194 | 0 | 50 | 36 | 39 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 94 | 32 | 0 | 0 | 0 | 26 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 95 | 0 | 0 | 95 | 0 | 52 | 0 | 12 | 17 | 10 | 315 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 12 | 188 | 17 | 8 | 126 | 0 | 0 | 17 | 1 | 35 | 17 | 300 | 0 | 0 | 950 | 0 | 637 | 0 | 0 | 2 |  | 916 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 71 | 0 | 1 | 0 | 1100 | 180 | 0 | 0 | 0 | 12 | 35 | 0 | 0 | 564 | 4 | 307 | 1454 | 27 | 0 | 0 | 7 |  | 7009 | 5739 | 12748 | 3513 | 916 | 1703 | 0 | 957 | 5243 | 200 | 0 | 60 | 94 | 62 | 0 | 622.66 | 93.02
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 450 | 152 | 15 | 51 | 25 | 333 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 14 | 15 | 0 | 6 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 240 | 211 | 0 | 70 | 36 | 30 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 88 | 27 | 0 | 0 | 0 | 26 | 68 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 95 | 0 | 0 | 95 | 0 | 53 | 0 | 12 | 17 | 10 | 312 | 58 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 28 | 12 | 180 | 17 | 18 | 126 | 0 | 0 | 17 | 3 | 35 | 17 | 230 | 0 | 0 | 950 | 3 | 636 | 0 | 0 | 10 |  | 916 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 71 | 0 | 2 | 0 | 1100 | 220 | 0 | 0 | 2 | 20 | 35 | 0 | 0 | 562 | 8 | 250 | 1436 | 51 | 0 | 0 | 10 |  | 6825 | 5751 | 12576 | 3345 | 916 | 1717 | 0 | 958 | 5165 | 199 | 0 | 60 | 88 | 125 | 3 | 643.67 | 93.01
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 152 | 15 | 51 | 25 | 329 | 0 | 0 | 9 | 8 | 36 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 14 | 15 | 0 | 6 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 240 | 211 | 0 | 50 | 37 | 12 | 0 | 51 | 0 | 28 | 15 | 0 | 0 | 0 | 17 | 80 | 27 | 0 | 0 | 1 | 26 | 68 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 95 | 0 | 0 | 95 | 0 | 53 | 2 | 12 | 17 | 10 | 312 | 58 | 52 | 0 | 3 | 0 | 0 | 0 | 17 | 28 | 12 | 205 | 17 | 16 | 126 | 0 | 0 | 17 | 9 | 50 | 17 | 230 | 0 | 0 | 950 | 3 | 634 | 0 | 0 | 21 |  | 916 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 2 | 0 | 0 | 0 | 76 | 0 | 3 | 0 | 1100 | 220 | 0 | 0 | 1 | 27 | 35 | 0 | 0 | 561 | 20 | 250 | 1416 | 131 | 0 | 0 | 13 |  | 6902 | 5841 | 12743 | 3377 | 916 | 1700 | 0 | 1015 | 5142 | 199 | 0 | 64 | 80 | 247 | 3 | 722.935 | 93.01
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 154 | 11 | 51 | 25 | 332 | 0 | 0 | 9 | 8 | 81 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 15 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 212 | 0 | 50 | 36 | 25 | 0 | 51 | 0 | 28 | 16 | 0 | 0 | 0 | 17 | 84 | 25 | 0 | 0 | 1 | 26 | 69 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 105 | 0 | 0 | 95 | 0 | 53 | 3 | 12 | 17 | 20 | 350 | 58 | 70 | 0 | 4 | 0 | 0 | 0 | 17 | 28 | 12 | 200 | 17 | 43 | 152 | 0 | 0 | 17 | 17 | 48 | 17 | 250 | 0 | 0 | 950 | 4 | 635 | 0 | 0 | 18 |  | 916 | 0 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 130 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 79 | 0 | 4 | 10 | 1100 | 220 | 0 | 0 | 5 | 51 | 35 | 0 | 0 | 561 | 17 | 250 | 1412 | 173 | 0 | 0 | 45 |  | 7132 | 6072 | 13204 | 3518 | 916 | 1793 | 0 | 1102 | 5099 | 198 | 0 | 109 | 84 | 381 | 4 | 664.68 | 93.01
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 |  | 0 | 450 | 155 | 0 | 51 | 25 | 332 | 0 | 0 | 10 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 15 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 210 | 0 | 50 | 36 | 30 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 17 | 84 | 10 | 0 | 0 | 1 | 26 | 68 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 146 | 0 | 0 | 95 | 0 | 72 | 3 | 12 | 17 | 47 | 363 | 58 | 70 | 0 | 5 | 0 | 0 | 0 | 17 | 28 | 12 | 200 | 20 | 25 | 162 | 0 | 0 | 17 | 18 | 48 | 17 | 250 | 0 | 0 | 950 | 0 | 633 | 0 | 0 | 32 |  | 915 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 170 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 25 | 0 | 85 | 0 | 6 | 35 | 1040 | 220 | 0 | 0 | 3 | 72 | 35 | 0 | 0 | 561 | 15 | 250 | 1414 | 197 | 0 | 0 | 25 |  | 7166 | 6154 | 13320 | 3496 | 915 | 1780 | 0 | 1256 | 5079 | 198 | 0 | 110 | 84 | 402 | 0 | 697.15 | 93.01
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 152 | 6 | 51 | 25 | 328 | 0 | 0 | 17 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 23 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 207 | 0 | 40 | 35 | 30 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 0 | 88 | 10 | 0 | 0 | 1 | 26 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 80 | 3 | 25 | 17 | 50 | 379 | 58 | 70 | 1 | 5 | 15 | 0 | 0 | 17 | 39 | 25 | 220 | 17 | 26 | 162 | 0 | 0 | 17 | 13 | 48 | 17 | 280 | 0 | 0 | 990 | 4 | 687 | 0 | 0 | 35 |  | 916 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 170 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 39 | 0 | 91 | 0 | 6 | 60 | 1020 | 220 | 0 | 0 | 6 | 41 | 54 | 0 | 0 | 560 | 19 | 250 | 1409 | 200 | 0 | 0 | 63 |  | 7367 | 6208 | 13575 | 3522 | 916 | 1786 | 0 | 1387 | 5146 | 198 | 0 | 110 | 88 | 418 | 4 | 759.225 | 93.01
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 152 | 7 | 36 | 25 | 330 | 0 | 0 | 17 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 280 | 240 | 199 | 0 | 40 | 35 | 30 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 17 | 100 | 10 | 0 | 0 | 2 | 26 | 67 | 0 | 0 | 163 | 0 | 29 | 0 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 76 | 0 | 25 | 17 | 55 | 357 | 58 | 70 | 17 | 1 | 15 | 0 | 0 | 17 | 37 | 25 | 200 | 17 | 33 | 162 | 0 | 0 | 17 | 16 | 48 | 17 | 280 | 0 | 0 | 1005 | 3 | 712 | 0 | 0 | 47 |  | 916 | 0 | 257 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 170 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 91 | 0 | 7 | 70 | 1020 | 220 | 0 | 0 | 5 | 30 | 54 | 0 | 0 | 559 | 25 | 250 | 1422 | 142 | 0 | 0 | 61 |  | 7414 | 6200 | 13614 | 3473 | 916 | 1801 | 0 | 1446 | 5198 | 198 | 0 | 110 | 100 | 369 | 3 | 846.13 | 93.01
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 152 | 7 | 34 | 19 | 327 | 0 | 0 | 17 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 206 | 0 | 40 | 36 | 27 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 17 | 92 | 10 | 0 | 0 | 2 | 26 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 78 | 0 | 25 | 17 | 55 | 352 | 58 | 70 | 17 | 1 | 15 | 0 | 0 | 17 | 37 | 25 | 200 | 17 | 53 | 162 | 0 | 0 | 17 | 27 | 49 | 17 | 250 | 17 | 0 | 950 | 0 | 751 | 0 | 0 | 37 |  | 915 | 0 | 258 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 90 | 0 | 6 | 70 | 1020 | 220 | 0 | 0 | 5 | 29 | 54 | 0 | 0 | 559 | 32 | 250 | 1410 | 151 | 0 | 0 | 48 |  | 7370 | 6192 | 13562 | 3442 | 915 | 1786 | 0 | 1440 | 5171 | 198 | 0 | 127 | 92 | 391 | 0 | 848.04 | 93.01
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 152 | 8 | 34 | 25 | 327 | 0 | 0 | 17 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 209 | 0 | 40 | 36 | 16 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 17 | 94 | 10 | 0 | 0 | 1 | 28 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 145 | 0 | 0 | 94 | 0 | 76 | 1 | 25 | 17 | 53 | 350 | 58 | 35 | 17 | 1 | 15 | 0 | 0 | 17 | 36 | 25 | 200 | 17 | 3 | 162 | 0 | 0 | 17 | 19 | 49 | 17 | 250 | 17 | 0 | 950 | 0 | 731 | 0 | 0 | 55 |  | 916 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 89 | 0 | 7 | 55 | 1030 | 220 | 0 | 0 | 3 | 33 | 54 | 0 | 0 | 562 | 24 | 250 | 1367 | 149 | 0 | 0 | 50 |  | 7290 | 6135 | 13425 | 3437 | 916 | 1786 | 0 | 1399 | 5120 | 200 | 0 | 127 | 94 | 346 | 0 | 1074.375 | 93.01
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 151 | 14 | 34 | 25 | 324 | 0 | 0 | 17 | 8 | 95 | 13 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 3 | 0 | 0 | 25 | 11 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 208 | 0 | 40 | 36 | 10 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 17 | 92 | 18 | 0 | 0 | 1 | 28 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 82 | 0 | 25 | 17 | 55 | 350 | 58 | 17 | 17 | 1 | 15 | 0 | 0 | 17 | 36 | 25 | 245 | 17 | 4 | 162 | 0 | 0 | 17 | 15 | 54 | 10 | 250 | 17 | 0 | 953 | 4 | 730 | 0 | 0 | 38 |  | 915 | 0 | 255 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 89 | 0 | 3 | 55 | 1030 | 180 | 0 | 0 | 1 | 27 | 54 | 0 | 0 | 566 | 21 | 250 | 1353 | 109 | 0 | 0 | 24 |  | 7363 | 6002 | 13365 | 3443 | 915 | 1726 | 0 | 1488 | 5113 | 200 | 0 | 140 | 92 | 244 | 4 | 988.425 | 93
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 152 | 11 | 34 | 25 | 328 | 0 | 0 | 17 | 8 | 98 | 13 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 9 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 25 | 12 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 240 | 210 | 0 | 40 | 36 | 10 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 17 | 92 | 28 | 0 | 0 | 0 | 28 | 68 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 145 | 0 | 0 | 95 | 0 | 78 | 1 | 25 | 17 | 63 | 350 | 58 | 17 | 17 | 0 | 15 | 0 | 0 | 17 | 45 | 25 | 250 | 17 | 1 | 162 | 0 | 0 | 17 | 6 | 67 | 17 | 250 | 17 | 0 | 948 | 1 | 728 | 0 | 0 | 14 |  | 916 | 0 | 253 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 80 | 8 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 35 | 0 | 15 | 0 | 15 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 55 | 0 | 83 | 0 | 0 | 55 | 1030 | 180 | 0 | 0 | 0 | 21 | 54 | 0 | 0 | 562 | 9 | 250 | 1304 | 58 | 0 | 0 | 9 |  | 7370 | 5895 | 13265 | 3463 | 916 | 1720 | 0 | 1525 | 5052 | 200 | 0 | 177 | 92 | 119 | 1 | 797.425 | 92.99
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 450 | 154 | 16 | 51 | 25 | 307 | 0 | 0 | 17 | 8 | 98 | 13 | 0 | 0 | 0 | 54 | 17 | 45 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 25 | 12 | 0 | 0 | 4 | 0 | 0 | 0 | 310 | 240 | 212 | 0 | 40 | 36 | 10 | 0 | 51 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 82 | 27 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 120 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 180 | 0 | 0 | 95 | 0 | 90 | 0 | 25 | 17 | 102 | 291 | 58 | 17 | 19 | 0 | 30 | 2 | 1 | 34 | 46 | 25 | 210 | 17 | 1 | 162 | 0 | 0 | 17 | 1 | 65 | 17 | 250 | 17 | 0 | 485 | 8 | 723 | 0 | 0 | 6 |  | 915 | 0 | 253 | 0 | 21 | 0 | 0 | 0 | 10 | 0 | 16 | 80 | 8 | 16 | 0 | 0 | 0 | 38 | 5 | 80 | 35 | 0 | 20 | 0 | 15 | 0 | 0 | 5 | 61 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 17 | 0 | 67 | 0 | 89 | 0 | 1 | 55 | 1030 | 180 | 0 | 5 | 0 | 4 | 74 | 0 | 0 | 506 | 1 | 285 | 1305 | 17 | 0 | 0 | 2 |  | 6933 | 5856 | 12789 | 3348 | 915 | 1567 | 0 | 1760 | 4565 | 200 | 0 | 311 | 82 | 33 | 8 | 679 | 92.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 151 | 15 | 68 | 25 | 310 | 0 | 0 | 17 | 48 | 115 | 13 | 0 | 0 | 0 | 54 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 76 | 85 | 25 | 23 | 26 | 0 | 11 | 0 | 0 | 0 | 280 | 270 | 211 | 0 | 42 | 36 | 10 | 0 | 51 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 100 | 28 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 120 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 265 | 12 | 2 | 0 | 255 | 0 | 0 | 122 | 0 | 94 | 0 | 25 | 44 | 125 | 291 | 77 | 72 | 85 | 0 | 100 | 51 | 51 | 34 | 46 | 25 | 220 | 17 | 0 | 162 | 32 | 0 | 17 | 0 | 74 | 17 | 230 | 108 | 0 | 565 | 5 | 732 | 0 | 0 | 0 |  | 916 | 0 | 256 | 0 | 35 | 0 | 0 | 0 | 33 | 21 | 16 | 130 | 10 | 32 | 0 | 0 | 0 | 38 | 13 | 85 | 35 | 0 | 42 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 170 | 17 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 20 | 0 | 110 | 0 | 91 | 0 | 0 | 55 | 980 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 307 | 1269 | 0 | 0 | 0 | 0 |  | 7906 | 6373 | 14279 | 3385 | 916 | 1702 | 0 | 2584 | 4701 | 200 | 17 | 669 | 100 | 0 | 5 | 688.555 | 92.95
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 153 | 16 | 80 | 55 | 331 | 0 | 0 | 17 | 49 | 115 | 13 | 0 | 0 | 0 | 54 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 80 | 85 | 25 | 32 | 44 | 0 | 15 | 0 | 0 | 0 | 280 | 270 | 211 | 0 | 45 | 36 | 10 | 0 | 51 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 94 | 28 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 136 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 262 | 0 | 0 | 122 | 0 | 107 | 0 | 25 | 103 | 129 | 385 | 77 | 72 | 85 | 0 | 100 | 54 | 70 | 34 | 46 | 25 | 210 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 105 | 17 | 230 | 108 | 0 | 603 | 4 | 732 | 0 | 0 | 0 |  | 917 | 0 | 261 | 0 | 32 | 0 | 0 | 0 | 39 | 41 | 16 | 126 | 10 | 48 | 0 | 0 | 0 | 37 | 15 | 85 | 35 | 0 | 42 | 0 | 25 | 0 | 0 | 5 | 62 | 0 | 170 | 16 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 53 | 0 | 113 | 0 | 98 | 0 | 0 | 55 | 1210 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1260 | 0 | 0 | 0 | 0 |  | 8352 | 6694 | 15046 | 3527 | 917 | 1756 | 0 | 2868 | 4964 | 200 | 16 | 700 | 94 | 0 | 4 | 691.42 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 450 | 154 | 16 | 85 | 55 | 333 | 0 | 0 | 17 | 49 | 132 | 13 | 0 | 0 | 0 | 54 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 17 | 0 | 120 | 80 | 0 | 0 | 17 | 222 | 0 | 0 | 0 |  | 6 | 80 | 85 | 25 | 32 | 46 | 0 | 19 | 0 | 0 | 0 | 285 | 270 | 214 | 0 | 52 | 37 | 10 | 0 | 51 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 92 | 30 | 0 | 0 | 0 | 28 | 68 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 258 | 0 | 0 | 122 | 0 | 100 | 0 | 25 | 103 | 129 | 386 | 76 | 72 | 85 | 0 | 100 | 54 | 70 | 34 | 47 | 25 | 210 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 97 | 17 | 230 | 108 | 0 | 593 | 12 | 729 | 0 | 0 | 0 |  | 916 | 0 | 260 | 0 | 57 | 0 | 0 | 0 | 0 | 55 | 16 | 126 | 10 | 48 | 0 | 0 | 0 | 37 | 18 | 85 | 35 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 170 | 16 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 80 | 0 | 113 | 0 | 105 | 0 | 0 | 55 | 1220 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1259 | 0 | 0 | 0 | 0 |  | 8374 | 6668 | 15042 | 3550 | 916 | 1669 | 0 | 2924 | 4961 | 200 | 16 | 702 | 92 | 0 | 12 | 532.89 | 92.96
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 |  | 0 | 450 | 151 | 12 | 85 | 55 | 328 | 0 | 0 | 17 | 49 | 132 | 13 | 0 | 0 | 0 | 54 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 17 | 0 | 120 | 80 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 2 | 81 | 85 | 25 | 32 | 47 | 0 | 19 | 0 | 0 | 0 | 315 | 300 | 210 | 0 | 52 | 37 | 10 | 0 | 51 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 92 | 31 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 260 | 0 | 0 | 123 | 0 | 118 | 0 | 25 | 103 | 134 | 388 | 78 | 72 | 85 | 0 | 107 | 54 | 70 | 70 | 47 | 25 | 255 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 98 | 17 | 300 | 108 | 0 | 592 | 7 | 734 | 0 | 0 | 0 |  | 782 | 0 | 265 | 0 | 62 | 0 | 0 | 0 | 6 | 45 | 16 | 126 | 10 | 64 | 0 | 0 | 0 | 37 | 20 | 85 | 35 | 0 | 42 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 87 | 0 | 113 | 0 | 106 | 0 | 0 | 55 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 250 | 1236 | 0 | 0 | 0 | 0 |  | 8632 | 6524 | 15156 | 3726 | 782 | 1730 | 0 | 3018 | 4904 | 200 | 0 | 697 | 92 | 0 | 7 | 567 | 92.95
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 |  | 0 | 450 | 150 | 17 | 85 | 33 | 323 | 0 | 0 | 17 | 49 | 132 | 13 | 0 | 0 | 0 | 35 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 17 | 0 | 118 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 81 | 85 | 25 | 38 | 29 | 0 | 28 | 0 | 0 | 0 | 280 | 270 | 193 | 0 | 52 | 37 | 10 | 0 | 51 | 0 | 28 | 33 | 0 | 0 | 0 | 17 | 94 | 30 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 265 | 0 | 0 | 123 | 0 | 112 | 0 | 25 | 103 | 120 | 388 | 78 | 72 | 85 | 0 | 107 | 54 | 89 | 70 | 46 | 25 | 251 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 81 | 17 | 250 | 17 | 0 | 614 | 2 | 733 | 0 | 0 | 0 |  | 782 | 0 | 269 | 0 | 70 | 0 | 0 | 0 | 20 | 33 | 16 | 124 | 10 | 80 | 0 | 0 | 0 | 37 | 24 | 85 | 35 | 0 | 42 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 89 | 0 | 113 | 0 | 106 | 0 | 0 | 55 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 250 | 1205 | 0 | 0 | 0 | 0 |  | 8352 | 6588 | 14940 | 3586 | 782 | 1801 | 0 | 2972 | 4896 | 198 | 0 | 609 | 94 | 0 | 2 | 630.3 | 92.94
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 |  | 0 | 450 | 150 | 8 | 85 | 30 | 326 | 0 | 0 | 17 | 49 | 116 | 13 | 0 | 0 | 0 | 35 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 17 | 0 | 118 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 81 | 80 | 25 | 38 | 26 | 0 | 32 | 0 | 0 | 0 | 280 | 270 | 202 | 0 | 51 | 37 | 10 | 0 | 51 | 0 | 28 | 16 | 0 | 0 | 0 | 17 | 102 | 30 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 270 | 0 | 0 | 123 | 0 | 116 | 0 | 25 | 103 | 98 | 389 | 78 | 35 | 85 | 0 | 107 | 54 | 89 | 70 | 47 | 25 | 245 | 0 | 0 | 162 | 53 | 0 | 17 | 0 | 53 | 17 | 250 | 17 | 0 | 615 | 6 | 734 | 0 | 0 | 0 |  | 783 | 0 | 269 | 0 | 80 | 0 | 0 | 0 | 21 | 31 | 16 | 124 | 10 | 105 | 0 | 0 | 0 | 37 | 24 | 85 | 35 | 0 | 42 | 0 | 22 | 0 | 0 | 8 | 60 | 0 | 170 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 89 | 0 | 55 | 0 | 106 | 0 | 0 | 55 | 1244 | 220 | 0 | 54 | 0 | 0 | 56 | 0 | 0 | 619 | 0 | 250 | 1213 | 0 | 0 | 0 | 0 |  | 8215 | 6478 | 14693 | 3595 | 783 | 1800 | 0 | 2720 | 4905 | 198 | 0 | 584 | 102 | 0 | 6 | 1057.185 | 92.93
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 |  | 0 | 450 | 154 | 9 | 85 | 30 | 333 | 0 | 0 | 17 | 16 | 82 | 13 | 0 | 0 | 0 | 35 | 28 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 3 | 80 | 68 | 25 | 39 | 26 | 0 | 29 | 0 | 0 | 0 | 280 | 270 | 205 | 0 | 50 | 37 | 10 | 0 | 51 | 0 | 28 | 16 | 0 | 0 | 0 | 17 | 106 | 32 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 134 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 175 | 0 | 0 | 125 | 0 | 115 | 0 | 25 | 103 | 95 | 387 | 78 | 17 | 85 | 0 | 107 | 54 | 89 | 34 | 32 | 25 | 250 | 0 | 0 | 162 | 53 | 0 | 17 | 0 | 49 | 17 | 250 | 17 | 0 | 612 | 3 | 731 | 0 | 0 | 0 |  | 782 | 0 | 269 | 0 | 79 | 0 | 0 | 0 | 10 | 29 | 16 | 128 | 10 | 110 | 0 | 0 | 0 | 30 | 22 | 85 | 35 | 0 | 42 | 0 | 22 | 0 | 0 | 8 | 60 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 88 | 0 | 55 | 0 | 106 | 0 | 0 | 55 | 1244 | 220 | 0 | 54 | 0 | 0 | 35 | 0 | 0 | 618 | 0 | 250 | 1160 | 0 | 0 | 0 | 0 |  | 7950 | 6365 | 14315 | 3611 | 782 | 1780 | 0 | 2475 | 4845 | 198 | 0 | 515 | 106 | 0 | 3 | 1370.425 | 92.92
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8910000 | 0 |  | 0 | 9978500 | 3629818 | 303360 | 1218668 | 681948 | 7802231 | 0 | 0 | 299520 | 382608 | 1842720 | 107000 | 0 | 0 | 0 | 1256400 | 183317 | 792167 | 0 | 321600 | 501480 | 516240 | 137900 | 172800 | 0 | 2871867 | 1940000 | 0 | 0 | 84483 | 5263371 | 0 | 0 | 0 |  | 101760 | 641712 | 676197 | 186960 | 305280 | 180960 | 0 | 440160 | 0 | 0 | 0 | 7318500 | 6395000 | 5067000 | 0 | 1164300 | 817488 | 388800 | 0 | 1150400 | 0 | 671968 | 515741 | 0 | 0 | 0 | 408630 | 2243520 | 526080 | 0 | 0 | 9600 | 640000 | 1595760 | 0 | 0 | 3714709 | 0 | 726240 | 0 | 0 | 3237210 | 0 | 0 | 0 | 7327000 | 278256 | 102384 | 0 | 4052180 | 0 | 0 | 2455200 | 0 | 1850400 | 13365 | 442560 | 885120 | 1980509 | 8920000 | 1502400 | 927360 | 632291 | 24238 | 817964 | 25679 | 465020 | 637260 | 867720 | 432960 | 5300800 | 268800 | 202560 | 3794400 | 303600 | 0 | 431640 | 162292 | 1430400 | 425880 | 6186000 | 515200 | 0 | 21359998 | 180480 | 16458181 | 0 | 0 | 350018 |  | 21660363 | 0 | 6180480 | 0 | 583680 | 0 | 0 | 0 | 128640 | 183168 | 189375 | 2611000 | 201437 | 567456 | 0 | 0 | 0 | 305102 | 145403 | 616576 | 292630 | 0 | 265801 | 0 | 233932 | 0 | 0 | 116190 | 1395054 | 0 | 4110000 | 25000 | 0 | 4353273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9295345 | 749760 | 0 | 1205952 | 0 | 2031091 | 0 | 40595 | 1017888 | 29185200 | 5245593 | 0 | 465600 | 34620 | 367920 | 1385280 | 0 | 0 | 13963640 | 221118 | 6196400 | 33120000 | 1414690 | 0 | 1774 | 360000 |  | 180332088 | 150467026 | 330799114 | 85397413 | 21660363 | 41371762 | 0 | 39891027 | 125788473 | 4811867 | 25000 | 6226419 | 2243520 | 3202790 | 180480 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25660800 | 0 |  | 0 | 31731630 | 12413977.56 | 5994393.6 | 22789091.6 | 12015923.76 | 23796804.55 | 0 | 0 | 5918515.2 | 6867813.6 | 35785622.4 | 1995550 | 0 | 0 | 0 | 22941864 | 2889075.92 | 14488734.43 | 0 | 241200 | 0 | 0 | 0 | 3094848 | 0 | 0 | 0 | 0 | 0 | 1600108.02 | 16790153.49 | 0 | 0 | 0 |  | 1789958.4 | 11300548.32 | 12110688.27 | 3563457.6 | 5974329.6 | 2978601.6 | 0 | 0 | 0 | 0 | 0 | 20418615 | 19568700 | 16822440 | 0 | 3760689 | 2754934.56 | 1702944 | 0 | 4613104 | 0 | 12034946.88 | 9314282.46 | 0 | 0 | 0 | 306472.5 | 14717491.2 | 1636108.8 | 0 | 0 | 0 | 2496000 | 5952184.8 | 0 | 0 | 12704304.78 | 0 | 4030632 | 0 | 0 | 9031815.9 | 0 | 0 | 0 | 22640430 | 208692 | 77811.84 | 0 | 82664472 | 0 | 0 | 47164392 | 0 | 32585544 | 0 | 7881993.6 | 15356832 | 32836839.22 | 23638000 | 28635744 | 17397273.6 | 11343300.54 | 0 | 13373711.4 | 499199.76 | 8342458.8 | 12178038.6 | 16842445.2 | 7711017.6 | 14100128 | 4588416 | 0 | 69399576 | 5094408 | 0 | 7713406.8 | 0 | 25775808 | 7214407.2 | 18372420 | 7254016 | 0 | 148879186.06 | 0 | 97103267.9 | 0 | 0 | 0 |  | 60865620.03 | 0 | 18232416 | 0 | 10126848 | 0 | 0 | 0 | 2419718.4 | 3445390.08 | 3370875 | 8250760 | 954811.38 | 9782941.44 | 0 | 0 | 0 | 5464376.82 | 2668145.05 | 10364642.56 | 6227166.4 | 0 | 4760495.91 | 0 | 4189722.12 | 0 | 0 | 87955.83 | 15387445.62 | 0 | 34688400 | 1397500 | 0 | 14365800.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27142407.4 | 12805900.8 | 0 | 23901968.64 | 0 | 40459332.72 | 0 | 0 | 20194897.92 | 189120096 | 16313794.23 | 0 | 9009360 | 0 | 0 | 24034608 | 0 | 0 | 101934572 | 0 | 46163180 | 218923200 | 0 | 0 | 0 | 0 |  | 1213472591.92 | 947054349.25 | 2160526941.17 | 250601535.17 | 60865620.03 | 130217403.35 | 0 | 738729731.03 | 852199347.58 | 0 | 1397500 | 111798312.81 | 14717491.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 |  | 0 | 450 | 152 | 6 | 51 | 25 | 328 | 0 | 0 | 17 | 8 | 82 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 23 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 240 | 207 | 0 | 40 | 35 | 30 | 0 | 51 | 0 | 28 | 24 | 0 | 0 | 0 | 0 | 88 | 10 | 0 | 0 | 1 | 26 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 80 | 3 | 25 | 17 | 50 | 379 | 58 | 70 | 1 | 5 | 15 | 0 | 0 | 17 | 39 | 25 | 220 | 17 | 26 | 162 | 0 | 0 | 17 | 13 | 48 | 17 | 280 | 0 | 0 | 990 | 4 | 687 | 0 | 0 | 35 |  | 916 | 0 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 170 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 39 | 0 | 91 | 0 | 6 | 60 | 1020 | 220 | 0 | 0 | 6 | 41 | 54 | 0 | 0 | 560 | 19 | 250 | 1409 | 200 | 0 | 0 | 63 |  | 13575 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 |  | 0 | 450 | 151 | 12 | 85 | 55 | 328 | 0 | 0 | 17 | 49 | 132 | 13 | 0 | 0 | 0 | 54 | 28 | 55 | 0 | 13 | 22 | 24 | 6 | 17 | 0 | 120 | 80 | 0 | 0 | 17 | 220 | 0 | 0 | 0 | 0 | 2 | 81 | 85 | 25 | 32 | 47 | 0 | 19 | 0 | 0 | 0 | 315 | 300 | 210 | 0 | 52 | 37 | 10 | 0 | 51 | 0 | 28 | 32 | 0 | 0 | 0 | 17 | 92 | 31 | 0 | 0 | 0 | 28 | 67 | 0 | 0 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 260 | 0 | 0 | 123 | 0 | 118 | 0 | 25 | 103 | 134 | 388 | 78 | 72 | 85 | 0 | 107 | 54 | 70 | 70 | 47 | 25 | 255 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 98 | 17 | 300 | 108 | 0 | 592 | 7 | 734 | 0 | 0 | 0 |  | 782 | 0 | 265 | 0 | 62 | 0 | 0 | 0 | 6 | 45 | 16 | 126 | 10 | 64 | 0 | 0 | 0 | 37 | 20 | 85 | 35 | 0 | 42 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 87 | 0 | 113 | 0 | 106 | 0 | 0 | 55 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 250 | 1236 | 0 | 0 | 0 | 0 |  | 15156 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 450 | 152 | 16 | 85 | 55 | 335 | 0 | 0 | 17 | 50 | 132 | 13 | 0 | 0 | 0 | 54 | 28 | 55 | 0 | 13 | 22 | 22 | 6 | 17 | 0 | 120 | 80 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 80 | 85 | 50 | 30 | 50 | 0 | 15 | 0 | 0 | 0 | 315 | 300 | 210 | 0 | 60 | 37 | 20 | 0 | 51 | 0 | 28 | 33 | 0 | 0 |  | 17 | 100 | 30 | 0 | 0 | 0 | 28 | 67 | 50 | 33 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 260 | 0 | 0 | 124 | 0 | 118 | 0 | 25 | 100 | 138 | 380 | 78 | 72 | 85 | 0 | 107 | 54 | 110 | 70 | 56 | 25 | 260 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 115 | 17 | 300 | 163 | 0 | 612 | 60 | 733 | 0 | 0 |  |  | 915 | 0 | 290 | 0 | 64 | 0 | 0 | 0 | 40 | 60 | 24 | 130 | 10 | 64 | 0 | 0 | 0 | 40 | 20 | 86 | 35 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 87 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1498 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 450 | 150 | 15 | 85 | 30 | 335 | 0 | 0 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 28 | 35 | 0 | 13 | 22 | 22 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 16 | 51 | 50 | 25 | 6 | 0 | 5 | 0 | 0 | 0 | 280 | 280 | 210 | 0 | 60 | 37 | 20 | 0 | 51 | 0 | 28 | 25 | 0 | 0 |  | 17 | 90 | 25 | 0 | 0 | 1.6 | 28 | 67 | 50 | 33 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 100 | 0 | 100 | 20 | 25 | 17 | 55 | 360 | 68 | 17 | 50 | 5 | 20 | 17 | 51 | 34 | 28 | 24 | 260 | 17 | 50 | 162 | 17 | 0 | 17 | 35 | 50 | 17 | 260 | 17 | 0 | 612 | 44 | 733 | 0 | 0 | 70 |  | 915 | 0 | 290 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 70 | 0 | 106 | 0 | 8 | 70 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 620 | 30 | 250 | 1498 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 450 | 154 | 8 | 85 | 15 | 335 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 280 | 270 | 212 | 0 | 50 | 37 | 10 | 0 | 51 | 0 | 21 | 15 | 0 | 0 | 0 | 17 | 86 | 28 | 0 | 0 | 1 | 27 | 68 | 50 | 33 | 130 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 8 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 71 | 1 | 24 | 17 | 10 | 362 | 58 | 17 | 0 | 1 | 15 | 0 | 0 | 34 | 28 | 25 | 260 | 0 | 15 | 108 | 0 | 0 | 17 | 6 | 34 | 17 | 250 | 0 | 0 | 612 | 6 | 733 | 0 | 0 | 21 | 0 | 915 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 160 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 35 | 0 | 106 | 0 | 1 | 35 | 1244 | 180 | 0 | 0 | 1 | 6 | 35 | 0 | 0 | 554 | 8 | 250 | 1498 | 104 | 0 | 0 | 8 | 0 |  |  |  | 126769175 | 21660363 | 25000 | 125788473 | 46117446 | 2243520 | 3202790 | 180480 | 4811867 |  |  | 330774114
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 126.7692 | 21.6604 | 0.025 | 125.7885 | 46.1174 | 2.2435 | 3.2028 | 0.18048 | 4.8119
| Minimum Generation |  | 12576 | 8:00
| Highest Generation |  | 15156 | 21:00 | [129 empty] | 0 | [73 empty] | 330.7991
| Day Peak Generation |  | 13575 | 12:00
| Evening Peak Generation |  | 15156 | 21:00 | [203 empty] | 202699852
| HVDC Max Flow |  | 917 | 6:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 782 | 21:00
| Load factor L.F |  | 90.94% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-07-31
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-07-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13575 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 12697
Evening Peak Generation : |  |  | 15156 | MW Hour : | 21:00 | Available Max Generation : |  | 16160
E.P. Demand (at gen end) : |  |  | 15750 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 16000
Maximum Generation : |  |  | 15156 | MW Hour : | 21:00 | Reserve(Generation end)
Total Gen. (MKWH) : |  |  | 330.7991 | System Load Factor : | 90.94% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 640 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-07-31
Actual : |  | 92.89 | Ft.(MSL) , | Rule curve : | 88.83 | Ft.( MSL )
Gas Consumed : |  | Total = | 942.3 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 380818938.52
: |  |  | Coal : | 852199347.58 | Oil : | 851925543.84 | Total : | 2084943829.94
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 132 | 3168:00 | 5341.9617 |  |  | 0 | -2.866%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | -1.035%
Khulna Area |  | 50 | 1200:00 | 2064.3332 |  |  | 0 | -0.6449%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | -0.2316%
Cumilla Area |  | 55 | 1320:00 | 1476.7776 |  |  | 0 | -0.4881%
Mymensingh Area |  | 220 | 5280:00 | 1099.0436 |  |  | 0 | -0.1293%
Sylhet Area |  | 15 | 360:00 | 615.3064 |  |  | 0 | -0.8142%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | -0.06366%
Rangpur Area |  | 95 | 2280:00 | 1004.2252 |  |  | 0 | -0.07249%
Total |  | 567 |  | 15383.3573 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:32 | 11:22 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to
project works
| 08:44 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT is restored.
| 08:44 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT is restored.
08:48 | 09:58 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to PBS Work |  |  |  |  | 40.0MW load interrup.
08:48 | 09:58 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to PBS Work |  |  |  |  | 40.0MW load interrup.
| 09:08 | Ishurdi 132/33kV S/S 132/33 kV T-1 HT is restored.
| 09:09 | Ishurdi 132/33kV S/S 132/33 kV T-1 LT is restored.
09:35 | 18:44 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Tower erection work
09:58 | 10:45 | Kushtia 132/33kV S/S T-1 LT Tripped showing 50/51 trip 50/51 N trip relays Due to 33 kv |  |  |  |  | 31.0MW load interrup.
out going feeder fault
09:58 | 10:46 | Kushtia 132/33kV S/S T2 LT Tripped showing 50/51 trip 50/51 N trip relays Due to 33 kv |  |  |  |  | 31.0MW load interrup.
out going feeder fault
10:30 | 13:18 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Due to 132 kv control & relay panel DC fail |  |  |  |  | 58.0MW load interrup.
10:31 | 13:17 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Due to 132 kv control & relay panel DC fail |  |  |  |  | 58.0MW load interrup.
11:34 |  | Sirajganj 132/33kV S/S Solar Park 2 Project Work S/D Due to For Testing Perposed
11:42 |  | Kushtia 132/33kV S/S T-1 LT Forced S/D |  |  |  |  | 45.0MW load interrup.
11:43 |  | Kushtia 132/33kV S/S T-1 HT Forced S/D |  |  |  |  | 45.0MW load interrup.
12:00 |  | Day peak generation: 13575 MW
12:59 |  | Sikalbaha-TK Chemical 132kV Ckt tripped as 132kV R-phase LA got burst at TK
Chemical S/S end.
12:59 | 18:32 | Sikalbaha-TKCL 132kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing Main-1
protection relay relays.
| 14:46 | Maniknagar-Narinda 132kV Ckt-1 is restored.
14:58 | 16:25 | Maniknagar-Narinda 132kV Ckt-1 Scheduled S/D from Maniknagar 132/33kV end Due to Shut
down taken by Mr. Rokonul Islam, SDE, Grid South-2, DPDC.
17:23 |  | SS Power Tripped with remarks:- unit1
17:23 |  | SS Power Tripped with remarks:- Unit-1
17:24 |  | SS Power Synchronized with remarks:- unit-2
| 18:18 | Maniknagar-Narinda 132kV Ckt-2 is restored.
| 18:44 | Aminbazar-Kaliakoir 230kV Ckt-1 is restored.
19:31 | 21:42 | Kushtia 132/33kV S/S T2 LT Forced S/D |  |  |  |  | 50.0MW load interrup.
19:32 | 21:40 | Kushtia 132/33kV S/S T2 HT Forced S/D |  |  |  |  | 50.0MW load interrup.
21:00 |  | Evening peak gen. 15156 MW.
00:40 |  | Juldah 132/33kV S/S 133/33 KV T-2 416T HT Forced S/D Due to Urgent spark maintenance work
of line DS(B-phase).
01:24 |  | Fatullah-Madanganj 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing 1. 21 Trip 2.
Zone-1 Trial & Again Trip: 01:45 1. 21 Trip 2. Zone-1 3. SOTF relays.
01:24 | 02:03 | Hasnabad 132/33kV S/S Fatulla (Pre-Brahmongaon) Tripped showing Main protection trip, |  |  |  |  | 65.0MW load interrup.
Lock Out, relays Due to Unknown
01:24 |  | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Tripped showing Zone 1 Trip Y phase
pickup B phase pickup relays Due to None
06:00 |  | Min. Gen. 12699 MW
06:32 | 07:42 | Dhamrai-Kaliakoir 132 kV Ckt-2 Project Work S/D from Dhamrai 132/33kV end Due to Project |  |  |  |  | 15.0MW load interrup.
|  | Work and from Kaliakoir 400/230/132kV end Due to NLDC |  |  |  |  | Dhamrai 132/33kV end
06:36 |  | Sylhet 225 MW CCPP GT was shutdown.
07:02 |  | Magura 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to RED HOT MAINTENANCE. |  |  |  |  | 20.0MW load interrup.
07:03 |  | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to RED HOT MAINTENANCE. |  |  |  |  | 20.0MW load interrup.
07:42 |  | Dhamrai-Kaliakoir 132 kV Ckt-1 Project Work S/D from Dhamrai 132/33kV end Due to Project |  |  |  |  | 20.0MW load interrup
|  | Work and from Kaliakoir 400/230/132kV end Due to By NLDC |  |  |  |  | Dhamrai 132/33kV end
07:49 |  | Jhenaidah-Khulna 230kV Ckt-2 Tripped from Khulna(S) 230/132kV end showing DIS.RELAY
relays. and from Jhenaidah 230/132kV end showing 86.1 OPERATED 86.2 OPERATED relays.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-07-30
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 356 | 8910000 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9978500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 12 | 303360 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 151 | 3629818 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 85 | 1218668 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 681948
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 107000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 17 | 299520 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7802231
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 49 | 382608 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1256400
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1842720 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 28 | 183317 | 33 kV line fault.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 792167
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 823080 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 516240 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 6 | 137900 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 172800 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 4052180 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 118 | 1850400 | Fuel shortage
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 72 | 927360 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 268800 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3794400
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 162292
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 425880 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 2513 | 50519589
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 84483 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 13365
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 180960 | Megnaghat bus section limitatiom.
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 200 | 4811867
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5263371
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 632291 | Megnaghat bus section limitatiom.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 81 | 641712 | Engine problem
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 676197 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 25 | 186960 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 442560 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 19 | 440160
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 32 | 305280 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24238
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 107 | 817964 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 25679
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 70 | 465020 | Megnaghat bus section limitatiom.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 432960 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 303600 | Megnaghat bus section limitatiom.
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 108 | 515200 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 592 | 21359998 | unit-1 tripped at 17:23
| Cox's Bazar Wind |  | IPP | 66 | 60 | 7 | 180480
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 734 | 16458181
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 2586 | 54262526
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 5067000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7318500 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6395000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 6186000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 817488 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 10 | 388800 | Engine problem
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1150400
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 134 | 1980509 | Engine problem
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 671968 | Machine problem.
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 52 | 1164300 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 103 | 885120 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 92 | 2243520
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 32 | 515741 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 408630 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 637260 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 867720 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 98 | 1430400 | Engine problem
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 350018
| Cumilla Area Total |  |  |  | 2950 | 1896 | 38478374
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 31 | 526080 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9600
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 123 | 2455200 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1502400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 202560
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 2 | 101760 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 431640 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 251 | 5229240
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 28 | 640000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 67 | 1595760 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3714709
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 102384 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 726240 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 0 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 136 | 3237210 | ST Under maint
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 278256 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7327000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 388 | 8920000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 255 | 5300800 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1386 | 31842359
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 782 | 21660363
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 62 | 583680 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 6 | 128640
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 183168 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 6180480 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 189375
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 87 | 749760 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 367920
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 618 | 13963640 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1881 | 44007026
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 567456 | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 201437
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 126 | 2611000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 29185200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5245593
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 465600 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 6196400
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 1774
| Barisal Area Total |  |  |  | 2236 | 2004 | 44474460
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 37 | 305102 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 145403 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 35 | 292630
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 265801
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 181 | 4353273
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 351 | 9295345 | Gas shortage
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 233932 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 116190 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 616576 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1205952
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 1017888 | low demand.
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34620
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1236 | 33120000
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 360000
| Rajshahi Area Total |  |  |  | 3381 | 2188 | 51362712
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 60 | 1395054
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4110000 | Machine problem.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 25000
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 2031091 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40595
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1385280
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 221118
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1414690
| Rangpur Area Total |  |  |  | 950 | 451 | 10622828
| Total |  |  |  | 26947 | 15156 | 330799114
| Eastern Grid Total |  |  |  | 16526 | 8632 | 180332088
| Western Grid Total |  |  |  | 10421 | 6524 | 150467026
| National Grid Total |  |  |  | 26947 | 15156 | 330799114
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Company of Bangladesh Limited (PGCB)
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-07-2024 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9560.8 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5011.6 | MW
i) Dhaka area |  |  | 5050.4 |  | MW | i) Khulna area |  |  |  | 1891.6 | MW
ii) Chattogram area |  |  | 1391.4 |  | MW | ii) Barishal area |  |  |  | 473.8 | MW
iii) Cumilla area |  |  | 1447 |  | MW | iii) Rajshahi area |  |  |  | 1656.2 | MW
iv) Mymensingh area |  |  | 1063 |  | MW | iv) Rangpur area |  |  |  | 990 | MW
v) Sylhet area |  |  | 609 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14572.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 16:00 | 67 | Jamalpur | 108 | 20:00 | 133 | Rahim | 40 | 11:00
2 | AKSML | 5 | 07:00 | 68 | Jashore | 144 | 00:00 | 134 | Rajbari | 84 | 23:00
3 | Aftabnagar | 36 | 00:00 | 69 | Jhenaidah | 142 | 21:00 | 135 | Rajendrapur | 100 | 21:00
4 | Agargaon | 119 | 11:00 | 70 | Joydebpur | 198 | 11:00 | 136 | Rajshahi | 135 | 21:00
5 | Agrabad | 90 | 19:00 | 71 | Joypurhat | 73 | 21:00 | 137 | Rajshahi-230 | 84 | 00:00
6 | Amnura | 90 | 21:00 | 72 | Juldah | 22 | 00:00 | 138 | Ramganj | 120 | 21:00
7 | Ashuganj | 87 | 00:00 | 73 | KSRM | 28 | 13:00 | 139 | Rampur | 38 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 291 | 19:00 | 140 | Rangamati | 19 | 19:30
9 | BSRM | 182 | 13:00 | 75 | Kachua | 82 | 19:30 | 141 | Rangpur | 139 | 21:00
10 | Bagerhat | 97 | 23:00 | 76 | Kallyanpur | 117 | 00:00 | 142 | Ruppur | 7.4 | 16:00
11 | Bakulia | 93 | 15:00 | 77 | Kalurghat | 36 | 15:00 | 143 | SSM | 13 | 23:00
12 | Banani | 71 | 11:00 | 78 | Kamrangirchar | 55 | 13:00 | 144 | Saidpur | 114 | 20:00
13 | Bangabhaban | 26 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 139 | 23:00
14 | Barapukuria | 77 | 20:00 | 80 | Kazla | 117 | 13:00 | 146 | Satmasjid | 114 | 13:00
15 | Barguna | 24 | 22:00 | 81 | Keranigonj | 83 | 00:00 | 147 | Savar | 207 | 19:00
16 | Barishal | 109 | 19:30 | 82 | Khagrachori | 34 | 21:00 | 148 | SevenRings | 17.85 | 00:00
17 | Barishal-230 | 106 | 22:00 | 83 | Khulna | 77 | 21:00 | 149 | ShahCement | 29 | 00:00
18 | Baroaulia | 67 | 23:00 | 84 | Khulshi | 175 | 12:00 | 150 | Shahjadpur | 94 | 20:00
19 | Baroirhat | 69 | 22:00 | 85 | Kishoreganj | 142 | 18:30 | 151 | Shahjibazar | 131 | 03:00
20 | Bashundhara | 159 | 11:00 | 86 | Kodda | 297 | 21:00 | 152 | Shahmirpur | 54 | 00:00
21 | BashundharaCement | 1 | 15:00 | 87 | Kulaura | 60 | 20:00 | 153 | Shariatpur | 91 | 00:00
22 | Beanibazar | 80 | 19:00 | 88 | Kurigram | 68 | 21:00 | 154 | Sherpur | 128 | 22:00
23 | Benapole | 70 | 23:00 | 89 | Kushtia | 150 | 00:00 | 155 | Shikalbaha | 27 | 14:00
24 | Bhaluka | 122 | 16:00 | 90 | Lalbag | 107 | 10:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 60.5 | 23:00 | 91 | Lalmonirhat | 62 | 19:00 | 157 | Shitalakhya | 84.7 | 13:00
26 | Bhangura | 40 | 22:00 | 92 | MI_Cement | 18.9 | 04:00 | 158 | Sholosohor | 43 | 12:00
27 | Bheramara(GK) | 84 | 20:00 | 93 | Madanganj | 41 | 10:00 | 159 | Shyampur | 172 | 12:00
28 | Bhulta | 225 | 20:00 | 94 | Madaripur | 116 | 00:00 | 160 | Siddhirganj | 121 | 23:00
29 | Bog-Sherpur | 74 | 21:00 | 95 | Madartek | 87.64 | 00:00 | 161 | Sirajganj | 132 | 21:00
30 | Bogura | 181 | 21:00 | 96 | Madunaghat | 50 | 19:00 | 162 | Sonargaon | 91 | 23:00
31 | Borhanuddin | 87 | 23:00 | 97 | Magura | 68 | 00:00 | 163 | Sreemongol | 78 | 21:00
32 | Brahmanbaria | 181 | 22:00 | 98 | Mahasthangarh | 84 | 22:00 | 164 | Sreepur | 98 | 17:00
33 | Cantonment | 118 | 11:00 | 99 | Manikganj | 118 | 22:00 | 165 | Srinagar | 48.4 | 22:00
34 | Chandpur | 76 | 20:00 | 100 | Maniknagar | 70 | 13:00 | 166 | Sunamganj | 56 | 04:00
35 | Chandraghona | 35 | 19:00 | 101 | Matarbari | 44 | 19:30 | 167 | Sylhet | 50 | 19:00
36 | Chapai | 78 | 22:00 | 102 | Matuail | 75 | 10:00 | 168 | Sylhet-132 | 127 | 19:00
37 | Charsaidpur | 30 | 03:00 | 103 | Millgate | 134 | 15:00 | 169 | TK | 32.4 | 19:00
38 | Chauddagram | 72 | 22:00 | 104 | Mirpur | 141 | 11:00 | 170 | Tangail | 192 | 20:00
39 | Chhatak | 36 | 21:00 | 105 | Mirsorai | 7 | 00:00 | 171 | Thakurgaon | 113 | 20:00
40 | Chowmuhani | 194 | 18:30 | 106 | Mirzapur | 34 | 05:00 | 172 | Tongi | 129 | 16:00
41 | Chuadanga | 120 | 20:00 | 107 | Mithapukur | 70 | 20:00 | 173 | Ullahpara | 28 | 06:00
42 | Coxsbazar | 113 | 19:30 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 58 | 00:00
43 | Cumilla(N) | 166 | 22:00 | 109 | Mogbazar | 124.6 | 11:00 | 175 | Uttara | 86 | 11:00
44 | Cumilla(S) | 188 | 19:00 | 110 | Mongla | 30 | 11:00 | 176 | UttaraNew | 62 | 00:00
45 | Daudkandi | 149 | 20:00 | 111 | Motijheel | 47 | 11:00 | 177 | Zigatola | 83 | 00:00
46 | Dhaka | 62 | 11:00 | 112 | Munshiganj | 112 | 20:00
47 | Dhamrai | 134 | 19:00 | 113 | Mymensingh | 233 | 07:00
48 | Dhanmondi | 145 | 11:00 | 114 | Naogaon | 157 | 21:00
49 | Dohazari | 93 | 22:00 | 115 | Narail | 62 | 23:00
50 | Faridpur | 174 | 23:00 | 116 | Narinda | 56 | 00:00
51 | Fatullah | 91 | 10:00 | 117 | Narshingdi | 166 | 18:30
52 | Fenchuganj | 47 | 19:00 | 118 | Natore | 168 | 21:00
53 | Feni | 108 | 21:00 | 119 | Nawabganj | 50.3 | 22:00
54 | GPH | 78 | 18:00 | 120 | Netrakona | 106 | 21:00
55 | Ghatail | 48 | 22:00 | 121 | New | 58.3 | 11:00
56 | Ghorashal | 68 | 21:00 | 122 | Niamatpur | 94 | 22:00
57 | Goalpara | 32 | 21:00 | 123 | Noapara | 58 | 19:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-07-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 383 | 18:30 | 369 | 12:00 | Kaliakoir | 373 | 18:00 | 357 | 12:00
| Ashuganj | 402 | 5:00 | 384 | 12:00 | Madunaghat_I | 401 | 19:00 | 395 | 23:00
| Bhulta | 393 | 06:00 | 378 | 12:00 | Meghnaghat | 379 | 18:30 | 366 | 12:00
| Bibiana | 395 | 18:00 | 385 | 10:00 | Payra | 409 | 18:30 | 401 | 00:00
| BIPTC | 403 | 08:00 | 394 | 00:00 | Rahanpur | 399 | 18:00 | 383 | 05:00
| Bogura | 390 | 18:30 | 370 | 05:00 | Rampal | 401 | 18:30 | 386 | 00:00
| Gopalganj | 396 | 18:30 | 383 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 226 | 06:00 | 213 | 12:00 | Haripur | 228 | 18:30 | 218 | 12:00
| AKSML | 237 | 17:00 | 225 | 01:00 | Hasnabad | 224 | 18:30 | 216 | 11:00
| Aminbazar | 224 | 04:00 | 214 | 09:00 | Hathazari | 237 | 19:30 | 227 | 14:00
| Ashuganj | 232 | 18:00 | 223 | 12:00 | Ishurdi | 236 | 06:00 | 227 | 19:30
| Ashuganj-400 | 230 | 20:00 | 223 | 12:00 | Jhenaidah | 228 | 18:30 | 216 | 19:30
| Baghabari | 231 | 18:30 | 223 | 19:30 | Kaliakoir | 232 | 18:30 | 222 | 12:00
| Barapukuria | 216 | 18:30 | 206 | 03:00 | Keranigonj | 225 | 06:00 | 213 | 12:00
| Barapukuria-230 | 215 | 16:00 | 205 | 4:00 | Khulna(S) | 231 | 18:30 | 219 | 00:00
| Barishal | 231 | 17:00 | 224 | 00:00 | Madunaghat_I | 237 | 19:00 | 229 | 14:00
| Bheramara | 235 | 06:00 | 226 | 19:30 | Maniknagar | 227 | 07:00 | 218 | 12:00
| Bhulta | 229 | 06:00 | 219 | 12:00 | Meghnaghat | 232 | 18:30 | 226 | 11:00
| Bibiana | 226 | 18:30 | 219 | 12:00 | Meghnaghat-400 | 231 | 18:30 | 222 | 12:00
| BIPTC | 236 | 06:00 | 225 | 19:30 | Mirsorai | 233 | 20:00 | 220 | 12:00
| Bogura | 224 | 18:00 | 213 | 05:00 | Rajshahi | 236 | 18:30 | 225 | 19:30
| Bogura-400 | 226 | 18:30 | 215 | 02:00 | Rampal | 231 | 18:30 | 219 | 00:00
| Borhanuddin | 237 | 08:00 | 230 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 232 | 20:00 | 221 | 12:00 | Rampura | 229 | 06:00 | 217 | 12:00
| Cumilla(N) | 227 | 18:00 | 216 | 12:00 | Shikalbaha | 238 | 00:00 | 224 | 11:00
| Faridpur | 234 | 18:30 | 224 | 00:00 | Shyampur | 227 | 18:30 | 217 | 12:00
| Fenchuganj | 226 | 18:00 | 222 | 12:00 | Siddhirganj | 229 | 04:00 | 219 | 12:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 236 | 18:30 | 230 | 00:00
| Ghorashal-230 | 228 | 18:30 | 218 | 12:00 | Sreepur | 227 | 18:30 | 222 | 00:00
| Gopalganj | 234 | 18:30 | 225 | 00:00 | Tongi | 225 | 07:00 | 217 | 12:00
| GPH | 233 | 18:30 | 224 | 10:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 133 | 06:00 | 124 | 12:00 | Kushtia | 136 | 18:00 | 128 | 00:00
| Agargaon | 134 | 06:00 | 125 | 12:00 | Lalbag | 131 | 06:00 | 122 | 12:00
| Agrabad | 134 | 18:30 | 127 | 12:00 | Lalmonirhat | 125 | 15:00 | 115 | 00:00
| AKS | 133 | 21:00 | 126 | 10:00 | Madanganj | 129 | 20:00 | 122 | 12:00
| Aminbazar | 134 | 04:00 | 125 | 15:00 | Madaripur | 133 | 18:30 | 126 | 00:00
| Amnura | 139 | 17:00 | 118 | 05:00 | Madartek | 134 | 06:00 | 123 | 12:00
| Ashuganj | 135 | 00:00 | 133 | 12:00 | Madunaghat | 135 | 18:30 | 128 | 14:00
| Bagerhat | 134 | 18:00 | 123 | 00:00 | Magura | 138 | 18:00 | 127 | 00:00
| Bakulia | 136 | 20:00 | 128 | 11:00 | Mahasthangarh | 129 | 18:30 | 120 | 03:00
| Banani | 134 | 06:00 | 122 | 12:00 | Manikganj | 126 | 18:30 | 120 | 12:00
| Bangabhaban | 129 | 04:00 | 122 | 12:00 | Maniknagar | 129 | 04:00 | 122 | 12:00
| Barapukuria | 132 | 15:00 | 124 | 03:00 | Matarbari | 127 | 18:30 | 116 | 00:00
| Barguna | 136 | 18:30 | 127 | 00:00 | Matuail | 128 | 05:00 | 122.4 | 12:00
| Barishal | 137 | 18:00 | 130 | 01:00 | Millgate | 132 | 18:00 | 124 | 12:00
| Barishal-230 | 138 | 18:00 | 131 | 01:00 | Mirpur | 133 | 04:00 | 126 | 11:00
| Baroaulia | 135 | 18:30 | 128 | 10:00 | Mirzapur | 127 | 18:00 | 120 | 16:00
| Baroirhat | 128 | 07:00 | 121 | 00:00 | Mithapukur | 127 | 15:00 | 117 | 01:00
| Bashundhara | 134 | 06:00 | 123 | 11:00 | MI_Cement | 129.3 | 20:00 | 122.1 | 12:00
| BashundharaCement | 129 | 20:00 | 122 | 12:00 | Modern | 134 | 18:00 | 128 | 10:00
| Beanibazar | 119 | 22:00 | 111 | 19:00 | Mogbazar | 134 | 05:00 | 125 | 10:00
| Benapole | 135 | 18:30 | 124 | 00:00 | Mongla | 133 | 18:00 | 123 | 00:00
| Bhaluka | 124 | 18:30 | 120 | 00:00 | Motijheel | 129 | 04:00 | 122 | 12:00
| Bhandaria | 133 | 18:30 | 121 | 23:00 | Munshiganj | 129 | 06:00 | 122 | 12:00
| Bhangura | 135 | 18:30 | 130 | 00:00 | Mymensingh | 131 | 06:00 | 115 | 22:00
| Bheramara | 136 | 18:30 | 130 | 00:00 | Naogaon | 125 | 18:00 | 114 | 07:00
| Bheramara(GK) | 136 | 18:00 | 130 | 00:00 | Narail | 139 | 18:00 | 127 | 00:00
| Bhulta | 120 | 05:00 | 115 | 10:00 | Narinda | 128 | 20:00 | 122 | 12:00
| Bog-Sherpur | 131 | 18:30 | 122 | 07:00 | Narshingdi | 119 | 05:00 | 112 | 15:00
| Bogura | 131 | 18:00 | 123 | 07:00 | Natore | 134 | 18:30 | 127 | 01:00
| Bogura-230 | 133 | 18:00 | 124 | 05:00 | Nawabganj | 131 | 06:00 | 124 | 11:00
| Brahmanbaria | 125 | 18:00 | 119 | 22:00 | Netrakona | 132 | 09:00 | 120 | 12:00
| Cantonment | 134 | 06:00 | 125 | 12:00 | New | 132 | 18:00 | 124 | 12:00
| Chandpur | 128 | 18:30 | 116 | 12:00 | Niamatpur | 134 | 18:00 | 126 | 04:00
| Chandraghona | 136 | 18:30 | 130 | 13:00 | Noapara | 138 | 18:30 | 128 | 00:00
| Chapai | 131 | 18:00 | 121 | 00:00 | Pabna | 134 | 18:00 | 128 | 19:30
| Charsaidpur | 129 | 19:30 | 123 | 10:00 | Palashbari | 125 | 18:30 | 114 | 05:00
| Chauddagram | 129 | 18:00 | 116 | 12:00 | Panchagarh | 129 | 15:00 | 111 | 07:00
| Chhatak | 119 | 22:00 | 110 | 21:00 | Patuakhali | 135 | 18:00 | 127 | 00:00
| Chowmuhani | 120 | 17:00 | 112 | 22:00 | Payra | 136 | 18:30 | 132 | 10:00
| Chuadanga | 131 | 06:00 | 119 | 00:00 | PHP | 127 | 19:30 | 121 | 00:00
| Coxsbazar | 125 | 17:00 | 118 | 00:00 | Postogola | 133 | 18:30 | 125 | 12:00
| Cumilla(N) | 131 | 18:00 | 124 | 12:00 | Purbachal | 133 | 04:00 | 123 | 12:00
| Cumilla(S) | 131 | 18:30 | 121 | 12:00 | Purbasadipur | 126 | 15:00 | 110 | 07:00
| Daudkandi | 122 | 03:00 | 113 | 12:00 | Rahanpur | 135 | 18:00 | 128 | 04:00
| Dhaka | 134 | 06:00 | 125 | 11:00 | Rahim | 128 | 03:00 | 123 | 10:00
| Dhamrai | 131 | 18:00 | 123 | 12:00 | Rajbari | 131 | 06:00 | 125 | 00:00
| Dhanmondi | 130 | 00:00 | 121 | 12:00 | Rajendrapur | 128 | 18:30 | 121 | 09:00
| Dohazari | 132 | 18:30 | 125 | 10:00 | Rajshahi | 135 | 18:30 | 128 | 19:30
| Faridpur | 131 | 18:30 | 125 | 01:00 | Rajshahi-230 | 136 | 18:00 | 115 | 00:00
| Fatullah | 131 | 20:00 | 124 | 12:00 | Ramganj | 123 | 18:00 | 111 | 12:00
| Fenchuganj | 127 | 18:30 | 122 | 21:00 | Rampur | 135 | 18:30 | 128 | 14:00
| Feni | 125 | 18:00 | 115 | 03:00 | Rampura | 133 | 06:00 | 123 | 12:00
| Ghatail | 128 | 18:00 | 116 | 12:00 | Rangamati | 133 | 06:00 | 129 | 12:00
| Ghorashal | 135 | 08:00 | 130 | 19:00 | Rangpur | 127 | 15:00 | 116 | 00:00
| Goalpara | 139 | 18:00 | 130 | 00:00 | Ruppur | 138 | 17:00 | 132 | 00:00
| Gollamari | 136 | 18:00 | 129 | 00:00 | Saidpur | 126 | 15:00 | 115 | 05:00
| Gopalganj | 133 | 18:30 | 125 | 00:00 | Satkhira | 135 | 18:00 | 121 | 00:00
| Gopalganj-400 | 133 | 18:00 | 127 | 00:00 | Satmasjid | 134 | 06:00 | 125 | 12:00
| Gulshan | 133 | 06:00 | 124 | 11:00 | Savar | 134 | 04:00 | 126 | 10:00
| Halishahar | 135 | 20:00 | 127 | 10:00 | SevenRings | 135 | 18:30 | 130 | 11:00
| Haripur | 128 | 03:00 | 123 | 10:00 | ShahCement | 129 | 19:30 | 123 | 10:00
| HaripurSBU | 128 | 03:00 | 123 | 10:00 | Shahjadpur | 135 | 02:00 | 132 | 01:00
| Hasnabad | 132 | 01:00 | 126 | 12:00 | Shahjibazar | 123 | 18:00 | 118 | 12:00
| Hathazari | 137 | 18:00 | 132 | 12:00 | Shahmirpur | 136 | 18:00 | 129 | 10:00
| Ishurdi | 137 | 06:00 | 132 | 00:00 | Shariatpur | 134 | 18:30 | 124 | 00:00
| Jaldhaka | 125 | 15:00 | 112 | 05:00 | Sherpur | 133 | 03:00 | 120 | 12:00
| Jamalpur | 132 | 00:00 | 123 | 12:00 | Shikalbaha | 125 | 21:00 | 118 | 10:00
| Jashore | 136 | 18:00 | 125 | 00:00 | Shikalbaha-230 | 137 | 18:30 | 128 | 11:00
| Jhenaidah | 139 | 18:30 | 128 | 01:00 | Shitalakhya | 129.3 | 20:00 | 122 | 12:00
| Jhenaidah-230 | 139 | 18:30 | 130 | 00:00 | Sholosohor | 135 | 20:00 | 128 | 10:00
| Joydebpur | 129 | 06:00 | 123 | 17:00 | Shyampur | 130 | 20:00 | 123 | 12:00
| Joypurhat | 123 | 18:00 | 111 | 07:00 | Shyampur-230 | 131 | 18:30 | 123 | 12:00
| Juldah | 136 | 20:00 | 128 | 10:00 | Siddhirganj | 128 | 18:00 | 123 | 12:00
| Kabirpur | 130 | 18:00 | 120 | 12:00 | Sirajganj | 130 | 18:00 | 124 | 20:00
| Kachua | 127 | 18:30 | 117 | 12:00 | Sonargaon | 126 | 18:00 | 119 | 12:00
| Kaliakoir | 133 | 18:00 | 124 | 12:00 | Sreemongol | 123 | 18:00 | 119 | 02:00
| Kallyanpur | 128 | 02:00 | 123 | 12:00 | Sreepur | 128 | 18:30 | 125 | 00:00
| Kalurghat | 136 | 20:00 | 128 | 12:00 | Srinagar | 131 | 06:00 | 123 | 12:00
| Kamrangirchar | 132 | 06:00 | 122 | 12:00 | SSM | 138 | 01:00 | 136 | 00:00
| Kaptai | 137 | 1:00 | 136 | 3:00 | Sunamganj | 122 | 02:00 | 109 | 04:00
| Kazla | 129 | 06:00 | 121 | 13:00 | Sylhet | 121 | 14:00 | 116 | 04:00
| Keranigonj | 131 | 06:00 | 124 | 12:00 | Sylhet-132 | 120 | 09:00 | 116 | 21:00
| Khagrachori | 135 | 20:00 | 129 | 10:00 | Tangail | 126 | 04:00 | 116 | 12:00
| Khulna | 137 | 18:00 | 128 | 00:00 | Thakurgaon | 128 | 18:30 | 109 | 07:00
| Khulna(S) | 138 | 18:30 | 129 | 00:00 | TK | 136 | 19:30 | 129 | 11:00
| Khulshi | 134 | 00:00 | 126 | 12:00 | Tongi | 132 | 07:00 | 125 | 16:00
| Kishoreganj | 127 | 18:30 | 122 | 10:00 | Ullahpara | 135 | 18:30 | 129 | 00:00
| Kodda | 129 | 18:00 | 120 | 14:00 | Ullon | 133 | 05:00 | 122 | 12:00
| KSRM | 136 | 19:30 | 128 | 14:00 | Uttara | 133 | 05:00 | 125 | 12:00
| Kulaura | 125 | 18:00 | 121 | 21:00 | UttaraNew | 133 | 07:00 | 125 | 12:00
| Kurigram | 124 | 15:00 | 112 | 05:00 | Zigatola | 131 | 18:30 | 123 | 12:00

## L-Curve
Date | 2024-07-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 896 | 7950 | 6365 | 14315 |  |  |  | QF-LDC-11
0:30 | 917 | 7781.5 | 6396 | 14177.5 | Date: | 2024-07-30
1:00 | 938 | 7613 | 6427 | 14040
1:30 | 904 | 7542.5 | 6357.5 | 13900
2:00 | 870 | 7472 | 6288 | 13760
2:30 | 916 | 7427 | 6285 | 13712 | [5 empty] | Gen. at Eve. Peak | 15156 | 15156 MW (21:00 )
3:00 | 962 | 7382 | 6282 | 13664 | [6 empty] | 21:00
3:30 | 924 | 7378 | 6167 | 13545 | [5 empty] | Gen. at Day Peak | 13575 | 13575 MW (12:00 )
4:00 | 886 | 7374 | 6052 | 13426 | [6 empty] | 12:00
4:30 | 867 | 7289 | 6049 | 13338 | [5 empty] | Highest Generation | 15156
5:00 | 848 | 7204 | 6046 | 13250 | [6 empty] | 21:00
5:30 | 840 | 7068.5 | 5902 | 12970.5
6:00 | 832 | 6933 | 5758 | 12691
6:30 | 818 | 6971 | 5748.5 | 12719.5
7:00 | 804 | 7009 | 5739 | 12748
7:30 | 871 | 6917 | 5745 | 12662
8:00 | 938 | 6825 | 5751 | 12576
8:30 | 999 | 6863.5 | 5796 | 12659.5
9:00 | 1060 | 6902 | 5841 | 12743
9:30 | 1101 | 7017 | 5956.5 | 12973.5
10:00 | 1142 | 7132 | 6072 | 13204
10:30 | 1169 | 7149 | 6113 | 13262
11:00 | 1196 | 7166 | 6154 | 13320
11:30 | 1223 | 7266.5 | 6181 | 13447.5
12:00 | 1250 | 7367 | 6208 | 13575
12:30 | 1230 | 7390.5 | 6204 | 13594.5
13:00 | 1210 | 7414 | 6200 | 13614
13:30 | 1210 | 7392 | 6196 | 13588
14:00 | 1210 | 7370 | 6192 | 13562
14:30 | 1198 | 7330 | 6163.5 | 13493.5
15:00 | 1186 | 7290 | 6135 | 13425
15:30 | 1199 | 7326.5 | 6068.5 | 13395
16:00 | 1212 | 7363 | 6002 | 13365
16:30 | 1161 | 7366.5 | 5948.5 | 13315
17:00 | 1110 | 7370 | 5895 | 13265
17:30 | 1095 | 7151.5 | 5875.5 | 13027
18:00 | 1080 | 6933 | 5856 | 12789
18:30 | 946 | 7419.5 | 6114.5 | 13534
19:00 | 812 | 7906 | 6373 | 14279
19:30 | 640 | 8352 | 6694 | 15046
20:00 | 678 | 8374 | 6668 | 15042 |  |  |  | Executive Engineer
20:30 | 669 | 8503 | 6596 | 15099 |  |  |  | Network Operation Division
21:00 | 660 | 8632 | 6524 | 15156
21:30 | 704 | 8492 | 6556 | 15048
22:00 | 748 | 8352 | 6588 | 14940 |  |  |  |  | Page 6 of 7
22:30 | 805 | 8283.5 | 6533 | 14816.5
23:00 | 862 | 8215 | 6478 | 14693
23:30 | 879 | 8082.5 | 6421.5 | 14504
24:00 | 896 | 7950 | 6365 | 14315
15156 MW (21:00 )
13575 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-07-30 |  | Energy |  | 330799114
[15 empty] | 2024-07-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3611 | 782 | 1780 | 0 | 2475 | 4845 | 198 | 0 | 515 | 106 | 0 | 3 | 1370.425
0:30 | 3577 | 843.5 | 1788 | 0 | 1959 | 5235.5 | 198.5 | 0 | 462.5 | 104 | 0 | 9.5 | 1400.7125 |  |  | Date: | 44041
1:00 | 3543 | 905 | 1796 | 0 | 1443 | 5626 | 199 | 0 | 410 | 102 | 0 | 16 | 1431
1:30 | 3531.5 | 904.5 | 1800.5 | 0 | 1381.5 | 5634.5 | 199.5 | 0 | 333 | 99 | 0 | 16 | 1396 | [9 empty] | Total Energy | 330.7991 | 330.7991 | Total Energy Gen 330.799 MKWHr Energy Not Served 20.698 MKWHr Energy Requirement 351.497 MKWHr
2:00 | 3520 | 904 | 1805 | 0 | 1320 | 5643 | 200 | 0 | 256 | 96 | 0 | 16 | 1361 | [9 empty] | Energy not Served | 20.6978 | 20.6978
2:30 | 3520.5 | 909.5 | 1803.5 | 0 | 1321 | 5610.5 | 200 | 0 | 232 | 97 | 0 | 18 | 1271.5 | [9 empty] | Energy Requirement | 351.4969 | 351.4969
3:00 | 3521 | 915 | 1802 | 0 | 1322 | 5578 | 200 | 0 | 208 | 98 | 0 | 20 | 1182
3:30 | 3494 | 915.5 | 1776 | 0 | 1318 | 5511 | 200 | 0 | 199.5 | 99 | 0 | 32 | 1080 | [8 empty] | Shortage
4:00 | 3467 | 916 | 1750 | 0 | 1314 | 5444 | 200 | 0 | 191 | 100 | 0 | 44 | 978
4:30 | 3480.5 | 916 | 1757.5 | 0 | 1240 | 5484 | 200 | 0 | 136.5 | 100 | 0 | 23.5 | 931.5
5:00 | 3494 | 916 | 1765 | 0 | 1166 | 5524 | 200 | 0 | 82 | 100 | 0 | 3 | 885
5:30 | 3450.5 | 916.5 | 1727 | 0 | 1082 | 5416.5 | 200 | 0 | 71 | 100 | 4 | 3 | 865.5
6:00 | 3407 | 917 | 1689 | 0 | 998 | 5309 | 200 | 0 | 60 | 100 | 8 | 3 | 846
6:30 | 3460 | 916.5 | 1696 | 0 | 977.5 | 5276 | 200 | 0 | 60 | 97 | 35 | 1.5 | 734.33 | [7 empty] | Coal
7:00 | 3513 | 916 | 1703 | 0 | 957 | 5243 | 200 | 0 | 60 | 94 | 62 | 0 | 622.66
7:30 | 3429 | 916 | 1710 | 0 | 957.5 | 5204 | 199.5 | 0 | 60 | 91 | 93.5 | 1.5 | 633.165 | [6 empty] | Oil
8:00 | 3345 | 916 | 1717 | 0 | 958 | 5165 | 199 | 0 | 60 | 88 | 125 | 3 | 643.67
8:30 | 3361 | 916 | 1708.5 | 0 | 986.5 | 5153.5 | 199 | 0 | 62 | 84 | 186 | 3 | 683.3025
9:00 | 3377 | 916 | 1700 | 0 | 1015 | 5142 | 199 | 0 | 64 | 80 | 247 | 3 | 722.935
9:30 | 3447.5 | 916 | 1746.5 | 0 | 1058.5 | 5120.5 | 198.5 | 0 | 86.5 | 82 | 314 | 3.5 | 693.8075
10:00 | 3518 | 916 | 1793 | 0 | 1102 | 5099 | 198 | 0 | 109 | 84 | 381 | 4 | 664.68
10:30 | 3507 | 915.5 | 1786.5 | 0 | 1179 | 5089 | 198 | 0 | 109.5 | 84 | 391.5 | 2 | 680.915
11:00 | 3496 | 915 | 1780 | 0 | 1256 | 5079 | 198 | 0 | 110 | 84 | 402 | 0 | 697.15
11:30 | 3509 | 915.5 | 1783 | 0 | 1321.5 | 5112.5 | 198 | 0 | 110 | 86 | 410 | 2 | 728.1875
12:00 | 3522 | 916 | 1786 | 0 | 1387 | 5146 | 198 | 0 | 110 | 88 | 418 | 4 | 759.225
12:30 | 3497.5 | 916 | 1793.5 | 0 | 1416.5 | 5172 | 198 | 0 | 110 | 94 | 393.5 | 3.5 | 803.6325
13:00 | 3473 | 916 | 1801 | 0 | 1446 | 5198 | 198 | 0 | 110 | 100 | 369 | 3 | 848.04
13:30 | 3473 | 916 | 1801 | 0 | 1446 | 5198 | 198 | 0 | 110 | 100 | 369 | 3 | 848.04
14:00 | 3473 | 916 | 1801 | 0 | 1446 | 5198 | 198 | 0 | 110 | 100 | 369 | 3 | 848.04
14:30 | 3455 | 916 | 1793.5 | 0 | 1422.5 | 5159 | 199 | 0 | 118.5 | 97 | 357.5 | 1.5 | 961.2075
15:00 | 3437 | 916 | 1786 | 0 | 1399 | 5120 | 200 | 0 | 127 | 94 | 346 | 0 | 1074.375
15:30 | 3440 | 915.5 | 1756 | 0 | 1443.5 | 5116.5 | 200 | 0 | 133.5 | 93 | 295 | 2 | 1031.4
16:00 | 3443 | 915 | 1726 | 0 | 1488 | 5113 | 200 | 0 | 140 | 92 | 244 | 4 | 988.425
16:30 | 3453 | 915.5 | 1723 | 0 | 1506.5 | 5082.5 | 200 | 0 | 158.5 | 92 | 181.5 | 2.5 | 892.925
17:00 | 3463 | 916 | 1720 | 0 | 1525 | 5052 | 200 | 0 | 177 | 92 | 119 | 1 | 797.425
17:30 | 3405.5 | 915.5 | 1643.5 | 0 | 1642.5 | 4808.5 | 200 | 0 | 244 | 87 | 76 | 4.5 | 738.2125
18:00 | 3348 | 915 | 1567 | 0 | 1760 | 4565 | 200 | 0 | 311 | 82 | 33 | 8 | 679
18:30 | 3366.5 | 915.5 | 1634.5 | 0 | 2172 | 4633 | 200 | 8.5 | 490 | 91 | 16.5 | 6.5 | 683.7775
19:00 | 3385 | 916 | 1702 | 0 | 2584 | 4701 | 200 | 17 | 669 | 100 | 0 | 5 | 688.555
19:30 | 3527 | 917 | 1756 | 0 | 2868 | 4964 | 200 | 16 | 700 | 94 | 0 | 4 | 610.7225
20:00 | 3550 | 916 | 1669 | 0 | 2924 | 4961 | 200 | 16 | 702 | 92 | 0 | 12 | 532.89
20:30 | 3638 | 849 | 1699.5 | 0 | 2971 | 4932.5 | 200 | 8 | 699.5 | 92 | 0 | 9.5 | 549.945
21:00 | 3726 | 782 | 1730 | 0 | 3018 | 4904 | 200 | 0 | 697 | 92 | 0 | 7 | 567
21:30 | 3656 | 782 | 1765.5 | 0 | 2995 | 4900 | 199 | 0 | 653 | 93 | 0 | 4.5 | 598.65
22:00 | 3586 | 782 | 1801 | 0 | 2972 | 4896 | 198 | 0 | 609 | 94 | 0 | 2 | 630.3
22:30 | 3590.5 | 782.5 | 1800.5 | 0 | 2846 | 4900.5 | 198 | 0 | 596.5 | 98 | 0 | 4 | 843.7425
23:00 | 3595 | 783 | 1800 | 0 | 2720 | 4905 | 198 | 0 | 584 | 102 | 0 | 6 | 1057.185
23:30 | 3603 | 782.5 | 1790 | 0 | 2597.5 | 4875 | 198 | 0 | 549.5 | 104 | 0 | 4.5 | 1213.805 |  |  | Max Temp. in Dhaka |  | 31.4°C
24:00 | 3611 | 782 | 1780 | 0 | 2475 | 4845 | 198 | 0 | 515 | 106 | 0 | 3 | 1370.425
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 330.799 MKWHr Energy Not Served 20.698 MKWHr Energy Requirement 351.497 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-07-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 119 | 120 | 120 | 120 | 120 | 120 | 120 | 119 | 119 | 118 | 118 | 118 | 118 | 118 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 118 | 118 | 118 | 2871867
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1940000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [16 empty] | 9 | 17 |  | 17 | 17 | 17 | 17 | 8 |  | 0 | 84483
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 0 | 2 | 3 | 3 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | [8 empty] | 13365
6 | Sikalbaha 225MW CCPP (Gas) | 222 | 222 | 222 | 223 | 223 | 223 | 223 | 223 | 218 | 220 | 220 | 220 | 218 | 218 | 217 | 219 | 219 | 219 |  | 222 | 222 | 222 | 220 | 220 | 219 | 219 | 5263371
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 51 | 34 | [15 empty] | 85 | 85 | 85 | 85 | 85 | 80 | 68 | 676197
12 | Hathazari 100 MW peaking PP | 48 | 48 | 48 | 48 | [15 empty] | 76 | 80 | 80 | 81 | 81 | 81 | 80 | 641712
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [11 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 19 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 632291
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 671968
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 330 | 333 | 333 | 330 | 330 | 333 | 280 | 333 | 329 | 332 | 332 | 328 | 330 | 327 | 327 | 324 | 328 | 307 |  | 310 | 331 | 333 | 328 | 323 | 326 | 333 | 7802231
18 | Kodda 300 MW PP Unit-2 (Summit) | 200 | 145 | 145 | 145 | 145 | 145 | 95 | 95 | 95 | 105 | 146 | 145 | 145 | 145 | 145 | 145 | 145 | 180 |  | 255 | 262 | 258 | 260 | 265 | 270 | 175 | 4052180
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 1143 | 1150 | 1096 | 1045 | 1047 | 950 | 950 | 950 | 950 | 950 | 950 | 990 | 1005 | 950 | 950 | 953 | 948 | 485 |  | 565 | 603 | 593 | 592 | 614 | 615 | 612 | 21359998
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 25 | 25 | 25 | 35 | 35 | 36 | 36 | 37 | 36 | 36 | 35 | 35 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 817488
33 | Ashuganj 225 MW CCPP | 211 | 213 | 213 | 212 | 213 | 212 | 194 | 211 | 211 | 212 | 210 | 207 | 199 | 206 | 209 | 208 | 210 | 212 |  | 211 | 211 | 214 | 210 | 193 | 202 | 205 | 5067000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 280 | 240 | 350 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 270 | 270 | 270 | 300 | 270 | 270 | 270 | 6395000
| Ashuganj 450 MW CCPP(North) | 300 | 280 | 280 | 290 | 285 | 280 | 350 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 310 |  | 280 | 280 | 285 | 315 | 280 | 280 | 280 | 7318500
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 260 | 300 | 230 | 230 | 250 | 250 | 280 | 280 | 250 | 250 | 250 | 250 | 250 |  | 230 | 230 | 230 | 300 | 250 | 250 | 250 | 6186000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 10 | 25 | 39 | 30 | 12 | 25 | 30 | 30 | 30 | 27 | 16 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 388800
36 | Chandpur 150 MW CCPP | 50 | 52 | 51 | 70 | 70 | 50 | 50 | 70 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 42 | 45 | 52 | 52 | 52 | 51 | 50 | 1164300
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 377 | 377 | 377 | 386 | 403 | 400 | 367 | 373 | 404 | 402 | 364 | 352 | 352 | 352 | 352 | 352 | 352 | 351 |  | 352 | 352 | 351 | 356 | 357 | 357 | 357 | 8910000
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9978500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 30 | 30 | 31 | 31 | 32 | 32 | 32 | 27 | 27 | 25 | 10 | 10 | 10 | 10 | 10 | 18 | 28 | 27 |  | 28 | 28 | 30 | 31 | 30 | 30 | 32 | 526080
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 8 | 18 | 16 | 43 | 25 | 26 | 33 | 53 | 3 | 4 | 1 | 1 | [8 empty] | 202560
44 | Fenchugonj CCPP Phase-1 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 640000
45 | Fenchugonj CCPP Phase-2 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 68 | 68 | 69 | 68 | 67 | 67 | 67 | 67 | 67 | 68 | 67 |  | 67 | 67 | 68 | 67 | 67 | 67 | 67 | 1595760
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 29 | 30 | 30 | 30 | 30 | 30 |  | 30 | 31 | 30 | 30 | 30 | 30 | 31 | 726240
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 130 | 132 | 134 | 134 | 134 | 134 | 134 | 134 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 136 |  | 136 | 136 | 136 | 136 | 136 | 136 | 134 | 3237210
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 102384
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278256
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 305 | 300 | 290 | 300 | 290 | 300 | 305 | 310 | 310 | 290 | 300 | 310 | 300 | 310 | 305 | 290 | 280 |  | 265 | 290 | 280 | 305 | 305 | 300 | 300 | 7327000
| Bibiyana South 400 MW | 220 | 205 | 205 | 215 | 210 | 180 | 188 | 180 | 205 | 200 | 200 | 220 | 200 | 200 | 200 | 245 | 250 | 210 |  | 220 | 210 | 210 | 255 | 251 | 245 | 250 | 5300800
58 | Nababganj 55 MW PP (Southern power ) | [5 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 792167
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 6 | 6 | 6 | 6 |  |  |  | 0 | 3 | 6 | 6 |  | 6 | 6 | 6 | 2 | 0 | 0 | 3 | 101760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 102 | 96 | 98 | 100 | 100 | 100 | 94 | 88 | 80 | 84 | 84 | 88 | 100 | 92 | 94 | 92 | 92 | 82 |  | 100 | 94 | 92 | 92 | 94 | 102 | 106 | 2243520
64 | Malancha, Ctg. EPZ (United) | 32 | 36 | 36 | 35 | 36 | 36 | 30 | 8 | 6 | 0 | 0 | 0 | 4 | 2 | 2 | 2 | 2 | 4 |  | 11 | 15 | 19 | 19 | 28 | 32 | 29 | 440160
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 408630
69 | Summit Ashulia | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 321600
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 23 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501480
71 | Maona 33 MW PP(Summit) | 22 | 22 | 24 | 24 | 24 | 24 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 516240
72 | Rupganj 33 MW PP(Summit) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 137900
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 34 | 34 | 34 | 70 | 70 | 70 | 34 | 637260
| Chowmuhani 113 MW | 34 | 28 | 28 | 28 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 39 | 37 | 37 | 36 | 36 | 45 | 46 |  | 46 | 46 | 47 | 47 | 46 | 47 | 32 | 867720
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 126 | 126 | 126 | 152 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3794400
77 | Siddhirganj 100 PP(Dutch Bangla) | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 299520
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 17 | 17 | 17 | 17 | 8 | 172800
79 | Kodda 150 MW PP | 82 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 36 | 81 | 82 | 82 | 82 | 82 | 82 | 95 | 98 | 98 |  | 115 | 115 | 132 | 132 | 132 | 116 | 82 | 1842720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 32 |  | 32 | 32 | 32 | 32 | 33 | 16 | 16 | 515741
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 70 | 70 | 70 | 70 | 70 | 35 | 17 | 17 | 17 |  | 72 | 72 | 72 | 72 | 72 | 35 | 17 | 927360
| Kaptai 7 MW Solar PP | [7 empty] | 1 | 3 | 4 | 5 | 5 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 24238
| Jodiac Power | [17 empty] | 2 |  | 51 | 54 | 54 | 54 | 54 | 54 | 54 | 25679
| Karnaphuli Power Ltd. | [17 empty] | 1 |  | 51 | 70 | 70 | 70 | 89 | 89 | 89 | 465020
82 | Madanganj 102 PP(Summit) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 36 | 34 | 34 | 34 | 34 | 51 |  | 68 | 80 | 85 | 85 | 85 | 85 | 85 | 1218668
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [15 empty] | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 107000
86 | Meghnaghat CCPP ( Summit) | 151 | 151 | 153 | 152 | 151 | 154 | 151 | 152 | 152 | 154 | 155 | 152 | 152 | 152 | 152 | 151 | 152 | 154 |  | 151 | 153 | 154 | 151 | 150 | 150 | 154 | 3629818
87 | Meghnaghat 100 MW(IEL) | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 15 | 11 |  | 6 | 7 | 7 | 8 | 14 | 11 | 16 |  | 15 | 16 | 16 | 12 | 17 | 8 | 9 | 303360
| Meghnaghat 104 MW PP (OPCL) | [6 empty] | 17 | 17 | 17 | 17 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 268800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [14 empty] | 6 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 186960
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1150400
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 48 | 49 | 49 | 49 | 49 | 49 | 16 | 382608
95 | Patenga 50MW PP (Baraka) | [19 empty] | 26 | 44 | 46 | 47 | 29 | 26 | 26 | 180960
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | 12 | [10 empty] | 3 | 11 | 12 | 12 |  | 23 | 32 | 32 | 32 | 38 | 38 | 39 | 305280
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 19 | 25 | 25 | 25 | 25 |  | 25 | 55 | 55 | 55 | 33 | 30 | 30 | 681948
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 183317
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3714709
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 9600
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 1256400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 94 | 95 | 95 | 95 |  | 122 | 122 | 122 | 123 | 123 | 123 | 125 | 2455200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 64 | 52 | 52 | 52 | 52 | 51 | 52 | 53 | 53 | 53 | 72 | 80 | 76 | 78 | 76 | 82 | 78 | 90 |  | 94 | 107 | 100 | 118 | 112 | 116 | 115 | 1850400
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 442560
116 | Chandpur 200 MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 44 | 103 | 103 | 103 | 103 | 103 | 103 | 885120
117 | Ashuganj 150 MW PP (Midland) | 123 | 123 | 125 | 120 | 120 | 10 | 10 | 10 | 10 | 20 | 47 | 50 | 55 | 55 | 53 | 55 | 63 | 102 |  | 125 | 129 | 129 | 134 | 120 | 98 | 95 | 1980509
118 | Bibiyana-III 400 MW CCPP | 365 | 361 | 348 | 355 | 349 | 328 | 315 | 312 | 312 | 350 | 363 | 379 | 357 | 352 | 350 | 350 | 350 | 291 |  | 291 | 385 | 386 | 388 | 388 | 389 | 387 | 8920000
| Jamalpur 115 MW PP (United) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 77 | 77 | 76 | 78 | 78 | 78 | 78 | 1502400
| Anwara 300 MW PP (United) | 15 | 15 | 15 | 15 | [7 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 30 |  | 100 | 100 | 100 | 107 | 107 | 107 | 107 | 817964
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 432960
| Anlima Energy Ltd. | [19 empty] | 32 | 53 | 53 | 53 | 53 | 53 | 53 | 303600
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 431640
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 1 | 3 | 9 | 17 | 18 | 13 | 16 | 27 | 19 | 15 | 6 | 1 | [8 empty] | 162292
| Chandpur 115(Doreen) | 83 | 71 | 72 | 69 | 37 | 35 | 35 | 35 | 50 | 48 | 48 | 48 | 48 | 49 | 49 | 54 | 67 | 65 |  | 74 | 105 | 97 | 98 | 81 | 53 | 49 | 1430400
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 10 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 425880
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 |  | 108 | 108 | 108 | 108 | 17 | 17 | 17 | 515200
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 16 | 16 | 20 | 44 | 3 | 3 | 0 | 3 | 3 | 4 | 0 | 4 | 3 | 0 | 0 | 4 | 1 | 8 |  | 5 | 4 | 12 | 7 | 2 | 6 | 3 | 180480
| Sonagazi 75 MW Solar Plant | [5 empty] | 0 | 2 | 10 | 21 | 18 | 32 | 35 | 47 | 37 | 55 | 38 | 14 | 6 | [8 empty] | 350018
| Matarbari 2*600 MW (CPGCL) | 630 | 628 | 628 | 630 | 628 | 628 | 637 | 636 | 634 | 635 | 633 | 687 | 712 | 751 | 731 | 730 | 728 | 723 |  | 732 | 732 | 729 | 734 | 733 | 734 | 731 | 16458181
120 | Eastern Zone Total | 7613 | 7472 | 7382 | 7374 | 7204 | 6933 | 7009 | 6825 | 6902 | 7132 | 7166 | 7367 | 7414 | 7370 | 7290 | 7363 | 7370 | 6933 |  | 7906 | 8352 | 8374 | 8632 | 8352 | 8215 | 7950 | 180332088
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 32 | 32 | 32 | 32 | [8 empty] | 16 | 16 | 16 | 16 | 16 | 21 |  | 35 | 32 | 57 | 62 | 70 | 80 | 79 | 583680
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 10 | 10 | [13 empty] | 10 |  | 33 | 39 |  | 6 | 20 | 21 | 10 | 128640
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 35 | 35 | 35 |  |  |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 53 | 80 | 87 | 89 | 89 | 88 | 749760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 12 | 20 | 27 | 51 | 72 | 41 | 30 | 29 | 33 | 27 | 21 | 4 | [8 empty] | 367920
131 | Rampal 1320 MW (BIFPCL) | 623 | 624 | 622 | 565 | 562 | 564 | 564 | 562 | 561 | 561 | 561 | 560 | 559 | 559 | 562 | 566 | 562 | 506 |  | 618 | 620 | 622 | 618 | 620 | 619 | 618 | 13963640
132 | United Payra Power Ltd. | [17 empty] | 5 |  | 90 | 90 | 90 | 90 | 90 | 54 | 54 | 465600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5245593
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 48 | 48 | 64 | 80 | 105 | 110 | 567456
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 250 | 250 | 250 | 291 | 307 | 307 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 285 |  | 307 | 307 | 307 | 250 | 250 | 250 | 250 | 6196400
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1774
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 128 | 128 | 128 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 126 | 126 | 126 | 128 | 130 | 80 | 80 | 80 |  | 130 | 126 | 126 | 126 | 124 | 124 | 128 | 2611000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 8 | 6 | 6 | 7 | 6 | 7 | 7 | 8 | 0 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 201437
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 24 | 8 | 8 | 8 | [11 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 189375
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 21 | 41 | 55 | 45 | 33 | 31 | 29 | 183168
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 905 | 904 | 915 | 916 | 916 | 917 | 916 | 916 | 916 | 916 | 915 | 916 | 916 | 915 | 916 | 915 | 916 | 915 |  | 916 | 917 | 916 | 782 | 782 | 783 | 782 | 21660363
147 | Bheramara 410 MW CCPP | 209 | 216 | 224 | 230 | 244 | 244 | 256 | 264 | 268 | 271 | 268 | 268 | 257 | 258 | 250 | 255 | 253 | 253 |  | 256 | 261 | 260 | 265 | 269 | 269 | 269 | 6180480
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1120 | 1100 | 1100 | 1100 | 1100 | 1040 | 1020 | 1020 | 1020 | 1030 | 1030 | 1030 | 1030 |  | 980 | 1210 | 1220 | 1244 | 1244 | 1244 | 1244 | 29185200
149
150 | Barapukuria TPP Unit-1 | 60 | 59 | 60 | 60 | 60 | 60 | 61 | 61 | 61 | 61 | 61 | 60 | 60 | 61 | 60 | 61 | 60 | 61 |  | 60 | 62 | 61 | 60 | 60 | 60 | 60 | 1395054
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 130 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4110000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 38 | [16 empty] | 38 |  | 38 | 37 | 37 | 37 | 37 | 37 | 30 | 305102
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 1 | 5 | 3 | 6 | 5 | 5 | 3 | 1 | 0 | 0 | [8 empty] | 34620
| Sirajganj 68 MW Solar Park | [6 empty] | 7 | 10 | 13 | 45 | 25 | 63 | 61 | 48 | 50 | 24 | 9 | 2 | [8 empty] | 360000
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 212 | 212 | 214 | 150 | 150 | 150 | 150 | 150 | 150 | 163 | 191 | 191 | 188 | 186 | 185 | 185 | 185 | 160 |  | 145 | 177 | 181 | 181 | 180 | 181 | 180 | 4353273
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 330 | 330 | 330 | 330 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 310 |  | 414 | 394 | 312 | 351 | 414 | 414 | 393 | 9295345
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 16 | 15 | [14 empty] | 4 | 5 |  | 13 | 15 | 18 | 20 | 24 | 24 | 22 | 145403
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 116190
165 | Amnura 50 MW PP(Sinha) | [15 empty] | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 292630
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 32 | [15 empty] | 15 | 20 |  | 42 | 42 | 46 | 42 | 42 | 42 | 42 | 265801
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | 22 | 22 | [11 empty] | 15 | 15 |  | 25 | 25 | 28 | 28 | 25 | 22 | 22 | 233932
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | 50 | [16 empty] | 80 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 616576
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | [5 empty] | 25 | 39 | 55 | 55 | 55 | 55 | 55 | 67 |  | 110 | 113 | 113 | 113 | 113 | 55 | 55 | 1205952
172 | Confidence Power Bogura Unit-1 113 MW | 55 | 35 | 35 | 35 | 35 |  |  |  |  | 10 | 35 | 60 | 70 | 70 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1017888
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 25000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 71 | 71 | 70 | 70 | 71 | 71 | 71 | 71 | 76 | 79 | 85 | 91 | 91 | 90 | 89 | 89 | 83 | 89 |  | 91 | 98 | 105 | 106 | 106 | 106 | 106 | 2031091
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 6 | 6 | 7 | 6 | 7 | 3 | 0 | 1 | [8 empty] | 40595
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 74 |  | 115 | 115 | 115 | 115 | 115 | 56 | 35 | 1385280
| Intraco Solar 30 MW | [5 empty] | 1 | 4 | 8 | 20 | 17 | 15 | 19 | 25 | 32 | 24 | 21 | 9 | 1 |  | 0 | [6 empty] | 221118
| Adani Power Jharkhanda Ltd | 1506 | 1518 | 1508 | 1480 | 1522 | 1510 | 1454 | 1436 | 1416 | 1412 | 1414 | 1409 | 1422 | 1410 | 1367 | 1353 | 1304 | 1305 |  | 1269 | 1260 | 1259 | 1236 | 1205 | 1213 | 1160 | 33120000
178 | Teesta Solar Limited | [5 empty] | 2 | 27 | 51 | 131 | 173 | 197 | 200 | 142 | 151 | 149 | 109 | 58 | 17 | [8 empty] | 1414690