## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-02 | Friday
|  | Date (day): | 2024-08-02 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13288.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16152 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-01 | 2024-08-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 402 | 333 | 350 | 380 | 20 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 410 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 7 | 15 | 16 | 84 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 120 | 150 | 152 | 183 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 65 | 65 | 85 | 85 | 17 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 13 | 0 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 100 | 100 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 17 | 17 | 83 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 250 | 0 | 0
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 24 | 8 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 16 | 64 | 149 |  | 0 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 28 | 0 | 30 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 30 | 35 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 35 | 35 | 35 |  | 45 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 24 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 6 | 9 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 228 | 145 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 97 | 149 | 149 | 49 |  | Fuel shortage
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 17 | 72 | 33 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 72 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 13 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 |  | 38 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 2050 | 1950 | 2034 | 2416 | 2665 | 893
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 10 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 5 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 198 | 198 | 200 | 200 | 30 |  | Low water lavel
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 221 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105 |  | 0
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 80 | 18 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 85 |  | 17 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 25 | 25 | 75 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 25 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 25 | 38 | 70 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 1 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 30 | 50 | 107 | 193 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 51 | 85 | 25 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 25 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 17 | 53 | 63 |  | Fuel shortage
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 17 | 163
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 495 | 374 | 300 | 450 |  |  | unit-1 under maint.
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 31 | 30 | 44 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 876 | 925 | 927 | 960
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1891 | 1941 | 2184 | 2832 | 812 | 347
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 142 | 130 | 150 | 11 |  | ST Under maint.
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 280 | 300 | 60 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 240 | 360 | 360 | 0
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 300 | 300 | 100 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 34 | 37 | 37 | 8 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 20 | 35 | 20 | 20 | 35 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 58 | 138 | 55 | 138 |  | 12 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 36 | 36 | 36 |  | 16 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 33 | 50 | 50 | 113 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 121 | 100 | 70 | 150 | 50 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 72 | 68 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 24 | 25 | 33 |  | 19 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 13 | 17 | 17 |  | 8 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 17 | 34 | 106 |  | 8
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 29 | 28 | 28 | 66 | 47 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 69 | 50 | 115
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 15 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2950 | 1566 | 1546 | 1703 | 2029 | 619 | 96
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 11 | 19 | 25 | 30 | 172 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 85 | 100 | 124 | 76 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 58 | 78 | 68 | 78 | 37 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 9 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 7 | 30 | 17 | 17
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 195 | 224 | 273.6 | 261 | 172 | 0
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 57 | 58 | 57 | 57 |  | 33 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 11 | 50 | 50
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 10 | 33 | 33 | 17 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 36 |  | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 3 | 30 | 0 | 0 |  |  | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 135 | 136 | 136 |  | 95 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 391 | 290 | 360 | 380 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 112 | 382 | 150 | 380 |  | 3 | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1231 | 1386 | 1339 | 1589 | 73 | 507
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 917 | 918 | 918
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 21 | 32 | 64 |  | 51 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 25 | 0 | 60 |  | 49 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 290 | 230 | 280 | 280 | 130 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 16 | 24 | 16 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 0 | 17 | 87 | 18 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 10 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 465 | 383 | 500 | 620 | 614 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1715 | 1618 | 1893 | 2093 | 1465 | 114
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 64 | 46 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 7 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 80 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 920 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 180 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 50 | 17 | 90 | 60 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 140 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1777 | 1393 | 1643 | 2065 | 106 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 35 | 0 | 0 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 176 | 140 | 160 | 180 | 30 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 241 | 380 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 50 | 86 |  | 18 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 70 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 0 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 730 | 1503 | 1000 | 1500 |  | 748
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 40 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1470 | 2073 | 1846 | 2582 | 693 | 855
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 61 | 64 | 64 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 98 | 96 | 106 | 106
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 86 | 35 | 115 |  | 0
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 119 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 354 | 243 | 373 | 285 | 40 | 384
| Total |  |  |  |  | 28098 | 26947 | 12249 | 12374 | 13288.6 | 16152 | 6645 | 3260
A. |  | 2024-08-01 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 13500 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 11219 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12374 | MW
3 | Day peak Generation : |  |  | 12249 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12026.95 | MW
4 | Evening peak Generation : |  |  | 12374 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 296.6395 | MKWHr | By Solar | 1.8649 | MKWHr
| By Gas : | 122.369 | MKWHr |  | By Oil: | 35.5782 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 107.3427 | MKWHr |  | By Hydro: | 4.7558 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.93342 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6645 | MW | Dhaka | 4659.35 | 4659.35 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3260 | MW | Chittagong | 1233.8 | 1233.8 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9905 | MW | Khulna | 1426.1 | 1426.1 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 903.34 | MMCFD |  |  | Rajshahi | 1253.6 | 1253.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 369206683.952 | ii) Oil : | Taka | 657113603.56 | Comilla | 983 | 983 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 713687243.11 | Total | Taka | 1740007530.622 | Mymensingh | 839 | 839 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7667.55 | MKWHr. | Sylhet | 591 | 591 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 964 | MW (W to E) at | 19:30 | hrs | Barisal | 259.1 | 259.1 |  | 0 |  | 24:00 |  | 48
| iii) Maximum : |  |  | 344 | MW at | 9:00 | hrs | Rangpur | 782 | 782 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.8°C |  |  | Total | 12026.95 | 12026.95 |  | 0
B. |  | 2024-08-02 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 28.8°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16152 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
4 | Reserve(Generation end) |  |  |  |  | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 274.6662 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9524 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.08 | MKWHr. | ii) HVDC Flow at Peak Time |  | 917 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7155 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 92.74 |  | (b) Today: | 93 |  | (c) Rule Curve: |  | 89.32
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-08-01 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 154 | 7 | 65 | 35 | 335 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 28 | 0 | 0 | 13 | 22 | 24 | 6 | 0 | 0 | 118 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 65 | 17 | 25 | 27 | 19 | 0 | 36 | 0 | 0 | 0 | 310 | 250 | 212 | 0 | 50 | 36 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 96 | 31 | 0 | 0 | 0 | 38 | 57 | 50 | 32 | 163 | 0 | 31 | 0 | 0 | 133 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 145 | 0 | 0 | 97 | 0 | 72 | 0 | 24 | 98 | 100 | 389 | 59 | 17 | 51 | 0 | 52 | 0 | 34 | 34 | 37 | 25 | 15 | 0 | 0 | 35 | 35 | 0 | 17 | 0 | 58 | 17 | 230 | 17 | 0 | 612 | 60 | 876 | 0 | 0 | 0 |  | 913 | 0 | 264 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 10 | 16 | 0 | 0 | 0 | 31 | 18 | 60 | 35 | 0 | 28 | 0 | 22 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 53 | 0 | 35 | 0 | 106 | 0 | 0 | 113 | 1120 | 180 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 627 | 0 | 270 | 1309 | 0 | 0 | 0 | 0 |  | 7407 | 6093 | 13500 | 3389 | 913 | 1835 | 0 | 1798 | 4875 | 198 | 0 | 336 | 96 | 0 | 60 | 983.65 | 92.76
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 153 | 7 | 65 | 41 | 335 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 28 | 0 | 0 | 13 | 22 | 24 | 6 | 0 | 0 | 118 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 16 | 0 | 12 | 23 | 0 | 0 | 37 | 0 | 0 | 0 | 285 | 250 | 214 | 0 | 52 | 36 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 92 | 30 | 0 | 0 | 0 | 38 | 57 | 50 | 36 | 163 | 0 | 31 | 0 | 0 | 133 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 145 | 0 | 0 | 96 | 0 | 57 | 0 | 24 | 68 | 95 | 347 | 58 | 17 | 17 | 0 | 15 | 0 | 34 | 34 | 35 | 25 | 35 | 0 | 0 | 35 | 31 | 0 | 17 | 0 | 49 | 17 | 230 | 17 | 0 | 612 | 63 | 877 | 0 | 0 | 0 |  | 913 | 0 | 265 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 80 | 9 | 16 | 0 | 0 | 0 | 31 | 12 | 0 | 35 | 0 | 28 | 0 | 16 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 52 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 1080 | 180 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 627 | 0 | 270 | 1518 | 0 | 0 | 0 | 0 |  | 7111 | 6033 | 13144 | 3346 | 913 | 1758 | 0 | 1563 | 5045 | 198 | 0 | 166 | 92 | 0 | 63 | 912.98 | 92.76
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 155 | 8 | 65 | 41 | 335 | 0 | 0 | 10 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 28 | 0 | 0 | 13 | 22 | 24 | 6 | 0 | 0 | 119 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 37 | 0 | 0 | 0 | 285 | 250 | 214 | 0 | 51 | 36 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 94 | 31 | 0 | 0 | 0 | 38 | 57 | 50 | 35 | 163 | 0 | 31 | 0 | 0 | 136 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 145 | 0 | 0 | 96 | 0 | 54 | 0 | 24 | 68 | 108 | 301 | 58 | 17 | 17 | 0 | 15 | 0 | 17 | 34 | 28 | 25 | 55 | 0 | 0 | 35 | 17 | 0 | 17 | 0 | 44 | 17 | 230 | 17 | 0 | 612 | 57 | 877 | 0 | 0 | 0 |  | 913 | 0 | 264 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 28 | 0 | 16 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 318 | 52 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 1080 | 180 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 625 | 0 | 270 | 1514 | 0 | 0 | 0 | 0 |  | 7008 | 5900 | 12908 | 3318 | 913 | 1748 | 0 | 1432 | 5040 | 199 | 0 | 107 | 94 | 0 | 57 | 708.61 | 92.75
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 153 | 7 | 65 | 41 | 335 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 28 | 0 | 0 | 13 | 22 | 24 | 6 | 0 | 0 | 119 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 37 | 0 | 0 | 0 | 285 | 250 | 215 | 0 | 51 | 36 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 88 | 30 | 0 | 0 | 0 | 38 | 57 | 50 | 36 | 163 | 0 | 31 | 0 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 145 | 0 | 0 | 97 | 0 | 53 | 0 | 24 | 68 | 113 | 305 | 58 | 17 | 17 | 0 | 15 | 0 | 0 | 34 | 28 | 25 | 55 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 38 | 17 | 230 | 17 | 0 | 612 | 10 | 878 | 0 | 0 | 0 |  | 913 | 0 | 275 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 52 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 1080 | 180 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 590 | 0 | 234 | 1519 | 0 | 0 | 0 | 0 |  | 6922 | 5789 | 12711 | 3334 | 913 | 1749 | 0 | 1381 | 4974 | 199 | 0 | 63 | 88 | 0 | 10 | 657.995 | 92.75
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 380 | 154 | 7 | 65 | 41 | 335 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 28 | 0 | 0 | 13 | 22 | 24 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 37 | 0 | 0 | 0 | 295 | 250 | 212 | 0 | 70 | 36 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 90 | 32 | 0 | 0 | 0 | 38 | 57 | 50 | 36 | 120 | 0 | 31 | 0 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 145 | 0 | 0 | 97 | 0 | 53 | 0 | 24 | 68 | 113 | 310 | 58 | 17 | 17 | 0 | 15 | 0 | 0 | 34 | 28 | 25 | 55 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 35 | 17 | 230 | 17 | 0 | 612 | 35 | 879 | 0 | 0 | 0 |  | 914 | 0 | 275 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 1040 | 180 | 0 | 17 | 0 | 0 | 35 | 0 | 0 | 542 | 0 | 220 | 1364 | 0 | 0 | 0 | 0 |  | 6891 | 5532 | 12423 | 3377 | 914 | 1682 | 0 | 1343 | 4719 | 200 | 0 | 63 | 90 | 0 | 35 | 598.785 | 92.74
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 340 | 120 | 7 | 65 | 41 | 250 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 22 | 24 | 6 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 38 | 0 | 0 | 0 | 285 | 250 | 214 | 0 | 70 | 36 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 80 | 32 | 0 | 0 | 0 | 38 | 57 | 50 | 36 | 120 | 0 | 31 | 0 | 0 | 138 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 145 | 0 | 0 | 97 | 0 | 53 | 0 | 24 | 68 | 115 | 305 | 58 | 17 | 17 | 0 | 15 | 0 | 0 | 34 | 28 | 25 | 55 | 0 | 0 | 35 | 0 | 0 | 17 | 1 | 33 | 17 | 230 | 17 | 0 | 580 | 42 | 875 | 0 | 0 | 1 |  | 913 | 0 | 277 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 960 | 180 | 0 | 17 | 0 | 1 | 35 | 0 | 0 | 512 | 1 | 195 | 1346 | 9 | 0 | 0 | 0 |  | 6628 | 5327 | 11955 | 3213 | 913 | 1560 | 0 | 1341 | 4530 | 200 | 0 | 63 | 80 | 13 | 42 | 501.375 | 92.74
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 |  | 0 | 340 | 120 | 8 | 65 | 41 | 250 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 22 | 24 | 6 | 2 | 0 | 120 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 285 | 310 | 188 | 0 | 50 | 33 | 20 | 0 | 51 | 0 | 30 | 16 | 0 | 0 | 0 | 17 | 80 | 31 | 0 | 0 | 0 | 38 | 57 | 50 | 36 | 120 | 0 | 30 | 0 | 0 | 137 | 0 | 0 | 0 | 280 | 0 | 8 | 0 | 145 | 0 | 0 | 97 | 0 | 55 | 0 | 24 | 68 | 113 | 305 | 58 | 17 | 17 | 0 | 15 | 0 | 0 | 34 | 28 | 25 | 55 | 0 | 2 | 35 | 0 | 0 | 17 | 8 | 32 | 17 | 230 | 17 | 0 | 550 | 48 | 874 | 0 | 0 | 1 |  | 913 | 0 | 286 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 17 | 0 | 35 | 0 | 106 | 0 | 1 | 35 | 940 | 180 | 0 | 17 | 0 | 2 | 36 | 0 | 0 | 512 | 6 | 170 | 1214 | 47 | 0 | 0 | 1 |  | 6574 | 5192 | 11766 | 3179 | 913 | 1550 | 0 | 1344 | 4321 | 200 | 0 | 63 | 80 | 68 | 48 | 491 | 92.73
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 |  | 0 | 340 | 121 | 7 | 65 | 41 | 250 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 11 | 0 | 0 | 12 | 0 | 0 | 0 | 280 | 250 | 196 | 0 | 50 | 36 | 20 | 0 | 51 | 0 | 29 | 7 | 0 | 0 | 0 | 0 | 70 | 27 | 0 | 0 | 1 | 38 | 57 | 50 | 33 | 120 | 0 | 32 | 0 | 0 | 135 | 0 | 0 | 0 | 265 | 0 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 0 | 12 | 17 | 50 | 333 | 58 | 17 | 17 | 1 | 15 | 0 | 0 | 22 | 28 | 12 | 55 | 0 | 3 | 35 | 0 | 0 | 17 | 12 | 37 | 17 | 230 | 0 | 0 | 503 | 58 | 877 | 0 | 0 | 2 |  | 913 | 0 | 288 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 17 | 0 | 35 | 0 | 106 | 0 | 4 | 35 | 940 | 180 | 0 | 17 | 1 | 10 | 36 | 0 | 0 | 422 | 3 | 170 | 999 | 68 | 0 | 0 | 8 |  | 6280 | 4939 | 11219 | 3136 | 913 | 1538 | 0 | 1174 | 3972 | 200 | 0 | 45 | 70 | 113 | 58 | 602.605 | 92.73
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 |  | 0 | 450 | 153 | 7 | 65 | 41 | 280 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 0 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 270 | 216 | 0 | 50 | 37 | 20 | 0 | 51 | 0 | 30 | 7 | 0 | 0 | 0 | 14 | 62 | 27 | 0 | 0 | 0 | 38 | 57 | 50 | 36 | 163 | 0 | 32 | 0 | 0 | 135 | 0 | 0 | 0 | 305 | 0 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 53 | 2 | 12 | 17 | 50 | 289 | 58 | 52 | 17 | 0 | 15 | 0 | 0 | 25 | 28 | 12 | 50 | 0 | 5 | 35 | 0 | 0 | 17 | 12 | 48 | 17 | 393 | 0 | 0 | 550 | 51 | 876 | 0 | 0 | 6 |  | 917 | 0 | 291 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 17 | 0 | 35 | 0 | 106 | 0 | 3 | 50 | 990 | 220 | 0 | 17 | 0 | 19 | 36 | 0 | 0 | 466 | 10 | 220 | 762 | 119 | 0 | 0 | 9 |  | 6820 | 4991 | 11811 | 3409 | 917 | 1773 | 0 | 1226 | 3926 | 200 | 0 | 62 | 62 | 185 | 51 | 466.995 | 92.73
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 153 | 7 | 65 | 42 | 280 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 0 | 24 | 6 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 315 | 305 | 200 | 0 | 50 | 34 | 20 | 0 | 51 | 0 | 30 | 7 | 0 | 0 | 0 | 13 | 66 | 11 | 0 | 0 | 0 | 38 | 57 | 47 | 5 | 163 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 145 | 0 | 0 | 95 | 0 | 53 | 6 | 12 | 17 | 50 | 308 | 58 | 52 | 17 | 0 | 15 | 0 | 0 | 34 | 29 | 12 | 82 | 0 | 9 | 90 | 0 | 0 | 17 | 7 | 48 | 17 | 300 | 0 | 0 | 551 | 54 | 877 | 0 | 0 | 4 |  | 917 | 0 | 292 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 17 | 0 | 35 | 0 | 99 | 0 | 4 | 94 | 1100 | 220 | 0 | 17 | 0 | 33 | 36 | 0 | 0 | 459 | 7 | 220 | 738 | 104 | 0 | 0 | 4 |  | 6886 | 5133 | 12019 | 3433 | 917 | 1758 | 0 | 1329 | 4006 | 200 | 0 | 78 | 66 | 178 | 54 | 258.805 | 92.73
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 150 | 7 | 65 | 42 | 280 | 0 | 0 | 10 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 3 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 240 | 209 | 0 | 40 | 37 | 20 | 0 | 51 | 0 | 30 | 10 | 0 | 0 | 0 | 14 | 68 | 11 | 0 | 0 | 1 | 38 | 57 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 325 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 6 | 12 | 44 | 58 | 391 | 58 | 52 | 17 | 1 | 15 | 0 | 0 | 34 | 28 | 12 | 87 | 0 | 12 | 108 | 0 | 0 | 17 | 15 | 50 | 17 | 230 | 0 | 0 | 492 | 53 | 878 | 0 | 0 | 8 |  | 917 | 0 | 291 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 17 | 0 | 35 | 0 | 98 | 0 | 5 | 109 | 1100 | 220 | 0 | 35 | 1 | 15 | 36 | 0 | 0 | 458 | 27 | 220 | 757 | 210 | 0 | 0 | 10 |  | 6743 | 5265 | 12008 | 3292 | 917 | 1705 | 0 | 1420 | 3966 | 198 | 0 | 78 | 68 | 311 | 53 | 259.76 | 92.73
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 152 | 8 | 65 | 42 | 330 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 30 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 300 | 240 | 212 | 0 | 40 | 20 | 20 | 0 | 51 | 0 | 37 | 24 | 0 | 0 | 0 | 13 | 72 | 11 | 0 | 0 | 2 | 40 | 57 | 0 | 0 | 163 | 0 | 0 | 3 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 10 | 12 | 121 | 58 | 391 | 58 | 52 | 17 | 1 | 15 | 0 | 0 | 34 | 29 | 12 | 112 | 0 | 9 | 108 | 0 | 0 | 7 | 13 | 50 | 17 | 230 | 0 | 0 | 495 | 31 | 876 | 0 | 0 | 15 |  | 917 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 98 | 0 | 2 | 35 | 1120 | 220 | 0 | 35 | 3 | 10 | 36 | 0 | 0 | 465 | 37 | 250 | 730 | 119 | 0 | 0 | 40 |  | 6933 | 5316 | 12249 | 3438 | 917 | 1791 | 0 | 1458 | 3998 | 198 | 0 | 85 | 72 | 261 | 31 | 382.955 | 92.74
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 150 | 8 | 65 | 42 | 335 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 0 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 300 | 240 | 216 | 0 | 35 | 30 | 20 | 0 | 51 | 0 | 36 | 24 | 0 | 0 | 0 | 13 | 78 | 11 | 0 | 0 | 1 | 40 | 57 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 4 | 12 | 164 | 58 | 312 | 58 | 52 | 0 | 0 | 15 | 0 | 0 | 34 | 28 | 12 | 125 | 7 | 7 | 108 | 0 | 0 | 16 | 16 | 50 | 11 | 230 | 10 | 0 | 440 | 35 | 873 | 0 | 0 | 22 |  | 916 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 10 | 0 | 35 | 0 | 97 | 0 | 8 | 35 | 1220 | 220 | 0 | 0 | 2 | 20 | 0 | 0 | 0 | 421 | 36 | 250 | 755 | 165 | 0 | 0 | 29 |  | 6867 | 5315 | 12182 | 3373 | 916 | 1771 | 0 | 1387 | 4020 | 198 | 0 | 94 | 78 | 310 | 35 | 494.69 | 92.75
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 |  | 0 | 450 | 152 | 7 | 65 | 55 | 280 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 0 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 280 | 213 | 0 | 35 | 34 | 20 | 0 | 51 | 0 | 36 | 24 | 0 | 0 | 0 | 13 | 82 | 9 | 0 | 0 | 0 | 40 | 57 | 4 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 0 | 12 | 192 | 57 | 290 | 58 | 52 | 0 | 0 | 6 | 0 | 0 | 34 | 29 | 12 | 136 | 17 | 10 | 108 | 0 | 0 | 17 | 2 | 65 | 17 | 230 | 17 | 0 | 405 | 36 | 959 | 0 | 0 | 12 |  | 916 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 55 | 0 | 97 | 0 | 7 | 35 | 1244 | 220 | 0 | 0 | 0 | 7 | 36 | 0 | 0 | 418 | 0 | 220 | 759 | 19 | 0 | 0 | 13 |  | 6810 | 5101 | 11911 | 3280 | 916 | 1671 | 0 | 1491 | 4066 | 198 | 0 | 101 | 82 | 70 | 36 | 161.395 | 92.73
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 450 | 152 | 7 | 85 | 55 | 280 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 35 | 0 | 13 | 0 | 24 | 6 | 8 | 0 | 115 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 250 | 213 | 0 | 32 | 34 | 20 | 0 | 51 | 0 | 36 | 24 | 0 | 0 | 0 | 13 | 76 | 10 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 16 | 0 | 135 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 0 | 12 | 190 | 58 | 289 | 58 | 35 | 0 | 0 | 6 | 0 | 0 | 34 | 28 | 12 | 147 | 17 | 13 | 108 | 0 | 0 | 17 | 4 | 68 | 17 | 230 | 17 | 0 | 402 | 50 | 987 | 0 | 0 | 16 |  | 916 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 12 | 0 | 6 | 35 | 1200 | 180 | 0 | 0 | 0 | 28 | 36 | 0 | 0 | 417 | 0 | 220 | 950 | 25 | 0 | 0 | 0 |  | 6840 | 5079 | 11919 | 3254 | 916 | 1638 | 0 | 1360 | 4237 | 195 | 0 | 101 | 76 | 92 | 50 | 0 | 92.77
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 450 | 152 | 8 | 72 | 55 | 280 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 0 | 13 | 15 | 24 | 6 | 8 | 0 | 115 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 250 | 213 | 8 | 33 | 34 | 20 | 0 | 51 | 0 | 36 | 8 | 0 | 0 | 0 | 13 | 66 | 11 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 18 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 61 | 0 | 0 | 51 | 60 | 287 | 58 | 17 | 0 | 0 | 5 | 0 | 0 | 17 | 25 | 0 | 200 | 17 | 19 | 108 | 0 | 0 | 17 | 8 | 67 | 17 | 230 | 0 | 0 | 403 | 31 | 931 | 0 | 0 | 13 |  | 917 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 180 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 415 | 6 | 220 | 1039 | 49 | 0 | 0 | 2 |  | 6567 | 4879 | 11446 | 3321 | 917 | 1657 | 0 | 1000 | 4088 | 195 | 0 | 68 | 66 | 103 | 31 | 32.47 | 92.78
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 |  | 0 | 450 | 153 | 7 | 65 | 55 | 280 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 13 | 15 | 24 | 6 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 250 | 120 | 8 | 34 | 10 | 0 | 0 | 51 | 0 | 36 | 7 | 0 | 0 | 0 | 10 | 62 | 15 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 27 | 0 | 135 | 0 | 0 | 0 | 285 | 12 | 8 | 0 | 95 | 0 | 0 | 96 | 0 | 71 | 0 | 0 | 35 | 30 | 289 | 58 | 17 | 0 | 0 | 5 | 0 | 0 | 0 | 9 | 0 | 200 | 17 | 5 | 108 | 0 | 0 | 0 | 1 | 55 | 0 | 230 | 0 | 0 | 403 | 44 | 931 | 0 | 0 | 4 |  | 917 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 180 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 409 | 3 | 220 | 1172 | 28 | 0 | 0 | 3 |  | 6195 | 4923 | 11118 | 3205 | 917 | 1619 | 0 | 786 | 4175 | 196 | 0 | 67 | 62 | 47 | 44 | 54.435 | 92.8
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 |  | 0 | 420 | 120 | 7 | 65 | 55 | 250 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 13 | 15 | 24 | 9 | 8 | 0 | 116 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 20 | 0 | 0 | 0 | 280 | 240 | 129 | 8 | 34 | 34 | 11 | 0 | 51 | 0 | 36 | 7 | 0 | 0 | 0 | 13 | 60 | 15 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 30 | 0 | 135 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 95 | 0 | 0 | 96 | 0 | 71 | 0 | 0 | 17 | 30 | 288 | 58 | 17 | 0 | 0 | 6 | 0 | 0 | 0 | 9 | 0 | 305 | 17 | 1 | 108 | 0 | 0 | 0 | 1 | 34 | 0 | 230 | 0 | 0 | 383 | 27 | 924 | 0 | 0 | 1 |  | 917 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 180 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 380 | 1 | 160 | 1382 | 7 | 0 | 0 | 0 |  | 6142 | 4872 | 11014 | 3281 | 917 | 1516 | 0 | 751 | 4190 | 196 | 0 | 64 | 60 | 12 | 27 | 0 | 92.82
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809.84 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 |  | 0 | 420 | 120 | 7 | 65 | 55 | 250 | 0 | 0 | 9 | 49 | 32 | 8 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 9 | 8 | 0 | 118 | 80 | 0 | 0 | 3 | 216 | 0 | 0 | 0 |  | 5 | 0 | 34 | 8 | 0 | 1 | 0 | 23 | 0 | 0 | 0 | 280 | 240 | 129 | 8 | 32 | 34 | 31 | 0 | 51 | 0 | 36 | 13 | 0 | 0 | 0 | 13 | 64 | 18 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 30 | 0 | 135 | 0 | 0 | 0 | 270 | 12 | 8 | 0 | 99 | 0 | 0 | 124 | 0 | 77 | 0 | 12 | 42 | 75 | 290 | 77 | 34 | 5 | 0 | 15 | 0 | 1 | 17 | 15 | 12 | 345 | 17 | 0 | 108 | 3 | 0 | 30 | 0 | 44 | 6 | 230 | 17 | 0 | 363 | 16 | 926 | 0 | 0 | 0 |  | 918 | 0 | 230 | 0 | 17 | 0 | 0 | 0 | 36 | 16 | 8 | 130 | 0 | 16 | 0 | 0 | 0 | 15 | 4 | 70 | 14 | 0 | 15 | 0 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 7 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 880 | 180 | 0 | 150 | 0 | 0 | 36 | 0 | 0 | 383 | 0 | 140 | 1502 | 0 | 0 | 0 | 0 |  | 6644 | 5304 | 11948 | 3231 | 918 | 1504 | 0 | 1470 | 4254 | 198 | 0 | 293 | 64 | 0 | 16 | 0 | 92.88
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 |  | 0 | 410 | 120 | 7 | 65 | 55 | 250 | 0 | 0 | 9 | 24 | 16 | 13 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 9 | 8 | 0 | 118 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 |  | 12 | 0 | 34 | 0 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 280 | 240 | 142 | 8 | 33 | 34 | 35 | 0 | 51 | 0 | 36 | 24 | 0 | 0 | 0 | 13 | 68 | 19 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 30 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 228 | 0 | 0 | 85 | 0 | 97 | 0 | 12 | 100 | 138 | 290 | 78 | 52 | 17 | 0 | 30 | 0 | 17 | 17 | 28 | 12 | 382 | 17 | 0 | 72 | 17 | 0 | 30 | 0 | 69 | 17 | 230 | 17 | 0 | 374 | 30 | 925 | 0 | 0 | 0 |  | 917 | 0 | 230 | 0 | 21 | 0 | 0 | 0 | 42 | 25 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 40 | 5 | 90 | 0 | 0 | 27 | 0 | 25 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 920 | 180 | 0 | 50 | 0 | 0 | 86 | 0 | 0 | 383 | 0 | 140 | 1503 | 0 | 0 | 0 | 0 |  | 7047 | 5327 | 12374 | 3240 | 917 | 1537 | 0 | 1721 | 4306 | 198 | 0 | 357 | 68 | 0 | 30 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 410 | 120 | 7 | 65 | 55 | 300 | 0 | 0 | 9 | 24 | 0 | 13 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 13 | 22 | 24 | 9 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 285 | 240 | 142 | 8 | 32 | 37 | 38 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 13 | 60 | 27 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 30 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 225 | 0 | 0 | 55 | 0 | 103 | 0 | 12 | 68 | 120 | 288 | 78 | 52 | 17 | 0 | 30 | 0 | 16 | 0 | 28 | 12 | 380 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 69 | 17 | 230 | 0 | 0 | 394 | 42 | 926 | 0 | 0 | 0 |  | 917 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 970 | 180 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 400 | 0 | 161 | 1519 | 0 | 0 | 0 | 0 |  | 6903 | 5223 | 12126 | 3401 | 917 | 1653 | 0 | 1388 | 4431 | 200 | 0 | 34 | 60 | 0 | 42 | 0 | 92.86
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 390 | 155 | 7 | 65 | 55 | 315 | 0 | 0 | 9 | 17 | 0 | 13 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 14 | 22 | 24 | 9 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 240 | 142 | 8 | 33 | 37 | 40 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 15 | 74 | 29 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 163 | 0 | 0 | 31 | 0 | 135 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 225 | 0 | 0 | 55 | 0 | 136 | 0 | 12 | 68 | 50 | 290 | 78 | 52 | 17 | 0 | 30 | 0 | 17 | 0 | 28 | 12 | 386 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 68 | 17 | 230 | 0 | 0 | 442 | 30 | 924 | 0 | 0 | 0 |  | 917 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 492 | 0 | 180 | 1415 | 0 | 0 | 0 | 0 |  | 7023 | 5339 | 12362 | 3519 | 917 | 1707 | 0 | 1325 | 4556 | 200 | 0 | 34 | 74 | 0 | 30 | 0 | 92.88
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 380 | 157 | 7 | 65 | 55 | 315 | 0 | 0 | 9 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 14 | 22 | 24 | 9 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 240 | 144 | 8 | 39 | 37 | 46 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 15 | 74 | 30 | 0 | 0 | 0 | 39 | 58 | 11 | 10 | 163 | 0 | 0 | 31 | 0 | 135 | 0 | 0 | 0 | 265 | 12 | 5 | 0 | 225 | 0 | 0 | 114 | 0 | 131 | 0 | 12 | 51 | 10 | 290 | 78 | 52 | 17 | 0 | 30 | 0 | 17 | 0 | 9 | 12 | 350 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 69 | 17 | 230 | 0 | 0 | 480 | 19 | 925 | 0 | 0 | 0 |  | 916 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1020 | 180 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 603 | 0 | 180 | 1230 | 0 | 0 | 0 | 0 |  | 7012 | 5212 | 12224 | 3501 | 916 | 1644 | 0 | 1322 | 4500 | 200 | 0 | 48 | 74 | 0 | 19 | 0 | 92.9
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 380 | 153 | 7 | 65 | 55 | 310 | 0 | 0 | 9 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 14 | 22 | 24 | 9 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 345 | 240 | 137 | 8 | 40 | 37 | 47 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 76 | 31 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 31 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 145 | 0 | 0 | 127 | 0 | 137 | 0 | 12 | 51 | 0 | 270 | 78 | 35 | 17 | 0 | 30 | 0 | 17 | 0 | 9 | 12 | 360 | 17 | 0 | 72 | 17 | 0 | 17 | 0 | 86 | 17 | 230 | 0 | 0 | 555 | 0 | 930 | 0 | 0 | 0 |  | 917 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1040 | 180 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 619 | 0 | 180 | 914 | 0 | 0 | 0 | 0 |  | 7041 | 4921 | 11962 | 3454 | 917 | 1710 | 0 | 1240 | 4301 | 200 | 0 | 64 | 76 | 0 | 0 | 0 | 92.92
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 |  | 0 | 380 | 154 | 7 | 65 | 55 | 240 | 0 | 0 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 14 | 22 | 24 | 9 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 260 | 145 | 8 | 40 | 37 | 48 | 0 | 51 | 0 | 0 | 23 | 0 | 0 | 0 | 18 | 74 | 31 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 163 | 0 | 0 | 31 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 146 | 0 | 0 | 127 | 0 | 141 | 0 | 25 | 62 | 0 | 347 | 78 | 17 | 36 | 0 | 49 | 0 | 24 | 52 | 21 | 25 | 380 | 17 | 0 | 84 | 33 | 0 | 17 | 0 | 89 | 17 | 300 | 0 | 0 | 585 | 57 | 911 | 0 | 0 | 0 |  | 914 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 13 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1200 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 618 | 0 | 230 | 799 | 0 | 0 | 0 | 0 |  | 7378 | 5052 | 12430 | 3588 | 914 | 1715 | 0 | 1415 | 4405 | 198 | 0 | 64 | 74 | 0 | 57 | 48 | 92.94
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9201600 | 0 |  | 0 | 9408500 | 3487971 | 188448 | 1504382 | 1159991 | 7142130 | 0 | 0 | 186106 | 292244 | 756480 | 35000 | 0 | 0 | 0 | 623088 | 498999 | 524603 | 0 | 325200 | 396360 | 582100 | 157500 | 147350 | 0 | 2823769 | 1932000 | 0 | 0 | 11412 | 5253778 | 0 | 0 | 0 |  | 248400 | 117360 | 117321 | 52800 | 125088 | 30240 | 0 | 564000 | 0 | 0 | 0 | 7328600 | 6226000 | 4508000 | 66909 | 1024260 | 784512 | 584640 | 0 | 1176466 | 0 | 633936 | 349330 | 0 | 0 | 0 | 349220 | 1715520 | 481920 | 0 | 0 | 7150 | 924000 | 1379400 | 617400 | 410616 | 3473836 | 0 | 328416 | 284160 | 0 | 3258060 | 0 | 0 | 0 | 7044000 | 245376 | 167552 | 0 | 3690873 | 0 | 0 | 2332800 | 0 | 1771056 | 27405 | 357120 | 1842240 | 1783127 | 7938000 | 1513200 | 775882 | 399781 | 4 | 554760 | 0 | 232508 | 603060 | 617400 | 361920 | 3915800 | 183360 | 127630 | 1789920 | 205419 | 0 | 403200 | 95927 | 1307520 | 390600 | 6039000 | 199054 | 0 | 12109089 | 933416 | 21803630 | 0 | 0 | 104964 |  | 22080000 | 0 | 6771744 | 0 | 446400 | 0 | 0 | 0 | 45120 | 37248 | 32625 | 2570000 | 124648 | 301632 | 0 | 0 | 0 | 71586 | 35939 | 161328 | 304190 | 0 | 96897 | 0 | 98902 | 0 | 0 | 103626 | 1425164 | 0 | 0 | 0 | 0 | 4597273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8094327 | 391344 | 0 | 619392 | 0 | 1936992 | 0 | 39008 | 815328 | 27496900 | 5032078 | 0 | 433200 | 9060 | 168480 | 832704 | 0 | 0 | 11970910 | 147385 | 5105500 | 27431526 | 1032690 | 0 | 915 | 104250 |  | 165673164 | 130966311 | 296639475 | 81999427 | 22080000 | 40369551 | 0 | 33207034 | 107342719 | 4755769 | 0 | 2371171 | 1715520 | 1864868 | 933416 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26500608 | 0 |  | 0 | 29919030 | 11928860.82 | 3723732.48 | 28131943.4 | 20439041.42 | 21783496.5 | 0 | 0 | 3677454.56 | 5245779.8 | 14690841.6 | 652750 | 0 | 0 | 0 | 11377586.88 | 7864224.24 | 9594988.87 | 0 | 243900 | 0 | 0 | 0 | 2639038.5 | 0 | 0 | 0 | 0 | 0 | 216143.28 | 16759551.82 | 0 | 0 | 0 |  | 4369356 | 2066709.6 | 2101219.11 | 1006368 | 2447972.16 | 497750.4 | 0 | 0 | 0 | 0 | 0 | 20446794 | 19051560 | 14966560 | 224145.15 | 3308359.8 | 2643805.44 | 2560723.2 | 0 | 4717628.66 | 0 | 11353793.76 | 6308899.8 | 0 | 0 | 0 | 261915 | 11253811.2 | 1498771.2 | 0 | 0 | 0 | 3603600 | 5145162 | 2809170 | 1868302.8 | 11880519.12 | 0 | 1822708.8 | 1483315.2 | 0 | 9089987.4 | 0 | 0 | 0 | 21765960 | 184032 | 127339.52 | 0 | 75293809.2 | 0 | 0 | 44813088 | 0 | 31188296.16 | 0 | 6360307.2 | 31962864 | 29564245.66 | 21035700 | 28841592 | 14555546.32 | 7172071.14 | 0 | 9070326 | 0 | 4171193.52 | 11524476.6 | 11983734 | 6445795.2 | 10416028 | 3129955.2 | 0 | 32737636.8 | 3446930.82 | 0 | 7205184 | 0 | 23561510.4 | 6616764 | 17935830 | 2802680.32 | 0 | 84400350.33 | 0 | 128641417 | 0 | 0 | 0 |  | 62044800 | 0 | 19976644.8 | 0 | 7745040 | 0 | 0 | 0 | 848707.2 | 700634.88 | 580725 | 8121200 | 590831.52 | 5200135.68 | 0 | 0 | 0 | 1282105.26 | 659480.65 | 2711923.68 | 6473163.2 | 0 | 1735425.27 | 0 | 1771334.82 | 0 | 0 | 78444.882 | 15719558.92 | 0 | 0 | 0 | 0 | 15171000.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23635434.84 | 6684155.52 | 0 | 12276349.44 | 0 | 38584880.64 | 0 | 0 | 16176107.52 | 178179912 | 15649762.58 | 0 | 8382420 | 0 | 0 | 14447414.4 | 0 | 0 | 87387643 | 0 | 38035975 | 181322386.86 | 0 | 0 | 0 | 0 |  | 1041132543.36 | 772173598.462 | 1813306141.822 | 240173000.062 | 62044800 | 129033683.89 | 0 | 614388747.41 | 713687243.11 | 0 | 0 | 42724856.15 | 11253811.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 152 | 8 | 65 | 42 | 330 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 28 | 30 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 300 | 240 | 212 | 0 | 40 | 20 | 20 | 0 | 51 | 0 | 37 | 24 | 0 | 0 | 0 | 13 | 72 | 11 | 0 | 0 | 2 | 40 | 57 | 0 | 0 | 163 | 0 | 0 | 3 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 53 | 10 | 12 | 121 | 58 | 391 | 58 | 52 | 17 | 1 | 15 | 0 | 0 | 34 | 29 | 12 | 112 | 0 | 9 | 108 | 0 | 0 | 7 | 13 | 50 | 17 | 230 | 0 | 0 | 495 | 31 | 876 | 0 | 0 | 15 |  | 917 | 0 | 290 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 35 | 0 | 98 | 0 | 2 | 35 | 1120 | 220 | 0 | 35 | 3 | 10 | 36 | 0 | 0 | 465 | 37 | 250 | 730 | 119 | 0 | 0 | 40 |  | 12249 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 |  | 0 | 410 | 120 | 7 | 65 | 55 | 250 | 0 | 0 | 9 | 24 | 16 | 13 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 13 | 22 | 24 | 9 | 8 | 0 | 118 | 80 | 0 | 0 | 8 | 221 | 0 | 0 | 0 | 0 | 12 | 0 | 34 | 0 | 0 | 5 | 0 | 24 | 0 | 0 | 0 | 280 | 240 | 142 | 8 | 33 | 34 | 35 | 0 | 51 | 0 | 36 | 24 | 0 | 0 | 0 | 13 | 68 | 19 | 0 | 0 | 0 | 40 | 58 | 11 | 10 | 120 | 0 | 0 | 30 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 228 | 0 | 0 | 85 | 0 | 97 | 0 | 12 | 100 | 138 | 290 | 78 | 52 | 17 | 0 | 30 | 0 | 17 | 17 | 28 | 12 | 382 | 17 | 0 | 72 | 17 | 0 | 30 | 0 | 69 | 17 | 230 | 17 | 0 | 374 | 30 | 925 | 0 | 0 | 0 |  | 917 | 0 | 230 | 0 | 21 | 0 | 0 | 0 | 42 | 25 | 0 | 80 | 7 | 16 | 0 | 0 | 0 | 40 | 5 | 90 | 0 | 0 | 27 | 0 | 25 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 920 | 180 | 0 | 50 | 0 | 0 | 86 | 0 | 0 | 383 | 0 | 140 | 1503 | 0 | 0 | 0 | 0 |  | 12374 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 152 | 16 | 85 | 55 | 0 | 0 | 100 | 17 | 50 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 13 | 22 | 24 | 12 | 17 | 0 | 120 | 80 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 80 | 85 | 25 | 38 | 50 | 0 | 25 | 0 | 0 | 0 | 300 | 360 | 150 | 0 | 50 | 37 | 20 | 0 | 51 | 0 | 36 | 33 | 0 | 0 |  | 17 | 100 | 30 | 0 | 0 | 0 | 40 | 57 | 50 | 33 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 280 | 0 | 0 | 124 | 0 | 149 | 0 | 25 | 150 | 138 | 380 | 78 | 72 | 105 | 0 | 107 | 54 | 85 | 106 | 66 | 25 | 380 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 115 | 17 | 300 | 163 | 0 | 450 | 60 | 960 | 0 | 0 |  |  | 918 | 0 | 280 | 0 | 64 | 0 | 0 | 0 | 40 | 60 | 24 | 130 | 10 | 64 | 0 | 0 | 0 | 40 | 20 | 86 | 35 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 87 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1500 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 450 | 150 | 15 | 85 | 55 | 0 | 0 | 100 | 17 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 35 | 0 | 13 | 22 | 24 | 12 | 8 | 0 | 120 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 16 | 51 | 25 | 25 | 6 | 0 | 25 | 0 | 0 | 0 | 280 | 360 | 130 | 0 | 50 | 37 | 20 | 0 | 51 | 0 | 36 | 25 | 0 | 0 |  | 17 | 90 | 25 | 0 | 0 | 1.6 | 40 | 57 | 50 | 33 | 163 | 0 | 30 | 0 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 100 | 0 | 149 | 20 | 25 | 70 | 55 | 360 | 68 | 17 | 105 | 5 | 50 | 17 | 51 | 34 | 28 | 25 | 150 | 17 | 50 | 162 | 17 | 0 | 17 | 35 | 50 | 17 | 300 | 17 | 0 | 300 | 44 | 927 | 0 | 0 | 70 |  | 918 | 0 | 280 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 70 | 0 | 106 | 0 | 8 | 70 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 250 | 1000 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 350 | 157 | 0 | 0 | 15 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 12 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 280 | 360 | 123 | 0 | 50 | 37 | 40 | 0 | 10 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 56 | 29 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 150 | 1 | 0 | 17 | 0 | 287 | 45 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 28 | 0 | 350 | 0 | 2 | 0 | 0 | 0 | 54 | 3 | 33 | 17 | 230 | 0 | 0 | 178 | 36 | 927 | 0 | 0 | 3 | 0 | 918 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 600 | 220 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 408 | 8 | 150 | 871 | 30 | 0 | 0 | 8 | 0 |  |  |  | 122368978 | 22080000 | 0 | 107342719 | 35578205 | 1715520 | 1864868 | 933416 | 4755769 |  |  | 296639475
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 122.369 | 22.08 | 0 | 107.3427 | 35.5782 | 1.7155 | 1.8649 | 0.93342 | 4.7558
| Minimum Generation |  | 11219 | 8:00
| Highest Generation |  | 13500 | 1:00 | [129 empty] | 0 | [73 empty] | 296.6395
| Day Peak Generation |  | 12249 | 12:00
| Evening Peak Generation |  | 12374 | 19:30 | [203 empty] | 202699852
| HVDC Max Flow |  | 918 | 19:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 917 | 19:30
| Load factor L.F |  | 91.56% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-02
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12249 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9524
Evening Peak Generation : |  |  | 12374 | MW Hour : | 19:30 | Available Max Generation : |  | 16152
E.P. Demand (at gen end) : |  |  | 12374 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12500
Maximum Generation : |  |  | 13500 | MW Hour : | 1:00 | Reserve(Generation end)
Total Gen. (MKWH) : |  |  | 296.6395 | System Load Factor : | 91.56% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 344 | MW at | 9:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-02
Actual : |  | 93 | Ft.(MSL) , | Rule curve : | 89.32 | Ft.( MSL )
Gas Consumed : |  | Total = | 903.34 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 369206683.952
: |  |  | Coal : | 713687243.11 | Oil : | 657113603.56 | Total : | 1740007530.622
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5341.9617 |  |  | 0 | -2.866%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | -1.035%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | -0.6449%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | -0.2316%
Cumilla Area |  | 0 | 0:00 | 1476.7776 |  |  | 0 | -0.4881%
Mymensingh Area |  | 0 | 0:00 | 1099.0436 |  |  | 0 | -0.1293%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | -0.8142%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | -0.06366%
Rangpur Area |  | 0 | 0:00 | 1004.2252 |  |  | 0 | -0.07249%
Total |  | 0 |  | 15383.3573 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:36 | 14:40 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Distance relays Due to Unknown
10:21 | 18:54 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to Tower Erection
10:46 |  | Madunaghat-Meghnaghat 400kV Ckt-2 Tripped from Meghnaghat 400/230kV end showing siprotec 5 and 3 relays Due to
Transient Fault
10:46 | 13:06 | Maniknagar-Siddhirganj 230kV Ckt-2 Tripped from Siddhirganj 230/132kV end showing REL670 relays Due to tripping
11:19 | 13:35 | Dhamrai-Kaliakoir 132 kV Ckt-2 Project Work S/D from Dhamrai 132/33kV end Due to Project work
11:58 |  | Bibiyana-III 400 MW CCPP, FGMO is ON with remarks:-
12:58 | 19:19 | Kurigram 132/33kV S/S Capacitor Bank Tripped showing Micom p-127 relays Due to Overvaltage
13:37 | 13:59 | Barapukuria-Rangpur 132 kV Ckt-1 Forced S/D from Barapukuria end Due to Emergency load management for NLDC.
13:51 | 13:59 | Barapukuria-Rangpur 132 kV Ckt-2 Forced S/D from Barapukuria end Due to Emergency load management for NLDC.
| 14:14 | Sirajganj 132/33kV S/S Solar Park 2 is restored.
15:15 | 15:29 | Jaldhaka 132/33kV S/S 406T-1 LT Tripped showing Micon P142 relays Due to Due 33kv PBS Domar-2 feeder
| 16:05 | Meghnaghat 400/230kV S/S Meghnaghat-Reliance PP 400KV Ckt-2 is restored.
16:40 |  | Meghnaghat 400/230kV S/S Meghnaghat-Reliance PP 400KV Ckt-1 Forced S/D Due to for route cause analysis
17:48 | 18:48 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to Red Hot |  |  |  |  | About 20 MW power interrupt.
19:26 | 21:02 | Kabirpur 132/33kV S/S XFR, T-3 HT Forced S/D Due to Kabirpur 132/33kV TR-3 shutdown taken by DPBS-1 at 19.26 due |  |  |  |  | About 80 MW power interrupt.
to bus side loop changing work of 33kV DEPZ and Nayerhat feeders.
20:55 | 22:41 | Chowmuhani 132/33kV S/S TR2 Forced S/D Due to 33 KV L-Bus Red hot maintenance. |  |  |  |  | About 30 MW power interrupt.
23:05 |  | Adani Power Jharkhand Ltd. Unit-1 was shutdown due to turbine rotor balancing.
23:47 |  | Bhola CCPP GT1 was shutdown due to air filter change.
00:24 |  | Siddhirganj 335 MW CCPP Shutdown with remarks:- ST
00:28 |  | Siddhirganj 335 MW CCPP Shutdown with remarks:- GT
01:21 |  | Siddhirgonj 2*120 MW GTPP Synchronized with remarks:- GT-2
02:02 |  | SS Power Tripped
02:03 | 02:09 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing 86.1 & 86.2 Master relays Due to df/dt |  |  |  |  | About 45 MW power interrupt.
03:46 |  | Adani Power Jharkhand Ltd. unit-1 was sync.
06:35 |  | Ashuganj 230/132/33kV S/S TR-OAT-12 LT Scheduled S/D Due to FOR BUSBAR-1 MAINTENANCE
06:50 |  | Thakurgaon 132/33kV S/S RPC Scheduled S/D Due to Pirgonj 33 kV feeder PT installation at Bus section-03
06:54 |  | SS Power Synchronized with remarks:- unit2
06:58 |  | Barapukuria 230/132KV T-06, 723T LT Tripped showing ABB REB 500 relays Due to Buchholz Trip OLTC at 230KV Side.
07:14 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Project Work S/D from Ishurdi 230/132kV end Due to line stringging work
07:14 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Project Work S/D from Ishurdi 230/132kV end Due to line stringging work
07:30 |  | Ishurdi-Pabna 132kV ckt S/D from Pabna end Due to for ruppur line and from Ishurdi 132/33kV end Due to line stringging work .
07:30 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Scheduled S/D from Thakurgaon 132/33kV end Due to Red hot maintenance
07:35 |  | Jashore 132/33kV S/S T-1 HT Project Work S/D Due to 33kv ds change
07:50 |  | Barapukuria 230/132/33kV S/S 230/132KV T-06, 723T HT Forced S/D Due to Emergency maintenance at OLTC Buchholz.
07:58 |  | Brahmanbaria 132/33kV S/S 403T HT Forced S/D Due to emergency red hot maintenance by PBS |  |  |  |  | About 23 MW power interrupt.
07:58 |  | Brahmanbaria 132/33kV S/S 402T HT Forced S/D Due to emergency red hot maintenance by PBS |  |  |  |  | About 23 MW power interrupt.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-01
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 333 | 9201600 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 410 | 9408500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 7 | 188448 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 120 | 3487971 | Unit-2 Under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 65 | 1504382 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 1159991
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 13 | 35000 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 186106 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 7142130 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 292244 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 623088
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 756480 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 498999 | 33 kV line fault.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 524603
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 721560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 582100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 9 | 157500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 147350 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 228 | 3690873 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 97 | 1771056 | Low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 775882 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 183360 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1789920 | Low demand
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 95927
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 390600 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 1950 | 45315670
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 11412 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 27405
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 5 | 30240 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 198 | 4755769
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 221 | 5253778
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 399781 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 117360 | Reserve
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 117321 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 52800 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 357120 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 564000
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 125088 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 4
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 554760 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 232508 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 361920 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 205419 | Low demand
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 199054 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 374 | 12109089 | Unit-1 Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 30 | 933416
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 925 | 21803630
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 1941 | 48211874
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 142 | 4508000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7328600 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6226000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 6039000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 784512 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 35 | 584640 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 66909 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1176466
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 1783127 | Engine problem
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 633936 | Machine problem.
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 33 | 1024260 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1842240 | Low demand
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 68 | 1715520
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 24 | 349330 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 13 | 349220 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 603060 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 617400 | Low demand
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 69 | 1307520 | Low demand
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 104964
| Cumilla Area Total |  |  |  | 2950 | 1546 | 37044704
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 19 | 481920 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7150
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 85 | 2332800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1513200 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 127630
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 248400 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 30 | 403200 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 224 | 5114300
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 924000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1379400 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3473836 | Frequency Control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 11 | 617400 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 410616 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 167552 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 328416 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 30 | 284160 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 3258060 | ST Under maint
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 245376 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7044000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 290 | 7938000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 382 | 3915800
| Sylhet Area Total |  |  |  | 2331 | 1386 | 29986616
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 917 | 22080000
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 21 | 446400 | Fuel shortage
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 42 | 45120
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 25 | 37248 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 230 | 6771744 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 32625 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 391344 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 168480
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 383 | 11970910 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1618 | 41943871
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 301632 | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 7 | 124648
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2570000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 920 | 27496900 | Frequency Control
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 180 | 5032078 | Frequency Control
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 50 | 433200 | Low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 140 | 5105500 | Low demand
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 915
| Barisal Area Total |  |  |  | 2236 | 1393 | 41064873
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 71586 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 35939 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 304190 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 96897
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 140 | 4597273 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 241 | 8094327
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 98902 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 2 | 103626 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 161328 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 619392 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 815328 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 9060
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1503 | 27431526
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 104250
| Rajshahi Area Total |  |  |  | 3381 | 2073 | 42543624
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1425164
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 96 | 1936992 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39008
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 86 | 832704 | Low demand
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 147385
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1032690
| Rangpur Area Total |  |  |  | 950 | 243 | 5413943
| Total |  |  |  | 26947 | 12374 | 296639475
| Eastern Grid Total |  |  |  | 16526 | 7047 | 165673164
| Western Grid Total |  |  |  | 10421 | 5327 | 130966311
| National Grid Total |  |  |  | 26947 | 12374 | 296639475
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-07-2024 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9560.8 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5011.6 | MW
i) Dhaka area |  |  | 5050.4 |  | MW | i) Khulna area |  |  |  | 1891.6 | MW
ii) Chattogram area |  |  | 1391.4 |  | MW | ii) Barishal area |  |  |  | 473.8 | MW
iii) Cumilla area |  |  | 1447 |  | MW | iii) Rajshahi area |  |  |  | 1656.2 | MW
iv) Mymensingh area |  |  | 1063 |  | MW | iv) Rangpur area |  |  |  | 990 | MW
v) Sylhet area |  |  | 609 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14572.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 17:00 | 67 | Jamalpur | 104 | 00:00 | 133 | Rahim | 40 | 15:00
2 | AKSML | 90 | 12:00 | 68 | Jashore | 128 | 00:00 | 134 | Rajbari | 76 | 00:00
3 | Aftabnagar | 32 | 00:00 | 69 | Jhenaidah | 126 | 00:00 | 135 | Rajendrapur | 90 | 12:00
4 | Agargaon | 110 | 13:00 | 70 | Joydebpur | 192 | 12:00 | 136 | Rajshahi | 141 | 00:00
5 | Agrabad | 76 | 14:00 | 71 | Joypurhat | 76 | 00:00 | 137 | Rajshahi-230 | 79 | 00:00
6 | Amnura | 88 | 00:00 | 72 | Juldah | 21 | 23:00 | 138 | Ramganj | 84 | 14:00
7 | Ashuganj | 85 | 00:00 | 73 | KSRM | 31 | 10:00 | 139 | Rampur | 34 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 297 | 15:00 | 140 | Rangamati | 15 | 19:30
9 | BSRM | 187 | 01:00 | 75 | Kachua | 70 | 21:00 | 141 | Rangpur | 134 | 19:30
10 | Bagerhat | 91 | 00:00 | 76 | Kallyanpur | 111 | 00:00 | 142 | Ruppur | 7 | 12:00
11 | Bakulia | 91 | 14:00 | 77 | Kalurghat | 34 | 12:00 | 143 | SSM | 16 | 00:00
12 | Banani | 58 | 15:00 | 78 | Kamrangirchar | 53 | 13:00 | 144 | Saidpur | 109 | 11:00
13 | Bangabhaban | 21 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 124 | 00:00
14 | Barapukuria | 63 | 09:00 | 80 | Kazla | 112 | 00:00 | 146 | Satmasjid | 106 | 13:00
15 | Barguna | 22 | 00:00 | 81 | Keranigonj | 82 | 19:30 | 147 | Savar | 205 | 17:00
16 | Barishal | 107 | 00:00 | 82 | Khagrachori | 26 | 18:30 | 148 | SevenRings | 5 | 03:00
17 | Barishal-230 | 98 | 00:00 | 83 | Khulna | 64 | 18:30 | 149 | ShahCement | 30 | 09:00
18 | Baroaulia | 69 | 12:00 | 84 | Khulshi | 143 | 05:00 | 150 | Shahjadpur | 66 | 01:00
19 | Baroirhat | 60 | 00:00 | 85 | Kishoreganj | 150 | 04:00 | 151 | Shahjibazar | 119 | 04:00
20 | Bashundhara | 160 | 13:00 | 86 | Kodda | 280 | 21:00 | 152 | Shahmirpur | 50 | 00:00
21 | BashundharaCement | 12 | 20:00 | 87 | Kulaura | 54 | 19:30 | 153 | Shariatpur | 85 | 00:00
22 | Beanibazar | 78 | 19:30 | 88 | Kurigram | 60 | 12:00 | 154 | Sherpur | 118 | 22:00
23 | Benapole | 62 | 00:00 | 89 | Kushtia | 137 | 00:00 | 155 | Shikalbaha | 31 | 00:00
24 | Bhaluka | 128 | 12:00 | 90 | Lalbag | 85 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 57 | 00:00 | 91 | Lalmonirhat | 56 | 23:00 | 157 | Shitalakhya | 81 | 12:00
26 | Bhangura | 34 | 01:00 | 92 | MI_Cement | 13 | 20:00 | 158 | Sholosohor | 44 | 15:00
27 | Bheramara(GK) | 68 | 00:00 | 93 | Madanganj | 39 | 00:00 | 159 | Shyampur | 168 | 12:00
28 | Bhulta | 222 | 19:30 | 94 | Madaripur | 106 | 00:00 | 160 | Siddhirganj | 116 | 08:00
29 | Bog-Sherpur | 66 | 03:00 | 95 | Madartek | 84 | 00:00 | 161 | Sirajganj | 114 | 00:00
30 | Bogura | 172 | 03:00 | 96 | Madunaghat | 45 | 18:30 | 162 | Sonargaon | 96 | 00:00
31 | Borhanuddin | 85 | 00:00 | 97 | Magura | 63 | 00:00 | 163 | Sreemongol | 76 | 00:00
32 | Brahmanbaria | 175 | 01:00 | 98 | Mahasthangarh | 90 | 00:00 | 164 | Sreepur | 92 | 10:00
33 | Cantonment | 112 | 13:00 | 99 | Manikganj | 114 | 22:00 | 165 | Srinagar | 47 | 00:00
34 | Chandpur | 58 | 05:00 | 100 | Maniknagar | 60 | 13:00 | 166 | Sunamganj | 58 | 21:00
35 | Chandraghona | 30 | 00:00 | 101 | Matarbari | 39 | 19:00 | 167 | Sylhet | 50 | 00:00
36 | Chapai | 71 | 05:00 | 102 | Matuail | 74 | 12:00 | 168 | Sylhet-132 | 121 | 19:00
37 | Charsaidpur | 40 | 15:00 | 103 | Millgate | 115 | 12:00 | 169 | TK | 30 | 00:00
38 | Chauddagram | 58 | 05:00 | 104 | Mirpur | 132 | 00:00 | 170 | Tangail | 162 | 00:00
39 | Chhatak | 34 | 23:00 | 105 | Mirsorai | 6 | 00:00 | 171 | Thakurgaon | 92 | 13:00
40 | Chowmuhani | 170 | 01:00 | 106 | Mirzapur | 39 | 21:00 | 172 | Tongi | 107 | 15:00
41 | Chuadanga | 119 | 00:00 | 107 | Mithapukur | 60 | 10:00 | 173 | Ullahpara | 26 | 00:00
42 | Coxsbazar | 112 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 55 | 00:00
43 | Cumilla(N) | 132 | 05:00 | 109 | Mogbazar | 120 | 13:00 | 175 | Uttara | 80 | 13:00
44 | Cumilla(S) | 176 | 00:00 | 110 | Mongla | 29 | 11:00 | 176 | UttaraNew | 58 | 00:00
45 | Daudkandi | 148 | 00:00 | 111 | Motijheel | 42 | 12:00 | 177 | Zigatola | 78 | 13:00
46 | Dhaka | 54 | 12:00 | 112 | Munshiganj | 114 | 00:00
47 | Dhamrai | 129 | 15:00 | 113 | Mymensingh | 225 | 02:00
48 | Dhanmondi | 142 | 13:00 | 114 | Naogaon | 157 | 00:00
49 | Dohazari | 80 | 22:00 | 115 | Narail | 55 | 01:00
50 | Faridpur | 171 | 00:00 | 116 | Narinda | 67 | 13:00
51 | Fatullah | 89 | 10:00 | 117 | Narshingdi | 162 | 19:30
52 | Fenchuganj | 41 | 03:00 | 118 | Natore | 164 | 00:00
53 | Feni | 108 | 19:00 | 119 | Nawabganj | 48 | 00:00
54 | GPH | 93 | 15:00 | 120 | Netrakona | 105 | 00:00
55 | Ghatail | 62 | 22:00 | 121 | New | 56 | 12:00
56 | Ghorashal | 51 | 10:00 | 122 | Niamatpur | 79 | 00:00
57 | Goalpara | 34 | 00:00 | 123 | Noapara | 47 | 00:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 389 | 07:00 | 371 | 11:00 | Kaliakoir | 400 | 7:00 | 388 | 19:00
| Ashuganj | 405 | 9:00 | 392 | 17:00 | Madunaghat_I | 405 | 11:00 | 390 | 20:00
| Bhulta | 400 | 06:00 | 384 | 11:00 | Meghnaghat | 384 | 07:00 | 371 | 11:00
| Bibiana | 399 | 07:00 | 390 | 10:00 | Payra | 411 | 06:00 | 404 | 00:00
| BIPTC | 406 | 06:00 | 396 | 00:00 | Rahanpur | 408 | 14:00 | 380 | 04:00
| Bogura | 399 | 14:00 | 363 | 04:00 | Rampal | 404 | 07:00 | 391 | 00:00
| Gopalganj | 400 | 07:00 | 388 | 01:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 07:00 | 217 | 11:00 | Haripur | 232 | 06:00 | 221 | 11:00
| AKSML | 234 | 00:00 | 226 | 07:00 | Hasnabad | 232 | 18:30 | 221 | 11:00
| Aminbazar | 230 | 02:00 | 220 | 10:00 | Hathazari | 237 | 05:00 | 231 | 12:00
| Ashuganj | 238 | 07:00 | 228 | 00:00 | Ishurdi | 234 | 08:00 | 225 | 00:00
| Ashuganj-400 | 232 | 9:00 | 220 | 18:00 | Jhenaidah | 227 | 17:00 | 216 | 00:00
| Baghabari | 231 | 14:00 | 224 | 00:00 | Kaliakoir | 218 | 12:00 | 210 | 23:00
| Barapukuria | 220 | 15:00 | 197 | 03:00 | Keranigonj | 230 | 07:00 | 218 | 11:00
| Barapukuria-230 | 220 | 12:00 | 208 | 21:00 | Khulna(S) | 232 | 07:00 | 222 | 00:00
| Barishal | 236 | 18:30 | 226 | 01:00 | Madunaghat_I | 221 | 13:00 | 210 | 0:00
| Bheramara | 232 | 17:00 | 224 | 00:00 | Maniknagar | 233 | 07:00 | 219 | 11:00
| Bhulta | 234 | 07:00 | 222 | 11:00 | Meghnaghat | 240 | 21:00 | 232 | 12:00
| Bibiana | 228 | 18:30 | 222 | 10:00 | Meghnaghat-400 | 235 | 07:00 | 226 | 11:00
| BIPTC | 234 | 08:00 | 223 | 00:00 | Mirsorai | 232 | 07:00 | 224 | 11:00
| Bogura | 228 | 14:00 | 214 | 06:00 | Rajshahi | 233 | 17:00 | 225 | 00:00
| Bogura-400 | 230 | 15:00 | 210 | 04:00 | Rampal | 232 | 07:00 | 220 | 00:00
| Borhanuddin | 242 | 08:00 | 234 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 232 | 07:00 | 224 | 11:00 | Rampura | 233 | 22:00 | 221 | 11:00
| Cumilla(N) | 231 | 07:00 | 223 | 00:00 | Shikalbaha | 233 | 00:00 | 227 | 16:00
| Faridpur | 236 | 07:00 | 227 | 00:00 | Shyampur | 232 | 07:00 | 220 | 11:00
| Fenchuganj | 230 | 07:00 | 225 | 11:00 | Siddhirganj | 233 | 22:00 | 226 | 15:00
| Ghorashal | 235 | 07:00 | 234 | 00:00 | Sirajgonj | 237 | 14:00 | 229 | 02:00
| Ghorashal-230 | 233 | 08:00 | 223 | 11:00 | Sreepur | 230 | 08:00 | 223 | 00:00
| Gopalganj | 236 | 19:00 | 227 | 01:00 | Tongi | 230 | 07:00 | 221 | 15:00
| GPH | 232 | 07:00 | 227 | 11:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 06:00 | 127 | 12:00 | Kushtia | 136 | 17:00 | 130 | 00:00
| Agargaon | 138 | 07:00 | 129 | 11:00 | Lalbag | 134 | 07:00 | 126 | 11:00
| Agrabad | 134 | 07:00 | 130 | 16:00 | Lalmonirhat | 137 | 14:00 | 114 | 03:00
| AKS | 133 | 07:00 | 129 | 17:00 | Madanganj | 132 | 08:00 | 126 | 12:00
| Aminbazar | 138 | 03:00 | 126 | 08:00 | Madaripur | 135 | 08:00 | 129 | 00:00
| Amnura | 138 | 14:00 | 117 | 03:00 | Madartek | 136 | 07:00 | 127 | 11:00
| Ashuganj | 139 | 07:00 | 135 | 00:00 | Madunaghat | 135 | 09:00 | 132 | 14:00
| Bagerhat | 135 | 06:00 | 126 | 23:00 | Magura | 138 | 17:00 | 130 | 00:00
| Bakulia | 134 | 00:00 | 130 | 15:00 | Mahasthangarh | 136 | 14:00 | 121 | 03:00
| Banani | 136 | 22:00 | 126 | 11:00 | Manikganj | 128 | 13:00 | 121 | 11:00
| Bangabhaban | 132 | 06:00 | 116 | 11:00 | Maniknagar | 132 | 07:00 | 117 | 11:00
| Barapukuria | 137 | 15:00 | 121 | 03:00 | Matarbari | 129 | 07:00 | 118 | 23:00
| Barguna | 140 | 18:30 | 130 | 00:00 | Matuail | 131.5 | 19:00 | 125 | 11:00
| Barishal | 141 | 07:00 | 134 | 01:00 | Millgate | 135 | 07:00 | 126 | 11:00
| Barishal-230 | 140 | 07:00 | 133 | 01:00 | Mirpur | 138 | 07:00 | 128 | 11:00
| Baroaulia | 135 | 08:00 | 131 | 16:00 | Mirzapur | 130 | 19:00 | 122 | 11:00
| Baroirhat | 133 | 08:00 | 125 | 00:00 | Mithapukur | 135 | 14:00 | 117 | 04:00
| Bashundhara | 136 | 06:00 | 126 | 11:00 | MI_Cement | 134 | 19:00 | 126 | 11:00
| BashundharaCement | 132 | 08:00 | 126 | 12:00 | Modern | 133 | 00:00 | 131 | 15:00
| Beanibazar | 126 | 18:00 | 119 | 00:00 | Mogbazar | 139 | 14:00 | 133 | 18:30
| Benapole | 136 | 06:00 | 128 | 00:00 | Mongla | 135 | 17:00 | 126 | 23:00
| Bhaluka | 128 | 07:00 | 122 | 00:00 | Motijheel | 132 | 07:00 | 116 | 11:00
| Bhandaria | 136 | 06:00 | 126 | 00:00 | Munshiganj | 133 | 19:00 | 125 | 11:00
| Bhangura | 136 | 14:00 | 130 | 00:00 | Mymensingh | 135 | 13:00 | 115 | 02:00
| Bheramara | 135 | 14:00 | 131 | 00:00 | Naogaon | 129 | 12:00 | 116 | 00:00
| Bheramara(GK) | 136 | 17:00 | 131 | 00:00 | Narail | 138 | 06:00 | 129 | 00:00
| Bhulta | 124 | 19:00 | 117 | 12:00 | Narinda | 132 | 7:00 | 117 | 11:00
| Bog-Sherpur | 136 | 14:00 | 123 | 03:00 | Narshingdi | 123 | 19:00 | 116 | 12:00
| Bogura | 137 | 14:00 | 125 | 03:00 | Natore | 134 | 14:00 | 127 | 00:00
| Bogura-230 | 137 | 14:00 | 128 | 00:00 | Nawabganj | 134 | 07:00 | 127 | 11:00
| Brahmanbaria | 131 | 07:00 | 123 | 01:00 | Netrakona | 136 | 00:00 | 120 | 19:30
| Cantonment | 138 | 07:00 | 128 | 11:00 | New | 135 | 07:00 | 128 | 11:00
| Chandpur | 135 | 13:00 | 123 | 23:00 | Niamatpur | 137 | 14:00 | 128 | 06:00
| Chandraghona | 136 | 07:00 | 133 | 15:00 | Noapara | 138 | 06:00 | 130 | 00:00
| Chapai | 133 | 14:00 | 122 | 03:00 | Pabna | 134 | 17:00 | 128 | 00:00
| Charsaidpur | 134 | 18:30 | 126 | 11:00 | Palashbari | 135 | 14:00 | 118 | 05:00
| Chauddagram | 130 | 13:00 | 119 | 23:00 | Panchagarh | 134 | 15:00 | 112 | 03:00
| Chhatak | 126 | 08:00 | 120 | 19:30 | Patuakhali | 136 | 18:00 | 130 | 01:00
| Chowmuhani | 127 | 19:30 | 115 | 23:00 | Payra | 136 | 05:00 | 132 | 01:00
| Chuadanga | 134 | 17:00 | 120 | 00:00 | PHP | 134 | 08:00 | 124 | 00:00
| Coxsbazar | 132 | 02:00 | 121 | 23:00 | Postogola | 137 | 18:30 | 128 | 11:00
| Cumilla(N) | 135 | 07:00 | 128 | 00:00 | Purbachal | 137 | 07:00 | 126 | 11:00
| Cumilla(S) | 133 | 07:00 | 125 | 23:00 | Purbasadipur | 135 | 15:00 | 111 | 03:00
| Daudkandi | 128 | 08:00 | 120 | 04:00 | Rahanpur | 138 | 14:00 | 128 | 03:00
| Dhaka | 136 | 06:00 | 127 | 11:00 | Rahim | 131 | 19:00 | 126 | 11:00
| Dhamrai | 132 | 08:00 | 126 | 10:00 | Rajbari | 132 | 07:00 | 127 | 00:00
| Dhanmondi | 132 | 22:00 | 125 | 12:00 | Rajendrapur | 127 | 00:00 | 118 | 12:00
| Dohazari | 132 | 05:00 | 128 | 18:00 | Rajshahi | 133 | 08:00 | 129 | 04:00
| Faridpur | 133 | 08:00 | 127 | 00:00 | Rajshahi-230 | 135 | 18:30 | 115 | 04:00
| Fatullah | 135 | 07:00 | 127 | 11:00 | Ramganj | 130 | 07:00 | 117 | 23:00
| Fenchuganj | 132 | 07:00 | 130 | 00:00 | Rampur | 134 | 08:00 | 129 | 17:00
| Feni | 128 | 00:00 | 116 | 23:00 | Rampura | 135 | 05:00 | 127 | 11:00
| Ghatail | 132 | 09:00 | 122 | 20:00 | Rangamati | 136 | 07:00 | 132 | 16:00
| Ghorashal | 138 | 07:00 | 132 | 11:00 | Rangpur | 140 | 14:00 | 114 | 04:00
| Goalpara | 140 | 06:00 | 132 | 21:00 | Ruppur | 137 | 18:30 | 132 | 00:00
| Gollamari | 138 | 07:00 | 132 | 00:00 | Saidpur | 133 | 15:00 | 113 | 04:00
| Gopalganj | 134 | 06:00 | 128 | 01:00 | Satkhira | 136 | 17:00 | 127 | 00:00
| Gopalganj-400 | 135 | 19:00 | 128 | 11:00 | Satmasjid | 137 | 07:00 | 128 | 11:00
| Gulshan | 135 | 05:00 | 126 | 11:00 | Savar | 137 | 19:00 | 130 | 09:00
| Halishahar | 135 | 07:00 | 129 | 16:00 | SevenRings | 138 | 07:00 | 132 | 11:00
| Haripur | 131 | 19:00 | 126 | 11:00 | ShahCement | 134 | 18:30 | 126 | 11:00
| HaripurSBU | 131 | 19:00 | 126 | 10:00 | Shahjadpur | 138 | 06:00 | 134 | 00:00
| Hasnabad | 136 | 19:00 | 129 | 12:00 | Shahjibazar | 129 | 08:00 | 121 | 00:00
| Hathazari | 136 | 18:30 | 133 | 10:00 | Shahmirpur | 135 | 13:00 | 130 | 16:00
| Ishurdi | 137 | 19:30 | 132 | 00:00 | Shariatpur | 136 | 18:30 | 127 | 00:00
| Jaldhaka | 133 | 15:00 | 113 | 03:00 | Sherpur | 138 | 14:00 | 124 | 20:00
| Jamalpur | 140 | 13:00 | 123 | 20:00 | Shikalbaha | 125 | 07:00 | 119 | 14:00
| Jashore | 137 | 17:00 | 128 | 00:00 | Shikalbaha-230 | 135 | 07:00 | 131 | 16:00
| Jhenaidah | 139 | 07:00 | 130 | 00:00 | Shitalakhya | 134 | 19:00 | 126 | 11:00
| Jhenaidah-230 | 139 | 07:00 | 131 | 00:00 | Sholosohor | 134 | 07:00 | 130 | 15:00
| Joydebpur | 135 | 07:00 | 130 | 00:00 | Shyampur | 135 | 22:00 | 127 | 11:00
| Joypurhat | 129 | 13:00 | 114 | 00:00 | Shyampur-230 | 134 | 19:00 | 126 | 11:00
| Juldah | 135 | 05:00 | 131 | 16:00 | Siddhirganj | 132 | 19:00 | 126 | 11:00
| Kabirpur | 133 | 22:00 | 121 | 11:00 | Sirajganj | 134 | 14:00 | 125 | 07:00
| Kachua | 134 | 13:00 | 120 | 16:00 | Sonargaon | 130 | 21:00 | 123 | 11:00
| Kaliakoir | 133 | 8:00 | 127 | 19:00 | Sreemongol | 129 | 07:00 | 123 | 00:00
| Kallyanpur | 131 | 05:00 | 124 | 12:00 | Sreepur | 130 | 08:00 | 124 | 01:00
| Kalurghat | 135 | 08:00 | 131 | 11:00 | Srinagar | 135 | 07:00 | 126 | 11:00
| Kamrangirchar | 135 | 19:00 | 125 | 11:00 | SSM | 139 | 08:00 | 133 | 16:00
| Kaptai | 136 | 18:00 | 132 | 23:00 | Sunamganj | 126 | 10:00 | 118 | 20:00
| Kazla | 132 | 08:00 | 120 | 12:00 | Sylhet | 128 | 09:00 | 121 | 00:00
| Keranigonj | 135 | 07:00 | 127 | 11:00 | Sylhet-132 | 128 | 09:00 | 123 | 00:00
| Khagrachori | 135 | 07:00 | 131 | 16:00 | Tangail | 130 | 19:00 | 120 | 20:00
| Khulna | 138 | 06:00 | 131 | 00:00 | Thakurgaon | 134 | 15:00 | 110 | 03:00
| Khulna(S) | 138 | 06:00 | 132 | 00:00 | TK | 134 | 03:00 | 132 | 10:00
| Khulshi | 133 | 01:00 | 129 | 16:00 | Tongi | 136 | 07:00 | 130 | 11:00
| Kishoreganj | 132 | 07:00 | 123 | 01:00 | Ullahpara | 136 | 14:00 | 129 | 02:00
| Kodda | 131 | 05:00 | 118 | 11:00 | Ullon | 135 | 05:00 | 127 | 11:00
| KSRM | 135 | 07:00 | 130 | 16:00 | Uttara | 138 | 07:00 | 127 | 11:00
| Kulaura | 131 | 07:00 | 126 | 00:00 | UttaraNew | 137 | 06:00 | 128 | 11:00
| Kurigram | 134 | 14:00 | 114 | 04:00 | Zigatola | 134 | 06:00 | 123 | 23:00

## L-Curve
Date | 2024-08-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 372 | 7378 | 5052 | 12430 |  |  |  | QF-LDC-11
0:30 | 665 | 7392.5 | 5572.5 | 12965 | Date: | 2024-08-01
1:00 | 958 | 7407 | 6093 | 13500
1:30 | 972 | 7259 | 6063 | 13322
2:00 | 986 | 7111 | 6033 | 13144
2:30 | 931 | 7059.5 | 5966.5 | 13026 | [5 empty] | Gen. at Eve. Peak | 12374 | 12374 MW (19:30 )
3:00 | 876 | 7008 | 5900 | 12908 | [6 empty] | 19:30
3:30 | 900 | 6965 | 5844.5 | 12809.5 | [5 empty] | Gen. at Day Peak | 12249 | 12249 MW (12:00 )
4:00 | 924 | 6922 | 5789 | 12711 | [6 empty] | 12:00
4:30 | 878 | 6906.5 | 5660.5 | 12567 | [5 empty] | Highest Generation | 13500
5:00 | 832 | 6891 | 5532 | 12423 | [6 empty] | 1:00
5:30 | 836 | 6759.5 | 5429.5 | 12189
6:00 | 840 | 6628 | 5327 | 11955
6:30 | 692 | 6601 | 5259.5 | 11860.5
7:00 | 544 | 6574 | 5192 | 11766
7:30 | 515 | 6427 | 5065.5 | 11492.5
8:00 | 486 | 6280 | 4939 | 11219
8:30 | 415 | 6550 | 4965 | 11515
9:00 | 344 | 6820 | 4991 | 11811
9:30 | 448 | 6853 | 5062 | 11915
10:00 | 552 | 6886 | 5133 | 12019
10:30 | 696 | 6814.5 | 5199 | 12013.5
11:00 | 840 | 6743 | 5265 | 12008
11:30 | 855 | 6838 | 5290.5 | 12128.5
12:00 | 870 | 6933 | 5316 | 12249
12:30 | 823 | 6900 | 5315.5 | 12215.5
13:00 | 776 | 6867 | 5315 | 12182
13:30 | 829 | 6838.5 | 5208 | 12046.5
14:00 | 882 | 6810 | 5101 | 11911
14:30 | 1042 | 6825 | 5090 | 11915
15:00 | 1202 | 6840 | 5079 | 11919
15:30 | 1215 | 6703.5 | 4979 | 11682.5
16:00 | 1228 | 6567 | 4879 | 11446
16:30 | 1270 | 6381 | 4901 | 11282
17:00 | 1312 | 6195 | 4923 | 11118
17:30 | 1299 | 6168.5 | 4897.5 | 11066
18:00 | 1286 | 6142 | 4872 | 11014
18:30 | 1156 | 6393 | 5088 | 11481
19:00 | 1026 | 6644 | 5304 | 11948
19:30 | 964 | 7047 | 5327 | 12374
20:00 | 974 | 6903 | 5223 | 12126 |  |  |  | Executive Engineer
20:30 | 976 | 6963 | 5281 | 12244 |  |  |  | Network Operation Division
21:00 | 978 | 7023 | 5339 | 12362
21:30 | 898 | 7017.5 | 5275.5 | 12293
22:00 | 818 | 7012 | 5212 | 12224 |  |  |  |  | Page 6 of 7
22:30 | 697 | 7026.5 | 5066.5 | 12093
23:00 | 576 | 7041 | 4921 | 11962
23:30 | 474 | 7209.5 | 4986.5 | 12196
24:00 | 372 | 7378 | 5052 | 12430
12374 MW (19:30 )
12249 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-01 |  | Energy |  | 296639475
[15 empty] | 2024-08-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3588 | 914 | 1715 | 0 | 1415 | 4405 | 198 | 0 | 64 | 74 | 0 | 57 | 48
0:30 | 3488.5 | 913.5 | 1775 | 0 | 1606.5 | 4640 | 198 | 0 | 200 | 85 | 0 | 58.5 | 515.825 |  |  | Date: | 44043
1:00 | 3389 | 913 | 1835 | 0 | 1798 | 4875 | 198 | 0 | 336 | 96 | 0 | 60 | 983.65
1:30 | 3367.5 | 913 | 1796.5 | 0 | 1680.5 | 4960 | 198 | 0 | 251 | 94 | 0 | 61.5 | 948.315 | [9 empty] | Total Energy | 296.6395 | 296.6395 | Total Energy Gen 296.639 MKWHr Energy Not Served 7.015 MKWHr Energy Requirement 303.654 MKWHr
2:00 | 3346 | 913 | 1758 | 0 | 1563 | 5045 | 198 | 0 | 166 | 92 | 0 | 63 | 912.98 | [9 empty] | Energy not Served | 7.0149 | 7.0149
2:30 | 3332 | 913 | 1753 | 0 | 1497.5 | 5042.5 | 198.5 | 0 | 136.5 | 93 | 0 | 60 | 810.795 | [9 empty] | Energy Requirement | 303.6544 | 303.6544
3:00 | 3318 | 913 | 1748 | 0 | 1432 | 5040 | 199 | 0 | 107 | 94 | 0 | 57 | 708.61
3:30 | 3326 | 913 | 1748.5 | 0 | 1406.5 | 5007 | 199 | 0 | 85 | 91 | 0 | 33.5 | 683.3025 | [8 empty] | Shortage
4:00 | 3334 | 913 | 1749 | 0 | 1381 | 4974 | 199 | 0 | 63 | 88 | 0 | 10 | 657.995
4:30 | 3355.5 | 913.5 | 1715.5 | 0 | 1362 | 4846.5 | 199.5 | 0 | 63 | 89 | 0 | 22.5 | 628.39
5:00 | 3377 | 914 | 1682 | 0 | 1343 | 4719 | 200 | 0 | 63 | 90 | 0 | 35 | 598.785
5:30 | 3295 | 913.5 | 1621 | 0 | 1342 | 4624.5 | 200 | 0 | 63 | 85 | 6.5 | 38.5 | 550.08
6:00 | 3213 | 913 | 1560 | 0 | 1341 | 4530 | 200 | 0 | 63 | 80 | 13 | 42 | 501.375
6:30 | 3196 | 913 | 1555 | 0 | 1342.5 | 4425.5 | 200 | 0 | 63 | 80 | 40.5 | 45 | 496.1875 | [7 empty] | Coal
7:00 | 3179 | 913 | 1550 | 0 | 1344 | 4321 | 200 | 0 | 63 | 80 | 68 | 48 | 491
7:30 | 3157.5 | 913 | 1544 | 0 | 1259 | 4146.5 | 200 | 0 | 54 | 75 | 90.5 | 53 | 546.8025 | [6 empty] | Oil
8:00 | 3136 | 913 | 1538 | 0 | 1174 | 3972 | 200 | 0 | 45 | 70 | 113 | 58 | 602.605
8:30 | 3272.5 | 915 | 1655.5 | 0 | 1200 | 3949 | 200 | 0 | 53.5 | 66 | 149 | 54.5 | 534.8
9:00 | 3409 | 917 | 1773 | 0 | 1226 | 3926 | 200 | 0 | 62 | 62 | 185 | 51 | 466.995
9:30 | 3421 | 917 | 1765.5 | 0 | 1277.5 | 3966 | 200 | 0 | 70 | 64 | 181.5 | 52.5 | 362.9
10:00 | 3433 | 917 | 1758 | 0 | 1329 | 4006 | 200 | 0 | 78 | 66 | 178 | 54 | 258.805
10:30 | 3362.5 | 917 | 1731.5 | 0 | 1374.5 | 3986 | 199 | 0 | 78 | 67 | 244.5 | 53.5 | 259.2825
11:00 | 3292 | 917 | 1705 | 0 | 1420 | 3966 | 198 | 0 | 78 | 68 | 311 | 53 | 259.76
11:30 | 3365 | 917 | 1748 | 0 | 1439 | 3982 | 198 | 0 | 81.5 | 70 | 286 | 42 | 321.3575
12:00 | 3438 | 917 | 1791 | 0 | 1458 | 3998 | 198 | 0 | 85 | 72 | 261 | 31 | 382.955
12:30 | 3405.5 | 916.5 | 1781 | 0 | 1422.5 | 4009 | 198 | 0 | 89.5 | 75 | 285.5 | 33 | 272.175
13:00 | 3373 | 916 | 1771 | 0 | 1387 | 4020 | 198 | 0 | 94 | 78 | 310 | 35 | 161.395
13:30 | 3373 | 916 | 1771 | 0 | 1387 | 4020 | 198 | 0 | 94 | 78 | 310 | 35 | 161.395
14:00 | 3373 | 916 | 1771 | 0 | 1387 | 4020 | 198 | 0 | 94 | 78 | 310 | 35 | 161.395
14:30 | 3313.5 | 916 | 1704.5 | 0 | 1373.5 | 4128.5 | 196.5 | 0 | 97.5 | 77 | 201 | 42.5 | 80.6975
15:00 | 3254 | 916 | 1638 | 0 | 1360 | 4237 | 195 | 0 | 101 | 76 | 92 | 50 | 0
15:30 | 3287.5 | 916.5 | 1647.5 | 0 | 1180 | 4162.5 | 195 | 0 | 84.5 | 71 | 97.5 | 40.5 | 16.235
16:00 | 3321 | 917 | 1657 | 0 | 1000 | 4088 | 195 | 0 | 68 | 66 | 103 | 31 | 32.47
16:30 | 3263 | 917 | 1638 | 0 | 893 | 4131.5 | 195.5 | 0 | 67.5 | 64 | 75 | 37.5 | 43.4525
17:00 | 3205 | 917 | 1619 | 0 | 786 | 4175 | 196 | 0 | 67 | 62 | 47 | 44 | 54.435
17:30 | 3243 | 917 | 1567.5 | 0 | 768.5 | 4182.5 | 196 | 0 | 65.5 | 61 | 29.5 | 35.5 | 27.2175
18:00 | 3281 | 917 | 1516 | 0 | 751 | 4190 | 196 | 0 | 64 | 60 | 12 | 27 | 0
18:30 | 3256 | 917.5 | 1510 | 0 | 1110.5 | 4222 | 197 | 0 | 178.5 | 62 | 6 | 21.5 | 0
19:00 | 3231 | 918 | 1504 | 0 | 1470 | 4254 | 198 | 0 | 293 | 64 | 0 | 16 | 0
19:30 | 3240 | 917 | 1537 | 0 | 1721 | 4306 | 198 | 0 | 357 | 68 | 0 | 30 | 0
20:00 | 3401 | 917 | 1653 | 0 | 1388 | 4431 | 200 | 0 | 34 | 60 | 0 | 42 | 0
20:30 | 3460 | 917 | 1680 | 0 | 1356.5 | 4493.5 | 200 | 0 | 34 | 67 | 0 | 36 | 0
21:00 | 3519 | 917 | 1707 | 0 | 1325 | 4556 | 200 | 0 | 34 | 74 | 0 | 30 | 0
21:30 | 3510 | 916.5 | 1675.5 | 0 | 1323.5 | 4528 | 200 | 0 | 41 | 74 | 0 | 24.5 | 0
22:00 | 3501 | 916 | 1644 | 0 | 1322 | 4500 | 200 | 0 | 48 | 74 | 0 | 19 | 0
22:30 | 3477.5 | 916.5 | 1677 | 0 | 1281 | 4400.5 | 200 | 0 | 56 | 75 | 0 | 9.5 | 0
23:00 | 3454 | 917 | 1710 | 0 | 1240 | 4301 | 200 | 0 | 64 | 76 | 0 | 0 | 0
23:30 | 3521 | 915.5 | 1712.5 | 0 | 1327.5 | 4353 | 199 | 0 | 64 | 75 | 0 | 28.5 | 24 |  |  | Max Temp. in Dhaka |  | 28.8°C
24:00 | 3588 | 914 | 1715 | 0 | 1415 | 4405 | 198 | 0 | 64 | 74 | 0 | 57 | 48
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 296.639 MKWHr Energy Not Served 7.015 MKWHr Energy Requirement 303.654 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 118 | 118 | 119 | 119 | 120 | 120 | 120 | 120 | 120 | 120 | 118 | 118 | 118 | 118 | 115 | 115 | 116 | 116 |  | 118 | 118 | 120 | 120 | 120 | 120 | 118 | 2823769
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1932000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 3 | 8 | [5 empty] | 11412
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 0 | 2 | 6 | 6 | 10 | 4 |  |  | 0 | 0 | [9 empty] | 27405
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 225 | 225 | 224 | 224 | 224 | 224 | 226 | 223 | 223 | 220 | 222 | 221 | 222 | 223 | 222 | 221 | 221 |  | 216 | 221 | 223 | 223 | 223 | 221 | 227 | 5253778
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [18 empty] | 34 | 34 | 34 | 34 |  |  |  | 117321
12 | Hathazari 100 MW peaking PP | 65 | 16 | [24 empty] | 117360
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [7 empty] | 5 | 17 | 17 | 17 | 17 | 17 | 36 | 399781
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 30 | 30 | 30 | 37 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | [5 empty] | 633936
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 335 | 250 | 250 | 250 | 280 | 280 | 280 | 330 | 335 | 280 | 280 | 280 | 280 | 250 |  | 250 | 250 | 300 | 315 | 315 | 310 | 240 | 7142130
18 | Kodda 300 MW PP Unit-2 (Summit) | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 95 | 95 |  | 99 | 228 | 225 | 225 | 225 | 145 | 146 | 3690873
19 | Ashuganj 195 MW PP (APSCL-United) | [15 empty] | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 66909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 612 | 612 | 612 | 612 | 612 | 580 | 550 | 503 | 550 | 551 | 492 | 495 | 440 | 405 | 402 | 403 | 403 | 383 |  | 363 | 374 | 394 | 442 | 480 | 555 | 585 | 12109089
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 36 | 36 | 36 | 36 | 36 | 36 | 33 | 36 | 37 | 34 | 37 | 20 | 30 | 34 | 34 | 34 | 10 | 34 |  | 34 | 34 | 37 | 37 | 37 | 37 | 37 | 784512
33 | Ashuganj 225 MW CCPP | 212 | 214 | 214 | 215 | 212 | 214 | 188 | 196 | 216 | 200 | 209 | 212 | 216 | 213 | 213 | 213 | 120 | 129 |  | 129 | 142 | 142 | 142 | 144 | 137 | 145 | 4508000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 250 | 310 | 250 | 270 | 305 | 240 | 240 | 240 | 280 | 250 | 250 | 250 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 260 | 6226000
| Ashuganj 450 MW CCPP(North) | 310 | 285 | 285 | 285 | 295 | 285 | 285 | 280 | 280 | 315 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 285 | 280 | 280 | 345 | 280 | 7328600
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 393 | 300 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 300 | 6039000
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 11 |  | 31 | 35 | 38 | 40 | 46 | 47 | 48 | 584640
36 | Chandpur 150 MW CCPP | 50 | 52 | 51 | 51 | 70 | 70 | 50 | 50 | 50 | 50 | 40 | 40 | 35 | 35 | 32 | 33 | 34 | 34 |  | 32 | 33 | 32 | 33 | 39 | 40 | 40 | 1024260
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 404 | 404 | 404 | 404 | 405 | 371 | 332 | 332 | 384 | 404 | 404 | 402 | 404 | 356 | 350 | 350 | 350 | 333 |  | 333 | 333 | 351 | 403 | 403 | 404 | 388 | 9201600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 380 | 340 | 340 | 340 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 420 |  | 420 | 410 | 410 | 390 | 380 | 380 | 380 | 9408500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 31 | 30 | 31 | 30 | 32 | 32 | 31 | 27 | 27 | 11 | 11 | 11 | 11 | 9 | 10 | 11 | 15 | 15 |  | 18 | 19 | 27 | 29 | 30 | 31 | 31 | 481920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 3 | 5 | 9 | 12 | 9 | 7 | 10 | 13 | 19 | 5 | 1 | [8 empty] | 127630
44 | Fenchugonj CCPP Phase-1 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 39 | 40 | 40 | 924000
45 | Fenchugonj CCPP Phase-2 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1379400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 32 | 32 | 31 | [16 empty] | 328416
48 | Shahjibazar 86 MW PP (Shahjibazar) | [11 empty] | 3 | 10 | 10 | 16 | 18 | 27 | 30 |  | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 284160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 133 | 133 | 136 | 137 | 137 | 138 | 137 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3258060
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 2 | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 167552
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 |  |  |  | 4 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 617400
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 245376
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 285 | 280 | 280 | 295 | 275 | 280 | 265 | 305 | 290 | 325 | 310 | 300 | 290 | 275 | 290 | 285 | 275 |  | 270 | 290 | 290 | 285 | 265 | 295 | 290 | 7044000
| Bibiyana South 400 MW | 15 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 50 | 82 | 87 | 112 | 125 | 136 | 147 | 200 | 200 | 305 |  | 345 | 382 | 380 | 386 | 350 | 360 | 380 | 3915800
58 | Nababganj 55 MW PP (Southern power ) | [5 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 524603
59 | Tangail Palli Power Gen 22 MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 7 | 12 | 12 | 0 | 0 |  | 5 | 12 |  |  | 6 | 12 | 14 | 248400
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 96 | 92 | 94 | 88 | 90 | 80 | 80 | 70 | 62 | 66 | 68 | 72 | 78 | 82 | 76 | 66 | 62 | 60 |  | 64 | 68 | 60 | 74 | 74 | 76 | 74 | 1715520
64 | Malancha, Ctg. EPZ (United) | 36 | 37 | 37 | 37 | 37 | 38 | 36 | 12 | 7 | 7 | 0 | 2 | 13 | 2 | 2 | 3 | 10 | 20 |  | 23 | 24 | 28 | 30 | 30 | 30 | 30 | 564000
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 14 | 13 | 14 | 13 | 13 | 13 | 13 | 13 | 10 | 13 |  | 13 | 13 | 13 | 15 | 15 | 18 | 18 | 349220
69 | Summit Ashulia | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 325200
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 3 | 22 |  | 0 |  | 15 | 15 | 15 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 396360
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 582100
72 | Rupganj 33 MW PP(Summit) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 157500
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 22 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 17 |  |  |  | 17 | 17 |  |  |  |  | 52 | 603060
| Chowmuhani 113 MW | 37 | 35 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 28 | 29 | 28 | 29 | 28 | 25 | 9 | 9 |  | 15 | 28 | 28 | 28 | 9 | 9 | 21 | 617400
| Manikgonj 162MW PP(MPGL) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 90 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 72 | 72 | 72 | 72 | 72 | 84 | 1789920
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 186106
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 147350
79 | Kodda 150 MW PP | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 16 | 16 |  | 32 | 16 |  |  | 48 | 64 | 64 | 756480
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 7 | 7 | 7 | 10 | 24 | 24 | 24 | 24 | 8 | 7 | 7 |  | 13 | 24 | 7 | 7 | 7 | 7 | 23 | 349330
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 17 | 17 | 17 |  | 34 | 52 | 52 | 52 | 52 | 35 | 17 | 775882
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 4
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 34 | 34 | 17 | [16 empty] | 1 | 17 | 16 | 17 | 17 | 17 | 24 | 232508
82 | Madanganj 102 PP(Summit) | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 85 | 72 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1504382
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 8 | 13 | 13 | 13 |  |  |  | 35000
86 | Meghnaghat CCPP ( Summit) | 154 | 153 | 155 | 153 | 154 | 120 | 120 | 121 | 153 | 153 | 150 | 152 | 150 | 152 | 152 | 152 | 153 | 120 |  | 120 | 120 | 120 | 155 | 157 | 153 | 154 | 3487971
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 8 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 8 | 8 | 7 | 7 | 8 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 188448
| Meghnaghat 104 MW PP (OPCL) | [12 empty] | 7 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 183360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 25 | 12 | [17 empty] | 8 | [6 empty] | 52800
92 | Fenchuganj 44 MW (Energyprima) | 32 | 36 | 35 | 36 | 36 | 36 | 36 | 33 | 36 | 5 |  |  |  |  | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 410616
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1176466
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 49 | 24 | 24 | 17 | 24 | 24 | 8 | 292244
95 | Patenga 50MW PP (Baraka) | 19 | [16 empty] | 1 |  | 1 | 5 | [5 empty] | 30240
96 | Chattogram 108 MW PP (ECPV) | 27 | 23 | 12 | 12 | 12 | 12 | 12 | 11 | [12 empty] | 0 | [5 empty] | 125088
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 35 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1159991
100 | Manikganj 55 MW PP (Northern) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | [9 empty] | 17 | 498999
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 163 | 163 | 120 | 163 | 163 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 163 | 163 | 120 | 163 | 3473836
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 7150
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 17 | 17 | 17 |  |  | 623088
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 96 | 96 | 97 | 97 | 97 | 97 | 96 | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 124 | 85 | 55 | 55 | 114 | 127 | 127 | 2332800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 72 | 57 | 54 | 53 | 53 | 53 | 55 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 61 | 71 | 71 |  | 77 | 97 | 103 | 136 | 131 | 137 | 141 | 1771056
115 | Juldah 100 MW PP Unit-3 (Acorn) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 357120
116 | Chandpur 200 MW (Desh energy) | 98 | 68 | 68 | 68 | 68 | 68 | 68 | 17 | 17 | 17 | 44 | 121 | 164 | 192 | 190 | 51 | 35 | 17 |  | 42 | 100 | 68 | 68 | 51 | 51 | 62 | 1842240
117 | Ashuganj 150 MW PP (Midland) | 100 | 95 | 108 | 113 | 113 | 115 | 113 | 50 | 50 | 50 | 58 | 58 | 58 | 57 | 58 | 60 | 30 | 30 |  | 75 | 138 | 120 | 50 | 10 |  |  | 1783127
118 | Bibiyana-III 400 MW CCPP | 389 | 347 | 301 | 305 | 310 | 305 | 305 | 333 | 289 | 308 | 391 | 391 | 312 | 290 | 289 | 287 | 289 | 288 |  | 290 | 290 | 288 | 290 | 290 | 270 | 347 | 7938000
| Jamalpur 115 MW PP (United) | 59 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 1513200
| Anwara 300 MW PP (United) | 52 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 6 | 6 | 5 | 5 | 6 |  | 15 | 30 | 30 | 30 | 30 | 30 | 49 | 554760
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  |  | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 361920
| Anlima Energy Ltd. | 35 | 31 | 17 | [16 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 33 | 205419
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 7 | 16 | 17 | 17 | 17 |  | 0 |  | 30 | 30 | 17 | 17 | 17 | 17 | 17 | 403200
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 8 | 12 | 12 | 7 | 15 | 13 | 16 | 2 | 4 | 8 | 1 | 1 | [8 empty] | 95927
| Chandpur 115(Doreen) | 58 | 49 | 44 | 38 | 35 | 33 | 32 | 37 | 48 | 48 | 50 | 50 | 50 | 65 | 68 | 67 | 55 | 34 |  | 44 | 69 | 69 | 68 | 69 | 86 | 89 | 1307520
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 17 |  |  |  | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 390600
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [5 empty] | 10 | 17 | 17 |  |  |  |  | 17 | 17 | [5 empty] | 199054
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 60 | 63 | 57 | 10 | 35 | 42 | 48 | 58 | 51 | 54 | 53 | 31 | 35 | 36 | 50 | 31 | 44 | 27 |  | 16 | 30 | 42 | 30 | 19 | 0 | 57 | 933416
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 1 | 2 | 6 | 4 | 8 | 15 | 22 | 12 | 16 | 13 | 4 | 1 | [8 empty] | 104964
| Matarbari 2*600 MW (CPGCL) | 876 | 877 | 877 | 878 | 879 | 875 | 874 | 877 | 876 | 877 | 878 | 876 | 873 | 959 | 987 | 931 | 931 | 924 |  | 926 | 925 | 926 | 924 | 925 | 930 | 911 | 21803630
120 | Eastern Zone Total | 7407 | 7111 | 7008 | 6922 | 6891 | 6628 | 6574 | 6280 | 6820 | 6886 | 6743 | 6933 | 6867 | 6810 | 6840 | 6567 | 6195 | 6142 |  | 6644 | 7047 | 6903 | 7023 | 7012 | 7041 | 7378 | 165673164
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | 68 | 80 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | [7 empty] | 17 | 21 | [5 empty] | 446400
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 36 | 42 | [5 empty] | 45120
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 52 | 52 | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 10 | [6 empty] | 7 | [5 empty] | 13 | 391344
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 2 | 10 | 19 | 33 | 15 | 10 | 20 | 7 | 28 | 6 | 3 | 1 | [8 empty] | 168480
131 | Rampal 1320 MW (BIFPCL) | 627 | 627 | 625 | 590 | 542 | 512 | 512 | 422 | 466 | 459 | 458 | 465 | 421 | 418 | 417 | 415 | 409 | 380 |  | 383 | 383 | 400 | 492 | 603 | 619 | 618 | 11970910
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | [5 empty] | 2 |  | 150 | 50 | [5 empty] | 433200
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 220 | 180 | 180 | 220 | 5032078
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [7 empty] | 16 | 16 | [5 empty] | 301632
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 270 | 270 | 270 | 234 | 220 | 195 | 170 | 170 | 220 | 220 | 220 | 250 | 250 | 220 | 220 | 220 | 220 | 160 |  | 140 | 140 | 161 | 180 | 180 | 180 | 230 | 5105500
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 915
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 130 | 130 | 80 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 80 | 130 | 130 | 128 | 80 | 63 | 2570000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 9 | 9 | 9 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 3 | 2 | 2 | 0 |  | 0 | 7 | 7 | 0 | 0 | 4 | 7 | 124648
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | [17 empty] | 8 | [6 empty] | 32625
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 16 | 25 | [5 empty] | 37248
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 913 | 913 | 913 | 913 | 914 | 913 | 913 | 913 | 917 | 917 | 917 | 917 | 916 | 916 | 916 | 917 | 917 | 917 |  | 918 | 917 | 917 | 917 | 916 | 917 | 914 | 22080000
147 | Bheramara 410 MW CCPP | 264 | 265 | 264 | 275 | 275 | 277 | 286 | 288 | 291 | 292 | 291 | 290 | 280 | 279 | 279 | 278 | 279 | 279 |  | 230 | 230 | 260 | 291 | 240 | 240 | 307 | 6771744
148 | Payra 1320 MW | 1120 | 1080 | 1080 | 1080 | 1040 | 960 | 940 | 940 | 990 | 1100 | 1100 | 1120 | 1220 | 1244 | 1200 | 1020 | 980 | 900 |  | 880 | 920 | 970 | 1040 | 1020 | 1040 | 1200 | 27496900
149
150 | Barapukuria TPP Unit-1 | 61 | 61 | 62 | 61 | 62 | 62 | 61 | 61 | 62 | 61 | 61 | 62 | 61 | 61 | 61 | 60 | 60 | 61 |  | 60 | 61 | 61 | 63 | 62 | 63 | 62 | 1425164
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 31 | 31 | [17 empty] | 15 | 40 | [5 empty] | 71586
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 9060
| Sirajganj 68 MW Solar Park | [6 empty] | 1 | 8 | 9 | 4 | 10 | 40 | 29 | 13 |  | 2 | 3 | [9 empty] | 104250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 192 | 192 | 191 | 192 | 195 | 160 | 160 | 160 | 160 | 160 | 160 | 176 | 194 | 196 | 196 | 197 | 196 | 186 |  | 140 | 140 | 140 | 154 | 214 | 170 | 206 | 4597273
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 324 | 318 | 320 | 350 | 323 | 310 | 340 | 312 | 346 | 363 | 414 | 388 | 346 | 348 | 342 | 312 | 260 |  | 230 | 241 | 350 | 313 | 312 | 390 | 312 | 8094327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 18 | 12 | [17 empty] | 4 | 5 | [5 empty] | 35939
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  |  | 2 | 5 | 2 | 5 | 2 | 0 | 103626
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 14 | [8 empty] | 35 | 35 | 35 | 35 | 14 | 14 | 14 |  | 14 | [6 empty] | 304190
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 28 | 28 | 28 | [16 empty] | 15 | 27 | [5 empty] | 96897
168 | Santahar 50 MW Peaking PP | 22 | 16 | 16 | [13 empty] | 15 | 12 |  | 18 | 25 | [5 empty] | 98902
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | 60 | [18 empty] | 70 | 90 | [5 empty] | 161328
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | [12 empty] | 619392
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 94 | 109 | 35 | 35 | 35 | 35 | [11 empty] | 815328
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 99 | 98 | 98 | 97 | 97 | 12 |  |  |  |  | 89 | 96 | 71 | 70 | 70 | 70 | 49 | 1936992
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 4 | 3 | 4 | 5 | 2 | 8 | 7 | 6 | [11 empty] | 39008
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 |  |  |  |  | 36 | 86 | 52 | 52 | 52 | 52 | 52 | 832704
| Intraco Solar 30 MW | [5 empty] | 1 | 6 | 3 | 10 | 7 | 27 | 37 | 36 |  |  | 6 | 3 | 1 |  | 0 | [6 empty] | 147385
| Adani Power Jharkhanda Ltd | 1309 | 1518 | 1514 | 1519 | 1364 | 1346 | 1214 | 999 | 762 | 738 | 757 | 730 | 755 | 759 | 950 | 1039 | 1172 | 1382 |  | 1502 | 1503 | 1519 | 1415 | 1230 | 914 | 799 | 27431526
178 | Teesta Solar Limited | [5 empty] | 9 | 47 | 68 | 119 | 104 | 210 | 119 | 165 | 19 | 25 | 49 | 28 | 7 | [8 empty] | 1032690