## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-04 | Sunday
|  | Date (day): | 2024-08-04 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13489.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15695 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-03 | 2024-08-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 390 | 409 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 7 | 7 | 8 | 8 | 92 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 154 | 152 | 150 | 152 | 183 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 14 | 65 | 50 | 70 |  | 32 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 20 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 8 | 9 | 91 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 32 | 20 | 180 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 48 | 8 | 48 | 54 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 140 | 64 | 149 |  |  | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 30 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 36 | 35 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 24 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 6 | 6 | 10 | 10 |  | 23 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 64 | 262 | 145 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 71 | 149 | 149 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 17 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 24 | 52 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1614 | 2266 | 2006 | 2603 | 2626 | 926
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 12 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 161 | 202 | 200 | 202 | 28 |  | Low water lavel
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 221 | 220 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 51 | 68 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 58 | 16 | 72 | 26 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 51 | 80 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 18 | 25 | 25 | 75 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 24 | 12 | 24 | 76 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 17 | 25 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 25 | 30 | 78 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 50 | 50 | 250 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 1 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 51 | 85 | 25 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 25 | 25 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 28 | 17 | 53 | 63 |  | Fuel shortage
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 84 | 17 | 163
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 340 | 340 | 320 | 320 |  | 612 | Unit-1 under maint.
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 9 | 16 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 812 | 720 | 930 | 850
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1564 | 1917 | 2155 | 2520 | 884 | 964
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 142 | 125 | 200 | 210 |  | 75 | ST Under maint.
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 300 | 300 | 60 |  | FGMO
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 280 | 300 | 300 |  |  | FGMO
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 280 | 230 | 300 | 300 | 100 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 30 | 30 | 30 | 15 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 0 | 10 | 10 | 10 | 45 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 40 | 55 | 138 |  | 12 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 33 | 33 | 35 |  | 17 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 40 | 50 | 50 | 113 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 62 | 51 | 70 | 100 | 100 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 62 | 80 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 42 | 42 | 42 |  | 10 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 9 | 17 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 21 | 88 | 34 | 88 |  | 26 | Engine problem
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 58 | 28 | 60 | 53 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 68 | 50 | 68 | 47 |  | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 6 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2950 | 1333 | 1515 | 1723 | 1892 | 728 | 188
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 27 | 32 | 30 | 35 | 167 |  | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 93 | 122 | 100 | 124 | 76 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 79 | 68 | 79 | 36 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 10 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 |  | 10 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 1 | 17 | 17 | 17
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 204 | 262 | 278.6 | 267 | 167 | 10
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 10 | 10 | 10 | 10 | 76 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 137 | 136 | 137 |  | 94 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 346 | 340 | 360 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 345 | 350 | 350 | 380 |  | 3 | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1421 | 1416 | 1417 | 1468 | 263 | 505
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 916 | 912 | 918 | 918
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 32 | 32 | 64 |  | 51 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 31 | 0 | 55 |  | 54 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 341 | 307 | 300 | 300 | 110 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 16 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 85 |  | 20 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 22 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 508 | 586 | 500 | 620 | 614 |  | Unit-2 S/D due to Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1787 | 1918 | 1913 | 2098 | 1435 | 139
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 16 | 64 | 46 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 9 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | GT-1 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1200 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 20 | 17 | 90 | 60 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 280 | 307 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1571 | 1853 | 1578 | 2000 | 106 | 129
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 173 | 194 | 160 | 180 | 30 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 389 | 390 | 380 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 75 | 50 | 85 |  | 19 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 70 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 90 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1170 | 1070 | 1200 | 1480
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 61 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1797 | 1948 | 2046 | 2561 | 693 | 108
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 64 | 65 | 64 | 65 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 95 | 106 | 106
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 1 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 5 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 75 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 146 | 275 | 373 | 286 | 40 | 384
| Total |  |  |  |  | 28098 | 26947 | 11437 | 13370 | 13489.6 | 15695 | 6942 | 3353
A. |  | 2024-08-03 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 13370 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 9444 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13370 | MW
3 | Day peak Generation : |  |  | 11437 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12845.92 | MW
4 | Evening peak Generation : |  |  | 13370 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 276.0601 | MKWHr | By Solar | 1.3624 | MKWHr
| By Gas : | 121.24 | MKWHr |  | By Oil: | 27.5919 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 96.477 | MKWHr |  | By Hydro: | 4.8117 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.564 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6942 | MW | Dhaka | 4682.42 | 4682.42 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3353 | MW | Chittagong | 1365.5 | 1365.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 10295 | MW | Khulna | 1580.6 | 1580.6 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 893.05 | MMCFD |  |  | Rajshahi | 1220.8 | 1220.8 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 360494047.09 | ii) Oil : | Taka | 506751136.39 | Comilla | 1196 | 1196 |  | 0 |  | 21:00 |  | 102
|  | iii) Coal : | Taka | 642714613.31 | Total | Taka | 1509959796.79 | Mymensingh | 1056 | 1056 |  | 0 |  | 22:00 |  | 114.6
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 8924.85 | MKWHr. | Sylhet | 547 | 547 |  | 0 |  | 23:00 |  | 150.89
| ii) During Peak Demand : |  |  | 910 | MW (W to E) at | 19:30 | hrs | Barisal | 400.6 | 400.6 |  | 0 |  | 24:00 |  | 148.025
| iii) Maximum : |  |  | 434 | MW at | 24:00 | hrs | Rangpur | 797 | 797 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.0°C |  |  | Total | 12845.92 | 12845.92 |  | 0
B. |  | 2024-08-04 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 31.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15695 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12800 | MW
4 | Reserve(Generation end) |  |  |  |  | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 305.5863 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10539 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.3273 | MKWHr. | ii) HVDC Flow at Peak Time |  | 912 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.6858 | MKWHr. | iii) Maximum HVDC Flow : |  | 916 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.93 |  | (b) Today: | 94.91 |  | (c) Rule Curve: |  | 89.64

## YesterdayGen
2024-08-03 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 154 | 0 | 0 | 15 | 0 | 0 | 40 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 145 | 0 | 50 | 31 | 5 | 0 | 51 | 0 | 0 | 14 | 0 | 0 | 0 | 18 | 74 | 48 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 62 | 0 | 0 | 85 | 0 | 349 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 33 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 82 | 17 | 295 | 0 | 0 | 340 | 27 | 1082 | 0 | 0 | 0 |  | 913 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 1110 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 280 | 907 | 0 | 0 | 0 | 0 |  | 6302 | 5036 | 11338 | 3452 | 913 | 1694 | 0 | 576 | 4338 | 200 | 0 | 64 | 74 | 0 | 27 | 0 | 93.68
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 153 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 143 | 0 | 50 | 31 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 74 | 47 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 53 | 0 | 0 | 68 | 0 | 352 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 28 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 64 | 17 | 295 | 0 | 0 | 340 | 29 | 934 | 0 | 0 | 0 |  | 913 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 226 | 1047 | 0 | 0 | 0 | 0 |  | 6007 | 4886 | 10893 | 3457 | 913 | 1730 | 0 | 453 | 4021 | 200 | 0 | 16 | 74 | 0 | 29 | 0 | 93.73
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 154 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 144 | 0 | 50 | 31 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 68 | 47 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 65 | 0 | 53 | 0 | 0 | 68 | 0 | 349 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 29 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 17 | 285 | 0 | 0 | 340 | 18 | 908 | 0 | 0 | 0 |  | 914 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 185 | 1235 | 0 | 0 | 0 | 0 |  | 5753 | 4813 | 10566 | 3376 | 914 | 1597 | 0 | 364 | 4013 | 200 | 0 | 16 | 68 | 0 | 18 | 0 | 93.78
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 152 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 144 | 0 | 51 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 68 | 48 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 53 | 0 | 0 | 51 | 0 | 349 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 17 | 285 | 0 | 0 | 340 | 19 | 809 | 0 | 0 | 0 |  | 913 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 160 | 954 | 0 | 0 | 0 | 0 |  | 5631 | 4517 | 10148 | 3379 | 913 | 1645 | 0 | 309 | 3599 | 200 | 0 | 16 | 68 | 0 | 19 | 0 | 93.83
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 153 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 144 | 0 | 51 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 68 | 48 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 53 | 0 | 0 | 51 | 0 | 349 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 17 | 285 | 0 | 0 | 340 | 19 | 810 | 0 | 0 | 0 |  | 913 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 160 | 923 | 0 | 0 | 0 | 0 |  | 5621 | 4478 | 10099 | 3378 | 913 | 1617 | 0 | 308 | 3580 | 200 | 0 | 16 | 68 | 0 | 19 | 0 | 93.88
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 153 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 240 | 142 | 0 | 70 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 62 | 48 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 0 | 0 | 51 | 0 | 299 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 17 | 290 | 0 | 0 | 340 | 29 | 812 | 0 | 0 | 1 |  | 914 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 140 | 811 | 0 | 0 | 0 | 0 |  | 5448 | 3996 | 9444 | 3227 | 914 | 1528 | 0 | 224 | 3243 | 200 | 0 | 16 | 62 | 1 | 29 | 0 | 93.93
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 154 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 24 | 15 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 200 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 315 | 345 | 142 | 0 | 70 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 62 | 48 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 17 | 0 | 330 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 33 | 17 | 315 | 0 | 0 | 340 | 27 | 813 | 0 | 0 | 7 |  | 913 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 220 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 363 | 1 | 140 | 824 | 6 | 0 | 0 | 0 |  | 5637 | 4031 | 9668 | 3456 | 913 | 1560 | 0 | 145 | 3264 | 200 | 0 | 16 | 62 | 25 | 27 | 0 | 93.98
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 153 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 13 | 0 | 0 | 121 | 80 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 325 | 340 | 140 | 0 | 50 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 60 | 44 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 17 | 0 | 352 | 8 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 28 | 0 | 340 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 33 | 17 | 325 | 0 | 0 | 341 | 30 | 814 | 0 | 0 | 22 |  | 913 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 720 | 220 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 365 | 1 | 170 | 826 | 2 | 0 | 0 | 3 |  | 5741 | 4187 | 9928 | 3514 | 913 | 1686 | 0 | 145 | 3300 | 201 | 0 | 16 | 60 | 63 | 30 | 0 | 94.02
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 150 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 24 | 12 | 2 | 0 | 128 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 290 | 280 | 141 | 0 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 18 | 62 | 30 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 0 | 0 | 0 | 30 | 0 | 19 | 6 | 0 | 24 | 0 | 354 | 56 | 17 | 0 | 2 | 0 | 0 | 0 | 17 | 28 | 0 | 340 | 0 | 1 | 0 | 0 | 0 | 0 | 5 | 46 | 17 | 250 | 0 | 0 | 340 | 12 | 814 | 0 | 0 | 25 |  | 913 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 870 | 220 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 448 | 1 | 220 | 1005 | 3 | 0 | 0 | 6 |  | 5695 | 4777 | 10472 | 3429 | 913 | 1663 | 0 | 258 | 3761 | 208 | 0 | 64 | 62 | 102 | 12 | 0 | 94.06
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 155 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 12 | 8 | 0 | 127 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 142 | 0 | 50 | 10 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 52 | 31 | 0 | 0 | 1 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 93 | 0 | 61 | 0 | 0 | 51 | 0 | 348 | 56 | 34 | 0 | 3 | 0 | 0 | 0 | 17 | 29 | 0 | 342 | 7 | 14 | 0 | 0 | 0 | 0 | 11 | 49 | 17 | 250 | 0 | 0 | 342 | 19 | 812 | 0 | 0 | 6 |  | 915 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 960 | 220 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 504 | 1 | 280 | 1010 | 15 | 0 | 0 | 17 |  | 5815 | 4958 | 10773 | 3332 | 915 | 1661 | 0 | 443 | 3972 | 207 | 0 | 64 | 52 | 108 | 19 | 0 | 94.1
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 |  | 0 | 450 | 154 | 1 | 0 | 15 | 0 | 0 | 0 | 7 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 127 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 270 | 141 | 0 | 45 | 10 | 0 | 0 | 25 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 58 | 26 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 25 | 0 | 0 | 93 | 0 | 71 | 15 | 0 | 51 | 0 | 350 | 59 | 52 | 0 | 0 | 0 | 0 | 0 | 17 | 29 | 0 | 342 | 17 | 14 | 17 | 0 | 0 | 0 | 19 | 49 | 17 | 250 | 0 | 0 | 342 | 11 | 810 | 0 | 0 | 9 |  | 915 | 0 | 349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 960 | 220 | 0 | 0 | 1 | 23 | 0 | 0 | 0 | 508 | 5 | 280 | 1157 | 8 | 0 | 0 | 20 |  | 5895 | 5058 | 10953 | 3201 | 915 | 1648 | 0 | 611 | 4121 | 207 | 0 | 64 | 58 | 117 | 11 | 0 | 94.14
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 |  | 0 | 450 | 154 | 7 | 14 | 20 | 32 | 0 | 0 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 81 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 270 | 142 | 0 | 45 | 20 | 0 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 62 | 27 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 64 | 0 | 0 | 93 | 0 | 71 | 12 | 0 | 62 | 0 | 350 | 59 | 52 | 0 | 2 | 0 | 0 | 0 | 21 | 28 | 0 | 345 | 24 | 10 | 54 | 0 | 0 | 1 | 20 | 49 | 17 | 280 | 0 | 0 | 340 | 9 | 812 | 0 | 0 | 6 |  | 916 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1000 | 220 | 0 | 0 | 2 | 22 | 1 | 0 | 0 | 508 | 5 | 280 | 1170 | 75 | 0 | 0 | 61 |  | 6136 | 5301 | 11437 | 3311 | 916 | 1742 | 0 | 780 | 4174 | 161 | 0 | 64 | 62 | 218 | 9 | 50 | 94.18
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 152 | 7 | 42 | 40 | 62 | 0 | 0 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 15 | 55 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 80 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 280 | 270 | 143 | 0 | 43 | 20 | 0 | 0 | 43 | 0 | 0 | 30 | 0 | 0 | 0 | 11 | 66 | 27 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 285 | 12 | 8 | 0 | 130 | 0 | 0 | 95 | 0 | 71 | 14 | 0 | 115 | 0 | 334 | 59 | 52 | 0 | 3 | 0 | 0 | 0 | 34 | 28 | 0 | 345 | 30 | 18 | 108 | 0 | 0 | 17 | 6 | 62 | 20 | 280 | 0 | 0 | 340 | 14 | 812 | 0 | 0 | 63 |  | 913 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1080 | 220 | 0 | 0 | 4 | 24 | 35 | 0 | 0 | 508 | 2 | 280 | 1174 | 62 | 0 | 0 | 65 |  | 6517 | 5312 | 11829 | 3319 | 913 | 1654 | 0 | 1117 | 4258 | 160 | 0 | 64 | 66 | 264 | 14 | 77 | 94.21
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 152 | 7 | 42 | 40 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 29 | 55 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 270 | 145 | 0 | 40 | 20 | 0 | 0 | 43 | 0 | 20 | 41 | 0 | 0 | 0 | 6 | 92 | 27 | 0 | 0 | 1 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 145 | 0 | 0 | 65 | 0 | 78 | 13 | 0 | 115 | 0 | 300 | 59 | 52 | 0 | 3 | 0 | 0 | 0 | 51 | 28 | 0 | 310 | 28 | 21 | 108 | 0 | 0 | 17 | 10 | 63 | 23 | 250 | 0 | 0 | 342 | 31 | 808 | 0 | 0 | 50 |  | 912 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1040 | 180 | 0 | 0 | 0 | 45 | 35 | 0 | 0 | 490 | 1 | 245 | 1178 | 60 | 0 | 0 | 2 |  | 6337 | 5192 | 11529 | 3136 | 912 | 1580 | 0 | 1153 | 4167 | 199 | 0 | 52 | 92 | 207 | 31 | 0 | 94.14
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 155 | 8 | 58 | 42 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 280 | 270 | 145 | 0 | 40 | 20 | 2 | 0 | 43 | 0 | 22 | 41 | 0 | 0 | 0 | 6 | 82 | 27 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 145 | 0 | 0 | 65 | 0 | 88 | 10 | 0 | 45 | 0 | 302 | 58 | 34 | 0 | 4 | 0 | 0 | 0 | 52 | 30 | 0 | 320 | 30 | 22 | 108 | 0 | 0 | 17 | 7 | 66 | 27 | 250 | 0 | 0 | 340 | 29 | 809 | 0 | 0 | 25 |  | 913 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1020 | 180 | 0 | 0 | 0 | 20 | 35 | 0 | 0 | 462 | 4 | 220 | 1175 | 69 | 0 | 0 | 1 |  | 6294 | 5083 | 11377 | 3150 | 913 | 1586 | 0 | 1111 | 4089 | 198 | 0 | 54 | 82 | 165 | 29 | 0 | 94.27
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 400 | 154 | 7 | 52 | 55 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 295 | 285 | 142 | 0 | 40 | 27 | 10 | 0 | 43 | 0 | 29 | 24 | 0 | 0 | 0 | 8 | 78 | 26 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 285 | 8 | 8 | 0 | 153 | 0 | 0 | 65 | 0 | 108 | 7 | 0 | 17 | 0 | 309 | 58 | 17 | 0 | 1 | 0 | 0 | 0 | 38 | 38 | 0 | 332 | 30 | 0 | 72 | 0 | 0 | 17 | 3 | 69 | 22 | 250 | 0 | 0 | 340 | 20 | 710 | 0 | 0 | 25 |  | 912 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1020 | 180 | 0 | 0 | 0 | 14 | 35 | 0 | 0 | 464 | 7 | 220 | 1177 | 36 | 0 | 0 | 3 |  | 6136 | 5032 | 11168 | 3203 | 912 | 1561 | 0 | 1058 | 3994 | 199 | 0 | 45 | 78 | 98 | 20 | 0 | 94.3
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 400 | 154 | 7 | 34 | 55 | 155 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 270 | 144 | 0 | 40 | 28 | 10 | 0 | 43 | 0 | 33 | 24 | 0 | 0 | 0 | 9 | 64 | 28 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 160 | 0 | 0 | 65 | 0 | 115 | 4 | 0 | 21 | 0 | 300 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 36 | 0 | 330 | 30 | 1 | 72 | 0 | 0 | 17 | 3 | 68 | 15 | 250 | 0 | 0 | 340 | 25 | 606 | 0 | 0 | 18 |  | 913 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1020 | 180 | 0 | 0 | 0 | 6 | 35 | 0 | 0 | 463 | 7 | 220 | 1274 | 1 | 0 | 0 | 1 |  | 6144 | 5090 | 11234 | 3336 | 913 | 1582 | 0 | 1036 | 3987 | 199 | 0 | 49 | 64 | 43 | 25 | 0 | 94.33
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 350 | 155 | 7 | 34 | 55 | 168 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 295 | 285 | 140 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 33 | 24 | 0 | 0 | 0 | 9 | 70 | 28 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 160 | 0 | 0 | 75 | 0 | 132 | 0 | 0 | 17 | 0 | 313 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 36 | 0 | 330 | 45 | 1 | 72 | 0 | 0 | 17 | 1 | 68 | 17 | 250 | 0 | 0 | 342 | 30 | 618 | 0 | 0 | 1 |  | 912 | 0 | 324 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 940 | 180 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 414 | 1 | 220 | 1177 | 8 | 0 | 0 | 1 |  | 6154 | 4857 | 11011 | 3344 | 912 | 1528 | 0 | 1089 | 3775 | 199 | 0 | 49 | 70 | 15 | 30 | 0 | 94.37
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 154 | 7 | 37 | 55 | 140 | 0 | 0 | 9 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 12 | 50 | 65 | 6 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 280 | 285 | 110 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 33 | 33 | 0 | 0 | 0 | 15 | 80 | 28 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 180 | 0 | 0 | 133 | 0 | 149 | 0 | 24 | 27 | 7 | 400 | 78 | 52 | 13 | 0 | 15 | 0 | 4 | 81 | 45 | 25 | 375 | 52 | 0 | 144 | 9 | 0 | 17 | 0 | 68 | 17 | 250 | 59 | 0 | 340 | 9 | 633 | 0 | 0 | 0 |  | 912 | 0 | 274 | 0 | 31 | 0 | 0 | 0 | 29 | 21 | 0 | 65 | 8 | 16 | 0 | 0 | 0 | 40 | 0 | 42 | 0 | 0 | 10 | 0 | 22 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 14 | 0 | 95 | 0 | 0 | 35 | 970 | 220 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 502 | 0 | 252 | 1136 | 0 | 0 | 0 | 0 |  | 7099 | 5403 | 12502 | 3389 | 912 | 1710 | 0 | 1800 | 3897 | 202 | 0 | 503 | 80 | 0 | 9 | 0 | 94.49
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 152 | 7 | 65 | 55 | 20 | 0 | 0 | 9 | 48 | 140 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 12 | 58 | 68 | 18 | 12 | 0 | 0 | 17 | 0 | 0 | 0 | 280 | 280 | 125 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 33 | 42 | 0 | 0 | 0 | 17 | 80 | 32 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 262 | 0 | 0 | 122 | 0 | 149 | 0 | 24 | 51 | 40 | 346 | 79 | 52 | 51 | 0 | 16 | 1 | 17 | 88 | 58 | 25 | 350 | 52 | 0 | 162 | 28 | 0 | 17 | 0 | 68 | 17 | 230 | 84 | 0 | 340 | 16 | 720 | 0 | 0 | 0 |  | 912 | 0 | 307 | 0 | 32 | 0 | 0 | 0 | 34 | 31 | 16 | 65 | 9 | 32 | 0 | 0 | 0 | 40 | 0 | 75 | 0 | 0 | 15 | 0 | 22 | 0 | 0 | 2 | 65 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 50 | 0 | 95 | 0 | 0 | 90 | 1200 | 220 | 0 | 20 | 0 | 0 | 115 | 0 | 0 | 586 | 0 | 307 | 1070 | 0 | 0 | 0 | 0 |  | 7376 | 5994 | 13370 | 3264 | 912 | 1759 | 0 | 2249 | 4288 | 202 | 0 | 600 | 80 | 0 | 16 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 153 | 7 | 65 | 55 | 24 | 0 | 0 | 9 | 48 | 145 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 12 | 62 | 68 | 25 | 10 | 0 | 0 | 22 | 0 | 0 | 0 | 280 | 280 | 125 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 33 | 42 | 0 | 0 | 0 | 18 | 80 | 32 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 263 | 0 | 0 | 124 | 0 | 149 | 0 | 24 | 51 | 35 | 348 | 78 | 52 | 51 | 0 | 16 | 18 | 26 | 88 | 59 | 25 | 350 | 52 | 0 | 162 | 31 | 0 | 17 | 0 | 68 | 17 | 230 | 90 | 0 | 340 | 24 | 719 | 0 | 0 | 0 |  | 913 | 0 | 274 | 0 | 57 | 0 | 0 | 0 | 30 | 40 | 16 | 65 | 9 | 32 | 0 | 0 | 0 | 40 | 0 | 87 | 0 | 0 | 22 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 47 | 0 | 97 | 0 | 0 | 106 | 1200 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 623 | 0 | 307 | 759 | 0 | 0 | 0 | 0 |  | 7393 | 5692 | 13085 | 3221 | 913 | 1639 | 0 | 2355 | 4012 | 202 | 0 | 639 | 80 | 0 | 24 | 0 | 94.45
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 153 | 7 | 65 | 55 | 221 | 0 | 0 | 9 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 122 | 80 | 0 | 0 | 3 | 223 | 0 | 0 | 0 |  | 12 | 72 | 36 | 25 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 250 | 144 | 0 | 40 | 30 | 8 | 0 | 43 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 80 | 33 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 283 | 0 | 0 | 127 | 0 | 149 | 0 | 24 | 51 | 10 | 349 | 78 | 52 | 68 | 0 | 32 | 0 | 34 | 88 | 63 | 25 | 350 | 52 | 0 | 108 | 53 | 0 | 17 | 0 | 67 | 17 | 230 | 54 | 0 | 340 | 19 | 720 | 0 | 0 | 0 |  | 912 | 0 | 312 | 0 | 81 | 0 | 0 | 0 | 30 | 55 | 16 | 65 | 10 | 48 | 0 | 0 | 0 | 40 | 0 | 42 | 0 | 0 | 46 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 50 | 1244 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 757 | 0 | 0 | 0 | 0 |  | 7473 | 5690 | 13163 | 3416 | 912 | 1727 | 0 | 2225 | 4053 | 202 | 0 | 529 | 80 | 0 | 19 | 102 | 94.49
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 153 | 7 | 68 | 55 | 221 | 0 | 0 | 9 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 122 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 64 | 34 | 25 | 12 | 0 | 0 | 30 | 0 | 0 | 0 | 280 | 250 | 144 | 0 | 40 | 30 | 5 | 0 | 43 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 78 | 33 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 291 | 0 | 0 | 127 | 0 | 149 | 0 | 24 | 51 | 10 | 347 | 78 | 52 | 68 | 0 | 98 | 0 | 34 | 70 | 58 | 25 | 350 | 51 | 0 | 54 | 53 | 0 | 6 | 0 | 68 | 34 | 230 | 54 | 0 | 340 | 31 | 860 | 0 | 0 | 0 |  | 842 | 0 | 311 | 0 | 81 | 0 | 0 | 0 | 29 | 41 | 24 | 65 | 10 | 64 | 0 | 0 | 0 | 40 | 0 | 42 | 0 | 0 | 42 | 0 | 22 | 0 | 0 | 5 | 65 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 623 | 0 | 307 | 754 | 0 | 0 | 0 | 0 |  | 7602 | 5558 | 13160 | 3438 | 842 | 1731 | 0 | 2145 | 4193 | 202 | 0 | 500 | 78 | 0 | 31 | 114.6 | 94.53
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 153 | 7 | 68 | 55 | 220 | 0 | 0 | 9 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 14 | 23 | 24 | 6 | 8 | 0 | 123 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 64 | 34 | 25 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 240 | 143 | 0 | 45 | 30 | 5 | 0 | 43 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 78 | 34 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 280 | 0 | 0 | 127 | 0 | 149 | 0 | 24 | 51 | 10 | 288 | 78 | 35 | 68 | 0 | 165 | 0 | 34 | 70 | 50 | 25 | 326 | 42 | 0 | 54 | 53 | 0 | 17 | 0 | 67 | 29 | 230 | 17 | 0 | 341 | 51 | 929 | 0 | 0 | 0 |  | 841 | 0 | 313 | 0 | 80 | 0 | 0 | 0 | 20 | 41 | 24 | 65 | 10 | 80 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 42 | 0 | 22 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 72 | 0 | 0 | 622 | 0 | 250 | 753 | 0 | 0 | 0 | 0 |  | 7548 | 5434 | 12982 | 3371 | 841 | 1634 | 0 | 2189 | 4203 | 203 | 0 | 412 | 78 | 0 | 51 | 150.89 | 94.57
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 153 | 7 | 70 | 55 | 220 | 0 | 0 | 9 | 48 | 117 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 14 | 23 | 24 | 6 | 8 | 0 | 123 | 80 | 0 | 0 | 8 | 222 | 0 | 0 | 0 |  | 12 | 40 | 0 | 25 | 12 | 0 | 0 | 36 | 0 | 0 | 0 | 280 | 240 | 144 | 0 | 45 | 30 | 5 | 0 | 43 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 84 | 34 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 278 | 0 | 0 | 127 | 0 | 149 | 0 | 24 | 51 | 10 | 289 | 78 | 17 | 68 | 0 | 200 | 0 | 34 | 70 | 30 | 25 | 326 | 17 | 0 | 54 | 38 | 0 | 17 | 0 | 66 | 17 | 230 | 54 | 0 | 340 | 46 | 926 | 0 | 0 | 0 |  | 841 | 0 | 308 | 0 | 80 | 0 | 0 | 0 | 10 | 36 | 24 | 65 | 10 | 96 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 35 | 0 | 18 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1244 | 220 | 0 | 17 | 0 | 0 | 72 | 0 | 0 | 618 | 0 | 250 | 751 | 0 | 0 | 0 | 0 |  | 7464 | 5401 | 12865 | 3389 | 841 | 1610 | 0 | 2149 | 4193 | 203 | 0 | 350 | 84 | 0 | 46 | 148.025 | 94.61
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9640800 | 0 |  | 0 | 9709000 | 3673978 | 102720 | 596359 | 677247 | 1364528 | 0 | 696000 | 105600 | 347040 | 1477920 | 0 | 0 | 0 | 0 | 574200 | 673017 | 495971 | 0 | 351000 | 534600 | 611300 | 230700 | 131520 | 0 | 2879700 | 1932000 | 0 | 0 | 27910 | 5135694 | 0 | 0 | 0 |  | 199200 | 317520 | 222582 | 105120 | 60480 | 7200 | 0 | 615840 | 0 | 0 | 0 | 7292000 | 6488000 | 3460000 | 0 | 1102380 | 628128 | 92160 | 0 | 714360 | 0 | 176176 | 524424 | 0 | 0 | 0 | 337460 | 1685760 | 816000 | 0 | 0 | 5900 | 941000 | 1381800 | 0 | 0 | 3451255 | 0 | 0 | 256320 | 0 | 3280240 | 0 | 0 | 0 | 7173000 | 275424 | 180528 | 0 | 2599418 | 0 | 0 | 1896000 | 0 | 2085408 | 76950 | 133440 | 1288320 | 130472 | 8377000 | 1368000 | 613978 | 352109 | 19633 | 406473 | 37594 | 173963 | 941640 | 861840 | 138240 | 8222900 | 500160 | 101660 | 1140480 | 243382 | 0 | 250880 | 86730 | 1400640 | 482040 | 6466200 | 297745 | 0 | 8209090 | 564000 | 19490909 | 0 | 0 | 247355 |  | 22327272 | 0 | 7784928 | 0 | 365760 | 0 | 0 | 0 | 138720 | 201856 | 93375 | 1543000 | 179507 | 279744 | 0 | 0 | 0 | 211280 | 0 | 174128 | 0 | 0 | 144636 | 0 | 116637 | 0 | 0 | 97650 | 1475345 | 0 | 0 | 0 | 0 | 4441091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8301745 | 4800 | 0 | 105024 | 0 | 501004 | 0 | 16315 | 165504 | 26195700 | 5392500 | 0 | 117600 | 10440 | 271440 | 807360 | 0 | 0 | 11600000 | 40227 | 5672700 | 23833296 | 324000 | 0 | 1270 | 160500 |  | 152963710 | 123096354 | 276060064 | 81680351 | 22327272 | 39559665 | 0 | 24112656 | 96477040 | 4811700 | 0 | 3479200 | 1685760 | 1362420 | 564000 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27765504 | 0 |  | 0 | 30874620 | 12565004.76 | 2029747.2 | 11151913.3 | 11933092.14 | 4161810.4 | 0 | 3723600 | 2086656 | 6229368 | 28701206.4 | 0 | 0 | 0 | 0 | 10484892 | 10606747.92 | 9071309.59 | 0 | 263250 | 0 | 0 | 0 | 2355523.2 | 0 | 0 | 0 | 0 | 0 | 528615.4 | 16382863.86 | 0 | 0 | 0 |  | 3503928 | 5591527.2 | 3986443.62 | 2003587.2 | 1183593.6 | 118512 | 0 | 0 | 0 | 0 | 0 | 20344680 | 19853280 | 11487200 | 0 | 3560687.4 | 2116791.36 | 403660.8 | 0 | 2864583.6 | 0 | 3155312.16 | 9471097.44 | 0 | 0 | 0 | 253095 | 11058585.6 | 2537760 | 0 | 0 | 0 | 3669900 | 5154114 | 0 | 0 | 11803292.1 | 0 | 0 | 1337990.4 | 0 | 9151869.6 | 0 | 0 | 0 | 22164570 | 206568 | 137201.28 | 0 | 53028127.2 | 0 | 0 | 36422160 | 0 | 36724034.88 | 0 | 2376566.4 | 22352352 | 2163225.76 | 22199050 | 26074080 | 11518227.28 | 6316835.46 | 0 | 6645833.55 | 730827.36 | 3120896.22 | 17994740.4 | 16728314.4 | 2462054.4 | 21872914 | 8537731.2 | 0 | 20859379.2 | 4083949.96 | 0 | 4483225.6 | 0 | 25239532.8 | 8165757.6 | 19204614 | 4192249.6 | 0 | 57217357.3 | 0 | 114996363.1 | 0 | 0 | 0 |  | 62739634.32 | 0 | 22965537.6 | 0 | 6345936 | 0 | 0 | 0 | 2609323.2 | 3796911.36 | 1662075 | 4875880 | 850863.18 | 4822786.56 | 0 | 0 | 0 | 3784024.8 | 0 | 2927091.68 | 0 | 0 | 2590430.76 | 0 | 2088968.67 | 0 | 0 | 73921.05 | 16273055.35 | 0 | 0 | 0 | 0 | 14655600.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24241095.4 | 81984 | 0 | 2081575.68 | 0 | 9979999.68 | 0 | 0 | 3283599.36 | 169748136 | 16770675 | 0 | 2275560 | 0 | 0 | 14007696 | 0 | 0 | 84680000 | 0 | 42261615 | 157538086.56 | 0 | 0 | 0 | 0 |  | 903745954.2 | 680012062.51 | 1583758016.71 | 236617691.85 | 62739634.32 | 123876355.24 | 0 | 443327646.94 | 642714613.31 | 0 | 0 | 63423489.45 | 11058585.6 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 |  | 0 | 450 | 154 | 7 | 14 | 20 | 32 | 0 | 0 | 9 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 55 | 35 | 0 | 14 | 22 | 24 | 6 | 8 | 0 | 81 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 270 | 142 | 0 | 45 | 20 | 0 | 0 | 43 | 0 | 0 | 16 | 0 | 0 | 0 | 9 | 62 | 27 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 64 | 0 | 0 | 93 | 0 | 71 | 12 | 0 | 62 | 0 | 350 | 59 | 52 | 0 | 2 | 0 | 0 | 0 | 21 | 28 | 0 | 345 | 24 | 10 | 54 | 0 | 0 | 1 | 20 | 49 | 17 | 280 | 0 | 0 | 340 | 9 | 812 | 0 | 0 | 6 |  | 916 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 64 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1000 | 220 | 0 | 0 | 2 | 22 | 1 | 0 | 0 | 508 | 5 | 280 | 1170 | 75 | 0 | 0 | 61 |  | 11437 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 152 | 7 | 65 | 55 | 20 | 0 | 0 | 9 | 48 | 140 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 13 | 22 | 24 | 6 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 12 | 58 | 68 | 18 | 12 | 0 | 0 | 17 | 0 | 0 | 0 | 280 | 280 | 125 | 0 | 40 | 30 | 10 | 0 | 43 | 0 | 33 | 42 | 0 | 0 | 0 | 17 | 80 | 32 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 262 | 0 | 0 | 122 | 0 | 149 | 0 | 24 | 51 | 40 | 346 | 79 | 52 | 51 | 0 | 16 | 1 | 17 | 88 | 58 | 25 | 350 | 52 | 0 | 162 | 28 | 0 | 17 | 0 | 68 | 17 | 230 | 84 | 0 | 340 | 16 | 720 | 0 | 0 | 0 |  | 912 | 0 | 307 | 0 | 32 | 0 | 0 | 0 | 34 | 31 | 16 | 65 | 9 | 32 | 0 | 0 | 0 | 40 | 0 | 75 | 0 | 0 | 15 | 0 | 22 | 0 | 0 | 2 | 65 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 50 | 0 | 95 | 0 | 0 | 90 | 1200 | 220 | 0 | 20 | 0 | 0 | 115 | 0 | 0 | 586 | 0 | 307 | 1070 | 0 | 0 | 0 | 0 |  | 13370 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 152 | 8 | 70 | 55 | 330 | 0 | 0 | 9 | 48 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 23 | 24 | 10 | 8 | 0 | 122 | 80 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 72 | 80 | 25 | 30 | 50 | 0 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 0 | 50 | 30 | 10 | 0 | 43 | 0 | 35 | 42 | 0 | 0 |  | 18 | 100 | 35 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 280 | 0 | 0 | 124 | 0 | 149 | 0 | 24 | 100 | 138 | 360 | 79 | 52 | 105 | 0 | 50 | 54 | 85 | 88 | 60 | 25 | 380 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 68 | 35 | 300 | 163 | 0 | 320 | 60 | 850 | 0 | 0 |  |  | 918 | 0 | 300 | 0 | 64 | 0 | 0 | 0 | 40 | 55 | 16 | 65 | 10 | 64 | 0 | 0 | 0 | 40 | 20 | 85 | 35 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 85 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1480 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 8 | 50 | 55 | 180 | 0 | 0 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 35 | 0 | 15 | 23 | 24 | 10 | 8 | 0 | 120 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 16 | 51 | 25 | 25 | 6 | 0 | 25 | 0 | 0 | 0 | 300 | 300 | 200 | 0 | 50 | 30 | 10 | 0 | 43 | 0 | 33 | 42 | 0 | 0 |  | 18 | 90 | 30 | 0 | 0 | 1.6 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 100 | 0 | 149 | 20 | 12 | 70 | 55 | 340 | 68 | 17 | 68 | 5 | 50 | 17 | 51 | 34 | 28 | 25 | 350 | 17 | 50 | 54 | 17 | 0 | 17 | 35 | 50 | 17 | 300 | 17 | 0 | 320 | 42 | 930 | 0 | 0 | 70 |  | 918 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 16 | 65 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 70 | 0 | 106 | 0 | 8 | 70 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 500 | 30 | 250 | 1200 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 360 | 150 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 24 | 10 | 2 | 0 | 121 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 345 | 335 | 45 | 0 | 45 | 34 | 49 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 58 | 34 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 136 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 97 | 0 | 52 | 0 | 0 | 17 | 0 | 220 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 27 | 0 | 350 | 0 | 10 | 0 | 0 | 0 | 0 | 13 | 17 | 35 | 310 | 0 | 0 | 340 | 13 | 867 | 0 | 0 | 2 | 0 | 914 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 1070 | 220 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 460 | 9 | 200 | 1206 | 58 | 0 | 0 | 9 | 0 |  |  |  | 121240016 | 22327272 | 0 | 96477040 | 27591856 | 1685760 | 1362420 | 564000 | 4811700 |  |  | 276060064
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 121.24 | 22.3273 | 0 | 96.477 | 27.5919 | 1.6858 | 1.3624 | 0.564 | 4.8117
| Minimum Generation |  | 9444 | 6:00
| Highest Generation |  | 13370 | 19:30 | [129 empty] | 0 | [73 empty] | 276.0601
| Day Peak Generation |  | 11437 | 12:00
| Evening Peak Generation |  | 13370 | 19:30 | [203 empty] | 202699852
| HVDC Max Flow |  | 916 | 12:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 912 | 19:30
| Load factor L.F |  | 86.03% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-04
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11437 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10539
Evening Peak Generation : |  |  | 13370 | MW Hour : | 19:30 | Available Max Generation : |  | 15695
E.P. Demand (at gen end) : |  |  | 13370 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14800
Maximum Generation : |  |  | 13370 | MW Hour : | 19:30 | Reserve(Generation end)
Total Gen. (MKWH) : |  |  | 276.0601 | System Load Factor : | 86.03% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 434 | MW at | 24:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-04
Actual : |  | 94.91 | Ft.(MSL) , | Rule curve : | 89.64 | Ft.( MSL )
Gas Consumed : |  | Total = | 893.05 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 360494047.09
: |  |  | Coal : | 642714613.31 | Oil : | 506751136.39 | Total : | 1509959796.79
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5341.9617 |  |  | 0 | -2.866%
Chittagong Area |  | 0 | 0:00 | 1472.672 |  |  | 0 | -1.035%
Khulna Area |  | 0 | 0:00 | 2064.3332 |  |  | 0 | -0.6449%
Rajshahi Area |  | 0 | 0:00 | 1795.576 |  |  | 0 | -0.2316%
Cumilla Area |  | 0 | 0:00 | 1476.7776 |  |  | 0 | -0.4881%
Mymensingh Area |  | 0 | 0:00 | 1099.0436 |  |  | 0 | -0.1293%
Sylhet Area |  | 0 | 0:00 | 615.3064 |  |  | 0 | -0.8142%
Barisal Area |  | 0 | 0:00 | 513.4616 |  |  | 0 | -0.06366%
Rangpur Area |  | 0 | 0:00 | 1004.2252 |  |  | 0 | -0.07249%
Total |  | 0 |  | 15383.3573 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:42 | 11:48 | Ashuganj-Brahmanbaria 132kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to NLDC AE.
and from Ashuganj 230/132/33kV end Due to PGCB GIS
| 08:49 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
| 08:50 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
08:54 | 18:31 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to Tower erection work
08:55 | 14:45 | Jhenaidah 132/33kV S/S Transformer T-2 HT Project Work S/D Due to জিএমডি ঝিনাইদহের আওতাধীন,
ঝিনাইদহ ১৩২/৩৩কেভি গ্রিড উপকেন্দ্রের বিদ্যুৎ বিতরণ ব্যাবস্থার সম্প্রসারণ ও আপগ্রেডেশন প্রকল্প
ওজোপাডিকো, খুলনা কর্তৃক ঝিনাইদহ ১৩২/৩৩কেভি গ্রিড উপকেন্দ্রের ৩৩/১১কেভি উপকেন্দ্র পুনর্বাসন
কাজের অংশ হিসেবে ৩৩কেভি বে এক্সটেনশন এর কআজ চলমান আছে ঝিনাইদহ ১৩২/৩৩কেভি গ্রিড
উপকেন্দ্রের ৩৩কেভি বাস সেকশন টি-২ এর সাথে আইসোলেটর সংযোগ স্থাপন করার জন্য সাট ডাইন প্রযোজন ।
ওজোপাডিকো বিতরণ বিভাগ-২ ঝিনাইদহ কর্তৃক ০৩/০৮/২০২৪ইং তারিখ
সকাল ০৮ টা থেকে দুপুর ০১ টা সাটডাউন নেওয়ার জন্য আবেদন ক
08:56 | 14:46 | Jhenaidah 132/33kV S/S Transformer T-2 LT Project Work S/D Due to জিএমডি ঝিনাইদহের আওতাধীন |  |  |  |  | 17.0MW load interruption.
, ঝিনাইদহ ১৩২/৩৩কেভি গ্রিড উপকেন্দ্রের বিদ্যুৎ বিতরণ ব্যাবস্থার সম্প্রসারণ ও আপগ্রেডেশন প্রকল্প
ওজোপাডিকো, খুলনা কর্তৃক ঝিনাইদহ ১৩২/৩৩কেভি গ্রিড উপকেন্দ্রের ৩৩/১১কেভি উপকেন্দ্র পুনর্বাসন
কাজের অংশ হিসেবে ৩৩কেভি বে এক্সটেনশন এর কআজ চলমান আছে ঝিনাইদহ ১৩২/৩৩কেভি গ্রিড
উপকেন্দ্রের ৩৩কেভি বাস সেকশন টি-২ এর সাথে আইসোলেটর সংযোগ স্থাপন করার জন্য সাট ডাইন প্রযোজন ।
ওজোপাডিকো বিতরণ বিভাগ-২ ঝিনাইদহ কর্তৃক ০৩/০৮/২০২৪ইং তারিখ
সকাল ০৮ টা থেকে দুপুর ০১ টা সাটডাউন নেওয়ার জন্য আবেদন ক
09:05 | 15:45 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT Scheduled S/D Due to Rooppur Neuclear
Power Plant (RNPP)-কে গ্রিডের সাথে সিংক করতে NLDC-তে Energy Management System
(EMS) Application সমূহ কার্যকর করার জন্য TRTUD, Bogura দপ্তরের তাগাদা মোতাবেক উপকেন্দ্রের
‍switching device (CB, DS, ES) সমূহের control/open-close status rectification করা।
09:06 | 15:45 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) HT Scheduled S/D Due to Rooppur Neuclear Power Plant (RNPP)-কে
গ্রিডের সাথে সিংক করতে NLDC-তে Energy Management System (EMS) Application সমূহ কার্যকর করার জন্য TRTUD,
Bogura দপ্তরের তাগাদা মোতাবেক উপকেন্দ্রের ‍switching device (CB, DS, ES) সমূহের control/open-close status
rectification করা।
10:53 |  | Siddhirgonj 2*120 MW GTPP Shutdown with remarks:- GT-2
10:55 | 11:08 | Jhenaidah 132/33kV S/S Transformer T-1 LT Tripped showing Over current, ABC trip relays Due to WZPDCL |  |  |  |  | 65.0MW load interruption.
shailkupa feder trip(due to not opening of shailkupa feder CB)
10:58 | 13:30 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to Red hot maintenance work |  |  |  |  | 10.0MW load interruption.
10:59 | 13:31 | Srinagar 132/33kV S/S Tr-01 LT Scheduled S/D Due to Red hot maintenance work
11:03 | 13:59 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to Annunciator Replace |  |  |  |  | 40.0MW load interruption.
11:04 | 13:57 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to Do
11:07 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D
11:17 | 11:36 | Kushtia 132/33kV S/S T-3 LT Tripped showing Micom relays Due to 33 kv feeder fault |  |  |  |  | 38.0MW load interruption.
11:20 |  | Siddhirganj 335 MW CCPP Synchronized with remarks:- GT
11:49 | 13:57 | Ashuganj-Brahmanbaria 132kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to Project work at
APSCL and from Ashuganj 230/132/33kV end Due to PGCB GIS
12:00 |  | Day Peak Generation: 11437 MW.
13:27 |  | Siddhirganj 335 MW CCPP Tripped with remarks:- GT
| 14:14 | Barishal 230/132kV S/S T-4 HT is restored.
| 14:16 | Barishal 230/132kV S/S T-4 LT is restored.
16:27 |  | Siddhirganj 335 MW CCPP Synchronized with remarks:- GT
18:13 |  | Meghnaghat 450 MW CCPP (MPL) GT-2 Synchronized with remarks:- GT-2 synchronized with grid since 14th July,2024 at 22:05 Hrs
18:22 |  | Meghnaghat 450 MW CCPP (MPL) ST Synchronized with remarks:- ST synchronized with grid since 14th July,2024 at 23:01 Hrs
19:30 |  | Evening Peak Gen. 13371 MW
19:57 |  | Adani U-1 was shut down for turbine balancing |  |  |  |  | 748MW generation interruption.
23:10 | 02:17 | Tangail 132/33kV S/S Tr-4 HT Forced S/D Due to Due to 33 kv shakhipur feeder
23:10 | 02:17 | Tangail 132/33kV S/S Tr-4 LT Forced S/D Due to Due to 33 kv shakhipur feeder
23:42 | 00:41 | Dohazari 132/33kV S/S Power Transformer -T-2 LT Forced S/D Due to Due to 33KV Satkania PDB Bus Isoletor red hot |  |  |  |  | 62.0MW load interruption.
maintenance by Satkania PDB.
23:42 | 00:41 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Forced S/D Due to Due to 33KV Satkania PDB Bus Isoletor red hot
maintenance by Satkania PDB.
04:09 |  | Meghnaghat CCPP(Summit) record a general event:- NLDC demand FGMO maximum.
05:01 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
07:00 |  | Minimum Generation = 10,540MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-03
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 409 | 9640800 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9709000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 7 | 102720 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 152 | 3673978 | Unit-2 Under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 65 | 596359 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 677247
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 696000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 105600 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 20 | 1364528 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 347040 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 574200
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 140 | 1477920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 673017
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 495971 | Low demand
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 885600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 611300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 6 | 230700 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 131520 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 262 | 2599418 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2085408
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 613978 | Low demand
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 52 | 500160 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1140480
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 86730
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 482040 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 2266 | 39501714
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 27910 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 76950
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 7200 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 202 | 4811700
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5135694
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 51 | 352109 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 58 | 317520 | Low demand
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 222582 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 18 | 105120 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 133440 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 615840
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 60480 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 19633
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 406473 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 1 | 37594 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 173963 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 138240 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 28 | 243382 | Low demand
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 84 | 297745 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 340 | 8209090 | Unit-1 Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 16 | 564000
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 720 | 19490909
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 1917 | 41447574
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 125 | 3460000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7292000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6488000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 6466200 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 628128 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 10 | 92160 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 714360
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 130472 | Low demand
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 33 | 176176 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1102380 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 1288320 | Low demand
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 80 | 1685760
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 524424 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 17 | 337460 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 88 | 941640 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 861840 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 1400640 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 247355
| Cumilla Area Total |  |  |  | 2950 | 1515 | 33837315
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 32 | 816000 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 5900
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 122 | 1896000 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 1368000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 101660
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 199200 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 250880 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 262 | 4637640
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 941000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1381800 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3451255
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 180528 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 10 | 256320 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 137 | 3280240 | ST Under maint
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 275424 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7173000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 346 | 8377000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 8222900 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1416 | 33539467
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 912 | 22327272
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 32 | 365760 | Low demand
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 34 | 138720 | Low demand
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 31 | 201856 | Low demand
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 307 | 7784928 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 93375 | Low demand
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 4800 | Reserve
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 271440
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 586 | 11600000 | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1918 | 42788151
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 279744 | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 9 | 179507
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1543000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 26195700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5392500
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 20 | 117600 | Low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 5672700
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 1270
| Barisal Area Total |  |  |  | 2236 | 1853 | 39382021
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 40 | 211280 | Fuel shortage
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 144636 | Low demand
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 194 | 4441091 | FGMO
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 8301745 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 116637
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 2 | 97650 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 75 | 174128 | Low demand
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 105024 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 165504 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 10440
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1070 | 23833296 | Machine problem.
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 160500
| Rajshahi Area Total |  |  |  | 3381 | 1948 | 37761931
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 65 | 1475345
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 95 | 501004 | Low demand
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 16315
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 807360
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 40227
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 324000
| Rangpur Area Total |  |  |  | 950 | 275 | 3164251
| Total |  |  |  | 26947 | 13370 | 276060064
| Eastern Grid Total |  |  |  | 16526 | 7376 | 152963710
| Western Grid Total |  |  |  | 10421 | 5994 | 123096354
| National Grid Total |  |  |  | 26947 | 13370 | 276060064
*Data collected from respective power station over telephone.
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 03-08-2024 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8846.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3999 | MW
i) Dhaka area |  |  | 4682.42 |  | MW | i) Khulna area |  |  |  | 1580.6 | MW
ii) Chattogram area |  |  | 1365.5 |  | MW | ii) Barishal area |  |  |  | 400.6 | MW
iii) Cumilla area |  |  | 1196 |  | MW | iii) Rajshahi area |  |  |  | 1220.8 | MW
iv) Mymensingh area |  |  | 1056 |  | MW | iv) Rangpur area |  |  |  | 797 | MW
v) Sylhet area |  |  | 547 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12845.92 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 8 | 12:00 | 67 | Jamalpur | 104 | 21:00 | 133 | Rahim | 42 | 11:00
2 | AKSML | 103 | 12:00 | 68 | Jashore | 122 | 19:30 | 134 | Rajbari | 68 | 20:00
3 | Aftabnagar | 30 | 12:00 | 69 | Jhenaidah | 124 | 19:30 | 135 | Rajendrapur | 88 | 19:30
4 | Agargaon | 95 | 13:00 | 70 | Joydebpur | 169 | 10:00 | 136 | Rajshahi | 104 | 19:30
5 | Agrabad | 84 | 19:00 | 71 | Joypurhat | 51 | 19:30 | 137 | Rajshahi-230 | 57 | 21:00
6 | Amnura | 57 | 22:00 | 72 | Juldah | 23 | 11:00 | 138 | Ramganj | 102 | 00:00
7 | Ashuganj | 83 | 03:00 | 73 | KSRM | 34 | 07:00 | 139 | Rampur | 36 | 19:30
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 292 | 15:00 | 140 | Rangamati | 18 | 20:00
9 | BSRM | 182 | 17:00 | 75 | Kachua | 70 | 00:00 | 141 | Rangpur | 118 | 19:30
10 | Bagerhat | 85 | 20:00 | 76 | Kallyanpur | 99 | 15:00 | 142 | Ruppur | 4.6 | 10:00
11 | Bakulia | 90 | 19:30 | 77 | Kalurghat | 34 | 12:00 | 143 | SSM | 3 | 23:00
12 | Banani | 50 | 13:00 | 78 | Kamrangirchar | 48 | 12:00 | 144 | Saidpur | 98 | 12:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 121 | 19:30
14 | Barapukuria | 54 | 19:00 | 80 | Kazla | 93 | 12:00 | 146 | Satmasjid | 102 | 13:00
15 | Barguna | 20 | 00:00 | 81 | Keranigonj | 84 | 13:00 | 147 | Savar | 201 | 15:00
16 | Barishal | 118 | 13:00 | 82 | Khagrachori | 26 | 18:30 | 148 | SevenRings | 14.35 | 13:00
17 | Barishal-230 | 76 | 00:00 | 83 | Khulna | 69 | 19:30 | 149 | ShahCement | 18 | 00:00
18 | Baroaulia | 71 | 10:00 | 84 | Khulshi | 155 | 12:00 | 150 | Shahjadpur | 67 | 20:00
19 | Baroirhat | 47 | 19:30 | 85 | Kishoreganj | 156 | 21:00 | 151 | Shahjibazar | 121 | 22:00
20 | Bashundhara | 151 | 13:00 | 86 | Kodda | 278 | 21:00 | 152 | Shahmirpur | 50 | 14:00
21 | BashundharaCement | 7 | 10:00 | 87 | Kulaura | 50 | 19:00 | 153 | Shariatpur | 73 | 23:00
22 | Beanibazar | 70 | 21:00 | 88 | Kurigram | 54 | 19:00 | 154 | Sherpur | 130 | 20:00
23 | Benapole | 52 | 19:30 | 89 | Kushtia | 133 | 20:00 | 155 | Shikalbaha | 29 | 23:00
24 | Bhaluka | 112 | 20:00 | 90 | Lalbag | 78 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 51 | 22:00 | 91 | Lalmonirhat | 50 | 19:30 | 157 | Shitalakhya | 77.4 | 12:00
26 | Bhangura | 30 | 19:30 | 92 | MI_Cement | 9.5 | 13:00 | 158 | Sholosohor | 41 | 15:00
27 | Bheramara(GK) | 56 | 21:00 | 93 | Madanganj | 30 | 00:00 | 159 | Shyampur | 152 | 00:00
28 | Bhulta | 231 | 15:00 | 94 | Madaripur | 92 | 22:00 | 160 | Siddhirganj | 119 | 16:00
29 | Bog-Sherpur | 56 | 20:00 | 95 | Madartek | 81.03 | 13:00 | 161 | Sirajganj | 88 | 20:00
30 | Bogura | 134 | 00:00 | 96 | Madunaghat | 53 | 19:00 | 162 | Sonargaon | 77 | 14:00
31 | Borhanuddin | 89 | 22:00 | 97 | Magura | 57 | 19:30 | 163 | Sreemongol | 68 | 19:00
32 | Brahmanbaria | 162 | 23:00 | 98 | Mahasthangarh | 60 | 00:00 | 164 | Sreepur | 95 | 12:00
33 | Cantonment | 125 | 07:00 | 99 | Manikganj | 121 | 19:30 | 165 | Srinagar | 43.68 | 23:00
34 | Chandpur | 62 | 00:00 | 100 | Maniknagar | 57 | 19:00 | 166 | Sunamganj | 52 | 22:00
35 | Chandraghona | 36 | 20:00 | 101 | Matarbari | 46 | 19:00 | 167 | Sylhet | 54 | 06:00
36 | Chapai | 58 | 22:00 | 102 | Matuail | 70 | 12:00 | 168 | Sylhet-132 | 114 | 14:00
37 | Charsaidpur | 32 | 21:00 | 103 | Millgate | 136 | 12:00 | 169 | TK | 33.5 | 19:30
38 | Chauddagram | 59 | 23:00 | 104 | Mirpur | 127 | 13:00 | 170 | Tangail | 182 | 19:30
39 | Chhatak | 31 | 01:00 | 105 | Mirsorai | 9 | 19:00 | 171 | Thakurgaon | 81 | 20:00
40 | Chowmuhani | 191 | 23:00 | 106 | Mirzapur | 42 | 19:30 | 172 | Tongi | 116 | 12:00
41 | Chuadanga | 99 | 19:30 | 107 | Mithapukur | 60 | 04:00 | 173 | Ullahpara | 25 | 19:00
42 | Coxsbazar | 124 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 47 | 19:30
43 | Cumilla(N) | 139 | 22:00 | 109 | Mogbazar | 105.2 | 13:00 | 175 | Uttara | 69 | 13:00
44 | Cumilla(S) | 155 | 21:00 | 110 | Mongla | 36 | 01:00 | 176 | UttaraNew | 49 | 13:00
45 | Daudkandi | 143 | 20:00 | 111 | Motijheel | 35 | 13:00 | 177 | Zigatola | 74 | 13:00
46 | Dhaka | 40 | 13:00 | 112 | Munshiganj | 101 | 01:00
47 | Dhamrai | 136 | 12:00 | 113 | Mymensingh | 208 | 22:00
48 | Dhanmondi | 121 | 13:00 | 114 | Naogaon | 110 | 19:30
49 | Dohazari | 93 | 21:00 | 115 | Narail | 53 | 19:30
50 | Faridpur | 153 | 21:00 | 116 | Narinda | 66.5 | 13:00
51 | Fatullah | 82 | 12:00 | 117 | Narshingdi | 167 | 19:30
52 | Fenchuganj | 41 | 19:30 | 118 | Natore | 124 | 20:00
53 | Feni | 105 | 21:00 | 119 | Nawabganj | 48.4 | 19:00
54 | GPH | 93 | 18:00 | 120 | Netrakona | 122 | 19:30
55 | Ghatail | 58 | 19:00 | 121 | New | 53.2 | 12:00
56 | Ghorashal | 50 | 00:00 | 122 | Niamatpur | 61 | 22:00
57 | Goalpara | 34 | 20:00 | 123 | Noapara | 44 | 20:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 391 | 06:00 | 375 | 09:00 | Kaliakoir | 381 | 05:00 | 364 | 08:00
| Ashuganj | 409 | 5:30 | 386 | 11:42 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bhulta | 401 | 06:00 | 382 | 12:00 | Meghnaghat | 386 | 06:00 | 368 | 12:00
| Bibiana | 399 | 20:00 | 391 | 03:00 | Payra | 412 | 06:00 | 404 | 00:00
| BIPTC | 404 | 08:00 | 395 | 19:30 | Rahanpur | 409 | 06:00 | 396 | 23:00
| Bogura | 399 | 06:00 | 385 | 03:00 | Rampal | 405 | 06:00 | 391 | 23:00
| Gopalganj | 401 | 05:00 | 387 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 258 | 23:00 | 219 | 12:00 | Haripur | 232 | 20:00 | 220 | 12:00
| AKSML | 235 | 05:00 | 223 | 11:00 | Hasnabad | 231 | 04:00 | 220 | 12:00
| Aminbazar | 232 | 05:00 | 219 | 12:00 | Hathazari | 234 | 23:00 | 228 | 10:00
| Ashuganj | 235 | 07:00 | 226 | 11:00 | Ishurdi | 236 | 06:00 | 228 | 12:00
| Ashuganj-400 | 235 | 07:00 | 226 | 11:00 | Jhenaidah | 228 | 06:00 | 217 | 19:00
| Baghabari | 232 | 06:00 | 226 | 11:00 | Kaliakoir | 236 | 05:00 | 226 | 11:00
| Barapukuria | 217 | 06:00 | 207 | 01:00 | Keranigonj | 232 | 06:00 | 219 | 12:00
| Barapukuria-230 | 217 | 06:00 | 207 | 01:00 | Khulna(S) | 231 | 06:00 | 220 | 19:00
| Barishal | 235 | 06:00 | 227 | 00:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bheramara | 234 | 06:00 | 225 | 19:00 | Maniknagar | 233 | 06:00 | 220 | 12:00
| Bhulta | 235 | 05:00 | 223 | 12:00 | Meghnaghat | 242 | 06:00 | 230 | 10:00
| Bibiana | 227 | 04:00 | 222 | 01:00 | Meghnaghat-400 | 236 | 06:00 | 225 | 12:00
| BIPTC | 236 | 06:00 | 225 | 19:00 | Mirsorai | 234 | 20:00 | 223 | 12:00
| Bogura | 228 | 06:00 | 221 | 12:00 | Rajshahi | 234 | 06:00 | 226 | 19:00
| Bogura-400 | 230 | 06:00 | 222 | 02:00 | Rampal | 232 | 06:00 | 220 | 19:00
| Borhanuddin | 239 | 06:00 | 235 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 233 | 20:00 | 223 | 12:00 | Rampura | 234 | 03:00 | 220 | 12:00
| Cumilla(N) | 230 | 05:00 | 221 | 12:00 | Shikalbaha | 235 | 21:00 | 225 | 12:00
| Faridpur | 237 | 05:00 | 229 | 00:00 | Shyampur | 233 | 06:00 | 221 | 12:00
| Fenchuganj | 229 | 05:00 | 225 | 03:00 | Siddhirganj | 234 | 20:00 | 222 | 11:00
| Ghorashal | 238 | 01:00 | 230 | 12:00 | Sirajgonj | 239 | 06:00 | 232 | 12:00
| Ghorashal-230 | 233 | 06:00 | 222 | 11:00 | Sreepur | 233 | 08:00 | 220 | 12:00
| Gopalganj | 236 | 05:00 | 229 | 11:00 | Tongi | 233 | 21:00 | 221 | 12:00
| GPH | 234 | 20:00 | 224 | 12:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 138 | 06:00 | 127 | 11:00 | Kushtia | 137 | 01:00 | 130 | 19:00
| Agargaon | 139 | 06:00 | 130 | 12:00 | Lalbag | 136 | 06:00 | 127 | 12:00
| Agrabad | 134 | 20:00 | 127 | 11:00 | Lalmonirhat | 129 | 18:30 | 122 | 00:00
| AKS | 132 | 20:00 | 126 | 10:00 | Madanganj | 132 | 21:00 | 124 | 12:00
| Aminbazar | 139 | 07:00 | 131 | 12:00 | Madaripur | 132 | 17:00 | 129 | 19:00
| Amnura | 137 | 20:00 | 128 | 23:00 | Madartek | 137 | 06:00 | 125 | 16:00
| Ashuganj | 139 | 06:00 | 135 | 09:00 | Madunaghat | 135 | 21:00 | 128 | 12:00
| Bagerhat | 133 | 05:00 | 124 | 19:00 | Magura | 138 | 06:00 | 129 | 19:00
| Bakulia | 135 | 20:00 | 128 | 12:00 | Mahasthangarh | 134 | 06:00 | 128 | 02:00
| Banani | 137 | 04:00 | 127 | 12:00 | Manikganj | 129 | 19:30 | 120 | 08:00
| Bangabhaban | 133 | 04:00 | 123 | 12:00 | Maniknagar | 133 | 06:00 | 124 | 12:00
| Barapukuria | 135 | 15:00 | 127 | 01:00 | Matarbari | 124 | 09:00 | 115 | 01:00
| Barguna | 133 | 05:00 | 129 | 00:00 | Matuail | 133.3 | 05:00 | 124 | 12:00
| Barishal | 138 | 06:00 | 132 | 00:00 | Millgate | 136 | 05:00 | 124 | 12:00
| Barishal-230 | 139 | 06:00 | 134 | 00:00 | Mirpur | 138 | 06:00 | 129 | 11:00
| Baroaulia | 135 | 20:00 | 128 | 12:00 | Mirzapur | 130 | 14:00 | 121 | 21:00
| Baroirhat | 129 | 23:00 | 122 | 04:00 | Mithapukur | 133 | 18:30 | 124 | 01:00
| Bashundhara | 138 | 06:00 | 125 | 12:00 | MI_Cement | 137 | 20:00 | 125.6 | 11:00
| BashundharaCement | 132 | 21:00 | 124 | 12:00 | Modern | 134 | 20:00 | 126 | 12:00
| Beanibazar | 124 | 04:00 | 119 | 23:00 | Mogbazar | 138 | 04:00 | 128 | 12:00
| Benapole | 134 | 05:00 | 123 | 19:30 | Mongla | 132 | 05:00 | 122 | 19:00
| Bhaluka | 131 | 01:00 | 122 | 12:00 | Motijheel | 133 | 04:00 | 123 | 12:00
| Bhandaria | 134 | 07:00 | 126 | 00:00 | Munshiganj | 133 | 20:00 | 125 | 11:00
| Bhangura | 139 | 06:00 | 133 | 11:00 | Mymensingh | 134 | 04:00 | 110 | 12:00
| Bheramara | 137 | 06:00 | 133 | 12:00 | Naogaon | 134 | 18:30 | 127 | 00:00
| Bheramara(GK) | 138 | 05:00 | 133 | 19:00 | Narail | 138 | 06:00 | 127 | 19:30
| Bhulta | 124 | 22:00 | 115 | 12:00 | Narinda | 133 | 06:00 | 124 | 12:00
| Bog-Sherpur | 136 | 06:00 | 130 | 11:00 | Narshingdi | 124 | 08:00 | 116 | 12:00
| Bogura | 137 | 06:00 | 132 | 00:00 | Natore | 135 | 06:00 | 130 | 00:00
| Bogura-230 | 137 | 06:00 | 132 | 12:00 | Nawabganj | 135 | 05:00 | 127 | 12:00
| Brahmanbaria | 130 | 06:00 | 124 | 12:00 | Netrakona | 132 | 09:00 | 123 | 07:00
| Cantonment | 138 | 04:00 | 130 | 12:00 | New | 137 | 06:00 | 128 | 10:00
| Chandpur | 132 | 13:00 | 124 | 01:00 | Niamatpur | 137 | 06:00 | 132 | 23:00
| Chandraghona | 135 | 20:00 | 130 | 12:00 | Noapara | 136 | 05:00 | 127 | 19:30
| Chapai | 134 | 06:00 | 129 | 23:00 | Pabna | 137 | 06:00 | 131 | 21:00
| Charsaidpur | 133 | 19:30 | 124 | 12:00 | Palashbari | 131 | 06:00 | 124 | 01:00
| Chauddagram | 128 | 19:30 | 122 | 00:00 | Panchagarh | 138 | 18:30 | 121 | 01:00
| Chhatak | 125 | 06:00 | 119 | 23:00 | Patuakhali | 133 | 05:00 | 129 | 00:00
| Chowmuhani | 125 | 13:00 | 114 | 02:00 | Payra | 135 | 06:00 | 131 | 00:00
| Chuadanga | 136 | 10:00 | 123 | 19:30 | PHP | 127 | 02:00 | 122 | 03:00
| Coxsbazar | 125 | 07:00 | 116 | 00:00 | Postogola | 137 | 20:00 | 129 | 11:00
| Cumilla(N) | 133 | 20:00 | 128 | 11:00 | Purbachal | 138 | 05:00 | 124 | 12:00
| Cumilla(S) | 132 | 20:00 | 126 | 02:00 | Purbasadipur | 133 | 18:30 | 121 | 03:00
| Daudkandi | 129 | 05:00 | 121 | 11:00 | Rahanpur | 138 | 06:00 | 133 | 23:00
| Dhaka | 137 | 05:00 | 128 | 11:00 | Rahim | 132 | 01:00 | 125 | 11:00
| Dhamrai | 134 | 05:00 | 126 | 12:00 | Rajbari | 134 | 06:00 | 129 | 00:00
| Dhanmondi | 133 | 05:00 | 124.5 | 12:00 | Rajendrapur | 131 | 20:00 | 120 | 09:00
| Dohazari | 131 | 20:00 | 124 | 11:00 | Rajshahi | 135 | 06:00 | 131 | 00:00
| Faridpur | 133 | 06:00 | 128 | 00:00 | Rajshahi-230 | 135 | 06:00 | 125 | 22:00
| Fatullah | 136 | 20:00 | 128 | 11:00 | Ramganj | 127 | 13:00 | 118 | 00:00
| Fenchuganj | 132 | 07:00 | 129 | 23:00 | Rampur | 134 | 21:00 | 127 | 12:00
| Feni | 126 | 20:00 | 120 | 00:00 | Rampura | 137 | 04:00 | 127 | 12:00
| Ghatail | 130 | 09:00 | 117 | 08:00 | Rangamati | 134 | 06:00 | 129 | 12:00
| Ghorashal | 140 | 04:00 | 132 | 13:00 | Rangpur | 130 | 16:00 | 124 | 09:00
| Goalpara | 135 | 06:00 | 13.5 | 10:00 | Ruppur | 137 | 05:00 | 132 | 00:00
| Gollamari | 136 | 06:00 | 128 | 19:00 | Saidpur | 133 | 16:00 | 123 | 01:00
| Gopalganj | 134 | 05:00 | 128 | 19:00 | Satkhira | 134 | 06:00 | 122 | 19:30
| Gopalganj-400 | 134 | 05:00 | 129 | 12:00 | Satmasjid | 139 | 06:00 | 130 | 11:00
| Gulshan | 137 | 06:00 | 127 | 12:00 | Savar | 139 | 20:00 | 127 | 11:00
| Halishahar | 134 | 20:00 | 127 | 12:00 | SevenRings | 139 | 06:00 | 131 | 12:00
| Haripur | 132 | 20:00 | 125 | 11:00 | ShahCement | 133 | 19:30 | 124 | 12:00
| HaripurSBU | 132 | 01:00 | 125 | 11:00 | Shahjadpur | 138 | 08:00 | 136 | 00:00
| Hasnabad | 136 | 23:00 | 129 | 11:00 | Shahjibazar | 129 | 08:00 | 123 | 12:00
| Hathazari | 137 | 23:00 | 34 | 03:00 | Shahmirpur | 134 | 19:30 | 128 | 11:00
| Ishurdi | 139 | 06:00 | 134 | 12:00 | Shariatpur | 133 | 07:00 | 127 | 00:00
| Jaldhaka | 132 | 18:30 | 119 | 01:00 | Sherpur | 136 | 05:00 | 118 | 08:00
| Jamalpur | 137 | 09:00 | 119 | 08:00 | Shikalbaha | 124 | 22:00 | 117 | 12:00
| Jashore | 134 | 04:00 | 125 | 19:00 | Shikalbaha-230 | 135 | 21:00 | 128 | 14:00
| Jhenaidah | 139 | 06:00 | 130 | 19:00 | Shitalakhya | 137 | 20:00 | 125.6 | 11:00
| Jhenaidah-230 | 140 | 06:00 | 131 | 19:00 | Sholosohor | 135 | 20:00 | 128 | 12:00
| Joydebpur | 135 | 06:00 | 125 | 12:00 | Shyampur | 136 | 21:00 | 127 | 11:00
| Joypurhat | 132 | 06:00 | 126 | 23:00 | Shyampur-230 | 136 | 20:00 | 127 | 12:00
| Juldah | 135 | 20:00 | 128 | 11:00 | Siddhirganj | 132 | 04:00 | 125 | 12:00
| Kabirpur | 133 | 02:00 | 122 | 12:00 | Sirajganj | 136 | 07:00 | 131 | 00:00
| Kachua | 130 | 13:00 | 120 | 23:00 | Sonargaon | 131 | 20:00 | 123 | 11:00
| Kaliakoir | 135 | 20:00 | 125 | 08:00 | Sreemongol | 130 | 08:00 | 123 | 23:00
| Kallyanpur | 134 | 03:00 | 126 | 12:00 | Sreepur | 132 | 06:00 | 124 | 12:00
| Kalurghat | 135 | 21:00 | 128 | 12:00 | Srinagar | 135 | 05:00 | 127 | 11:00
| Kamrangirchar | 136 | 04:00 | 125 | 12:00 | SSM | 139 | 20:00 | 129 | 16:00
| Kaptai | 136 | 4:00 | 133 | 12:00 | Sunamganj | 124 | 07:00 | 118 | 22:00
| Kazla | 132 | 05:00 | 123 | 12:00 | Sylhet | 127 | 06:00 | 124 | 12:00
| Keranigonj | 136 | 06:00 | 128 | 11:00 | Sylhet-132 | 126 | 05:00 | 124 | 12:00
| Khagrachori | 134 | 21:00 | 129 | 12:00 | Tangail | 130 | 05:00 | 123 | 16:00
| Khulna | 136 | 06:00 | 126 | 19:00 | Thakurgaon | 136 | 18:30 | 122 | 09:00
| Khulna(S) | 137 | 05:00 | 129 | 19:00 | TK | 135 | 20:00 | 129 | 12:00
| Khulshi | 133 | 20:00 | 126 | 12:00 | Tongi | 137 | 04:00 | 124 | 09:00
| Kishoreganj | 131 | 04:00 | 123 | 14:00 | Ullahpara | 135 | 06:00 | 133 | 00:00
| Kodda | 133 | 22:00 | 122 | 08:00 | Ullon | 137 | 06:00 | 128 | 12:00
| KSRM | 135 | 20:00 | 129 | 12:00 | Uttara | 139 | 06:00 | 129 | 11:00
| Kulaura | 132 | 06:00 | 127 | 23:00 | UttaraNew | 139 | 06:00 | 128 | 11:00
| Kurigram | 132 | 18:30 | 122 | 01:00 | Zigatola | 135 | 06:00 | 128 | 11:00

## L-Curve
Date | 2024-08-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 434 | 7464 | 5401 | 12865 |  |  |  | QF-LDC-11
0:30 | 599 | 6883 | 5218.5 | 12101.5 | Date: | 2024-08-03
1:00 | 764 | 6302 | 5036 | 11338
1:30 | 856 | 6154.5 | 4961 | 11115.5
2:00 | 948 | 6007 | 4886 | 10893
2:30 | 981 | 5880 | 4849.5 | 10729.5 | [5 empty] | Gen. at Eve. Peak | 13370 | 13370 MW (19:30 )
3:00 | 1014 | 5753 | 4813 | 10566 | [6 empty] | 19:30
3:30 | 964 | 5692 | 4665 | 10357 | [5 empty] | Gen. at Day Peak | 11437 | 11437 MW (12:00 )
4:00 | 914 | 5631 | 4517 | 10148 | [6 empty] | 12:00
4:30 | 902 | 5626 | 4497.5 | 10123.5 | [5 empty] | Highest Generation | 13370
5:00 | 890 | 5621 | 4478 | 10099 | [6 empty] | 19:30
5:30 | 807 | 5534.5 | 4237 | 9771.5
6:00 | 724 | 5448 | 3996 | 9444
6:30 | 687 | 5542.5 | 4013.5 | 9556
7:00 | 650 | 5637 | 4031 | 9668
7:30 | 684 | 5689 | 4109 | 9798
8:00 | 718 | 5741 | 4187 | 9928
8:30 | 910 | 5718 | 4482 | 10200
9:00 | 1102 | 5695 | 4777 | 10472
9:30 | 1177 | 5755 | 4867.5 | 10622.5
10:00 | 1252 | 5815 | 4958 | 10773
10:30 | 1332 | 5855 | 5008 | 10863
11:00 | 1412 | 5895 | 5058 | 10953
11:30 | 1437 | 6015.5 | 5179.5 | 11195
12:00 | 1462 | 6136 | 5301 | 11437
12:30 | 1365 | 6326.5 | 5306.5 | 11633
13:00 | 1268 | 6517 | 5312 | 11829
13:30 | 1329 | 6427 | 5252 | 11679
14:00 | 1390 | 6337 | 5192 | 11529
14:30 | 1394 | 6315.5 | 5137.5 | 11453
15:00 | 1398 | 6294 | 5083 | 11377
15:30 | 1404 | 6215 | 5057.5 | 11272.5
16:00 | 1410 | 6136 | 5032 | 11168
16:30 | 1382 | 6140 | 5061 | 11201
17:00 | 1354 | 6144 | 5090 | 11234
17:30 | 1286 | 6149 | 4973.5 | 11122.5
18:00 | 1218 | 6154 | 4857 | 11011
18:30 | 1111 | 6626.5 | 5130 | 11756.5
19:00 | 1004 | 7099 | 5403 | 12502
19:30 | 910 | 7376 | 5994 | 13370
20:00 | 570 | 7393 | 5692 | 13085 |  |  |  | Executive Engineer
20:30 | 545 | 7433 | 5691 | 13124 |  |  |  | Network Operation Division
21:00 | 520 | 7473 | 5690 | 13163
21:30 | 487 | 7537.5 | 5624 | 13161.5
22:00 | 454 | 7602 | 5558 | 13160 |  |  |  |  | Page 6 of 7
22:30 | 469 | 7575 | 5496 | 13071
23:00 | 484 | 7548 | 5434 | 12982
23:30 | 459 | 7506 | 5417.5 | 12923.5
24:00 | 434 | 7464 | 5401 | 12865
13370 MW (19:30 )
11437 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-03 |  | Energy |  | 276060064
[15 empty] | 2024-08-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3389 | 841 | 1610 | 0 | 2149 | 4193 | 203 | 0 | 350 | 84 | 0 | 46 | 148.025
0:30 | 3420.5 | 877 | 1652 | 0 | 1362.5 | 4265.5 | 201.5 | 0 | 207 | 79 | 0 | 36.5 | 74.0125 |  |  | Date: | 44045
1:00 | 3452 | 913 | 1694 | 0 | 576 | 4338 | 200 | 0 | 64 | 74 | 0 | 27 | 0
1:30 | 3454.5 | 913 | 1712 | 0 | 514.5 | 4179.5 | 200 | 0 | 40 | 74 | 0 | 28 | 0 | [9 empty] | Total Energy | 276.0601 | 276.0601 | Total Energy Gen 276.060 MKWHr Energy Not Served 0.614 MKWHr Energy Requirement 276.674 MKWHr
2:00 | 3457 | 913 | 1730 | 0 | 453 | 4021 | 200 | 0 | 16 | 74 | 0 | 29 | 0 | [9 empty] | Energy not Served | 0.61395 | 0.61395
2:30 | 3416.5 | 913.5 | 1663.5 | 0 | 408.5 | 4017 | 200 | 0 | 16 | 71 | 0 | 23.5 | 0 | [9 empty] | Energy Requirement | 276.674 | 276.674
3:00 | 3376 | 914 | 1597 | 0 | 364 | 4013 | 200 | 0 | 16 | 68 | 0 | 18 | 0
3:30 | 3377.5 | 913.5 | 1621 | 0 | 336.5 | 3806 | 200 | 0 | 16 | 68 | 0 | 18.5 | 0 | [8 empty] | Shortage
4:00 | 3379 | 913 | 1645 | 0 | 309 | 3599 | 200 | 0 | 16 | 68 | 0 | 19 | 0
4:30 | 3378.5 | 913 | 1631 | 0 | 308.5 | 3589.5 | 200 | 0 | 16 | 68 | 0 | 19 | 0
5:00 | 3378 | 913 | 1617 | 0 | 308 | 3580 | 200 | 0 | 16 | 68 | 0 | 19 | 0
5:30 | 3302.5 | 913.5 | 1572.5 | 0 | 266 | 3411.5 | 200 | 0 | 16 | 65 | 0.5 | 24 | 0
6:00 | 3227 | 914 | 1528 | 0 | 224 | 3243 | 200 | 0 | 16 | 62 | 1 | 29 | 0
6:30 | 3341.5 | 913.5 | 1544 | 0 | 184.5 | 3253.5 | 200 | 0 | 16 | 62 | 13 | 28 | 0 | [7 empty] | Coal
7:00 | 3456 | 913 | 1560 | 0 | 145 | 3264 | 200 | 0 | 16 | 62 | 25 | 27 | 0
7:30 | 3485 | 913 | 1623 | 0 | 145 | 3282 | 200.5 | 0 | 16 | 61 | 44 | 28.5 | 0 | [6 empty] | Oil
8:00 | 3514 | 913 | 1686 | 0 | 145 | 3300 | 201 | 0 | 16 | 60 | 63 | 30 | 0
8:30 | 3471.5 | 913 | 1674.5 | 0 | 201.5 | 3530.5 | 204.5 | 0 | 40 | 61 | 82.5 | 21 | 0
9:00 | 3429 | 913 | 1663 | 0 | 258 | 3761 | 208 | 0 | 64 | 62 | 102 | 12 | 0
9:30 | 3380.5 | 914 | 1662 | 0 | 350.5 | 3866.5 | 207.5 | 0 | 64 | 57 | 105 | 15.5 | 0
10:00 | 3332 | 915 | 1661 | 0 | 443 | 3972 | 207 | 0 | 64 | 52 | 108 | 19 | 0
10:30 | 3266.5 | 915 | 1654.5 | 0 | 527 | 4046.5 | 207 | 0 | 64 | 55 | 112.5 | 15 | 0
11:00 | 3201 | 915 | 1648 | 0 | 611 | 4121 | 207 | 0 | 64 | 58 | 117 | 11 | 0
11:30 | 3256 | 915.5 | 1695 | 0 | 695.5 | 4147.5 | 184 | 0 | 64 | 60 | 167.5 | 10 | 25
12:00 | 3311 | 916 | 1742 | 0 | 780 | 4174 | 161 | 0 | 64 | 62 | 218 | 9 | 50
12:30 | 3315 | 914.5 | 1698 | 0 | 948.5 | 4216 | 160.5 | 0 | 64 | 64 | 241 | 11.5 | 25
13:00 | 3319 | 913 | 1654 | 0 | 1117 | 4258 | 160 | 0 | 64 | 66 | 264 | 14 | 0
13:30 | 3319 | 913 | 1654 | 0 | 1117 | 4258 | 160 | 0 | 64 | 66 | 264 | 14 | 0
14:00 | 3319 | 913 | 1654 | 0 | 1117 | 4258 | 160 | 0 | 64 | 66 | 264 | 14 | 0
14:30 | 3234.5 | 913 | 1620 | 0 | 1114 | 4173.5 | 179 | 0 | 59 | 74 | 214.5 | 21.5 | 0
15:00 | 3150 | 913 | 1586 | 0 | 1111 | 4089 | 198 | 0 | 54 | 82 | 165 | 29 | 0
15:30 | 3176.5 | 912.5 | 1573.5 | 0 | 1084.5 | 4041.5 | 198.5 | 0 | 49.5 | 80 | 131.5 | 24.5 | 0
16:00 | 3203 | 912 | 1561 | 0 | 1058 | 3994 | 199 | 0 | 45 | 78 | 98 | 20 | 0
16:30 | 3269.5 | 912.5 | 1571.5 | 0 | 1047 | 3990.5 | 199 | 0 | 47 | 71 | 70.5 | 22.5 | 0
17:00 | 3336 | 913 | 1582 | 0 | 1036 | 3987 | 199 | 0 | 49 | 64 | 43 | 25 | 0
17:30 | 3340 | 912.5 | 1555 | 0 | 1062.5 | 3881 | 199 | 0 | 49 | 67 | 29 | 27.5 | 0
18:00 | 3344 | 912 | 1528 | 0 | 1089 | 3775 | 199 | 0 | 49 | 70 | 15 | 30 | 0
18:30 | 3366.5 | 912 | 1619 | 0 | 1444.5 | 3836 | 200.5 | 0 | 276 | 75 | 7.5 | 19.5 | 0
19:00 | 3389 | 912 | 1710 | 0 | 1800 | 3897 | 202 | 0 | 503 | 80 | 0 | 9 | 0
19:30 | 3264 | 912 | 1759 | 0 | 2249 | 4288 | 202 | 0 | 600 | 80 | 0 | 16 | 0
20:00 | 3221 | 913 | 1639 | 0 | 2355 | 4012 | 202 | 0 | 639 | 80 | 0 | 24 | 0
20:30 | 3318.5 | 912.5 | 1683 | 0 | 2290 | 4032.5 | 202 | 0 | 584 | 80 | 0 | 21.5 | 51
21:00 | 3416 | 912 | 1727 | 0 | 2225 | 4053 | 202 | 0 | 529 | 80 | 0 | 19 | 102
21:30 | 3427 | 877 | 1729 | 0 | 2185 | 4123 | 202 | 0 | 514.5 | 79 | 0 | 25 | 108.3
22:00 | 3438 | 842 | 1731 | 0 | 2145 | 4193 | 202 | 0 | 500 | 78 | 0 | 31 | 114.6
22:30 | 3404.5 | 841.5 | 1682.5 | 0 | 2167 | 4198 | 202.5 | 0 | 456 | 78 | 0 | 41 | 132.745
23:00 | 3371 | 841 | 1634 | 0 | 2189 | 4203 | 203 | 0 | 412 | 78 | 0 | 51 | 150.89
23:30 | 3380 | 841 | 1622 | 0 | 2169 | 4198 | 203 | 0 | 381 | 81 | 0 | 48.5 | 149.4575 |  |  | Max Temp. in Dhaka |  | 31.0°C
24:00 | 3389 | 841 | 1610 | 0 | 2149 | 4193 | 203 | 0 | 350 | 84 | 0 | 46 | 148.025
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 276.060 MKWHr Energy Not Served 0.614 MKWHr Energy Requirement 276.674 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 121 | 128 | 127 | 127 | 81 | 80 | 119 | 118 | 119 | 119 | 119 |  | 122 | 122 | 122 | 122 | 122 | 123 | 123 | 2879700
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1932000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [22 empty] | 3 | 8 | 8 | 8 | 27910
| Teknaf 20MW PP (Solartech) | [8 empty] | 6 |  | 15 | 12 | 14 | 13 | 10 | 7 | 4 | 0 | [8 empty] | 76950
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 223 | 223 | 223 | 201 | 200 | 201 | 221 | 223 | 223 | 221 | 221 | 221 | 223 | 220 | 222 | 220 |  | 218 | 220 | 223 | 223 | 222 | 222 | 222 | 5135694
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 65 | 68 | 68 | 36 | 34 | 34 |  | 222582
12 | Hathazari 100 MW peaking PP | [19 empty] | 50 | 58 | 62 | 72 | 64 | 64 | 40 | 317520
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 13 | 51 | 51 | 68 | 68 | 68 | 68 | 352109
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [13 empty] | 20 | 22 | 29 | 33 | 33 |  | 33 | 33 | 33 |  |  |  |  | 176176
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 40 | 40 | 40 | 40 | 39 | 39 | 40 | 99 | 100 | 99 | [16 empty] | 696000
17 | Siddhirganj 335 MW CCPP | [11 empty] | 32 | 62 |  |  |  | 155 | 168 |  | 140 | 20 | 24 | 221 | 221 | 220 | 220 | 1364528
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 25 | 64 | 130 | 145 | 145 | 153 | 160 | 160 |  | 180 | 262 | 263 | 283 | 291 | 280 | 278 | 2599418
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 341 | 340 | 342 | 342 | 340 | 340 | 342 | 340 | 340 | 340 | 342 |  | 340 | 340 | 340 | 340 | 340 | 341 | 340 | 8209090
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 27 | 28 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 628128
33 | Ashuganj 225 MW CCPP | 145 | 143 | 144 | 144 | 144 | 142 | 142 | 140 | 141 | 142 | 141 | 142 | 143 | 145 | 145 | 142 | 144 | 140 |  | 110 | 125 | 125 | 144 | 144 | 143 | 144 | 3460000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 345 | 340 | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 285 | 270 | 285 |  | 285 | 280 | 280 | 250 | 250 | 240 | 240 | 6488000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 315 | 325 | 290 | 280 | 280 | 280 | 280 | 280 | 280 | 295 | 280 | 295 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7292000
| Ashuganj 420 MW CCPP(East) | 295 | 295 | 285 | 285 | 285 | 290 | 315 | 325 | 250 | 250 | 250 | 280 | 280 | 250 | 250 | 250 | 250 | 250 |  | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 6466200
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | [12 empty] | 2 | 10 | 10 | 10 |  | 10 | 10 | 10 | 8 | 5 | 5 | 5 | 92160
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 51 | 51 | 70 | 70 | 50 | 50 | 50 | 45 | 45 | 43 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 45 | 45 | 1102380
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 403 | 404 | 404 | 405 | 405 | 404 | 405 | 405 | 405 | 370 | 370 | 390 | 404 | 401 | 406 | 405 | 406 | 371 |  | 400 | 409 | 404 | 401 | 401 | 401 | 401 | 9640800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 400 | 350 |  | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 9709000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 48 | 47 | 47 | 48 | 48 | 48 | 48 | 44 | 30 | 31 | 26 | 27 | 27 | 27 | 27 | 26 | 28 | 28 |  | 28 | 32 | 32 | 33 | 33 | 34 | 34 | 816000
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 1 | 2 | 1 | 14 | 14 | 10 | 18 | 21 | 22 | 0 | 1 | 1 | [8 empty] | 101660
44 | Fenchugonj CCPP Phase-1 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 941000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1381800
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 256320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 137 | 137 | 137 |  | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 3280240
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 180528
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 8 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 275424
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 270 | 300 | 290 | 275 | 310 | 315 | 305 | 300 | 290 | 300 | 285 | 275 | 295 | 285 | 305 | 300 |  | 305 | 295 | 290 | 290 | 300 | 290 | 300 | 7173000
| Bibiyana South 400 MW | 350 | 351 | 350 | 350 | 350 | 320 | 350 | 340 | 340 | 342 | 342 | 345 | 345 | 310 | 320 | 332 | 330 | 330 |  | 375 | 350 | 350 | 350 | 350 | 326 | 326 | 8222900
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 495971
59 | Tangail Palli Power Gen 22 MW | 12 | 8 | [7 empty] | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 4 | 11 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 199200
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 74 | 74 | 68 | 68 | 68 | 62 | 62 | 60 | 62 | 52 | 58 | 62 | 66 | 92 | 82 | 78 | 64 | 70 |  | 80 | 80 | 80 | 80 | 78 | 78 | 84 | 1685760
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 15 | 5 | 5 | 6 | 7 | 11 | 8 | 5 | 7 | 10 | 7 |  | 17 | 17 | 22 | 30 | 30 | 36 | 36 | 615840
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 9 | 9 | 11 | 6 | 6 | 8 | 9 | 9 |  | 15 | 17 | 18 | 18 | 18 | 18 | 18 | 337460
69 | Summit Ashulia | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 |  | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 351000
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 534600
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 611300
72 | Rupganj 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 12 | 12 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 230700
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 34 | 51 | 52 | 38 | 34 | 34 |  | 81 | 88 | 88 | 88 | 70 | 70 | 70 | 941640
| Chowmuhani 113 MW | 33 | 28 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 28 | 28 | 28 | 30 | 38 | 36 | 36 |  | 45 | 58 | 59 | 63 | 58 | 50 | 30 | 861840
| Manikgonj 162MW PP(MPGL) | [10 empty] | 17 | 54 | 108 | 108 | 108 | 72 | 72 | 72 |  | 144 | 162 | 162 | 108 | 54 | 54 | 54 | 1140480
77 | Siddhirganj 100 PP(Dutch Bangla) | [10 empty] | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 105600
78 | Gazipur 52 MW PP | [8 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 131520
79 | Kodda 150 MW PP | 64 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 64 | 64 | 64 | 64 | 64 | 32 | 32 | 16 | 16 | 16 |  | 132 | 140 | 145 | 132 | 132 | 132 | 117 | 1477920
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 14 | 8 | 8 | [5 empty] | 2 | 16 | 16 | 16 | 30 | 41 | 41 | 24 | 24 | 24 |  | 33 | 42 | 42 | 42 | 42 | 42 | 42 | 524424
| Gazipur 100 MW PP | 17 | [7 empty] | 17 | 34 | 52 | 52 | 52 | 52 | 34 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 35 | 17 | 613978
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 3 |  | 2 | 3 | 3 | 4 | 1 | 0 | 0 | [8 empty] | 19633
| Jodiac Power | [20 empty] | 1 | 18 |  |  |  |  | 37594
| Karnaphuli Power Ltd. | [19 empty] | 4 | 17 | 26 | 34 | 34 | 34 | 34 | 173963
82 | Madanganj 102 PP(Summit) | [11 empty] | 14 | 42 | 42 | 58 | 52 | 34 | 34 |  | 37 | 65 | 65 | 65 | 68 | 68 | 70 | 596359
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 154 | 153 | 154 | 152 | 153 | 153 | 154 | 153 | 150 | 155 | 154 | 154 | 152 | 152 | 155 | 154 | 154 | 155 |  | 154 | 152 | 153 | 153 | 153 | 153 | 153 | 3673978
87 | Meghnaghat 100 MW(IEL) | [10 empty] | 1 | 7 | 7 | 7 | 8 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 102720
| Meghnaghat 104 MW PP (OPCL) | 17 | [8 empty] | 7 | 17 | 24 | 30 | 28 | 30 | 30 | 30 | 45 |  | 52 | 52 | 52 | 52 | 51 | 42 | 17 | 500160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 6 | 18 | 25 | 25 | 25 | 25 | 25 | 105120
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | [8 empty] | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 714360
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 347040
95 | Patenga 50MW PP (Baraka) | [26 empty] | 7200
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 12 | 10 | 12 | 12 | 12 | 12 | 60480
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | [9 empty] | 15 | 20 | 40 | 40 | 42 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 677247
100 | Manikganj 55 MW PP (Northern) | [10 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 673017
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 120 |  | 120 | 163 | 120 | 120 | 163 | 120 | 120 | 3451255
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 5900
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 15 | 29 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 574200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 65 | 35 | 35 | 8 | 8 | 8 | 30 | 93 | 93 | 93 | 95 | 65 | 65 | 65 | 65 | 75 |  | 133 | 122 | 124 | 127 | 127 | 127 | 127 | 1896000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 62 | 53 | 53 | 53 | 53 | 40 | 17 | 17 | 19 | 61 | 71 | 71 | 71 | 78 | 88 | 108 | 115 | 132 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2085408
115 | Juldah 100 MW PP Unit-3 (Acorn) | [19 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 133440
116 | Chandpur 200 MW (Desh energy) | 85 | 68 | 68 | 51 | 51 | 51 | 17 | 17 | 24 | 51 | 51 | 62 | 115 | 115 | 45 | 17 | 21 | 17 |  | 27 | 51 | 51 | 51 | 51 | 51 | 51 | 1288320
117 | Ashuganj 150 MW PP (Midland) | [19 empty] | 7 | 40 | 35 | 10 | 10 | 10 | 10 | 130472
118 | Bibiyana-III 400 MW CCPP | 349 | 352 | 349 | 349 | 349 | 299 | 330 | 352 | 354 | 348 | 350 | 350 | 334 | 300 | 302 | 309 | 300 | 313 |  | 400 | 346 | 348 | 349 | 347 | 288 | 289 | 8377000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 58 | 24 | 8 | 8 | 56 | 56 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 59 |  | 78 | 79 | 78 | 78 | 78 | 78 | 78 | 1368000
| Anwara 300 MW PP (United) | [19 empty] | 15 | 16 | 16 | 32 | 98 | 165 | 200 | 406473
| Juldah unit-2 (Acorn) | [19 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 138240
| Anlima Energy Ltd. | [19 empty] | 9 | 28 | 31 | 53 | 53 | 53 | 38 | 243382
| Bhairob 54.5 MW | 17 | 17 | [9 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 6 | 17 | 17 | 250880
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 1 | 3 | 5 | 11 | 19 | 20 | 6 | 10 | 7 | 3 | 3 | 1 | [8 empty] | 86730
| Chandpur 115(Doreen) | 82 | 64 | 48 | 49 | 49 | 39 | 33 | 33 | 46 | 49 | 49 | 49 | 62 | 63 | 66 | 69 | 68 | 68 |  | 68 | 68 | 68 | 67 | 68 | 67 | 66 | 1400640
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 23 | 27 | 22 | 15 | 17 |  | 17 | 17 | 17 | 17 | 34 | 29 | 17 | 482040
| Mirsharai 150 MW (Oil) | [19 empty] | 59 | 84 | 90 | 54 | 54 | 17 | 54 | 297745
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 27 | 29 | 18 | 19 | 19 | 29 | 27 | 30 | 12 | 19 | 11 | 9 | 14 | 31 | 29 | 20 | 25 | 30 |  | 9 | 16 | 24 | 19 | 31 | 51 | 46 | 564000
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 7 | 22 | 25 | 6 | 9 | 6 | 63 | 50 | 25 | 25 | 18 | 1 | [8 empty] | 247355
| Matarbari 2*600 MW (CPGCL) | 1082 | 934 | 908 | 809 | 810 | 812 | 813 | 814 | 814 | 812 | 810 | 812 | 812 | 808 | 809 | 710 | 606 | 618 |  | 633 | 720 | 719 | 720 | 860 | 929 | 926 | 19490909
120 | Eastern Zone Total | 6302 | 6007 | 5753 | 5631 | 5621 | 5448 | 5637 | 5741 | 5695 | 5815 | 5895 | 6136 | 6517 | 6337 | 6294 | 6136 | 6144 | 6154 |  | 7099 | 7376 | 7393 | 7473 | 7602 | 7548 | 7464 | 152963710
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 5 |  | 31 | 32 | 57 | 81 | 81 | 80 | 80 | 365760
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 29 | 34 | 30 | 30 | 29 | 20 | 10 | 138720
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [25 empty] | 0 | 4800
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 9 | 28 | 52 | 38 | 23 | 22 | 24 | 45 | 20 | 14 | 6 | 1 | [8 empty] | 271440
131 | Rampal 1320 MW (BIFPCL) | 556 | 410 | 361 | 362 | 363 | 356 | 363 | 365 | 448 | 504 | 508 | 508 | 508 | 490 | 462 | 464 | 463 | 414 |  | 502 | 586 | 623 | 621 | 623 | 622 | 618 | 11600000
132 | United Payra Power Ltd. | [20 empty] | 20 | 54 | 17 | 17 | 17 | 17 | 117600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5392500
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 32 | 32 | 48 | 64 | 80 | 96 | 279744
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 280 | 226 | 185 | 160 | 160 | 140 | 140 | 170 | 220 | 280 | 280 | 280 | 280 | 245 | 220 | 220 | 220 | 220 |  | 252 | 307 | 307 | 307 | 307 | 250 | 250 | 5672700
136 | Barisal 1 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1270
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 64 | 64 | 64 | 64 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1543000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 9 | 10 | 10 | 8 | 7 | 5 | 6 | 6 | 5 | 6 | 7 | 6 | 3 | 6 | 6 | 6 |  | 8 | 9 | 9 | 10 | 10 | 10 | 10 | 179507
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [20 empty] | 16 | 16 | 16 | 24 | 24 | 24 | 93375
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 21 | 31 | 40 | 55 | 41 | 41 | 36 | 201856
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 913 | 913 | 914 | 913 | 913 | 914 | 913 | 913 | 913 | 915 | 915 | 916 | 913 | 912 | 913 | 912 | 913 | 912 |  | 912 | 912 | 913 | 912 | 842 | 841 | 841 | 22327272
147 | Bheramara 410 MW CCPP | 364 | 366 | 300 | 300 | 300 | 230 | 230 | 230 | 359 | 351 | 349 | 341 | 337 | 332 | 327 | 328 | 324 | 324 |  | 274 | 307 | 274 | 312 | 311 | 313 | 308 | 7784928
148 | Payra 1320 MW | 1110 | 1000 | 920 | 910 | 920 | 720 | 720 | 720 | 870 | 960 | 960 | 1000 | 1080 | 1040 | 1020 | 1020 | 1020 | 940 |  | 970 | 1200 | 1200 | 1244 | 1244 | 1244 | 1244 | 26195700
149
150 | Barapukuria TPP Unit-1 | 63 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 63 | 63 | 64 | 64 |  | 64 | 65 | 64 | 64 | 65 | 64 | 64 | 1475345
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 211280
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 10440
| Sirajganj 68 MW Solar Park | [7 empty] | 3 | 6 | 17 | 20 | 61 | 65 | 2 | 1 | 3 | 1 | 1 | [8 empty] | 160500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 214 | 188 | 156 | 150 | 173 | 156 | 150 | 150 | 152 | 163 | 154 |  | 160 | 194 | 176 | 148 | 173 | 192 | 214 | 4441091
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 314 | 347 | 322 | 341 | 322 | 250 | 250 | 355 | 354 | 352 | 325 | 389 | 313 | 386 | 373 | 346 | 344 | 347 |  | 373 | 390 | 312 | 393 | 397 | 347 | 313 | 8301745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 |  |  | 2 | 2 | 2 |  | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 97650
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 10 | 15 | 22 | 46 | 42 | 42 | 35 | 144636
168 | Santahar 50 MW Peaking PP | [19 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 116637
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 42 | 75 | 87 | 42 | 42 |  |  | 174128
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 14 | 50 | 47 |  |  |  |  | 105024
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 35 | 90 | 106 | 50 |  |  |  | 165504
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 15 | [18 empty] | 95 | 95 | 97 | 70 | 70 | 70 | 70 | 501004
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 1 | [8 empty] | 16315
178 | Energypac Power Venture Thakurgaon Ltd. | [11 empty] | 1 | 35 | 35 | 35 | 35 | 35 | 35 |  | 110 | 115 | 115 | 115 | 70 | 72 | 72 | 807360
| Intraco Solar 30 MW | [5 empty] | 0 | 1 | 1 | 1 | 1 | 5 | 5 | 2 | 1 | 4 | 7 | 7 | 1 | [8 empty] | 40227
| Adani Power Jharkhanda Ltd | 907 | 1047 | 1235 | 954 | 923 | 811 | 824 | 826 | 1005 | 1010 | 1157 | 1170 | 1174 | 1178 | 1175 | 1177 | 1274 | 1177 |  | 1136 | 1070 | 759 | 757 | 754 | 753 | 751 | 23833296
178 | Teesta Solar Limited | [6 empty] | 6 | 2 | 3 | 15 | 8 | 75 | 62 | 60 | 69 | 36 | 1 | 8 | [8 empty] | 324000