## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-06 | Tuesday
|  | Date (day): | 2024-08-06 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13937.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15856 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-05 | 2024-08-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 200 | 140 | 140 | 40 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 320 | 373 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 8 | 8 | 92 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 152 | 160 | 320 | 320 | 15 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 100 | 100 | 100 | 110 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 8 | 9 | 91 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 325 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 48 | 64 | 149 |  |  | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 30 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 35 | 38 | 38 |  | 42 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 16 | 24 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 8 | 10 | 10 |  | 23 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 145 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 78 | 88 | 72 | 149
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 17 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 54 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 15 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1387 | 1888 | 2524 | 2986 | 2258 | 911
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 205 | 201 | 200 | 202 | 28 |  | Low water lavel
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 222 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 72 | 26 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 80 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 12 | 24 | 76 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 25 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 25 | 30 | 78 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 50 | 50 | 250 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 51 | 85 | 25 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 25 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 17 | 53 | 63 |  | Fuel shortage
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 17 | 163
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 320 | 340 | 340 | 340 |  | 612 | Unit-1 under maint.
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 20 | 9 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 635 | 573 | 360 | 360 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1464 | 1458 | 1642 | 2050 | 884 | 964
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 217 | 200 | 210 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 0 | 0 | 0 |  | 360 | Under maint
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 300 | 300 | 300 |  |  | FGMO
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 285 | 300 | 300 | 100 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 30 | 30 | 15 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 42 | 47 | 45 | 45 | 10 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 55 | 100 | 100 | 95 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 51 | 43 | 43 |  | 8 | Engine problem
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 55 | 138 |  | 12 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 33 | 35 |  | 17 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 85 | 95 | 95 | 68 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 100 | 70 | 100 | 100 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 76 | 74 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 7 | 8 | 8 | 8 |  | 44 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 |  | 97 | Engine problem
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 14 | 27 | 28 | 60 | 53 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 32 | 65 | 68 | 68 | 47 |  | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 62 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2950 | 1460 | 1382 | 1570 | 1667 | 488 | 578
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 193 | 202 | 200 | 200
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 0 | 35 | 96 | 122 | 78 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 0 | 47 | 68 | 79 | 36 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 18 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 12 | 12 |  | 10 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | engine problem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 211 | 290 | 444.6 | 430 | 0 | 47
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 39 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 32 | 30 | 30 | 36 |  | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 10 | 0 | 10 | 10 | 76 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 20 | 135 | 136 | 137 |  | 94 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 334 | 270 | 340 | 360 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 340 | 350 | 380 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1302 | 1347 | 1447 | 1498 | 233 | 502
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 914 | 915 | 918 | 918
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 16 | 32 | 64 |  | 51 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 369 | 300 | 300 | 110 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 16 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 85 |  | 20 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 20 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 757 | 970 | 900 | 900 | 334 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1971 | 2270 | 2313 | 2378 | 1155 | 139
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 64 | 46 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 4 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 65 | 65 |  | 129 | GT-1 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 560 | 900 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 90 | 60 |  | Fuel shortage.
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 150 | 307 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 934 | 1437 | 1578 | 2000 | 106 | 129
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 35
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 156 | 174 | 160 | 180 | 30 |  | Gas shortage
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 348 | 414 | 380 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 30 |  | 20 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 85 |  | 19 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 70 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 925 | 1112 | 1200 | 1480
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 15 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1450 | 1705 | 2046 | 2561 | 693 | 108
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 61 | 64 | 65 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 106 | 106 | 106
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 28 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 133 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 260 | 282 | 373 | 286 | 40 | 384
| Total |  |  |  |  | 28098 | 26947 | 10439 | 12059 | 13937.6 | 15856 | 5857 | 3762
A. |  | 2024-08-05 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 12393 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10311 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12059 | MW
3 | Day peak Generation : |  |  | 10439 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11544.4 | MW
4 | Evening peak Generation : |  |  | 12059 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 259.8849 | MKWHr | By Solar | 1.3033 | MKWHr
| By Gas : | 124.7705 | MKWHr |  | By Oil: | 12.2162 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 92.5862 | MKWHr |  | By Hydro: | 4.7277 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.3168 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5857 | MW | Dhaka | 3630 | 3630 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3762 | MW | Chittagong | 1025 | 1025 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9619 | MW | Khulna | 1502.9 | 1502.9 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 967.73 | MMCFD |  |  | Rajshahi | 1256 | 1256 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 377681348.39 | ii) Oil : | Taka | 223494138.58 | Comilla | 1254 | 1254 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 624351877.73 | Total | Taka | 1225527364.7 | Mymensingh | 1035 | 1035 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5704.05 | MKWHr. | Sylhet | 533 | 533 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 640 | MW (W to E) at | 21:00 | hrs | Barisal | 398.5 | 398.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 450 | MW at | 19:30 | hrs | Rangpur | 910 | 910 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.4°C |  |  | Total | 11544.4 | 11544.4 |  | 0
B. |  | 2024-08-06 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 33.3°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15856 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 1856 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 293.5841 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9991 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1671 | MKWHr. | ii) HVDC Flow at Peak Time |  | 915 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7971 | MKWHr. | iii) Maximum HVDC Flow : |  | 915 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 95.97 |  | (b) Today: | 96.67 |  | (c) Rule Curve: |  | 90.28
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-08-05 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 136 | 7 | 20 | 30 | 330 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 14 | 22 | 24 | 17 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 8 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 250 | 217 | 0 | 50 | 33 | 30 | 0 | 43 | 0 | 7 | 8 | 0 | 0 | 0 | 18 | 88 | 150 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 15 | 0 | 0 | 97 | 0 | 99 | 0 | 24 | 51 | 0 | 349 | 59 | 17 | 51 | 0 | 50 | 0 | 17 | 17 | 23 | 25 | 345 | 34 | 0 | 17 | 17 | 0 | 17 | 0 | 68 | 35 | 230 | 0 | 0 | 320 | 9 | 781 | 0 | 0 | 0 |  | 915 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 22 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 17 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1030 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 180 | 1226 | 0 | 0 | 0 | 0 |  | 6723 | 5670 | 12393 | 3831 | 915 | 1716 | 0 | 1023 | 4498 | 200 | 0 | 113 | 88 | 0 | 9 | 312.285 | 95.82
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 |  | 0 | 450 | 141 | 7 | 17 | 30 | 280 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 22 | 24 | 17 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 250 | 217 | 0 | 50 | 33 | 30 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 86 | 150 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 15 | 0 | 0 | 96 | 0 | 88 | 0 | 24 | 51 | 0 | 348 | 59 | 17 | 17 | 0 | 15 | 0 | 17 | 17 | 12 | 25 | 345 | 33 | 0 | 17 | 17 | 0 | 17 | 0 | 66 | 35 | 230 | 0 | 0 | 320 | 17 | 789 | 0 | 0 | 0 |  | 914 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 17 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1020 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 811 | 0 | 180 | 1231 | 0 | 0 | 0 | 0 |  | 6497 | 5504 | 12001 | 3778 | 914 | 1650 | 0 | 896 | 4412 | 200 | 0 | 48 | 86 | 0 | 17 | 314.195 | 95.85
3:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 146 | 8 | 0 | 15 | 280 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 17 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 295 | 250 | 216 | 0 | 70 | 33 | 36 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 86 | 150 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 84 | 0 | 0 | 51 | 0 | 353 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 325 | 33 | 0 | 0 | 0 | 0 | 17 | 0 | 66 | 35 | 230 | 0 | 0 | 320 | 14 | 790 | 0 | 0 | 0 |  | 915 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1020 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 749 | 0 | 150 | 1128 | 0 | 0 | 0 | 0 |  | 6332 | 5250 | 11582 | 3931 | 915 | 1659 | 0 | 542 | 4219 | 200 | 0 | 16 | 86 | 0 | 14 | 303.69 | 95.88
4:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 143 | 7 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 17 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 270 | 189 | 0 | 50 | 33 | 48 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 92 | 150 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 0 | 0 | 51 | 0 | 348 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 35 | 230 | 0 | 0 | 320 | 13 | 790 | 0 | 0 | 0 |  | 915 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 61 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1030 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 0 | 150 | 1021 | 0 | 0 | 0 | 0 |  | 6224 | 5163 | 11387 | 3874 | 915 | 1687 | 0 | 463 | 4127 | 200 | 0 | 16 | 92 | 0 | 13 | 298.915 | 95.91
5:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 142 | 7 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 17 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 270 | 193 | 0 | 50 | 33 | 50 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 86 | 160 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 0 | 0 | 51 | 0 | 349 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 49 | 35 | 230 | 0 | 0 | 320 | 11 | 789 | 0 | 0 | 0 |  | 914 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 880 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 150 | 1025 | 0 | 0 | 0 | 0 |  | 6232 | 5013 | 11245 | 3890 | 914 | 1689 | 0 | 460 | 3979 | 200 | 0 | 16 | 86 | 0 | 11 | 291.275 | 95.94
6:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 362 | 0 |  | 0 | 330 | 139 | 7 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 16 | 0 | 0 | 120 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 189 | 0 | 50 | 33 | 51 | 0 | 43 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 78 | 200 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 30 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 1 | 0 | 51 | 0 | 327 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 320 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 51 | 35 | 230 | 0 | 0 | 324 | 16 | 665 | 0 | 0 | 2 |  | 914 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 62 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 756 | 1 | 150 | 939 | 12 | 0 | 0 | 0 |  | 5835 | 4764 | 10599 | 3673 | 914 | 1526 | 0 | 462 | 3696 | 200 | 0 | 16 | 78 | 18 | 16 | 249.255 | 95.97
7:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 323 | 0 |  | 0 | 330 | 147 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 24 | 15 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 290 | 275 | 195 | 0 | 50 | 33 | 49 | 0 | 5 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 78 | 198 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 20 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 78 | 1 | 0 | 51 | 0 | 301 | 16 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 9 | 0 | 320 | 0 | 4 | 0 | 0 | 0 | 17 | 3 | 50 | 17 | 230 | 0 | 0 | 320 | 8 | 666 | 0 | 0 | 5 |  | 914 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 740 | 180 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 758 | 5 | 150 | 924 | 46 | 0 | 0 | 2 |  | 5676 | 4768 | 10444 | 3626 | 914 | 1532 | 0 | 366 | 3619 | 202 | 0 | 16 | 78 | 83 | 8 | 101.23 | 96
8:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 330 | 137 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 24 | 15 | 8 | 0 | 122 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 285 | 270 | 190 | 0 | 50 | 33 | 48 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 70 | 192 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 20 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 78 | 10 | 0 | 51 | 0 | 302 | 8 | 17 | 0 | 2 | 0 | 0 | 0 | 17 | 9 | 0 | 320 | 0 | 7 | 0 | 0 | 0 | 17 | 5 | 50 | 17 | 230 | 0 | 0 | 320 | 6 | 611 | 0 | 0 | 22 |  | 913 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 0 | 720 | 180 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 757 | 5 | 150 | 922 | 30 | 0 | 0 | 12 |  | 5582 | 4729 | 10311 | 3605 | 913 | 1477 | 0 | 357 | 3543 | 202 | 0 | 16 | 70 | 122 | 6 | 84.995 | 96.03
9:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 330 | 124 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 24 | 15 | 8 | 0 | 123 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 190 | 0 | 50 | 30 | 43 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 17 | 72 | 185 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 20 | 0 | 0 | 0 | 265 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 78 | 14 | 0 | 51 | 0 | 302 | 8 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 15 | 0 | 320 | 0 | 5 | 0 | 0 | 0 | 17 | 6 | 50 | 17 | 230 | 0 | 0 | 320 | 8 | 727 | 0 | 0 | 29 |  | 915 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 0 | 680 | 180 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 758 | 10 | 150 | 917 | 85 | 0 | 0 | 7 |  | 5682 | 4726 | 10408 | 3596 | 915 | 1438 | 0 | 363 | 3615 | 203 | 0 | 16 | 72 | 182 | 8 | 78.31 | 96.06
10:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 330 | 129 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 24 | 15 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 190 | 0 | 50 | 30 | 42 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 72 | 188 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 20 | 0 | 0 | 0 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 20 | 0 | 34 | 0 | 302 | 8 | 17 | 0 | 2 | 0 | 0 | 0 | 17 | 14 | 0 | 315 | 0 | 5 | 0 | 0 | 0 | 0 | 15 | 51 | 0 | 230 | 0 | 0 | 320 | 21 | 635 | 0 | 0 | 36 |  | 914 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 49 | 0 | 1 | 0 | 620 | 220 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 758 | 11 | 150 | 922 | 117 | 0 | 0 | 14 |  | 5578 | 4739 | 10317 | 3532 | 914 | 1495 | 0 | 282 | 3466 | 205 | 0 | 16 | 72 | 314 | 21 | 0 | 96.09
11:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 330 | 136 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 16 | 15 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 285 | 270 | 190 | 0 | 70 | 33 | 41 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 74 | 193 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 20 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 8 | 0 | 17 | 0 | 302 | 0 | 17 | 0 | 5 | 0 | 0 | 0 | 17 | 9 | 0 | 320 | 0 | 26 | 0 | 0 | 0 | 0 | 22 | 32 | 0 | 230 | 0 | 0 | 325 | 18 | 634 | 0 | 0 | 76 |  | 914 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 610 | 220 | 0 | 0 | 1 | 69 | 0 | 0 | 0 | 757 | 22 | 150 | 918 | 184 | 0 | 0 | 10 |  | 5632 | 4705 | 10337 | 3509 | 914 | 1501 | 0 | 219 | 3455 | 205 | 0 | 16 | 74 | 426 | 18 | 0 | 96.12
12:00 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 330 | 152 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 14 | 16 | 15 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 320 | 305 | 212 | 0 | 70 | 33 | 42 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 76 | 193 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 20 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 19 | 0 | 17 | 0 | 334 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 17 | 14 | 0 | 370 | 0 | 18 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 230 | 0 | 0 | 320 | 20 | 635 | 0 | 0 | 62 |  | 914 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 560 | 220 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 757 | 28 | 150 | 925 | 133 | 0 | 0 | 15 |  | 5824 | 4615 | 10439 | 3685 | 914 | 1573 | 0 | 224 | 3409 | 205 | 0 | 16 | 76 | 317 | 20 | 0 | 96.15
13:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 370 | 151 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 16 | 15 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 270 | 193 | 8 | 80 | 33 | 41 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 78 | 193 | 0 | 0 | 1 | 39 | 58 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 20 | 0 | 17 | 0 | 311 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 17 | 21 | 0 | 360 | 0 | 3 | 0 | 0 | 0 | 0 | 14 | 29 | 0 | 280 | 0 | 0 | 322 | 35 | 635 | 0 | 0 | 29 |  | 913 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 600 | 220 | 0 | 0 | 2 | 11 | 0 | 0 | 0 | 752 | 18 | 150 | 921 | 33 | 0 | 0 | 28 |  | 5995 | 4559 | 10554 | 3803 | 913 | 1669 | 0 | 228 | 3442 | 205 | 0 | 16 | 78 | 165 | 35 | 0 | 96.17
14:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 370 | 137 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 15 | 8 | 0 | 121 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 305 | 305 | 189 | 8 | 80 | 33 | 40 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 70 | 200 | 0 | 0 | 1 | 39 | 58 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 10 | 0 | 17 | 0 | 302 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 27 | 0 | 350 | 0 | 2 | 0 | 0 | 0 | 0 | 9 | 32 | 0 | 325 | 0 | 0 | 320 | 32 | 632 | 0 | 0 | 31 |  | 914 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 660 | 220 | 0 | 0 | 1 | 10 | 0 | 0 | 0 | 756 | 12 | 200 | 918 | 185 | 0 | 0 | 10 |  | 5980 | 4774 | 10754 | 3862 | 914 | 1601 | 0 | 237 | 3546 | 201 | 0 | 16 | 70 | 275 | 32 | 0 | 96.12
15:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 370 | 136 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 16 | 15 | 8 | 0 | 119 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 310 | 305 | 189 | 8 | 90 | 33 | 42 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 70 | 200 | 0 | 0 | 0 | 38 | 58 | 0 | 0 | 163 | 0 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 6 | 0 | 17 | 0 | 300 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 0 | 5 | 0 | 0 | 0 | 0 | 8 | 32 | 0 | 325 | 0 | 0 | 322 | 21 | 634 | 0 | 0 | 54 |  | 913 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 680 | 220 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 753 | 26 | 200 | 922 | 61 | 0 | 0 | 7 |  | 6001 | 4696 | 10697 | 3872 | 913 | 1619 | 0 | 238 | 3574 | 199 | 0 | 16 | 70 | 175 | 21 | 0 | 96.21
16:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 300 | 120 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 16 | 15 | 8 | 0 | 118 | 80 | 0 | 0 | 0 | 206 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 270 | 163 | 8 | 90 | 33 | 34 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 64 | 201 | 0 | 0 | 0 | 38 | 58 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 270 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1 | 0 | 17 | 0 | 288 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 28 | 0 | 360 | 0 | 5 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 300 | 0 | 0 | 322 | 14 | 630 | 0 | 0 | 33 |  | 913 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 520 | 220 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 726 | 13 | 150 | 815 | 40 | 0 | 0 | 1 |  | 5579 | 4206 | 9785 | 3593 | 913 | 1447 | 0 | 186 | 3226 | 198 | 0 | 16 | 64 | 128 | 14 | 0 | 96.23
17:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 304 | 0 |  | 0 | 280 | 120 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 8 | 8 | 0 | 71 | 40 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 280 | 250 | 162 | 0 | 90 | 20 | 10 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 60 | 140 | 0 | 0 | 0 | 38 | 58 | 0 | 0 | 120 | 0 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 260 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 115 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 6 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 230 | 0 | 0 | 320 | 9 | 580 | 0 | 0 | 20 |  | 913 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 500 | 180 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 740 | 6 | 140 | 819 | 41 | 0 | 0 | 0 |  | 4816 | 3931 | 8747 | 3081 | 913 | 1197 | 0 | 93 | 3161 | 111 | 0 | 16 | 60 | 106 | 9 | 0 | 96.26
18:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 304 | 0 |  | 0 | 280 | 120 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 8 | 0 | 0 | 100 | 50 | 0 | 0 | 0 | 187 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 250 | 162 | 0 | 90 | 20 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 56 | 140 | 0 | 0 | 0 | 30 | 58 | 0 | 0 | 110 | 0 | 20 | 0 | 0 | 65 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1 | 0 | 17 | 0 | 121 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 230 | 0 | 0 | 321 | 7 | 585 | 0 | 0 | 5 |  | 914 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 500 | 180 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 730 | 2 | 140 | 817 | 4 | 0 | 0 | 0 |  | 4767 | 3850 | 8617 | 3054 | 914 | 1171 | 0 | 75 | 3155 | 150 | 0 | 16 | 56 | 19 | 7 | 0 | 96.29
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 391 | 0 |  | 0 | 420 | 149 | 0 | 0 | 0 | 326 | 0 | 99 | 0 | 4 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 19 | 16 | 8 | 3 | 0 | 120 | 50 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 228 | 320 | 213 | 30 | 90 | 31 | 10 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 70 | 204 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 10 | 0 | 43 | 0 | 6 | 23 | 0 | 220 | 8 | 52 | 3 | 0 | 15 | 0 | 0 | 17 | 3 | 12 | 350 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 330 | 0 | 0 | 321 | 0 | 578 | 0 | 0 | 0 |  | 914 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 580 | 220 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 940 | 0 | 176 | 1013 | 0 | 0 | 0 | 0 |  | 6109 | 4748 | 10857 | 3964 | 914 | 1688 | 0 | 335 | 3668 | 170 | 0 | 48 | 70 | 0 | 0 | 0 | 96.38
19:30 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 375 | 0 |  | 0 | 420 | 147 | 0 | 0 | 0 | 328 | 0 | 99 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 14 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 320 | 213 | 55 | 90 | 31 | 30 | 0 | 20 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 72 | 203 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 12 | 68 | 0 | 270 | 45 | 52 | 17 | 0 | 30 | 0 | 0 | 17 | 27 | 12 | 347 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 295 | 0 | 0 | 339 | 1 | 574 | 0 | 0 | 0 |  | 915 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 880 | 220 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 964 | 0 | 230 | 1114 | 0 | 0 | 0 | 0 |  | 6279 | 5255 | 11534 | 3770 | 915 | 1716 | 0 | 651 | 4161 | 200 | 0 | 48 | 72 | 0 | 1 | 0 | 0
20:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 371 | 0 |  | 0 | 420 | 132 | 0 | 0 | 13 | 325 | 0 | 99 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 15 | 8 | 0 | 120 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 216 | 55 | 90 | 31 | 37 | 0 | 40 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 70 | 204 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 12 | 75 | 0 | 270 | 45 | 52 | 17 | 0 | 30 | 0 | 0 | 17 | 27 | 12 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 285 | 0 | 0 | 340 | 4 | 571 | 0 | 0 | 0 |  | 915 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 880 | 220 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 965 | 0 | 282 | 1124 | 0 | 0 | 0 | 0 |  | 6257 | 5355 | 11612 | 3732 | 915 | 1708 | 0 | 713 | 4222 | 200 | 0 | 48 | 70 | 0 | 4 | 0 | 96.35
21:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 420 | 160 | 0 | 0 | 30 | 325 | 0 | 100 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 8 | 8 | 0 | 121 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 217 | 55 | 85 | 33 | 47 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 74 | 202 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 32 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 12 | 100 | 0 | 270 | 47 | 52 | 17 | 0 | 30 | 0 | 0 | 17 | 27 | 12 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 340 | 9 | 573 | 0 | 0 | 0 |  | 915 | 0 | 369 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 970 | 0 | 307 | 1112 | 0 | 0 | 0 | 0 |  | 6365 | 5694 | 12059 | 3861 | 915 | 1872 | 0 | 816 | 4263 | 201 | 0 | 48 | 74 | 0 | 9 | 0 | 96.38
22:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 420 | 163 | 0 | 0 | 30 | 330 | 0 | 100 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 8 | 8 | 0 | 121 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 270 | 215 | 55 | 85 | 36 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 80 | 202 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 280 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 12 | 100 | 0 | 270 | 45 | 52 | 17 | 0 | 30 | 0 | 0 | 17 | 28 | 12 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 342 | 7 | 574 | 0 | 0 | 0 |  | 915 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 960 | 0 | 307 | 1125 | 0 | 0 | 0 | 0 |  | 6367 | 5652 | 12019 | 3936 | 915 | 1800 | 0 | 762 | 4270 | 201 | 0 | 48 | 80 | 0 | 7 | 0 | 96.41
23:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 298 | 0 | 0 | 30 | 330 | 0 | 100 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 6 | 8 | 0 | 121 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 270 | 217 | 55 | 85 | 36 | 49 | 0 | 51 | 0 | 0 | 9 | 0 | 0 | 0 | 18 | 82 | 198 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 12 | 107 | 0 | 270 | 45 | 35 | 17 | 0 | 30 | 0 | 0 | 34 | 31 | 12 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 342 | 5 | 573 | 0 | 0 | 0 |  | 913 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 962 | 0 | 307 | 1104 | 0 | 0 | 0 | 0 |  | 6530 | 5666 | 12196 | 4002 | 913 | 1922 | 0 | 773 | 4250 | 201 | 0 | 48 | 82 | 0 | 5 | 0 | 96.45
24:00 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 316 | 0 | 0 | 0 | 330 | 0 | 101 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 6 | 8 | 0 | 121 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 270 | 216 | 55 | 85 | 36 | 49 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 80 | 198 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 32 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 0 | 136 | 0 | 255 | 45 | 17 | 17 | 0 | 15 | 0 | 0 | 34 | 37 | 12 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 342 | 5 | 577 | 0 | 0 | 0 |  | 914 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 840 | 220 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 956 | 0 | 307 | 1109 | 0 | 0 | 0 | 0 |  | 6454 | 5639 | 12093 | 3989 | 914 | 1964 | 0 | 715 | 4193 | 201 | 0 | 32 | 80 | 0 | 5 | 0 | 96.49
KWH | 0 | 0 | 3439094 | 0 | 0 | 0 | 0 | 8589600 | 0 |  | 0 | 9082500 | 3552204 | 48960 | 46270 | 220909 | 6933248 | 0 | 614000 | 15360 | 62208 | 647520 | 0 | 0 | 0 | 0 | 23400 | 53189 | 52439 | 0 | 333600 | 512625 | 488600 | 291000 | 142080 | 0 | 2871704 | 1856000 | 0 | 0 | 0 | 5026327 | 0 | 0 | 0 |  | 45360 | 8800 | 0 | 0 | 16320 | 0 | 0 | 1054080 | 0 | 0 | 0 | 5875500 | 6704000 | 4851000 | 301090 | 1651860 | 766368 | 923040 | 0 | 595658 | 0 | 28352 | 191971 | 0 | 0 | 0 | 417010 | 1797120 | 4165440 | 0 | 0 | 3200 | 922000 | 1379520 | 0 | 0 | 3443727 | 0 | 483264 | 135360 | 0 | 2066550 | 0 | 0 | 0 | 7045000 | 266640 | 192384 | 0 | 55200 | 0 | 0 | 549600 | 0 | 1934208 | 105705 | 117120 | 1218720 | 3345 | 7265000 | 674400 | 576000 | 200727 | 20043 | 276000 | 0 | 38472 | 401280 | 434280 | 136320 | 8011500 | 242880 | 89340 | 41760 | 46418 | 0 | 172080 | 114789 | 1098240 | 297360 | 6322000 | 3345 | 0 | 7816362 | 316800 | 15905454 | 0 | 0 | 374273 |  | 22167127 | 0 | 7953408 | 0 | 35520 | 0 | 0 | 0 | 0 | 0 | 0 | 704000 | 187492 | 34272 | 0 | 0 | 0 | 0 | 0 | 4896 | 0 | 0 | 31396 | 0 | 0 | 0 | 0 | 87570 | 1435200 | 0 | 0 | 0 | 0 | 3937182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7681164 | 33600 | 0 | 0 | 0 | 1456617 | 0 | 33398 | 0 | 20431000 | 518895 | 0 | 0 | 9960 | 277200 | 498969 | 0 | 0 | 19381818 | 163190 | 4494500 | 23121819 | 0 | 0 | 2700 | 109500 |  | 145092472 | 114792393 | 259884865 | 90250290 | 22167127 | 34520210 | 0 | 11491854 | 92586153 | 4727704 | 0 | 724309 | 1797120 | 1303298 | 316800 | 0
Fuel Cost | 0 | 0 | 14753713.26 | 0 | 0 | 0 | 0 | 24738048 | 0 |  | 0 | 28882350 | 12148537.68 | 967449.6 | 865249 | 3892416.58 | 21146406.4 | 0 | 3284900 | 303513.6 | 1116633.6 | 12574838.4 | 0 | 0 | 0 | 0 | 427284 | 838258.64 | 959109.31 | 0 | 250200 | 0 | 0 | 0 | 2544652.8 | 0 | 0 | 0 | 0 | 0 | 0 | 16033983.13 | 0 | 0 | 0 |  | 797882.4 | 154968 | 0 | 0 | 319382.4 | 0 | 0 | 0 | 0 | 0 | 0 | 16392645 | 20514240 | 16105320 | 1008651.5 | 5335507.8 | 2582660.16 | 4042915.2 | 0 | 2388588.58 | 0 | 507784.32 | 3466996.26 | 0 | 0 | 0 | 312757.5 | 11789107.2 | 12954518.4 | 0 | 0 | 0 | 3595800 | 5145609.6 | 0 | 0 | 11777546.34 | 0 | 2682115.2 | 706579.2 | 0 | 5765674.5 | 0 | 0 | 0 | 21769050 | 199980 | 146211.84 | 0 | 1126080 | 0 | 0 | 10557816 | 0 | 34061402.88 | 0 | 2085907.2 | 21144792 | 55460.1 | 19252250 | 12854064 | 10805760 | 3601042.38 | 0 | 4512600 | 0 | 690187.68 | 7668460.8 | 8429374.8 | 2427859.2 | 21310590 | 4145961.6 | 0 | 763790.4 | 778894.04 | 0 | 3075069.6 | 0 | 19790284.8 | 5037278.4 | 18776340 | 47097.6 | 0 | 54480043.14 | 0 | 93842178.6 | 0 | 0 | 0 |  | 62289626.87 | 0 | 23462553.6 | 0 | 616272 | 0 | 0 | 0 | 0 | 0 | 0 | 2224640 | 888712.08 | 590849.28 | 0 | 0 | 0 | 0 | 0 | 82301.76 | 0 | 0 | 562302.36 | 0 | 0 | 0 | 0 | 66290.49 | 15830256 | 0 | 0 | 0 | 0 | 12992700.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22428998.88 | 573888 | 0 | 0 | 0 | 29015810.64 | 0 | 0 | 0 | 132392880 | 1613763.45 | 0 | 0 | 0 | 0 | 8657112.15 | 0 | 0 | 141487271.4 | 0 | 33484025 | 152835223.59 | 0 | 0 | 0 | 0 |  | 657510620.62 | 642095478.15 | 1299606098.77 | 270025655.48 | 62289626.87 | 107655692.91 | 0 | 209564846.14 | 624351877.73 | 0 | 0 | 13929292.44 | 11789107.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 330 | 152 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 14 | 16 | 15 | 8 | 0 | 125 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 320 | 305 | 212 | 0 | 70 | 33 | 42 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 76 | 193 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 20 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 19 | 0 | 17 | 0 | 334 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 17 | 14 | 0 | 370 | 0 | 18 | 0 | 0 | 0 | 0 | 15 | 32 | 0 | 230 | 0 | 0 | 320 | 20 | 635 | 0 | 0 | 62 |  | 914 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 560 | 220 | 0 | 0 | 1 | 20 | 0 | 0 | 0 | 757 | 28 | 150 | 925 | 133 | 0 | 0 | 15 |  | 10439 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 373 | 0 |  | 0 | 420 | 160 | 0 | 0 | 30 | 325 | 0 | 100 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 8 | 8 | 0 | 121 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 217 | 55 | 85 | 33 | 47 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 74 | 202 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 32 | 0 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 88 | 0 | 12 | 100 | 0 | 270 | 47 | 52 | 17 | 0 | 30 | 0 | 0 | 17 | 27 | 12 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 285 | 0 | 0 | 340 | 9 | 573 | 0 | 0 | 0 |  | 915 | 0 | 369 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 900 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 970 | 0 | 307 | 1112 | 0 | 0 | 0 | 0 |  | 12059 | EvPeak
Forecast for Evening | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 320 | 8 | 85 | 55 | 330 | 0 | 100 | 9 | 8 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 15 | 23 | 24 | 10 | 8 | 0 | 122 | 80 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 72 | 80 | 25 | 30 | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 300 | 210 | 100 | 95 | 30 | 45 | 0 | 43 | 0 | 35 | 8 | 0 | 0 |  | 18 | 100 | 200 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 280 | 0 | 0 | 122 | 0 | 149 | 0 | 24 | 100 | 138 | 360 | 79 | 52 | 105 | 0 | 50 | 54 | 85 | 17 | 60 | 25 | 380 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 68 | 35 | 300 | 163 | 0 | 340 | 60 | 360 | 0 | 0 |  |  | 918 | 0 | 300 | 0 | 64 | 0 | 0 | 0 | 40 | 55 | 16 | 65 | 10 | 64 | 0 | 0 | 0 | 40 | 20 | 85 | 35 | 0 | 46 | 0 | 30 | 0 | 0 | 5 | 65 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 85 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 90 | 0 | 0 | 115 | 0 | 0 | 900 | 0 | 307 | 1480 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 320 | 8 | 85 | 55 | 330 | 0 | 100 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 35 | 0 | 15 | 23 | 24 | 10 | 8 | 0 | 120 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 16 | 51 | 25 | 25 | 6 | 0 | 25 | 0 | 0 | 0 | 0 | 300 | 200 | 100 | 95 | 30 | 45 | 0 | 43 | 0 | 33 | 8 | 0 | 0 |  | 18 | 90 | 200 | 0 | 0 | 1.6 | 40 | 58 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 72 | 20 | 12 | 70 | 55 | 340 | 68 | 17 | 105 | 5 | 50 | 17 | 51 | 17 | 28 | 25 | 350 | 17 | 50 | 54 | 17 | 0 | 17 | 35 | 68 | 17 | 300 | 17 | 0 | 340 | 42 | 360 | 0 | 0 | 70 |  | 918 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 16 | 65 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 64 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 70 | 0 | 106 | 0 | 8 | 70 | 1000 | 220 |  | 17 | 6 | 100 | 35 | 0 | 0 | 900 | 30 | 250 | 1200 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 330 | 315 | 0 | 0 | 0 | 290 | 0 | 38 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 16 | 6 | 8 | 0 | 123 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 285 | 216 | 55 | 95 | 35 | 49 | 0 | 5 | 0 | 0 | 7 | 0 | 0 | 0 | 18 | 62 | 198 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 31 | 0 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 71 | 0 | 0 | 68 | 0 | 259 | 16 | 17 | 0 | 3 | 0 | 0 | 0 | 17 | 11 | 0 | 360 | 0 | 25 | 0 | 0 | 0 | 0 | 14 | 32 | 0 | 300 | 0 | 0 | 340 | 1 | 575 | 0 | 0 | 8 | 0 | 913 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 180 | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 765 | 5 | 150 | 822 | 28 | 0 | 0 | 19 | 0 |  |  |  | 124770500 | 22167127 | 0 | 92586153 | 12216163 | 1797120 | 1303298 | 316800 | 4727704 |  |  | 259884865
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 124.7705 | 22.1671 | 0 | 92.5862 | 12.2162 | 1.7971 | 1.3033 | 0.3168 | 4.7277
| Minimum Generation |  | 10311 | 8:00
| Highest Generation |  | 12393 | 1:00 | [129 empty] | 0 | [73 empty] | 259.8849
| Day Peak Generation |  | 10439 | 12:00
| Evening Peak Generation |  | 12059 | 21:00 | [203 empty] | 202699852
| HVDC Max Flow |  | 915 | 1:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 915 | 21:00
| Load factor L.F |  | 87.38% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-06
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10439 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9991
Evening Peak Generation : |  |  | 12059 | MW Hour : | 21:00 | Available Max Generation : |  | 15856
E.P. Demand (at gen end) : |  |  | 12059 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 12393 | MW Hour : | 1:00 | Reserve(Generation end) |  | 1856
Total Gen. (MKWH) : |  |  | 259.8849 | System Load Factor : | 87.38% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 450 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-06
Actual : |  | 96.67 | Ft.(MSL) , | Rule curve : | 90.28 | Ft.( MSL )
Gas Consumed : |  | Total = | 967.73 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 377681348.39
: |  |  | Coal : | 624351877.73 | Oil : | 223494138.58 | Total : | 1225527364.7
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4695.4665 |  |  | 0 | -14.58%
Chittagong Area |  | 0 | 0:00 | 1291.088 |  |  | 0 | -12.74%
Khulna Area |  | 0 | 0:00 | 1808.7915 |  |  | 0 | -12.35%
Rajshahi Area |  | 0 | 0:00 | 1572.379 |  |  | 0 | -11.93%
Cumilla Area |  | 0 | 0:00 | 1293.6804 |  |  | 0 | -12.19%
Mymensingh Area |  | 0 | 0:00 | 962.2882 |  |  | 0 | -11.83%
Sylhet Area |  | 0 | 0:00 | 539.2681 |  |  | 0 | -12.52%
Barisal Area |  | 0 | 0:00 | 449.5289 |  |  | 0 | -11.76%
Rangpur Area |  | 0 | 0:00 | 879.1971 |  |  | 0 | -11.77%
Total |  | 0 |  | 13491.6877 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
9:10 | 17:18 | Srinagar 132/33kV S/S Tr-02 LT Scheduled S/D Due to ১৩২/৩৩ কেভি ট্রান্সফরমার-২ এবং ইনকামার বে-২ এর বিভিন্ন জাংশন
পয়েন্টে রেডহট হওয়ায় সাটডাউন গ্রহণ।
9:10 | 17:16 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to ১৩২/৩৩ কেভি ট্রান্সফরমার-২ এবং ইনকামার বে-২ এর বিভিন্ন জাংশন
পয়েন্টে রেডহট হওয়ায় সাটডাউন গ্রহণ।
19:29 | - | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- gt
- | 10:08 | Barguna 132/33kV S/S Transformer-1 HT is restored.
10:42 | - | Chauddagram-Feni 132 kV Ckt-1 Forced S/D from Feni 132/33kV end Due to Emergency Shutdown for Kite in line.
12:00 | - | Day peak Generation :10440 MW
15:15 | 19:33 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Backup protection relays.
15:53 | 19:40 | Madanganj 132/33kV S/S GT-2 LT Tripped showing Phase instantaneous fault relays Due to Due to 33 kv PBS T2 feeder fault
20:40 | - | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- GT-2 synch as per NLDC demand
20:40 | - | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT2
7:00 | - | Min. Gen. 9992 MW
18:02 | - | Siddhirgonj 2*120 MW GTPP Synchronized with remarks:- GT-1
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-05
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 3439094
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 373 | 8589600
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9082500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 48960 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 160 | 3552204 | Unit-2 Under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 46270 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 220909 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 100 | 614000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 15360 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 6933248
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 62208 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 23400 | Reserve
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 647520 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 53189 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 52439 | Reserve
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 35 | 846225 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 488600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 8 | 291000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 142080 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 55200 | Reserve
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 1934208 | Low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 576000 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 242880 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 41760 | Reserve
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 114789
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 297360 | Reserve
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 1888 | 38411003
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 105705
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 201 | 4727704
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5026327
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 200727 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 8800 | Reserve
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Reserve
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 117120 | Low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1054080
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 16320 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20043
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 276000 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 38472 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 136320 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 46418 | Reserve
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 3345 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 340 | 7816362 | Unit-1 Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 9 | 316800
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 573 | 15905454
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 1458 | 35815997
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 4851000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 5875500
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6704000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 285 | 6322000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 766368 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 47 | 923040 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 301090 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 595658
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 3345 | Reserve
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 28352 | Reserve
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 1651860 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 100 | 1218720 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 74 | 1797120
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 191971 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 417010 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 401280 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 434280 | Low demand
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 65 | 1098240 | Low demand
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 374273
| Cumilla Area Total |  |  |  | 2950 | 1382 | 33955107
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 202 | 4165440
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3200
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 35 | 549600 | Low demand
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 674400 | Low demand
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 89340
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 45360 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 172080 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 290 | 5699420
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 39 | 922000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1379520 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3443727
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 483264 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 0 | 135360 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 2066550 | ST Under maint
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 266640 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7045000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 270 | 7265000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8011500 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1347 | 31210945
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 915 | 22167127
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 35520 | Low demand
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 369 | 7953408 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 33600 | Reserve
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 277200
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 970 | 19381818
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 2270 | 49848673
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 34272 | Reserve
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 187492
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 704000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 20431000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 518895
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 4494500
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 2700
| Barisal Area Total |  |  |  | 2236 | 1437 | 26372859
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 31396 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 174 | 3937182 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7681164
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 87570 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 4896 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 9960
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1112 | 23121819
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 109500
| Rajshahi Area Total |  |  |  | 3381 | 1705 | 34983487
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1435200
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1456617 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33398
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 498969
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 163190
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 0
| Rangpur Area Total |  |  |  | 950 | 282 | 3587374
| Total |  |  |  | 26947 | 12059 | 259884865
| Eastern Grid Total |  |  |  | 16526 | 6365 | 145092472
| Western Grid Total |  |  |  | 10421 | 5694 | 114792393
| National Grid Total |  |  |  | 26947 | 12059 | 259884865
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-08-05 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7457.97 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4067.4 | MW
i) Dhaka area |  |  | 3627.97 |  | MW | i) Khulna area |  |  |  | 1502.9 | MW
ii) Chattogram area |  |  | 1008 |  | MW | ii) Barishal area |  |  |  | 398.5 | MW
iii) Cumilla area |  |  | 1254 |  | MW | iii) Rajshahi area |  |  |  | 1256 | MW
iv) Mymensingh area |  |  | 1035 |  | MW | iv) Rangpur area |  |  |  | 910 | MW
v) Sylhet area |  |  | 533 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11525.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 20:00 | 67 | Jamalpur | 127 | 00:00 | 133 | Rahim | 0 | 00:00
2 | AKSML | 75 | 12:00 | 68 | Jashore | 123 | 00:00 | 134 | Rajbari | 68 | 21:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jhenaidah | 117 | 00:00 | 135 | Rajendrapur | 78 | 00:00
4 | Agargaon | 85 | 00:00 | 70 | Joydebpur | 123 | 20:00 | 136 | Rajshahi | 104 | 00:00
5 | Agrabad | 70 | 00:00 | 71 | Joypurhat | 61 | 00:00 | 137 | Rajshahi-230 | 63 | 23:00
6 | Amnura | 65 | 00:00 | 72 | Juldah | 15 | 00:00 | 138 | Ramganj | 116 | 23:00
7 | Ashuganj | 82 | 01:00 | 73 | KSRM | 13 | 00:00 | 139 | Rampur | 37 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 172 | 19:30 | 140 | Rangamati | 17 | 19:00
9 | BSRM | 176 | 00:00 | 75 | Kachua | 72 | 21:00 | 141 | Rangpur | 131 | 19:30
10 | Bagerhat | 79 | 00:00 | 76 | Kallyanpur | 96 | 00:00 | 142 | Ruppur | 6.8 | 16:00
11 | Bakulia | 76 | 00:00 | 77 | Kalurghat | 22 | 00:00 | 143 | SSM | 2 | 01:00
12 | Banani | 32 | 19:00 | 78 | Kamrangirchar | 45.2 | 13:00 | 144 | Saidpur | 100 | 21:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 112 | 20:00
14 | Barapukuria | 60 | 21:00 | 80 | Kazla | 71 | 00:00 | 146 | Satmasjid | 90 | 14:00
15 | Barguna | 19 | 00:00 | 81 | Keranigonj | 76 | 14:00 | 147 | Savar | 152 | 00:00
16 | Barishal | 103 | 12:00 | 82 | Khagrachori | 26 | 14:00 | 148 | SevenRings | 11.25 | 00:00
17 | Barishal-230 | 74 | 00:00 | 83 | Khulna | 54 | 00:00 | 149 | ShahCement | 16 | 00:00
18 | Baroaulia | 52 | 00:00 | 84 | Khulshi | 84 | 00:00 | 150 | Shahjadpur | 68 | 21:00
19 | Baroirhat | 53 | 00:00 | 85 | Kishoreganj | 154 | 21:00 | 151 | Shahjibazar | 127 | 00:00
20 | Bashundhara | 127 | 00:00 | 86 | Kodda | 181 | 00:00 | 152 | Shahmirpur | 41 | 02:00
21 | BashundharaCement | 1 | 00:00 | 87 | Kulaura | 48 | 00:00 | 153 | Shariatpur | 86 | 22:00
22 | Beanibazar | 72 | 00:00 | 88 | Kurigram | 62 | 20:00 | 154 | Sherpur | 128 | 00:00
23 | Benapole | 58 | 00:00 | 89 | Kushtia | 112 | 00:00 | 155 | Shikalbaha | 19 | 00:00
24 | Bhaluka | 110 | 21:00 | 90 | Lalbag | 70 | 00:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 49 | 01:00 | 91 | Lalmonirhat | 58 | 20:00 | 157 | Shitalakhya | 65 | 13:00
26 | Bhangura | 34 | 19:30 | 92 | MI_Cement | 9.9 | 04:00 | 158 | Sholosohor | 34 | 21:00
27 | Bheramara(GK) | 62 | 22:00 | 93 | Madanganj | 27 | 01:00 | 159 | Shyampur | 146 | 00:00
28 | Bhulta | 215 | 00:00 | 94 | Madaripur | 101 | 22:00 | 160 | Siddhirganj | 92 | 00:00
29 | Bog-Sherpur | 56 | 00:00 | 95 | Madartek | 83.11 | 00:00 | 161 | Sirajganj | 88 | 21:00
30 | Bogura | 123 | 00:00 | 96 | Madunaghat | 45 | 01:00 | 162 | Sonargaon | 66 | 00:00
31 | Borhanuddin | 82 | 00:00 | 97 | Magura | 58 | 00:00 | 163 | Sreemongol | 69 | 00:00
32 | Brahmanbaria | 176 | 22:00 | 98 | Mahasthangarh | 62 | 01:00 | 164 | Sreepur | 60 | 00:00
33 | Cantonment | 88 | 13:00 | 99 | Manikganj | 78 | 21:00 | 165 | Srinagar | 62.4 | 11:00
34 | Chandpur | 66 | 23:00 | 100 | Maniknagar | 43 | 13:00 | 166 | Sunamganj | 58 | 00:00
35 | Chandraghona | 34 | 19:00 | 101 | Matarbari | 42 | 19:00 | 167 | Sylhet | 40 | 00:00
36 | Chapai | 63 | 21:00 | 102 | Matuail | 54 | 00:00 | 168 | Sylhet-132 | 100 | 00:00
37 | Charsaidpur | 21 | 10:00 | 103 | Millgate | 77 | 00:00 | 169 | TK | 30 | 22:00
38 | Chauddagram | 67 | 23:00 | 104 | Mirpur | 112 | 23:00 | 170 | Tangail | 182 | 00:00
39 | Chhatak | 31 | 22:00 | 105 | Mirsorai | 8 | 00:00 | 171 | Thakurgaon | 99 | 23:00
40 | Chowmuhani | 194 | 22:00 | 106 | Mirzapur | 38 | 00:00 | 172 | Tongi | 79 | 00:00
41 | Chuadanga | 100 | 22:00 | 107 | Mithapukur | 58 | 21:00 | 173 | Ullahpara | 24 | 19:00
42 | Coxsbazar | 107 | 20:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 49 | 00:00
43 | Cumilla(N) | 153 | 00:00 | 109 | Mogbazar | 77.8 | 00:00 | 175 | Uttara | 56 | 00:00
44 | Cumilla(S) | 150 | 00:00 | 110 | Mongla | 24 | 02:00 | 176 | UttaraNew | 47 | 00:00
45 | Daudkandi | 150 | 00:00 | 111 | Motijheel | 27 | 00:00 | 177 | Zigatola | 66 | 00:00
46 | Dhaka | 20 | 11:00 | 112 | Munshiganj | 103 | 00:00
47 | Dhamrai | 106 | 00:00 | 113 | Mymensingh | 213 | 00:00
48 | Dhanmondi | 69.5 | 00:00 | 114 | Naogaon | 117 | 00:00
49 | Dohazari | 84 | 00:00 | 115 | Narail | 52 | 00:00
50 | Faridpur | 149 | 21:00 | 116 | Narinda | 43.5 | 13:00
51 | Fatullah | 59 | 00:00 | 117 | Narshingdi | 168 | 20:00
52 | Fenchuganj | 38 | 00:00 | 118 | Natore | 133 | 23:00
53 | Feni | 97 | 22:00 | 119 | Nawabganj | 46.73 | 22:00
54 | GPH | 83 | 08:00 | 120 | Netrakona | 119 | 01:00
55 | Ghatail | 70 | 00:00 | 121 | New | 35.8 | 00:00
56 | Ghorashal | 53 | 00:00 | 122 | Niamatpur | 74 | 00:00
57 | Goalpara | 36 | 12:00 | 123 | Noapara | 52 | 22:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 395 | 18:00 | 382 | 00:00 | Kaliakoir | 383 | 17:00 | 372 | 01:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Bhulta | 406 | 16:00 | 393 | 22:00 | Meghnaghat | 391 | 17:00 | 378 | 00:00
| Bibiana | 401 | 09:00 | 293 | 22:00 | Payra | 414 | 16:00 | 405 | 02:00
| BIPTC | 400 | 06:00 | 393 | 22:00 | Rahanpur | 410 | 18:00 | 390 | 00:00
| Bogura | 400 | 17:00 | 376 | 00:00 | Rampal | 408 | 18:00 | 394 | 00:00
| Gopalganj | 405 | 18:00 | 391 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 18:00 | 227 | 00:00 | Haripur | 236 | 17:00 | 228 | 00:00
| AKSML | 235 | 08:00 | 229 | 14:00 | Hasnabad | 236 | 18:00 | 228 | 00:00
| Aminbazar | 235 | 16:00 | 227 | 00:00 | Hathazari | 236 | 06:00 | 232 | 13:00
| Ashuganj | 238 | 16:00 | 230 | 00:00 | Ishurdi | 237 | 16:00 | 224 | 22:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Jhenaidah | 229 | 16:00 | 215 | 22:00
| Baghabari | 233 | 15:00 | 223 | 00:00 | Kaliakoir | 239 | 18:00 | 231 | 00:00
| Barapukuria | 217 | 18:00 | 200 | 00:00 | Keranigonj | 235 | 18:00 | 226 | 01:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Khulna(S) | 233 | 16:00 | 220 | 22:00
| Barishal | 238 | 18:00 | 228 | 22:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bheramara | 235 | 16:00 | 222 | 22:00 | Maniknagar | 237 | 18:00 | 229 | 00:00
| Bhulta | 238 | 16:00 | 230 | 01:00 | Meghnaghat | 243 | 16:00 | 235 | 00:00
| Bibiana | 230 | 09:00 | 222 | 00:00 | Meghnaghat-400 | 239 | 17:00 | 231 | 00:00
| BIPTC | 236 | 16:00 | 222 | 20:00 | Mirsorai | 233 | 16:00 | 226 | 02:00
| Bogura | 230 | 18:00 | 215 | 00:00 | Rajshahi | 234 | 11:00 | 220 | 22:00
| Bogura-400 | 230 | 17:00 | 215 | 00:00 | Rampal | 233 | 18:00 | 222 | 00:00
| Borhanuddin | 240 | 16:00 | 234 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 234 | 16:00 | 227 | 00:00 | Rampura | 235 | 07:00 | 230 | 00:00
| Cumilla(N) | 232 | 18:00 | 224 | 00:00 | Shikalbaha | 233 | 07:00 | 230 | 01:00
| Faridpur | 238 | 16:00 | 229 | 22:00 | Shyampur | 236 | 18:00 | 228 | 00:00
| Fenchuganj | 231 | 08:00 | 224 | 02:00 | Siddhirganj | 235 | 05:00 | 231 | 00:00
| Ghorashal | 235 | 14:00 | 225 | 00:00 | Sirajgonj | 239 | 18:00 | 230 | 00:00
| Ghorashal-230 | 236 | 16:00 | 227 | 01:00 | Sreepur | 234 | 17:00 | 223 | 00:00
| Gopalganj | 238 | 15:00 | 230 | 00:00 | Tongi | 237 | 15:00 | 227 | 00:00
| GPH | 234 | 16:00 | 229 | 03:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 06:00 | 133 | 10:00 | Kushtia | 138 | 16:00 | 130 | 22:00
| Agargaon | 140 | 16:00 | 133 | 22:00 | Lalbag | 137 | 16:00 | 132 | 00:00
| Agrabad | 135 | 16:00 | 131 | 14:00 | Lalmonirhat | 127 | 17:00 | 118 | 00:00
| AKS | 133 | 00:00 | 130 | 06:00 | Madanganj | 135 | 18:00 | 130 | 01:00
| Aminbazar | 141 | 16:00 | 131 | 00:00 | Madaripur | 135 | 16:00 | 129 | 00:00
| Amnura | 136 | 09:00 | 125 | 00:00 | Madartek | 138 | 16:00 | 133 | 01:00
| Ashuganj | 140 | 09:00 | 137 | 00:00 | Madunaghat | 135 | 16:00 | 130 | 23:00
| Bagerhat | 136 | 16:00 | 123 | 23:00 | Magura | 139 | 18:00 | 127 | 22:00
| Bakulia | 134 | 07:00 | 130 | 22:00 | Mahasthangarh | 135 | 18:00 | 124 | 00:00
| Banani | 138 | 11:00 | 132 | 21:00 | Manikganj | 134 | 17:00 | 127 | 00:00
| Bangabhaban | 135 | 16:00 | 130 | 00:00 | Maniknagar | 135 | 16:00 | 10 | 01:00
| Barapukuria | 134 | 18:00 | 122 | 00:00 | Matarbari | 127 | 16:00 | 118 | 19:30
| Barguna | 135 | 18:00 | 129 | 00:00 | Matuail | 135.7 | 18:00 | 130 | 01:00
| Barishal | 140 | 17:00 | 133 | 00:00 | Millgate | 140 | 17:00 | 132 | 00:00
| Barishal-230 | 141 | 18:00 | 134 | 00:00 | Mirpur | 140 | 18:00 | 134 | 00:00
| Baroaulia | 135 | 04:00 | 132 | 14:00 | Mirzapur | 131 | 09:00 | 126 | 00:00
| Baroirhat | 128 | 06:00 | 118 | 22:00 | Mithapukur | 131 | 18:00 | 121 | 00:00
| Bashundhara | 140 | 16:00 | 132 | 01:00 | MI_Cement | 136 | 18:00 | 131 | 02:00
| BashundharaCement | 135 | 18:30 | 130 | 01:00 | Modern | 135 | 17:00 | 131 | 23:00
| Beanibazar | 125 | 16:00 | 118 | 00:00 | Mogbazar | 138 | 06:00 | 133 | 18:30
| Benapole | 136 | 18:00 | 123 | 22:00 | Mongla | 136 | 18:00 | 123 | 00:00
| Bhaluka | 131 | 14:00 | 121 | 00:00 | Motijheel | 135 | 18:00 | 130 | 00:00
| Bhandaria | 137 | 18:00 | 127 | 00:00 | Munshiganj | 135 | 16:00 | 130 | 06:00
| Bhangura | 138 | 16:00 | 131 | 00:00 | Mymensingh | 131 | 20:00 | 118 | 00:00
| Bheramara | 137 | 16:00 | 131 | 00:00 | Naogaon | 135 | 16:00 | 122 | 00:00
| Bheramara(GK) | 138 | 16:00 | 131 | 22:00 | Narail | 138 | 16:00 | 126 | 00:00
| Bhulta | 129 | 16:00 | 120 | 00:00 | Narinda | 135 | 16:00 | 10 | 01:00
| Bog-Sherpur | 136 | 17:00 | 127 | 00:00 | Narshingdi | 129 | 17:00 | 120 | 00:00
| Bogura | 138 | 17:00 | 127 | 00:00 | Natore | 136 | 17:00 | 127 | 22:00
| Bogura-230 | 138 | 18:00 | 127 | 00:00 | Nawabganj | 137 | 17:00 | 131 | 00:00
| Brahmanbaria | 132 | 08:00 | 123 | 00:00 | Netrakona | 130 | 06:00 | 124 | 04:00
| Cantonment | 167 | 14:00 | 133 | 22:00 | New | 140 | 18:00 | 133 | 00:00
| Chandpur | 127 | 09:00 | 120 | 15:00 | Niamatpur | 138 | 17:00 | 130 | 00:00
| Chandraghona | 136 | 09:00 | 133 | 04:00 | Noapara | 137 | 18:00 | 19 | 19:30
| Chapai | 136 | 18:00 | 126 | 00:00 | Pabna | 136 | 16:00 | 129 | 22:00
| Charsaidpur | 136 | 18:00 | 131 | 00:00 | Palashbari | 130 | 18:00 | 118 | 00:00
| Chauddagram | 129 | 00:00 | 119 | 22:00 | Panchagarh | 133 | 18:00 | 113 | 00:00
| Chhatak | 126 | 16:00 | 119 | 00:00 | Patuakhali | 134 | 16:00 | 130 | 00:00
| Chowmuhani | 121 | 09:00 | 113 | 18:00 | Payra | 136 | 17:00 | 133 | 00:00
| Chuadanga | 135 | 17:00 | 122 | 00:00 | PHP | 128 | 06:00 | 117 | 22:00
| Coxsbazar | 127 | 09:00 | 119 | 19:00 | Postogola | 139 | 18:00 | 134 | 00:00
| Cumilla(N) | 134 | 09:00 | 127 | 00:00 | Purbachal | 139 | 18:00 | 133 | 00:00
| Cumilla(S) | 131 | 09:00 | 125 | 00:00 | Purbasadipur | 129 | 18:00 | 112 | 00:00
| Daudkandi | 126 | 18:00 | 118 | 01:00 | Rahanpur | 139 | 18:00 | 132 | 00:00
| Dhaka | 138 | 08:00 | 133 | 22:00 | Rahim | 1320 | 03:00 | 130 | 00:00
| Dhamrai | 137 | 17:00 | 131 | 00:00 | Rajbari | 134 | 16:00 | 128 | 00:00
| Dhanmondi | 135 | 16:00 | 130 | 01:00 | Rajendrapur | 136 | 19:30 | 131 | 01:00
| Dohazari | 132 | 16:00 | 126 | 03:00 | Rajshahi | 136 | 17:00 | 127 | 22:00
| Faridpur | 134 | 16:00 | 128 | 00:00 | Rajshahi-230 | 136 | 16:00 | 122 | 00:00
| Fatullah | 137 | 17:00 | 132 | 00:00 | Ramganj | 123 | 09:00 | 114 | 15:00
| Fenchuganj | 134 | 17:00 | 128 | 02:00 | Rampur | 135 | 00:00 | 130 | 23:00
| Feni | 124 | 09:00 | 116 | 22:00 | Rampura | 138 | 16:00 | 132 | 22:00
| Ghatail | 130 | 09:00 | 125 | 00:00 | Rangamati | 135 | 17:00 | 132 | 13:00
| Ghorashal | 139 | 05:00 | 136 | 00:00 | Rangpur | 129 | 18:00 | 118 | 00:00
| Goalpara | 139 | 18:00 | 129 | 22:00 | Ruppur | 138 | 16:00 | 131 | 22:00
| Gollamari | 138 | 16:00 | 129 | 22:00 | Saidpur | 130 | 18:00 | 118 | 13:00
| Gopalganj | 136 | 18:00 | 127 | 22:00 | Satkhira | 137 | 18:00 | 123 | 00:00
| Gopalganj-400 | 135 | 16:00 | 130 | 00:00 | Satmasjid | 140 | 16:00 | 133 | 21:00
| Gulshan | 137 | 09:00 | 132 | 19:30 | Savar | 139 | 17:00 | 134 | 00:00
| Halishahar | 134 | 09:00 | 130 | 18:30 | SevenRings | 141 | 16:00 | 136 | 00:00
| Haripur | 134 | 16:00 | 130 | 00:00 | ShahCement | 136 | 18:00 | 130 | 03:00
| HaripurSBU | 134 | 18:00 | 130 | 00:00 | Shahjadpur | 140 | 15:00 | 134 | 22:00
| Hasnabad | 138 | 16:00 | 133 | 00:00 | Shahjibazar | 131 | 18:00 | 121 | 00:00
| Hathazari | 137 | 06:00 | 135 | 00:00 | Shahmirpur | 135 | 17:00 | 132 | 12:00
| Ishurdi | 139 | 16:00 | 132 | 00:00 | Shariatpur | 135 | 18:00 | 127 | 00:00
| Jaldhaka | 130 | 18:00 | 112 | 00:00 | Sherpur | 128 | 00:00 | 114 | 14:00
| Jamalpur | 131 | 00:00 | 119 | 13:00 | Shikalbaha | 124 | 07:00 | 121 | 00:00
| Jashore | 139 | 16:00 | 124 | 00:00 | Shikalbaha-230 | 135 | 07:00 | 131 | 22:00
| Jhenaidah | 140 | 17:00 | 129 | 22:00 | Shitalakhya | 136 | 18:00 | 131 | 03:00
| Jhenaidah-230 | 140 | 16:00 | 130 | 00:00 | Sholosohor | 134 | 08:00 | 131 | 03:00
| Joydebpur | 140 | 11:00 | 134 | 15:00 | Shyampur | 137 | 17:00 | 130 | 00:00
| Joypurhat | 134 | 18:00 | 119 | 00:00 | Shyampur-230 | 137 | 18:00 | 131 | 01:00
| Juldah | 134 | 07:00 | 131 | 21:00 | Siddhirganj | 135 | 18:00 | 130 | 00:00
| Kabirpur | 138 | 19:30 | 130 | 00:00 | Sirajganj | 136 | 16:00 | 127 | 22:00
| Kachua | 127 | 09:00 | 121 | 15:00 | Sonargaon | 133 | 17:00 | 126 | 01:00
| Kaliakoir | 139 | 17:00 | 131 | 00:00 | Sreemongol | 131 | 08:00 | 123 | 00:00
| Kallyanpur | 135 | 16:00 | 130 | 00:00 | Sreepur | 133 | 16:00 | 126 | 00:00
| Kalurghat | 136 | 10:00 | 132 | 00:00 | Srinagar | 136 | 16:00 | 132 | 01:00
| Kamrangirchar | 138 | 18:00 | 129 | 00:00 | SSM | 140 | 04:00 | 132 | 11:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 124 | 17:00 | 118 | 00:00
| Kazla | 134 | 17:00 | 130 | 00:00 | Sylhet | 128 | 17:00 | 123 | 00:00
| Keranigonj | 138 | 18:00 | 132 | 00:00 | Sylhet-132 | 127 | 08:00 | 124 | 00:00
| Khagrachori | 135 | 17:00 | 131 | 22:00 | Tangail | 130 | 09:00 | 123 | 22:00
| Khulna | 138 | 18:00 | 127 | 22:00 | Thakurgaon | 130 | 18:00 | 109 | 00:00
| Khulna(S) | 138 | 16:00 | 129 | 22:00 | TK | 135 | 07:00 | 131 | 22:00
| Khulshi | 133 | 08:00 | 130 | 23:00 | Tongi | 140 | 15:00 | 134 | 00:00
| Kishoreganj | 131 | 15:00 | 125 | 00:00 | Ullahpara | 138 | 17:00 | 130 | 22:00
| Kodda | 137 | 19:30 | 130 | 01:00 | Ullon | 137 | 06:00 | 132 | 22:00
| KSRM | 135 | 08:00 | 132 | 01:00 | Uttara | 141 | 15:00 | 135 | 01:00
| Kulaura | 132 | 10:00 | 127 | 00:00 | UttaraNew | 140 | 16:00 | 135 | 00:00
| Kurigram | 129 | 18:00 | 116 | 00:00 | Zigatola | 138 | 17:00 | 132 | 01:00

## L-Curve
Date | 2024-08-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 646 | 6454 | 5639 | 12093 |  |  |  | QF-LDC-11
0:30 | 705 | 6588.5 | 5654.5 | 12243 | Date: | 2024-08-05
1:00 | 764 | 6723 | 5670 | 12393
1:30 | 763 | 6610 | 5587 | 12197
2:00 | 762 | 6497 | 5504 | 12001
2:30 | 736 | 6414.5 | 5377 | 11791.5 | [5 empty] | Gen. at Eve. Peak | 12059 | 12059 MW (21:00 )
3:00 | 710 | 6332 | 5250 | 11582 | [6 empty] | 21:00
3:30 | 670 | 6278 | 5206.5 | 11484.5 | [5 empty] | Gen. at Day Peak | 10439 | 10439 MW (12:00 )
4:00 | 630 | 6224 | 5163 | 11387 | [6 empty] | 12:00
4:30 | 631 | 6228 | 5088 | 11316 | [5 empty] | Highest Generation | 12393
5:00 | 632 | 6232 | 5013 | 11245 | [6 empty] | 1:00
5:30 | 637 | 6033.5 | 4888.5 | 10922
6:00 | 642 | 5835 | 4764 | 10599
6:30 | 637 | 5755.5 | 4766 | 10521.5
7:00 | 632 | 5676 | 4768 | 10444
7:30 | 638 | 5629 | 4748.5 | 10377.5
8:00 | 644 | 5582 | 4729 | 10311
8:30 | 667 | 5632 | 4727.5 | 10359.5
9:00 | 690 | 5682 | 4726 | 10408
9:30 | 738 | 5630 | 4732.5 | 10362.5
10:00 | 786 | 5578 | 4739 | 10317
10:30 | 762 | 5605 | 4722 | 10327
11:00 | 738 | 5632 | 4705 | 10337
11:30 | 623 | 5728 | 4660 | 10388
12:00 | 508 | 5824 | 4615 | 10439
12:30 | 522 | 5909.5 | 4587 | 10496.5
13:00 | 536 | 5995 | 4559 | 10554
13:30 | 556 | 5987.5 | 4666.5 | 10654
14:00 | 576 | 5980 | 4774 | 10754
14:30 | 549 | 5990.5 | 4735 | 10725.5
15:00 | 522 | 6001 | 4696 | 10697
15:30 | 527 | 5790 | 4451 | 10241
16:00 | 532 | 5579 | 4206 | 9785
16:30 | 569 | 5197.5 | 4068.5 | 9266
17:00 | 606 | 4816 | 3931 | 8747
17:30 | 611 | 4791.5 | 3890.5 | 8682
18:00 | 616 | 4767 | 3850 | 8617
18:30 | 540 | 5438 | 4299 | 9737
19:00 | 464 | 6109 | 4748 | 10857
19:30 | 450 | 6279 | 5255 | 11534
20:00 | 472 | 6257 | 5355 | 11612 |  |  |  | Executive Engineer
20:30 | 556 | 6311 | 5524.5 | 11835.5 |  |  |  | Network Operation Division
21:00 | 640 | 6365 | 5694 | 12059
21:30 | 630 | 6366 | 5673 | 12039
22:00 | 620 | 6367 | 5652 | 12019 |  |  |  |  | Page 6 of 7
22:30 | 595 | 6448.5 | 5659 | 12107.5
23:00 | 570 | 6530 | 5666 | 12196
23:30 | 608 | 6492 | 5652.5 | 12144.5
24:00 | 646 | 6454 | 5639 | 12093
12059 MW (21:00 )
10439 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-05 |  | Energy |  | 259884865
[14 empty] | Date: | 2024-08-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3989 | 914 | 1964 | 0 | 715 | 4193 | 201 | 0 | 32 | 80 | 0 | 5 | 0
0:30 | 3910 | 914.5 | 1840 | 0 | 869 | 4345.5 | 200.5 | 0 | 72.5 | 84 | 0 | 7 | 156.1425 |  |  | Date: | 44047
1:00 | 3831 | 915 | 1716 | 0 | 1023 | 4498 | 200 | 0 | 113 | 88 | 0 | 9 | 312.285
1:30 | 3804.5 | 914.5 | 1683 | 0 | 959.5 | 4455 | 200 | 0 | 80.5 | 87 | 0 | 13 | 313.24 | [9 empty] | Total Energy | 259.8849 | 259.8849 | Total Energy Gen 259.885 MKWHr Energy Not Served 1.953 MKWHr Energy Requirement 261.838 MKWHr
2:00 | 3778 | 914 | 1650 | 0 | 896 | 4412 | 200 | 0 | 48 | 86 | 0 | 17 | 314.195 | [9 empty] | Energy not Served | 1.9528 | 1.9528
2:30 | 3854.5 | 914.5 | 1654.5 | 0 | 719 | 4315.5 | 200 | 0 | 32 | 86 | 0 | 15.5 | 308.9425 | [9 empty] | Energy Requirement | 261.8376 | 261.8376
3:00 | 3931 | 915 | 1659 | 0 | 542 | 4219 | 200 | 0 | 16 | 86 | 0 | 14 | 303.69
3:30 | 3902.5 | 915 | 1673 | 0 | 502.5 | 4173 | 200 | 0 | 16 | 89 | 0 | 13.5 | 301.3025 | [8 empty] | Shortage
4:00 | 3874 | 915 | 1687 | 0 | 463 | 4127 | 200 | 0 | 16 | 92 | 0 | 13 | 298.915
4:30 | 3882 | 914.5 | 1688 | 0 | 461.5 | 4053 | 200 | 0 | 16 | 89 | 0 | 12 | 295.095
5:00 | 3890 | 914 | 1689 | 0 | 460 | 3979 | 200 | 0 | 16 | 86 | 0 | 11 | 291.275
5:30 | 3781.5 | 914 | 1607.5 | 0 | 461 | 3837.5 | 200 | 0 | 16 | 82 | 9 | 13.5 | 270.265
6:00 | 3673 | 914 | 1526 | 0 | 462 | 3696 | 200 | 0 | 16 | 78 | 18 | 16 | 249.255
6:30 | 3649.5 | 914 | 1529 | 0 | 414 | 3657.5 | 201 | 0 | 16 | 78 | 50.5 | 12 | 175.2425 | [7 empty] | Coal
7:00 | 3626 | 914 | 1532 | 0 | 366 | 3619 | 202 | 0 | 16 | 78 | 83 | 8 | 101.23
7:30 | 3615.5 | 913.5 | 1504.5 | 0 | 361.5 | 3581 | 202 | 0 | 16 | 74 | 102.5 | 7 | 93.1125 | [6 empty] | Oil
8:00 | 3605 | 913 | 1477 | 0 | 357 | 3543 | 202 | 0 | 16 | 70 | 122 | 6 | 84.995
8:30 | 3600.5 | 914 | 1457.5 | 0 | 360 | 3579 | 202.5 | 0 | 16 | 71 | 152 | 7 | 81.6525
9:00 | 3596 | 915 | 1438 | 0 | 363 | 3615 | 203 | 0 | 16 | 72 | 182 | 8 | 78.31
9:30 | 3564 | 914.5 | 1466.5 | 0 | 322.5 | 3540.5 | 204 | 0 | 16 | 72 | 248 | 14.5 | 39.155
10:00 | 3532 | 914 | 1495 | 0 | 282 | 3466 | 205 | 0 | 16 | 72 | 314 | 21 | 0
10:30 | 3520.5 | 914 | 1498 | 0 | 250.5 | 3460.5 | 205 | 0 | 16 | 73 | 370 | 19.5 | 0
11:00 | 3509 | 914 | 1501 | 0 | 219 | 3455 | 205 | 0 | 16 | 74 | 426 | 18 | 0
11:30 | 3597 | 914 | 1537 | 0 | 221.5 | 3432 | 205 | 0 | 16 | 75 | 371.5 | 19 | 0
12:00 | 3685 | 914 | 1573 | 0 | 224 | 3409 | 205 | 0 | 16 | 76 | 317 | 20 | 0
12:30 | 3744 | 913.5 | 1621 | 0 | 226 | 3425.5 | 205 | 0 | 16 | 77 | 241 | 27.5 | 0
13:00 | 3803 | 913 | 1669 | 0 | 228 | 3442 | 205 | 0 | 16 | 78 | 165 | 35 | 0
13:30 | 3803 | 913 | 1669 | 0 | 228 | 3442 | 205 | 0 | 16 | 78 | 165 | 35 | 0
14:00 | 3803 | 913 | 1669 | 0 | 228 | 3442 | 205 | 0 | 16 | 78 | 165 | 35 | 0
14:30 | 3837.5 | 913 | 1644 | 0 | 233 | 3508 | 202 | 0 | 16 | 74 | 170 | 28 | 0
15:00 | 3872 | 913 | 1619 | 0 | 238 | 3574 | 199 | 0 | 16 | 70 | 175 | 21 | 0
15:30 | 3732.5 | 913 | 1533 | 0 | 212 | 3400 | 198.5 | 0 | 16 | 67 | 151.5 | 17.5 | 0
16:00 | 3593 | 913 | 1447 | 0 | 186 | 3226 | 198 | 0 | 16 | 64 | 128 | 14 | 0
16:30 | 3337 | 913 | 1322 | 0 | 139.5 | 3193.5 | 154.5 | 0 | 16 | 62 | 117 | 11.5 | 0
17:00 | 3081 | 913 | 1197 | 0 | 93 | 3161 | 111 | 0 | 16 | 60 | 106 | 9 | 0
17:30 | 3067.5 | 913.5 | 1184 | 0 | 84 | 3158 | 130.5 | 0 | 16 | 58 | 62.5 | 8 | 0
18:00 | 3054 | 914 | 1171 | 0 | 75 | 3155 | 150 | 0 | 16 | 56 | 19 | 7 | 0
18:30 | 3509 | 914 | 1429.5 | 0 | 205 | 3411.5 | 160 | 0 | 32 | 63 | 9.5 | 3.5 | 0
19:00 | 3964 | 914 | 1688 | 0 | 335 | 3668 | 170 | 0 | 48 | 70 | 0 | 0 | 0
19:30 | 3770 | 915 | 1716 | 0 | 651 | 4161 | 200 | 0 | 48 | 72 | 0 | 1 | 0
20:00 | 3732 | 915 | 1708 | 0 | 713 | 4222 | 200 | 0 | 48 | 70 | 0 | 4 | 0
20:30 | 3796.5 | 915 | 1790 | 0 | 764.5 | 4242.5 | 200.5 | 0 | 48 | 72 | 0 | 6.5 | 0
21:00 | 3861 | 915 | 1872 | 0 | 816 | 4263 | 201 | 0 | 48 | 74 | 0 | 9 | 0
21:30 | 3898.5 | 915 | 1836 | 0 | 789 | 4266.5 | 201 | 0 | 48 | 77 | 0 | 8 | 0
22:00 | 3936 | 915 | 1800 | 0 | 762 | 4270 | 201 | 0 | 48 | 80 | 0 | 7 | 0
22:30 | 3969 | 914 | 1861 | 0 | 767.5 | 4260 | 201 | 0 | 48 | 81 | 0 | 6 | 0
23:00 | 4002 | 913 | 1922 | 0 | 773 | 4250 | 201 | 0 | 48 | 82 | 0 | 5 | 0
23:30 | 3995.5 | 913.5 | 1943 | 0 | 744 | 4221.5 | 201 | 0 | 40 | 81 | 0 | 5 | 0 |  |  | Max Temp. in Dhaka |  | 32.4°C
24:00 | 3989 | 914 | 1964 | 0 | 715 | 4193 | 201 | 0 | 32 | 80 | 0 | 5 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 259.885 MKWHr Energy Not Served 1.953 MKWHr Energy Requirement 261.838 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 120 | 120 | 120 | 120 | 120 | 120 | 122 | 122 | 123 | 125 | 125 | 125 | 125 | 121 | 119 | 118 | 71 | 100 |  | 120 | 120 | 120 | 121 | 121 | 121 | 121 | 2871704
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 40 | 50 |  | 50 | 80 | 80 | 80 | 80 | 80 | 80 | 1856000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [26 empty] | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 1 | 10 | 14 | 20 | 8 | 19 | 20 | 10 | 6 | 1 |  | 1 | [8 empty] | 105705
6 | Sikalbaha 225MW CCPP (Gas) | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 222 | 226 | 225 | 220 | 221 | 220 | 221 | 206 | 187 | 187 |  | 219 | 222 | 224 | 222 | 222 | 222 | 222 | 5026327
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [26 empty] | 0
12 | Hathazari 100 MW peaking PP | 8 | [25 empty] | 8800
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 17 | [17 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 200727
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 7 | [25 empty] | 28352
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [19 empty] | 99 | 99 | 99 | 100 | 100 | 100 | 101 | 614000
17 | Siddhirganj 335 MW CCPP | 330 | 280 | 280 | 280 | 280 | 270 | 250 | 250 | 250 | 250 | 250 | 250 | 290 | 290 | 290 | 260 | 240 | 240 |  | 326 | 328 | 325 | 325 | 330 | 330 | 330 | 6933248
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 15 | [24 empty] | 55200
19 | Ashuganj 195 MW PP (APSCL-United) | [12 empty] | 8 | 8 | 8 | 8 |  |  |  | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 301090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 |  |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 140 | 200 | 200 | 200 | 150 | 150 | 130 |  | 200 | 200 | 200 | 200 | 200 | 200 | 201 | 3439094
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 320 | 320 | 320 | 320 | 320 | 324 | 320 | 320 | 320 | 320 | 325 | 320 | 322 | 320 | 322 | 322 | 320 | 321 |  | 321 | 339 | 340 | 340 | 342 | 342 | 342 | 7816362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 20 | 20 |  | 31 | 31 | 31 | 33 | 36 | 36 | 36 | 766368
33 | Ashuganj 225 MW CCPP | 217 | 217 | 216 | 189 | 193 | 189 | 195 | 190 | 190 | 190 | 190 | 212 | 193 | 189 | 189 | 163 | 162 | 162 |  | 213 | 213 | 216 | 217 | 215 | 217 | 216 | 4851000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 270 | 270 | 270 | 275 | 270 | 270 | 270 | 270 | 305 | 270 | 305 | 305 | 270 | 250 | 250 |  | 320 | 320 | 300 | 300 | 270 | 270 | 270 | 6704000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 295 | 280 | 280 | 285 | 290 | 285 | 285 | 285 | 285 | 320 | 310 | 305 | 310 | 280 | 280 | 280 |  | 228 | [6 empty] | 5875500
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 280 | 325 | 325 | 300 | 230 | 230 |  | 330 | 295 | 285 | 285 | 285 | 285 | 285 | 6322000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 36 | 48 | 50 | 51 | 49 | 48 | 43 | 42 | 41 | 42 | 41 | 40 | 42 | 34 | 10 | 8 |  | 10 | 30 | 37 | 47 | 48 | 49 | 49 | 923040
36 | Chandpur 150 MW CCPP | 50 | 50 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 80 | 80 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 85 | 85 | 85 | 85 | 1651860
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 412 | 413 | 407 | 401 | 405 | 362 | 323 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 304 | 304 |  | 391 | 375 | 371 | 373 | 400 | 401 | 401 | 8589600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 370 | 370 | 370 | 300 | 280 | 280 |  | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 9082500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 150 | 150 | 150 | 150 | 160 | 200 | 198 | 192 | 185 | 188 | 193 | 193 | 193 | 200 | 200 | 201 | 140 | 140 |  | 204 | 203 | 204 | 202 | 202 | 198 | 198 | 4165440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 7 | 5 | 5 | 26 | 18 | 3 | 2 | 5 | 5 | 6 | 0 | [8 empty] | 89340
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 38 | 38 | 38 | 30 |  | 40 | 40 | 39 | 39 | 39 | 39 | 40 | 922000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1379520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | [6 empty] | 31 | 31 | 31 | 31 | 31 | 30 | 20 | 20 | 20 | 20 | 20 | 20 |  | 31 | 31 | 31 | 32 | 31 | 31 | 32 | 483264
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [14 empty] | 135360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 65 | 65 | 65 | 65 | 65 | 65 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2066550
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 266640
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 280 | 295 | 295 | 280 | 295 | 290 | 265 | 270 | 280 | 300 | 315 | 295 | 290 | 270 | 260 | 280 |  | 310 | 310 | 290 | 290 | 280 | 300 | 290 | 7045000
| Bibiyana South 400 MW | 345 | 345 | 325 | 320 | 320 | 320 | 320 | 320 | 320 | 315 | 320 | 370 | 360 | 350 | 350 | 360 | 320 | 320 |  | 350 | 347 | 340 | 340 | 340 | 340 | 340 | 8011500
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | [24 empty] | 52439
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | [18 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 45360
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 88 | 86 | 86 | 92 | 86 | 78 | 78 | 70 | 72 | 72 | 74 | 76 | 78 | 70 | 70 | 64 | 60 | 56 |  | 70 | 72 | 70 | 74 | 80 | 82 | 80 | 1797120
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 29 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 7 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1054080
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 417010
69 | Summit Ashulia | 14 | 14 | 14 | 14 | 14 | 14 | 17 | 17 | 18 | 16 | 16 | 16 | 17 |  |  | 15 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 333600
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 14 | 16 | 22 | 22 | 22 | 22 | 22 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 512625
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 488600
72 | Rupganj 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 8 |  | 8 | 14 | 15 | 8 | 8 | 6 | 6 | 291000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 401280
| Chowmuhani 113 MW | 23 | 12 | 9 | 9 | 9 | 9 | 9 | 9 | 15 | 14 | 9 | 14 | 21 | 27 | 28 | 28 | 9 |  |  | 3 | 27 | 27 | 27 | 28 | 31 | 37 | 434280
| Manikgonj 162MW PP(MPGL) | 17 | 17 | [24 empty] | 41760
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | [24 empty] | 15360
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 142080
79 | Kodda 150 MW PP | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 647520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 8 | 8 | 9 | 16 | 191971
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 35 | 17 | 576000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 1 | 2 | 5 | 3 | 3 | 1 | 1 | 1 | 0 | [9 empty] | 20043
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 17 | 17 | [24 empty] | 38472
82 | Madanganj 102 PP(Summit) | 20 | 17 | [24 empty] | 46270
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 136 | 141 | 146 | 143 | 142 | 139 | 147 | 137 | 124 | 129 | 136 | 152 | 151 | 137 | 136 | 120 | 120 | 120 |  | 149 | 147 | 132 | 160 | 163 | 298 | 316 | 3552204
87 | Meghnaghat 100 MW(IEL) | 7 | 7 | 8 | 7 | 7 | 7 | [20 empty] | 48960
| Meghnaghat 104 MW PP (OPCL) | 34 | 33 | 33 | 17 | 17 | 17 | [13 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 0 | 242880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  |  | 5 | 20 | 40 | 51 | 51 | 51 | 51 | 595658
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | [16 empty] | 4 | 8 | 8 | 8 | 8 | 8 |  | 62208
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | 12 | [8 empty] | 0 | 0 | [15 empty] | 16320
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 15 | [18 empty] | 13 | 30 | 30 | 30 |  | 220909
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | [24 empty] | 53189
101 | Kushiara 163 MW CCPP (KP) | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3443727
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 3200
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [25 empty] | 23400
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 96 | 45 | 8 | 8 | 8 | 8 | 8 | 8 | [10 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 549600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 99 | 88 | 84 | 96 | 96 | 96 | 78 | 78 | 78 | 77 | 78 | 78 | 78 | 78 | 78 | 75 | 35 | 34 |  | 43 | 88 | 88 | 88 | 88 | 88 | 88 | 1934208
115 | Juldah 100 MW PP Unit-3 (Acorn) | 24 | 24 | [17 empty] | 6 | 12 | 12 | 12 | 12 | 12 |  | 117120
116 | Chandpur 200 MW (Desh energy) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 23 | 68 | 75 | 100 | 100 | 107 | 136 | 1218720
117 | Ashuganj 150 MW PP (Midland) | [26 empty] | 3345
118 | Bibiyana-III 400 MW CCPP | 349 | 348 | 353 | 348 | 349 | 327 | 301 | 302 | 302 | 302 | 302 | 334 | 311 | 302 | 300 | 288 | 115 | 121 |  | 220 | 270 | 270 | 270 | 270 | 270 | 255 | 7265000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 59 | 59 | 16 | 8 | 8 | 8 | [9 empty] | 8 | 45 | 45 | 47 | 45 | 45 | 45 | 674400
| Anwara 300 MW PP (United) | 50 | 15 | [17 empty] | 15 | 30 | 30 | 30 | 30 | 30 | 15 | 276000
| Juldah unit-2 (Acorn) | 25 | 25 | [17 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 136320
| Anlima Energy Ltd. | 17 | 17 | [24 empty] | 46418
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [17 empty] | 172080
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 5 | 6 | 15 | 22 | 15 | 14 | 9 | 8 | 7 | 3 | 2 | [8 empty] | 114789
| Chandpur 115(Doreen) | 68 | 66 | 66 | 52 | 49 | 51 | 50 | 50 | 50 | 51 | 32 | 32 | 29 | 32 | 32 | 17 |  |  |  | 6 | 49 | 54 | 65 | 65 | 65 | 65 | 1098240
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | [17 empty] | 297360
| Mirsharai 150 MW (Oil) | [26 empty] | 3345
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 9 | 17 | 14 | 13 | 11 | 16 | 8 | 6 | 8 | 21 | 18 | 20 | 35 | 32 | 21 | 14 | 9 | 7 |  | 0 | 1 | 4 | 9 | 7 | 5 | 5 | 316800
| Sonagazi 75 MW Solar Plant | [5 empty] | 2 | 5 | 22 | 29 | 36 | 76 | 62 | 29 | 31 | 54 | 33 | 20 | 5 | [8 empty] | 374273
| Matarbari 2*600 MW (CPGCL) | 781 | 789 | 790 | 790 | 789 | 665 | 666 | 611 | 727 | 635 | 634 | 635 | 635 | 632 | 634 | 630 | 580 | 585 |  | 578 | 574 | 571 | 573 | 574 | 573 | 577 | 15905454
120 | Eastern Zone Total | 6723 | 6497 | 6332 | 6224 | 6232 | 5835 | 5676 | 5582 | 5682 | 5578 | 5632 | 5824 | 5995 | 5980 | 6001 | 5579 | 4816 | 4767 |  | 6109 | 6279 | 6257 | 6365 | 6367 | 6530 | 6454 | 145092472
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [20 empty] | 16 | 16 | 16 |  |  |  | 35520
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | [24 empty] | 33600
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 16 | 28 | 24 | 93 | 69 | 20 | 11 | 10 | 2 | 23 | 27 | 4 | [8 empty] | 277200
131 | Rampal 1320 MW (BIFPCL) | 900 | 811 | 749 | 755 | 753 | 756 | 758 | 757 | 758 | 758 | 757 | 757 | 752 | 756 | 753 | 726 | 740 | 730 |  | 940 | 964 | 965 | 970 | 960 | 962 | 956 | 19381818
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 518895
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | [24 empty] | 34272
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 180 | 180 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 200 | 200 | 150 | 140 | 140 |  | 176 | 230 | 282 | 307 | 307 | 307 | 307 | 4494500
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2700
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | [15 empty] | 65 | 65 | 704000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 10 | 9 | 9 | 7 | 7 | 6 | 6 | 6 | 4 | 4 | 6 | 6 | 6 | 6 | 5 | 6 |  | 9 | 9 | 9 | 10 | 10 | 9 | 10 | 187492
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 915 | 914 | 915 | 915 | 914 | 914 | 914 | 913 | 915 | 914 | 914 | 914 | 913 | 914 | 913 | 913 | 913 | 914 |  | 914 | 915 | 915 | 915 | 915 | 913 | 914 | 22167127
147 | Bheramara 410 MW CCPP | 397 | 395 | 405 | 407 | 405 | 330 | 330 | 330 | 330 | 330 | 280 | 280 | 280 | 280 | 285 | 250 | 180 | 180 |  | 250 | 250 | 250 | 369 | 402 | 406 | 405 | 7953408
148 | Payra 1320 MW | 1030 | 1020 | 1020 | 1030 | 880 | 800 | 740 | 720 | 680 | 620 | 610 | 560 | 600 | 660 | 680 | 520 | 500 | 500 |  | 580 | 880 | 880 | 900 | 900 | 900 | 840 | 20431000
149
150 | Barapukuria TPP Unit-1 | 61 | 61 | 62 | 61 | 62 | 62 | 61 | 63 | 63 | 61 | 61 | 62 | 62 | 60 | 63 | 63 | 62 | 62 |  | 60 | 60 | 60 | 61 | 62 | 62 | 62 | 1435200
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 9960
| Sirajganj 68 MW Solar Park | [6 empty] | 2 | 12 | 7 | 14 | 10 | 15 | 28 | 10 | 7 | 1 | 0 | [9 empty] | 109500
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 150 | 149 | 149 | 150 | 150 | 149 | 151 | 153 | 150 | 150 | 150 | 156 | 173 | 185 | 177 | 130 | 130 | 130 |  | 135 | 160 | 160 | 174 | 214 | 214 | 214 | 3937182
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 322 | 345 | 342 | 347 | 348 | 324 | 347 | 322 | 313 | 321 | 313 | 348 | 348 | 315 | 337 | 327 | 180 | 180 |  | 330 | 300 | 300 | 414 | 348 | 315 | 348 | 7681164
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [5 empty] | 5 | 5 | 5 | 5 | 87570
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 28 | [25 empty] | 31396
168 | Santahar 50 MW Peaking PP | 22 | [25 empty] | 0
169 | Natore 52 MW PP (Rajlanka)
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 4896
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [26 empty] | 0
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 106 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 49 | 34 | 34 | 34 | 34 | 34 |  |  |  |  | 56 | 67 | 72 | 106 | 92 | 92 | 92 | 1456617
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 5 | 4 | 3 | 1 | [8 empty] | 33398
178 | Energypac Power Venture Thakurgaon Ltd. | [19 empty] | 65 | 70 | 102 | 115 | 92 | 92 | 92 | 498969
| Intraco Solar 30 MW | [5 empty] | 1 | 5 | 5 | 10 | 11 | 22 | 28 | 18 | 12 | 26 | 13 | 6 | 2 | [8 empty] | 163190
| Adani Power Jharkhanda Ltd | 1226 | 1231 | 1128 | 1021 | 1025 | 939 | 924 | 922 | 917 | 922 | 918 | 925 | 921 | 918 | 922 | 815 | 819 | 817 |  | 1013 | 1114 | 1124 | 1112 | 1125 | 1104 | 1109 | 23121819
178 | Teesta Solar Limited | [5 empty] | 12 | 46 | 30 | 85 | 117 | 184 | 133 | 33 | 185 | 61 | 40 | 41 | 4