## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-08 | Thursday
|  | Date (day): | 2024-08-08 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14726.6 | MW |  |  | (b) At Evening Peak Hour : |  | 17615 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-07 | 2024-08-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 150 | 200 | 180 | 180 | 0
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 402 | 409 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 8 | 8 | 92 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 308 | 296 | 320 | 320 | 15 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 | 62 |  | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 75 | 204 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 8 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 326 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 147 | 16 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 30 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 40 | 43 | 43 |  | 37 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 24 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 14 | 14 | 14 |  | 19 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 145 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 64 | 115 | 54 | 135
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 17 | 52 | 53 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 3 | 17 | 17 | 17 | 87 |  | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 54 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1979 | 2445 | 2407 | 2920 | 2319 | 902
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 5 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 212 | 212 | 212 | 212 | 18
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 219 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 16 | 72 | 26 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 80 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 | 75 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 25 | 50 | 50 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 9 | 25 | 10 | 20
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 30 | 35 | 73 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 32 | 50 | 100 | 200 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 51 | 92 | 18 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 25 | 38 | 62 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 17 | 53 | 63 |  | Fuel shortage
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 0 | 17 | 163
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 350 | 400 | 612 | 612 |  | 612 | Unit-1 under maint.
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 20 | 17 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 1026 | 1150 | 730 | 1150 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1839 | 2113 | 2299 | 3213 | 773 | 964
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 215 | 215 | 215 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 270 | 300 | 300 |  |  | FGMO
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 310 | 295 | 300 | 300 | 100 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 35 | 30 | 35 | 10 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 44 | 49 | 45 | 45 | 10 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 140 | 185 | 110 | 180 | 15 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51 |  | 0
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150 |  | 0
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 33 | 35 |  | 17 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 50 | 95 | 95 | 68 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 156 | 68 | 150 | 50 |  | Fuel shortage
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 80 | 90 | 90 | 100
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 16 | 43 |  | 9 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 70 | 17 | 80 |  | 34 | Engine problem
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 10 | 47 | 27 | 55 | 58 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 49 | 49 | 50 | 72 | 43 |  | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 7 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2950 | 1440 | 1651 | 1685 | 1924 | 354 | 460
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 188 | 138 | 190 | 190
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 101 | 96 | 122 | 78 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 92 | 58 | 92 | 23 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 16 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 6 | 12 | 12 |  | 10 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 17 | 17 |  | 37 | engine problem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 238 | 337 | 424.6 | 433 | 0 | 47
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 58 | 58 | 58 | 58 |  | 32 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 8 | 8 |  | 3 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 10 | 10 | 10 | 10 | 76 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 131 | 132 | 136 | 137 |  | 94 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 265 | 269 | 265 | 265 |  |  | FGMO
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 340 | 350 | 380 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1347 | 1329 | 1342 | 1373 | 263 | 502
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 918 | 805 | 918 | 918
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 98 |  | 17 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 309 | 380 | 380 | 30 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 16 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 17 | 85 |  | 20 | Engine problem
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 76 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 761 | 916 | 1000 | 1234 | 0
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 2095 | 2030 | 2493 | 2826 | 741 | 105
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 64 | 46 |  | Fuel shortage
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 69 | 68 | 69 | 69 |  | 125 | GT-2 & ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 880 | 1090 | 1000 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 54 | 150 | 0
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 191 | 250 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1366 | 1638 | 1619 | 2064 | 46 | 125
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 36 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 164 | 155 | 200 | 200 | 10
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 380 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 25 | 35 |  | 15 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 85 |  | 19 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 70 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1079 | 1302 | 1200 | 1480
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 22 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1682 | 1914 | 2086 | 2579 | 673 | 103
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 62 | 62 | 62 | 62 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 106 | 106 | 106 |  | 9
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 8 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 35 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 97 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 263 | 283 | 371 | 283 | 40 | 393
| Total |  |  |  |  | 28098 | 26947 | 12249 | 13740 | 14726.6 | 17615 | 5209 | 3601
A. |  | 2024-08-07 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 13760 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11112 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13790 | MW
3 | Day peak Generation : |  |  | 12249 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13226.7 | MW
4 | Evening peak Generation : |  |  | 13740 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 48 | MW
5 | Total Energy Generation : |  | 318.9257 | MKWHr | By Solar | 3.241 | MKWHr
| By Gas : | 160.7281 | MKWHr |  | By Oil: | 16.3495 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 110.2546 | MKWHr |  | By Hydro: | 5.1559 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.5616 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5209 | MW | Dhaka | 4417.6 | 4369.6 |  | 48 |  | 18:00 |  | 120
|  |  | For Plants S/D or M/C prob = |  |  | 3601 | MW | Chittagong | 1281 | 1281 |  | 0 |  | 19:00 |  | 123
|  |  | Total = |  |  | 8810 | MW | Khulna | 1649.4 | 1649.4 |  | 0 |  | 19:30 |  | 202
7 | Total Gas Supplied : |  |  | 1055.71 | MMCFD |  |  | Rajshahi | 1420.2 | 1420.2 |  | 0 |  | 20:00 |  | 189
8 | Fuel Cost : | i) Gas : | Taka | 555939953.914 | ii) Oil : | Taka | 300867713.43 | Comilla | 1314 | 1314 |  | 0 |  | 21:00 |  | 48
|  | iii) Coal : | Taka | 736665018.59 | Total | Taka | 1593472685.934 | Mymensingh | 1209 | 1209 |  | 0 |  | 22:00 |  | 56.345
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5646.3 | MKWHr. | Sylhet | 606 | 606 |  | 0 |  | 23:00 |  | 76.4
| ii) During Peak Demand : |  |  | 564 | MW (W to E) at | 21:00 | hrs | Barisal | 428.5 | 428.5 |  | 0 |  | 24:00 |  | 197.685
| iii) Maximum : |  |  | 274 | MW at | 8:00 | hrs | Rangpur | 901 | 901 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.5°C |  |  | Total | 13226.7 | 13178.7 |  | 48
B. |  | 2024-08-08 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.9°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 17615 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12800 | MW
4 | Reserve(Generation end) |  |  |  | 3515 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 326.8061 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11274 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.6575 | MKWHr. | ii) HVDC Flow at Peak Time |  | 805 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.9776 | MKWHr. | iii) Maximum HVDC Flow : |  | 919 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 96.98 |  | (b) Today: | 97.05 |  | (c) Rule Curve: |  | 91.24
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-08-07 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 0 | 20 | 0 | 406 | 0 |  | 0 | 450 | 300 | 0 | 0 | 0 | 327 | 0 | 135 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 270 | 216 | 160 | 70 | 35 | 46 | 0 | 51 | 0 | 15 | 8 | 0 | 0 | 0 | 18 | 82 | 200 | 0 | 0 | 0 | 39 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 275 | 12 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 80 | 0 | 0 | 52 | 0 | 268 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 29 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 285 | 0 | 0 | 526 | 6 | 818 | 0 | 0 | 0 |  | 918 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 1040 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 1018 | 0 | 250 | 1203 | 0 | 0 | 0 | 0 |  | 6942 | 5766 | 12708 | 3852 | 918 | 2090 | 0 | 551 | 4917 | 213 | 0 | 79 | 82 | 0 | 6 | 183.36 | 96.93
2:00 | 0 | 0 | 200 | 0 | 0 | 20 | 0 | 406 | 0 |  | 0 | 450 | 291 | 0 | 0 | 0 | 325 | 0 | 135 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 270 | 217 | 160 | 80 | 35 | 52 | 0 | 51 | 0 | 15 | 8 | 0 | 0 | 0 | 18 | 82 | 200 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 52 | 0 | 0 | 51 | 0 | 268 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 285 | 0 | 0 | 475 | 12 | 820 | 0 | 0 | 0 |  | 912 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 960 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 1022 | 0 | 200 | 1119 | 0 | 0 | 0 | 0 |  | 6890 | 5486 | 12376 | 3867 | 912 | 2087 | 0 | 467 | 4658 | 212 | 0 | 79 | 82 | 0 | 12 | 166.17 | 96.94
3:00 | 0 | 0 | 200 | 0 | 0 | 20 | 0 | 406 | 0 |  | 0 | 450 | 300 | 0 | 0 | 0 | 325 | 0 | 75 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 270 | 217 | 160 | 80 | 35 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 80 | 200 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 45 | 0 | 52 | 0 | 0 | 51 | 0 | 268 | 57 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 285 | 0 | 0 | 473 | 13 | 815 | 0 | 0 | 0 |  | 913 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 949 | 0 | 200 | 1026 | 0 | 0 | 0 | 0 |  | 6769 | 5277 | 12046 | 3808 | 913 | 2111 | 0 | 428 | 4465 | 212 | 0 | 16 | 80 | 0 | 13 | 147.07 | 96.95
4:00 | 0 | 0 | 200 | 0 | 0 | 20 | 0 | 406 | 0 |  | 0 | 450 | 297 | 0 | 0 | 0 | 325 | 0 | 75 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 270 | 217 | 158 | 80 | 35 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 78 | 200 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 52 | 0 | 0 | 51 | 0 | 268 | 57 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 285 | 0 | 0 | 472 | 12 | 815 | 0 | 0 | 0 |  | 916 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 818 | 0 | 200 | 956 | 0 | 0 | 0 | 0 |  | 6718 | 5080 | 11798 | 3807 | 916 | 2102 | 0 | 393 | 4263 | 211 | 0 | 16 | 78 | 0 | 12 | 145.16 | 96.96
5:00 | 0 | 0 | 200 | 0 | 0 | 20 | 0 | 405 | 0 |  | 0 | 450 | 298 | 0 | 0 | 0 | 324 | 0 | 75 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 270 | 216 | 158 | 80 | 35 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 78 | 201 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 285 | 12 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 52 | 0 | 0 | 51 | 0 | 268 | 59 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 27 | 0 | 350 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 285 | 0 | 0 | 470 | 9 | 815 | 0 | 0 | 0 |  | 918 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 200 | 913 | 0 | 0 | 0 | 0 |  | 6709 | 5017 | 11726 | 3804 | 918 | 2077 | 0 | 393 | 4220 | 211 | 0 | 16 | 78 | 0 | 9 | 166.17 | 96.97
6:00 | 0 | 0 | 150 | 0 | 0 | 20 | 0 | 405 | 0 |  | 0 | 400 | 289 | 0 | 0 | 0 | 260 | 0 | 75 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 270 | 217 | 138 | 80 | 35 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 72 | 201 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 52 | 0 | 0 | 51 | 0 | 205 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 330 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 320 | 0 | 0 | 418 | 21 | 815 | 0 | 0 | 1 |  | 917 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 800 | 220 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 818 | 1 | 200 | 829 | 8 | 0 | 0 | 0 |  | 6322 | 4814 | 11136 | 3648 | 917 | 1971 | 0 | 325 | 3942 | 212 | 0 | 16 | 72 | 12 | 21 | 156.62 | 96.98
7:00 | 0 | 0 | 150 | 0 | 0 | 20 | 0 | 405 | 0 |  | 0 | 400 | 314 | 0 | 0 | 0 | 260 | 0 | 75 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 22 | 16 | 8 | 3 | 0 | 132 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 345 | 216 | 138 | 80 | 35 | 49 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 68 | 200 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 52 | 1 | 0 | 51 | 0 | 209 | 24 | 17 | 0 | 2 | 0 | 0 | 0 | 17 | 28 | 0 | 350 | 0 | 6 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 290 | 0 | 0 | 350 | 21 | 818 | 0 | 0 | 11 |  | 917 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 770 | 5 | 150 | 825 | 32 | 0 | 0 | 8 |  | 6369 | 4751 | 11120 | 3738 | 917 | 1967 | 0 | 329 | 3774 | 212 | 0 | 16 | 68 | 78 | 21 | 143.25 | 96.99
8:00 | 0 | 0 | 150 | 0 | 0 | 25 | 0 | 406 | 0 |  | 0 | 400 | 310 | 0 | 0 | 0 | 260 | 0 | 75 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 16 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 280 | 214 | 138 | 85 | 35 | 51 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 68 | 200 | 0 | 0 | 1 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 54 | 3 | 0 | 51 | 0 | 209 | 24 | 17 | 0 | 2 | 0 | 0 | 0 | 17 | 27 | 0 | 338 | 0 | 8 | 0 | 0 | 0 | 0 | 3 | 49 | 0 | 290 | 0 | 0 | 350 | 28 | 823 | 0 | 0 | 18 |  | 918 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 0 | 780 | 180 | 0 | 0 | 1 | 40 | 0 | 0 | 0 | 766 | 8 | 150 | 827 | 50 | 0 | 0 | 27 |  | 6309 | 4803 | 11112 | 3668 | 918 | 1949 | 0 | 333 | 3758 | 212 | 0 | 16 | 68 | 162 | 28 | 198.64 | 96.99
9:00 | 0 | 0 | 150 | 0 | 0 | 27 | 0 | 407 | 0 |  | 0 | 400 | 304 | 0 | 0 | 0 | 260 | 0 | 77 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 270 | 214 | 138 | 85 | 35 | 49 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 74 | 198 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 54 | 6 | 0 | 51 | 0 | 209 | 24 | 17 | 0 | 4 | 0 | 0 | 0 | 17 | 17 | 0 | 335 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 49 | 0 | 285 | 0 | 0 | 350 | 50 | 873 | 0 | 0 | 61 |  | 919 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 63 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 70 | 0 | 4 | 0 | 780 | 180 | 0 | 0 | 4 | 51 | 0 | 0 | 0 | 765 | 15 | 150 | 825 | 69 | 0 | 0 | 41 |  | 6468 | 4862 | 11330 | 3662 | 919 | 1946 | 0 | 323 | 3806 | 212 | 0 | 16 | 74 | 322 | 50 | 210.1 | 97
10:00 | 0 | 0 | 150 | 0 | 0 | 27 | 0 | 406 | 0 |  | 0 | 400 | 309 | 0 | 0 | 0 | 315 | 0 | 75 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 310 | 212 | 138 | 86 | 35 | 49 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 80 | 195 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 315 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 54 | 9 | 0 | 51 | 0 | 205 | 24 | 35 | 0 | 5 | 0 | 0 | 0 | 17 | 9 | 0 | 370 | 0 | 15 | 0 | 0 | 0 | 0 | 7 | 50 | 0 | 320 | 0 | 0 | 350 | 28 | 920 | 0 | 0 | 67 |  | 918 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 49 | 0 | 5 | 0 | 780 | 220 | 0 | 0 | 4 | 34 | 0 | 0 | 0 | 766 | 24 | 150 | 893 | 92 | 0 | 0 | 40 |  | 6660 | 5015 | 11675 | 3842 | 918 | 2001 | 0 | 329 | 3921 | 212 | 0 | 40 | 80 | 304 | 28 | 233.975 | 97
11:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 420 | 310 | 0 | 0 | 0 | 328 | 0 | 76 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 305 | 210 | 138 | 80 | 32 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 86 | 195 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 133 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 54 | 16 | 0 | 51 | 0 | 265 | 24 | 36 | 0 | 3 | 0 | 0 | 0 | 17 | 9 | 0 | 360 | 0 | 45 | 0 | 0 | 0 | 0 | 35 | 49 | 0 | 315 | 0 | 0 | 350 | 28 | 932 | 0 | 0 | 3 |  | 918 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 49 | 0 | 8 | 0 | 870 | 220 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | 760 | 22 | 150 | 945 | 188 | 0 | 0 | 15 |  | 6784 | 5204 | 11988 | 3850 | 918 | 2020 | 0 | 330 | 4069 | 212 | 0 | 64 | 86 | 411 | 28 | 202.46 | 97.01
12:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 308 | 0 | 0 | 0 | 325 | 0 | 75 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 335 | 211 | 140 | 80 | 29 | 44 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 80 | 188 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 131 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 64 | 5 | 0 | 51 | 0 | 265 | 24 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 350 | 3 | 16 | 0 | 0 | 0 | 0 | 35 | 49 | 0 | 310 | 0 | 0 | 350 | 20 | 1026 | 0 | 0 | 7 |  | 918 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 8 | 0 | 880 | 220 | 0 | 0 | 1 | 76 | 35 | 0 | 0 | 761 | 12 | 191 | 1079 | 97 | 0 | 0 | 22 |  | 6843 | 5406 | 12249 | 3853 | 918 | 2095 | 0 | 377 | 4349 | 212 | 0 | 64 | 80 | 281 | 20 | 191.955 | 97.01
13:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 311 | 0 | 0 | 0 | 322 | 0 | 75 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 305 | 213 | 140 | 80 | 33 | 44 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 90 | 163 | 0 | 0 | 1 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 99 | 7 | 0 | 51 | 0 | 265 | 24 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 340 | 17 | 15 | 0 | 0 | 0 | 0 | 36 | 60 | 0 | 320 | 0 | 0 | 350 | 25 | 1071 | 0 | 0 | 20 |  | 917 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 8 | 0 | 890 | 220 | 0 | 0 | 5 | 103 | 36 | 0 | 0 | 761 | 26 | 200 | 1185 | 155 | 0 | 0 | 34 |  | 6924 | 5628 | 12552 | 3783 | 917 | 2088 | 0 | 444 | 4519 | 212 | 0 | 64 | 90 | 410 | 25 | 141 | 97.02
14:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 420 | 305 | 0 | 0 | 0 | 325 | 0 | 75 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 320 | 210 | 138 | 70 | 32 | 41 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 92 | 150 | 0 | 0 | 1 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 133 | 0 | 0 | 0 | 305 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 95 | 0 | 0 | 51 | 0 | 265 | 24 | 34 | 0 | 5 | 0 | 0 | 0 | 17 | 13 | 0 | 345 | 17 | 14 | 0 | 0 | 0 | 0 | 25 | 63 | 0 | 330 | 0 | 0 | 350 | 26 | 1072 | 0 | 0 | 35 |  | 918 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 4 | 0 | 950 | 220 | 0 | 0 | 3 | 45 | 36 | 0 | 0 | 762 | 28 | 200 | 1182 | 162 | 0 | 0 | 37 |  | 6925 | 5661 | 12586 | 3817 | 918 | 2080 | 0 | 440 | 4578 | 212 | 0 | 64 | 92 | 359 | 26 | 147 | 97.01
15:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 420 | 308 | 0 | 0 | 0 | 325 | 0 | 139 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 305 | 211 | 138 | 70 | 34 | 43 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 82 | 137 | 0 | 0 | 1 | 40 | 57 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 1 | 0 | 51 | 0 | 265 | 24 | 17 | 0 | 1 | 0 | 0 | 0 | 17 | 27 | 0 | 350 | 17 | 45 | 0 | 0 | 0 | 0 | 26 | 67 | 0 | 320 | 0 | 0 | 350 | 33 | 1072 | 0 | 0 | 49 |  | 918 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 48 | 0 | 5 | 0 | 1000 | 220 | 0 | 0 | 1 | 15 | 36 | 0 | 0 | 763 | 29 | 200 | 1201 | 176 | 0 | 0 | 4 |  | 7003 | 5664 | 12667 | 3831 | 918 | 2087 | 0 | 441 | 4646 | 212 | 0 | 64 | 82 | 353 | 33 | 212.965 | 97.02
16:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 420 | 288 | 0 | 0 | 0 | 324 | 0 | 140 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 305 | 215 | 138 | 70 | 31 | 44 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 90 | 137 | 0 | 0 | 1 | 40 | 56 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 1 | 0 | 51 | 0 | 268 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 260 | 17 | 30 | 0 | 0 | 0 | 0 | 4 | 67 | 0 | 315 | 0 | 0 | 353 | 20 | 1070 | 0 | 0 | 32 |  | 911 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 0 | 48 | 0 | 2 | 0 | 1030 | 220 | 0 | 0 | 0 | 18 | 36 | 0 | 0 | 752 | 4 | 200 | 1265 | 110 | 0 | 0 | 3 |  | 6778 | 5610 | 12388 | 3729 | 911 | 1977 | 0 | 450 | 4730 | 212 | 0 | 64 | 90 | 205 | 20 | 202.46 | 97.02
17:00 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 420 | 282 | 0 | 0 | 0 | 322 | 0 | 73 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 305 | 214 | 138 | 50 | 31 | 46 | 0 | 51 | 0 | 0 | 22 | 0 | 0 | 0 | 18 | 82 | 137 | 0 | 0 | 1 | 40 | 57 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 275 | 12 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 0 | 0 | 74 | 0 | 268 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 28 | 0 | 212 | 17 | 3 | 0 | 0 | 0 | 0 | 4 | 83 | 0 | 315 | 0 | 0 | 350 | 18 | 1005 | 0 | 0 | 6 |  | 901 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 0 | 980 | 180 | 0 | 0 | 0 | 16 | 36 | 0 | 0 | 753 | 10 | 200 | 1180 | 55 | 0 | 0 | 4 |  | 6549 | 5286 | 11835 | 3589 | 901 | 1846 | 0 | 495 | 4528 | 212 | 0 | 64 | 82 | 100 | 18 | 138.475 | 97.03
18:00 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 316 | 0 |  | 0 | 360 | 304 | 0 | 0 | 0 | 250 | 0 | 80 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 270 | 213 | 88 | 50 | 34 | 47 | 0 | 51 | 0 | 0 | 37 | 0 | 0 | 0 | 18 | 76 | 137 | 0 | 0 | 0 | 40 | 57 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 265 | 12 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 96 | 0 | 0 | 149 | 0 | 189 | 24 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 44 | 0 | 212 | 17 | 2 | 0 | 0 | 0 | 0 | 1 | 84 | 0 | 295 | 0 | 0 | 340 | 33 | 954 | 0 | 0 | 1 |  | 901 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 840 | 180 | 0 | 0 | 0 | 4 | 36 | 0 | 0 | 758 | 3 | 150 | 1061 | 14 | 0 | 0 | 2 |  | 6179 | 4955 | 11134 | 3271 | 901 | 1784 | 0 | 602 | 4164 | 212 | 0 | 64 | 76 | 27 | 33 | 120 | 97.03
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 450 | 310 | 0 | 0 | 1 | 325 | 0 | 79 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 29 | 17 | 13 | 0 | 20 | 22 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 197 | 0 | 0 | 0 |  | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 340 | 212 | 88 | 50 | 35 | 47 | 0 | 51 | 0 | 23 | 43 | 0 | 0 | 0 | 18 | 88 | 138 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 5 | 0 | 0 | 35 | 0 | 96 | 0 | 25 | 156 | 0 | 267 | 56 | 52 | 19 | 0 | 32 | 0 | 0 | 17 | 47 | 25 | 310 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 79 | 0 | 330 | 0 | 0 | 350 | 32 | 1105 | 0 | 0 | 0 |  | 901 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 940 | 220 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 906 | 0 | 234 | 1209 | 0 | 0 | 0 | 0 |  | 7263 | 5748 | 13011 | 3758 | 901 | 1967 | 0 | 1010 | 4805 | 212 | 0 | 238 | 88 | 0 | 32 | 123 | 97.04
19:30 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 275 | 0 | 0 | 15 | 325 | 0 | 76 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 20 | 22 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 300 | 216 | 88 | 50 | 35 | 48 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 90 | 138 | 0 | 0 | 0 | 40 | 57 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 45 | 0 | 0 | 90 | 0 | 116 | 0 | 25 | 155 | 0 | 269 | 74 | 52 | 34 | 0 | 32 | 0 | 0 | 27 | 47 | 25 | 325 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 69 | 0 | 295 | 0 | 0 | 385 | 24 | 1150 | 0 | 0 | 0 |  | 900 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 45 | 30 | 0 | 65 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 913 | 0 | 250 | 1307 | 0 | 0 | 0 | 0 |  | 7613 | 5975 | 13588 | 3754 | 900 | 1939 | 0 | 1228 | 5146 | 212 | 0 | 295 | 90 | 0 | 24 | 202 | 0
20:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 276 | 0 | 0 | 15 | 326 | 0 | 71 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 20 | 22 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 270 | 217 | 88 | 50 | 35 | 49 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 92 | 138 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 15 | 0 | 0 | 102 | 0 | 114 | 0 | 12 | 156 | 0 | 268 | 89 | 52 | 17 | 0 | 32 | 0 | 0 | 52 | 47 | 12 | 340 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 68 | 0 | 295 | 0 | 0 | 400 | 30 | 1150 | 0 | 0 | 0 |  | 900 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 24 | 30 | 0 | 60 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1080 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 914 | 0 | 250 | 1319 | 0 | 0 | 0 | 0 |  | 7611 | 5921 | 13532 | 3724 | 900 | 1927 | 0 | 1191 | 5175 | 212 | 0 | 281 | 92 | 0 | 30 | 189 | 97.04
21:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 296 | 0 | 0 | 15 | 326 | 0 | 204 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 18 | 22 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 17 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 270 | 215 | 185 | 50 | 35 | 49 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 90 | 138 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 15 | 0 | 0 | 101 | 0 | 115 | 0 | 12 | 156 | 0 | 269 | 92 | 52 | 17 | 0 | 32 | 0 | 0 | 70 | 47 | 12 | 340 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 49 | 0 | 295 | 0 | 0 | 400 | 17 | 1150 | 0 | 0 | 0 |  | 805 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1090 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 916 | 0 | 250 | 1302 | 0 | 0 | 0 | 0 |  | 7875 | 5865 | 13740 | 3853 | 805 | 2173 | 0 | 1193 | 5170 | 212 | 0 | 227 | 90 | 0 | 17 | 48 | 97.04
22:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 308 | 0 | 0 | 15 | 330 | 0 | 204 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 18 | 22 | 24 | 14 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 270 | 215 | 187 | 50 | 33 | 49 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 98 | 109 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 295 | 8 | 5 | 0 | 0 | 0 | 0 | 110 | 0 | 115 | 0 | 0 | 156 | 0 | 269 | 87 | 52 | 17 | 0 | 50 | 0 | 0 | 70 | 47 | 12 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 295 | 0 | 0 | 400 | 21 | 1150 | 0 | 0 | 0 |  | 808 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 913 | 0 | 250 | 1314 | 0 | 0 | 0 | 0 |  | 7806 | 5885 | 13691 | 3823 | 808 | 2184 | 0 | 1163 | 5188 | 213 | 0 | 193 | 98 | 0 | 21 | 56.345 | 97.04
23:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 313 | 0 | 0 | 15 | 334 | 0 | 201 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 18 | 22 | 24 | 14 | 8 | 0 | 134 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 305 | 214 | 187 | 50 | 33 | 50 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 98 | 129 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 0 | 0 | 0 | 110 | 0 | 115 | 0 | 0 | 155 | 0 | 268 | 87 | 35 | 17 | 0 | 50 | 0 | 0 | 70 | 42 | 12 | 375 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 325 | 0 | 0 | 400 | 17 | 1150 | 0 | 0 | 0 |  | 808 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 912 | 0 | 250 | 1323 | 0 | 0 | 0 | 0 |  | 7891 | 5869 | 13760 | 3987 | 808 | 2135 | 0 | 1111 | 5197 | 214 | 0 | 193 | 98 | 0 | 17 | 76.4 | 97.05
24:00 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 450 | 308 | 0 | 0 | 15 | 333 | 0 | 140 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 18 | 22 | 24 | 14 | 8 | 0 | 134 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 300 | 214 | 187 | 50 | 35 | 51 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 94 | 127 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 320 | 12 | 5 | 0 | 0 | 0 | 0 | 110 | 0 | 116 | 0 | 0 | 91 | 0 | 265 | 87 | 17 | 17 | 0 | 50 | 0 | 0 | 70 | 32 | 12 | 365 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 320 | 0 | 0 | 401 | 14 | 1150 | 0 | 0 | 0 |  | 911 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 913 | 0 | 250 | 1303 | 0 | 0 | 0 | 0 |  | 7650 | 5943 | 13593 | 3906 | 911 | 2213 | 0 | 937 | 5179 | 214 | 0 | 125 | 94 | 0 | 14 | 197.685 | 97.06
KWH | 0 | 0 | 4654344 | 0 | 0 | 232090 | 0 | 9885600 | 0 |  | 0 | 9977500 | 7186705 | 0 | 0 | 79508 | 7439040 | 0 | 27340000 | 0 | 26928 | 1464000 | 0 | 0 | 0 | 0 | 462600 | 95029 | 61170 | 0 | 378600 | 528120 | 498600 | 231000 | 145920 | 0 | 3231867 | 1924000 | 0 | 0 | 0 | 5210309 | 0 | 0 | 0 |  | 30480 | 0 | 49019 | 0 | 0 | 0 | 0 | 540000 | 0 | 0 | 0 | 0 | 7058000 | 5222000 | 3462545 | 1652630 | 809280 | 1154400 | 0 | 1149652 | 0 | 176080 | 452837 | 0 | 0 | 0 | 430290 | 1977600 | 3950400 | 0 | 0 | 13300 | 942000 | 1371480 | 0 | 0 | 3616855 | 0 | 0 | 247680 | 0 | 3205480 | 0 | 0 | 0 | 7233000 | 265152 | 162604 | 0 | 90327 | 0 | 0 | 854400 | 0 | 1959840 | 42660 | 55680 | 1932000 | 0 | 6315000 | 1160400 | 667200 | 122945 | 25195 | 225818 | 0 | 0 | 634980 | 697200 | 81600 | 7959200 | 288000 | 273840 | 80640 | 0 | 0 | 0 | 201173 | 1397760 | 0 | 7355300 | 0 | 0 | 9469090 | 561600 | 23330909 | 0 | 0 | 322000 |  | 20657454 | 0 | 7807392 | 0 | 0 | 0 | 0 | 0 | 32140 | 35200 | 0 | 1625000 | 191148 | 0 | 0 | 0 | 0 | 0 | 0 | 59604 | 0 | 0 | 0 | 0 | 155178 | 0 | 0 | 122562 | 1415127 | 0 | 0 | 0 | 0 | 4211091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8576072 | 4800 | 0 | 0 | 0 | 1721740 | 0 | 47655 | 0 | 24708500 | 529964 | 0 | 0 | 25620 | 504720 | 1048512 | 0 | 0 | 20130911 | 206587 | 4887300 | 26312728 | 1283000 | 0 | 1959 | 293250 |  | 192330451 | 126595214 | 318925665 | 116630474 | 20657454 | 44097611 | 0 | 14378314 | 110254565 | 5155867 | 0 | 1971221 | 1977600 | 3240959 | 561600 | 0
Fuel Cost | 0 | 0 | 19967135.76 | 0 | 0 | 886583.8 | 0 | 28470528 | 0 |  | 0 | 31728450 | 24578531.1 | 0 | 0 | 1400930.96 | 22689072 | 0 | 146269000 | 0 | 483357.6 | 28430880 | 0 | 0 | 0 | 0 | 8447076 | 1497657.04 | 1118799.3 | 0 | 283950 | 0 | 0 | 0 | 2613427.2 | 0 | 0 | 0 | 0 | 0 | 0 | 16620885.71 | 0 | 0 | 0 |  | 536143.2 | 0 | 877930.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21597480 | 17337040 | 11599525.75 | 5337994.9 | 2727273.6 | 5056272 | 0 | 4610104.52 | 0 | 3153592.8 | 8178236.22 | 0 | 0 | 0 | 322717.5 | 12973056 | 12285744 | 0 | 0 | 0 | 3673800 | 5115620.4 | 0 | 0 | 12369644.1 | 0 | 0 | 1292889.6 | 0 | 8943289.2 | 0 | 0 | 0 | 22349970 | 198864 | 123579.04 | 0 | 1842670.8 | 0 | 0 | 16413024 | 0 | 34512782.4 | 0 | 991660.8 | 33520200 | 0 | 16734750 | 22117224 | 12516672 | 2205633.3 | 0 | 3692124.3 | 0 | 0 | 12134467.8 | 13532652 | 1453296 | 21171472 | 4916160 | 0 | 1474905.6 | 0 | 0 | 0 | 0 | 25187635.2 | 0 | 21845241 | 0 | 0 | 65999557.3 | 0 | 137652363.1 | 0 | 0 | 0 |  | 58047445.74 | 0 | 23031806.4 | 0 | 0 | 0 | 0 | 0 | 604553.4 | 662112 | 0 | 5135000 | 906041.52 | 0 | 0 | 0 | 0 | 0 | 0 | 1001943.24 | 0 | 0 | 0 | 0 | 2779237.98 | 0 | 0 | 92779.434 | 15608850.81 | 0 | 0 | 0 | 0 | 13896600.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25042130.24 | 81984 | 0 | 0 | 0 | 34297060.8 | 0 | 0 | 0 | 160111080 | 1648188.04 | 0 | 0 | 0 | 0 | 18191683.2 | 0 | 0 | 146955650.3 | 0 | 36410385 | 173927132.08 | 0 | 0 | 0 | 0 |  | 946061523.19 | 718431664.484 | 1664493187.674 | 413871623.244 | 58047445.74 | 142068330.67 | 0 | 263357463.72 | 736665018.59 | 0 | 0 | 37510249.71 | 12973056 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 308 | 0 | 0 | 0 | 325 | 0 | 75 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 8 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 335 | 211 | 140 | 80 | 29 | 44 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 80 | 188 | 0 | 0 | 2 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 131 | 0 | 0 | 0 | 310 | 12 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 64 | 5 | 0 | 51 | 0 | 265 | 24 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 350 | 3 | 16 | 0 | 0 | 0 | 0 | 35 | 49 | 0 | 310 | 0 | 0 | 350 | 20 | 1026 | 0 | 0 | 7 |  | 918 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 8 | 0 | 880 | 220 | 0 | 0 | 1 | 76 | 35 | 0 | 0 | 761 | 12 | 191 | 1079 | 97 | 0 | 0 | 22 |  | 12249 | DayPeak
Yesterday Evening Peak | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 296 | 0 | 0 | 15 | 326 | 0 | 204 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 18 | 22 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 270 | 215 | 185 | 50 | 35 | 49 | 0 | 51 | 0 | 28 | 43 | 0 | 0 | 0 | 18 | 90 | 138 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 132 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 15 | 0 | 0 | 101 | 0 | 115 | 0 | 12 | 156 | 0 | 269 | 92 | 52 | 17 | 0 | 32 | 0 | 0 | 70 | 47 | 12 | 340 | 17 | 0 | 17 | 0 | 0 | 0 | 0 | 49 | 0 | 295 | 0 | 0 | 400 | 17 | 1150 | 0 | 0 | 0 |  | 805 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | 1090 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 916 | 0 | 250 | 1302 | 0 | 0 | 0 | 0 |  | 13740 | EvPeak
Forecast for Evening | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 320 | 8 | 85 | 55 | 330 | 0 | 0 | 8 | 8 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 20 | 23 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 12 | 72 | 80 | 25 | 35 | 50 | 0 | 20 | 0 | 0 | 0 | 0 | 300 | 215 | 180 | 95 | 35 | 45 | 0 | 51 | 0 | 35 | 43 | 0 | 0 |  | 18 | 100 | 190 | 0 | 0 | 0 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 280 | 0 | 0 | 122 | 0 | 135 | 0 | 50 | 150 | 150 | 265 | 92 | 52 | 105 | 0 | 100 | 54 | 92 | 80 | 55 | 38 | 380 | 17 | 0 | 162 | 53 | 0 | 17 | 0 | 72 | 35 | 300 | 163 | 0 | 612 | 60 | 1150 | 0 | 0 |  |  | 918 | 0 | 380 | 0 | 98 | 0 | 0 | 0 | 40 | 55 | 16 | 69 | 10 | 64 | 0 | 0 | 0 | 40 | 20 | 85 | 28 | 0 | 46 | 0 | 35 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 85 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 1234 | 0 | 307 | 1480 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 320 | 8 | 85 | 55 | 330 | 0 | 0 | 8 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 30 | 35 | 0 | 20 | 23 | 24 | 14 | 8 | 0 | 132 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 12 | 16 | 51 | 25 | 30 | 6 | 0 | 10 | 0 | 0 | 0 | 0 | 300 | 215 | 110 | 95 | 30 | 45 | 0 | 51 | 0 | 33 | 16 | 0 | 0 |  | 18 | 90 | 190 | 0 | 0 | 1.6 | 40 | 58 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 8 | 0 | 145 | 0 | 0 | 96 | 0 | 54 | 20 | 25 | 68 | 150 | 265 | 58 | 17 | 105 | 5 | 50 | 17 | 51 | 17 | 27 | 25 | 350 | 17 | 50 | 54 | 17 | 0 | 17 | 35 | 50 | 17 | 300 | 17 | 0 | 612 | 42 | 730 | 0 | 0 | 70 |  | 918 | 0 | 380 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 16 | 69 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 36 | 0 | 25 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 17 | 0 | 70 | 0 | 106 | 0 | 8 | 70 | 1000 | 220 |  | 54 | 6 | 100 | 35 | 0 | 0 | 1000 | 30 | 250 | 1200 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 370 | 289 | 0 | 0 | 0 | 332 | 0 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 22 | 24 | 14 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 270 | 219 | 110 | 50 | 32 | 47 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 68 | 107 | 0 | 0 | 1 | 40 | 58 | 0 | 0 | 130 | 0 | 0 | 60 | 0 | 20 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 0 | 0 | 0 | 96 | 0 | 53 | 4 | 0 | 51 | 0 | 268 | 59 | 17 | 0 | 1 | 0 | 0 | 0 | 70 | 9 | 0 | 340 | 17 | 6 | 0 | 0 | 0 | 0 | 17 | 48 | 0 | 295 | 0 | 0 | 350 | 1 | 730 | 0 | 0 | 10 | 0 | 904 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 106 | 0 | 3 | 0 | 880 | 220 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 813 | 9 | 200 | 912 | 46 | 0 | 0 | 20 | 0 |  |  |  | 160728085 | 20657454 | 0 | 110254565 | 16349535 | 1977600 | 3240959 | 561600 | 5155867 |  |  | 318925665
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 160.7281 | 20.6575 | 0 | 110.2546 | 16.3495 | 1.9776 | 3.241 | 0.5616 | 5.1559
| Minimum Generation |  | 11112 | 8:00
| Highest Generation |  | 13760 | 23:00 | [129 empty] | 0 | [73 empty] | 318.9257
| Day Peak Generation |  | 12249 | 12:00
| Evening Peak Generation |  | 13740 | 21:00 | [203 empty] | 202699852
| HVDC Max Flow |  | 919 | 9:00 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 805 | 21:00
| Load factor L.F |  | 96.57% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-08
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12249 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11274
Evening Peak Generation : |  |  | 13740 | MW Hour : | 21:00 | Available Max Generation : |  | 17615
E.P. Demand (at gen end) : |  |  | 13790 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14100
Maximum Generation : |  |  | 13760 | MW Hour : | 23:00 | Reserve(Generation end) |  | 3515
Total Gen. (MKWH) : |  |  | 318.9257 | System Load Factor : | 96.57% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 274 | MW at | 8:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-08
Actual : |  | 97.05 | Ft.(MSL) , | Rule curve : | 91.24 | Ft.( MSL )
Gas Consumed : |  | Total = | 1055.71 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 555939953.914
: |  |  | Coal : | 736665018.59 | Oil : | 300867713.43 | Total : | 1593472685.934
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 48 | 1152:00 | 4695.4665 |  |  | 0 | -14.58%
Chittagong Area |  | 0 | 0:00 | 1291.088 |  |  | 0 | -12.74%
Khulna Area |  | 0 | 0:00 | 1808.7915 |  |  | 0 | -12.35%
Rajshahi Area |  | 0 | 0:00 | 1572.379 |  |  | 0 | -11.93%
Cumilla Area |  | 0 | 0:00 | 1293.6804 |  |  | 0 | -12.19%
Mymensingh Area |  | 0 | 0:00 | 962.2882 |  |  | 0 | -11.83%
Sylhet Area |  | 0 | 0:00 | 539.2681 |  |  | 0 | -12.52%
Barisal Area |  | 0 | 0:00 | 449.5289 |  |  | 0 | -11.76%
Rangpur Area |  | 0 | 0:00 | 879.1971 |  |  | 0 | -11.77%
Total |  | 48 |  | 13491.6877 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
09:08 |  | Faridpur 230/132KV ATR-1 S/D.
12:17 |  | Faridpur 230/132KV ATR-1 S/D Withdraw.
12:29 |  | Faridpur 230/132KV ATR-2 S/D.
14:17 |  | At Faridpur S/S, 230/132KV ATR-2 S/D Withdraw.
15:58 | 16:24 | Keranigonj 230/132/33kV S/S TR-1 Tripped showing o/c operated, 86.1 relay operated relays Due to due to atibazar feeder |  |  |  |  | 45 MW load interrup.
21:46 |  | Siddhirgonj 2*120 MW GTPP Synchronized with remarks:- GT-2
22:17 |  | Baroirhat-Hathazari 132 kV Ckt-2 Forced S/D from Baroirhat 132/33kV end. |  |  |  |  | 10 MW load interrup in
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-07
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4654344
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 232090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 409 | 9885600
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9977500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 296 | 7186705
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 79508 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 204 | 27340000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7439040
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 26928 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 462600
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 147 | 1464000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 95029 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 61170 | Low demand
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 40 | 906720 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 498600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 14 | 231000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 145920 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 90327 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 1959840 | Low demand
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 667200
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 288000 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 80640 | Low demand
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 201173
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 2445 | 73973934
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 0 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 42660
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 212 | 5155867
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 219 | 5210309
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 122945 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 49019 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Reserve
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 55680 | Low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 540000
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25195
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 32 | 225818 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | Reserve
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 81600 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 0 | 0 | Reserve
60 | SS Power I |  | SS Power | 2*612 | 1224 | 400 | 9469090 | Unit-1 Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 17 | 561600
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 1150 | 23330909
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 2113 | 44870692
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 5222000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7058000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 295 | 7355300 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 35 | 809280 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 49 | 1154400 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 185 | 3462545
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1149652
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 176080 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1652630 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 1932000 | Fuel shortage
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 90 | 1977600
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 452837 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 430290 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 634980 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 47 | 697200 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 49 | 1397760 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 322000
| Cumilla Area Total |  |  |  | 2950 | 1651 | 35884554
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 138 | 3950400 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13300
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 101 | 854400 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 1160400 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 273840
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 30480 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 0 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 337 | 6282820
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 942000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1371480 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3616855
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 162604 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 10 | 247680 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 132 | 3205480 | ST Under maint
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 265152 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7233000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 269 | 6315000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 7959200 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1329 | 31318451
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 805 | 20657454
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 32140 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 35200 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 309 | 7807392 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 4800 | Reserve
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 504720
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 916 | 20130911
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 2030 | 49172617
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 191148
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1625000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 24708500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 529964
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 250 | 4887300
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 1959
| Barisal Area Total |  |  |  | 2236 | 1638 | 31943871
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 155 | 4211091 | Gas shortage
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 8576072
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 155178 | Reserve
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 122562 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 59604 | Reserve
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | Reserve
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | Reserve
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25620
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1302 | 26312728
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 293250
| Rajshahi Area Total |  |  |  | 3381 | 1914 | 39756105
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 62 | 1415127
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 1721740 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47655
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1048512
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 206587
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1283000
| Rangpur Area Total |  |  |  | 950 | 283 | 5722621
| Total |  |  |  | 26947 | 13740 | 318925665
| Eastern Grid Total |  |  |  | 16526 | 7875 | 192330451
| Western Grid Total |  |  |  | 10421 | 5865 | 126595214
| National Grid Total |  |  |  | 26947 | 13740 | 318925665
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-08-07 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7457.97 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4067.4 | MW
i) Dhaka area |  |  | 3627.97 |  | MW | i) Khulna area |  |  |  | 1502.9 | MW
ii) Chattogram area |  |  | 1008 |  | MW | ii) Barishal area |  |  |  | 398.5 | MW
iii) Cumilla area |  |  | 1254 |  | MW | iii) Rajshahi area |  |  |  | 1256 | MW
iv) Mymensingh area |  |  | 1035 |  | MW | iv) Rangpur area |  |  |  | 910 | MW
v) Sylhet area |  |  | 533 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11525.37 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 5 | 00:00 | 67 | Jamalpur | 119 | 20:00 | 133 | Rahim | 39 | 07:00
2 | AKSML | 92 | 12:00 | 68 | Jashore | 138 | 19:30 | 134 | Rajbari | 76 | 19:30
3 | Aftabnagar | 32 | 14:00 | 69 | Jhenaidah | 126 | 19:00 | 135 | Rajendrapur | 94 | 22:00
4 | Agargaon | 104 | 13:00 | 70 | Joydebpur | 178 | 21:00 | 136 | Rajshahi | 106 | 21:00
5 | Agrabad | 86 | 12:00 | 71 | Joypurhat | 62 | 21:00 | 137 | Rajshahi-230 | 73 | 13:00
6 | Amnura | 67 | 21:00 | 72 | Juldah | 23 | 12:00 | 138 | Ramganj | 108 | 19:00
7 | Ashuganj | 80 | 00:00 | 73 | KSRM | 19 | 12:00 | 139 | Rampur | 35 | 00:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 194 | 15:00 | 140 | Rangamati | 18 | 18:30
9 | BSRM | 188 | 13:00 | 75 | Kachua | 74 | 22:00 | 141 | Rangpur | 141 | 19:00
10 | Bagerhat | 89 | 22:00 | 76 | Kallyanpur | 102 | 20:00 | 142 | Ruppur | 6.8 | 10:00
11 | Bakulia | 85 | 15:00 | 77 | Kalurghat | 34 | 10:00 | 143 | SSM | 0 | 00:00
12 | Banani | 56 | 11:00 | 78 | Kamrangirchar | 46.6 | 13:00 | 144 | Saidpur | 108 | 19:00
13 | Bangabhaban | 23 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 115 | 00:00
14 | Barapukuria | 63 | 19:30 | 80 | Kazla | 90 | 12:00 | 146 | Satmasjid | 101 | 14:00
15 | Barguna | 20 | 21:00 | 81 | Keranigonj | 76 | 19:00 | 147 | Savar | 176 | 15:00
16 | Barishal | 108 | 13:00 | 82 | Khagrachori | 30 | 19:30 | 148 | SevenRings | 5.34 | 11:00
17 | Barishal-230 | 82 | 22:00 | 83 | Khulna | 57 | 13:00 | 149 | ShahCement | 12 | 00:00
18 | Baroaulia | 65 | 00:00 | 84 | Khulshi | 141 | 00:00 | 150 | Shahjadpur | 80 | 20:00
19 | Baroirhat | 53 | 22:00 | 85 | Kishoreganj | 162 | 22:00 | 151 | Shahjibazar | 130 | 21:00
20 | Bashundhara | 151 | 13:00 | 86 | Kodda | 248 | 21:00 | 152 | Shahmirpur | 53.5 | 00:00
21 | BashundharaCement | 0 | 00:00 | 87 | Kulaura | 58 | 19:00 | 153 | Shariatpur | 81 | 00:00
22 | Beanibazar | 78 | 20:00 | 88 | Kurigram | 64 | 19:00 | 154 | Sherpur | 142 | 23:00
23 | Benapole | 58 | 21:00 | 89 | Kushtia | 124 | 19:30 | 155 | Shikalbaha | 23 | 22:00
24 | Bhaluka | 118 | 19:00 | 90 | Lalbag | 69 | 19:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 50 | 22:00 | 91 | Lalmonirhat | 64 | 21:00 | 157 | Shitalakhya | 75 | 12:00
26 | Bhangura | 36 | 21:00 | 92 | MI_Cement | 12.7 | 13:00 | 158 | Sholosohor | 41 | 15:00
27 | Bheramara(GK) | 64 | 01:00 | 93 | Madanganj | 20 | 00:00 | 159 | Shyampur | 134 | 12:00
28 | Bhulta | 216 | 12:00 | 94 | Madaripur | 110 | 22:00 | 160 | Siddhirganj | 116 | 12:00
29 | Bog-Sherpur | 64 | 21:00 | 95 | Madartek | 85.6 | 23:00 | 161 | Sirajganj | 112 | 20:00
30 | Bogura | 160 | 20:00 | 96 | Madunaghat | 50 | 19:00 | 162 | Sonargaon | 85 | 23:00
31 | Borhanuddin | 77 | 00:00 | 97 | Magura | 64 | 19:30 | 163 | Sreemongol | 70 | 22:00
32 | Brahmanbaria | 167 | 20:00 | 98 | Mahasthangarh | 78 | 00:00 | 164 | Sreepur | 91 | 19:30
33 | Cantonment | 106 | 13:00 | 99 | Manikganj | 103 | 21:00 | 165 | Srinagar | 46.61 | 22:00
34 | Chandpur | 69 | 22:00 | 100 | Maniknagar | 57 | 13:00 | 166 | Sunamganj | 61 | 21:00
35 | Chandraghona | 32 | 19:30 | 101 | Matarbari | 43 | 00:00 | 167 | Sylhet | 50 | 20:00
36 | Chapai | 65 | 22:00 | 102 | Matuail | 66 | 12:00 | 168 | Sylhet-132 | 114 | 14:00
37 | Charsaidpur | 21 | 01:00 | 103 | Millgate | 110 | 15:00 | 169 | TK | 30 | 01:00
38 | Chauddagram | 67 | 23:00 | 104 | Mirpur | 129 | 15:00 | 170 | Tangail | 200 | 20:00
39 | Chhatak | 35 | 19:30 | 105 | Mirsorai | 6 | 15:00 | 171 | Thakurgaon | 100 | 19:30
40 | Chowmuhani | 213 | 21:00 | 106 | Mirzapur | 61 | 19:30 | 172 | Tongi | 104 | 15:00
41 | Chuadanga | 110 | 22:00 | 107 | Mithapukur | 60 | 00:00 | 173 | Ullahpara | 24 | 00:00
42 | Coxsbazar | 108 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 52 | 15:00
43 | Cumilla(N) | 160 | 00:00 | 109 | Mogbazar | 110.6 | 13:00 | 175 | Uttara | 76 | 13:00
44 | Cumilla(S) | 172 | 22:00 | 110 | Mongla | 38 | 12:00 | 176 | UttaraNew | 54 | 23:00
45 | Daudkandi | 149 | 21:00 | 111 | Motijheel | 35 | 13:00 | 177 | Zigatola | 76 | 12:00
46 | Dhaka | 40 | 11:00 | 112 | Munshiganj | 106 | 00:00
47 | Dhamrai | 122 | 08:00 | 113 | Mymensingh | 240 | 21:00
48 | Dhanmondi | 114 | 13:00 | 114 | Naogaon | 126 | 23:00
49 | Dohazari | 92 | 19:30 | 115 | Narail | 55 | 20:00
50 | Faridpur | 160 | 19:00 | 116 | Narinda | 53 | 13:00
51 | Fatullah | 79 | 10:00 | 117 | Narshingdi | 165 | 00:00
52 | Fenchuganj | 43 | 19:00 | 118 | Natore | 153 | 00:00
53 | Feni | 104 | 22:00 | 119 | Nawabganj | 49 | 22:00
54 | GPH | 88 | 19:00 | 120 | Netrakona | 139 | 22:00
55 | Ghatail | 68 | 19:30 | 121 | New | 51 | 12:00
56 | Ghorashal | 49 | 00:00 | 122 | Niamatpur | 72 | 00:00
57 | Goalpara | 36 | 13:00 | 123 | Noapara | 42 | 19:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 389 | 06:00 | 376 | 15:00 | Kaliakoir | 380 | 6:00 | 365 | 14:00
| Ashuganj | 404 | 6:00 | 389 | 12:00 | Madunaghat_I | 398 | 7:00 | 386 | 14:00
| Bhulta | 400 | 06:00 | 384 | 15:00 | Meghnaghat | 384 | 04:00 | 370 | 15:00
| Bibiana | 396 | 06:00 | 389 | 12:00 | Payra | 411 | 06:00 | 403 | 00:00
| BIPTC | 402 | 05:00 | 394 | 20:00 | Rahanpur | 403 | 06:00 | 386 | 23:00
| Bogura | 391 | 09:00 | 371 | 00:00 | Rampal | 403 | 07:00 | 390 | 00:00
| Gopalganj | 399 | 06:00 | 387 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 06:00 | 220 | 15:00 | Haripur | 232 | 04:00 | 225 | 15:00
| AKSML | 232 | 06:00 | 224 | 14:00 | Hasnabad | 230 | 00:00 | 223 | 14:00
| Aminbazar | 232 | 04:00 | 220 | 13:00 | Hathazari | 235 | 06:00 | 228 | 15:00
| Ashuganj | 237 | 06:00 | 228 | 14:00 | Ishurdi | 237 | 18:30 | 226 | 00:00
| Ashuganj-400 | 236 | 6:00 | 221 | 14:00 | Jhenaidah | 229 | 18:30 | 214 | 23:00
| Baghabari | 232 | 05:00 | 222 | 00:00 | Kaliakoir | 235 | 18:00 | 224 | 15:00
| Barapukuria | 212 | 18:30 | 200 | 19:00 | Keranigonj | 231 | 06:00 | 220 | 13:00
| Barapukuria-230 | 212 | 18:30 | 200 | 19:00 | Khulna(S) | 231 | 18:30 | 217 | 23:00
| Barishal | 233 | 07:00 | 224 | 00:00 | Madunaghat_I | 234 | 7:00 | 227 | 14:00
| Bheramara | 235 | 18:30 | 224 | 00:00 | Maniknagar | 233 | 04:00 | 224 | 15:00
| Bhulta | 235 | 06:00 | 225 | 12:00 | Meghnaghat | 239 | 07:00 | 231 | 14:00
| Bibiana | 228 | 06:00 | 222 | 00:00 | Meghnaghat-400 | 235 | 18:30 | 227 | 15:00
| BIPTC | 237 | 18:30 | 224 | 00:00 | Mirsorai | 230 | 08:00 | 221 | 15:00
| Bogura | 225 | 06:00 | 213 | 00:00 | Rajshahi | 235 | 06:00 | 222 | 00:00
| Bogura-400 | 225 | 18:00 | 214 | 00:00 | Rampal | 230 | 06:00 | 219 | 00:00
| Borhanuddin | 240 | 17:00 | 231 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 230 | 05:00 | 221 | 13:00 | Rampura | 233 | 06:00 | 223 | 12:00
| Cumilla(N) | 231 | 18:00 | 221 | 15:00 | Shikalbaha | 231 | 07:00 | 223 | 16:00
| Faridpur | 236 | 08:00 | 226 | 00:00 | Shyampur | 233 | 06:00 | 223 | 13:00
| Fenchuganj | 231 | 18:30 | 223 | 15:00 | Siddhirganj | 235 | 04:00 | 227 | 12:00
| Ghorashal | 235 | 18:00 | 230 | 00:00 | Sirajgonj | 237 | 06:00 | 230 | 00:00
| Ghorashal-230 | 233 | 05:00 | 224 | 15:00 | Sreepur | 231 | 06:00 | 223 | 15:00
| Gopalganj | 235 | 06:00 | 227 | 00:00 | Tongi | 231 | 07:00 | 222 | 15:00
| GPH | 231 | 18:30 | 223 | 05:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 135 | 18:00 | 127 | 13:00 | Kushtia | 137 | 18:00 | 129 | 22:00
| Agargaon | 135 | 06:00 | 127 | 13:00 | Lalbag | 135 | 05:00 | 123 | 23:00
| Agrabad | 132 | 05:00 | 128 | 11:00 | Lalmonirhat | 125 | 16:00 | 115 | 19:00
| AKS | 132 | 06:00 | 126 | 15:00 | Madanganj | 132 | 18:00 | 126 | 15:00
| Aminbazar | 140 | 04:00 | 123 | 11:00 | Madaripur | 133 | 18:30 | 128 | 00:00
| Amnura | 138 | 18:30 | 120 | 23:00 | Madartek | 134 | 05:00 | 127 | 12:00
| Ashuganj | 139 | 06:00 | 135 | 13:00 | Madunaghat | 134 | 06:00 | 129 | 13:00
| Bagerhat | 133 | 18:00 | 118 | 22:00 | Magura | 137 | 18:00 | 126 | 23:00
| Bakulia | 133 | 18:30 | 128 | 15:00 | Mahasthangarh | 131 | 18:00 | 122 | 00:00
| Banani | 134 | 05:00 | 127 | 11:00 | Manikganj | 131 | 06:00 | 124 | 10:00
| Bangabhaban | 133 | 06:00 | 126 | 11:00 | Maniknagar | 133 | 05:00 | 125 | 13:00
| Barapukuria | 132 | 18:30 | 123 | 02:00 | Matarbari | 125 | 09:00 | 116 | 00:00
| Barguna | 133 | 07:00 | 128 | 00:00 | Matuail | 133 | 03:00 | 127 | 13:00
| Barishal | 138 | 18:30 | 131 | 00:00 | Millgate | 135 | 03:00 | 127 | 14:00
| Barishal-230 | 138 | 06:00 | 131 | 23:00 | Mirpur | 138 | 06:00 | 128 | 13:00
| Baroaulia | 132 | 01:00 | 129 | 14:00 | Mirzapur | 129 | 07:00 | 123 | 15:00
| Baroirhat | 155 | 10:00 | 113 | 15:00 | Mithapukur | 129 | 18:30 | 120 | 00:00
| Bashundhara | 136 | 05:00 | 124 | 10:00 | MI_Cement | 133.3 | 06:00 | 127 | 12:00
| BashundharaCement | 132 | 18:00 | 126 | 15:00 | Modern | 133 | 06:00 | 128 | 15:00
| Beanibazar | 124 | 08:00 | 117 | 22:00 | Mogbazar | 135 | 04:00 | 129 | 12:00
| Benapole | 134 | 18:30 | 120 | 23:00 | Mongla | 132 | 18:00 | 119 | 23:00
| Bhaluka | 127 | 06:00 | 120 | 15:00 | Motijheel | 133 | 06:00 | 126 | 11:00
| Bhandaria | 134 | 09:00 | 125 | 00:00 | Munshiganj | 131 | 04:00 | 125 | 14:00
| Bhangura | 136 | 18:00 | 130 | 00:00 | Mymensingh | 131 | 11:00 | 114 | 22:00
| Bheramara | 137 | 18:30 | 131 | 00:00 | Naogaon | 130 | 18:00 | 118 | 00:00
| Bheramara(GK) | 137 | 18:00 | 131 | 00:00 | Narail | 137 | 18:30 | 125 | 22:00
| Bhulta | 124 | 18:00 | 117 | 12:00 | Narinda | 133 | 05:00 | 125 | 13:00
| Bog-Sherpur | 133 | 18:00 | 124 | 00:00 | Narshingdi | 124 | 03:00 | 117 | 00:00
| Bogura | 134 | 18:00 | 126 | 00:00 | Natore | 135 | 18:30 | 126 | 00:00
| Bogura-230 | 134 | 18:00 | 126 | 00:00 | Nawabganj | 135 | 06:00 | 128 | 13:00
| Brahmanbaria | 130 | 07:00 | 124 | 00:00 | Netrakona | 130 | 09:00 | 123 | 00:00
| Cantonment | 135 | 06:00 | 127 | 12:00 | New | 136 | 03:00 | 128 | 15:00
| Chandpur | 133 | 18:30 | 121 | 12:00 | Niamatpur | 136 | 09:00 | 127 | 22:00
| Chandraghona | 135 | 07:00 | 131 | 00:00 | Noapara | 135 | 18:30 | 124 | 23:00
| Chapai | 133 | 18:30 | 123 | 22:00 | Pabna | 136 | 18:30 | 128 | 00:00
| Charsaidpur | 133 | 05:00 | 127 | 12:00 | Palashbari | 127 | 18:30 | 116 | 19:00
| Chauddagram | 127 | 18:00 | 119 | 00:00 | Panchagarh | 132 | 18:30 | 115 | 02:00
| Chhatak | 125 | 06:00 | 118 | 00:00 | Patuakhali | 133 | 07:00 | 128 | 00:00
| Chowmuhani | 120 | 18:30 | 114 | 23:00 | Payra | 136 | 18:00 | 131 | 00:00
| Chuadanga | 133 | 16:00 | 117 | 23:00 | PHP | 125 | 20:00 | 112 | 12:00
| Coxsbazar | 125 | 08:00 | 115 | 00:00 | Postogola | 135 | 06:00 | 130 | 12:00
| Cumilla(N) | 134 | 18:30 | 126 | 00:00 | Purbachal | 136 | 05:00 | 127 | 12:00
| Cumilla(S) | 132 | 18:30 | 124 | 13:00 | Purbasadipur | 130 | 18:00 | 118 | 10:00
| Daudkandi | 122 | 04:00 | 116 | 11:00 | Rahanpur | 136 | 06:00 | 129 | 23:00
| Dhaka | 136 | 18:30 | 128 | 12:00 | Rahim | 133 | 05:00 | 127 | 13:00
| Dhamrai | 133 | 18:30 | 126 | 15:00 | Rajbari | 133 | 18:30 | 126 | 00:00
| Dhanmondi | 133 | 06:00 | 126.5 | 13:00 | Rajendrapur | 136 | 20:00 | 127 | 15:00
| Dohazari | 131 | 07:00 | 124 | 00:00 | Rajshahi | 136 | 18:30 | 127 | 22:00
| Faridpur | 132 | 18:00 | 127 | 00:00 | Rajshahi-230 | 136 | 18:30 | 117 | 23:00
| Fatullah | 135 | 06:00 | 128 | 13:00 | Ramganj | 126 | 18:00 | 115 | 12:00
| Fenchuganj | 132 | 07:00 | 128 | 21:00 | Rampur | 133 | 18:30 | 128 | 00:00
| Feni | 125 | 18:30 | 115 | 12:00 | Rampura | 134 | 04:00 | 128 | 10:00
| Ghatail | 128 | 05:00 | 120 | 22:00 | Rangamati | 133 | 08:00 | 130 | 00:00
| Ghorashal | 139 | 05:00 | 133 | 14:00 | Rangpur | 127 | 16:00 | 118 | 00:00
| Goalpara | 138 | 18:00 | 126 | 23:00 | Ruppur | 137 | 07:00 | 131 | 00:00
| Gollamari | 136 | 18:00 | 127 | 23:00 | Saidpur | 128 | 18:30 | 115 | 03:00
| Gopalganj | 134 | 18:30 | 125 | 23:00 | Satkhira | 134 | 18:00 | 120 | 23:00
| Gopalganj-400 | 133 | 06:00 | 128 | 00:00 | Satmasjid | 134 | 04:00 | 126 | 13:00
| Gulshan | 135 | 18:30 | 128 | 10:00 | Savar | 136 | 07:00 | 126 | 15:00
| Halishahar | 132 | 04:00 | 127 | 15:00 | SevenRings | 139 | 04:00 | 134 | 12:00
| Haripur | 133 | 04:00 | 127 | 12:00 | ShahCement | 133 | 05:00 | 127 | 12:00
| HaripurSBU | 133 | 04:00 | 127 | 12:00 | Shahjadpur | 140 | 18:30 | 132 | 19:30
| Hasnabad | 136 | 05:00 | 129 | 15:00 | Shahjibazar | 129 | 18:30 | 122 | 00:00
| Hathazari | 135 | 06:00 | 131 | 00:00 | Shahmirpur | 133 | 07:00 | 128 | 15:00
| Ishurdi | 139 | 18:30 | 132 | 00:00 | Shariatpur | 134 | 18:30 | 125 | 00:00
| Jaldhaka | 126 | 18:30 | 114 | 19:00 | Sherpur | 129 | 20:00 | 115 | 07:00
| Jamalpur | 132 | 19:30 | 120 | 01:00 | Shikalbaha | 123 | 07:00 | 117 | 01:00
| Jashore | 135 | 18:30 | 122 | 22:00 | Shikalbaha-230 | 134 | 08:00 | 129 | 00:00
| Jhenaidah | 139 | 18:00 | 128 | 22:00 | Shitalakhya | 133.3 | 06:00 | 127 | 12:00
| Jhenaidah-230 | 139 | 18:00 | 128 | 23:00 | Sholosohor | 133 | 06:00 | 128 | 13:00
| Joydebpur | 138 | 20:00 | 129 | 15:00 | Shyampur | 134 | 08:00 | 127 | 15:00
| Joypurhat | 129 | 18:30 | 117 | 00:00 | Shyampur-230 | 135 | 06:00 | 128 | 12:00
| Juldah | 131 | 05:00 | 128 | 00:00 | Siddhirganj | 133 | 05:00 | 127 | 16:00
| Kabirpur | 140 | 20:00 | 125 | 15:00 | Sirajganj | 133 | 18:00 | 126 | 00:00
| Kachua | 132 | 18:30 | 122 | 11:00 | Sonargaon | 130 | 07:00 | 125 | 15:00
| Kaliakoir | 133 | 6:00 | 124 | 16:00 | Sreemongol | 128 | 07:00 | 122 | 00:00
| Kallyanpur | 132 | 04:00 | 127 | 13:00 | Sreepur | 130 | 05:00 | 124 | 15:00
| Kalurghat | 134 | 06:00 | 128 | 15:00 | Srinagar | 134 | 05:00 | 127 | 15:00
| Kamrangirchar | 135 | 05:00 | 125 | 15:00 | SSM | 138 | 04:00 | 132 | 00:00
| Kaptai | 134 | 6:00 | 127 | 16:00 | Sunamganj | 122 | 06:00 | 116 | 00:00
| Kazla | 133 | 06:00 | 125 | 13:00 | Sylhet | 127 | 07:00 | 122 | 21:00
| Keranigonj | 135 | 06:00 | 128 | 13:00 | Sylhet-132 | 127 | 07:00 | 122 | 23:00
| Khagrachori | 133 | 06:00 | 129 | 13:00 | Tangail | 127 | 05:00 | 120 | 00:00
| Khulna | 136 | 18:00 | 125 | 22:00 | Thakurgaon | 130 | 18:30 | 113 | 03:00
| Khulna(S) | 138 | 18:30 | 127 | 22:00 | TK | 132 | 08:00 | 129 | 00:00
| Khulshi | 132 | 07:00 | 127 | 00:00 | Tongi | 135 | 04:00 | 129 | 13:00
| Kishoreganj | 130 | 17:00 | 122 | 15:00 | Ullahpara | 134 | 07:00 | 129 | 00:00
| Kodda | 136 | 19:30 | 127 | 14:00 | Ullon | 134 | 05:00 | 128 | 10:00
| KSRM | 133 | 06:00 | 128 | 14:00 | Uttara | 137 | 05:00 | 128 | 15:00
| Kulaura | 131 | 08:00 | 126 | 23:00 | UttaraNew | 137 | 02:00 | 127 | 15:00
| Kurigram | 126 | 18:00 | 115 | 22:00 | Zigatola | 135 | 06:00 | 128 | 13:00

## L-Curve
Date | 2024-08-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 560 | 7650 | 5943 | 13593 |  |  |  | QF-LDC-11
0:30 | 590 | 7296 | 5854.5 | 13150.5 | Date: | 2024-08-07
1:00 | 620 | 6942 | 5766 | 12708
1:30 | 609 | 6916 | 5626 | 12542
2:00 | 598 | 6890 | 5486 | 12376
2:30 | 574 | 6829.5 | 5381.5 | 12211 | [5 empty] | Gen. at Eve. Peak | 13740 | 13740 MW (21:00 )
3:00 | 550 | 6769 | 5277 | 12046 | [6 empty] | 21:00
3:30 | 532 | 6743.5 | 5178.5 | 11922 | [5 empty] | Gen. at Day Peak | 12249 | 12249 MW (12:00 )
4:00 | 514 | 6718 | 5080 | 11798 | [6 empty] | 12:00
4:30 | 484 | 6713.5 | 5048.5 | 11762 | [5 empty] | Highest Generation | 13760
5:00 | 454 | 6709 | 5017 | 11726 | [6 empty] | 23:00
5:30 | 447 | 6515.5 | 4915.5 | 11431
6:00 | 440 | 6322 | 4814 | 11136
6:30 | 359 | 6345.5 | 4782.5 | 11128
7:00 | 278 | 6369 | 4751 | 11120
7:30 | 276 | 6339 | 4777 | 11116
8:00 | 274 | 6309 | 4803 | 11112
8:30 | 327.5 | 6388.5 | 4832.5 | 11221
9:00 | 381 | 6468 | 4862 | 11330
9:30 | 394 | 6564 | 4938.5 | 11502.5
10:00 | 407 | 6660 | 5015 | 11675
10:30 | 457.5 | 6722 | 5109.5 | 11831.5
11:00 | 508 | 6784 | 5204 | 11988
11:30 | 568 | 6813.5 | 5305 | 12118.5
12:00 | 628 | 6843 | 5406 | 12249
12:30 | 798 | 6883.5 | 5517 | 12400.5
13:00 | 968 | 6924 | 5628 | 12552
13:30 | 893 | 6924.5 | 5644.5 | 12569
14:00 | 818 | 6925 | 5661 | 12586
14:30 | 857 | 6964 | 5662.5 | 12626.5
15:00 | 896 | 7003 | 5664 | 12667
15:30 | 868 | 6890.5 | 5637 | 12527.5
16:00 | 840 | 6778 | 5610 | 12388
16:30 | 816 | 6663.5 | 5448 | 12111.5
17:00 | 792 | 6549 | 5286 | 11835
17:30 | 734 | 6364 | 5120.5 | 11484.5
18:00 | 676 | 6179 | 4955 | 11134
18:30 | 671 | 6721 | 5351.5 | 12072.5
19:00 | 666 | 7263 | 5748 | 13011
19:30 | 610 | 7613 | 5975 | 13588
20:00 | 632 | 7611 | 5921 | 13532 |  |  |  | Executive Engineer
20:30 | 598 | 7743 | 5893 | 13636 |  |  |  | Network Operation Division
21:00 | 564 | 7875 | 5865 | 13740
21:30 | 540 | 7840.5 | 5875 | 13715.5
22:00 | 516 | 7806 | 5885 | 13691 |  |  |  |  | Page 6 of 7
22:30 | 543 | 7848.5 | 5877 | 13725.5
23:00 | 570 | 7891 | 5869 | 13760
23:30 | 565 | 7770.5 | 5906 | 13676.5
24:00 | 560 | 7650 | 5943 | 13593
13740 MW (21:00 )
12249 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-07 |  | Energy |  | 318925665
[15 empty] | 2024-08-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3906 | 911 | 2213 | 0 | 937 | 5179 | 214 | 0 | 125 | 94 | 0 | 14 | 197.685
0:30 | 3879 | 914.5 | 2151.5 | 0 | 744 | 5048 | 213.5 | 0 | 102 | 88 | 0 | 10 | 190.5225 |  |  | Date: | 44049
1:00 | 3852 | 918 | 2090 | 0 | 551 | 4917 | 213 | 0 | 79 | 82 | 0 | 6 | 183.36
1:30 | 3859.5 | 915 | 2088.5 | 0 | 509 | 4787.5 | 212.5 | 0 | 79 | 82 | 0 | 9 | 174.765 | [9 empty] | Total Energy | 318.9257 | 318.9257 | Total Energy Gen 318.926 MKWHr Energy Not Served 3.746 MKWHr Energy Requirement 322.672 MKWHr
2:00 | 3867 | 912 | 2087 | 0 | 467 | 4658 | 212 | 0 | 79 | 82 | 0 | 12 | 166.17 | [9 empty] | Energy not Served | 3.746 | 3.746
2:30 | 3837.5 | 912.5 | 2099 | 0 | 447.5 | 4561.5 | 212 | 0 | 47.5 | 81 | 0 | 12.5 | 156.62 | [9 empty] | Energy Requirement | 322.6717 | 322.6717
3:00 | 3808 | 913 | 2111 | 0 | 428 | 4465 | 212 | 0 | 16 | 80 | 0 | 13 | 147.07
3:30 | 3807.5 | 914.5 | 2106.5 | 0 | 410.5 | 4364 | 211.5 | 0 | 16 | 79 | 0 | 12.5 | 146.115 | [8 empty] | Shortage
4:00 | 3807 | 916 | 2102 | 0 | 393 | 4263 | 211 | 0 | 16 | 78 | 0 | 12 | 145.16
4:30 | 3805.5 | 917 | 2089.5 | 0 | 393 | 4241.5 | 211 | 0 | 16 | 78 | 0 | 10.5 | 155.665
5:00 | 3804 | 918 | 2077 | 0 | 393 | 4220 | 211 | 0 | 16 | 78 | 0 | 9 | 166.17
5:30 | 3726 | 917.5 | 2024 | 0 | 359 | 4081 | 211.5 | 0 | 16 | 75 | 6 | 15 | 161.395
6:00 | 3648 | 917 | 1971 | 0 | 325 | 3942 | 212 | 0 | 16 | 72 | 12 | 21 | 156.62
6:30 | 3693 | 917 | 1969 | 0 | 327 | 3858 | 212 | 0 | 16 | 70 | 45 | 21 | 149.935 | [7 empty] | Coal
7:00 | 3738 | 917 | 1967 | 0 | 329 | 3774 | 212 | 0 | 16 | 68 | 78 | 21 | 143.25
7:30 | 3703 | 917.5 | 1958 | 0 | 331 | 3766 | 212 | 0 | 16 | 68 | 120 | 24.5 | 170.945 | [6 empty] | Oil
8:00 | 3668 | 918 | 1949 | 0 | 333 | 3758 | 212 | 0 | 16 | 68 | 162 | 28 | 198.64
8:30 | 3665 | 918.5 | 1947.5 | 0 | 328 | 3782 | 212 | 0 | 16 | 71 | 242 | 39 | 204.37
9:00 | 3662 | 919 | 1946 | 0 | 323 | 3806 | 212 | 0 | 16 | 74 | 322 | 50 | 210.1
9:30 | 3752 | 918.5 | 1973.5 | 0 | 326 | 3863.5 | 212 | 0 | 28 | 77 | 313 | 39 | 222.0375
10:00 | 3842 | 918 | 2001 | 0 | 329 | 3921 | 212 | 0 | 40 | 80 | 304 | 28 | 233.975
10:30 | 3846 | 918 | 2010.5 | 0 | 329.5 | 3995 | 212 | 0 | 52 | 83 | 357.5 | 28 | 218.2175
11:00 | 3850 | 918 | 2020 | 0 | 330 | 4069 | 212 | 0 | 64 | 86 | 411 | 28 | 202.46
11:30 | 3851.5 | 918 | 2057.5 | 0 | 353.5 | 4209 | 212 | 0 | 64 | 83 | 346 | 24 | 197.2075
12:00 | 3853 | 918 | 2095 | 0 | 377 | 4349 | 212 | 0 | 64 | 80 | 281 | 20 | 191.955
12:30 | 3818 | 917.5 | 2091.5 | 0 | 410.5 | 4434 | 212 | 0 | 64 | 85 | 345.5 | 22.5 | 169.4775
13:00 | 3783 | 917 | 2088 | 0 | 444 | 4519 | 212 | 0 | 64 | 90 | 410 | 25 | 147
13:30 | 3783 | 917 | 2088 | 0 | 444 | 4519 | 212 | 0 | 64 | 90 | 410 | 25 | 147
14:00 | 3783 | 917 | 2088 | 0 | 444 | 4519 | 212 | 0 | 64 | 90 | 410 | 25 | 147
14:30 | 3807 | 917.5 | 2087.5 | 0 | 442.5 | 4582.5 | 212 | 0 | 64 | 86 | 381.5 | 29 | 179.9825
15:00 | 3831 | 918 | 2087 | 0 | 441 | 4646 | 212 | 0 | 64 | 82 | 353 | 33 | 212.965
15:30 | 3780 | 914.5 | 2032 | 0 | 445.5 | 4688 | 212 | 0 | 64 | 86 | 279 | 26.5 | 207.7125
16:00 | 3729 | 911 | 1977 | 0 | 450 | 4730 | 212 | 0 | 64 | 90 | 205 | 20 | 202.46
16:30 | 3659 | 906 | 1911.5 | 0 | 472.5 | 4629 | 212 | 0 | 64 | 86 | 152.5 | 19 | 170.4675
17:00 | 3589 | 901 | 1846 | 0 | 495 | 4528 | 212 | 0 | 64 | 82 | 100 | 18 | 138.475
17:30 | 3430 | 901 | 1815 | 0 | 548.5 | 4346 | 212 | 0 | 64 | 79 | 63.5 | 25.5 | 129.2375
18:00 | 3271 | 901 | 1784 | 0 | 602 | 4164 | 212 | 0 | 64 | 76 | 27 | 33 | 120
18:30 | 3514.5 | 901 | 1875.5 | 0 | 806 | 4484.5 | 212 | 0 | 151 | 82 | 13.5 | 32.5 | 121.5
19:00 | 3758 | 901 | 1967 | 0 | 1010 | 4805 | 212 | 0 | 238 | 88 | 0 | 32 | 123
19:30 | 3754 | 900 | 1939 | 0 | 1228 | 5146 | 212 | 0 | 295 | 90 | 0 | 24 | 156
20:00 | 3724 | 900 | 1927 | 0 | 1191 | 5175 | 212 | 0 | 281 | 92 | 0 | 30 | 189
20:30 | 3788.5 | 852.5 | 2050 | 0 | 1192 | 5172.5 | 212 | 0 | 254 | 91 | 0 | 23.5 | 118.5
21:00 | 3853 | 805 | 2173 | 0 | 1193 | 5170 | 212 | 0 | 227 | 90 | 0 | 17 | 48
21:30 | 3838 | 806.5 | 2178.5 | 0 | 1178 | 5179 | 212.5 | 0 | 210 | 94 | 0 | 19 | 52.1725
22:00 | 3823 | 808 | 2184 | 0 | 1163 | 5188 | 213 | 0 | 193 | 98 | 0 | 21 | 56.345
22:30 | 3905 | 808 | 2159.5 | 0 | 1137 | 5192.5 | 213.5 | 0 | 193 | 98 | 0 | 19 | 66.3725
23:00 | 3987 | 808 | 2135 | 0 | 1111 | 5197 | 214 | 0 | 193 | 98 | 0 | 17 | 76.4
23:30 | 3946.5 | 859.5 | 2174 | 0 | 1024 | 5188 | 214 | 0 | 159 | 96 | 0 | 15.5 | 137.0425 |  |  | Max Temp. in Dhaka |  | 33.5°C
24:00 | 3906 | 911 | 2213 | 0 | 937 | 5179 | 214 | 0 | 125 | 94 | 0 | 14 | 197.685
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 318.926 MKWHr Energy Not Served 3.746 MKWHr Energy Requirement 322.672 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 133 | 132 | 132 | 131 | 131 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 133 | 134 | 134 | 3231867
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1924000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [25 empty] | 0 | 0
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 3 | 6 | 9 | 16 | 5 | 7 |  | 1 | 1 | 0 | 0 | [8 empty] | 42660
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 223 | 223 | 223 | 225 | 224 | 221 | 220 | 218 | 218 | 217 | 216 | 216 | 217 | 217 | 217 | 201 |  | 197 | 219 | 219 | 219 | 219 | 220 | 222 | 5210309
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 17 | 17 | 17 | 17 |  |  |  | 49019
12 | Hathazari 100 MW peaking PP | [25 empty] | 0 | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 19 | 34 | 17 | 17 | 17 | 17 | 17 | 122945
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 15 | 15 | [17 empty] | 23 | 28 | 28 | 28 | 28 | 28 | 28 | 176080
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 135 | 135 | 75 | 75 | 75 | 75 | 75 | 75 | 77 | 75 | 76 | 75 | 75 | 75 | 139 | 140 | 73 | 80 |  | 79 | 76 | 71 | 204 | 204 | 201 | 140 | 27340000
17 | Siddhirganj 335 MW CCPP | 327 | 325 | 325 | 325 | 324 | 260 | 260 | 260 | 260 | 315 | 328 | 325 | 322 | 325 | 325 | 324 | 322 | 250 |  | 325 | 325 | 326 | 326 | 330 | 334 | 333 | 7439040
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 5 | 45 | 15 | 15 |  |  | 0 | 90327
19 | Ashuganj 195 MW PP (APSCL-United) | 160 | 160 | 160 | 158 | 158 | 138 | 138 | 138 | 138 | 138 | 138 | 140 | 140 | 138 | 138 | 138 | 138 | 88 |  | 88 | 88 | 88 | 185 | 187 | 187 | 187 | 3462545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 130 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4654344
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 526 | 475 | 473 | 472 | 470 | 418 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 353 | 350 | 340 |  | 350 | 385 | 400 | 400 | 400 | 400 | 401 | 9469090
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 32 | 29 | 33 | 32 | 34 | 31 | 31 | 34 |  | 35 | 35 | 35 | 35 | 33 | 33 | 35 | 809280
33 | Ashuganj 225 MW CCPP | 216 | 217 | 217 | 217 | 216 | 217 | 216 | 214 | 214 | 212 | 210 | 211 | 213 | 210 | 211 | 215 | 214 | 213 |  | 212 | 216 | 217 | 215 | 215 | 214 | 214 | 5222000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 345 | 280 | 270 | 310 | 305 | 335 | 305 | 320 | 305 | 305 | 305 | 270 |  | 340 | 300 | 270 | 270 | 270 | 305 | 300 | 7058000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 285 | 285 | 285 | 285 | 285 | 320 | 290 | 290 | 285 | 320 | 315 | 310 | 320 | 330 | 320 | 315 | 315 | 295 |  | 330 | 295 | 295 | 295 | 295 | 325 | 320 | 7355300
35 | Ashuganj 55 MW PP (Precision) | 46 | 52 | 51 | 51 | 51 | 51 | 49 | 51 | 49 | 49 | 48 | 44 | 44 | 41 | 43 | 44 | 46 | 47 |  | 47 | 48 | 49 | 49 | 49 | 50 | 51 | 1154400
36 | Chandpur 150 MW CCPP | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 85 | 85 | 86 | 80 | 80 | 80 | 70 | 70 | 70 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1652630
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 406 | 406 | 406 | 406 | 405 | 405 | 405 | 406 | 407 | 406 | 405 | 402 | 402 | 403 | 401 | 405 | 407 | 316 |  | 320 | 412 | 405 | 409 | 411 | 409 | 407 | 9885600
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 400 | 400 | 400 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 360 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9977500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 200 | 200 | 200 | 200 | 201 | 201 | 200 | 200 | 198 | 195 | 195 | 188 | 163 | 150 | 137 | 137 | 137 | 137 |  | 138 | 138 | 138 | 138 | 109 | 129 | 127 | 3950400
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 6 | 8 | 48 | 15 | 45 | 16 | 15 | 14 | 45 | 30 | 3 | 2 | [8 empty] | 273840
44 | Fenchugonj CCPP Phase-1 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 942000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 57 | 56 | 57 | 57 |  | 58 | 57 | 58 | 58 | 58 | 58 | 58 | 1371480
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 247680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 133 | 131 | 132 | 133 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 3205480
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 162604
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 8 | 12 | 12 | 265152
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 290 | 295 | 290 | 285 | 290 | 295 | 300 | 310 | 315 | 300 | 310 | 300 | 305 | 310 | 285 | 275 | 265 |  | 285 | 290 | 280 | 300 | 295 | 305 | 320 | 7233000
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 330 | 350 | 338 | 335 | 370 | 360 | 350 | 340 | 345 | 350 | 260 | 212 | 212 |  | 310 | 325 | 340 | 340 | 340 | 375 | 365 | 7959200
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 13 | 17 | 17 | 17 | 17 |  | 0 | 61170
59 | Tangail Palli Power Gen 22 MW | [20 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 30480
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 82 | 82 | 80 | 78 | 78 | 72 | 68 | 68 | 74 | 80 | 86 | 80 | 90 | 92 | 82 | 90 | 82 | 76 |  | 88 | 90 | 92 | 90 | 98 | 98 | 94 | 1977600
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 42 | 42 | 37 | 11 | 5 | 4 | 5 | 9 | 9 | 7 | 5 | 5 | 12 | 12 |  | 14 | 19 | 19 | 25 | 27 | 29 | 29 | 540000
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 430290
69 | Summit Ashulia | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 378600
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528120
71 | Maona 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 498600
72 | Rupganj 33 MW PP(Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 231000
73 | Ghorashal 108 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 27 | 27 | [15 empty] | 0 | 232090
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 27 | 52 | 70 | 70 | 70 | 70 | 634980
| Chowmuhani 113 MW | 29 | 28 | 28 | 28 | 27 | 28 | 28 | 27 | 17 | 9 | 9 | 10 | 16 | 13 | 27 | 28 | 28 | 44 |  | 47 | 47 | 47 | 47 | 47 | 42 | 32 | 697200
| Manikgonj 162MW PP(MPGL) | [19 empty] | 35 | 35 | 17 | 17 |  |  | 0 | 80640
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 145920
79 | Kodda 150 MW PP | 64 | 64 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 40 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 98 | 98 | 147 | 147 | 130 | 130 | 64 | 1464000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 22 | 37 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 452837
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 36 | 34 | 34 | 34 | 17 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 35 | 17 | 667200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 4 | 5 | 3 |  |  | 5 | 1 | 0 | 0 | [9 empty] | 25195
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 300 | 291 | 300 | 297 | 298 | 289 | 314 | 310 | 304 | 309 | 310 | 308 | 311 | 305 | 308 | 288 | 282 | 304 |  | 310 | 275 | 276 | 296 | 308 | 313 | 308 | 7186705
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | [6 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 288000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1149652
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 8 | 8 | 8 | 8 |  |  | 0 | 26928
95 | Patenga 50MW PP (Baraka)
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 1 | 15 | 15 | 15 | 15 | 15 | 15 | 79508
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 95029
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 |  | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 3616855
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 13300
103 | Kamalaghat 54 MW PP(Banco Energy) | [8 empty] | 0 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 29 | 54 | 54 | 54 | 54 | 54 | 54 | 462600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 45 | 45 | 45 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 35 | 90 | 102 | 101 | 110 | 110 | 110 | 854400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 80 | 52 | 52 | 52 | 52 | 52 | 52 | 54 | 54 | 54 | 54 | 64 | 99 | 95 | 96 | 96 | 96 | 96 |  | 96 | 116 | 114 | 115 | 115 | 115 | 116 | 1959840
115 | Juldah 100 MW PP Unit-3 (Acorn) | [19 empty] | 25 | 25 | 12 | 12 |  |  | 0 | 55680
116 | Chandpur 200 MW (Desh energy) | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 74 | 149 |  | 156 | 155 | 156 | 156 | 156 | 155 | 91 | 1932000
117 | Ashuganj 150 MW PP (Midland) | [25 empty] | 0 | 0
118 | Bibiyana-III 400 MW CCPP | 268 | 268 | 268 | 268 | 268 | 205 | 209 | 209 | 209 | 205 | 265 | 265 | 265 | 265 | 265 | 268 | 268 | 189 |  | 267 | 269 | 268 | 269 | 269 | 268 | 265 | 6315000
| Jamalpur 115 MW PP (United) | 59 | 58 | 57 | 57 | 59 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 56 | 74 | 89 | 92 | 87 | 87 | 87 | 1160400
| Anwara 300 MW PP (United) | [19 empty] | 32 | 32 | 32 | 32 | 50 | 50 | 50 | 225818
| Juldah unit-2 (Acorn) | [19 empty] | 25 | 25 | 12 | 12 | 12 | 12 | 12 | 81600
| Anlima Energy Ltd. | [25 empty] | 0 | 0
| Bhairob 54.5 MW | [25 empty] | 0 | 0
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 3 | 17 | 7 | 35 | 35 | 36 | 25 | 26 | 4 | 4 | 1 | [8 empty] | 201173
| Chandpur 115(Doreen) | 66 | 67 | 66 | 51 | 50 | 49 | 50 | 49 | 49 | 50 | 49 | 49 | 60 | 63 | 67 | 67 | 83 | 84 |  | 79 | 69 | 68 | 49 | 49 | 37 | 33 | 1397760
| Kanchan Purbachal Power Generation Ltd. | [25 empty] | 0 | 0
| Mirsharai 150 MW (Oil) | [25 empty] | 0
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 6 | 12 | 13 | 12 | 9 | 21 | 21 | 28 | 50 | 28 | 28 | 20 | 25 | 26 | 33 | 20 | 18 | 33 |  | 32 | 24 | 30 | 17 | 21 | 17 | 14 | 561600
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 11 | 18 | 61 | 67 | 3 | 7 | 20 | 35 | 49 | 32 | 6 | 1 | [8 empty] | 322000
| Matarbari 2*600 MW (CPGCL) | 818 | 820 | 815 | 815 | 815 | 815 | 818 | 823 | 873 | 920 | 932 | 1026 | 1071 | 1072 | 1072 | 1070 | 1005 | 954 |  | 1105 | 1150 | 1150 | 1150 | 1150 | 1150 | 1150 | 23330909
120 | Eastern Zone Total | 6942 | 6890 | 6769 | 6718 | 6709 | 6322 | 6369 | 6309 | 6468 | 6660 | 6784 | 6843 | 6924 | 6925 | 7003 | 6778 | 6549 | 6179 |  | 7263 | 7613 | 7611 | 7875 | 7806 | 7891 | 7650 | 192330451
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 10 | 45 | 24 |  |  |  |  | 32140
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [26 empty] | 4800
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 8 | 40 | 51 | 34 | 74 | 76 | 103 | 45 | 15 | 18 | 16 | 4 | [8 empty] | 504720
131 | Rampal 1320 MW (BIFPCL) | 1018 | 1022 | 949 | 818 | 820 | 818 | 770 | 766 | 765 | 766 | 760 | 761 | 761 | 762 | 763 | 752 | 753 | 758 |  | 906 | 913 | 914 | 916 | 913 | 912 | 913 | 20130911
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 180 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 529964
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 150 | 150 | 150 | 191 | 200 | 200 | 200 | 200 | 200 | 150 |  | 234 | 250 | 250 | 250 | 250 | 250 | 250 | 4887300
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1959
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 66 | 68 | 68 | 68 | 68 | 68 | 69 | 69 | 69 | 68 | 68 | 69 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 65 | 60 | 68 | 68 | 68 | 68 | 1625000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 9 | 9 | 9 | 7 | 8 | 6 | 5 | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 191148
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 17 | 30 | 30 |  |  |  |  | 35200
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 918 | 912 | 913 | 916 | 918 | 917 | 917 | 918 | 919 | 918 | 918 | 918 | 917 | 918 | 918 | 911 | 901 | 901 |  | 901 | 900 | 900 | 805 | 808 | 808 | 911 | 20657454
147 | Bheramara 410 MW CCPP | 300 | 303 | 303 | 303 | 303 | 304 | 326 | 323 | 318 | 362 | 338 | 340 | 306 | 325 | 305 | 303 | 303 | 304 |  | 361 | 303 | 305 | 309 | 313 | 345 | 340 | 7807392
148 | Payra 1320 MW | 1040 | 960 | 940 | 940 | 940 | 800 | 800 | 780 | 780 | 780 | 870 | 880 | 890 | 950 | 1000 | 1030 | 980 | 840 |  | 940 | 1080 | 1080 | 1090 | 1100 | 1100 | 1100 | 24708500
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 62 | 63 | 62 | 62 | 62 | 62 | 62 | 60 | 60 | 60 | 61 |  | 61 | 61 | 62 | 62 | 61 | 62 | 62 | 1415127
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 4 | 4 | 0 | 1 | 5 | 3 | 1 | 0 | 0 | 0 | [8 empty] | 25620
| Sirajganj 68 MW Solar Park | [6 empty] | 8 | 27 | 41 | 40 | 15 | 22 | 34 | 37 | 4 | 3 | 4 | 2 | [8 empty] | 293250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 168 | 168 | 170 | 169 | 168 | 170 | 174 | 176 | 185 | 188 | 160 | 164 | 181 | 188 | 194 | 179 | 174 | 173 |  | 176 | 177 | 172 | 155 | 150 | 160 | 169 | 4211091
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 345 | 330 | 342 | 343 | 320 | 333 | 345 | 347 | 347 | 352 | 350 | 414 | 414 | 414 | 414 | 390 | 306 | 341 |  | 362 | 315 | 311 | 414 | 414 | 347 | 414 | 8576072
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 122562
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 30 | 35 | 35 | 35 | 35 | 35 | 33 | 155178
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 43 | 42 |  |  |  |  | 0 | 59604
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [25 empty] | 0 | 0
172 | Confidence Power Bogura Unit-1 113 MW
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 71 | 71 | 70 | 71 | 71 | 71 | 71 | 70 | 70 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 |  | 105 | 105 | 106 | 106 | 106 | 106 | 106 | 1721740
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 4 | 5 | 8 | 8 | 8 | 4 | 5 | 2 | 1 | 0 | [8 empty] | 47655
178 | Energypac Power Venture Thakurgaon Ltd. | 90 | 36 | [9 empty] | 35 | 36 | 36 | 36 | 36 | 36 | 36 |  | 90 | 112 | 115 | 115 | 115 | 115 | 36 | 1048512
| Intraco Solar 30 MW | [5 empty] | 1 | 5 | 8 | 15 | 24 | 22 | 12 | 26 | 28 | 29 | 4 | 10 | 3 | [8 empty] | 206587
| Adani Power Jharkhanda Ltd | 1203 | 1119 | 1026 | 956 | 913 | 829 | 825 | 827 | 825 | 893 | 945 | 1079 | 1185 | 1182 | 1201 | 1265 | 1180 | 1061 |  | 1209 | 1307 | 1319 | 1302 | 1314 | 1323 | 1303 | 26312728
178 | Teesta Solar Limited | [5 empty] | 8 | 32 | 50 | 69 | 92 | 188 | 97 | 155 | 162 | 176 | 110 | 55 | 14 | [8 empty] | 1283000