## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-11 | Sunday
|  | Date (day): | 2024-08-11 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14117.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15287 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-10 | 2024-08-11 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 402 | 382 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 8 | 8 | 92 |  | Fuel shortage.
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 250 | 150 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 34 | 85 | 85 |  | 17 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 13 | 62 |  | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 327 | 330 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Loop Oil problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 131 | 64 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 21 | 55 | 30 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 36 | 43 | 43 |  | 37 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 24 | 24 | 24 |  | 9 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 13 | 11 | 17 | 17 |  | 16 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 85 | 280 | 280 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 133 | 54 | 132 |  | 17 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 52 | 17 | 53 | 52 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 107 | 17 | 17 | 17 | 87 |  | Loop Oil problem
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 10 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
39 | Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1754 | 2389 | 2411 | 2618 | 2626 | 916
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 16 | 8 | 17 | 8 |  | Fuel shortage
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 10 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 6 | 50
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 214 | 212 | 212 | 212 | 18
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 224 | 222 | 225 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 85 | 85 | 85 | 85
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 41 | 16 | 70 | 28 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 80 |  | 22 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 37 | 25 | 37 | 63 |  | Fuel shortage
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 32 | 10 | 30
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 36 | 30 | 35 | 73 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 67 | 52 | 50 | 50 | 250 |  | Fuel shortage
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 34 | 17 | 54
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 40 | 72 | 110 | 110
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 37 | 37 | 25 | 25 | 75 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 97 | 108 | 108 | 108 | 8 |  | Fuel shortage
60 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 90 | 54 | 90
61 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 578 | 608 | 612 | 612 |  | 612 | Unit-1 under maint.
. | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 37 | 8 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 0 | 0 | 0 | 0 |  |  | On test.
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1434 | 1743 | 1711 | 1950 | 703 | 964
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 217 | 217 | 200 | 210
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 305 | 300 | 305 |  |  | FGMO
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 330 | 300 | 330 | 330 |  |  | FGMO
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 32 | 33 | 30 | 35 | 10 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 42 | 46 | 45 | 46 | 9 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 88 | 110 | 160 | 35 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 90 | 100 | 150
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 28 | 33 | 36 |  | 16 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 33 | 50 | 50 | 113 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 170 | 100 | 150 | 50
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 74 | 76 | 90 | 90
76 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 24 | 42 | 24 | 43 |  | 9 | Engine problem
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 17 | 52 | 62 |  | fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
81 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 32 | 67 | 68 | 68 | 47 |  | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 5 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2950 | 1344 | 1607 | 1645 | 1803 | 430 | 425
82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 29 | 30 | 40 | 45
83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 125 | 95 | 125 | 75 |  | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 59 | 79 | 58 | 75 | 40 |  | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 7 | 0 | 50 | 0
88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 2 | 6 | 6 |  | 16 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 4 | 35 | 17 | 35 |  | 19 | engine problem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 172 | 271 | 267.6 | 286 | 0 | 35
89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 27 | 27 | 30 | 30 |  | 60 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 120 | 163 | 163
92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 5 | 5 |  | 6 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 31 | 30 | 30 | 36 |  | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 0 | 10 | 10 | 10 | 10 | 76 |  | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 208 | 211 | 210 | 210 |  | 21 | Machine problem
100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
101 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 12 | 12 | 12 |  | 13 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 275 | 300 | 300 | 300 |  |  | FGMO
103 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 270 | 270 | 280 | 280 |  | 120 | ST Under maint.
104 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 340 | 350 | 380 | 400 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2331 | 1377 | 1376 | 1460 | 1480 | 233 | 580
106 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 877 | 781 | 921 | 921
107 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 48 | 32 | 98 |  | 17 | Engine problem
108 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40 |  | 14 | Engine problem
109 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
111 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 358 | 308 | 300 | 300 | 110 |  | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 16 | 16 | 24 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
113 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 20 | 60 | 53 | 70 | 35 |  | Fuel shortage
114 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 10 | 0 | 100 | 0
116 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
117 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 588 | 622 | 600 | 617 |  | 617 | Unit-2 under maint.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1853 | 1819 | 2052 | 2117 | 856 | 702
118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 110 | 16 | 110 | 0
119 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 136 | 136 | 130 | 130 |  | 64 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1030 | 1244 | 1244 | 1244
122 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 54 | 150
124 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 280 | 307 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1720 | 2081 | 1924 | 2171 | 0 | 64
125 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 37 | 24 | 40 |  | 12 | Engine problem
127 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28
129 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 46 | 25 | 46
131 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 212 | 209 | 200 | 200 | 10
132 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
133 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 311 | 332 | 380 | 414
135 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 25 | 35 |  | 15 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 8 | 5 | 5 |  | 6 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 50 | 85 |  | 19 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 70 | 113
140 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 70 | 113
141 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1352 | 1517 | 1400 | 1480
| Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 0 | 0 | 68 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3403 | 3381 | 1949 | 2409 | 2275 | 2579 | 673 | 103
142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 61 | 63 | 62 | 62 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Machine problem
144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 48 | 99 | 106 | 106 |  | 9 | Engine problem
147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
148 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 115 | 36 | 115
149 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 30 | 0
150 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 189 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 347 | 277 | 372 | 283 | 40 | 393
| Total |  |  |  |  | 28098 | 26947 | 11950 | 13972 | 14117.6 | 15287 | 5561 | 4182
A. |  | 2024-08-10 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 13972 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 10927 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14130 | MW
3 | Day peak Generation : |  |  | 11950 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13652.6 | MW
4 | Evening peak Generation : |  |  | 13972 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 151 | MW
5 | Total Energy Generation : |  | 304.0609 | MKWHr | By Solar | 2.3529 | MKWHr
| By Gas : | 130.2999 | MKWHr |  | By Oil: | 38.4947 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 102.2256 | MKWHr |  | By Hydro: | 5.0356 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.52032 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5561 | MW | Dhaka | 4924 | 4853 |  | 71 |  | 18:00 |  | 191
|  |  | For Plants S/D or M/C prob = |  |  | 4182 | MW | Chittagong | 1184.7 | 1184.7 |  | 0 |  | 19:00 |  | 193.865
|  |  | Total = |  |  | 9743 | MW | Khulna | 1725 | 1725 |  | 0 |  | 19:30 |  | 212.01
7 | Total Gas Supplied : |  |  | 926 | MMCFD |  |  | Rajshahi | 1430.4 | 1430.4 |  | 0 |  | 20:00 |  | 189.09
8 | Fuel Cost : | i) Gas : | Taka | 393654631.826 | ii) Oil : | Taka | 697819376.68 | Comilla | 1242 | 1242 |  | 0 |  | 21:00 |  | 150.89
|  | iii) Coal : | Taka | 696877195.12 | Total | Taka | 1788351203.626 | Mymensingh | 1193 | 1113 |  | 80 |  | 22:00 |  | 127.97
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 9248.25 | MKWHr. | Sylhet | 598 | 598 |  | 0 |  | 23:00 |  | 171.9
| ii) During Peak Demand : |  |  | 904 | MW (W to E) at | 21:00 | hrs | Barisal | 438.5 | 438.5 |  | 0 |  | 24:00 |  | 192.91
| iii) Maximum : |  |  | 880 | MW at | 7:00 | hrs | Rangpur | 917 | 917 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.1°C |  |  | Total | 13652.6 | 13501.6 |  | 151
B. |  | 2024-08-11 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.1°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15287 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13500 | MW
4 | Reserve(Generation end) |  |  |  | 287 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 326.4324 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11654 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 23.2916 | MKWHr. | ii) HVDC Flow at Peak Time |  | 781 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8403 | MKWHr. | iii) Maximum HVDC Flow : |  | 899 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.04 |  | (b) Today: | 96.85 |  | (c) Rule Curve: |  | 92.2
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-08-10 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 |  | 0 | 450 | 252 | 0 | 0 | 15 | 270 | 0 | 0 | 0 | 8 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 15 | 0 | 24 | 17 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 2 | 32 | 17 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 218 | 110 | 50 | 30 | 48 | 0 | 51 | 0 | 36 | 16 | 0 | 0 | 0 | 18 | 90 | 47 | 0 | 0 | 0 | 40 | 28 | 0 | 0 | 120 | 0 | 32 | 10 | 0 | 209 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 95 | 0 | 0 | 97 | 0 | 53 | 0 | 24 | 155 | 0 | 241 | 59 | 17 | 0 | 0 | 100 | 0 | 0 | 17 | 9 | 25 | 340 | 17 | 0 | 0 | 0 | 0 | 20 | 0 | 68 | 35 | 345 | 0 | 0 | 590 | 12 | 564 | 0 | 0 | 0 |  | 875 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 17 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 1415 | 0 | 0 | 0 | 0 |  | 6759 | 6096 | 12855 | 3570 | 875 | 1984 | 0 | 1102 | 4803 | 215 | 0 | 204 | 90 | 0 | 12 | 138.475 | 97.05
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 450 | 251 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 15 | 10 | 24 | 17 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 315 | 216 | 110 | 50 | 27 | 47 | 0 | 51 | 0 | 36 | 16 | 0 | 0 | 0 | 18 | 80 | 48 | 0 | 0 | 0 | 40 | 28 | 0 | 0 | 120 | 0 | 32 | 10 | 0 | 209 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 45 | 0 | 0 | 98 | 0 | 53 | 0 | 24 | 155 | 0 | 251 | 59 | 17 | 0 | 0 | 50 | 0 | 0 | 17 | 9 | 25 | 364 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 68 | 35 | 350 | 0 | 0 | 590 | 11 | 368 | 0 | 0 | 0 |  | 876 | 0 | 382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 1376 | 0 | 0 | 0 | 0 |  | 6422 | 6059 | 12481 | 3591 | 876 | 2025 | 0 | 981 | 4568 | 215 | 0 | 134 | 80 | 0 | 11 | 113.645 | 97.05
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 450 | 253 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 15 | 22 | 24 | 17 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 12 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 300 | 217 | 110 | 50 | 27 | 47 | 0 | 51 | 0 | 29 | 16 | 0 | 0 | 0 | 18 | 80 | 49 | 0 | 0 | 0 | 40 | 28 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 209 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 45 | 0 | 0 | 98 | 0 | 53 | 0 | 24 | 155 | 0 | 241 | 59 | 17 | 0 | 0 | 50 | 0 | 0 | 17 | 9 | 25 | 340 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 67 | 35 | 345 | 0 | 0 | 590 | 16 | 217 | 0 | 0 | 0 |  | 875 | 0 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 17 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 620 | 0 | 307 | 1371 | 0 | 0 | 0 | 0 |  | 6204 | 6049 | 12253 | 3561 | 875 | 2023 | 0 | 980 | 4411 | 214 | 0 | 93 | 80 | 0 | 16 | 102.185 | 97.05
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 0 |  | 0 | 450 | 252 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 17 | 0 | 0 | 133 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 310 | 216 | 110 | 50 | 27 | 48 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 78 | 49 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 32 | 10 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 0 | 0 | 0 | 98 | 0 | 53 | 0 | 0 | 155 | 0 | 0 | 59 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 9 | 25 | 355 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 17 | 340 | 0 | 0 | 590 | 22 | 248 | 0 | 0 | 0 |  | 876 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 618 | 0 | 250 | 1360 | 0 | 0 | 0 | 0 |  | 5800 | 5883 | 11683 | 3339 | 876 | 2027 | 0 | 692 | 4372 | 213 | 0 | 64 | 78 | 0 | 22 | 49.66 | 97.04
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 252 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 17 | 0 | 0 | 132 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 320 | 215 | 110 | 50 | 27 | 47 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 72 | 49 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 163 | 0 | 31 | 10 | 0 | 210 | 0 | 0 | 0 | 315 | 12 | 5 | 0 | 0 | 0 | 0 | 98 | 0 | 53 | 0 | 0 | 155 | 0 | 0 | 59 | 17 | 0 | 0 | 20 | 0 | 0 | 17 | 9 | 0 | 358 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 17 | 330 | 0 | 0 | 592 | 23 | 214 | 0 | 0 | 0 |  | 878 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 624 | 0 | 250 | 1367 | 0 | 0 | 0 | 0 |  | 5897 | 5886 | 11783 | 3446 | 878 | 2084 | 0 | 651 | 4353 | 212 | 0 | 64 | 72 | 0 | 23 | 63.985 | 97.04
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 |  | 0 | 400 | 250 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 23 | 24 | 17 | 0 | 0 | 131 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 305 | 216 | 110 | 70 | 27 | 47 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 82 | 50 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 213 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 53 | 0 | 0 | 85 | 0 | 0 | 59 | 17 | 0 | 0 | 15 | 0 | 0 | 17 | 9 | 0 | 345 | 27 | 2 | 0 | 0 | 0 | 0 | 0 | 32 | 17 | 345 | 0 | 0 | 590 | 23 | 216 | 0 | 0 | 1 |  | 877 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1100 | 220 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 623 | 1 | 250 | 1260 | 7 | 0 | 0 | 2 |  | 5651 | 5431 | 11082 | 3361 | 877 | 1898 | 0 | 452 | 4100 | 211 | 0 | 64 | 82 | 14 | 23 | 74.49 | 97.04
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 |  | 0 | 370 | 250 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 17 | 2 | 0 | 132 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 305 | 217 | 78 | 50 | 27 | 47 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 74 | 50 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 213 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 53 | 1 | 0 | 85 | 0 | 215 | 59 | 17 | 0 | 2 | 15 | 0 | 0 | 17 | 9 | 0 | 341 | 75 | 21 | 0 | 0 | 0 | 0 | 3 | 32 | 17 | 360 | 0 | 0 | 589 | 17 | 215 | 0 | 0 | 5 |  | 877 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 560 | 5 | 250 | 1260 | 23 | 0 | 0 | 12 |  | 5821 | 5271 | 11092 | 3538 | 877 | 1830 | 0 | 468 | 3935 | 212 | 0 | 64 | 74 | 77 | 17 | 79.265 | 97.03
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 |  | 0 | 370 | 253 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 24 | 17 | 8 | 0 | 132 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 260 | 216 | 78 | 50 | 27 | 47 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 72 | 44 | 0 | 0 | 1 | 40 | 30 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 213 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 53 | 8 | 0 | 85 | 0 | 270 | 59 | 17 | 0 | 2 | 15 | 0 | 0 | 17 | 9 | 0 | 366 | 105 | 13 | 0 | 0 | 0 | 0 | 14 | 32 | 17 | 360 | 0 | 0 | 590 | 17 | 214 | 0 | 0 | 30 |  | 878 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 180 | 0 | 0 | 2 | 12 | 0 | 0 | 0 | 555 | 8 | 250 | 1267 | 77 | 0 | 0 | 17 |  | 5786 | 5141 | 10927 | 3414 | 878 | 1740 | 0 | 504 | 3858 | 212 | 0 | 48 | 72 | 184 | 17 | 165.215 | 97.03
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 370 | 257 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 22 | 24 | 15 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 295 | 215 | 78 | 50 | 27 | 46 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 66 | 44 | 0 | 0 | 1 | 40 | 27 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 212 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 0 | 0 | 0 | 65 | 0 | 52 | 7 | 0 | 85 | 0 | 270 | 59 | 17 | 1 | 2 | 15 | 0 | 0 | 17 | 9 | 0 | 340 | 105 | 5 | 0 | 0 | 0 | 0 | 24 | 32 | 17 | 345 | 0 | 0 | 598 | 19 | 160 | 0 | 0 | 27 |  | 877 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 960 | 220 | 0 | 0 | 2 | 31 | 0 | 0 | 0 | 557 | 21 | 250 | 1335 | 85 | 0 | 0 | 25 |  | 5847 | 5491 | 11338 | 3593 | 877 | 1864 | 0 | 504 | 3923 | 213 | 0 | 48 | 66 | 231 | 19 | 154.71 | 97.02
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 370 | 250 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 24 | 14 | 8 | 0 | 133 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 270 | 216 | 78 | 50 | 25 | 45 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 70 | 30 | 0 | 0 | 1 | 40 | 27 | 0 | 0 | 163 | 0 | 31 | 10 | 0 | 212 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 35 | 0 | 0 | 65 | 0 | 52 | 17 | 0 | 85 | 0 | 270 | 59 | 35 | 34 | 4 | 35 | 0 | 0 | 17 | 9 | 0 | 340 | 107 | 23 | 0 | 1 | 0 | 0 | 22 | 32 | 29 | 330 | 0 | 0 | 606 | 29 | 0 | 0 | 0 | 19 |  | 877 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 62 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 1 | 0 | 0 | 0 | 46 | 0 | 1 | 0 | 980 | 220 | 0 | 0 | 2 | 44 | 35 | 0 | 0 | 560 | 11 | 250 | 1363 | 135 | 0 | 0 | 16 |  | 5784 | 5674 | 11458 | 3570 | 877 | 1812 | 0 | 723 | 3821 | 213 | 0 | 48 | 70 | 295 | 29 | 159.485 | 97.02
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 370 | 250 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 22 | 24 | 13 | 8 | 0 | 134 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 295 | 214 | 78 | 50 | 29 | 43 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 18 | 74 | 29 | 0 | 0 | 1 | 40 | 27 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 212 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 45 | 0 | 0 | 65 | 0 | 95 | 10 | 15 | 85 | 0 | 270 | 59 | 35 | 39 | 3 | 66 | 0 | 6 | 17 | 9 | 12 | 352 | 107 | 54 | 0 | 42 | 0 | 0 | 9 | 32 | 35 | 345 | 0 | 0 | 608 | 42 | 0 | 0 | 0 | 11 |  | 878 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 17 | 0 | 0 | 0 | 48 | 0 | 2 | 0 | 1000 | 220 | 0 | 0 | 5 | 14 | 35 | 0 | 0 | 586 | 37 | 253 | 1359 | 65 | 0 | 0 | 49 |  | 6117 | 5722 | 11839 | 3660 | 878 | 1847 | 0 | 934 | 3866 | 214 | 0 | 64 | 74 | 260 | 42 | 154 | 97.01
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 370 | 250 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 0 | 12 | 22 | 20 | 13 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 270 | 217 | 78 | 50 | 32 | 42 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 18 | 74 | 29 | 0 | 0 | 2 | 40 | 27 | 0 | 0 | 163 | 0 | 31 | 10 | 0 | 208 | 0 | 0 | 0 | 275 | 8 | 5 | 0 | 85 | 0 | 0 | 65 | 0 | 0 | 10 | 38 | 85 | 10 | 270 | 59 | 0 | 85 | 0 | 67 | 0 | 40 | 17 | 9 | 37 | 340 | 107 | 7 | 54 | 97 | 0 | 4 | 10 | 32 | 35 | 330 | 0 | 0 | 578 | 37 | 0 | 0 | 0 | 5 |  | 877 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 20 | 0 | 0 | 0 | 48 | 0 | 1 | 0 | 1030 | 220 | 0 | 0 | 4 | 10 | 35 | 0 | 0 | 588 | 13 | 280 | 1352 | 189 | 0 | 0 | 68 |  | 6081 | 5869 | 11950 | 3556 | 877 | 1783 | 0 | 1201 | 3889 | 214 | 0 | 0 | 74 | 319 | 37 | 306 | 97
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 370 | 250 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 12 | 22 | 20 | 13 | 5 | 0 | 134 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 19 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 270 | 216 | 78 | 45 | 33 | 41 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 18 | 74 | 29 | 0 | 0 | 2 | 40 | 27 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 210 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 145 | 0 | 0 | 65 | 0 | 30 | 19 | 37 | 85 | 94 | 270 | 58 | 35 | 85 | 2 | 69 | 0 | 51 | 26 | 9 | 37 | 365 | 107 | 8 | 54 | 108 | 0 | 25 | 26 | 32 | 35 | 330 | 0 | 0 | 585 | 32 | 0 | 0 | 0 | 3 |  | 879 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317 | 32 | 0 | 0 | 0 | 48 | 0 | 1 | 0 | 1050 | 220 | 0 | 0 | 5 | 5 | 35 | 0 | 0 | 620 | 30 | 307 | 1366 | 60 | 0 | 0 | 65 |  | 6528 | 5858 | 12386 | 3577 | 879 | 1794 | 0 | 1537 | 3989 | 214 | 0 | 64 | 74 | 226 | 32 | 180 | 96.99
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 370 | 150 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 15 | 22 | 24 | 13 | 8 | 0 | 134 | 80 | 0 | 0 | 5 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 31 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 265 | 214 | 78 | 42 | 33 | 43 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 78 | 28 | 0 | 0 | 2 | 40 | 27 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 210 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 145 | 0 | 0 | 65 | 0 | 99 | 14 | 37 | 85 | 119 | 270 | 58 | 35 | 85 | 3 | 70 | 0 | 51 | 17 | 9 | 37 | 340 | 107 | 7 | 54 | 108 | 0 | 35 | 14 | 32 | 35 | 330 | 0 | 0 | 590 | 41 | 0 | 0 | 0 | 4 |  | 878 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 396 | 35 | 0 | 0 | 0 | 46 | 0 | 1 | 0 | 1090 | 220 | 0 | 0 | 5 | 14 | 35 | 0 | 0 | 623 | 15 | 307 | 1372 | 135 | 0 | 0 | 65 |  | 6523 | 5993 | 12516 | 3470 | 878 | 1778 | 0 | 1671 | 4043 | 214 | 0 | 64 | 78 | 279 | 41 | 175.72 | 97.01
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 150 | 0 | 0 | 55 | 324 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 15 | 22 | 24 | 13 | 8 | 0 | 135 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 31 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 300 | 213 | 78 | 40 | 33 | 43 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 80 | 28 | 0 | 0 | 1 | 40 | 27 | 0 | 0 | 163 | 0 | 29 | 10 | 0 | 210 | 0 | 0 | 0 | 305 | 12 | 5 | 0 | 145 | 0 | 0 | 65 | 0 | 107 | 5 | 37 | 85 | 115 | 280 | 58 | 35 | 85 | 3 | 70 | 0 | 51 | 17 | 9 | 37 | 350 | 52 | 9 | 54 | 108 | 0 | 35 | 7 | 32 | 25 | 335 | 0 | 0 | 590 | 32 | 0 | 0 | 0 | 2 |  | 878 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 51 | 0 | 0 | 0 | 49 | 0 | 2 | 0 | 1120 | 220 | 0 | 0 | 1 | 13 | 35 | 0 | 0 | 620 | 16 | 307 | 1369 | 25 | 0 | 0 | 20 |  | 6607 | 5969 | 12576 | 3622 | 878 | 1866 | 0 | 1648 | 4067 | 215 | 0 | 64 | 80 | 104 | 32 | 185.27 | 96.97
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 150 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 135 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 31 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 305 | 215 | 103 | 40 | 33 | 44 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 6 | 82 | 28 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 163 | 0 | 31 | 10 | 0 | 206 | 0 | 0 | 0 | 280 | 8 | 5 | 0 | 145 | 0 | 0 | 55 | 0 | 107 | 2 | 37 | 85 | 60 | 280 | 58 | 35 | 77 | 2 | 70 | 0 | 51 | 34 | 9 | 37 | 350 | 17 | 6 | 54 | 108 | 0 | 35 | 12 | 32 | 31 | 330 | 0 | 0 | 551 | 55 | 0 | 0 | 0 | 5 |  | 897 | 0 | 323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 50 | 0 | 0 | 0 | 49 | 0 | 2 | 0 | 1060 | 220 | 0 | 0 | 1 | 29 | 34 | 0 | 0 | 561 | 11 | 227 | 1410 | 117 | 0 | 0 | 18 |  | 6488 | 5826 | 12314 | 3601 | 897 | 1764 | 0 | 1561 | 3870 | 215 | 0 | 64 | 82 | 205 | 55 | 196.73 | 96.96
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 150 | 0 | 0 | 55 | 324 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 136 | 80 | 0 | 0 | 13 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 37 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 310 | 213 | 107 | 38 | 33 | 44 | 0 | 51 | 0 | 2 | 33 | 0 | 0 | 0 | 16 | 68 | 28 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 206 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 125 | 0 | 0 | 55 | 0 | 107 | 4 | 12 | 85 | 40 | 279 | 58 | 35 | 51 | 1 | 62 | 0 | 34 | 34 | 12 | 12 | 350 | 17 | 2 | 54 | 65 | 0 | 35 | 7 | 32 | 35 | 330 | 0 | 0 | 505 | 14 | 0 | 0 | 0 | 1 |  | 897 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 6 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 51 | 0 | 0 | 0 | 49 | 0 | 1 | 0 | 1060 | 220 | 0 | 0 | 1 | 22 | 35 | 0 | 0 | 510 | 6 | 200 | 1418 | 27 | 0 | 0 | 18 |  | 6218 | 5670 | 11888 | 3610 | 897 | 1819 | 0 | 1353 | 3755 | 216 | 0 | 66 | 68 | 90 | 14 | 202.46 | 96.95
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 150 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 131 | 80 | 0 | 0 | 16 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 37 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 320 | 212 | 108 | 38 | 30 | 45 | 0 | 10 | 0 | 14 | 41 | 0 | 0 | 0 | 16 | 66 | 28 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 120 | 0 | 20 | 10 | 0 | 210 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 125 | 0 | 0 | 58 | 0 | 115 | 1 | 12 | 85 | 70 | 220 | 58 | 35 | 51 | 0 | 52 | 0 | 34 | 34 | 13 | 12 | 356 | 17 | 2 | 54 | 53 | 0 | 35 | 1 | 33 | 35 | 330 | 0 | 0 | 500 | 15 | 0 | 0 | 0 | 1 |  | 897 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 52 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1000 | 180 | 0 | 0 | 0 | 3 | 35 | 0 | 0 | 511 | 3 | 200 | 1323 | 6 | 0 | 0 | 1 |  | 6120 | 5380 | 11500 | 3498 | 897 | 1719 | 0 | 1402 | 3596 | 211 | 0 | 78 | 66 | 18 | 15 | 191 | 96.94
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193.865 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 420 | 150 | 0 | 8 | 55 | 327 | 0 | 0 | 0 | 8 | 131 | 0 | 0 | 0 | 0 | 10 | 35 | 20 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 131 | 80 | 0 | 0 | 16 | 218 | 0 | 0 | 0 |  | 5 | 33 | 34 | 0 | 40 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 315 | 215 | 108 | 33 | 33 | 44 | 0 | 21 | 0 | 27 | 42 | 0 | 0 | 0 | 16 | 76 | 28 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 210 | 0 | 0 | 0 | 315 | 12 | 5 | 0 | 160 | 0 | 0 | 123 | 0 | 120 | 0 | 22 | 122 | 76 | 260 | 78 | 52 | 60 | 0 | 52 | 0 | 48 | 34 | 9 | 35 | 345 | 17 | 0 | 120 | 55 | 0 | 35 | 0 | 52 | 35 | 325 | 70 | 0 | 555 | 7 | 0 | 0 | 0 | 0 |  | 898 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 9 | 80 | 0 | 0 | 0 | 40 | 0 | 83 | 0 | 0 | 14 | 0 | 32 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 52 | 0 | 5 | 0 | 85 | 0 | 0 | 35 | 1030 | 220 | 0 | 29 | 0 | 0 | 115 | 0 | 0 | 618 | 0 | 262 | 1457 | 0 | 0 | 0 | 0 |  | 6823 | 6204 | 13027 | 3579 | 898 | 1854 | 0 | 1953 | 3985 | 211 | 0 | 464 | 76 | 0 | 7 | 193.865 | 96.91
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 |  | 0 | 420 | 150 | 0 | 34 | 55 | 326 | 0 | 0 | 0 | 8 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 131 | 80 | 0 | 0 | 16 | 221 | 0 | 0 | 0 |  | 0 | 33 | 34 | 0 | 38 | 12 | 0 | 25 | 0 | 0 | 0 | 0 | 305 | 217 | 108 | 33 | 33 | 45 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 82 | 30 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 163 | 0 | 31 | 10 | 0 | 210 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 278 | 0 | 0 | 123 | 0 | 128 | 0 | 37 | 170 | 90 | 270 | 78 | 52 | 85 | 0 | 52 | 13 | 72 | 34 | 9 | 37 | 345 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 67 | 35 | 330 | 90 | 0 | 578 | 9 | 0 | 0 | 0 | 0 |  | 899 | 0 | 311 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 10 | 96 | 0 | 0 | 0 | 37 | 0 | 89 | 0 | 0 | 14 | 0 | 33 | 0 | 0 | 8 | 62 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 326 | 52 | 0 | 35 | 0 | 92 | 0 | 0 | 50 | 1220 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 307 | 1496 | 0 | 0 | 0 | 0 |  | 7374 | 6504 | 13878 | 3541 | 899 | 1818 | 0 | 2545 | 4284 | 211 | 0 | 489 | 82 | 0 | 9 | 212.01 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 |  | 0 | 360 | 150 | 0 | 34 | 55 | 280 | 0 | 0 | 0 | 8 | 131 | 0 | 0 | 0 | 0 | 51 | 55 | 35 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 131 | 80 | 0 | 0 | 16 | 222 | 0 | 0 | 0 |  | 0 | 38 | 34 | 0 | 35 | 19 | 0 | 27 | 0 | 0 | 0 | 0 | 305 | 217 | 108 | 33 | 33 | 45 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 78 | 30 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 32 | 10 | 0 | 211 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 266 | 0 | 0 | 126 | 0 | 131 | 0 | 37 | 170 | 90 | 270 | 78 | 52 | 85 | 0 | 52 | 31 | 72 | 34 | 9 | 37 | 350 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 65 | 35 | 330 | 90 | 0 | 587 | 13 | 0 | 0 | 0 | 0 |  | 898 | 0 | 312 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 10 | 96 | 0 | 0 | 0 | 40 | 0 | 89 | 0 | 0 | 32 | 0 | 32 | 0 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 52 | 0 | 60 | 0 | 92 | 0 | 0 | 70 | 1240 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 623 | 0 | 307 | 1513 | 0 | 0 | 0 | 0 |  | 7254 | 6598 | 13852 | 3507 | 898 | 1693 | 0 | 2605 | 4333 | 211 | 0 | 514 | 78 | 0 | 13 | 189.09 | 96.92
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 400 | 150 | 0 | 34 | 55 | 327 | 0 | 0 | 0 | 8 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 132 | 80 | 0 | 0 | 16 | 222 | 0 | 0 | 0 |  | 2 | 41 | 34 | 0 | 36 | 19 | 0 | 32 | 0 | 0 | 0 | 0 | 305 | 217 | 88 | 33 | 33 | 46 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 76 | 30 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 211 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 125 | 0 | 133 | 0 | 37 | 170 | 90 | 270 | 79 | 52 | 85 | 0 | 52 | 34 | 72 | 34 | 9 | 37 | 350 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 67 | 35 | 300 | 90 | 0 | 608 | 8 | 0 | 0 | 0 | 0 |  | 781 | 0 | 308 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 10 | 110 | 0 | 0 | 0 | 37 | 0 | 88 | 0 | 0 | 46 | 0 | 32 | 0 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 60 | 0 | 70 | 0 | 99 | 0 | 0 | 70 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1517 | 0 | 0 | 0 | 0 |  | 7386 | 6586 | 13972 | 3545 | 781 | 1759 | 0 | 2703 | 4361 | 212 | 0 | 527 | 76 | 0 | 8 | 150.89 | 96.91
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 150 | 0 | 28 | 55 | 325 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 0 | 23 | 24 | 11 | 8 | 0 | 133 | 80 | 0 | 0 | 8 | 223 | 0 | 0 | 0 |  | 0 | 41 | 34 | 0 | 38 | 19 | 0 | 21 | 0 | 0 | 0 | 0 | 305 | 217 | 88 | 34 | 34 | 46 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 80 | 30 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 211 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 280 | 0 | 0 | 125 | 0 | 133 | 0 | 37 | 170 | 90 | 270 | 78 | 52 | 85 | 0 | 52 | 34 | 75 | 34 | 9 | 37 | 350 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 68 | 35 | 295 | 90 | 0 | 606 | 18 | 0 | 0 | 0 | 0 |  | 780 | 0 | 304 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 9 | 110 | 0 | 0 | 0 | 31 | 0 | 88 | 0 | 0 | 40 | 0 | 32 | 0 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 70 | 0 | 70 | 0 | 99 | 0 | 0 | 70 | 1244 | 220 | 0 | 72 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1502 | 0 | 0 | 0 | 0 |  | 7367 | 6529 | 13896 | 3539 | 780 | 1718 | 0 | 2688 | 4344 | 213 | 0 | 516 | 80 | 0 | 18 | 127.97 | 96.9
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 150 | 0 | 17 | 55 | 326 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 0 | 23 | 24 | 12 | 8 | 0 | 134 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 0 | 41 | 34 | 0 | 38 | 20 | 0 | 34 | 0 | 0 | 0 | 0 | 280 | 215 | 88 | 34 | 34 | 46 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 82 | 30 | 0 | 0 | 0 | 40 | 28 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 211 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 278 | 0 | 0 | 125 | 0 | 133 | 0 | 37 | 170 | 90 | 271 | 79 | 35 | 85 | 0 | 52 | 34 | 92 | 34 | 8 | 37 | 330 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 68 | 35 | 295 | 17 | 0 | 608 | 12 | 0 | 0 | 0 | 0 |  | 899 | 0 | 308 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 110 | 0 | 0 | 0 | 31 | 0 | 88 | 0 | 0 | 40 | 0 | 32 | 0 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 70 | 0 | 70 | 0 | 99 | 0 | 0 | 70 | 1244 | 180 | 0 | 120 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1508 | 0 | 0 | 0 | 0 |  | 7219 | 6641 | 13860 | 3442 | 899 | 1719 | 0 | 2697 | 4352 | 214 | 0 | 443 | 82 | 0 | 12 | 171.9 | 96.89
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 400 | 150 | 0 | 17 | 55 | 327 | 0 | 0 | 0 | 8 | 132 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 15 | 23 | 24 | 12 | 8 | 0 | 134 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 3 | 41 | 34 | 0 | 39 | 20 | 0 | 37 | 0 | 0 | 0 | 0 | 275 | 217 | 88 | 36 | 34 | 46 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 88 | 30 | 0 | 0 | 0 | 40 | 28 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 211 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 276 | 0 | 0 | 125 | 0 | 133 | 0 | 25 | 170 | 90 | 271 | 79 | 17 | 85 | 0 | 52 | 34 | 92 | 17 | 9 | 25 | 320 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 67 | 35 | 290 | 17 | 0 | 608 | 9 | 0 | 0 | 0 | 0 |  | 899 | 0 | 307 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 110 | 0 | 0 | 0 | 31 | 0 | 57 | 0 | 0 | 40 | 0 | 21 | 0 | 0 | 5 | 63 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 70 | 0 | 70 | 0 | 99 | 0 | 0 | 70 | 1244 | 180 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 250 | 1513 | 0 | 0 | 0 | 0 |  | 7184 | 6574 | 13758 | 3439 | 899 | 1739 | 0 | 2670 | 4299 | 214 | 0 | 401 | 88 | 0 | 9 | 192.91 | 96.88
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9442800 | 0 |  | 0 | 9364500 | 4977367 | 0 | 121481 | 738689 | 7334703 | 0 | 0 | 0 | 117648 | 1866240 | 0 | 0 | 0 | 0 | 243720 | 570025 | 469544 | 0 | 318600 | 495360 | 562320 | 327400 | 138240 | 0 | 3095624 | 1940000 | 0 | 0 | 110485 | 5314621 | 0 | 0 | 0 |  | 117600 | 240864 | 198010 | 0 | 458880 | 89760 | 0 | 608160 | 0 | 0 | 0 | 0 | 7232000 | 5243000 | 2325091 | 1066090 | 715608 | 1083840 | 0 | 1079334 | 0 | 297104 | 641453 | 0 | 0 | 0 | 394000 | 1840320 | 822720 | 0 | 0 | 11950 | 943000 | 652800 | 0 | 0 | 3458781 | 0 | 723648 | 260160 | 0 | 5230790 | 0 | 0 | 0 | 7205500 | 270672 | 111888 | 0 | 2777564 | 0 | 0 | 2107200 | 0 | 2061360 | 94635 | 504000 | 2966880 | 1184291 | 5776000 | 1540800 | 704640 | 1121563 | 23879 | 1216909 | 181721 | 814610 | 570000 | 236880 | 506880 | 8372200 | 1155840 | 178500 | 1300320 | 1293436 | 0 | 487440 | 147697 | 1186560 | 744480 | 8054000 | 341236 | 0 | 14056362 | 520320 | 2778181 | 0 | 0 | 90955 |  | 23291636 | 0 | 8480736 | 0 | 100800 | 0 | 0 | 0 | 0 | 0 | 0 | 2851000 | 185049 | 1095936 | 0 | 0 | 0 | 204137 | 0 | 448848 | 0 | 0 | 169745 | 0 | 193811 | 0 | 0 | 128088 | 1445236 | 0 | 0 | 0 | 0 | 4855091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8639636 | 730080 | 0 | 375840 | 0 | 1443705 | 0 | 12264 | 375552 | 28915500 | 5393320 | 0 | 421200 | 34320 | 236880 | 1510656 | 0 | 0 | 14421820 | 157666 | 6545500 | 34063000 | 998000 | 0 | 862 | 365250 |  | 155969729 | 148091164 | 304060893 | 85719135 | 23291636 | 44580738 | 0 | 34534668 | 102225599 | 5035624 | 0 | 3959995 | 1840320 | 2352858 | 520320 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27195264 | 0 |  | 0 | 29779110 | 17022595.14 | 0 | 2271694.7 | 13015700.18 | 22370844.15 | 0 | 0 | 0 | 2111781.6 | 36242380.8 | 0 | 0 | 0 | 0 | 4450327.2 | 8983594 | 8587959.76 | 0 | 238950 | 0 | 0 | 0 | 2475878.4 | 0 | 0 | 0 | 0 | 0 | 2092585.9 | 16953640.99 | 0 | 0 | 0 |  | 2068584 | 4241615.04 | 3546359.1 | 0 | 8980281.6 | 1477449.6 | 0 | 0 | 0 | 0 | 0 | 0 | 22129920 | 17406760 | 7789054.85 | 3443470.7 | 2411598.96 | 4747219.2 | 0 | 4328129.34 | 0 | 5321132.64 | 11584641.18 | 0 | 0 | 0 | 295500 | 12072499.2 | 2558659.2 | 0 | 0 | 0 | 3677700 | 2434944 | 0 | 0 | 11829031.02 | 0 | 4016246.4 | 1358035.2 | 0 | 14593904.1 | 0 | 0 | 0 | 22264995 | 203004 | 85034.88 | 0 | 56662305.6 | 0 | 0 | 40479312 | 0 | 36300549.6 | 0 | 8976240 | 51475368 | 19635544.78 | 15306400 | 29367648 | 13219046.4 | 20120840.22 | 0 | 19896462.15 | 3532656.24 | 14614103.4 | 10892700 | 4597840.8 | 9027532.8 | 22270052 | 19730188.8 | 0 | 23782852.8 | 21703856.08 | 0 | 8710552.8 | 0 | 21381811.2 | 12611491.2 | 23920380 | 4804602.88 | 0 | 97972843.14 | 0 | 16391267.9 | 0 | 0 | 0 |  | 65449497.16 | 0 | 25018171.2 | 0 | 1748880 | 0 | 0 | 0 | 0 | 0 | 0 | 9009160 | 877132.26 | 18893936.64 | 0 | 0 | 0 | 3656093.67 | 0 | 7545134.88 | 0 | 0 | 3040132.95 | 0 | 3471155.01 | 0 | 0 | 96962.616 | 15940953.08 | 0 | 0 | 0 | 0 | 16021800.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25227737.12 | 12469766.4 | 0 | 7449148.8 | 0 | 28758603.6 | 0 | 0 | 7450951.68 | 187372440 | 16773225.2 | 0 | 8150220 | 0 | 0 | 26209881.6 | 0 | 0 | 105279286 | 0 | 48763975 | 225156430 | 0 | 0 | 0 | 0 |  | 996042524.82 | 869830675.166 | 1865873199.986 | 251658367.496 | 65449497.16 | 141996264.33 | 0 | 625950769.71 | 696877195.12 | 0 | 0 | 71868606.97 | 12072499.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 370 | 250 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 0 | 12 | 22 | 20 | 13 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 270 | 217 | 78 | 50 | 32 | 42 | 0 | 51 | 0 | 0 | 24 | 0 | 0 | 0 | 18 | 74 | 29 | 0 | 0 | 2 | 40 | 27 | 0 | 0 | 163 | 0 | 31 | 10 | 0 | 208 | 0 | 0 | 0 | 275 | 8 | 5 | 0 | 85 | 0 | 0 | 65 | 0 | 0 | 10 | 38 | 85 | 10 | 270 | 59 | 0 | 85 | 0 | 67 | 0 | 40 | 17 | 9 | 37 | 340 | 107 | 7 | 54 | 97 | 0 | 4 | 10 | 32 | 35 | 330 | 0 | 0 | 578 | 37 | 0 | 0 | 0 | 5 |  | 877 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 20 | 0 | 0 | 0 | 48 | 0 | 1 | 0 | 1030 | 220 | 0 | 0 | 4 | 10 | 35 | 0 | 0 | 588 | 13 | 280 | 1352 | 189 | 0 | 0 | 68 |  | 11950 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 400 | 150 | 0 | 34 | 55 | 327 | 0 | 0 | 0 | 8 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 14 | 22 | 24 | 11 | 8 | 0 | 132 | 80 | 0 | 0 | 16 | 222 | 0 | 0 | 0 | 0 | 2 | 41 | 34 | 0 | 36 | 19 | 0 | 32 | 0 | 0 | 0 | 0 | 305 | 217 | 88 | 33 | 33 | 46 | 0 | 51 | 0 | 28 | 42 | 0 | 0 | 0 | 18 | 76 | 30 | 0 | 0 | 0 | 40 | 27 | 0 | 0 | 120 | 0 | 31 | 10 | 0 | 211 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 125 | 0 | 133 | 0 | 37 | 170 | 90 | 270 | 79 | 52 | 85 | 0 | 52 | 34 | 72 | 34 | 9 | 37 | 350 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 67 | 35 | 300 | 90 | 0 | 608 | 8 | 0 | 0 | 0 | 0 |  | 781 | 0 | 308 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 10 | 110 | 0 | 0 | 0 | 37 | 0 | 88 | 0 | 0 | 46 | 0 | 32 | 0 | 0 | 8 | 63 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 60 | 0 | 70 | 0 | 99 | 0 | 0 | 70 | 1244 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 622 | 0 | 307 | 1517 | 0 | 0 | 0 | 0 |  | 13972 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 150 | 8 | 85 | 55 | 335 | 0 | 0 | 50 | 8 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 20 | 23 | 24 | 17 | 8 | 0 | 132 | 80 | 0 | 0 | 17 | 225 | 0 | 0 | 0 |  | 6 | 70 | 80 | 0 | 35 | 50 | 0 | 30 | 0 | 0 | 0 | 0 | 305 | 210 | 160 | 50 | 35 | 46 | 0 | 51 | 0 | 36 | 43 | 0 | 0 |  | 18 | 90 | 45 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 125 | 0 | 132 | 0 | 37 | 150 | 150 | 280 | 75 | 53 | 85 | 0 | 50 | 54 | 110 | 52 | 9 | 25 | 400 | 17 | 0 | 162 | 108 | 0 | 35 | 0 | 68 | 35 | 330 | 90 | 0 | 612 | 60 | 0 | 0 | 0 |  |  | 921 | 0 | 300 | 0 | 98 | 0 | 0 | 0 | 40 | 55 | 16 | 130 | 10 | 110 | 0 | 0 | 0 | 40 | 20 | 85 | 28 | 0 | 46 | 0 | 35 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 70 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 617 | 0 | 307 | 1480 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 150 | 8 | 85 | 55 | 330 | 0 | 0 | 50 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 35 | 0 | 20 | 23 | 24 | 17 | 8 | 0 | 132 | 80 | 0 | 0 | 8 | 225 |  | 0 | 0 | 0 | 6 | 16 | 51 | 0 | 30 | 6 | 0 | 10 | 0 | 0 | 0 | 0 | 300 | 200 | 110 | 50 | 30 | 45 | 0 | 51 | 0 | 33 | 24 | 0 | 0 |  | 18 | 90 | 40 | 0 | 0 | 1.6 | 40 | 30 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 210 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 280 | 0 | 0 | 95 | 0 | 54 | 20 | 25 | 100 | 100 | 280 | 58 | 17 | 85 | 5 | 50 | 17 | 110 | 17 | 9 | 25 | 380 | 17 | 50 | 162 | 108 | 0 | 17 | 35 | 68 | 35 | 330 | 54 | 0 | 612 | 42 | 0 | 0 | 0 | 70 |  | 921 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 16 | 130 | 10 | 16 | 0 | 0 | 0 | 24 | 0 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 53 | 0 | 70 | 0 | 106 | 0 | 8 | 70 | 1244 | 220 |  | 54 | 6 | 100 | 36 | 0 | 0 | 600 | 30 | 250 | 1400 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 450 | 150 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 22 | 24 | 13 | 8 | 0 | 131 | 80 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 310 | 215 | 185 | 40 | 30 | 46 | 0 | 51 | 0 | 0 | 22 | 0 | 0 | 0 | 18 | 74 | 28 | 0 | 0 | 0 | 40 | 30 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 211 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 245 | 0 | 0 | 97 | 0 | 53 | 0 | 25 | 106 | 0 | 221 | 59 | 17 | 85 | 0 | 50 | 0 | 34 | 17 | 9 | 25 | 376 | 4 | 6 | 35 | 53 | 0 | 17 | 3 | 50 | 35 | 195 | 0 | 0 | 550 | 17 | 0 | 0 | 0 | 28 | 0 | 903 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 52 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1100 | 180 | 0 | 0 | 0 | 21 | 35 | 0 | 0 | 560 | 10 | 307 | 1411 | 22 | 0 | 0 | 7 | 0 |  |  |  | 130299873 | 23291636 | 0 | 102225599 | 38494663 | 1840320 | 2352858 | 520320 | 5035624 |  |  | 304060893
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [5 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 130.2999 | 23.2916 | 0 | 102.2256 | 38.4947 | 1.8403 | 2.3529 | 0.52032 | 5.0356
| Minimum Generation |  | 10927 | 8:00
| Highest Generation |  | 13972 | 21:00 | [129 empty] | 0 | [73 empty] | 304.0609
| Day Peak Generation |  | 11950 | 12:00
| Evening Peak Generation |  | 13972 | 21:00 | [203 empty] | 202699852
| HVDC Max Flow |  | 899 | 19:30 | [203 empty] | 202.6999
| HVDC EvPeak Flow |  | 781 | 21:00
| Load factor L.F |  | 90.68% | [167 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-11
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-10 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11950 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11654
Evening Peak Generation : |  |  | 13972 | MW Hour : | 21:00 | Available Max Generation : |  | 15287
E.P. Demand (at gen end) : |  |  | 14130 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 13972 | MW Hour : | 21:00 | Reserve(Generation end) |  | 287
Total Gen. (MKWH) : |  |  | 304.0609 | System Load Factor : | 90.68% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 880 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-11
Actual : |  | 96.85 | Ft.(MSL) , | Rule curve : | 92.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 926 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 393654631.826
: |  |  | Coal : | 696877195.12 | Oil : | 697819376.68 | Total : | 1788351203.626
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 71 | 1704:00 | 5018.7141 |  |  | 0 | -3.533%
Chittagong Area |  | 0 | 0:00 | 1381.88 |  |  | 0 | -1.596%
Khulna Area |  | 0 | 0:00 | 1936.5624 |  |  | 0 | -1.182%
Rajshahi Area |  | 0 | 0:00 | 1683.9775 |  |  | 0 | -0.744%
Cumilla Area |  | 0 | 0:00 | 1385.229 |  |  | 0 | -1.016%
Mymensingh Area |  | 80 | 1920:00 | 1030.6659 |  |  | 0 | -0.6355%
Sylhet Area |  | 0 | 0:00 | 577.2872 |  |  | 0 | -1.362%
Barisal Area |  | 0 | 0:00 | 481.4952 |  |  | 0 | -0.5658%
Rangpur Area |  | 0 | 0:00 | 941.7111 |  |  | 0 | -0.5752%
Total |  | 151 |  | 14437.5225 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Rampal Unit-2
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
| 09:12 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
09:41 | 13:16 | Aminbazar-Kaliakoir 230kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end.
09:56 | 11:09 | BIPTC S/S 10CF15 Tripped showing 60/61 relays Due to Capacitor unbalance
10:36 | 12:06 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Hot point maintenance work |  |  |  |  | 20.0MW load
interrup.
11:37 |  | Full interruption was occurring under Joydevpur, Kodda and Rajendrapur grid substation
with partial interruption under Kabirpur grid substation ( total about 300 MW) 11:37 hrs
to 11:47 hrs due to tripping of 132 kV Ghorashal- Jodevpur line- 1 & 2, showing
distance relay zone 2 Blue phase at Ghorashal end. Ghorashal- Jodevpur line- 2 was
switched on at 11:47 hrs and Ghorashal- Jodevpur line-1 was switched on at 12:22 hrs.
11:43 |  | BSRM 230/33kV S/S 230/33 kV Transformer-3 (125/140 MVA) LT Project Work S/D Due to
remaining civil works, punch points related works and interchanging of overhead
conductor.
11:45 |  | BSRM 230/33kV S/S 230/33 kV Transformer-1 (125/140 MVA) HT Project Work S/D Due to
remaining civil works, punch points related works and interchanging of overhead
conductor.
12:00 |  | Day peak generation :11951 MW
12:08 | 13:10 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Hot point maintenance work |  |  |  |  | 20.0MW load
interrup.
12:48 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:- NLDC demand 250 MW
13:30 |  | Meghnaghat CCPP(Summit) Synchronized
13:42 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
13:42 |  | Meghnaghat CCPP(Summit) GT-1 Shutdown with remarks:- GT-1 Shutdown given as per NLDC
demand.
13:43 |  | Meghnaghat CCPP(Summit) GT-1 Ready with remarks:- GT-1 is in standby condition
13:50 |  | Meghnaghat CCPP(Summit) Synchronized
14:05 |  | Meghnaghat CCPP(Summit) record a general event:- NLDC demand full load with one GT
| 18:31 | Kabirpur-Kaliakoir 132kV Ckt-1 is restored.
21:00 |  | Peak generation 13972 MW
21:00 |  | Evening peak Generation is 13972 MW
06:53 | 07:25 | Madunaghat 132/33kV S/S TR-2(517T) LT Tripped showing REF-615,REF-670 relays Due to PDB |  |  |  |  | 13.0MW load
|  | OLD WASA Feeder Trip |  |  |  |  | interrup.
06:55 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to 33 kV bus side red hot maintenance
06:56 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33 kV bus side red hot maintenance
07:00 |  | Minimum Generation: 11654 MW.
07:10 |  | Chandpur 132/33kV S/S Bus-B Scheduled S/D Due to Red hot maintenance.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-10
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 382 | 9442800 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9364500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 4977367 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 121481 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 738689
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7334703
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 117648 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 243720
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 131 | 1866240 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 570025
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 469544 | Engine problem
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0 | Contract Expired
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 36 | 813960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 562320 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 327400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 138240 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 2777564 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 2061360 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 704640 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 1155840 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1300320
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 147697
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 744480 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 6217 | 2389 | 45980538
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 16 | 110485 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 94635
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 89760 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 212 | 5035624
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 222 | 5314621
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 85 | 1121563 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 41 | 240864 | Low demand
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 198010 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 37 | 504000 | Fuel shortage
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 608160
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 36 | 458880 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23879
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 52 | 1216909 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 34 | 181721 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 72 | 814610 | Fuel shortage
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 37 | 506880 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 1293436 | Engine problem
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 90 | 341236 | Fuel shortage
60 | SS Power I |  | SS Power | 2*612 | 1224 | 608 | 14056362 | Unit-1 Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 8 | 520320
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 0 | 2778181
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 1743 | 35510136
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 5243000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7232000 | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 300 | 8054000 | FGMO
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 715608 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 46 | 1083840 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 88 | 2325091 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1079334
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 90 | 1184291 | Transformer O/L.
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 297104 | Machine problem.
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 33 | 1066090 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 2966880 | Line O/L
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 76 | 1840320
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 641453 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 394000 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 570000 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 236880 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 67 | 1186560 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 90955
| Cumilla Area Total |  |  |  | 2950 | 1607 | 36207406
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 30 | 822720 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11950
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 125 | 2107200 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 79 | 1540800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 178500
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 2 | 117600 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 487440 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 271 | 5266210
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 943000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 27 | 652800 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3458781 | Frequency control
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 111888 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 31 | 723648 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 0 | 10 | 260160 | Contract Expired
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 211 | 5230790
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 270672 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7205500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 270 | 5776000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 350 | 8372200 | FGMO
| Sylhet Area Total |  |  |  | 2331 | 1376 | 33005439
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 781 | 23291636
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 48 | 100800 | Low demand
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 308 | 8480736 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Reserve
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 60 | 730080 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 236880
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 622 | 14421820
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1819 | 47261952
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1095936
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 185049
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 136 | 2851000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 28915500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5393320
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 421200 | Fuel shortage
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6545500
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 862
| Barisal Area Total |  |  |  | 2236 | 2081 | 45408367
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 37 | 204137 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 46 | 169745
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 209 | 4855091
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 332 | 8639636 | Gas shortage
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 193811 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 128088 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 448848 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 375840 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 375552 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34320
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1517 | 34063000
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 0 | 0 | 365250
| Rajshahi Area Total |  |  |  | 3381 | 2409 | 49853318
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 63 | 1445236
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1443705 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 12264
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1510656
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 157666
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 998000
| Rangpur Area Total |  |  |  | 950 | 277 | 5567527
| Total |  |  |  | 26947 | 13972 | 304060893
| Eastern Grid Total |  |  |  | 16526 | 7386 | 155969729
| Western Grid Total |  |  |  | 10421 | 6586 | 148091164
| National Grid Total |  |  |  | 26947 | 13972 | 304060893
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-08-09 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8908.89 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4510.9 | MW
i) Dhaka area |  |  | 4748.19 |  | MW | i) Khulna area |  |  |  | 1725 | MW
ii) Chattogram area |  |  | 1203.7 |  | MW | ii) Barishal area |  |  |  | 438.5 | MW
iii) Cumilla area |  |  | 1246 |  | MW | iii) Rajshahi area |  |  |  | 1430.4 | MW
iv) Mymensingh area |  |  | 1113 |  | MW | iv) Rangpur area |  |  |  | 917 | MW
v) Sylhet area |  |  | 598 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13419.79 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 7 | 11:00 | 67 | Jamalpur | 117 | 00:00 | 133 | Rahim | 44 | 15:00
2 | AKSML | 105 | 03:00 | 68 | Jashore | 121 | 21:00 | 134 | Rajbari | 76 | 19:30
3 | Aftabnagar | 32 | 19:00 | 69 | Jhenaidah | 127 | 19:30 | 135 | Rajendrapur | 90 | 21:00
4 | Agargaon | 99 | 13:00 | 70 | Joydebpur | 170 | 19:00 | 136 | Rajshahi | 118 | 21:00
5 | Agrabad | 86 | 19:30 | 71 | Joypurhat | 65 | 21:00 | 137 | Rajshahi-230 | 72 | 21:00
6 | Amnura | 66 | 00:00 | 72 | Juldah | 18 | 00:00 | 138 | Ramganj | 108 | 19:00
7 | Ashuganj | 74 | 00:00 | 73 | KSRM | 31 | 14:00 | 139 | Rampur | 37 | 23:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 256 | 22:00 | 140 | Rangamati | 19 | 19:00
9 | BSRM | 170 | 04:00 | 75 | Kachua | 72 | 22:00 | 141 | Rangpur | 126 | 09:00
10 | Bagerhat | 95 | 22:00 | 76 | Kallyanpur | 108 | 23:00 | 142 | Ruppur | 4.8 | 09:00
11 | Bakulia | 91 | 19:30 | 77 | Kalurghat | 34 | 12:00 | 143 | SSM | 0 | 00:00
12 | Banani | 48 | 11:00 | 78 | Kamrangirchar | 49 | 13:00 | 144 | Saidpur | 101 | 10:00
13 | Bangabhaban | 9 | 11:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 120 | 22:00
14 | Barapukuria | 59 | 19:00 | 80 | Kazla | 93 | 12:00 | 146 | Satmasjid | 106 | 13:00
15 | Barguna | 21 | 22:00 | 81 | Keranigonj | 88 | 22:00 | 147 | Savar | 212 | 12:00
16 | Barishal | 110 | 23:00 | 82 | Khagrachori | 26 | 18:30 | 148 | SevenRings | 14.97 | 16:00
17 | Barishal-230 | 86 | 19:30 | 83 | Khulna | 58 | 19:30 | 149 | ShahCement | 23 | 00:00
18 | Baroaulia | 63 | 09:00 | 84 | Khulshi | 134 | 13:00 | 150 | Shahjadpur | 81 | 19:30
19 | Baroirhat | 57 | 22:00 | 85 | Kishoreganj | 162 | 22:00 | 151 | Shahjibazar | 126 | 21:00
20 | Bashundhara | 157 | 12:00 | 86 | Kodda | 262 | 21:00 | 152 | Shahmirpur | 53 | 01:00
21 | BashundharaCement | 7 | 04:00 | 87 | Kulaura | 52 | 19:00 | 153 | Shariatpur | 87 | 22:00
22 | Beanibazar | 74 | 22:00 | 88 | Kurigram | 66 | 23:00 | 154 | Sherpur | 140 | 19:00
23 | Benapole | 74 | 22:00 | 89 | Kushtia | 145 | 19:30 | 155 | Shikalbaha | 29 | 15:00
24 | Bhaluka | 122 | 12:00 | 90 | Lalbag | 76 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 50 | 19:00 | 91 | Lalmonirhat | 58 | 19:30 | 157 | Shitalakhya | 79 | 13:00
26 | Bhangura | 36 | 19:30 | 92 | MI_Cement | 11.6 | 15:00 | 158 | Sholosohor | 42 | 12:00
27 | Bheramara(GK) | 66 | 21:00 | 93 | Madanganj | 34 | 19:30 | 159 | Shyampur | 154 | 13:00
28 | Bhulta | 246 | 12:00 | 94 | Madaripur | 111 | 22:00 | 160 | Siddhirganj | 118 | 13:00
29 | Bog-Sherpur | 64 | 22:00 | 95 | Madartek | 90.03 | 23:00 | 161 | Sirajganj | 104 | 19:30
30 | Bogura | 167 | 21:00 | 96 | Madunaghat | 58 | 19:00 | 162 | Sonargaon | 82 | 22:00
31 | Borhanuddin | 80 | 23:00 | 97 | Magura | 64 | 21:00 | 163 | Sreemongol | 69 | 22:00
32 | Brahmanbaria | 168 | 22:00 | 98 | Mahasthangarh | 74 | 00:00 | 164 | Sreepur | 114 | 19:00
33 | Cantonment | 110 | 13:00 | 99 | Manikganj | 116 | 21:00 | 165 | Srinagar | 46.7 | 22:00
34 | Chandpur | 72 | 00:00 | 100 | Maniknagar | 53 | 13:00 | 166 | Sunamganj | 57 | 20:00
35 | Chandraghona | 35 | 19:30 | 101 | Matarbari | 47 | 20:00 | 167 | Sylhet | 46 | 19:00
36 | Chapai | 64 | 13:00 | 102 | Matuail | 71 | 10:00 | 168 | Sylhet-132 | 114 | 16:00
37 | Charsaidpur | 34 | 00:00 | 103 | Millgate | 120 | 11:00 | 169 | TK | 32 | 22:00
38 | Chauddagram | 62 | 00:00 | 104 | Mirpur | 134 | 15:00 | 170 | Tangail | 186 | 21:00
39 | Chhatak | 35 | 23:00 | 105 | Mirsorai | 5 | 21:00 | 171 | Thakurgaon | 104 | 19:30
40 | Chowmuhani | 189 | 21:00 | 106 | Mirzapur | 42 | 12:00 | 172 | Tongi | 119 | 12:00
41 | Chuadanga | 110 | 22:00 | 107 | Mithapukur | 58 | 01:00 | 173 | Ullahpara | 26 | 19:30
42 | Coxsbazar | 127 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 56 | 19:00
43 | Cumilla(N) | 147 | 00:00 | 109 | Mogbazar | 109.5 | 16:00 | 175 | Uttara | 78 | 12:00
44 | Cumilla(S) | 160 | 19:30 | 110 | Mongla | 31 | 23:00 | 176 | UttaraNew | 54 | 00:00
45 | Daudkandi | 147 | 19:00 | 111 | Motijheel | 35 | 13:00 | 177 | Zigatola | 76 | 13:00
46 | Dhaka | 42 | 13:00 | 112 | Munshiganj | 106 | 21:00
47 | Dhamrai | 138 | 11:00 | 113 | Mymensingh | 235 | 20:00
48 | Dhanmondi | 118 | 12:00 | 114 | Naogaon | 129 | 19:30
49 | Dohazari | 91 | 19:00 | 115 | Narail | 57 | 19:30
50 | Faridpur | 172 | 21:00 | 116 | Narinda | 68 | 13:00
51 | Fatullah | 85 | 16:00 | 117 | Narshingdi | 167 | 00:00
52 | Fenchuganj | 42 | 19:00 | 118 | Natore | 146 | 21:00
53 | Feni | 96 | 19:30 | 119 | Nawabganj | 48.2 | 22:00
54 | GPH | 90 | 15:00 | 120 | Netrakona | 113 | 23:00
55 | Ghatail | 66 | 19:00 | 121 | New | 54.3 | 16:00
56 | Ghorashal | 53 | 00:00 | 122 | Niamatpur | 83 | 21:00
57 | Goalpara | 32 | 12:00 | 123 | Noapara | 46 | 15:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-10 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 387 | 07:00 | 376 | 14:00 | Kaliakoir | 377 | 19:00 | 229 | 00:00
| Ashuganj | 407 | 17:00 | 392 | 3:00 | Madunaghat_I | 402 | 19:00 | 393 | 22:00
| Bhulta | 399 | 07:00 | 385 | 15:00 | Meghnaghat | 384 | 07:00 | 373 | 15:00
| Bibiana | 397 | 13:00 | 388 | 15:00 | Payra | 409 | 08:00 | 402 | 00:00
| BIPTC | 402 | 06:00 | 395 | 00:00 | Rahanpur | 398 | 18:30 | 384 | 00:00
| Bogura | 386 | 18:30 | 369 | 00:00 | Rampal | 399 | 18:30 | 388 | 00:00
| Gopalganj | 396 | 07:00 | 385 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 230 | 06:00 | 219 | 11:00 | Haripur | 231 | 20:00 | 225 | 14:00
| AKSML | 242 | 19:00 | 229 | 01:00 | Hasnabad | 232 | 06:00 | 223 | 11:00
| Aminbazar | 230 | 05:00 | 222 | 10:00 | Hathazari | 239 | 16:00 | 232 | 00:00
| Ashuganj | 235 | 05:00 | 229 | 00:00 | Ishurdi | 233 | 18:30 | 224 | 00:00
| Ashuganj-400 | 239 | 18:00 | 229 | 0:00 | Jhenaidah | 225 | 18:30 | 213 | 00:00
| Baghabari | 230 | 06:00 | 222 | 23:00 | Kaliakoir | 234 | 19:00 | 227 | 09:00
| Barapukuria | 213 | 18:00 | 202 | 00:00 | Keranigonj | 230 | 06:00 | 220 | 11:00
| Barapukuria-230 | 212 | 18:30 | 202 | 23:00 | Khulna(S) | 228 | 18:00 | 217 | 00:00
| Barishal | 234 | 18:00 | 226 | 00:00 | Madunaghat_I | 239 | 18:00 | 229 | 00:00
| Bheramara | 232 | 18:30 | 222 | 23:00 | Maniknagar | 233 | 05:00 | 224 | 15:00
| Bhulta | 234 | 07:00 | 224 | 15:00 | Meghnaghat | 239 | 20:00 | 232 | 10:00
| Bibiana | 227 | 12:00 | 223 | 00:00 | Meghnaghat-400 | 235 | 06:00 | 227 | 15:00
| BIPTC | 233 | 18:30 | 222 | 23:00 | Mirsorai | 239 | 19:30 | 227 | 04:00
| Bogura | 222 | 18:30 | 211 | 01:00 | Rajshahi | 231 | 18:30 | 222 | 00:00
| Bogura-400 | 223 | 18:30 | 213 | 00:00 | Rampal | 229 | 18:30 | 219 | 00:00
| Borhanuddin | 238 | 08:00 | 235 | 02:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 238 | 19:00 | 228 | 00:00 | Rampura | 233 | 05:00 | 223 | 15:00
| Cumilla(N) | 231 | 07:00 | 224 | 15:00 | Shikalbaha | 239 | 19:30 | 230 | 02:00
| Faridpur | 234 | 07:00 | 225 | 00:00 | Shyampur | 232 | 07:00 | 223 | 11:00
| Fenchuganj | 231 | 14:00 | 225 | 22:00 | Siddhirganj | 233 | 07:00 | 226 | 10:00
| Ghorashal | 235 | 01:00 | 230 | 18:30 | Sirajgonj | 234 | 06:00 | 229 | 00:00
| Ghorashal-230 | 231 | 06:00 | 224 | 11:00 | Sreepur | 228 | 06:00 | 222 | 23:00
| Gopalganj | 233 | 06:00 | 227 | 00:00 | Tongi | 230 | 04:00 | 225 | 10:00
| GPH | 239 | 19:30 | 230 | 00:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 136 | 06:00 | 128 | 14:00 | Kushtia | 135 | 18:00 | 128 | 23:00
| Agargaon | 134 | 06:00 | 127 | 11:00 | Lalbag | 134 | 06:00 | 127 | 12:00
| Agrabad | 137 | 19:30 | 13 | 12:00 | Lalmonirhat | 127 | 18:30 | 115 | 21:00
| AKS | 135 | 19:00 | 6 | 06:00 | Madanganj | 132 | 07:00 | 126 | 15:00
| Aminbazar | 138 | 03:00 | 129 | 19:00 | Madaripur | 132 | 18:00 | 126 | 00:00
| Amnura | 135 | 21:00 | 13 | 11:00 | Madartek | 136 | 07:00 | 128 | 15:00
| Ashuganj | 140 | 13:00 | 136 | 00:00 | Madunaghat | 138 | 22:00 | 132 | 01:00
| Bagerhat | 133 | 16:00 | 122 | 00:00 | Magura | 135 | 10:00 | 125 | 23:00
| Bakulia | 137 | 19:30 | 132 | 03:00 | Mahasthangarh | 131 | 18:30 | 122 | 00:00
| Banani | 136 | 07:00 | 127 | 15:00 | Manikganj | 130 | 13:00 | 123 | 23:00
| Bangabhaban | 133 | 07:00 | 125 | 11:00 | Maniknagar | 132 | 03:00 | 126 | 11:00
| Barapukuria | 133 | 18:00 | 12 | 02:00 | Matarbari | 127 | 16:00 | 117 | 00:00
| Barguna | 134 | 23:00 | 128 | 00:00 | Matuail | 132 | 06:00 | 126 | 11:00
| Barishal | 139 | 18:00 | 131 | 00:00 | Millgate | 134 | 06:00 | 128 | 10:00
| Barishal-230 | 140 | 18:00 | 132 | 00:00 | Mirpur | 136 | 06:00 | 127 | 11:00
| Baroaulia | 137 | 21:00 | 132 | 09:00 | Mirzapur | 129 | 13:00 | 122 | 00:00
| Baroirhat | 133 | 12:00 | 127 | 00:00 | Mithapukur | 129 | 18:30 | 121 | 00:00
| Bashundhara | 135 | 05:00 | 127 | 15:00 | MI_Cement | 133 | 07:00 | 127 | 11:00
| BashundharaCement | 132 | 07:00 | 126 | 15:00 | Modern | 137 | 19:00 | 132 | 00:00
| Beanibazar | 129 | 18:30 | 120 | 00:00 | Mogbazar | 137 | 04:00 | 129 | 15:00
| Benapole | 131 | 17:00 | 121 | 00:00 | Mongla | 132 | 16:00 | 122 | 00:00
| Bhaluka | 127 | 06:00 | 120 | 23:00 | Motijheel | 133 | 07:00 | 125 | 11:00
| Bhandaria | 135 | 17:00 | 125 | 08:00 | Munshiganj | 132 | 07:00 | 127 | 10:00
| Bhangura | 135 | 18:30 | 130 | 00:00 | Mymensingh | 134 | 18:00 | 115 | 23:00
| Bheramara | 135 | 06:00 | 131 | 00:00 | Naogaon | 130 | 18:30 | 119 | 00:00
| Bheramara(GK) | 135 | 06:00 | 132 | 00:00 | Narail | 133 | 10:00 | 125 | 00:00
| Bhulta | 125 | 19:00 | 119 | 11:00 | Narinda | 132 | 03:00 | 126 | 11:00
| Bog-Sherpur | 133 | 18:30 | 124 | 00:00 | Narshingdi | 123 | 05:00 | 117 | 10:00
| Bogura | 134 | 18:30 | 126 | 01:00 | Natore | 160 | 05:00 | 126 | 00:00
| Bogura-230 | 134 | 18:30 | 126 | 00:00 | Nawabganj | 162 | 06:00 | 128 | 11:00
| Brahmanbaria | 130 | 07:00 | 123 | 00:00 | Netrakona | 132 | 20:00 | 118 | 00:00
| Cantonment | 134 | 06:00 | 126 | 11:00 | New | 135 | 04:00 | 128 | 10:00
| Chandpur | 130 | 04:00 | 122 | 15:00 | Niamatpur | 133 | 18:30 | 126 | 22:00
| Chandraghona | 137 | 13:00 | 134 | 00:00 | Noapara | 135 | 18:30 | 125 | 00:00
| Chapai | 132 | 18:30 | 122 | 21:00 | Pabna | 134 | 06:00 | 128 | 23:00
| Charsaidpur | 133 | 07:00 | 127 | 11:00 | Palashbari | 128 | 18:30 | 119 | 00:00
| Chauddagram | 127 | 05:00 | 122 | 00:00 | Panchagarh | 135 | 18:30 | 118 | 08:00
| Chhatak | 127 | 08:00 | 122 | 00:00 | Patuakhali | 135 | 23:00 | 128 | 00:00
| Chowmuhani | 122 | 05:00 | 114 | 22:00 | Payra | 135 | 18:30 | 131 | 00:00
| Chuadanga | 130 | 10:00 | 118 | 23:00 | PHP | 131 | 13:00 | 125 | 00:00
| Coxsbazar | 127 | 17:00 | 118 | 01:00 | Postogola | 135 | 05:00 | 130 | 10:00
| Cumilla(N) | 133 | 07:00 | 128 | 15:00 | Purbachal | 137 | 05:00 | 127 | 15:00
| Cumilla(S) | 131 | 07:00 | 126 | 19:30 | Purbasadipur | 131 | 18:30 | 115 | 08:00
| Daudkandi | 125 | 06:00 | 116 | 23:00 | Rahanpur | 135 | 18:30 | 129 | 00:00
| Dhaka | 136 | 07:00 | 128 | 15:00 | Rahim | 132 | 01:00 | 126 | 15:00
| Dhamrai | 132 | 06:00 | 125 | 15:00 | Rajbari | 131 | 18:00 | 126 | 00:00
| Dhanmondi | 138 | 02:00 | 129 | 15:00 | Rajendrapur | 135 | 13:00 | 127 | 10:00
| Dohazari | 134 | 13:00 | 128 | 00:00 | Rajshahi | 133 | 18:30 | 127 | 00:00
| Faridpur | 131 | 08:00 | 127 | 00:00 | Rajshahi-230 | 133 | 18:00 | 117 | 00:00
| Fatullah | 134 | 07:00 | 128 | 11:00 | Ramganj | 125 | 12:00 | 116 | 15:00
| Fenchuganj | 133 | 13:00 | 129 | 02:00 | Rampur | 136 | 19:00 | 131 | 03:00
| Feni | 124 | 12:00 | 117 | 15:00 | Rampura | 136 | 05:00 | 127 | 15:00
| Ghatail | 130 | 18:30 | 122 | 00:00 | Rangamati | 136 | 16:00 | 133 | 00:00
| Ghorashal | 140 | 13:00 | 134 | 11:00 | Rangpur | 129 | 18:30 | 117 | 08:00
| Goalpara | 136 | 18:00 | 127 | 01:00 | Ruppur | 136 | 06:00 | 131 | 00:00
| Gollamari | 136 | 18:30 | 128 | 00:00 | Saidpur | 129 | 18:30 | 117 | 09:00
| Gopalganj | 132 | 18:00 | 125 | 00:00 | Satkhira | 132 | 18:00 | 122 | 00:00
| Gopalganj-400 | 132 | 07:00 | 128 | 00:00 | Satmasjid | 133 | 06:00 | 127 | 11:00
| Gulshan | 135 | 06:00 | 127 | 15:00 | Savar | 137 | 20:00 | 127 | 10:00
| Halishahar | 137 | 19:00 | 131 | 09:00 | SevenRings | 139 | 12:00 | 133 | 15:00
| Haripur | 132 | 01:00 | 126 | 15:00 | ShahCement | 133 | 07:00 | 127 | 11:00
| HaripurSBU | 132 | 01:00 | 126 | 15:00 | Shahjadpur | 138 | 04:00 | 134 | 00:00
| Hasnabad | 135 | 03:00 | 130 | 15:00 | Shahjibazar | 128 | 07:00 | 122 | 23:00
| Hathazari | 139 | 16:00 | 135 | 09:00 | Shahmirpur | 136 | 13:00 | 130 | 01:00
| Ishurdi | 136 | 06:00 | 131 | 23:00 | Shariatpur | 132 | 18:00 | 125 | 00:00
| Jaldhaka | 128 | 18:30 | 116 | 08:00 | Sherpur | 133 | 20:00 | 120 | 04:00
| Jamalpur | 135 | 19:30 | 124 | 05:00 | Shikalbaha | 125 | 13:00 | 121 | 01:00
| Jashore | 132 | 18:00 | 122 | 00:00 | Shikalbaha-230 | 138 | 19:30 | 8 | 06:00
| Jhenaidah | 136 | 15:00 | 128 | 00:00 | Shitalakhya | 133 | 07:00 | 127 | 11:00
| Jhenaidah-230 | 136 | 10:00 | 129 | 00:00 | Sholosohor | 137 | 19:00 | 131 | 09:00
| Joydebpur | 140 | 12:00 | 129 | 15:00 | Shyampur | 134 | 19:00 | 128 | 10:00
| Joypurhat | 128 | 18:30 | 117 | 00:00 | Shyampur-230 | 133 | 06:00 | 127 | 11:00
| Juldah | 137 | 19:30 | 132 | 00:00 | Siddhirganj | 132 | 06:00 | 127 | 15:00
| Kabirpur | 135 | 19:30 | 125 | 10:00 | Sirajganj | 130 | 06:00 | 126 | 00:00
| Kachua | 131 | 20:00 | 123 | 15:00 | Sonargaon | 131 | 06:00 | 125 | 00:00
| Kaliakoir | 134 | 04:00 | 129 | 09:00 | Sreemongol | 129 | 06:00 | 123 | 15:00
| Kallyanpur | 132 | 07:00 | 127 | 15:00 | Sreepur | 129 | 06:00 | 123 | 23:00
| Kalurghat | 137 | 19:00 | 132 | 02:00 | Srinagar | 134 | 06:00 | 128 | 11:00
| Kamrangirchar | 135 | 07:00 | 126 | 11:00 | SSM | 140 | 07:00 | 138 | 00:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 125 | 07:00 | 119 | 22:00
| Kazla | 132 | 06:00 | 126 | 11:00 | Sylhet | 128 | 07:00 | 125 | 00:00
| Keranigonj | 134 | 06:00 | 128 | 11:00 | Sylhet-132 | 128 | 07:00 | 125 | 00:00
| Khagrachori | 135 | 13:00 | 130 | 00:00 | Tangail | 127 | 18:30 | 119 | 00:00
| Khulna | 135 | 18:00 | 126 | 00:00 | Thakurgaon | 134 | 18:30 | 115 | 08:00
| Khulna(S) | 136 | 18:00 | 128 | 00:00 | TK | 137 | 19:30 | 132 | 03:00
| Khulshi | 136 | 19:30 | 131 | 00:00 | Tongi | 136 | 04:00 | 129 | 12:00
| Kishoreganj | 130 | 06:00 | 123 | 23:00 | Ullahpara | 135 | 04:00 | 129 | 00:00
| Kodda | 137 | 13:00 | 127 | 23:00 | Ullon | 135 | 05:00 | 127 | 15:00
| KSRM | 137 | 18:30 | 132 | 00:00 | Uttara | 136 | 20:00 | 129 | 10:00
| Kulaura | 131 | 08:00 | 127 | 23:00 | UttaraNew | 137 | 05:00 | 129 | 10:00
| Kurigram | 127 | 18:30 | 115 | 07:00 | Zigatola | 135 | 07:00 | 128 | 11:00

## L-Curve
Date | 2024-08-10
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1076 | 7184 | 6574 | 13758 |  |  |  | QF-LDC-11
0:30 | 991 | 6971.5 | 6335 | 13306.5 | Date: | 2024-08-10
1:00 | 906 | 6759 | 6096 | 12855
1:30 | 927 | 6590.5 | 6077.5 | 12668
2:00 | 948 | 6422 | 6059 | 12481
2:30 | 973 | 6313 | 6054 | 12367 | [5 empty] | Gen. at Eve. Peak | 13972 | 13972 MW (21:00 )
3:00 | 998 | 6204 | 6049 | 12253 | [6 empty] | 21:00
3:30 | 1019 | 6002 | 5966 | 11968 | [5 empty] | Gen. at Day Peak | 11950 | 11950 MW (12:00 )
4:00 | 1040 | 5800 | 5883 | 11683 | [6 empty] | 12:00
4:30 | 1048 | 5848.5 | 5884.5 | 11733 | [5 empty] | Highest Generation | 13972
5:00 | 1056 | 5897 | 5886 | 11783 | [6 empty] | 21:00
5:30 | 1043 | 5774 | 5658.5 | 11432.5
6:00 | 1030 | 5651 | 5431 | 11082
6:30 | 955 | 5736 | 5351 | 11087
7:00 | 880 | 5821 | 5271 | 11092
7:30 | 918 | 5803.5 | 5206 | 11009.5
8:00 | 956 | 5786 | 5141 | 10927
8:30 | 1069 | 5816.5 | 5316 | 11132.5
9:00 | 1182 | 5847 | 5491 | 11338
9:30 | 1269 | 5815.5 | 5582.5 | 11398
10:00 | 1356 | 5784 | 5674 | 11458
10:30 | 1309 | 5950.5 | 5698 | 11648.5
11:00 | 1262 | 6117 | 5722 | 11839
11:30 | 1216 | 6099 | 5795.5 | 11894.5
12:00 | 1170 | 6081 | 5869 | 11950
12:30 | 1089 | 6304.5 | 5863.5 | 12168
13:00 | 1008 | 6528 | 5858 | 12386
13:30 | 1119 | 6525.5 | 5925.5 | 12451
14:00 | 1230 | 6523 | 5993 | 12516
14:30 | 1190 | 6565 | 5981 | 12546
15:00 | 1150 | 6607 | 5969 | 12576
15:30 | 1225 | 6547.5 | 5897.5 | 12445
16:00 | 1300 | 6488 | 5826 | 12314
16:30 | 1311 | 6353 | 5748 | 12101
17:00 | 1322 | 6218 | 5670 | 11888
17:30 | 1267 | 6169 | 5525 | 11694
18:00 | 1212 | 6120 | 5380 | 11500
18:30 | 1126 | 6471.5 | 5792 | 12263.5
19:00 | 1040 | 6823 | 6204 | 13027
19:30 | 990 | 7374 | 6504 | 13878
20:00 | 1004 | 7254 | 6598 | 13852 |  |  |  | Executive Engineer
20:30 | 954 | 7320 | 6592 | 13912 |  |  |  | Network Operation Division
21:00 | 904 | 7386 | 6586 | 13972
21:30 | 895 | 7376.5 | 6557.5 | 13934
22:00 | 886 | 7367 | 6529 | 13896 |  |  |  |  | Page 6 of 7
22:30 | 979 | 7293 | 6585 | 13878
23:00 | 1072 | 7219 | 6641 | 13860
23:30 | 1074 | 7201.5 | 6607.5 | 13809
24:00 | 1076 | 7184 | 6574 | 13758
13972 MW (21:00 )
11950 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-10 |  | Energy |  | 304060893
[14 empty] | Date: | 2024-08-10 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3439 | 899 | 1739 | 0 | 2670 | 4299 | 214 | 0 | 401 | 88 | 0 | 9 | 192.91
0:30 | 3504.5 | 887 | 1861.5 | 0 | 1886 | 4551 | 214.5 | 0 | 302.5 | 89 | 0 | 10.5 | 165.6925 |  |  | Date: | 44052
1:00 | 3570 | 875 | 1984 | 0 | 1102 | 4803 | 215 | 0 | 204 | 90 | 0 | 12 | 138.475
1:30 | 3580.5 | 875.5 | 2004.5 | 0 | 1041.5 | 4685.5 | 215 | 0 | 169 | 85 | 0 | 11.5 | 126.06 | [9 empty] | Total Energy | 304.0609 | 304.0609 | Total Energy Gen 304.061 MKWHr Energy Not Served 3.659 MKWHr Energy Requirement 307.720 MKWHr
2:00 | 3591 | 876 | 2025 | 0 | 981 | 4568 | 215 | 0 | 134 | 80 | 0 | 11 | 113.645 | [9 empty] | Energy not Served | 3.6587 | 3.6587
2:30 | 3576 | 875.5 | 2024 | 0 | 980.5 | 4489.5 | 214.5 | 0 | 113.5 | 80 | 0 | 13.5 | 107.915 | [9 empty] | Energy Requirement | 307.7195 | 307.7195
3:00 | 3561 | 875 | 2023 | 0 | 980 | 4411 | 214 | 0 | 93 | 80 | 0 | 16 | 102.185
3:30 | 3450 | 875.5 | 2025 | 0 | 836 | 4391.5 | 213.5 | 0 | 78.5 | 79 | 0 | 19 | 75.9225 | [8 empty] | Shortage
4:00 | 3339 | 876 | 2027 | 0 | 692 | 4372 | 213 | 0 | 64 | 78 | 0 | 22 | 49.66
4:30 | 3392.5 | 877 | 2055.5 | 0 | 671.5 | 4362.5 | 212.5 | 0 | 64 | 75 | 0 | 22.5 | 56.8225
5:00 | 3446 | 878 | 2084 | 0 | 651 | 4353 | 212 | 0 | 64 | 72 | 0 | 23 | 63.985
5:30 | 3403.5 | 877.5 | 1991 | 0 | 551.5 | 4226.5 | 211.5 | 0 | 64 | 77 | 7 | 23 | 69.2375
6:00 | 3361 | 877 | 1898 | 0 | 452 | 4100 | 211 | 0 | 64 | 82 | 14 | 23 | 74.49
6:30 | 3449.5 | 877 | 1864 | 0 | 460 | 4017.5 | 211.5 | 0 | 64 | 78 | 45.5 | 20 | 76.8775 | [7 empty] | Coal
7:00 | 3538 | 877 | 1830 | 0 | 468 | 3935 | 212 | 0 | 64 | 74 | 77 | 17 | 79.265
7:30 | 3476 | 877.5 | 1785 | 0 | 486 | 3896.5 | 212 | 0 | 56 | 73 | 130.5 | 17 | 122.24 | [6 empty] | Oil
8:00 | 3414 | 878 | 1740 | 0 | 504 | 3858 | 212 | 0 | 48 | 72 | 184 | 17 | 165.215
8:30 | 3503.5 | 877.5 | 1802 | 0 | 504 | 3890.5 | 212.5 | 0 | 48 | 69 | 207.5 | 18 | 159.9625
9:00 | 3593 | 877 | 1864 | 0 | 504 | 3923 | 213 | 0 | 48 | 66 | 231 | 19 | 154.71
9:30 | 3581.5 | 877 | 1838 | 0 | 613.5 | 3872 | 213 | 0 | 48 | 68 | 263 | 24 | 157.0975
10:00 | 3570 | 877 | 1812 | 0 | 723 | 3821 | 213 | 0 | 48 | 70 | 295 | 29 | 159.485
10:30 | 3615 | 877.5 | 1829.5 | 0 | 828.5 | 3843.5 | 213.5 | 0 | 56 | 72 | 277.5 | 35.5 | 156.7425
11:00 | 3660 | 878 | 1847 | 0 | 934 | 3866 | 214 | 0 | 64 | 74 | 260 | 42 | 154
11:30 | 3608 | 877.5 | 1815 | 0 | 1067.5 | 3877.5 | 214 | 0 | 32 | 74 | 289.5 | 39.5 | 230
12:00 | 3556 | 877 | 1783 | 0 | 1201 | 3889 | 214 | 0 | 0 | 74 | 319 | 37 | 306
12:30 | 3566.5 | 878 | 1788.5 | 0 | 1369 | 3939 | 214 | 0 | 32 | 74 | 272.5 | 34.5 | 240.86
13:00 | 3577 | 879 | 1794 | 0 | 1537 | 3989 | 214 | 0 | 64 | 74 | 226 | 32 | 175.72
13:30 | 3577 | 879 | 1794 | 0 | 1537 | 3989 | 214 | 0 | 64 | 74 | 226 | 32 | 175.72
14:00 | 3577 | 879 | 1794 | 0 | 1537 | 3989 | 214 | 0 | 64 | 74 | 226 | 32 | 175.72
14:30 | 3599.5 | 878.5 | 1830 | 0 | 1592.5 | 4028 | 214.5 | 0 | 64 | 77 | 165 | 32 | 180.495
15:00 | 3622 | 878 | 1866 | 0 | 1648 | 4067 | 215 | 0 | 64 | 80 | 104 | 32 | 185.27
15:30 | 3611.5 | 887.5 | 1815 | 0 | 1604.5 | 3968.5 | 215 | 0 | 64 | 81 | 154.5 | 43.5 | 191
16:00 | 3601 | 897 | 1764 | 0 | 1561 | 3870 | 215 | 0 | 64 | 82 | 205 | 55 | 196.73
16:30 | 3605.5 | 897 | 1791.5 | 0 | 1457 | 3812.5 | 215.5 | 0 | 65 | 75 | 147.5 | 34.5 | 199.595
17:00 | 3610 | 897 | 1819 | 0 | 1353 | 3755 | 216 | 0 | 66 | 68 | 90 | 14 | 202.46
17:30 | 3554 | 897 | 1769 | 0 | 1377.5 | 3675.5 | 213.5 | 0 | 72 | 67 | 54 | 14.5 | 196.73
18:00 | 3498 | 897 | 1719 | 0 | 1402 | 3596 | 211 | 0 | 78 | 66 | 18 | 15 | 191
18:30 | 3538.5 | 897.5 | 1786.5 | 0 | 1677.5 | 3790.5 | 211 | 0 | 271 | 71 | 9 | 11 | 192.4325
19:00 | 3579 | 898 | 1854 | 0 | 1953 | 3985 | 211 | 0 | 464 | 76 | 0 | 7 | 193.865
19:30 | 3541 | 899 | 1818 | 0 | 2545 | 4284 | 211 | 0 | 489 | 82 | 0 | 9 | 191.4775
20:00 | 3507 | 898 | 1693 | 0 | 2605 | 4333 | 211 | 0 | 514 | 78 | 0 | 13 | 189.09
20:30 | 3526 | 839.5 | 1726 | 0 | 2654 | 4347 | 211.5 | 0 | 520.5 | 77 | 0 | 10.5 | 169.99
21:00 | 3545 | 781 | 1759 | 0 | 2703 | 4361 | 212 | 0 | 527 | 76 | 0 | 8 | 150.89
21:30 | 3542 | 780.5 | 1738.5 | 0 | 2695.5 | 4352.5 | 212.5 | 0 | 521.5 | 78 | 0 | 13 | 139.43
22:00 | 3539 | 780 | 1718 | 0 | 2688 | 4344 | 213 | 0 | 516 | 80 | 0 | 18 | 127.97
22:30 | 3490.5 | 839.5 | 1718.5 | 0 | 2692.5 | 4348 | 213.5 | 0 | 479.5 | 81 | 0 | 15 | 149.935
23:00 | 3442 | 899 | 1719 | 0 | 2697 | 4352 | 214 | 0 | 443 | 82 | 0 | 12 | 171.9
23:30 | 3440.5 | 899 | 1729 | 0 | 2683.5 | 4325.5 | 214 | 0 | 422 | 85 | 0 | 10.5 | 182.405 |  |  | Max Temp. in Dhaka |  | 33.1°C
24:00 | 3439 | 899 | 1739 | 0 | 2670 | 4299 | 214 | 0 | 401 | 88 | 0 | 9 | 192.91
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 304.061 MKWHr Energy Not Served 3.659 MKWHr Energy Requirement 307.720 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-10
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 135 | 135 | 134 | 133 | 132 | 131 | 132 | 132 | 133 | 133 | 134 | 134 | 134 | 134 | 135 | 135 | 136 | 131 |  | 131 | 131 | 131 | 132 | 133 | 134 | 134 | 3095624
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1940000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [13 empty] | 5 | 8 | 8 | 13 | 16 |  | 16 | 16 | 16 | 16 | 8 | 0 | 0 | 110485
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 8 | 7 | 17 | 10 | 10 | 19 | 14 | 5 | 2 | 4 | 1 | [8 empty] | 94635
6 | Sikalbaha 225MW CCPP (Gas) | 225 | 225 | 225 | 224 | 224 | 223 | 224 | 224 | 224 | 224 | 221 | 224 | 224 | 224 | 220 | 220 | 221 | 219 |  | 218 | 221 | 222 | 222 | 223 | 223 | 224 | 5314621
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | [18 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 198010
12 | Hathazari 100 MW peaking PP | 32 | [18 empty] | 33 | 33 | 38 | 41 | 41 | 41 | 41 | 240864
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [8 empty] | 1 | 34 | 39 | 85 | 85 | 85 | 85 | 77 | 51 | 51 |  | 60 | 85 | 85 | 85 | 85 | 85 | 85 | 1121563
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 29 | [13 empty] | 2 | 14 |  | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 297104
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 270 | 270 | 330 | 332 | 330 | 270 | 270 | 270 | 327 | 280 | 280 | 280 | 324 | 322 | 324 | 325 |  | 327 | 326 | 280 | 327 | 325 | 326 | 327 | 7334703
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 45 | 45 | [6 empty] | 35 | 45 | 85 | 145 | 145 | 145 | 145 | 125 | 125 |  | 160 | 278 | 266 | 280 | 280 | 278 | 276 | 2777564
19 | Ashuganj 195 MW PP (APSCL-United) | 110 | 110 | 110 | 110 | 110 | 110 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 103 | 107 | 108 |  | 108 | 108 | 108 | 88 | 88 | 88 | 88 | 2325091
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 590 | 590 | 590 | 590 | 592 | 590 | 589 | 590 | 598 | 606 | 608 | 578 | 585 | 590 | 590 | 551 | 505 | 500 |  | 555 | 578 | 587 | 608 | 606 | 608 | 608 | 14056362
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 25 | 29 | 32 | 33 | 33 | 33 | 33 | 33 | 30 |  | 33 | 33 | 33 | 33 | 34 | 34 | 34 | 715608
33 | Ashuganj 225 MW CCPP | 218 | 216 | 217 | 216 | 215 | 216 | 217 | 216 | 215 | 216 | 214 | 217 | 216 | 214 | 213 | 215 | 213 | 212 |  | 215 | 217 | 217 | 217 | 217 | 215 | 217 | 5243000
34 | Ashuganj 450 MW CCPP(South) | 300 | 315 | 300 | 310 | 320 | 305 | 305 | 260 | 295 | 270 | 295 | 270 | 270 | 265 | 300 | 305 | 310 | 320 |  | 315 | 305 | 305 | 305 | 305 | 280 | 275 | 7232000
Ashuganj 450 MW CCPP(North)
| Ashuganj 420 MW CCPP(East) | 345 | 350 | 345 | 340 | 330 | 345 | 360 | 360 | 345 | 330 | 345 | 330 | 330 | 330 | 335 | 330 | 330 | 330 |  | 325 | 330 | 330 | 300 | 295 | 295 | 290 | 8054000
35 | Ashuganj 55 MW PP (Precision) | 48 | 47 | 47 | 48 | 47 | 47 | 47 | 47 | 46 | 45 | 43 | 42 | 41 | 43 | 43 | 44 | 44 | 45 |  | 44 | 45 | 45 | 46 | 46 | 46 | 46 | 1083840
36 | Chandpur 150 MW CCPP | 50 | 50 | 50 | 50 | 50 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 42 | 40 | 40 | 38 | 38 |  | 33 | 33 | 33 | 33 | 34 | 34 | 36 | 1066090
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 360 | 360 | 367 | 405 | 387 | 354 | 334 | 402 | 408 | 403 | 402 | 402 | 402 | 402 | 402 | 402 | 402 |  | 402 | 353 | 357 | 382 | 401 | 401 | 401 | 9442800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 400 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 420 | 420 | 420 | 420 |  | 420 | 420 | 360 | 400 | 400 | 400 | 400 | 9364500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 47 | 48 | 49 | 49 | 49 | 50 | 50 | 44 | 44 | 30 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 |  | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 822720
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 21 | 13 | 5 | 23 | 54 | 7 | 8 | 7 | 9 | 6 | 2 | 2 | [8 empty] | 178500
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 943000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 27 | 27 | 27 | 27 | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30 |  | 30 | 27 | 27 | 27 | 27 | 28 | 28 | 652800
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 32 | 31 | 32 | 31 | 31 | 31 | 30 | 30 | 31 | 30 | 31 | 30 | 30 | 29 | 31 | 30 | 20 |  | 31 | 31 | 32 | 31 | 31 | 31 | 31 | 723648
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 260160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 209 | 209 | 209 | 210 | 210 | 213 | 213 | 213 | 212 | 212 | 212 | 208 | 210 | 210 | 210 | 206 | 206 | 210 |  | 210 | 210 | 211 | 211 | 211 | 211 | 211 | 5230790
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 111888
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 8 | 12 | 12 | 12 | 8 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 270672
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 300 | 310 | 300 | 315 | 290 | 295 | 290 | 310 | 285 | 305 | 275 | 285 | 280 | 305 | 280 | 290 | 295 |  | 315 | 290 | 280 | 300 | 290 | 285 | 300 | 7205500
| Bibiyana South 400 MW | 340 | 364 | 340 | 355 | 358 | 345 | 341 | 366 | 340 | 340 | 352 | 340 | 365 | 340 | 350 | 350 | 350 | 356 |  | 345 | 345 | 350 | 350 | 350 | 330 | 320 | 8372200
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | [8 empty] | 35 | 35 | 35 | 35 | 35 | 17 | 17 |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 469544
59 | Tangail Palli Power Gen 22 MW | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 5 | 0 | 0 | 2 | 0 | 0 | 3 | 117600
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 90 | 80 | 80 | 78 | 72 | 82 | 74 | 72 | 66 | 70 | 74 | 74 | 74 | 78 | 80 | 82 | 68 | 66 |  | 76 | 82 | 78 | 76 | 80 | 82 | 88 | 1840320
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 33 | 15 | 6 | 5 | 5 | 7 | 4 | 12 | 6 | 6 | 10 | 17 |  | 23 | 25 | 27 | 32 | 21 | 34 | 37 | 608160
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 6 | 16 | 16 |  | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 394000
69 | Summit Ashulia | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 13 | 13 | 12 | 12 | 12 | 12 | 15 | 15 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 |  |  | 15 | 318600
70 | Summit Madhabdi | 0 | 10 | 22 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 495360
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 20 | 20 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 562320
72 | Rupganj 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 14 | 13 | 13 | 13 | 13 | 13 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 327400
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 17 | 17 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 570000
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 12 | 13 |  | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 236880
| Manikgonj 162MW PP(MPGL) | [11 empty] | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 120 | 162 | 162 | 162 | 162 | 162 | 162 | 1300320
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 |  | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 138240
79 | Kodda 150 MW PP | 98 | 98 | 64 | 64 | 64 | 64 | 64 | 48 | 48 | 48 | 64 |  | 64 | 64 | 64 | 64 | 64 | 64 |  | 131 | 131 | 131 | 131 | 132 | 132 | 132 | 1866240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 25 | 25 | 25 | 33 | 41 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 641453
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 52 | 52 | 52 | 52 | 52 | 35 | 17 | 704640
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 2 | 2 | 4 | 3 | 0 | 2 | 3 | 3 | 2 | 1 | [9 empty] | 23879
| Jodiac Power | [20 empty] | 13 | 31 | 34 | 34 | 34 | 34 | 181721
| Karnaphuli Power Ltd. | [10 empty] | 6 | 40 | 51 | 51 | 51 | 51 | 34 | 34 |  | 48 | 72 | 72 | 72 | 75 | 92 | 92 | 814610
82 | Madanganj 102 PP(Summit) | [19 empty] | 8 | 34 | 34 | 34 | 28 | 17 | 17 | 121481
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 252 | 251 | 253 | 252 | 252 | 250 | 250 | 253 | 257 | 250 | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4977367
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 27 | 75 | 105 | 105 | 107 | 107 | 107 | 107 | 107 | 52 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 1155840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 |  | 21 | 51 | 51 | 51 | 51 | 51 | 51 | 1079334
94 | Gagnagar 102 MW PP (Digital Power) | 8 | [10 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 117648
95 | Patenga 50MW PP (Baraka) | [20 empty] | 12 | 19 | 19 | 19 | 20 | 20 | 89760
96 | Chattogram 108 MW PP (ECPV) | 12 | 12 | 12 | [9 empty] | 19 | 31 | 31 | 31 | 37 | 37 |  | 40 | 38 | 35 | 36 | 38 | 38 | 39 | 458880
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | [10 empty] | 30 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 738689
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | [8 empty] | 21 | 35 | 35 | 35 | 35 | 17 | 17 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 570025
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 163 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 120 |  | 120 | 163 | 120 | 120 | 120 | 120 | 120 | 3458781
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 11950
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 10 | 54 | 51 | 54 | 54 | 35 | 35 | 243720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 98 | 98 | 98 | 98 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 55 | 55 | 58 |  | 123 | 123 | 126 | 125 | 125 | 125 | 125 | 2107200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 52 | 95 |  | 30 | 99 | 107 | 107 | 107 | 115 |  | 120 | 128 | 131 | 133 | 133 | 133 | 133 | 2061360
115 | Juldah 100 MW PP Unit-3 (Acorn) | 24 | 24 | 24 | [7 empty] | 15 | 38 | 37 | 37 | 37 | 37 | 12 | 12 |  | 22 | 37 | 37 | 37 | 37 | 37 | 25 | 504000
116 | Chandpur 200 MW (Desh energy) | 155 | 155 | 155 | 155 | 155 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 122 | 170 | 170 | 170 | 170 | 170 | 170 | 2966880
117 | Ashuganj 150 MW PP (Midland) | [11 empty] | 10 | 94 | 119 | 115 | 60 | 40 | 70 |  | 76 | 90 | 90 | 90 | 90 | 90 | 90 | 1184291
118 | Bibiyana-III 400 MW CCPP | 241 | 251 | 241 |  |  | 0 | 215 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 279 | 220 |  | 260 | 270 | 270 | 270 | 270 | 271 | 271 | 5776000
| Jamalpur 115 MW PP (United) | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 58 | 58 | 58 | 58 | 58 |  | 78 | 78 | 78 | 79 | 78 | 79 | 79 | 1540800
| Anwara 300 MW PP (United) | 100 | 50 | 50 | 15 | 20 | 15 | 15 | 15 | 15 | 35 | 66 | 67 | 69 | 70 | 70 | 70 | 62 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1216909
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | [6 empty] | 12 | 37 | 37 | 37 | 37 | 37 | 12 | 12 |  | 35 | 37 | 37 | 37 | 37 | 37 | 25 | 506880
| Anlima Energy Ltd. | [9 empty] | 1 | 42 | 97 | 108 | 108 | 108 | 108 | 65 | 53 |  | 55 | 108 | 108 | 108 | 108 | 108 | 108 | 1293436
| Bhairob 54.5 MW | 20 | 17 | 17 | [8 empty] | 4 | 25 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 487440
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 14 | 24 | 22 | 9 | 10 | 26 | 14 | 7 | 12 | 7 | 1 | [8 empty] | 147697
| Chandpur 115(Doreen) | 68 | 68 | 67 | 67 | 66 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 |  | 52 | 67 | 65 | 67 | 68 | 68 | 67 | 1186560
| Kanchan Purbachal Power Generation Ltd. | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 35 | 35 | 35 | 35 | 25 | 31 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 744480
| Mirsharai 150 MW (Oil) | [19 empty] | 70 | 90 | 90 | 90 | 90 | 17 | 17 | 341236
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 12 | 11 | 16 | 22 | 23 | 23 | 17 | 17 | 19 | 29 | 42 | 37 | 32 | 41 | 32 | 55 | 14 | 15 |  | 7 | 9 | 13 | 8 | 18 | 12 | 9 | 520320
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 5 | 30 | 27 | 19 | 11 | 5 | 3 | 4 | 2 | 5 | 1 | 1 | [8 empty] | 90955
| Matarbari 2*600 MW (CPGCL) | 564 | 368 | 217 | 248 | 214 | 216 | 215 | 214 | 160 | 0 | [15 empty] | 0 | 2778181
120 | Eastern Zone Total | 6759 | 6422 | 6204 | 5800 | 5897 | 5651 | 5821 | 5786 | 5847 | 5784 | 6117 | 6081 | 6528 | 6523 | 6607 | 6488 | 6218 | 6120 |  | 6823 | 7374 | 7254 | 7386 | 7367 | 7219 | 7184 | 155969729
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [20 empty] | 12 | 16 | 48 | 16 | 16 | 16 | 100800
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | [6 empty] | 1 | 17 | 20 | 32 | 35 | 51 | 50 | 51 | 52 |  | 52 | 52 | 52 | 60 | 70 | 70 | 70 | 730080
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 4 | 12 | 31 | 44 | 14 | 10 | 5 | 14 | 13 | 29 | 22 | 3 | [7 empty] | 0 | 236880
131 | Rampal 1320 MW (BIFPCL) | 621 | 621 | 620 | 618 | 624 | 623 | 560 | 555 | 557 | 560 | 586 | 588 | 620 | 623 | 620 | 561 | 510 | 511 |  | 618 | 621 | 623 | 622 | 622 | 622 | 621 | 14421820
132 | United Payra Power Ltd. | [19 empty] | 29 | 54 | 54 | 54 | 72 | 120 | 150 | 421200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 180 |  | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 5393320
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [9 empty] | 16 | 32 | 48 | 48 | 64 | 80 | 80 | 64 | 80 |  | 80 | 96 | 96 | 110 | 110 | 110 | 110 | 1095936
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 307 | 307 | 307 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 253 | 280 | 307 | 307 | 307 | 227 | 200 | 200 |  | 262 | 307 | 307 | 307 | 307 | 307 | 250 | 6545500
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 862
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 138 | 138 | 138 | 138 | 138 | 80 | 80 | 80 | 136 | 136 | 136 | 136 | 136 | 80 | 136 | 140 | 140 | 80 |  | 136 | 136 | 136 | 136 | 136 | 80 | 80 | 2851000
140 | Bhola 33 MW PP (Venture) | 10 | 10 | 10 | 10 | 10 | 8 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 5 | 6 | 6 |  | 9 | 10 | 10 | 10 | 9 | 9 | 10 | 185049
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 875 | 876 | 875 | 876 | 878 | 877 | 877 | 878 | 877 | 877 | 878 | 877 | 879 | 878 | 878 | 897 | 897 | 897 |  | 898 | 899 | 898 | 781 | 780 | 899 | 899 | 23291636
147 | Bheramara 410 MW CCPP | 386 | 382 | 383 | 376 | 376 | 375 | 375 | 320 | 358 | 370 | 361 | 358 | 351 | 335 | 332 | 323 | 318 | 317 |  | 312 | 311 | 312 | 308 | 304 | 308 | 307 | 8480736
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1100 | 1000 | 920 | 960 | 980 | 1000 | 1030 | 1050 | 1090 | 1120 | 1060 | 1060 | 1000 |  | 1030 | 1220 | 1240 | 1244 | 1244 | 1244 | 1244 | 28915500
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 62 | 63 | 62 | 60 | 61 | 61 | 61 | 61 | 61 | 62 | 62 |  | 63 | 62 | 63 | 63 | 63 | 63 | 63 | 1445236
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 40 | 37 | 40 | 37 | 31 | 31 | 31 | 204137
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 2 | 2 | 5 | 4 | 5 | 5 | 1 | 1 | 1 | 0 | [8 empty] | 34320
| Sirajganj 68 MW Solar Park | [5 empty] | 2 | 12 | 17 | 25 | 16 | 49 | 68 | 65 | 65 | 20 | 18 | 18 | 1 | [8 empty] | 365250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 177 | 180 | 190 | 189 | 197 | 177 | 182 | 182 | 212 | 212 | 211 | 212 | 212 | 209 | 209 | 214 | 212 | 212 |  | 210 | 209 | 208 | 209 | 208 | 206 | 206 | 4855091
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 391 | 414 | 400 | 414 | 414 | 350 | 350 | 320 | 348 | 329 | 347 | 311 | 317 | 396 | 414 | 312 | 348 | 358 |  | 414 | 326 | 312 | 332 | 313 | 346 | 347 | 8639636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 5 | 2 | 5 | 5 | 5 | 5 |  | 5 | 8 | 8 | 8 | 8 | 8 | 5 | 128088
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 14 | 14 | 32 | 46 | 40 | 40 | 40 | 169745
168 | Santahar 50 MW Peaking PP | 21 | [18 empty] | 32 | 33 | 32 | 32 | 32 | 32 | 21 | 193811
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 83 | 89 | 89 | 88 | 88 | 88 | 57 | 448848
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 5 | 35 | 60 | 70 | 70 | 70 | 70 | 375840
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 35 | 50 | 70 | 70 | 70 | 70 | 70 | 375552
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 92 | 92 | 92 | 49 | 49 | 34 |  |  |  | 46 | 48 | 48 | 48 | 46 | 49 | 49 | 49 | 49 |  | 85 | 92 | 92 | 99 | 99 | 99 | 99 | 1443705
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 2 | 1 | 0 | [8 empty] | 12264
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 72 | 52 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 35 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1510656
| Intraco Solar 30 MW | [5 empty] | 1 | 5 | 8 | 21 | 11 | 37 | 13 | 30 | 15 | 16 | 11 | 6 | 3 | [8 empty] | 157666
| Adani Power Jharkhanda Ltd | 1415 | 1376 | 1371 | 1360 | 1367 | 1260 | 1260 | 1267 | 1335 | 1363 | 1359 | 1352 | 1366 | 1372 | 1369 | 1410 | 1418 | 1323 |  | 1457 | 1496 | 1513 | 1517 | 1502 | 1508 | 1513 | 34063000
178 | Teesta Solar Limited | [5 empty] | 7 | 23 | 77 | 85 | 135 | 65 | 189 | 60 | 135 | 25 | 117 | 27 | 6 | [8 empty] | 998000