## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-03-12 | Tuesday
|  | Date (day): | 2019-03-12 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11581 | MW |  |  | (b) At Evening Peak Hour : |  | 13040 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-03-11 | 2019-03-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 188 | 94 | 188 |  | 170 | Under Maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 120 | 120 | 120
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 380 | 380 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 75 | 50 | 40 | 78 | 0
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 108 | 110 | 108 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 40 | 40 | 40
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 379 | 388 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under Maint.
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 370 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 10 | 100 | 0 | 150 |  | 155 | Machine problem.
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 110 | 110 | 110 | 110
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 67 | 120 | 200 | 200 | 10 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint.
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 70 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 48 | 48 | 48 | 48
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 61 | 54 | 50 | 50 |  | 58 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 50 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 31 | 29 | 29
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 65 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 80 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 2153 | 2707 | 3989 | 4571 | 115 | 1032
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 125 | 130 | 130 | 50 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20.14 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 70 | 71 | 71 |  | 159 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 210 | 201 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 41 | 51 | 51
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 75
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 0 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 77 | 77 | 77 |  | 23 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 92 | 100 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 16 | 9 | 16
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 98 | 98 | 98
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 597.14 | 859 | 876 | 1006 | 230 | 372
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 209 | 182 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 360 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 330 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 31 | 37 | 40 | 40
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 100 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 95 | 100 | 100 |  | 63 | ST under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 52 | 200 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 116 | 144 | 103 | 126
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 22 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1518 | 1749 | 1987 | 2160 | 523 | 79
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 146 | 147 | 158 | 158
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 80 | 87 | 87 | 87 |  | 8 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.5 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 32 | 200 | 100 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 281.5 | 456 | 484 | 582 | 0 | 8
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 49 | 70 | 70 | 70 |  | 20
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 114 | 114 | 114 | 114 |  | 216 | GT-2 Under maint.
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 58 | 66 | 66
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 44 | 50 | 50
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 48 | 42 | 0 | 0 |  | 142 | Under maint.
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 20 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 40 | 44 | 44 | 44 |  | 6 | Engine problem
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 17 | 17 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 341 | 341
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 39 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1165 | 1044 | 1155 | 1155 | 0 | 384
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 714 | 860 | 717 | 866
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 44
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 82 | 0 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 422 | 410 | 410
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 20 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1139 | 1688 | 1487 | 1806 | 0 | 0
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 100 | 100 |  | 10 | Engine problem
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 15 | 26 | 26 |  | 7 | Engine problem
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 171 | 174 | 174
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 50 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 237 | 329 | 395 | 425 | 0 | 17
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 65 | 65
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 24 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 201 | 182 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 226 | 178 | 200 | 200 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 203 | 184 | 220 | 220
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Under S/D
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 29
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 17 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 104 | 104 | 104 | 0 | 102 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
| Confidence CPBL-2 |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1835 | 1825 | 819 | 952 | 1027 | 1151 | 382 | 0
126 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
127 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 149 | 149 | 125 |  | Coal shortage
128 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
129 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 18 | 15 | 15 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 167 | 181 | 181 | 184 | 125 | 170
| Total |  |  |  |  | 18079 | 17536 | 8076.64 | 9965 | 11581 | 13040 | 1375 | 2062
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7532.794 | 9294 | 10801.1855 | 12161.9428
A. |  | 2019-03-11 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 9965 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 6023 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9965 | MW
3 | Day peak Generation : |  |  | 8076.64 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9294 | MW
4 | Evening peak Generation : |  |  | 9965 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 190.5793 | MKWHr | By Solar | 0.15373 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 140.7124 | MKWHr |  | By Oil: | 24.6172 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6593 | MKWHr |  | By Hydro: | 1.603 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1375 | MW | Dhaka | 3447 | 3447 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2062 | MW | Chittagong | 994 | 994 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3437 | MW | Khulna | 1133 | 1133 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1222.96 | MMCFD |  |  | Rajshahi | 1021 | 1021 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 101117708.962 | ii) Oil : | Taka | 185102312.13 | Comilla | 805 | 805 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14124898 | Total | Taka | 300344919.092 | Mymensingh | 717 | 717 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.105 | MKWHr. | Sylhet | 343 | 343 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -270 | MW (E to W) at | 19:30 | hrs | Barisal | 201 | 201 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -320 | MW at | 8:00 | hrs | Rangpur | 633 | 633 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30° C |  |  | Total | 9294 | 9294 |  | 0
B. |  | 2019-03-12 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13040 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 3040 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 191.2486 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6501 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1927 | MKWHr. | ii) HVDC Flow at Peak Time |  | 860 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.641 | MKWHr. | iii) Maximum HVDC Flow : |  | 860 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.71 |  | (b) Today: | 90.37 |  | (c) Rule Curve: |  | 91.24
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-03-11
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 190 | 300 | 111 | 40 | 349 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 75 | 110 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 42 | 30 | 135 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 20 | 35 | 70 | 80 | 0 | 320 | 320 | 185 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 94 | 154 | 7 | 22 | 0 | 58 | 50 | 50 | 50 | 130 | 110 | 40 | 5 | 48 | 80 | 0 | 47 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 |  | 567 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 5 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 179 | 0 | 50 | 0 | 184 | 0 | 0 | 0 | 0 | 0 |  | 4814 | 1909 | 6723 | 4429 | 567 | 1264 | 148 | 149 | 72 | 0 | 94 | 0 | 0 | 90.8
2:00 | 35 | 0 | 0 | 190 | 300 | 52 | 40 | 351 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 75 | 110 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 42 | 30 | 135 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 35 | 70 | 80 | 0 | 300 | 300 | 184 | 8 | 80 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 94 | 148 | 0 | 0 | 0 | 58 | 50 | 5 | 5 | 130 | 109 | 40 | 5 | 48 | 80 | 0 | 47 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 567 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 16 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 180 | 0 | 180 | 0 | 10 | 0 | 164 | 0 | 0 | 0 | 0 | 0 |  | 4489 | 1826 | 6315 | 4290 | 567 | 1057 | 86 | 149 | 72 | 0 | 94 | 0 | 0 | 90.79
3:00 | 35 | 0 | 0 | 190 | 300 | 12 | 40 | 361 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 110 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 40 | 30 | 135 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 35 | 70 | 80 | 0 | 300 | 300 | 204 | 8 | 80 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 92 | 156 | 0 | 0 | 0 | 58 | 50 | 5 | 5 | 130 | 110 | 40 | 5 | 48 | 80 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 567 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 186 | 0 | 162 | 0 | 10 | 0 | 163 | 0 | 0 | 0 | 0 | 0 |  | 4355 | 1811 | 6166 | 4214 | 567 | 988 | 86 | 149 | 70 | 0 | 92 | 0 | 0 | 90.77
4:00 | 35 | 0 | 0 | 190 | 300 | 12 | 40 | 362 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 110 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 40 | 30 | 135 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 36 | 70 | 80 | 0 | 300 | 300 | 184 | 8 | 90 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 90 | 142 | 0 | 0 | 0 | 58 | 50 | 5 | 5 | 130 | 109 | 40 | 5 | 48 | 80 | 0 | 6 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 567 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 191 | 0 | 157 | 0 | 10 | 0 | 163 | 0 | 0 | 0 | 0 | 0 |  | 4334 | 1811 | 6145 | 4198 | 567 | 985 | 86 | 149 | 70 | 0 | 90 | 0 | 0 | 90.75
5:00 | 35 | 0 | 0 | 190 | 300 | 12 | 40 | 350 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 110 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 40 | 30 | 135 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 36 | 70 | 80 | 0 | 280 | 280 | 184 | 8 | 90 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 90 | 160 | 0 | 0 | 0 | 58 | 50 | 5 | 5 | 130 | 109 | 40 | 5 | 48 | 80 | 0 | 6 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 567 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 156 | 0 | 148 | 0 | 10 | 0 | 154 | 0 | 0 | 0 | 0 | 0 |  | 4285 | 1738 | 6023 | 4086 | 567 | 975 | 86 | 149 | 70 | 0 | 90 | 0 | 0 | 90.73
6:00 | 35 | 0 | 0 | 190 | 300 | 12 | 40 | 363 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 110 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 40 | 30 | 135 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 36 | 70 | 80 | 0 | 280 | 280 | 190 | 8 | 80 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 86 | 150 | 0 | 0 | 0 | 60 | 50 | 20 | 17 | 130 | 107 | 53 | 50 | 48 | 80 | 0 | 24 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 713 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 14 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 22 | 6 | 5 | 0 | 0 | 149 | 0 | 0 | 169 | 0 | 157 | 0 | 10 | 0 | 163 | 0 | 0 | 0 | 0 | 0 |  | 4418 | 1930 | 6348 | 4123 | 713 | 1092 | 115 | 149 | 70 | 0 | 86 | 0 | 0 | 90.71
7:00 | 35 | 0 | 0 | 190 | 300 | 12 | 40 | 365 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 110 | 125 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 35 | 0 | 35 | 0 | 25 | 31 | 25 | 31 | 0 | 0 | 40 | 30 | 140 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 22 | 34 | 70 | 80 | 0 | 320 | 280 | 202 | 8 | 90 | 37 | 5 | 5 | 28 | 0 | 0 | 0 | 0 | 8 | 30 | 21 | 84 | 157 | 7 | 22 | 0.1 | 60 | 50 | 48 | 44 | 130 | 108 | 68 | 86 | 48 | 80 | 0 | 40 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 10 | 0 | 0 | 0 | 0 |  | 712 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 13 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 50 | 0 | 0 | 52 | 0 | 22 | 15 | 11 | 0 | 0 | 149 | 0 | 0 | 169 | 0 | 157 | 0 | 10 | 0 | 163 | 0 | 0 | 0 | 0 | 0 |  | 4752.8 | 2061 | 6813.8 | 4327 | 712 | 1238 | 231 | 149 | 70 | 0 | 84 | 2.8 | 0 | 90.7
8:00 | 35 | 0 | 0 | 190 | 380 | 12 | 60 | 361 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 110 | 155 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 35 | 0 | 35 | 0 | 25 | 0 | 25 | 31 | 0 | 0 | 41 | 30 | 140 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 12 | 70 | 80 | 0 | 360 | 360 | 188 | 8 | 90 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 0 | 8 | 33 | 21 | 86 | 150 | 67 | 22 | 0.3 | 60 | 50 | 48 | 50 | 130 | 108 | 66 | 86 | 48 | 80 | 0 | 20 | 10 | 305 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.25 | 30 | 0 | 0 | 0 | 0 |  | 714 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 16 | 11 | 0 | 0 | 149 | 0 | 0 | 156 | 0 | 182 | 0 | 11 | 0 | 162 | 0 | 0 | 0 | 0 | 0 |  | 5016.55 | 2086 | 7102.55 | 4498 | 714 | 1234 | 342 | 149 | 71 | 0 | 86 | 8.55 | 0 | 90.7
9:00 | 35 | 0 | 0 | 190 | 380 | 108 | 60 | 370 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 110 | 160 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 16 | 0 | 31 | 9 | 0 | 41 | 30 | 135 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 2 | 70 | 80 | 0 | 360 | 360 | 203 | 8 | 80 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 8 | 8 | 33 | 21 | 92 | 153 | 74 | 22 | 1.1 | 60 | 50 | 48 | 50 | 130 | 115 | 63 | 83 | 48 | 68 | 19 | 44 | 10 | 300 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.95 | 30 | 17 | 0 | 0 | 0 |  | 714 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 10 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 168 | 0 | 231 | 0 | 11 | 0 | 165 | 0 | 0 | 0 | 0 | 0 |  | 5283.05 | 2106 | 7389.05 | 4598 | 714 | 1375 | 375 | 149 | 71 | 0 | 92 | 15.05 | 0 | 0
10:00 | 35 | 0 | 0 | 190 | 380 | 108 | 77 | 380 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 115 | 97 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 26 | 25 | 31 | 25 | 0 | 41 | 30 | 135 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 2 | 100 | 80 | 0 | 360 | 360 | 221 | 8 | 90 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 96 | 137 | 80 | 22 | 1.1 | 60 | 49 | 45 | 50 | 163 | 108 | 66 | 83 | 48 | 49 | 19 | 38 | 10 | 295 | 17 | 8 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 17.91 | 52 | 23 | 3 | 0 | 0 |  | 713 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 171 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 18 | 171 | 0 | 231 | 0 | 45 | 0 | 167 | 0 | 0 | 0 | 0 | 16 |  | 5528.01 | 2138 | 7666.01 | 4570 | 713 | 1513 | 517 | 149 | 71 | 18 | 96 | 19.01 | 0 | 0
11:00 | 35 | 0 | 0 | 190 | 380 | 108 | 77 | 353 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 2 | 0 | 110 | 67 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 12 | 35 | 0 | 35 | 22 | 25 | 26 | 25 | 32 | 25 | 0 | 42 | 0 | 135 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 20 | 2 | 80 | 80 | 0 | 320 | 330 | 212 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 8 | 33 | 21 | 108 | 151 | 80 | 22 | 0.9 | 60 | 49 | 45 | 50 | 130 | 114 | 64 | 83 | 0 | 49 | 19 | 39 | 10 | 270 | 17 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 19.9 | 60 | 52 | 45 | 40 | 0 |  | 714 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 12 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 35 | 0 | 22 | 14 | 0 | 0 | 0 | 149 | 0 | 18 | 185 | 0 | 230 | 0 | 51 | 0 | 186 | 0 | 0 | 0 | 0 | 4 |  | 5433.8 | 2174 | 7607.8 | 4521 | 714 | 1416 | 619 | 149 | 42 | 18 | 108 | 20.8 | 0 | 0
12:00 | 35 | 0 | 0 | 190 | 380 | 108 | 75 | 379 | 0 | 0 | 0 | 450 | 10 | 0 | 0 | 15 | 0 | 110 | 67 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 48 | 35 | 0 | 35 | 22 | 25 | 26 | 25 | 32 | 25 | 0 | 42 | 30 | 130 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 21 | 2 | 80 | 80 | 0 | 330 | 330 | 209 | 8 | 100 | 31 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 146 | 80 | 22 | 1.5 | 60 | 49 | 50 | 50 | 163 | 114 | 64 | 85 | 45 | 48 | 19 | 40 | 10 | 310 | 17 | 2 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 20.14 | 92 | 52 | 50 | 39 | 0 |  | 714 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 14 | 0 | 0 | 0 | 149 | 0 | 18 | 201 | 0 | 226 | 0 | 50 | 0 | 203 | 0 | 0 | 35 | 0 | 0 |  | 5714.64 | 2362 | 8076.64 | 4693 | 714 | 1540 | 753 | 149 | 72 | 18 | 116 | 21.64 | 0 | 91.02
13:00 | 35 | 0 | 0 | 190 | 380 | 108 | 74 | 375 | 0 | 0 | 0 | 450 | 10 | 0 | 0 | 27 | 0 | 110 | 125 | 0 | 0 | 4 | 0 | 0 | 60 | 0 | 48 | 35 | 0 | 35 | 22 | 25 | 22 | 25 | 31 | 25 | 0 | 43 | 30 | 130 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 21 | 5 | 80 | 80 | 0 | 330 | 330 | 186 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 118 | 139 | 80 | 22 | 2.1 | 60 | 70 | 50 | 50 | 163 | 113 | 57 | 85 | 45 | 47 | 19 | 41 | 10 | 280 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 14.31 | 100 | 52 | 50 | 32 | 0 |  | 714 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 162 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 15 | 0 | 0 | 0 | 149 | 0 | 17 | 204 | 0 | 225 | 0 | 71 | 0 | 207 | 0 | 0 | 53 | 0 | 0 |  | 5734.41 | 2455 | 8189.41 | 4772 | 714 | 1536 | 794 | 149 | 73 | 17 | 118 | 16.41 | 0 | 91.01
14:00 | 35 | 0 | 0 | 190 | 380 | 111 | 74 | 348 | 0 | 0 | 0 | 420 | 65 | 0 | 0 | 55 | 0 | 110 | 60 | 0 | 0 | 7 | 0 | 0 | 58 | 0 | 48 | 35 | 36 | 35 | 22 | 25 | 26 | 25 | 31 | 25 | 0 | 43 | 30 | 130 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 21 | 2 | 80 | 80 | 0 | 330 | 330 | 184 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 137 | 87 | 22 | 1.9 | 60 | 70 | 50 | 50 | 100 | 115 | 60 | 85 | 46 | 47 | 19 | 41 | 10 | 240 | 16 | 3 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 18.6 | 100 | 52 | 50 | 34 | 0 |  | 713 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 173 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 17 | 0 | 0 | 0 | 149 | 0 | 18 | 164 | 0 | 226 | 0 | 71 | 0 | 157 | 0 | 0 | 53 | 0 | 0 |  | 5646.5 | 2245 | 7891.5 | 4470 | 713 | 1406 | 922 | 149 | 73 | 18 | 120 | 20.5 | 0 | 91.01
15:00 | 35 | 0 | 0 | 190 | 382 | 107 | 73 | 290 | 0 | 0 | 0 | 420 | 75 | 0 | 0 | 55 | 0 | 110 | 99 | 0 | 0 | 7 | 0 | 0 | 59 | 0 | 48 | 35 | 36 | 35 | 22 | 25 | 29 | 25 | 31 | 33 | 0 | 42 | 30 | 130 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 80 | 0 | 360 | 330 | 183 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 137 | 87 | 22 | 1.5 | 58 | 70 | 47 | 50 | 140 | 113 | 56 | 85 | 46 | 48 | 19 | 41 | 10 | 300 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 14.5 | 100 | 52 | 50 | 35 | 0 |  | 714 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 173 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 21 | 17 | 0 | 0 | 0 | 149 | 0 | 12 | 188 | 0 | 214 | 0 | 92 | 0 | 165 | 0 | 0 | 53 | 0 | 0 |  | 5772 | 2365 | 8137 | 4586 | 714 | 1518 | 941 | 149 | 72 | 17 | 124 | 16 | 0 | 91
16:00 | 35 | 44 | 0 | 190 | 320 | 106 | 73 | 348 | 0 | 0 | 0 | 390 | 100 | 0 | 0 | 55 | 0 | 110 | 57 | 0 | 0 | 7 | 0 | 0 | 58 | 0 | 48 | 35 | 36 | 35 | 22 | 25 | 29 | 25 | 31 | 51 | 0 | 40 | 30 | 130 | 0 | 1 | 205 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 80 | 80 | 0 | 360 | 330 | 182 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 5 | 33 | 15 | 112 | 137 | 87 | 22 | 0.9 | 58 | 70 | 45 | 50 | 100 | 115 | 41 | 83 | 46 | 48 | 19 | 40 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 12 | 9 | 100 | 53 | 50 | 15 | 0 |  | 713 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 40 | 161 | 13 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 21 | 14 | 0 | 0 | 0 | 149 | 0 | 12 | 185 | 0 | 179 | 0 | 96 | 0 | 152 | 0 | 0 | 53 | 0 | 0 |  | 5653.9 | 2270 | 7923.9 | 4438 | 713 | 1412 | 997 | 149 | 70 | 23 | 112 | 9.9 | 0 | 91
17:00 | 35 | 44 | 0 | 140 | 280 | 109 | 40 | 350 | 0 | 0 | 0 | 360 | 100 | 0 | 0 | 55 | 0 | 110 | 76 | 0 | 0 | 7 | 0 | 0 | 59 | 0 | 48 | 35 | 36 | 35 | 22 | 25 | 30 | 0 | 31 | 51 | 0 | 40 | 30 | 130 | 0 | 8 | 202 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 5 | 20 | 5 | 80 | 80 | 0 | 320 | 330 | 183 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 139 | 87 | 22 | 0.3 | 58 | 68 | 47 | 50 | 100 | 118 | 45 | 40 | 46 | 48 | 19 | 40 | 10 | 280 | 17 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 15 | 3.2 | 100 | 53 | 50 | 34 | 0 |  | 713 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 174 | 1 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 50 | 0 | 0 | 24 | 0 | 21 | 17 | 0 | 0 | 0 | 149 | 0 | 12 | 186 | 0 | 156 | 0 | 96 | 0 | 152 | 0 | 0 | 53 | 0 | 0 |  | 5482.5 | 2181 | 7663.5 | 4311 | 713 | 1315 | 962 | 149 | 70 | 26 | 114 | 3.5 | 0 | 90.99
18:00 | 35 | 62 | 0 | 120 | 280 | 110 | 40 | 353 | 0 | 0 | 40 | 360 | 100 | 0 | 0 | 55 | 0 | 110 | 80 | 0 | 0 | 10 | 0 | 0 | 58 | 0 | 48 | 35 | 36 | 35 | 22 | 25 | 30 | 25 | 32 | 51 | 0 | 40 | 30 | 130 | 0 | 8 | 206 | 0 | 0 | 0 | 0 | 41 | 0 | 6 | 10 | 10 | 6 | 20 | 9 | 80 | 80 | 0 | 320 | 330 | 199 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 145 | 87 | 22 | 0 | 60 | 70 | 50 | 50 | 100 | 113 | 65 | 40 | 46 | 48 | 19 | 42 | 10 | 290 | 16 | 8 | 0 | 2 | 0 | 0 | 32 | 0 | 15 | 0 | 100 | 53 | 50 | 35 | 0 |  | 770 | 0 | 300 | 0 | 13 | 0 | 0 | 0 | 21 | 31 | 8 | 174 | 4 | 0 | 0 | 0 | 55 | 16 | 0 | 0 | 50 | 0 | 0 | 24 | 27 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 15 | 185 | 0 | 149 | 0 | 52 | 0 | 155 | 0 | 0 | 53 | 0 | 0 |  | 5648 | 2301 | 7949 | 4433 | 770 | 1295 | 990 | 149 | 70 | 116 | 126 | 0 | 0 | 90.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 189 | 0 | 120 | 380 | 110 | 60 | 388 | 0 | 0 | 40 | 400 | 100 | 0 | 0 | 55 | 0 | 110 | 160 | 0 | 0 | 58 | 0 | 0 | 54 | 0 | 47 | 35 | 55 | 55 | 22 | 25 | 25 | 25 | 31 | 51 | 0 | 40 | 30 | 125 | 0 | 21 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 34 | 75 | 93 | 36 | 22 | 16 | 80 | 80 | 0 | 360 | 330 | 183 | 8 | 95 | 37 | 5 | 5 | 35 | 0 | 8 | 0 | 22 | 11 | 33 | 22 | 148 | 143 | 87 | 22 | 0 | 58 | 70 | 50 | 50 | 130 | 113 | 66 | 85 | 46 | 48 | 19 | 44 | 10 | 310 | 17 | 11 | 0 | 27 | 0 | 0 | 146 | 0 | 51 | 0 | 100 | 123 | 77 | 35 | 0 |  | 860 | 0 | 380 | 0 | 102 | 0 | 0 | 0 | 44 | 63 | 40 | 173 | 15 | 48 | 0 | 0 | 60 | 17 | 0 | 70 | 50 | 24 | 0 | 40 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 15 | 203 | 0 | 190 | 0 | 89 | 20 | 196 | 0 | 0 | 105 | 0 | 0 |  | 6764 | 3049 | 9813 | 4966 | 860 | 1507 | 1816 | 149 | 70 | 297 | 148 | 0 | 0 | 90.98
19:30 | 35 | 188 | 0 | 120 | 380 | 110 | 50 | 388 | 0 | 0 | 40 | 370 | 100 | 0 | 0 | 55 | 0 | 110 | 120 | 0 | 0 | 70 | 0 | 0 | 54 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 25 | 25 | 31 | 51 | 0 | 40 | 30 | 125 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 34 | 77 | 98 | 50 | 22 | 16 | 80 | 80 | 0 | 360 | 330 | 182 | 8 | 95 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 144 | 147 | 87 | 22 | 0 | 60 | 70 | 50 | 50 | 100 | 114 | 58 | 85 | 44 | 42 | 19 | 44 | 10 | 270 | 17 | 11 | 0 | 65 | 0 | 0 | 200 | 0 | 80 | 0 | 100 | 200 | 100 | 0 | 0 |  | 860 | 0 | 422 | 0 | 115 | 0 | 0 | 0 | 44 | 82 | 40 | 171 | 15 | 48 | 0 | 0 | 60 | 24 | 0 | 102 | 50 | 50 | 0 | 43 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 15 | 182 | 0 | 178 | 0 | 95 | 20 | 184 | 0 | 0 | 105 | 0 | 0 |  | 6815 | 3150 | 9965 | 4877 | 860 | 1401 | 2117 | 149 | 70 | 347 | 144 | 0 | 0 | 0
20:00 | 35 | 188 | 0 | 120 | 320 | 52 | 50 | 350 | 0 | 0 | 40 | 370 | 100 | 0 | 0 | 55 | 0 | 110 | 120 | 0 | 0 | 48 | 0 | 0 | 54 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 30 | 25 | 32 | 51 | 0 | 42 | 30 | 130 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 34 | 84 | 101 | 50 | 22 | 23 | 80 | 80 | 0 | 325 | 330 | 182 | 8 | 95 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 34 | 22 | 144 | 145 | 87 | 22 | 0 | 60 | 70 | 50 | 50 | 100 | 113 | 56 | 85 | 46 | 43 | 19 | 45 | 10 | 270 | 16 | 11 | 0 | 65 | 0 | 0 | 150 | 0 | 80 | 0 | 100 | 185 | 80 | 0 | 0 |  | 860 | 0 | 421 | 0 | 115 | 0 | 0 | 0 | 39 | 69 | 40 | 171 | 9 | 48 | 0 | 0 | 60 | 30 | 0 | 102 | 50 | 50 | 0 | 43 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 15 | 181 | 0 | 178 | 0 | 96 | 20 | 184 | 0 | 0 | 105 | 0 | 0 |  | 6546 | 3131 | 9677 | 4749 | 860 | 1348 | 2020 | 149 | 72 | 335 | 144 | 0 | 0 | 90.98
21:00 | 35 | 188 | 0 | 120 | 320 | 52 | 50 | 350 | 0 | 0 | 40 | 330 | 100 | 0 | 0 | 55 | 0 | 110 | 100 | 0 | 0 | 48 | 0 | 0 | 53 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 4 | 25 | 31 | 51 | 0 | 42 | 30 | 130 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 34 | 84 | 71 | 50 | 20 | 28 | 80 | 80 | 0 | 320 | 330 | 182 | 8 | 95 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 140 | 145 | 87 | 22 | 0 | 58 | 70 | 50 | 50 | 100 | 115 | 66 | 85 | 46 | 43 | 20 | 45 | 10 | 280 | 17 | 11 | 0 | 62 | 0 | 0 | 150 | 0 | 80 | 0 | 100 | 145 | 70 | 0 | 0 |  | 860 | 0 | 421 | 0 | 73 | 0 | 0 | 0 | 41 | 40 | 40 | 168 | 18 | 48 | 0 | 0 | 60 | 43 | 0 | 102 | 50 | 25 | 0 | 43 | 29 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 18 | 182 | 0 | 178 | 0 | 96 | 0 | 184 | 0 | 0 | 105 | 0 | 0 |  | 6390 | 3039 | 9429 | 4704 | 860 | 1331 | 1849 | 149 | 72 | 324 | 140 | 0 | 0 | 90.97
22:00 | 35 | 188 | 0 | 120 | 320 | 52 | 50 | 349 | 0 | 0 | 40 | 330 | 100 | 0 | 0 | 55 | 0 | 110 | 105 | 0 | 0 | 32 | 0 | 0 | 54 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 30 | 25 | 31 | 51 | 0 | 42 | 30 | 130 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 50 | 7 | 50 | 19 | 35 | 80 | 80 | 0 | 320 | 330 | 182 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 134 | 145 | 87 | 22 | 0 | 60 | 70 | 50 | 50 | 100 | 114 | 64 | 85 | 48 | 42 | 20 | 45 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 58 | 0 | 100 | 72 | 43 | 0 | 0 |  | 860 | 0 | 421 | 0 | 32 | 0 | 0 | 0 | 41 | 20 | 40 | 173 | 17 | 32 | 0 | 0 | 60 | 43 | 0 | 60 | 50 | 0 | 0 | 47 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 178 | 0 | 95 | 0 | 184 | 0 | 0 | 105 | 0 | 0 |  | 6043 | 2868 | 8911 | 4740 | 860 | 1339 | 1424 | 149 | 72 | 193 | 134 | 0 | 0 | 90.97
23:00 | 35 | 0 | 0 | 120 | 320 | 52 | 50 | 364 | 0 | 0 | 40 | 330 | 100 | 0 | 0 | 55 | 0 | 110 | 105 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 18 | 35 | 18 | 55 | 22 | 25 | 30 | 25 | 18 | 51 | 0 | 42 | 30 | 130 | 0 | 25 | 214 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 50 | 0 | 50 | 20 | 35 | 80 | 80 | 0 | 320 | 330 | 205 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 126 | 154 | 87 | 22 | 0 | 59 | 70 | 50 | 50 | 100 | 114 | 67 | 85 | 48 | 0 | 20 | 46 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 33 | 0 | 100 | 72 | 0 | 0 | 0 |  | 761 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 40 | 174 | 16 | 32 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 192 | 0 | 188 | 0 | 96 | 0 | 194 | 0 | 0 | 105 | 0 | 0 |  | 5702 | 2523 | 8225 | 4588 | 761 | 1360 | 1164 | 149 | 72 | 5 | 126 | 0 | 0 | 90.96
24:00 | 35 | 0 | 0 | 120 | 320 | 52 | 50 | 368 | 0 | 0 | 40 | 330 | 100 | 0 | 0 | 55 | 0 | 110 | 105 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 18 | 35 | 18 | 0 | 22 | 25 | 31 | 25 | 31 | 51 | 0 | 42 | 30 | 130 | 0 | 25 | 203 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 50 | 22 | 35 | 80 | 80 | 0 | 320 | 330 | 184 | 8 | 100 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 150 | 87 | 22 | 0 | 58 | 70 | 50 | 50 | 100 | 113 | 67 | 85 | 48 | 0 | 20 | 46 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 72 | 0 | 0 | 0 |  | 761 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 14 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 197 | 0 | 192 | 0 | 95 | 0 | 199 | 0 | 0 | 17 | 0 | 0 |  | 5465 | 2433 | 7898 | 4582 | 761 | 1367 | 841 | 149 | 72 | 0 | 126 | 0 | 0 | 90.96
KWH | 844000 | 972000 | 0 | 4095000 | 8049818 | 1711409 | 1615040 | 8679420 | 0 | 0 | 543300 | 8733425 | 1109353 | 0 | 0 | 656212 | 148873 | 2601900 | 2741000 | 0 | 0 | 276048 | 0 | 0 | 827520 | 0 | 591648 | 777600 | 3876930 | 958421 | 333828 | 600000 | 619920 | 544500 | 787500 | 634440 | 0 | 927000 | 676000 | 3200000 | 0 | 163948 | 4861126 | 0 | 0 | 0 | 0 | 857760 | 0 | 109349 | 586920 | 306240 | 300960 | 484416 | 448320 | 1848682 | 1889945 | 0 | 8156000 | 7924000 | 4700000 | 217454 | 2135030 | 860544 | 128160 | 120000 | 666906 | 0 | 6880 | 0 | 327204 | 217620 | 594500 | 516360 | 2640960 | 3476000 | 1402560 | 409248 | 12250 | 1408000 | 1430400 | 953400 | 981000 | 3247077 | 2446000 | 1319232 | 1481280 | 1082880 | 1404750 | 308000 | 885700 | 166140 | 7463250 | 248352 | 143808 | 0 | 165600 | 0 | 0 | 1063200 | 0 | 367200 | 141480 | 1453440 | 1201440 | 752727 | 286000 | 0 |  | 17192727 | 0 | 8070336 | 0 | 336000 | 0 | 0 | 0 | 182880 | 269952 | 591375 | 4186824 | 305200 | 215040 | 0 | 0 | 135000 | 130004 | 0 | 346052 | 774530 | 104367 | 0 | 1820000 | 142370 | 449760 | 326116 | 143946 | 0 | 0 | 3659300 | 54000 | 201000 | 4631582 | 0 | 4711891 | 0 | 1309094 | 36480 | 4384909 | 0 | 0 | 932160 | 0 | 34560 |  | 134901803 | 55677455 | 190579258 | 108420764 | 17192727 | 32291611 | 23174679 | 3659300 | 1603000 | 1442487 | 2640960 | 153730 | 0
Fuel Cost | 725840 | 835920 | 0 | 3521700 | 5151883.52 | 1386241.29 | 1518137.6 | 5294446.2 | 0 | 0 | 744321 | 5851394.75 | 16851072.07 | 0 | 0 | 4009455.32 | 96767.45 | 2497824 | 3042510 | 0 | 0 | 1819156.32 | 0 | 0 | 4956844.8 | 0 | 3946292.16 | 5544288 | 24230812.5 | 6009299.67 | 250371 | 450000 | 0 | 0 | 0 | 6001802.4 | 0 | 0 | 0 | 3520000 | 0 | 1552587.56 | 3208343.16 | 0 | 0 | 0 | 0 | 7539710.4 | 0 | 1063965.77 | 3633034.8 | 1978310.4 | 1968278.4 | 411753.6 | 0 | 1682300.62 | 1719849.95 | 0 | 5056720 | 5467560 | 3290000 | 150043.26 | 2049628.8 | 576564.48 | 110217.6 | 110400 | 546862.92 | 0 | 74579.2 | 0 | 251947.08 | 163215 | 457765 | 387270 | 18064166.4 | 2607000 | 12889526.4 | 315120.96 | 0 | 1464320 | 1487616 | 915264 | 882900 | 2532720.06 | 1712200 | 1503924.48 | 1584969.6 | 1191168 | 1601415 | 394240 | 823701 | 154510.2 | 4776480 | 186264 | 109294.08 | 0 | 1202256 | 0 | 0 | 7601880 | 0 | 0 | 0 | 0 | 11221449.6 | 7030470.18 | 248820 | 0 |  | 87682907.7 | 0 | 5407125.12 | 0 | 2785440 | 0 | 0 | 0 | 2059228.8 | 3180034.56 | 4660035 | 2888908.56 | 302148 | 1591296 | 0 | 0 | 141750 | 1488545.8 | 0 | 3100625.92 | 6699684.5 | 928866.3 | 0 | 18054400 | 1675694.9 | 494736 | 306549.04 | 108967.122 | 0 | 0 | 14124898 | 1740420 | 5380770 | 3149475.76 | 0 | 3298323.7 | 0 | 0 | 632198.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 234208964.01 | 171883029.182 | 406091993.192 | 77479265.642 | 87682907.7 | 23638443.32 | 165338447.18 | 14124898 | 0 | 19763864.95 | 18064166.4 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 190 | 380 | 108 | 75 | 379 | 0 | 0 | 0 | 450 | 10 | 0 | 0 | 15 | 0 | 110 | 67 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 48 | 35 | 0 | 35 | 22 | 25 | 26 | 25 | 32 | 25 | 0 | 42 | 30 | 130 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 21 | 2 | 80 | 80 | 0 | 330 | 330 | 209 | 8 | 100 | 31 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 146 | 80 | 22 | 1.5 | 60 | 49 | 50 | 50 | 163 | 114 | 64 | 85 | 45 | 48 | 19 | 40 | 10 | 310 | 17 | 2 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 20.14 | 92 | 52 | 50 | 39 | 0 |  | 714 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 50 | 0 | 0 | 43 | 0 | 22 | 14 | 0 | 0 | 0 | 149 | 0 | 18 | 201 | 0 | 226 | 0 | 50 | 0 | 203 | 0 | 0 | 35 | 0 | 0 |  | 8076.64 | DayPeak
Yesterday Evening Peak | 35 | 188 | 0 | 120 | 380 | 110 | 50 | 388 | 0 | 0 | 40 | 370 | 100 | 0 | 0 | 55 | 0 | 110 | 120 | 0 | 0 | 70 | 0 | 0 | 54 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 25 | 25 | 31 | 51 | 0 | 40 | 30 | 125 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 34 | 77 | 98 | 50 | 22 | 16 | 80 | 80 | 0 | 360 | 330 | 182 | 8 | 95 | 37 | 5 | 5 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 144 | 147 | 87 | 22 | 0 | 60 | 70 | 50 | 50 | 100 | 114 | 58 | 85 | 44 | 42 | 19 | 44 | 10 | 270 | 17 | 11 | 0 | 65 | 0 | 0 | 200 | 0 | 80 | 0 | 100 | 200 | 100 | 0 | 0 |  | 860 | 0 | 422 | 0 | 115 | 0 | 0 | 0 | 44 | 82 | 40 | 171 | 15 | 48 | 0 | 0 | 60 | 24 | 0 | 102 | 50 | 50 | 0 | 43 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 15 | 182 | 0 | 178 | 0 | 95 | 20 | 184 | 0 | 0 | 105 | 0 | 0 |  | 9965 | EvPeak
Forecast for Evening | 35 | 188 | 0 | 120 | 360 | 108 | 78 | 412 | 0 | 110 | 40 | 450 | 150 | 100 | 100 | 55 | 0 | 110 | 200 | 100 | 100 | 102 | 149 | 100 | 50 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 29 | 51 | 0 | 41 | 30 | 130 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 51 | 75 | 68 | 77 | 98 | 50 | 20 | 16 | 80 | 80 | 0 | 360 | 360 | 221 | 8 | 100 | 40 | 5 | 5 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 126 | 158 | 87 | 22 | 0 | 60 | 70 | 51 | 44 | 163 | 114 | 66 | 86 | 50 | 0 | 20 | 44 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 |  | 866 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 44 | 80 | 40 | 174 | 26 | 100 | 30 | 0 | 65 | 50 | 45 | 100 | 50 | 50 | 40 | 52 | 29 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 18 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 0
Forecast for Day | 35 | 94 | 0 | 120 | 360 | 108 | 40 | 412 | 0 | 110 | 40 | 450 | 0 | 100 | 100 | 55 | 0 | 110 | 200 | 100 | 100 | 102 | 149 | 100 | 50 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 29 | 51 | 0 | 41 | 30 | 130 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 77 | 98 | 50 | 20 | 9 | 80 | 80 | 0 | 360 | 360 | 221 | 8 | 100 | 40 | 5 | 5 | 35 | 0 | 0 | 52 | 22 | 11 | 33 | 22 | 103 | 158 | 87 | 22 | 2 | 60 | 70 | 51 | 44 | 163 | 114 | 66 | 86 | 50 | 0 | 20 | 44 | 10 | 341 | 25 | 11 | 100 | 200 | 200 | 50 | 100 | 50 | 149 | 20 | 100 | 200 | 150 | 0 | 115 |  | 717 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 26 | 100 | 0 | 0 | 65 | 0 | 0 | 100 | 50 | 50 | 40 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 15 | 200 | 0 | 200 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 0
Generation at 08:00(Today) | 35 | 94 | 0 | 120 | 380 | 12 | 40 | 370 | 0 | 0 | 40 | 450 | 0 | 0 | 0 | 0 | 0 | 110 | 105 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 17 | 25 | 31 | 25 | 0 | 41 | 30 | 130 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 21 | 9 | 80 | 80 | 0 | 360 | 315 | 183 | 8 | 90 | 34 | 5 | 5 | 28 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 98 | 158 | 64 | 22 | 0.8 | 58 | 70 | 50 | 50 | 130 | 114 | 66 | 83 | 47 | 0 | 20 | 43 | 10 | 341 | 17 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 20 | 35 | 0 | 0 | 0 | 0 | 709 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 174 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 14 | 8 | 0 | 49 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 0 | 205 | 0 | 200 | 0 | 61 | 0 | 200 | 0 | 0 | 53 | 0 | 0 | 0
199
| Minimum Generation |  | 6023 | 5:00
| Highest Generation |  | 9965 | 19:30
| Day Peak Generation |  | 8076.64 | 12:00
| Evening Peak Generation |  | 9965 | 19:30
| HVDC Max Flow |  | 860 | 19:00
| HVDC EvPeak Flow |  | 860 | 19:30
| Load factor L.F |  | 79.69%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-03-12
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-03-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8076.64 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6501 | MW
Evening Peak Generation : |  | 9965 | MW Hour : | 19:30 | Available Max Generation : |  | 13040 | MW
E.P. Demand (at gen end) : |  | 9965 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 9965 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3040 | MW
Total Gen. (MKWH) : |  | 190.5793 | System Load Factor : | 79.69% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -320 | MW at | 8:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-03-12
Actual : | 90.37 | Ft.(MSL) , | Rule curve : | 91.24 | Ft.( MSL )
Gas Consumed : | Total = | 1222.96 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 101117708.962
|  | Coal : | 14124898 | Oil : | 185102312.13 | Total : | 300344919.092
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3480.9435 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1180.3277 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1056.9312 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 954.8123 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 862.9682 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 696.3762 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 393.7363 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 179.4135 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 537.0591 |  |  | 0 | 0%
Total | 0 |  | 9342.5678 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Shajibazar 330 MW GT-2
|  |  |  | 2) Khulna ST 110 MW |  | 11) Sylhet 150 MW
|  |  |  | 3) Ghorasal Unit-1,4 |  | 12) Siddhirganj 335 MW
4) Bhagabari 100 MW
5) Sikalbaha 150MW Peaking
6) Haripur 360 MW
7) Ashuganj #5
8) Siddhirganj 335 MW
9) Tongi GT
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Aminbazar 230 kV bus-1 was shut down at 10:00 for A/M.
b) Jamalpur-Mymensingh 1323 kV Ckt-2 was under shut down from 09:58 to 16:26 for A/M.
c) Kulaura 132/33 kV T1 transformer was under shut down from 10:23 to 14:13 for A/M.
d) Netrokona 132/33 kV T1 transformer was under shut down from 10:01 to 18:09 for C/M.
e) Bibiyana 400 kV bus-1 was under shut down from 10:16 to 21:51 for D/W.
f) Mongla-Bagerhat 132 kV Ckt was under shut down from 07:01 to 17:03 for C/M.
g) Mymensingh-Netrokona 132 kV Ckt-1 tripped at 10:06 showing Dist Z2, BC from Mymensingh end and
was switched on at 10:12.
h) Dohazari-Cox's bazar 132 kV Ckt-2 was under shut down from 15:01 to 17:34 for replace Energy meter
at Cox's bazar end.
i) Ghorasal Unit-3 was synchronized at 15:18 for test purpose and tripped at 22:30 again synchronized
at 01:37(12/03/2019).
j) Bagherhat-Mongla 132 kV Ckt tripped at 17:11 showing O/C relay due to fire at WZPDCO C/R and was
switched on at 17:32.
k) Madunaghat-TK Chemical 132 kV Ckt open at 20:48 at CK Chemical end due to sparking of CT terminal
at TK Chemical end.
l) Mymensingh 132/33 kV T3 transformer tripped at 18:32 due to 33 kV Fulbaria feeder fault and |  |  |  | About 49 MW power interruption occurred under Mymensingh S/S
was switched on at 18:40. |  |  |  | area from 10:43 to 20:14.
m) Mymensingh 132/33 kV T3 transformer was under shut down from 19:53 to 21:10 for Gas filling.
o) Sylhet 150 MW GT was shut down at 22:42 due to DP high.
n) Amnura 132/33 kV T3 transformer tripped at 22:58 due to 132 kV R-phase CT burst. At the same time |  |  |  | About 32 MW power interruption occurred under Amnura S/S
Amnura 50 MW P/S, Amnura -Chapainawabganj 132 kV Ckt & Amnura -Rajshahi 132 kV Ckt got tripped and |  |  |  | area from 22:58 to 01:05(12/03/2019).
both Ckts were switched on at 01:05(12/03/2019).
o) Haripur-Maniknagar 132 kV Ckt-2 was charged at 22:55 at Haripur end.
p) Bibiyana 400 KV dia-1, Bibiyana Unit-3 STG bay to cable was charged at 23:44.
q) Fenchuganj S/S-Sylhet 132 kV Ckt tripped at 04:25(12/03/2019) from both ends showing Gen trip, Dist Z1 |  |  |  | About 14 MW power interruption occurred under Biyanibazar S/S
at Fenchuganj end & Dist Z3 A-phase at Sylhet end and was switched on at 04:56. |  |  |  | area from 04:25 to 04:56(12/03/2019).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-03-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 844000 | #2 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 188 | 972000 | On test
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 4095000
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 380 | 8049818
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 50 | 1615040 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 110 | 1711409
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 40 | 543300
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 388 | 8679420 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 370 | 8733425 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 100 | 1109353 | On test
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 0 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 656212
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 333828
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 110 | 2601900
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 120 | 2741000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 148873 | Machine problem
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 70 | 276048 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 591648
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 35 | 777600 | Low demand
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 3876930
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 958421
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 54 | 827520 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1219920 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 544500 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 31 | 787500
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 634440
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 65 | 165600 | Low demand
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 80 | 367200 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2707 | 53861905
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 125 | 3200000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 163948
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 141480
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 300960
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1603000 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 201 | 4861126 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 41 | 857760 | Engine problem
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 34 | 109349 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 77 | 586920 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 100 | 1453440
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 484416
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 448320
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 306240 | Engine problem
| Chattogram area Total |  |  |  | 1681 | 859 | 14516959
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1848682 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1889945 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 182 | 4700000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 8156000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7924000
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 37 | 860544 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 128160 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 35 | 666906 | Engine problem
| Midland 150MW |  | IPP | 23*7.015 | 150 | 100 | 752727 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 6880 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2135030
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 200 | 1201440
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 327204
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 217620
** | Tripura |  | Imported power | 0 | 160 | 144 | 2640960
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 594500
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 516360
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1749 | 34904412
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 147 | 3476000 | GT-3 Under maint.
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 409248
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 87 | 1402560 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12250
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 200 | 1063200
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 456 | 6363258
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1408000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 70 | 1430400
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3247077 | Frequency control
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 114 | 2446000 | GT-2 Under maint.
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 953400
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 981000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 143808
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 58 | 1319232 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 85 | 1481280
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 44 | 1082880
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 42 | 1404750 | FGMO
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 308000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 44 | 885700
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 17 | 248352
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 270 | 7463250 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 286000 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 166140
| Sylhet Area Total |  |  |  | 1549 | 1044 | 25255269
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 860 | 17192727
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 336000
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 44 | 182880
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 82 | 269952
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 422 | 8070336
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 591375
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 20 | 36480 | Low demand
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 932160
| Khulna Area Total |  |  |  | 2209 | 1688 | 27611910
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 48 | 215040 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 15 | 305200 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 171 | 4186824
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 1309094
| Barisal Area Total |  |  |  | 462 | 329 | 6016158
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 135000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 24 | 130004 | Low demand
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 774530
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 104367
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 182 | 4631582 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4711891 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 184 | 4384909 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 29 | 142370
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 449760
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 17 | 326116
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 143946
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 1820000
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 346052
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 0 | 0 | 34560 | On test
| Rajshahi Area Total |  |  |  | 1825 | 952 | 18135087
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3659300
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 54000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 15 | 201000
| Rangpur Area Total |  |  |  | 484 | 181 | 3914300
| Total |  |  |  | 17536 | 9965 | 190579258
| Eastern Grid Total |  |  |  | 12556 | 6815 | 134901803
| Western Grid Total |  |  |  | 4980 | 3150 | 55677455
| National Grid Total |  |  |  | 17536 | 9965 | 190579258
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-03-11 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6306 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2988 | MW
i) Dhaka area |  |  | 3447 | MW | i) Khulna area |  |  | 1133 | MW
ii) Chittagong area |  |  | 994 | MW | ii) Rajshahi area |  |  | 1021 | MW
iii) Comilla area |  |  | 805 | MW | iii) Barisal area |  |  | 201 | MW
iv) Mymensingh area |  |  | 717 | MW | iv) Rangpur area |  |  | 633 | MW
v) Sylhet area |  |  | 343 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9294 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 104 | 1100 | Netrokona | 82 | 1900 | Central s/s | 78 | 1900
Munsiganj | 97 | 2100 | Jamalpur | 98 | 1830 | Noapara | 84 | 1930
Sonargaon | 58 | 2100 | Sherpur | 80 | 1830 | Jessore | 136 | 1930
Shyampur | 170 | 900 | Srimongal | 23 | 2100 | Jhenida | 88 | 1930
Bhulta | 170 | 1700 | Shahjibazar | 88 | 1900 | Bottail | 102 | 1900
Madanganj | 52 | 1400 | Fenchuganj | 33 | 1830 | G.K Project | 43 | 1900
Shitalakhya | 103 | 1600 | Kulawara | 28 | 1830 | Faridpur | 130 | 1930
Rahim steel | 20 | 1200 | Sylhet | 107 | 1830 | Madaripur | 107 | 2000
Matuail | 82 | 1000 | Chatak | 25 | 1830 | Gopalganj | 64 | 1900
Ghorasal | 67 | 1930 | Sunamganj | 24 | 1830 | Bagerhat | 64 | 1800
Narsingdi | 109 | 2100 | Biani Bazar | 30 | 1930 | Mongla | 32 | 700
Haripur (SBU) | 79 | 2100 | Comilla (S) | 148 | 1900 | Satkhira | 82 | 1930
Ullon | 68 | 1800 | Comilla(N) | 93 | 1900 | Gallamari | 41 | 1930
Hasnabad | 161 | 1830 | Chandpur | 84 | 2000 | Magura | 48 | 1930
Magbazar | 101 | 1400 | Feni | 105 | 1900 | Chuadanga | 66 | 2000
Maniknagar | 90 | 1600 | Chowmuhani | 132 | 1830 | Barisal | 94 | 2000
Bangabhaban | 24 | 1600 | Ashuganj | 47 | 1930 | Patuakhali | 60 | 1930
Narinda | 93 | 1300 | Daudkandi | 104 | 1900 | Bhandaria | 44 | 1900
Dhanmondi | 100 | 1500 | B.Baria | 104 | 2000 | Ishurdi | 44 | 1900
Lalbag | 71 | 1930 | Ramganj | 37 | 1900 | Ruppur Paromanobik | 1 | 100
Madartek | 42 | 1930 | Madunaghat | 59 | 1930 | Natore | 96 | 1900
Mirpur | 87 | 1900 | Hathazari | 74 | 1900 | Bogra | 205 | 1900
Kalyanpur | 93 | 1830 | Khulshi | 184 | 1700 | Noagaon | 106 | 1900
Gulshan | 108 | 1300 | Halishahar | 107 | 2100 | Rajshahi | 116 | 2000
Uttara | 41 | 1830 | Baraulia | 135 | 1500 | C.Nawabganj | 62 | 2000
Uttara(New) | 12 | 900 | Sikalbaha | 29 | 1930 | Amnura | 37 | 1930
Kamrangirchar | 80 | 1900 | Dohazari | 70 | 1830 | Pabna | 92 | 1900
Savar | 108 | 1900 | Cox'sbazar | 76 | 1900 | Shahjadpur | 80 | 2000
Bhasantec | 128 | 1830 | Chandraghona | 21 | 1930 | Serajganj | 85 | 1200
Agargaon | 43 | 1400 | Kaptai | 4 | 1900 | Niyamatpur | 79 | 1930
Satmosjid | 75 | 1900 | A. Khaer Stl. | 0 | 0 | Joypurhat | 43 | 1930
Tongi | 130 | 1700 | Bakulia | 88 | 1900 | Mohastangor | 5 | 1100
Kabirpur | 189 | 1600 | Julda | 22 | 1830 | Rangpur | 106 | 1830
Basundhara | 108 | 1830 | TK chemical | 4 | 1400 | Lalmonirhat | 81 | 1930
Manikganj | 74 | 1900 | Modern Steel | 14 | 900 | Saidpur | 99 | 1830
Joydevpur | 200 | 1930 | Shahmirpur | 26 | 1830 | Purbasadipur | 93 | 2000
New Tongi | 92 | 1200 | Khagrachhari | 15 | 2000 | Thakurgaon | 66 | 1930
Kodda | 193 | 1900 | Matarbari | 22 | 1930 | Palashbari | 92 | 1830
Dhamrai | 42 | 1900 | Baroiar Hat | 18 | 1800 | Barapukuria | 48 | 900
Valuka | 59 | 1900 | Rangamati | 10 | 1830 | Panchagar | 40 | 1930
Tangail | 164 | 1900 | Abul Khair 230 | 141 | 600 | Joldhaka | 17 | 1830
Mymensing | 182 | 1830 | BSRM | 130 | 700
Kishorganj | 88 | 1900 | Goalpara | 23 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-03-11
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 406 | 1:00 | 393 | 12:00 | Kaliakoir | 395 | 4:00 | 375 | 12:00
Bheramara | 404 | 1:00 | 384 | 18:30 | Bhulta | 405 | 1:00 | 386 | 12:00
Ashuganj(N) | 408 | 4:00 | 393 | 12:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 236 | 1:00 | 230 | 10:00 | Hathazari | 220 | 21:00 | 210 | 15:00
Ishurdi | 237 | 5:00 | 227 | 8:00 | Megnaghat | 232 | 1:00 | 224 | 15:00
Ashuganj | 242 | 7:00 | 235 | 12:00 | Fenchuganj | 240 | 6:00 | 235 | 11:00
Serajganj | 231 | 3:00 | 220 | 13:00 | Siddhirganj | 234 | 2:00 | 221 | 12:00
Baghabari | 232 | 6:00 | 222 | 7:00 | Maniknagar | 233 | 4:00 | 219 | 15:00
Barapukuria | 234 | 3:00 | 221 | 9:00 | Old Airport | 232 | 2:00 | 219 | 12:00
Bogra | 226 | 2:00 | 210 | 18:30 | Barisal | 238 | 19:30 | 226 | 7:00
Khulna South | 237 | 5:00 | 217 | 7:00 | AKSML | 223 | 20:00 | 210 | 15:00
Rampura | 231 | 4:00 | 220 | 12:00 | BSRM | 224 | 4:00 | 215 | 13:00
Haripur | 230 | 5:00 | 220 | 12:00 | Bibiyana | 238 | 4:00 | 232 | 17:00
Hasnabad | 230 | 1:00 | 220 | 11:00 | Bhulta | 234 | 2:00 | 221 | 12:00
Aminbazar | 233 | 3:00 | 220 | 11:00 | Ashuganj (S) | 242 | 5:00 | 232 | 13:00
Tongi | 229 | 4:00 | 215 | 11:00 | Kaliakoir | 235 | 2:00 | 221 | 12:00
Comilla (N) | 239 | 8:00 | 230 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 200 | 128 | 1200 | Madanhat | 134 | 1930 | 127 | 1200
Munsiganj | 134 | 300 | 129 | 1200 | Hathazari | 133 | 2000 | 126 | 1500
Megnaghat | 132 | 100 | 129 | 1000 | Khulshi | 131 | 1930 | 123 | 1100
Shyampur | 134 | 400 | 125 | 1200 | Halishahar | 134 | 2000 | 125 | 1100
Bhulta | 130 | 700 | 125 | 1200 | Baraulia | 132 | 1930 | 124 | 1100
Madanganj | 135 | 500 | 127 | 1200 | Sikalbaha | 134 | 1930 | 126 | 1100
Shitalakhya | 138 | 200 | 128 | 1200 | Dohazari | 132 | 1930 | 126 | 1100
Rahim steal | 135 | 500 | 129 | 1200 | Cox'sbazar | 126 | 1900 | 120 | 1200
Matuail | 135 | 600 | 127 | 1200 | Chandraghona | 133 | 2000 | 126 | 1500
Ghorasal | 138 | 100 | 135 | 1400 | Kaptai | 132 | 100 | 128 | 1100
Narsinghdi | 133 | 800 | 127 | 1300 | A. Khaer Stl. | 130 | 1900 | 124 | 1500
Haripur (SBU) | 135 | 300 | 132 | 1000 | Bakulia | 132 | 2000 | 124 | 1100
Ullon | 135 | 600 | 125 | 1200 | Julda | 135 | 2000 | 127 | 1100
Hasnabad | 137 | 600 | 130 | 1200 | TK Chemical | 136 | 2000 | 128 | 800
Magbazar | 135 | 600 | 125 | 1200 | Modern Steel | 132 | 1930 | 124 | 1200
Maniknagar | 135 | 600 | 127 | 1200 | Shahmirpur | 135 | 2000 | 126 | 1100
Bangabhaban | 137 | 500 | 129 | 1300 | Khagrachhari | 132 | 1930 | 126 | 2000
Narinda | 136 | 500 | 125 | 1200 | Matarbari | 128 | 700 | 122 | 1500
Dhanmondi | 135 | 600 | 127 | 1200 | Baroiar Hat | 131 | 100 | 128 | 1200
Lalbag | 137 | 500 | 129 | 1300 | Rangamati | 132 | 1930 | 125 | 1500
Madartek | 136 | 500 | 125 | 1200 | Goalpara | 138 | 1930 | 125 | 800
Mirpur | 135 | 700 | 130 | 1500 | Central s/s | 135 | 1930 | 122 | 700
Kalyanpur | 134 | 600 | 127 | 1200 | Noapara | 133 | 1930 | 123 | 800
Gulshan | 134 | 100 | 124 | 1200 | Jessore | 133 | 500 | 120 | 800
Uttara | 136 | 400 | 125 | 1100 | Jhenida | 131 | 400 | 112 | 1900
Uttara New | 132 | 100 | 124 | 1200 | Bottail | 138 | 100 | 129 | 1830
Kamrangirchar | 137 | 500 | 125 | 1200 | G.K.Project | 141 | 200 | 137 | 900
Savar | 133 | 600 | 124 | 1200 | Faridpur | 132 | 100 | 126 | 1830
Bhasantec | 135 | 200 | 123 | 1200 | Madaripur | 134 | 500 | 126 | 1830
Agargaon | 134 | 600 | 127 | 1200 | Gopalganj | 134 | 600 | 126 | 700
Satmosjid | 134 | 600 | 125 | 1200 | Bagerhat | 138 | 1930 | 129 | 1830
Tongi | 135 | 400 | 127 | 1100 | Mongla | 137 | 1930 | 123 | 800
Kabirpur | 135 | 100 | 125 | 1200 | Satkhira | 134 | 1500 | 121 | 800
Basundhara | 131 | 200 | 120 | 1300 | Gallamari | 136 | 400 | 123 | 700
Manikganj | 139 | 200 | 132 | 1830 | Magura | 132 | 100 | 115 | 1830
Joydevpur | 139 | 2000 | 130 | 1200 | Chuadanga | 130 | 400 | 105 | 1900
New Tongi | 133 | 800 | 125 | 1200 | Barisal | 138 | 2000 | 133 | 1830
Kodda | 137 | 2000 | 127 | 1200 | Patuakhali | 136 | 500 | 127 | 1830
Dhamrai | 135 | 100 | 126 | 1200 | Bhandaria | 135 | 1500 | 126 | 700
Valuka | 132 | 100 | 115 | 1500 | Ishurdi | 140 | 400 | 132 | 1830
Tangail | 134 | 100 | 125 | 1200 | Ruppur Paromanobik | 141 | 100 | 134 | 1100
Mymensing | 133 | 2300 | 121 | 1300 | Natore | 137 | 200 | 126 | 14830
Kishorganj | 132 | 400 | 125 | 900 | Bogra | 136 | 100 | 124 | 900
Netrokona | 131 | 100 | 117 | 1300 | Noagaon | 132 | 300 | 118 | 900
Jamalpur | 138 | 2300 | 116 | 700 | Rajshahi | 133 | 600 | 123 | 1830
Sherpur | 136 | 1930 | 114 | 700 | C.Nawabganj | 130 | 1500 | 122 | 800
Srimongal | 139 | 400 | 136 | 1100 | Amnura | 135 | 1930 | 122 | 900
Shahjibazar | 138 | 500 | 134 | 1400 | Pabna | 135 | 100 | 127 | 1200
Fenchuganj | 137 | 600 | 135 | 900 | Shahjadpur | 143 | 100 | 134 | 1100
Khulawara | 138 | 400 | 134 | 1400 | Serajganj | 137 | 100 | 126 | 900
Sylhet | 136 | 100 | 134 | 1100 | Niyamatpur | 130 | 200 | 112 | 900
Chatak | 136 | 100 | 132 | 1900 | Joypurhat | 132 | 200 | 115 | 1200
Sunamganj | 136 | 100 | 132 | 1400 | Mohastangor | 136 | 300 | 122 | 900
Biani Bazar | 136 | 100 | 132 | 1830 | Rangpur | 132 | 400 | 115 | 900
Comilla(s) | 125 | 800 | 124 | 1500 | Lalmonirhat | 128 | 300 | 108 | 800
Comilla(n) | 137 | 700 | 135 | 1500 | Saidpur | 130 | 100 | 114 | 1830
Chandpur | 138 | 1830 | 136 | 2300 | Purbasadipur | 132 | 100 | 115 | 1830
Feni | 131 | 800 | 127 | 1830 | Thakurgaon | 127 | 300 | 104 | 1900
Chowmuhani | 131 | 1100 | 126 | 1830 | Palashbari | 132 | 200 | 118 | 800
Ashuganj | 138 | 600 | 134 | 1500 | Barapukuria | 134 | 300 | 121 | 900
Daudkandi | 135 | 700 | 129 | 1300 | Panchagar | 126 | 300 | 100 | 900
B.Baria | 134 | 1000 | 130 | 1200 | Joldhaka | 132 | 300 | 112 | 900

## L-Curve
Date | 2019-03-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 90 | 5465 | 2433 | 7898 |  |  |  | QF-LDC-12
0:30 | 125 | 5139.5 | 2171 | 7310.5 | Date: | 2019-03-11
1:00 | 160 | 4814 | 1909 | 6723
1:30 | 155 | 4651.5 | 1867.5 | 6519
2:00 | 150 | 4489 | 1826 | 6315
2:30 | 145 | 4422 | 1818.5 | 6240.5 | [5 empty] | Gen. at Eve. Peak | 9965 | 9965 MW (19:30 )
3:00 | 140 | 4355 | 1811 | 6166 | [6 empty] | 19:30
3:30 | 145 | 4344.5 | 1811 | 6155.5 | [5 empty] | Gen. at Day Peak | 8076.64 | 8076.64 MW (12:00 )
4:00 | 150 | 4334 | 1811 | 6145 | [6 empty] | 12:00
4:30 | 155 | 4309.5 | 1774.5 | 6084 | [5 empty] | Highest Generation | 9965
5:00 | 160 | 4285 | 1738 | 6023 | [6 empty] | 19:30
5:30 | 145 | 4351.5 | 1834 | 6185.5
6:00 | 130 | 4418 | 1930 | 6348
6:30 | 195 | 4585.4 | 1995.5 | 6580.9
7:00 | 260 | 4752.8 | 2061 | 6813.8
7:30 | 290 | 4884.675 | 2073.5 | 6958.175
8:00 | 320 | 5016.55 | 2086 | 7102.55
8:30 | 280 | 5149.8 | 2096 | 7245.8
9:00 | 240 | 5283.05 | 2106 | 7389.05
9:30 | 145 | 5405.53 | 2122 | 7527.53
10:00 | 50 | 5528.01 | 2138 | 7666.01
10:30 | 30 | 5480.905 | 2156 | 7636.905
11:00 | 10 | 5433.8 | 2174 | 7607.8
11:30 | 20 | 5574.22 | 2268 | 7842.22
12:00 | 30 | 5714.64 | 2362 | 8076.64
12:30 | 70 | 5724.525 | 2408.5 | 8133.025
13:00 | 110 | 5734.41 | 2455 | 8189.41
13:30 | 70 | 5690.455 | 2350 | 8040.455
14:00 | 30 | 5646.5 | 2245 | 7891.5
14:30 | 80 | 5709.25 | 2305 | 8014.25
15:00 | 130 | 5772 | 2365 | 8137
15:30 | 130 | 5712.95 | 2317.5 | 8030.45
16:00 | 130 | 5653.9 | 2270 | 7923.9
16:30 | 115 | 5568.2 | 2225.5 | 7793.7
17:00 | 100 | 5482.5 | 2181 | 7663.5
17:30 | 90 | 5565.25 | 2241 | 7806.25
18:00 | 80 | 5648 | 2301 | 7949
18:30 | 160 | 6206 | 2675 | 8881
19:00 | 240 | 6764 | 3049 | 9813
19:30 | 270 | 6815 | 3150 | 9965
20:00 | 0 | 6546 | 3131 | 9677 |  |  |  | Executive Engineer
20:30 | 0 | 6468 | 3085 | 9553 |  |  |  | Network Operation Division
21:00 | 0 | 6390 | 3039 | 9429
21:30 | 40 | 6216.5 | 2953.5 | 9170
22:00 | 80 | 6043 | 2868 | 8911 |  |  |  |  | Page 6 of 7
22:30 | 75 | 5872.5 | 2695.5 | 8568
23:00 | 70 | 5702 | 2523 | 8225
23:30 | 80 | 5583.5 | 2478 | 8061.5
24:00 | 90 | 5465 | 2433 | 7898
9965 MW (19:30 )
8076.64 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-03-11 |  | Energy | 190579258
[10 empty] | 2019-03-11 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4582 | 761 | 1367 | 841 | 149 | 72 | 0 | 0 | 126
0:30 | 4505.5 | 664 | 1315.5 | 494.5 | 149 | 72 | 0 | 0 | 110 | Date: | 2019-03-11
1:00 | 4429 | 567 | 1264 | 148 | 149 | 72 | 0 | 0 | 94
1:30 | 4359.5 | 567 | 1160.5 | 117 | 149 | 72 | 0 | 0 | 94 | [7 empty] | Total Energy | 190.5793 | Total Energy Gen 190.579 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 190.579 MKWHr
2:00 | 4290 | 567 | 1057 | 86 | 149 | 72 | 0 | 0 | 94 | [7 empty] | Energy not Served | 0
2:30 | 4252 | 567 | 1022.5 | 86 | 149 | 71 | 0 | 0 | 93 | [7 empty] | Energy Requirement | 190.5793
3:00 | 4214 | 567 | 988 | 86 | 149 | 70 | 0 | 0 | 92
3:30 | 4206 | 567 | 986.5 | 86 | 149 | 70 | 0 | 0 | 91 | [6 empty] | Shortage
4:00 | 4198 | 567 | 985 | 86 | 149 | 70 | 0 | 0 | 90
4:30 | 4142 | 567 | 980 | 86 | 149 | 70 | 0 | 0 | 90
5:00 | 4086 | 567 | 975 | 86 | 149 | 70 | 0 | 0 | 90
5:30 | 4104.5 | 640 | 1033.5 | 100.5 | 149 | 70 | 0 | 0 | 88
6:00 | 4123 | 713 | 1092 | 115 | 149 | 70 | 0 | 0 | 86
6:30 | 4225 | 712.5 | 1165 | 173 | 149 | 70 | 0 | 0 | 85 |  |  |  |  | Coal
7:00 | 4327 | 712 | 1238 | 231 | 149 | 70 | 0 | 0 | 84
7:30 | 4412.5 | 713 | 1236 | 286.5 | 149 | 70.5 | 0 | 0 | 85 |  |  |  | Oil |  |  |  | ,
8:00 | 4498 | 714 | 1234 | 342 | 149 | 71 | 0 | 0 | 86
8:30 | 4548 | 714 | 1304.5 | 358.5 | 149 | 71 | 0 | 0 | 89
9:00 | 4598 | 714 | 1375 | 375 | 149 | 71 | 0 | 0 | 92
9:30 | 4584 | 713.5 | 1444 | 446 | 149 | 71 | 9 | 0 | 94
10:00 | 4570 | 713 | 1513 | 517 | 149 | 71 | 18 | 0 | 96
10:30 | 4545.5 | 713.5 | 1464.5 | 568 | 149 | 56.5 | 18 | 0 | 102
11:00 | 4521 | 714 | 1416 | 619 | 149 | 42 | 18 | 0 | 108
11:30 | 4607 | 714 | 1478 | 686 | 149 | 57 | 18 | 0 | 112
12:00 | 4693 | 714 | 1540 | 753 | 149 | 72 | 18 | 0 | 116
12:30 | 4732.5 | 714 | 1538 | 773.5 | 149 | 72.5 | 17.5 | 0 | 117
13:00 | 4772 | 714 | 1536 | 794 | 149 | 73 | 17 | 0 | 118
13:30 | 4772 | 714 | 1536 | 794 | 149 | 73 | 17 | 0 | 118
14:00 | 4772 | 714 | 1536 | 794 | 149 | 73 | 17 | 0 | 118
14:30 | 4679 | 714 | 1527 | 867.5 | 149 | 72.5 | 17 | 0 | 121
15:00 | 4586 | 714 | 1518 | 941 | 149 | 72 | 17 | 0 | 124
15:30 | 4512 | 713.5 | 1465 | 969 | 149 | 71 | 20 | 0 | 118
16:00 | 4438 | 713 | 1412 | 997 | 149 | 70 | 23 | 0 | 112
16:30 | 4374.5 | 713 | 1363.5 | 979.5 | 149 | 70 | 24.5 | 0 | 113
17:00 | 4311 | 713 | 1315 | 962 | 149 | 70 | 26 | 0 | 114
17:30 | 4372 | 741.5 | 1305 | 976 | 149 | 70 | 71 | 0 | 120
18:00 | 4433 | 770 | 1295 | 990 | 149 | 70 | 116 | 0 | 126
18:30 | 4699.5 | 815 | 1401 | 1403 | 149 | 70 | 206.5 | 0 | 137
19:00 | 4966 | 860 | 1507 | 1816 | 149 | 70 | 297 | 0 | 148
19:30 | 4877 | 860 | 1401 | 2117 | 149 | 70 | 347 | 0 | 144
20:00 | 4749 | 860 | 1348 | 2020 | 149 | 72 | 335 | 0 | 144
20:30 | 4726.5 | 860 | 1339.5 | 1934.5 | 149 | 72 | 329.5 | 0 | 142
21:00 | 4704 | 860 | 1331 | 1849 | 149 | 72 | 324 | 0 | 140
21:30 | 4722 | 860 | 1335 | 1636.5 | 149 | 72 | 258.5 | 0 | 137
22:00 | 4740 | 860 | 1339 | 1424 | 149 | 72 | 193 | 0 | 134
22:30 | 4664 | 810.5 | 1349.5 | 1294 | 149 | 72 | 99 | 0 | 130
23:00 | 4588 | 761 | 1360 | 1164 | 149 | 72 | 5 | 0 | 126
23:30 | 4585 | 761 | 1363.5 | 1002.5 | 149 | 72 | 2.5 | 0 | 126 | Max Temp. in Dhaka |  | 30° C
24:00 | 4582 | 761 | 1367 | 841 | 149 | 72 | 0 | 0 | 126
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 190.579 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 190.579 MKWHr
Note on W13: Author:

## Generation
2019-03-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 42 | 42 | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 41 | 42 | 42 | 43 | 43 | 42 | 40 | 40 | 40 |  | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 927000
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 676000
3 | Chattogram ST-1 (Raozan) | 135 | 135 | 135 | 135 | 135 | 135 | 140 | 140 | 135 | 135 | 135 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 125 | 125 | 130 | 130 | 130 | 130 | 130 | 3200000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 8 | 8 |  | 21 | 25 | 25 | 25 | 25 | 25 | 25 | 163948
| Teknaf Solartech 20MW | [5 empty] | 0 | 2.7 | 8.25 | 13.95 | 17.91 | 19.9 | 20.14 | 14.31 | 18.6 | 14.5 | 9 | 3.2 | 0 | [8 empty] | 141480
6 | Sikalbaha 225MW (Gas) | 201 | 201 | 214 | 202 | 202 | 202 | 207 | 202 | 218 | 204 | 208 | 210 | 200 | 201 | 204 | 205 | 202 | 206 |  | 201 | 201 | 201 | 201 | 201 | 214 | 203 | 4861126
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [17 empty] | 6 |  | 34 | 34 | 34 | 34 | 0 | 0 |  | 109349
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 8 | 0 | 0 |  |  |  |  | 6880
15 | Siddhirgonj ST 210MW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 115 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2601900
16 | Siddhirgonj GT Unit-1& 2 | 156 | 120 | 80 | 100 | 95 | 120 | 125 | 155 | 160 | 97 | 67 | 67 | 125 | 60 | 99 | 57 | 76 | 80 |  | 160 | 120 | 120 | 100 | 105 | 105 | 105 | 2741000
17 | Siddhirganj CCPP-335 MW | 75 | 75 | 0 | [23 empty] | 148873
18 | Summit Gazipur -2 | [17 empty] | 2 |  | 27 | 65 | 65 | 62 | 0 | 0 |  | 165600
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 844000
21 | Ghorasal GT: Unit-3 | [15 empty] | 44 | 44 | 62 |  | 189 | 188 | 188 | 188 | 188 | 0 | 0 | 972000
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 140 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 4095000
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 382 | 320 | 280 | 280 |  | 380 | 380 | 320 | 320 | 320 | 320 | 320 | 8049818
26
28 | Ashuganj ST: Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1848682
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1889945
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 37 | 37 | 37 | 37 | 31 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 860544
33 | Ashuganj CCPP 225 MW | 185 | 184 | 204 | 184 | 184 | 190 | 202 | 188 | 203 | 221 | 212 | 209 | 186 | 184 | 183 | 182 | 183 | 199 |  | 183 | 182 | 182 | 182 | 182 | 205 | 184 | 4700000
34 | Ashuganj CCPP(South) | 320 | 300 | 300 | 300 | 280 | 280 | 280 | 360 | 360 | 360 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7924000
| Ashuganj CCPP(North) | 320 | 300 | 300 | 300 | 280 | 280 | 320 | 360 | 360 | 360 | 320 | 330 | 330 | 330 | 360 | 360 | 320 | 320 |  | 360 | 360 | 325 | 320 | 320 | 320 | 320 | 8156000
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 128160
36 | Chandpur CCPP | 100 | 80 | 80 | 90 | 90 | 80 | 90 | 90 | 80 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 95 | 95 | 95 | 95 | 100 | 100 | 100 | 2135030
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | [17 empty] | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 543300
39 | Haripur 412 MW CCPP | 349 | 351 | 361 | 362 | 350 | 363 | 365 | 361 | 370 | 380 | 353 | 379 | 375 | 348 | 290 | 348 | 350 | 353 |  | 388 | 388 | 350 | 350 | 349 | 364 | 368 | 8679420
40 | Meghnaghat CCPP 450MW | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 380 | 450 | 450 | 450 | 450 | 420 | 420 | 390 | 360 | 360 |  | 400 | 370 | 370 | 330 | 330 | 330 | 330 | 8733425
41 | Haripur Power CCPP 360MW
42 | Mymensingh RPCL 210MW | 154 | 148 | 156 | 142 | 160 | 150 | 157 | 150 | 153 | 137 | 151 | 146 | 139 | 137 | 137 | 137 | 139 | 145 |  | 143 | 147 | 145 | 145 | 145 | 154 | 150 | 3476000
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 58 | 58 | 60 |  | 58 | 60 | 60 | 58 | 60 | 59 | 58 | 1408000
45 | Fenchugonj CCPP-2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 70 | 70 | 70 | 70 | 68 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1430400
46 | Shajibazar 330 MW | 110 | 109 | 110 | 109 | 109 | 107 | 108 | 108 | 115 | 108 | 114 | 114 | 113 | 115 | 113 | 115 | 118 | 113 |  | 113 | 114 | 113 | 115 | 114 | 114 | 113 | 2446000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 40 | 40 | 40 | 40 | 53 | 68 | 66 | 63 | 66 | 64 | 64 | 57 | 60 | 56 | 41 | 45 | 65 |  | 66 | 58 | 56 | 66 | 64 | 67 | 67 | 1319232
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 50 | 86 | 86 | 83 | 83 | 83 | 85 | 85 | 85 | 85 | 83 | 40 | 40 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1481280
49 | Shahjibazar (EPL) 50MW | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 0 | 45 | 45 | 46 | 46 | 46 | 46 | 46 |  | 46 | 44 | 46 | 46 | 48 | 48 | 48 | 1082880
50 | Sylhet GT 150 MW | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 68 | 49 | 49 | 48 | 47 | 47 | 48 | 48 | 48 | 48 |  | 48 | 42 | 43 | 43 | 42 | 0 | 0 | 1404750
51 | Sylhet GT 20 MW | [8 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 308000
52 | Sylhet (EPL) 50MW | 47 | 47 | 0 | 6 | 6 | 24 | 40 | 20 | 44 | 38 | 39 | 40 | 41 | 41 | 41 | 40 | 40 | 42 |  | 44 | 44 | 45 | 45 | 45 | 46 | 46 | 885700
53 | Sylhet (Desh) 10MW | [6 empty] | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 166140
54 | Hobiganj 11MW | [6 empty] | 0 | 11 | 8 | 8 | 0 | 2 | 8 | 3 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 143808
55 | Fenchugonj (Barakatullah) 51MW | 50 | 5 | 5 | 5 | 5 | 20 | 48 | 48 | 48 | 45 | 45 | 50 | 50 | 50 | 47 | 45 | 47 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 953400
56 | Shahjahanulla 25 MW | [7 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 16 | 17 | 16 |  | 17 | 17 | 16 | 17 | 16 | 16 | 16 | 248352
57 | Summit Bibiana- 2 | 280 | 290 | 310 | 300 | 290 | 300 | 310 | 305 | 300 | 295 | 270 | 310 | 280 | 240 | 300 | 270 | 280 | 290 |  | 310 | 270 | 270 | 280 | 280 | 300 | 310 | 7463250
58 | Southern 55MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 958421
59 | Sikalbaha (Energis) | 41 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 857760
60 | Barabkunda (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 19 | 19 | 20 | 20 |  | 22 | 22 | 22 | 20 | 19 | 20 | 22 | 484416
61 | Narshingdi (Doreen) | [7 empty] | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 333828
62 | Tangail (Doreen) 22MW | 22 | 0 |  |  |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 409248
63 | Tripura | 94 | 94 | 92 | 90 | 90 | 86 | 84 | 86 | 92 | 96 | 108 | 116 | 118 | 120 | 124 | 112 | 114 | 126 |  | 148 | 144 | 144 | 140 | 134 | 126 | 126 | 2640960
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 36 | 36 | 36 | 34 | 12 | 2 | 2 | 2 | 2 | 5 | 2 | 2 | 2 | 5 | 9 |  | 16 | 16 | 23 | 28 | 35 | 35 | 35 | 448320
65 | Feni (Doreen) 22MW | [7 empty] | 0 | 8 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 327204
66 | Feni, Mohipal (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 217620
67 | Jangalia (Summit) 33MW | 0 | [5 empty] | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 34 | 33 | 33 | 33 | 33 | 594500
68 | Summit Cumilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 516360
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 0 | 16 | 26 | 26 | 26 | 22 | 26 | 29 | 29 | 30 | 30 |  | 25 | 25 | 30 | 4 | 30 | 30 | 31 | 619920
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 544500
72 | Summit Rupganj | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 32 |  | 31 | 31 | 32 | 31 | 31 | 18 | 31 | 787500
73 | Ghorashal (Regent) | 111 | 52 | 12 | 12 | 12 | 12 | 12 | 12 | 108 | 108 | 108 | 108 | 108 | 111 | 107 | 106 | 109 | 110 |  | 110 | 110 | 52 | 52 | 52 | 52 | 52 | 1711409
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | 0 | [6 empty] | 0 | 9 | 25 | 25 | 25 | 25 | 25 | 33 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 634440
79 | Kodda 149MW
80 | Jamalpur 95MW | 7 | 0 |  |  |  | 0 | 7 | 67 | 74 | 80 | 80 | 80 | 80 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 1402560
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit) | [11 empty] | 10 | 10 | 65 | 75 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1109353
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 77 | 77 | 75 | 74 | 74 | 73 | 73 | 40 | 40 |  | 60 | 50 | 50 | 50 | 50 | 50 | 50 | 1615040
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 75 | 77 | 84 | 84 | 50 | 50 | 10 | 586920
92 | Fenchuganj (EPL) 44MW | 50 | 5 | 5 | 5 | 5 | 17 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 981000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 28 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 666906
94 | Gagnagar (Orion) | [11 empty] | 0 | 4 | 7 | 7 | 7 | 7 | 10 |  | 58 | 70 | 48 | 48 | 32 | 0 | 0 | 276048
95 | Patenga 50MW | [15 empty] | 0 | 5 | 6 |  | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 300960
96 | Chattogram ECPV 108 MW | [17 empty] | 10 |  | 93 | 98 | 101 | 71 | 7 | 0 | 0 | 306240
97 | Katpotti 51 MW | [10 empty] | 12 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 47 | 48 | 48 | 48 | 48 | 18 | 18 | 591648
98 | Bosila 108MW | [5 empty] | 0 | 8 | 8 | 8 | 52 | 62 | 61 | 60 | 58 | 59 | 58 | 59 | 58 |  | 54 | 54 | 54 | 53 | 54 | 54 | 54 | 827520
99 | Madanganj-55 MW | [10 empty] | 2 | 15 | 27 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 656212
100 | Northern 55 MW | [13 empty] | 36 | 36 | 36 | 36 | 36 |  | 55 | 55 | 55 | 55 | 55 | 18 | 18 | 3876930
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 100 | 140 | 100 | 100 | 100 |  | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 3247077
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.3 | 1.1 | 1.1 | 0.9 | 1.5 | 2.1 | 1.9 | 1.5 | 0.9 | 0.3 | 0 | [8 empty] | 12250
103 | Banco Energy 54MW | 35 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 777600
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | [8 empty] | 0 | 29 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 146 | 200 | 150 | 150 | 100 | 100 | 0 | 1063200
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [15 empty] | 12 | 15 | 15 |  | 51 | 80 | 80 | 80 | 58 | 33 | 0 | 367200
115 | Juldah 100 MW Unit-3 | 20 | 0 |  |  |  | 0 | 10 | 30 | 30 | 52 | 60 | 92 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1453440
116 | Chandpur Desh 200MW | 0 | [6 empty] | 0 | 17 | 23 | 52 | 52 | 52 | 52 | 52 | 53 | 53 | 53 |  | 123 | 200 | 185 | 145 | 72 | 72 | 72 | 1201440
117 | Midland 150MW | [8 empty] | 0 | 3 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 77 | 100 | 80 | 70 | 43 | 0 | 0 | 752727
118 | Bibiyana-3 285MW | [10 empty] | 40 | 39 | 32 | 34 | 35 | 15 | 34 | 35 |  | 35 | 0 | 0 |  |  |  |  | 286000
United Jamalpur PPL
120 | Eastern Zone Total | 4814 | 4489 | 4355 | 4334 | 4285 | 4418 | 4752.8 | 5016.55 | 5283.05 | 5528.01 | 5433.8 | 5704.64 | 5724.41 | 5646.5 | 5772 | 5653.9 | 5482.5 | 5648 |  | 6764 | 6815 | 6546 | 6390 | 6043 | 5702 | 5465 | 134901803
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [17 empty] | 13 |  | 102 | 115 | 115 | 73 | 32 | 0 |  | 336000
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [17 empty] | 21 |  | 44 | 44 | 39 | 41 | 41 | 5 | 0 | 182880
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [11 empty] | 35 | 53 | 53 | 53 | 53 | 53 | 53 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 932160
130
131
132
133
| Summit Barisal 110 MW | [19 empty] | 48 | 48 | 48 | 48 | 32 | 32 | 16 | 215040
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 45 | 51 | 50 | 71 | 71 | 92 | 96 | 96 | 52 |  | 89 | 95 | 96 | 96 | 95 | 96 | 95 | 1309094
| Bhola CCPP 194MW | 169 | 174 | 174 | 174 | 174 | 173 | 173 | 174 | 174 | 171 | 174 | 174 | 162 | 173 | 173 | 161 | 174 | 174 |  | 173 | 171 | 171 | 168 | 173 | 174 | 174 | 4186824
140 | Bhola (Venture) 33MW | 16 | 16 | 14 | 14 | 14 | 14 | 13 | 11 | 10 | 10 | 12 | 13 | 14 | 14 | 14 | 13 | 1 | 4 |  | 15 | 15 | 9 | 18 | 17 | 16 | 14 | 305200
141 | Bangla Trak Noapara | [19 empty] | 20 | 20 | 20 | 0 |  |  |  | 36480
142 | Noapara (KZA) 40MW | [6 empty] | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 591375
143 | Gopalganj Peaking | [14 empty] | 5 | 11 | 14 | 31 |  | 63 | 82 | 69 | 40 | 20 | 0 |  | 269952
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 567 | 567 | 567 | 567 | 567 | 713 | 712 | 714 | 714 | 713 | 714 | 714 | 714 | 713 | 714 | 713 | 713 | 770 |  | 860 | 860 | 860 | 860 | 860 | 761 | 761 | 17192727
147 | Bheramara 360 MW | 320 | 320 | 320 | 320 | 300 | 270 | 300 | 280 | 240 | 210 | 230 | 350 | 414 | 280 | 360 | 320 | 300 | 300 |  | 380 | 422 | 421 | 421 | 421 | 418 | 420 | 8070336
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3659300
153 | Baghabari GT 71MW | 50 | 50 | 50 | 50 | 50 | 50 | 65 | 65 | 65 | 60 | 60 | 60 | 55 | 55 | 55 | 58 | 55 | 55 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 135000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [17 empty] | 16 |  | 17 | 24 | 30 | 43 | 43 | 0 | 0 | 130004
157 | Sirajgonj Unit-1 225MW (Gas) | 181 | 180 | 186 | 191 | 156 | 169 | 169 | 156 | 168 | 171 | 185 | 201 | 204 | 164 | 188 | 185 | 186 | 185 |  | 203 | 182 | 181 | 182 | 182 | 192 | 197 | 4631582
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 179 | 180 | 162 | 157 | 148 | 157 | 157 | 182 | 231 | 231 | 230 | 226 | 225 | 226 | 214 | 179 | 156 | 149 |  | 190 | 178 | 178 | 178 | 178 | 188 | 192 | 4711891
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 184 | 164 | 163 | 163 | 154 | 163 | 163 | 162 | 165 | 167 | 186 | 203 | 207 | 157 | 165 | 152 | 152 | 155 |  | 196 | 184 | 184 | 184 | 184 | 194 | 199 | 4384909
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 22 | 5 | 5 | 5 | 5 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 449760
163 | Bogra (EPL) | 17 | 6 | 6 | 6 | 6 | 6 | 15 | 16 | 16 | 14 | 14 | 14 | 15 | 17 | 17 | 14 | 17 | 17 |  | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 326116
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 143946
165 | Amnura 50MW | 0 | [5 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 774530
166 | Katakhali (Northern) | [19 empty] | 24 | 50 | 50 | 25 | 0 | 0 | 0 | 104367
167 | Katakhali Peaking
168 | Santahar Peaking | [17 empty] | 27 |  | 29 | 29 | 29 | 29 | 29 | 0 | 0 | 142370
169 | Rajlanka 52 MW | 0 |  |  |  | 0 | 29 | 52 | 43 | 43 | 43 | 35 | 43 | 43 | 43 | 43 | 43 | 24 | 24 |  | 40 | 43 | 43 | 43 | 47 | 43 | 52 | 1820000
170 | Chapainawabganj-100 MW | 0 | [18 empty] | 70 | 102 | 102 | 102 | 60 | 0 | 0 | 346052
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [9 empty] | 16 | 4 | 0 | 0 | 0 | 0 | [11 empty] | 34560
173 | Rangpur GT | [19 empty] | 17 | 17 | 17 | 17 | 0 |  |  | 54000
175 | Saidpur GT | [9 empty] | 18 | 18 | 18 | 17 | 18 | 12 | 12 | 12 | 15 |  | 15 | 15 | 15 | 18 | 0 |  |  | 201000
176
177
178
178 | Western Zone Total | 1909 | 1826 | 1811 | 1811 | 1738 | 1930 | 2061 | 2086 | 2106 | 2138 | 2174 | 2362 | 2455 | 2245 | 2365 | 2270 | 2181 | 2301 |  | 3049 | 3150 | 3131 | 3039 | 2868 | 2523 | 2433 | 55677455