## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: June 2024
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2024-06-01 |  | 2024-05-01 |  | 2023-06-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15798 | 2024-06-11 | 16067 | 2024-05-23 | 14655 | 2023-06-08 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 21:00
2 | Minimum Generation (MW) | 8396 | 2024-06-20 | 3651 | 2024-05-28 | 7589 | 2023-06-28 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 16067 | 2024-05-23 | 16067 | 2024-05-23 | 14655 | 2023-06-08 | 16477 | 2024-04-30
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 14167 | 2024-06-11 | 14488 | 2024-05-16 | 12677 | 2023-06-08 | 14488 | 2024-05-16
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 16700 | 2024-06-30 | 16400 | 2024-05-23 | 15800 | 2023-06-30 | 17200 | 2024-04-29
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14053.0333 |  | 14021 |  | 13225.3 |  | - | -
7 | Average Generation (MW) at Day Peak | 12257.2667 |  | 12364.2258 |  | 11423.9667 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 938 | 2024-06-07 | 939 | 2024-05-08 | 930 | 2023-06-25 | 964 | 2024-03-28
|  |  | 3:30 |  | 10:30 |  | 7:30 |  | 13:30
9 | Maximum Power Import from Tripura, India (MW) | 100 | 2024-06-05 | 100 | 2024-05-25 | 184 | 2023-06-13 | 194 | 12/06/19
|  |  | 20:00 |  | 19:00 |  | 19:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1727 | 2024-06-25 | 845 | 2024-05-16 | 1945 | 2023-06-06 | 4395 | 04/10/2022
|  |  | 19:30 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13792 | 2024-06-25 | 14965 | 2024-05-16 | 13763 | 45083 | 14965 | 2024-05-16
|  | - | 19:30 | - | 21:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2024-06-15 | 0 | 2024-05-11 | 30 | 45103 | - | -
|  |  | 21:00 |  | 19:30 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13723 | 2024-06-15 | 13341 | 2024-05-11 | 13364 | 2023-06-26 | - | -
|  |  | 21:00 |  | 19:30 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 1808 | 2024-06-25 | 526 | 2024-05-02 | 2675 | 45082 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12757 | 2024-06-25 | 14149 | 2024-05-02 | 12099 | 45082 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2024-06-15 | 0 | 2024-05-11 | 162 | 45088 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11757 | 2024-06-15 | 10559 | 2024-05-02 | 12356 | 45088 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 22 |  | 22 |  | 22 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 19 |  | 21 |  | 26 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 2340.8823 |  | 2216.8164 |  | 1745.3811 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 125.5183 |  | 116.8801 |  | 88.4927 |  | - | -
22 | Net Generation of BPDB (MKWH) | 2215.364 |  | 2099.9364 |  | 1656.8884 |  | - | -
23 | Net Generation of IPP (MKWH) | 5237.2842 |  | 5569.5361 |  | 4513.7304 |  | - | -
24 | Net Generation of REB (MKWH) | 69.9332 |  | 99.879 |  | 121.3394 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 239.9504 |  | 239.9743 |  | 364.0404 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7762.5318 |  | 8009.3258 |  | 6655.9986 |  | 8000.69 | June'24
26 | Energy Generation by Gas (MKWH) | 4103.364 |  | 4771.0602 |  | 4651.8044 |  | 4771.06 | May-24
27 | Energy Generation by Diesel (MKWH) | 23.2046 |  | 20.5221 |  | 299.6883 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1429.8415 |  | 1295.8587 |  | 1291.3754 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 80.8001 |  | 22.2695 |  | 25.8407 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 44.0204 |  | 55.4311 |  | 34.6981 |  | 57.09 | March-24
31 | Energy Generation by Coal (MKWH) | 988.7654 |  | 987.5956 |  | 441.0844 |  | 1047.9615 | April'24
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 700.4526 |  | 646.3346 |  | 737.9119 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 76.6243 |  | 78.2556 |  | 78.4931 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: June 2024
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15798 | 2024-06-11 | 21:00
Generation Period
| Dhaka | MW | 5536.25
| Chattogram | MW | 1429
| Cumilla | MW | 1338
| Mymensingh | MW | 1024
| Sylhet | MW | 632
a) | Total supply in East zone | MW | 9959.25
| Khulna | MW | 2043
| Barisal | MW | 520
| Rajshahi | MW | 1668.6
| Rangpur | MW | 967
b) | Total supply in West zone | MW | 5198.6
c) | Total supply in both zone ( a+b) | MW | 15157.85
Ref: | 27.21.0000.603.16.087.20.831 | Date: 18/06/2024
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June 2024
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 308 | 2024-06-28 | 22:00
| b) Ishurdi end | MW | 380 | 2024-06-01 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 848 | 2024-06-01 | 9:00
| b) Ishurdi end | MW | 108 | 2024-06-28 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 2.1625
| b) Ishurdi end | MKWH | 78.6215
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 76.2629
| b) Ishurdi end | MKWH | 2.0995
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 |  |  |  |  | 2.955
| a) Ashuganj end | MW | 470 | 2024-06-28 | 19:30
| b)Serajganj end | MW | 640 | 2024-06-01 | 8:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2026-06-01 | 9:00
| b)Sirajganj end | MW | 180 | 2024-06-28 | 22:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 2.4178
| b)Sirajganj end | MKWH | 207.052
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 200.955
| b)Sirajganj end | MKWH | 2.472
30 | Transmission loss of EWI /NO-2 | % | 2.885'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2284 | 2024-06-03 | 23:00
|  | MW | 1408
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2246 | 2024-06-03 | 23:00
|  | MW | 1397
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MKWH | 29.926 | 2024-06-03 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MKWH | 29.542 | 2024-06-03
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 530.736
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 531.233
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | -0.093737
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-06-27 17:45 | 2024-06-27 23:44 | 5:59 | E/O | C.T problem | 40 | 239.3333 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-06-13 14:29 | 2024-06-13 14:41 | 0:12 | T | U/F | 130 | 26 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2024-06-27 15:54 | 2024-06-27 17:04 | 1:10 | E/O | Temperature problem | 40 | 46.6667 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-06-13 14:29 | 2024-06-13 14:41 | 0:12 | T | U/F | 130 | 26 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-06-27 10:48 | 2024-06-27 12:27 | 1:39 | E/O | 33 KV T2 CT both side high temperature | 50 | 82.5 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2024-06-12 19:53 | 2024-06-13 19:43 | 23:50 | E/O | GT-2 33KV BUS and 33KV feeder Rajendrapur-4 CB Maintenance | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 LT | 2024-06-12 19:02 | 2024-06-12 19:02 | 0:00 | T | 33kv Rajendrapur-4 feeder breaker fault. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-06-05 00:57 | 2024-06-05 01:29 | 0:32 | E/O | Shutdown taken by DPBS-1 due to red hot maintenance at 33 kV DEPZ feeder's bus DS (B phase) load side. | 50 | 26.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-06-05 21:51 | 2024-06-05 23:47 | 1:56 | E/O | Red hot 33kv bus DS maintenance | 75 | 145 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-06-10 11:00 | 2024-06-10 13:00 | 2:00 | E/O | Shutdown taken by DPBS1 due to 33 kV TR-1 & TR-2 section DS maintenance purpose. | 70 | 140 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2024-06-28 15:42 | 2024-06-28 17:52 | 2:10 | E/O | Shutdown is taken by Gazipur PBS due to red hot maintenance work at 33 kV Kashimpur-4. | 50 | 108.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2024-06-28 15:39 | 2024-06-28 17:51 | 2:12 | E/O | Shutdown is taken by Gazipur PBS due to red hot maintenance work at 33 kV Kashimpur-4. | 60 | 132 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | 33 kV T3 Bus | 2024-06-22 11:30 | 2024-06-22 14:21 | 2:51 | E/O | Hot spot mitigation works at T-3 internal bus coupler side. shutdown taken by Kishoreganj PBS | 45 | 128.25 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-06-26 14:38 | 2024-06-26 15:30 | 0:52 | T | PRD | 22 | 19.0667 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) HT | 2024-06-28 15:27 | 2024-06-28 17:22 | 1:55 | T | PRD | 15 | 28.75 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-06-07 14:48 | 2024-06-07 15:56 | 1:08 | E/O | Due to emeregency maint.work | 50 | 56.6667 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2024-06-08 23:34 | 2024-06-09 00:14 | 0:40 | E/O | 33kv Nandail-2 feeder Red-hot Maintenance works. | 55 | 36.6667 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-01(E05) LT | 2024-06-11 13:06 | 2024-06-11 14:16 | 1:10 | E/O | 33 kv Nut-bult tightening | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-06-14 08:13 | 2024-06-14 08:26 | 0:13 | T | SPBS DC System fail & Dubaora 33 KV feeder fault. | 3 | 0.65 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2024-06-14 08:13 | 2024-06-14 08:25 | 0:12 | T | SPBS DC System fail & Dubaora 33 KV feeder fault. | 3 | 0.6 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132 kV BUS-2 | 2024-06-01 15:50 | 2024-06-01 15:50 | 0:00 | E/O | Due to Red hot Bus DS Bhaluka line | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2024-06-03 16:29 | 2024-06-03 16:50 | 0:21 | T | df/dt Trip | 46 | 16.1 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2024-06-08 02:15 | 2024-06-08 03:18 | 1:03 | E/O | 33 KV KACHUADANGA FEDDER FAULT | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-07 23:42 | 2024-06-08 00:09 | 0:27 | T | 33kv ghatail feeder fault | 112 | 50.4 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-06-03 03:01 | 2024-06-03 03:45 | 0:44 | T | 86x Master Relay Operated | 30 | 22 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-06-03 06:25 | 2024-06-03 06:35 | 0:10 | T | 86x Master Relay Operated | 30 | 5 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-06-08 02:15 | 2024-06-08 03:18 | 1:03 | E/O | 33 KV KACHUADANGA FEDDER FAULT | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-06-28 09:47 | 2024-06-28 10:07 | 0:20 | T | 86X Trip Relay | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2024-06-28 10:25 | 2024-06-28 10:56 | 0:31 | T | 86X Trip Relay | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2024-06-07 23:42 | 2024-06-08 00:09 | 0:27 | T | 33KV GHATAIL FEDDER FAULT | 57 | 25.65 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 2024-06-26 20:46 | 2024-06-26 23:48 | 3:02 | T | Due to T3 auxillary bus loop out | 30 | 91 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2024-06-13 08:41 | 2024-06-16 09:40 | 72:59 | E/O | Emergency work at replacement | 200 | 196.67 | Power interruption 08:41 to 09:40
|  |  | Total : | 132:00 |  | Unserved Energy: |  | 1649.97
Dhaka (South) Grid Circle :
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2024-06-06 20:04 | 2024-06-06 20:18 | 0:14 | T | due to 33 kv Zinzira ckt-3 feeder of DPBS-4 fault | 28 | 6.5333 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 404 T-1 LT | 2024-06-24 17:11 | 2024-06-24 17:50 | 0:39 | T | 33 kv zin-2 & Bashundhara ckts fault | 22 | 14.3 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 HT | 2024-06-24 17:11 | 2024-06-24 17:11 | 0:00 | T | 33 kv zin-2 & Bashundhara ckts fault | 25 | 0 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 HT | 2024-06-24 17:51 | 2024-06-24 17:51 | 0:00 | E/O | 33 kv Circuit breaker damage | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-06-13 06:59 | 2024-06-13 07:09 | 0:10 | T | Due to 33kv Zinzira-1 ans Zinzira-2 faulty | 28 | 4.6667 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-06-24 17:11 | 2024-06-24 17:11 | 0:00 | T | 33 kv zin-2 & Bashundhara ckts fault | 25 | 0 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2024-06-24 17:51 | 2024-06-24 17:51 | 0:00 | E/O | 33 kv Circuit breaker damage | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 LT | 2024-06-06 20:04 | 2024-06-06 20:18 | 0:14 | T | due to 33 kv Zinzira ckt-3 feeder of DPBS-4 fault | 28 | 6.5333 | Power interruption
Hasnabad 132/33kV Grid Substation | 132/33kV 424 T-5 LT | 2024-06-24 17:11 | 2024-06-24 17:50 | 0:39 | T | 33 kv zin-2 & Bashundhara ckts fault | 22 | 14.3 | Power interruption
Madanganj 132/33kV Grid Sub-Station | GT-2 LT | 2024-06-18 22:24 | 2024-06-18 23:29 | 1:05 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-06-14 14:34 | 2024-06-14 16:43 | 2:09 | T | df/dt Trip | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2024-06-11 16:33 | 2024-06-11 17:55 | 1:22 | E/O | TR-3 Underground cable checking | 40 | 54.6667 | Power interruption
Nawabganj 132/33kV Grid Sub-Station | TR-1 HT | 2024-06-10 06:54 | 2024-06-10 07:55 | 1:01 | E/O | Redhot on incommer-01 blue phase | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 HT | 2024-06-01 21:10 | 2024-06-01 21:46 | 0:36 | E/O | Due to Redhot maintenance | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 HT | 2024-06-15 22:06 | 2024-06-15 22:51 | 0:45 | E/O | Shutdown for redhot maintenance. | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2024-06-07 16:44 | 2024-06-07 16:59 | 0:15 | T | Incomer-02 trips due to overcurrent fault in 33 KV Baruakhali feeder. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2024-06-20 12:00 | 2024-06-20 15:17 | 3:17 | T | Trip | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 HT | 2024-06-20 15:36 | 2024-06-20 20:34 | 4:58 | T | Trip | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-07 17:02 | 2024-06-07 17:25 | 0:23 | T | PBS 33kv Meghnaghat, Avarest and Sonargaon feeder fault due to Thunder storm. | 14 | 5.3667 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-13 18:10 | 2024-06-13 19:05 | 0:55 | T | PBS MIEZ feeder Y; B ph line zamper out with CT head cap out. | 24 | 22 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-25 07:39 | 2024-06-25 07:47 | 0:08 | T | PBS Meghnaghat feeder over current fault . | 20 | 2.6667 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2024-06-22 18:20 | 2024-06-22 18:38 | 0:18 | T | 33kv out going Norsingdi feeder fault | 16 | 4.8 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 HT | 2024-06-26 07:47 | 2024-06-26 11:53 | 4:06 | T | Keraniganj ckt-02 yellow phase PT Blast. | 0 | 0 | No interruption
|  |  | Total : | 23:14 |  | Unserved Energy: |  | 135.8333
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2024-06-06 06:08 | 2024-06-06 07:54 | 1:46 | E/O | Red hot maintenance work | 25 | 44.1667 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T LT | 2024-06-07 15:37 | 2024-06-07 17:57 | 2:20 | E/O | Red hot maintenance work | 30 | 70 | Power interruption
Baroirhat 132/33kV Grid Sub-Station | TR-2, 416T HT | 2024-06-06 06:09 | 2024-06-06 07:54 | 1:45 | E/O | Red hot maintenance work | 25 | 43.75 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2024-06-19 15:13 | 2024-06-19 15:24 | 0:11 | T | 33 KV Feeder Failt | 29 | 5.3167 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2024-06-19 16:09 | 2024-06-19 16:12 | 0:03 | T | 33 KV feeder fault | 24 | 1.2 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-06-06 19:21 | 2024-06-06 19:43 | 0:22 | T | Special O/C Protection Operated from hathazari Grid | 75 | 27.5 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2024-06-11 10:40 | 2024-06-11 11:38 | 0:58 | E/O | BPDB GIS incomer cable nut-bolt red hot | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 HT | 2024-06-12 13:01 | 2024-06-13 09:47 | 20:46 | E/O | HT Red Phase Bushing Change & Oil Centrifusing | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) HT | 2024-06-13 05:53 | 2024-06-13 07:02 | 1:09 | E/O | Red -hot maintenance TR-2 primary bushing in R-phase | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 415T (T2) LT | 2024-06-25 07:06 | 2024-06-25 07:34 | 0:28 | T | 33kv Stadium ckt -1 trip | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-06-03 20:46 | 2024-06-03 22:16 | 1:30 | E/O | Mohora-03 33kV feeder red-hot maintenance work of BPDB | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-06-29 19:38 | 2024-06-29 21:21 | 1:43 | T | OLD WASA 33 kv feeder R-phase Loop break | 6 | 10.3 | Power interruption
Rangamati 132/33kV Grid Sub-Station | Main Bus 01 | 2024-06-05 14:36 | 2024-06-05 14:36 | 0:00 | E/O | Bus-1 shutdown due to bird nest cleaning. | 0 | 0 | No interruption
|  |  | Total : | 33:01 |  | Unserved Energy: |  | 202.2333
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 402T LT | 2024-06-18 11:31 | 2024-06-18 12:20 | 0:49 | E/O | 33 Kv bus coupler clamp connector red Hot maintenance work by PDB authority. | 15 | 12.25 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 HT | 2024-06-14 21:12 | 2024-06-14 22:48 | 1:36 | E/O | Emergency red hot maintenance work. | 33 | 52.8 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-2 LT | 2024-06-07 15:34 | 2024-06-07 17:41 | 2:07 | E/O | Red hot maintenance. | 26 | 55.0333 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-3 HT | 2024-06-08 10:48 | 2024-06-08 12:18 | 1:30 | E/O | Red hot maintenance work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2024-06-09 08:30 | 2024-06-09 10:20 | 1:50 | E/O | 33 kv riser DS R phase red hot maintenance. | 25 | 45.8333 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2024-06-29 21:40 | 2024-06-29 23:20 | 1:40 | E/O | 33kv Bus maintenance. | 20 | 33.3333 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 LT | 2024-06-08 11:23 | 2024-06-08 13:41 | 2:18 | E/O | Maintenance work on 33 KV Bus coupler DS-4(Y Phase Clamp) | 30 | 69 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 LT | 2024-06-27 17:48 | 2024-06-27 18:13 | 0:25 | T | 33 KV kotbari feeder fault(PDB) | 40 | 16.6667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 LT | 2024-06-27 17:48 | 2024-06-27 18:13 | 0:25 | T | 33 KV kotbari feeder fault.(PDB) | 40 | 16.6667 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-15 22:01 | 2024-06-16 11:36 | 13:35 | E/O | Red hot maintenance of PBS-3. | 55 | 747.0833 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-06-06 08:36 | 2024-06-06 09:58 | 1:22 | E/O | Taken by pbs-3 for Red Hot maintanence | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Trafo-1 LT | 2024-06-18 15:09 | 2024-06-18 16:46 | 1:37 | E/O | red hot maintenance at 33 kv feeder | 1.5 | 2.425 | Power interruption
|  |  | Total : | 29:14 |  | Unserved Energy: |  | 1051.0917
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2024-06-30 12:42 | 2024-06-30 12:53 | 0:11 | T |  | 12 | 2.2 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-06-11 22:02 | 2024-06-12 00:04 | 2:02 | E/O | 33 kv chandanimahal feeder red hot maintenance work | 15 | 30.5 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2024-06-30 12:42 | 2024-06-30 12:53 | 0:11 | T | Trip | 12 | 2.2 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) HT | 2024-06-27 06:28 | 2024-06-27 07:38 | 1:10 | E/O | Red Hot at Bagachara Feeder | 36 | 42 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-06-22 22:43 | 2024-06-23 02:06 | 3:23 | T | LA blast, B phase 132 kv side. | 26 | 87.9667 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-06-24 21:20 | 2024-06-25 06:23 | 9:03 | T | 132kv LA ( B Phase) Blas.t | 45 | 407.25 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-06-26 10:26 | 2024-06-26 10:49 | 0:23 | E/O | Due to Bus coupler red hot maintenance. | 35 | 13.4167 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-06-30 01:53 | 2024-06-30 08:25 | 6:32 | E/O | 189B DS Y phase contact point flashing | 25 | 163.3333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-26 10:26 | 2024-06-26 10:55 | 0:29 | E/O | Due to Bus coupler red hot maintenance. | 35 | 16.9167 | Power interruption
Borhanuddin 230/33kV Grid Sub-Station | Tr-Load HT | 2024-06-01 15:51 | 2024-06-01 18:06 | 2:15 | E/O | Due to emeregency maint.work | 55 | 123.75 | Power interruption
Borhanuddin 230/33kV Grid Sub-Station | Tr-Load LT | 2024-06-24 14:35 | 2024-06-24 15:15 | 0:40 | E/O | Protection Work. | 50 | 33.3333 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-27 15:08 | 2024-06-27 15:29 | 0:21 | T | 33kv feeder fault. | 33 | 11.55 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-06-27 15:08 | 2024-06-27 19:09 | 4:01 | T | 33kv feeder fault | 33 | 132.55 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-06-01 16:33 | 2024-06-01 17:53 | 1:20 | E/O | Bpbs Red hot maintenance | 20 | 26.6667 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-06-19 17:11 | 2024-06-19 21:09 | 3:58 | T | O/c | 14 | 55.5333 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2024-06-14 06:29 | 2024-06-14 09:54 | 3:25 | E/O | Red hot maintenance | 14 | 47.8333 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Auxiliary Transformer HT | 2024-06-04 11:26 | 2024-06-04 12:16 | 0:50 | E/O | Cable maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-06-16 04:38 | 2024-06-19 11:15 | 78:37 | T | 33 kv Cable burn ( R- phase) | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2024-06-26 12:31 | 2024-06-26 13:44 | 1:13 | E/O | Due to temperature rise of 33 kv loop point | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 LT | 2024-06-21 19:45 | 2024-06-21 23:40 | 3:55 | E/O | Red Hot | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2024-06-12 11:50 | 2024-06-12 12:30 | 0:40 | T | 33KV WZ Feeder fault. | 38 | 25.3333 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2024-06-12 11:50 | 2024-06-12 12:35 | 0:45 | T | 33KV,WZ Feeder fault | 38 | 28.5 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2024-06-02 13:35 | 2024-06-02 14:15 | 0:40 | T | 33kv rampal ckt-1 fault | 25 | 16.6667 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2024-06-29 11:43 | 2024-06-29 13:48 | 2:05 | E/O | 33 kv bus and feeder redhot maintenance | 0.5 | 1.0417 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 LT | 2024-06-20 15:27 | 2024-06-20 17:17 | 1:50 | T | REB-5 33KV Feeder Fault | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2024-06-20 15:27 | 2024-06-20 16:08 | 0:41 | T | REB-5 33KV Feeder Fault | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2024-06-26 20:28 | 2024-06-26 20:28 | 0:00 | E/O | T-3 33kV CB Pole problem | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-06-22 16:20 | 2024-06-26 18:47 | 98:27 | E/O | SF6 Gas Pressure Low | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-06-26 20:36 | 2024-06-26 20:36 | 0:00 | E/O | T-3 33kV CB pole problem. | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-06-25 01:09 | 2024-06-25 01:23 | 0:14 | T | SCADA operation by NLDC | 27 | 6.3 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-25 01:09 | 2024-06-25 01:23 | 0:14 | T | SCADA Operation by NLDC | 27 | 6.3 | Power interruption
|  |  | Total : | 229:35 |  | Unserved Energy: |  | 1281.1417
HVDC Grid Circle :
Chuadanga 132/33kV Grid Sub-Station | 132kV Tr. T3 LT | 2024-06-13 06:17 | 2024-06-13 08:46 | 2:29 | E/O | Due to red hot of T3A | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2024-06-12 06:23 | 2024-06-12 07:18 | 0:55 | E/O | Auxilary transformer (East) oil leakage maintanance | 45 | 41.25 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-06-13 07:06 | 2024-06-13 13:23 | 6:17 | E/O | None | 20 | 125.6667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-06-14 07:21 | 2024-06-14 12:10 | 4:49 | E/O | T1A 33 kv DS Red hot maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T2 HT | 2024-06-03 07:20 | 2024-06-03 09:11 | 1:51 | E/O | 33 kv PBS feeder red hot maintenance | 34 | 62.9 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2024-06-09 20:30 | 2024-06-09 21:38 | 1:08 | E/O | Red-hot Maintenance 33 Kv CB B-phase | 0 | 0 | No interruption
|  |  | Total : | 17:29 |  | Unserved Energy: |  | 229.8167
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132 KV Bus B | 2024-06-28 09:57 | 2024-06-28 11:03 | 1:06 | E/O | Red hot maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2024-06-24 16:35 | 2024-06-24 18:44 | 2:09 | E/O | Red Hot maintenance work. | 40 | 86 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T HT | 2024-06-26 12:23 | 2024-06-26 15:50 | 3:27 | E/O | Emergency Maintenance. | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2024-06-26 00:14 | 2024-06-26 00:14 | 0:00 | T | 33KV R- Phase Cable fault. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | 132KV Bus-A | 2024-06-09 22:50 | 2024-06-09 22:50 | 0:00 | E/O | Bus cupler CT (R-phase) maintenance work | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-06-16 13:07 | 2024-06-16 19:34 | 6:27 | E/O | T-2 132 CB Maintenance Work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-06-24 16:36 | 2024-06-24 17:50 | 1:14 | E/O | T-2 132kV CB Hydraulic oil leakage maintenance work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-06-30 17:37 | 2024-06-30 18:18 | 0:41 | T | For Bogura PBS-2 feeder. which tripped by Inst. O/C, Inst. E/F. | 35 | 23.9167 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 33 KV BUS | 2024-06-19 09:38 | 2024-06-19 11:32 | 1:54 | E/O | Red Hot at 33kv Bus Coupler D/S-2 | 10 | 19 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-06-04 12:32 | 2024-06-04 13:53 | 1:21 | T | 33kv Feeder faultof PBS Jaldhaka and Dommer | 21 | 28.35 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T-1 LT | 2024-06-04 14:53 | 2024-06-04 17:50 | 2:57 | E/O | 33kv Tr_1 Shutdown due to 33kv BUS D/S post Insulator change By PBS Jaldhaka. | 15 | 44.25 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-06-04 12:32 | 2024-06-04 13:30 | 0:58 | T | 33kv Feeder fault PBS Jaldhaka and Dommer. | 21 | 20.3 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-06-04 14:53 | 2024-06-04 17:50 | 2:57 | E/O | 33kv Tr_2 Shutdown due to 33kv BUS D/S post Insulator change By PBS Jaldhaka | 30 | 88.5 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T-2 LT | 2024-06-19 09:38 | 2024-06-19 11:31 | 1:53 | E/O | Red Hot at 33kv Bus Coupler D/S-2. | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) LT | 2024-06-09 19:40 | 2024-06-09 20:40 | 1:00 | E/O | Red hot at LT busing. | 20 | 20 | Power interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-2 (Tr-413T) HT | 2024-06-02 03:23 | 2024-06-02 07:55 | 4:32 | T | No physical fault found | 0 | 0 | No interruption
Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2024-06-29 17:53 | 2024-06-29 18:57 | 1:04 | E/O | Transformer-1 CT Redhot Mainteance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2024-06-07 13:57 | 2024-06-07 14:21 | 0:24 | T | Stormy weather | 37 | 14.8 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2024-06-07 13:57 | 2024-06-07 14:21 | 0:24 | T | Stormy weather | 37 | 14.8 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2024-06-06 01:34 | 2024-06-06 01:43 | 0:09 | T | For Singra 33 kVfeeder foult | 35 | 5.25 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2024-06-06 01:34 | 2024-06-06 01:43 | 0:09 | T | For singra 33kV foult | 35 | 5.25 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) HT | 2024-06-11 16:18 | 2024-06-11 17:57 | 1:39 | E/O | T-3 LT BUS (lochangor feeder) red-hot.So PBS-1S/DT-3 transformer. | 33 | 54.45 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) HT | 2024-06-12 14:41 | 2024-06-12 17:37 | 2:56 | E/O | Due to DC Earth fault. | 0 | 0 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) LT | 2024-06-07 14:58 | 2024-06-07 15:13 | 0:15 | T | Porsha &sapahar feeder faul | 15 | 3.75 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-06-03 22:32 | 2024-06-04 00:04 | 1:32 | E/O | Red hot | 28 | 42.9333 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-06-13 06:00 | 2024-06-13 07:20 | 1:20 | E/O | Red hot | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-06-15 06:42 | 2024-06-15 08:05 | 1:23 | E/O | Deluabari feeder red hot problem Y phase. | 20 | 27.6667 | Power interruption
Palashbari 132/33kV Grid Sub-Station | TR2-404T LT | 2024-06-12 10:55 | 2024-06-12 11:59 | 1:04 | E/O | red hot maintenance | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | TR3-424T HT | 2024-06-11 14:20 | 2024-06-11 15:45 | 1:25 | E/O | 33 kV Bus maintenance of Gaibandha PBS | 10 | 14.1667 | Power interruption
Palashbari 132/33kV Grid Sub-Station | TR4-434T HT | 2024-06-11 14:21 | 2024-06-11 15:46 | 1:25 | E/O | Due to emeregency maint.work | 10 | 14.1667 | Power interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2024-06-16 03:25 | 2024-06-16 11:22 | 7:57 | T | Heavy storm and rain | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2024-06-18 17:04 | 2024-06-18 21:01 | 3:57 | T | TRIP | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) LT | 2024-06-23 11:25 | 2024-06-23 11:59 | 0:34 | E/O | 33kV Balubari feeder incoming isolator Red Hot | 30 | 17 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2024-06-15 04:26 | 2024-06-15 04:58 | 0:32 | T | Bad weather and heavy thundaring. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2024-06-20 09:57 | 2024-06-20 10:20 | 0:23 | T | Due to 33 kV feeder fault | 17 | 6.5167 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2024-06-20 09:57 | 2024-06-20 10:20 | 0:23 | T | Due to 33 kV feeder fault | 17 | 6.5167 | Power interruption
|  |  | Total : | 61:31 |  | Unserved Energy: |  | 557.5833
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 526:04 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-1 | 2024-06-23 11:55 | 2024-06-23 11:55 | 0:00 | T | DC MCB-2 TRIP | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | BR Powergen Ckt- 01 | 2024-06-23 14:34 | 2024-06-23 15:42 | 1:08 | T | TRIp | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 01 | 2024-06-01 14:54 | 2024-06-01 17:34 | 2:40 | E/O | Red hot on LA (Y-phase) | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur Ckt- 01 | 2024-06-19 08:34 | 2024-06-19 08:55 | 0:21 | T | Thundering. | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-1 | 2024-06-10 05:13 | 2024-06-10 05:28 | 0:15 | T | Due to Thundering and strom | 30 | 7.5 | Power interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-1 | 2024-06-12 23:25 | 2024-06-12 23:30 | 0:05 | T | Due to Thundering and strom | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-2 | 2024-06-10 05:13 | 2024-06-10 05:28 | 0:15 | T | Due Thundering and strom | 30 | 7.5 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2024-06-04 18:54 | 2024-06-04 19:01 | 0:07 | T | None | 29 | 3.3833 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2024-06-04 19:13 | 2024-06-05 00:33 | 5:20 | T | TRIp | 29 | 154.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-1 | 2024-06-12 17:10 | 2024-06-12 17:55 | 0:45 | T | TRIp | 50 | 37.5 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-06-09 16:19 | 2024-06-09 16:25 | 0:06 | E/O | crane movement at Ashuganj powerstation | 20 | 2 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-06-09 16:26 | 2024-06-09 16:30 | 0:04 | E/O | crane movement at Ashuganj powerstation | 20 | 1.3333 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-06-28 11:57 | 2024-06-28 21:33 | 9:36 | E/O | work at ashuganj s/s | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Bhaluka Ckt-1 | 2024-06-29 12:13 | 2024-06-29 12:22 | 0:09 | T | Heavy thunderstorms | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Netrakona Ckt-1 | 2024-06-18 07:25 | 2024-06-18 11:03 | 3:38 | T | Rain and heavy Thandaring | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-06-05 14:55 | 2024-06-05 17:51 | 2:56 | E/O | To clear object from line. Shutdown taken by joydevpur s/s. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2024-06-20 12:26 | 2024-06-20 13:05 | 0:39 | T | Thunderstorm | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2024-06-19 08:33 | 2024-06-19 08:52 | 0:19 | T | unknown | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2024-06-02 11:28 | 2024-06-02 11:38 | 0:10 | T | Heavy wind. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2024-06-02 22:19 | 2024-06-02 22:52 | 0:33 | T | TRIp | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2024-06-10 07:38 | 2024-06-10 07:48 | 0:10 | T | TRIp | 0 | 0 | No interruption
|  |  | Total : | 29:16 |  | Unserved Energy: |  | 213.8833
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-06-29 10:57 | 2024-06-29 14:19 | 3:22 | T | due to heavy rain | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-06-30 15:07 | 2024-06-30 20:51 | 5:44 | T |  | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2024-06-04 16:32 | 2024-06-04 16:59 | 0:27 | T | Rainfall. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-06-07 16:16 | 2024-06-07 20:13 | 3:57 | T | Rainy weather. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Nawabganj-2 | 2024-06-13 17:49 | 2024-06-13 18:39 | 0:50 | T | Zone-1 11.5 km trip,Relay Trip,AR Blocked | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Srinagar-2 | 2024-06-26 07:47 | 2024-06-26 07:47 | 0:00 | T | due to PT blast at Srinagar End | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Bashundhara 132 kv Ckt | 2024-06-12 10:03 | 2024-06-12 11:31 | 1:28 | E/O | Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -DPDC Char sayedpur 132k Ckt-1 | 2024-06-12 17:32 | 2024-06-12 20:07 | 2:35 | E/O | Red hot maintenance char-soyedpur ss end | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-06-29 12:02 | 2024-06-29 14:20 | 2:18 | E/O | Overload of 132 KV Hasnabad-Shitalakhya ckt | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2024-06-30 15:10 | 2024-06-30 20:52 | 5:42 | E/O | Overload of 132 KV Hasnabad - Shitalakhya ckt | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-06-29 10:57 | 2024-06-29 14:19 | 3:22 | T | TRIp | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-06-30 15:07 | 2024-06-30 20:52 | 5:45 | T | TRIp | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-06-02 15:41 | 2024-06-02 15:41 | 0:00 | T | TRIp | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-2 | 2024-06-10 08:58 | 2024-06-10 10:35 | 1:37 | E/O | Narinda ckt 2 cable flute maintenance. | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Madunaghat 400KV Ckt-2 | 2024-06-17 09:23 | 2024-06-17 15:26 | 6:03 | E/O | by NLDC | 28 | 169.4 | Power interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Madunaghat 400KV Ckt-2 | 2024-06-19 13:46 | 2024-06-19 15:36 | 1:50 | T | Heavy Rain Fail with Storm | 50 | 91.6667 | Power interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2024-06-11 06:11 | 2024-06-11 11:10 | 4:59 | E/O | Red hot Maintenance at Basundhara End ss. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2024-06-08 17:57 | 2024-06-08 19:48 | 1:51 | E/O | NLDC | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Digital Powerplant | 2024-06-24 06:31 | 2024-06-24 06:57 | 0:26 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-06-05 08:32 | 2024-06-06 19:01 | 34:29 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2024-06-03 08:53 | 2024-06-03 10:59 | 2:06 | E/O | Maintenances work in Siddhirganj 230kv Ends. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-02(Powerpac) | 2024-06-26 07:47 | 2024-06-26 07:47 | 0:00 | T | Keraniganj ckt-02 Y phase PT Blast. | 0 | 0 | No interruption
|  |  | Total : | 88:51 |  | Unserved Energy: |  | 261.0667
Chattogram Grid Circle :
AKS 132/33kV Grid Sub-Station | Khulshi | 2024-06-25 23:45 | 2024-06-26 14:58 | 15:13 | T | PT blast of Khulshi end. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2024-06-19 12:15 | 2024-06-19 12:37 | 0:22 | T | Distance trip Phase B | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-06-24 10:01 | 2024-06-24 10:21 | 0:20 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-06-28 06:06 | 2024-06-28 09:12 | 3:06 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2024-06-28 06:11 | 2024-06-28 09:12 | 3:01 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2024-06-15 17:29 | 2024-06-15 18:11 | 0:42 | E/O | Emergency Tree Trimming | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-06-19 20:54 | 2024-06-19 21:18 | 0:24 | T | Zone-1, R-phase,general trip. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2024-06-18 22:06 | 2024-06-18 22:37 | 0:31 | T | TRIp | 8 | 4.1333 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2024-06-18 22:06 | 2024-06-18 22:37 | 0:31 | T | rain, Thunderstome. | 8 | 4.1333 | Power interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2024-06-19 11:18 | 2024-06-19 11:36 | 0:18 | E/O | s/d | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-1 | 2024-06-28 05:52 | 2024-06-28 09:12 | 3:20 | E/O | hathazari grid bus maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2024-06-28 05:53 | 2024-06-28 09:12 | 3:19 | E/O | hathazari grid bus maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2024-06-24 09:53 | 2024-06-28 05:55 | 92:02 | E/O | The breaker operated with the Instructions of the NLDC SDE. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2024-06-25 23:42 | 2024-06-26 00:05 | 0:23 | T | Due to PT Burst at khulshi-AKSPL Line | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2024-06-21 13:02 | 2024-06-21 16:17 | 3:15 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Intermediate-2 | 2024-06-06 10:21 | 2024-06-06 11:19 | 0:58 | T | TRIp | 0 | 0 | No interruption
|  |  | Total : | 127:45 |  | Unserved Energy: |  | 8.2667
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | Sylhet-Fenchugang -T -Branibazar-1 | 2024-06-17 11:51 | 2024-06-17 12:02 | 0:11 | T | For heavy rain | 40 | 7.3333 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Narsingdi Circuit-1 | 2024-06-30 10:01 | 2024-06-30 10:27 | 0:26 | T | TRIp | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2024-06-09 14:37 | 2024-06-09 15:46 | 1:09 | E/O | Sticking the kite tower top (178no.). | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2024-06-18 11:57 | 2024-06-18 12:16 | 0:19 | T | TRIp | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2024-06-21 11:50 | 2024-06-21 12:13 | 0:23 | T | TRIp | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-06-10 07:25 | 2024-06-10 08:09 | 0:44 | T | Bad Weather | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-06-17 11:53 | 2024-06-17 12:03 | 0:10 | T | Thunderstorm, rainy weather | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2024-06-11 17:08 | 2024-06-11 17:17 | 0:09 | T | Un known | 28 | 4.2 | Power interruption
Kulaura 132/33kV Grid Sub-Station | 132 Fenchuganj-1 | 2024-06-30 09:40 | 2024-06-30 10:24 | 0:44 | T | TRIp | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2024-06-12 10:24 | 2024-06-12 11:33 | 1:09 | E/O | Ashuganj S/S Line Bay Maintenece | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2024-06-17 11:51 | 2024-06-17 12:06 | 0:15 | T | no | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2024-06-14 09:53 | 2024-06-14 13:18 | 3:25 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2024-06-17 11:51 | 2024-06-17 12:06 | 0:15 | T | no | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-06-17 04:18 | 2024-06-17 04:38 | 0:20 | T | Bad Weather and Thunderstom | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2024-06-17 05:23 | 2024-06-17 05:43 | 0:20 | T | Bad Weather | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-06-17 04:22 | 2024-06-17 04:45 | 0:23 | T | Bad Weather and Thunderstom | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-2 | 2024-06-17 05:23 | 2024-06-17 05:39 | 0:16 | T | Bad Weather | 0 | 0 | No interruption
Sylhet (South) 132/33kV GIS Grid Sub-Station | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2024-06-17 11:53 | 2024-06-17 12:02 | 0:09 | T | trip | 40 | 6 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2024-06-17 05:43 | 2024-06-17 05:51 | 0:08 | T | trip | 4 | 0.53333 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-06-12 02:32 | 2024-06-12 02:44 | 0:12 | T | Thundering and Raining | 64 | 12.8 | Power interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2024-06-17 05:22 | 2024-06-17 05:37 | 0:15 | T | trip | 0 | 0 | No interruption
|  |  | Total : | 11:22 |  | Unserved Energy: |  | 30.8667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-06-13 06:36 | 2024-06-13 07:13 | 0:37 | T | Unknown | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-06-19 21:07 | 2024-06-19 23:25 | 2:18 | E/O | OCB CLAMP R PHASE RED HOT MAINTENANCE WORKS. | 40 | 92 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2024-06-22 22:18 | 2024-06-22 22:28 | 0:10 | T | Unknown | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | Madaripur ckt-01 | 2024-06-30 12:59 | 2024-06-30 13:07 | 0:08 | T | Rainy Weather | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Bagerhat (L3) | 2024-06-26 07:08 | 2024-06-26 10:45 | 3:37 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Bagerhat (L3) | 2024-06-26 14:05 | 2024-06-26 14:06 | 0:01 | E/O | Due to power received from Barishal by Bus coupler | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Bagerhat | 2024-06-16 18:22 | 2024-06-16 19:03 | 0:41 | T | Zone -1,24KM,Phase -ab, 3-phase trip No E/F, No O/C trip | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2024-06-20 18:13 | 2024-06-20 19:23 | 1:10 | E/O | LA Change ( Y- Phase) KPCL end. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-1 | 2024-06-20 13:36 | 2024-06-20 14:04 | 0:28 | T | None | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Magura 2 | 2024-06-29 12:07 | 2024-06-29 13:45 | 1:38 | E/O | A kites found in Magura ckt-02 between Y & B phase. | 0 | 0 | No interruption
|  |  | Total : | 10:48 |  | Unserved Energy: |  | 92
HVDC Grid Circle :
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2024-06-06 01:29 | 2024-06-06 01:52 | 0:23 | T | trip | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 2 | 2024-06-30 13:06 | 2024-06-30 17:17 | 4:11 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-1(L2) | 2024-06-05 07:06 | 2024-06-05 09:36 | 2:30 | E/O | Jhenaidah 230 kv T1-xformer overloaded due to T2-xformer shutdown. | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | JH-2(L1) | 2024-06-05 07:09 | 2024-06-05 09:36 | 2:27 | E/O | Jhenaidah 230 kv T1-xformer overloaded due to T2-xformer shutdown. | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2024-06-12 05:49 | 2024-06-12 07:28 | 1:39 | E/O | Redhot Maintanance For Noapara End | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2024-06-26 14:42 | 2024-06-26 15:27 | 0:45 | E/O | Due to kite tying in Noapara CKT-1 | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2024-06-12 07:31 | 2024-06-12 08:41 | 1:10 | E/O | Redhot Maintanance For Noapara End | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2024-06-05 07:14 | 2024-06-05 09:34 | 2:20 | E/O | As per order of ALDC | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-2 | 2024-06-05 07:14 | 2024-06-05 09:34 | 2:20 | E/O | As per order of ALDC | 0 | 0 | No interruption
|  |  | Total : | 17:45 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt1 | 2024-06-16 03:26 | 2024-06-16 04:14 | 0:48 | T | Thunderstorm | 60 | 48 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt1 | 2024-06-18 04:41 | 2024-06-18 04:54 | 0:13 | T | trip | 40 | 8.6667 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt2 | 2024-06-16 03:26 | 2024-06-16 04:16 | 0:50 | T | Thunderstorm | 60 | 50 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2024-06-15 04:26 | 2024-06-15 04:44 | 0:18 | T | Auto reclose operated | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2024-06-18 04:38 | 2024-06-18 06:38 | 2:00 | T | trip | 35 | 70 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt2 | 2024-06-18 04:38 | 2024-06-18 06:38 | 2:00 | T | trip | 35 | 70 | Power interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-2 | 2024-06-16 11:01 | 2024-06-16 11:33 | 0:32 | T | trip | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Serajganj Line-2 | 2024-06-19 08:50 | 2024-06-19 15:38 | 6:48 | E/O | Forced Shutdown | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2024-06-18 04:46 | 2024-06-18 05:15 | 0:29 | T | trip | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-06-29 05:23 | 2024-06-29 05:52 | 0:29 | T | Trip | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-06-30 17:51 | 2024-06-30 17:51 | 0:00 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | Thakurgaon-1 | 2024-06-18 04:35 | 2024-06-18 06:15 | 1:40 | T | N/A | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2024-06-06 01:29 | 2024-06-06 01:57 | 0:28 | T | thundering | 50 | 23.3333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2024-06-20 02:54 | 2024-06-20 03:18 | 0:24 | T | None | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2024-06-20 03:21 | 2024-06-20 06:18 | 2:57 | T | trip | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2024-06-29 13:48 | 2024-06-29 14:04 | 0:16 | T | thundering | 50 | 13.3333 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2024-06-06 01:29 | 2024-06-06 01:47 | 0:18 | T | thundering | 50 | 15 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2024-06-21 19:52 | 2024-06-21 20:03 | 0:11 | T | trip | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2024-06-29 13:48 | 2024-06-29 14:06 | 0:18 | T | trip | 50 | 15 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-1 | 2024-06-27 14:36 | 2024-06-27 15:13 | 0:37 | T | pt mcb trip | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Kurigram | 2024-06-16 04:00 | 2024-06-16 04:09 | 0:09 | T | Thundering | 15 | 2.25 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Kurigram | 2024-06-19 01:30 | 2024-06-19 01:44 | 0:14 | T | R phase Y phase zone 1 Block air signal show | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Lalmonirhat | 2024-06-16 03:40 | 2024-06-16 04:01 | 0:21 | T | Thundering | 30 | 10.5 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2024-06-15 04:26 | 2024-06-15 04:44 | 0:18 | T | Bad weather and heavy thundaring. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2024-06-18 04:38 | 2024-06-18 06:37 | 1:59 | T | Heavy thundering and rain fall | 30 | 59.5 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Jaldhaka CKT-01 | 2024-06-30 07:36 | 2024-06-30 07:56 | 0:20 | T | trip | 22 | 7.3333 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Jaldhaka CKT-02 | 2024-06-30 07:36 | 2024-06-30 07:57 | 0:21 | T | trip | 22 | 7.7 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Purbosadipur CKT-02 | 2024-06-15 04:14 | 2024-06-15 04:54 | 0:40 | T | Bad weather and heavy rain as well as thundaring. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2024-06-11 04:57 | 2024-06-11 05:30 | 0:33 | T | trip | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Solar Park 1 | 2024-06-21 17:15 | 2024-06-21 21:23 | 4:08 | T | Due to Differential test at plant site. | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Bogura -02 | 2024-06-18 09:38 | 2024-06-18 17:22 | 7:44 | E/O | Emergency Maintenance Work | 0 | 0 | No interruption
Sirajgonj 230 kV Switching Station | Sreepur-02 | 2024-06-20 12:27 | 2024-06-20 13:04 | 0:37 | T | Line to Neutral Fault | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Panchagar CKT-1 | 2024-06-26 05:55 | 2024-06-26 06:15 | 0:20 | T | Tripped showing Distance Relay relays | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-1 | 2024-06-18 04:35 | 2024-06-18 04:54 | 0:19 | T | N/A | 11 | 3.4833 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-1 | 2024-06-18 04:56 | 2024-06-18 06:16 | 1:20 | T | High Voltage | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-2 | 2024-06-21 19:52 | 2024-06-21 20:03 | 0:11 | T | Distance Relay (Zone-1) | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-2 | 2024-06-18 04:56 | 2024-06-18 06:30 | 1:34 | T | High voltage | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Thakurgaon-EPV Ckt-2 | 2024-06-22 09:50 | 2024-06-22 10:12 | 0:22 | T | trip | 107 | 39.2333 | Power interruption
|  |  | Total : | 43:06 |  | Unserved Energy: |  | 443.3333
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 328:53 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: June 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | 132kV Transformer-1 (405T1) LT | 2024-06-15 07:07 | 2024-06-15 11:53 | 4:46 | S/O | Shutdown due to PRD & OSR's Plastic Pipe replaced with SS Pipe | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2024-06-23 07:16 | 2024-06-24 15:51 | 32:35 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-06-22 09:27 | 2024-06-22 17:52 | 8:25 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2024-06-24 16:25 | 2024-06-24 17:38 | 1:13 | S/O | Conductor Change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 02 | 2024-06-12 07:05 | 2024-06-12 18:20 | 11:15 | S/O | PT changed | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 HT | 2024-06-22 09:31 | 2024-06-24 17:30 | 55:59 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan HT | 2024-06-09 08:11 | 2024-06-09 16:58 | 8:47 | D/W | GIS Project Work | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2024-06-08 07:07 | 2024-06-08 12:55 | 5:48 | S/O | PBS Works | 50 | 290 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2024-06-08 07:38 | 2024-06-08 09:15 | 1:37 | S/O | 33 kv T1& T2 bus section D/S maintenance work | 35 | 56.5833 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2024-06-08 07:38 | 2024-06-08 09:15 | 1:37 | S/O | 33 kv T1& T2 bus section D/S maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2024-06-25 21:04 | 2024-06-25 22:18 | 1:14 | S/O | 33Kv bus coupler DS joint point Red hot | 30 | 37 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2024-06-07 06:42 | 2024-06-07 11:22 | 4:40 | S/O | High temperature maintenance work 33 KV TR-2 bus DS R phase. | 70 | 326.6667 | Power interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2024-06-14 07:26 | 2024-06-14 11:06 | 3:40 | S/O | Oil leakage remove | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2024-06-20 09:07 | 2024-06-20 11:27 | 2:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2024-06-07 06:08 | 2024-06-07 08:46 | 2:38 | S/O | Redhot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-06-10 07:22 | 2024-06-10 09:53 | 2:31 | S/O | LT side Red hot maintenance | 17 | 42.7833 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-06-26 06:40 | 2024-06-26 18:05 | 11:25 | D/W | 400kV GNDP project work | 10 | 114.1667 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-06-29 06:39 | 2024-06-29 18:10 | 11:31 | D/W | Due to project work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2024-06-30 13:22 | 2024-06-30 16:51 | 3:29 | D/W | 400kV GNDP project work. | 15 | 52.25 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-06-27 06:11 | 2024-06-27 15:12 | 9:01 | D/W | Project work | 20 | 180.3333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2024-06-28 07:42 | 2024-06-28 18:20 | 10:38 | D/W | Project work | 15 | 159.5 | Power interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2024-06-27 06:50 | 2024-06-29 08:55 | 50:05 | D/W | 132kV CB Replacement Work | 0 | 0 | No interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Transformer-02(E07) LT | 2024-06-01 10:43 | 2024-06-01 15:23 | 4:40 | D/W | 33 KV AVR Configuration | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2024-06-07 03:27 | 2024-06-07 12:32 | 9:05 | S/O | For T-4 Transformer installation work by CCCE. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2024-06-07 03:27 | 2024-06-07 12:32 | 9:05 | S/O | For T-4 Transformer installation work by CCCE. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Main Bus | 2024-06-07 03:30 | 2024-06-07 12:29 | 8:59 | S/O | For T-4 Transformer installation work by CCCE. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 HT | 2024-06-29 07:08 | 2024-06-29 12:42 | 5:34 | S/O | Buchholz relay replacement work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Transfer Bus | 2024-06-07 03:30 | 2024-06-07 12:29 | 8:59 | S/O | For T-4 Transformer installation work by CCCE. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-06-03 08:03 | 2024-06-03 19:21 | 11:18 | D/W | Project work | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2024-06-12 07:24 | 2024-06-12 21:31 | 14:07 | S/O | Relay Replacement works. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 HT | 2024-06-03 08:04 | 2024-06-03 19:27 | 11:23 | D/W | Project work | 5 | 56.9167 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 HT | 2024-06-11 13:24 | 2024-06-12 00:56 | 11:32 | S/O | Relay unbalance current maintenance work | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 2024-06-28 08:19 | 2024-06-28 09:17 | 0:58 | S/O | Change Isolator of auxiliary transformer(33/.440 kV) | 30 | 29 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2024-06-16 18:02 | 2024-06-16 18:02 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 340:54 |  | Unserved Energy: |  | 1345.2
Dhaka (South) Grid Circle : | [9 empty] | 39.3333
Bhulta 132/33kV Grid Sub-Station | GT1 LT | 2024-06-20 10:41 | 2024-06-20 11:47 | 1:06 | S/O | Red hot maintenance work at HT/LT bushing clamp | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2024-06-20 08:29 | 2024-06-20 08:59 | 0:30 | S/O | Red hot maintenance work on HT/LT bushing clamp | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 LT | 2024-06-08 10:21 | 2024-06-14 18:14 | 151:53 | S/O | Oil Centrifuzing Work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Auto TR-3 LT | 2024-06-23 10:06 | 2024-06-27 09:36 | 95:30 | S/O | Oil centrifuzing. | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | 33kv Main Bus | 2024-06-11 11:02 | 2024-06-11 12:49 | 1:47 | S/O | Nowabganj-01 33 kv feeder main bus R phase loop conductor joint point maintenance. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-1 | 2024-06-08 08:41 | 2024-06-08 12:54 | 4:13 | S/O | DS-811M high temperature found. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Bus-2 | 2024-06-03 09:54 | 2024-06-03 13:20 | 3:26 | S/O | Tripping test. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 HT | 2024-06-03 14:21 | 2024-06-03 21:10 | 6:49 | S/O | High temparature maintenance. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 LT | 2024-06-03 10:33 | 2024-06-03 14:10 | 3:37 | S/O | High Temperature Maintenance work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-2 HT | 2024-06-14 09:24 | 2024-06-14 11:37 | 2:13 | S/O | Taken by DPDC according to instructions by NLDC. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-2 HT | 2024-06-28 07:42 | 2024-06-28 14:33 | 6:51 | S/O | Maintenance works to 33kv bus. (33Kv bus problem.) | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2024-06-22 07:09 | 2024-06-22 07:51 | 0:42 | S/O | T-1 33 kV Tertiary Loop connection with 230/132 kV Transformer-1. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 HT | 2024-06-04 04:35 | 2024-06-04 06:59 | 2:24 | S/O | The high temperature at the R-ph arm box at DS721S. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 HT | 2024-06-21 23:42 | 2024-06-21 23:46 | 0:04 | S/O | Transformer (TX-1)carrying. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2024-06-03 08:52 | 2024-06-03 11:00 | 2:08 | S/O | Red hot | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-24 09:31 | 2024-06-24 16:08 | 6:37 | S/O | T-01 33 kv Y Phase CT oil leakage corrective maintenance work purpose. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2024-06-27 07:17 | 2024-06-27 14:41 | 7:24 | S/O | Y-ph CT replacement | 0 | 0 | No interruption
|  |  | Total : | 297:14 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2024-06-18 06:28 | 2024-06-18 08:13 | 1:45 | S/O |  | 51 | 89.25 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2024-06-16 02:14 | 2024-06-16 02:57 | 0:43 | S/O | REDHOT Maintenance by Lohagara & Chandanaish PBS | 60 | 43 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2024-06-16 09:31 | 2024-06-16 12:25 | 2:54 | S/O | Transformer Inspection. | 0 | 0 | No interruption
GPH 230/33kV Grid Sub-Station | Transformer-01(D05) HT | 2024-06-16 12:35 | 2024-06-16 13:43 | 1:08 | S/O | Inspection Work | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | 132KV MAIN BUS-01 | 2024-06-28 06:25 | 2024-06-28 09:05 | 2:40 | D/W | Loop disconnect | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2024-06-02 05:31 | 2024-06-02 07:33 | 2:02 | S/O | corrective maintenance | 15 | 30.5 | Power interruption
Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2024-06-02 05:40 | 2024-06-02 07:56 | 2:16 | S/O | corrective maintenance | 15 | 34 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | T-2 33kV BUS | 2024-06-01 10:47 | 2024-06-01 12:12 | 1:25 | S/O | Mohora-03 33kV feeder red-hot maintenance work of BPDB | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) HT | 2024-06-13 08:58 | 2024-06-13 12:16 | 3:18 | S/O | BPDB à¦•à¦°à§à¦¤à§ƒà¦• Tr-01 à¦à¦° à¦¬à¦¾à¦¸ -à§¦à§§ à¦à¦° Maintenance à¦•à¦¾à¦œà§‡à¦° à¦œà¦¨à§à¦¯ | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2024-06-29 22:40 | 2024-06-29 23:23 | 0:43 | S/O | Mohora-3 ,33kV feeder redhot Maintenance. | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Bus-1 | 2024-06-07 06:52 | 2024-06-07 09:10 | 2:18 | D/W | Transformer 02 Circuit breaker commissioning and testing under G2G project. | 35 | 80.5 | Power interruption
|  |  | Total : | 21:12 |  |  |  | 277.25
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2024-06-06 07:02 | 2024-06-06 10:56 | 3:54 | S/O | Shutdown taken by AE PDB distribution | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2024-06-08 06:10 | 2024-06-08 14:10 | 8:00 | S/O | Maintenance work by PBS | 30 | 240 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2024-06-11 05:57 | 2024-06-11 12:30 | 6:33 | S/O | Shutdown taken for red hot maintenance | 20 | 131 | Power interruption
Chandpur 132/33kV Grid Sub-Station | Bus A | 2024-06-04 07:06 | 2024-06-04 12:27 | 5:21 | S/O | Maintenance work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2024-06-20 12:27 | 2024-06-20 13:28 | 1:01 | S/O | 33KV B-para feeder red hot | 60 | 61 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2024-06-21 09:50 | 2024-06-21 11:19 | 1:29 | S/O | 33 KV Summit Feeder Bus DS Red Hot Remove. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-05 HT | 2024-06-20 13:32 | 2024-06-20 14:19 | 0:47 | S/O | Pbs Bus coupler DS Y phase red hot remove | 30 | 23.5 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 LT | 2024-06-08 09:08 | 2024-06-08 19:47 | 10:39 | S/O | Control Cable Re-winding | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2024-06-26 06:49 | 2024-06-26 08:16 | 1:27 | S/O | None | 43 | 62.35 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2024-06-12 08:10 | 2024-06-12 10:29 | 2:19 | S/O | Hot point Maintenance. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-25 08:10 | 2024-06-25 14:59 | 6:49 | S/O | Hot point Maintenance. | 40 | 272.6667 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | 132 KV Bus-2 | 2024-06-04 15:03 | 2024-06-04 16:33 | 1:30 | S/O | G2G project works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-06-04 14:43 | 2024-06-04 17:11 | 2:28 | D/W | G2G Project Work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-06-22 10:59 | 2024-06-22 14:55 | 3:56 | S/O | T-2 A oil leakage maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2024-06-23 09:46 | 2024-06-23 16:20 | 6:34 | S/O | Bowring grounding work. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-06-06 08:21 | 2024-06-06 09:37 | 1:16 | S/O | For Transformer Bay Maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-06-07 07:03 | 2024-06-07 11:22 | 4:19 | S/O | 33KV Bus -01 S/D taken by BPDB for 33/11KV New GIS Substation Inconer work. | 10 | 43.1667 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2024-06-12 07:02 | 2024-06-12 10:15 | 3:13 | S/O | 33 kv Bus section DS Maintenance of BPDB | 24 | 77.2 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2024-06-25 09:46 | 2024-06-25 10:11 | 0:25 | S/O | To load Control by NLDC. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-06-08 07:45 | 2024-06-08 10:37 | 2:52 | S/O | work by pdb 33 kv bus | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2024-06-12 07:03 | 2024-06-12 09:07 | 2:04 | S/O | 33 kv bus section DS Maintenance of BPDB | 69 | 142.6 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2024-06-13 11:41 | 2024-06-13 17:08 | 5:27 | S/O | For development work | 0 | 0 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2024-06-14 08:06 | 2024-06-14 08:47 | 0:41 | S/O | hot spot maintenance | 20 | 13.6667 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 HT | 2024-06-14 06:18 | 2024-06-14 07:47 | 1:29 | S/O | hot spot maintenance | 15 | 22.25 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2024-06-06 07:02 | 2024-06-06 07:54 | 0:52 | S/O | BPDB Red Hot maintenece work | 35 | 30.3333 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-06-11 22:03 | 2024-06-11 23:17 | 1:14 | S/O | Shutdown taken by PBS for 33KV Feeder D/S Maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2024-06-30 21:06 | 2024-06-30 22:14 | 1:08 | S/O | Madhabpur 01 isolator red hot maintenance by PBS | 43 | 48.7333 | Power interruption
|  |  | Total : | 87:47 |  | Unserved Energy: |  | 1168.4667
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2024-06-13 07:07 | 2024-06-13 11:03 | 3:56 | S/O | High temperature on 132 kV side at Y phase DS loop. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2024-06-14 09:01 | 2024-06-14 12:36 | 3:35 | S/O | Babignj 33kV Source DS R phase maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2024-06-14 06:36 | 2024-06-14 12:37 | 6:01 | S/O | Banaripara 33kV source DS R&B Red hot maintenanace | 24 | 144.4 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-06-02 06:34 | 2024-06-02 09:31 | 2:57 | D/W | WZPDCL aux- x- former installation | 5 | 14.75 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-06-12 04:35 | 2024-06-12 08:06 | 3:31 | D/W | Due to project work | 54 | 189.9 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2024-06-29 05:56 | 2024-06-29 11:52 | 5:56 | D/W | Damage Radiator re connecting by CCCE , under G2G Project. | 30 | 178 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 HT | 2024-06-12 04:38 | 2024-06-12 07:59 | 3:21 | D/W | Due to project work | 54 | 180.9 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2024-06-01 06:38 | 2024-06-01 08:38 | 2:00 | S/O | High Temperature maintenance of 33 kv Bus DS clapm for Section 1 . | 35 | 70 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-15 06:43 | 2024-06-15 09:53 | 3:10 | S/O | Hot Spot Maintenance | 45 | 142.5 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2024-06-04 07:32 | 2024-06-04 11:14 | 3:42 | S/O | new feeder Installation. | 5 | 18.5 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2024-06-04 07:32 | 2024-06-04 11:18 | 3:46 | S/O | new feeder Installation. | 5 | 18.8333 | Power interruption
Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2024-06-08 06:40 | 2024-06-08 06:59 | 0:19 | S/O | shutdown by WZPDCL | 15 | 4.75 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2024-06-21 06:40 | 2024-06-21 09:09 | 2:29 | S/O | BPBS-1 Red hot maintenance. | 15 | 37.25 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 HT | 2024-06-20 07:04 | 2024-06-20 09:34 | 2:30 | S/O | 33 kv REB-3 wire change. | 35 | 87.5 | Power interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2024-06-03 10:44 | 2024-06-03 21:20 | 10:36 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 2 | 2024-06-06 09:32 | 2024-06-06 21:28 | 11:56 | D/W | Due to project work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2024-06-01 07:24 | 2024-06-01 08:47 | 1:23 | S/O | Khoaspur 33kv feeder red hot maintenance | 15 | 20.75 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-1 HT | 2024-06-22 16:32 | 2024-06-22 18:20 | 1:48 | S/O | REB-5 33kV Feeder Maintenance. | 17 | 30.6 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2024-06-11 12:47 | 2024-06-13 14:25 | 49:38 | S/O | Energy meter change | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-13 06:18 | 2024-06-13 08:18 | 2:00 | S/O | WZPDCL new feeder loop connection. | 3 | 6 | Power interruption
|  |  | Total : | 124:34 |  | Unserved Energy : |  | 1144.6333
HVDC Grid Circle
BIPTC | 21T01 LT | 2024-06-14 05:29 | 2024-06-14 12:44 | 7:15 | S/O | Due to maint.work | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2024-06-03 10:52 | 2024-06-03 17:49 | 6:57 | S/O | Due to maint.work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2024-06-10 06:24 | 2024-06-10 08:03 | 1:39 | S/O | Auxiliary Tx (East) Oil Leakage Maintenance | 42 | 69.3 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2024-06-16 06:01 | 2024-06-16 07:24 | 1:23 | S/O | 33KV CT C Phase Redhot Maintenance | 60 | 83 | Power interruption
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 LT | 2024-06-05 07:18 | 2024-06-05 09:16 | 1:58 | S/O | Emergency Maintenance | 0 | 0 | No interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2024-06-29 09:23 | 2024-06-29 12:23 | 3:00 | S/O | Schedule maintenance | 25 | 75 | Power interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2024-06-04 14:17 | 2024-06-04 14:41 | 0:24 | D/W | Power flow direction change at 33kV CRP panel. | 0 | 0 | No interruption
Ullahpara 132/33kV Grid Sub-Station | Power Transformer-2 LT | 2024-06-29 11:15 | 2024-06-29 12:00 | 0:45 | S/O | PBS on request | 0 | 0 | No interruption
|  |  | Total : | 23:21 |  | Unserved Energy : |  | 227.3
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2024-06-15 09:05 | 2024-06-15 10:48 | 1:43 | S/O | Red hot maintenance of 33kV NESCO Feeder. | 48 | 82.4 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2024-06-22 07:44 | 2024-06-22 20:10 | 12:26 | S/O | CB pump problem | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2024-06-01 10:25 | 2024-06-01 21:20 | 10:55 | D/W | 230kV Bogura(W) Ckt.-1 & Ckt.-2 Commissioning work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-06-02 14:56 | 2024-06-02 21:28 | 6:32 | S/O | Project Work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2024-06-06 17:32 | 2024-06-06 17:49 | 0:17 | D/W | Bogura(W) ckt1&2 commissioning . | 0 | 0 | No interruption
Bogura 400/230kV Grid Sub-Station | ATR-03 LT | 2024-06-27 08:28 | 2024-06-27 14:59 | 6:31 | S/O | CSD Commissioning work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) LT | 2024-06-02 08:17 | 2024-06-02 18:47 | 10:30 | S/O | 33kv incomer ds control cable connection and open close stats rectification | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) HT | 2024-06-26 08:20 | 2024-06-26 20:25 | 12:05 | S/O | Due to maint.work | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2024-06-11 00:40 | 2024-06-11 00:57 | 0:17 | S/O | Due to GIS Switching station work of NESCO, Rajshahi. | 25 | 7.0833 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2024-06-24 08:27 | 2024-06-24 18:45 | 10:18 | S/O | T-04 # shutdown is required due to 33 kvi ncomer D/S control cable & junction box installation in order to open close status rectification in crp panel . T-04 # load will will be served by T-02 & T-03 # .there will be no load shed | 0 | 0 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-1 425T HT | 2024-06-25 07:02 | 2024-06-25 08:25 | 1:23 | S/O | T-1 33KV Busbar Red Hot Maintenance | 27 | 37.35 | Power interruption
Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2024-06-06 08:34 | 2024-06-06 11:36 | 3:02 | S/O | Kalai Feder Maintenance | 15 | 45.5 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2024-06-14 07:05 | 2024-06-14 10:07 | 3:02 | S/O | 33kV Bus Maintenance by NPBS-1. | 45 | 136.5 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) LT | 2024-06-14 07:05 | 2024-06-14 10:08 | 3:03 | S/O | 33kV Bus Maintenance by NPBS-1. | 45 | 137.25 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) HT | 2024-06-14 10:28 | 2024-06-14 11:45 | 1:17 | S/O | LT D/S Post insulator change | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Main Bus | 2024-06-30 15:10 | 2024-06-30 16:55 | 1:45 | S/O | Bus bar scheme change | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) HT | 2024-06-04 08:19 | 2024-06-05 09:52 | 25:33 | S/O | 132 kV Bus bar scheme change | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) HT | 2024-06-11 09:28 | 2024-06-11 15:39 | 6:11 | D/W | 132 kv busbar modification | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-1(407T) HT | 2024-06-30 09:20 | 2024-06-30 13:15 | 3:55 | S/O | Transformer T-1 shutdown due to busbar relay configuration for 132 kv busbar scheme | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) HT | 2024-06-05 10:13 | 2024-06-05 17:41 | 7:28 | S/O | Project work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-06-05 10:12 | 2024-06-05 10:12 | 0:00 | S/O | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-2 (417T) LT | 2024-06-11 15:42 | 2024-06-11 17:40 | 1:58 | D/W | 132 kv busbar scheme change, interlock check & trip transfer work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) LT | 2024-06-06 08:25 | 2024-06-06 12:59 | 4:34 | D/W | P/W | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Transformer-3(426T) LT | 2024-06-30 13:40 | 2024-06-30 17:16 | 3:36 | S/O | Main & Transfer Bus to Double bus. | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-2 Transformer (413T) LT | 2024-06-28 07:30 | 2024-06-28 08:58 | 1:28 | S/O | Due to maint.work | 30 | 44 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-06-08 08:53 | 2024-06-08 12:10 | 3:17 | D/W | PROJECT WORK OF NESCO | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2024-06-11 09:35 | 2024-06-11 14:43 | 5:08 | S/O | Due to GIS Switching station work of NESCO, Rajshahi. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2024-06-08 07:01 | 2024-06-08 09:31 | 2:30 | S/O | High temperature (Red Hot Maintenance work). | 20 | 50 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2024-06-07 06:05 | 2024-06-07 09:45 | 3:40 | S/O | Due to maint.work | 50 | 183.3333 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) HT | 2024-06-07 06:07 | 2024-06-07 09:46 | 3:39 | S/O | Due to maint.work | 50 | 182.5 | Power interruption
Saidpur 132/33kV Grid Sub-Station | BUS A | 2024-06-11 11:18 | 2024-06-11 12:16 | 0:58 | S/O | High temperature on BUS A ,Rangpur ckt-01 DS. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | BUS B | 2024-06-11 08:48 | 2024-06-11 10:04 | 1:16 | S/O | None | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2024-06-11 11:05 | 2024-06-11 12:38 | 1:33 | S/O | Due to maint.work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2024-06-06 07:49 | 2024-06-06 10:36 | 2:47 | S/O | QF- GMD-39 and As the instruction of ALDC Bogura | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Auxiliary Transformer-2 HT | 2024-06-28 07:32 | 2024-06-28 09:37 | 2:05 | S/O | Neckmorad 33kV Riser change | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-06-27 06:10 | 2024-06-27 09:58 | 3:48 | S/O | T-1 Oil leakage. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2024-06-28 07:31 | 2024-06-28 09:36 | 2:05 | S/O | Neckmorad 33kV Riser change | 36 | 75 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) LT | 2024-06-27 12:18 | 2024-06-27 15:58 | 3:40 | S/O | Removal of High Temperature Points in T-3 Bay | 17 | 62.3333 | Power interruption
|  |  | Total : | 176:15 |  | Unserved Energy : |  | 1043.25
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1071:17 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2024
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV Grid Sub-Station | Aminbazar Ckt-2 | 2024-06-25 12:28 | 2024-06-28 14:20 | 73:52 | S/O | Due to PT Change. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Manikgonj Power Plant-01 | 2024-06-25 08:41 | 2024-06-26 00:43 | 16:02 | S/O | Line Ds Change | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-1 | 2024-06-10 09:09 | 2024-06-10 16:44 | 7:35 | D/W | LILO connection for 132KV Muktagacha Grid S/S. | 0 | 0 | No interruption
Ghatail 132/33kV Grid Sub-Station | RPCL-2 | 2024-06-08 08:31 | 2024-06-08 17:47 | 9:16 | D/W | LILO Connection work for 132kV Muktagasa ss Under G2G Project. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Dhamrai-1 | 2024-06-28 06:15 | 2024-06-28 10:38 | 4:23 | D/W | Project works. | 30 | 131.5 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Dhamrai-2 | 2024-06-28 06:15 | 2024-06-28 10:38 | 4:23 | D/W | Project work. | 30 | 131.5 | Power interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Tongi-2 | 2024-06-04 14:41 | 2024-06-04 19:09 | 4:28 | S/O | Emergency Maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-06-03 08:43 | 2024-06-03 19:03 | 10:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-06-05 09:27 | 2024-06-05 09:31 | 0:04 | D/W | A Crain moving at Ashuganj Substation | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-1 | 2024-06-05 15:44 | 2024-06-05 15:50 | 0:06 | D/W | A Crain moving at Ashuganj Substation | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-06-05 09:18 | 2024-06-05 09:25 | 0:07 | D/W | A Crain moving at Ashuganj Substation | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-06-05 15:50 | 2024-06-05 15:53 | 0:03 | D/W | A Crain moving at Ashuganj Substation | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-06-27 09:37 | 2024-06-27 09:47 | 0:10 | S/O | Ashuganj end Work by Ashuganj Power plant | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2024-06-28 07:08 | 2024-06-28 09:02 | 1:54 | S/O | work at ashuganj s/s | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2024-06-08 09:14 | 2024-06-08 12:22 | 3:08 | S/O | By order NLDC.Work at Mymensingh End. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-06-26 06:40 | 2024-06-26 18:05 | 11:25 | D/W | 400kV GNDP project work | 10 | 114.1667 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-06-27 06:35 | 2024-06-27 15:12 | 8:37 | D/W | Project work | 20 | 172.3333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-06-28 08:02 | 2024-06-28 18:20 | 10:18 | D/W |  | 15 | 154.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-06-29 06:39 | 2024-06-29 18:10 | 11:31 | D/W |  | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2024-06-30 13:21 | 2024-06-30 16:51 | 3:30 | D/W | 400kV GNDP project work. | 15 | 52.5 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakair-ckt-2A(E08) | 2024-06-07 09:21 | 2024-06-07 11:43 | 2:22 | S/O | Shutdown for Kaliakoir 400kv S/s bus DS Repair | 10 | 23.6667 | Power interruption
Mirzapur 132/33kV GIS Grid Sub-Station | Mirzapur-Kaliakoir ckt-2B(E-09) | 2024-06-07 09:21 | 2024-06-07 11:43 | 2:22 | S/O | S/D for Kaliakoir 400kv bus DS repair | 10 | 23.6667 | Power interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-1 | 2024-06-07 03:30 | 2024-06-07 12:29 | 8:59 | S/O | For T-4 Transformer installation work by CCCE. | 75 | 673.75 | Power interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2024-06-07 03:30 | 2024-06-07 12:29 | 8:59 | S/O | For T-4 Transformer installation work by CCCE. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-01 | 2024-06-12 14:44 | 2024-06-12 16:24 | 1:40 | S/O | Relay replacement works by SPMD. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-02 | 2024-06-12 16:26 | 2024-06-12 16:36 | 0:10 | S/O | Relay Replacement works. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-1 | 2024-06-10 11:25 | 2024-06-10 15:22 | 3:57 | S/O | Project work | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2024-06-14 15:12 | 2024-06-14 17:16 | 2:04 | S/O | Tan-Delta test Bus CT, T-phase (RTS) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2024-06-14 14:16 | 2024-06-14 14:51 | 0:35 | S/O | Maintenance work (SPMD) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2024-06-14 14:53 | 2024-06-14 17:14 | 2:21 | S/O | Maintenance work (SPMD) | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2024-06-03 10:07 | 2024-06-03 12:43 | 2:36 | S/O | Maintenance work. | 0 | 0 | No interruption
|  |  | Total : | 217:17 |  | Unserved Energy: |  | 1477.5833
Dhaka (South) Grid Circle :
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-06-05 06:59 | 2024-06-06 21:11 | 38:12 | S/O | New Tower Conducting by Project. CB open:- 06:59 Line Isolator Open:- 07:11 Earth switch Close:- 07:14 | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2024-06-10 06:01 | 2024-06-12 22:02 | 64:01 | S/O | Due to maint.work | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | EGCB 412MW | 2024-06-29 07:11 | 2024-06-29 16:42 | 9:31 | S/O | High Temperature Junction Point Maintenance. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2024-06-14 06:12 | 2024-06-14 11:54 | 5:42 | S/O | Another side by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2024-06-01 05:51 | 2024-06-01 11:33 | 5:42 | S/O | dead line checking by ullon ss. | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Shyampur-APR-Hasnabad Ckt-2 | 2024-06-28 08:20 | 2024-06-28 20:42 | 12:22 | S/O | Connect OPGW | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aggreko | 2024-06-03 14:53 | 2024-06-03 15:54 | 1:01 | S/O | As per direction of NLDC. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2024-06-03 14:36 | 2024-06-04 10:07 | 19:31 | S/O | Emergency instruction by NLDC . | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-06-01 06:32 | 2024-06-01 20:06 | 13:34 | S/O | CT change at Hasnabad end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad-1 | 2024-06-03 09:15 | 2024-06-03 13:50 | 4:35 | S/O | For Protection work By NLDC Instruction | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Srinagar-2 | 2024-06-26 13:53 | 2024-06-27 16:34 | 26:41 | S/O | srinagar side PT balast | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-06-05 06:53 | 2024-06-06 21:12 | 38:19 | S/O | Due to maint.work | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2024-06-10 05:58 | 2024-06-12 22:02 | 64:04 | S/O | Due to maint.work | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-1 | 2024-06-01 10:12 | 2024-06-09 15:06 | 196:54 | S/O | Under ground cable transfer work by DPDC. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Motijheel Ckt-2 | 2024-06-10 09:27 | 2024-06-14 13:08 | 99:41 | S/O | Motijheel Ckt-2 Maintenance works. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Start Up(MPL) | 2024-06-12 08:50 | 2024-06-12 14:49 | 5:59 | S/O | For preventive maintenance work. | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Madunaghat 400KV Ckt-2 | 2024-06-30 13:58 | 2024-06-30 13:58 | 0:00 | S/O | Regular Connection of Madhunaghat 440/230 GIS SS by DCMPGSP | 0 | 0 | No interruption
Meghnaghat 400/230kV Grid Sub-Station | Meghnaghat-Reliance PP 400KV Ckt-2 | 2024-06-02 11:43 | 2024-06-12 13:18 | 241:35 | D/W | Due to maint.work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-03 | 2024-06-25 07:02 | 2024-06-25 11:55 | 4:53 | S/O | CT & PT Maintenance. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-03 | 2024-06-29 07:18 | 2024-06-29 07:18 | 0:00 | S/O | CT change | 0 | 0 | No interruption
Shitalakhya 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2024-06-12 07:18 | 2024-06-15 15:00 | 79:42 | S/O | Scheduled Shutdown | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2024-06-22 07:15 | 2024-06-22 07:51 | 0:36 | S/O | Maintenance work of Maniknagar end | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-01 | 2024-06-15 06:08 | 2024-06-15 07:44 | 1:36 | S/O | Shutdown taken from Daudkandi end. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2024-06-15 06:08 | 2024-06-15 07:44 | 1:36 | S/O | Shutdown taken from Daudkandi end. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Keraniganj-02(Powerpac) | 2024-06-26 13:48 | 2024-06-26 13:48 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 935:47 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2024-06-01 06:13 | 2024-06-01 15:57 | 9:44 | D/W | Stringing work of LILO Baraiyarhat Hathazari ckt-01 | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2024-06-05 06:34 | 2024-06-05 17:12 | 10:38 | D/W | patiya LILO work | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2024-06-06 07:50 | 2024-06-06 13:35 | 5:45 | D/W | SD taken by Shikalbaha Grid | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2024-06-06 13:36 | 2024-06-06 14:27 | 0:51 | D/W | SD taken by Shikalbaha Grid | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2024-06-07 07:12 | 2024-06-07 15:52 | 8:40 | D/W | Due to Project work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2024-06-02 05:23 | 2024-06-02 07:49 | 2:26 | S/O | Due to bus shutdown at julda s/s end | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-06-27 06:02 | 2024-06-27 19:58 | 13:56 | D/W | Lilo connection at anandabazar s/s end. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-06-28 05:56 | 2024-06-28 17:21 | 11:25 | S/O | Due to ESPNER Project Work | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2024-06-29 06:11 | 2024-06-29 17:56 | 11:45 | S/O | Due to Project work. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2024-06-29 06:11 | 2024-06-29 19:13 | 13:02 | S/O | Due to Project work. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | GPH-01 | 2024-06-28 10:00 | 2024-06-28 15:59 | 5:59 | S/O | LA shifting | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Shikolbaha-02 | 2024-06-29 07:12 | 2024-06-29 17:53 | 10:41 | D/W | Shikalbaha line connection to Madhunaghat. | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 2024-06-02 05:27 | 2024-06-02 07:50 | 2:23 | S/O | corrective maintenance | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 1 | 2024-06-07 06:21 | 2024-06-07 08:57 | 2:36 | D/W | nldc | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2024-06-02 05:27 | 2024-06-02 07:50 | 2:23 | S/O | corrective maintenance | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2024-06-07 06:21 | 2024-06-07 08:58 | 2:37 | D/W | nldc | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2024-06-02 05:43 | 2024-06-02 07:31 | 1:48 | S/O | corrective maintenance | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-1 | 2024-06-02 05:36 | 2024-06-02 07:55 | 2:19 | S/O | corrective maintenance | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | Julda power plant unit-2 & 3 | 2024-06-02 05:36 | 2024-06-02 07:55 | 2:19 | S/O | corrective maintenance | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-AKSPL Line | 2024-06-01 06:28 | 2024-06-01 08:38 | 2:10 | D/W | AKSPL and Sholoshaher-02 line shifting between both circuit for ESPNCA project work. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-2(Rampur) | 2024-06-12 06:16 | 2024-06-12 07:50 | 1:34 | S/O | Due to Project work. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-06-28 06:56 | 2024-06-28 17:22 | 10:26 | D/W | LILO work by ESPNER project | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-3 | 2024-06-29 06:15 | 2024-06-29 17:57 | 11:42 | D/W | Project Work | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Sholoshahar CKT-1(Madunaghat) | 2024-06-29 05:17 | 2024-06-29 09:54 | 4:37 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2024-06-27 06:19 | 2024-06-27 06:19 | 0:00 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2024-06-29 06:25 | 2024-06-29 19:14 | 12:49 | D/W | project work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2024-06-12 06:14 | 2024-06-12 07:51 | 1:37 | S/O | S/D via NLDC over IP phone | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2024-06-22 07:15 | 2024-06-22 17:46 | 10:31 | D/W | project work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2024-06-29 10:45 | 2024-06-29 15:47 | 5:02 | D/W | project work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2024-06-29 07:13 | 2024-06-29 17:52 | 10:39 | D/W | project work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Intermediate-2 | 2024-06-14 07:30 | 2024-06-14 10:57 | 3:27 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-1 | 2024-06-07 06:36 | 2024-06-07 11:12 | 4:36 | S/O | Due to maint.work | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Shahmirpur-2 | 2024-06-07 06:52 | 2024-06-07 09:12 | 2:20 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 202:47 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2024-06-13 09:26 | 2024-06-13 09:59 | 0:33 | S/O | NLDC AE. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2024-06-13 08:49 | 2024-06-13 09:25 | 0:36 | S/O | NLDC AE. | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-1 | 2024-06-11 13:38 | 2024-06-11 15:45 | 2:07 | S/O | High temperature remove work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2024-06-11 16:15 | 2024-06-11 19:54 | 3:39 | S/O | High temperature remove work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | HFPL line | 2024-06-28 09:04 | 2024-06-28 15:32 | 6:28 | S/O | 132 KV HFPL Line maintenance | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2024-06-15 05:53 | 2024-06-15 07:57 | 2:04 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2024-06-15 05:53 | 2024-06-15 07:57 | 2:04 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-06-07 05:34 | 2024-06-07 10:16 | 4:42 | D/W | 132KV Kachua-Laksham Transmission line Conductor Stringing | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Kachua Ckt-1 | 2024-06-08 06:04 | 2024-06-08 09:01 | 2:57 | S/O | Due to maint.work | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2024-06-24 06:21 | 2024-06-24 09:10 | 2:49 | S/O | CB and DS(Q7) Maintenance work | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-1 | 2024-06-20 11:03 | 2024-06-20 15:44 | 4:41 | S/O | Red hot | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2024-06-23 12:41 | 2024-06-23 14:09 | 1:28 | S/O | System Protection works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2024-06-14 08:35 | 2024-06-14 09:50 | 1:15 | S/O | Circuit breaker Red maintenance | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | Cumilla North CKT | 2024-06-07 05:35 | 2024-06-07 10:16 | 4:41 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 40:04 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-06-13 11:17 | 2024-06-13 12:43 | 1:26 | S/O | To remove red hot problem | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2024-06-26 10:40 | 2024-06-26 14:06 | 3:26 | S/O | Approved by ALDC | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132kv Patuakhali ckt | 2024-06-08 05:50 | 2024-06-08 18:26 | 12:36 | D/W | Project work at bakerganj substation. | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Bagerhat (L3) | 2024-06-12 04:41 | 2024-06-22 22:43 | 258:02 | D/W | Project Work | 0 | 0 | No interruption
Bhandaria 132/33kV Grid Sub-Station | Barishal (L4) | 2024-06-12 04:41 | 2024-06-12 07:50 | 3:09 | D/W | Project Work | 54 | 170.1 | Power interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2024-06-22 08:36 | 2024-06-22 13:28 | 4:52 | S/O | Tower Insulator Maintenance | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2024-06-10 10:12 | 2024-06-10 11:47 | 1:35 | D/W | Due to punch point rectification work by siemens | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | Modhumoti 100MW PS | 2024-06-25 12:18 | 2024-06-25 14:41 | 2:23 | S/O | Energy meter change | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2024-06-06 06:08 | 2024-06-06 10:01 | 3:53 | S/O | Project Work | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-01 | 2024-06-06 09:09 | 2024-06-06 17:25 | 8:16 | D/W | Project work | 0 | 0 | No interruption
|  |  | Total : | 299:38 |  | Unserved Energy: |  | 170.1
HVDC Grid Circle :
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-1 | 2024-06-07 05:44 | 2024-06-07 16:35 | 10:51 | D/W | Rooppur Project work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Sirajgonj-2 | 2024-06-07 05:44 | 2024-06-07 10:28 | 4:44 | D/W | Rooppur Project work. | 0 | 0 | No interruption
|  |  | Total : | 15:35 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Barapukuria 230/132/33kV Grid Sub-Station | Saidpur 132 KV Ckt1 | 2024-06-28 09:17 | 2024-06-28 14:53 | 5:36 | D/W | Project Work | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2024-06-29 09:46 | 2024-06-29 16:15 | 6:29 | S/O | OPGW wire change | 5 | 32.4167 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2024-06-29 09:48 | 2024-06-29 16:18 | 6:30 | S/O | OPGW wire change | 5 | 32.5 | Power interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-06-03 08:24 | 2024-06-03 18:47 | 10:23 | S/O | Project works for Niamatpur S/S side | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-06-06 00:42 | 2024-06-06 21:27 | 20:45 | D/W | Maintenace work of Niamotpur s/s | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Nia Ckt-1 | 2024-06-10 10:07 | 2024-06-10 13:52 | 3:45 | D/W | bus upgradetion for Niamatpur S/S. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-SPPP Ckt-1 | 2024-06-29 09:58 | 2024-06-29 16:38 | 6:40 | S/O | OPGW wire change | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-06-08 08:17 | 2024-06-08 11:42 | 3:25 | D/W | 132 kv busbar scheme change. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132 kV Rahanpur Ckt-2 | 2024-06-10 16:12 | 2024-06-10 16:56 | 0:44 | D/W | 132 kv busbar scheme change interlock testing & protection shift to bus coupler cb relay open. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-06-07 08:20 | 2024-06-07 17:45 | 9:25 | S/O | Project work | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-06-10 13:58 | 2024-06-10 16:10 | 2:12 | S/O | Project work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 132kV Rahanpur Ckt-1 | 2024-06-30 11:06 | 2024-06-30 11:47 | 0:41 | S/O | Busbar scheme change interlock testing & protection shift to bus coupler CB relay open. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | Naogaon Niamatpur 132 KV ckt-1 | 2024-06-29 16:25 | 2024-06-30 17:50 | 25:25 | S/O | Due to maint. Of ALDC | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-1 | 2024-06-14 07:30 | 2024-06-14 11:30 | 4:00 | D/W | None | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-2 | 2024-06-14 07:30 | 2024-06-14 11:50 | 4:20 | D/W | None | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Kurigram | 2024-06-07 06:43 | 2024-06-07 18:26 | 11:43 | D/W | Project Work | 50 | 585.8333 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-1 | 2024-06-11 08:18 | 2024-06-11 12:38 | 4:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-01 | 2024-06-28 09:16 | 2024-06-28 14:53 | 5:37 | S/O | Due to Saidpur-Barapukuria ckt-1 and ckt-2 shut down, Load shed in Rangpur zone- 90MW | 45 | 252.75 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Baropukuria CKT-02 | 2024-06-28 09:17 | 2024-06-28 14:55 | 5:38 | S/O | Due to Saidpur-Barapukuria ckt-1 and ckt-2 shut down, Load shed in Rangpur zone- 90MW | 45 | 253.5 | Power interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-01 | 2024-06-27 09:01 | 2024-06-27 14:41 | 5:40 | S/O | Distance relay replacement | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Solar Park 1 | 2024-06-12 12:10 | 2024-06-12 16:43 | 4:33 | D/W | Relay test for power station. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Solar Park 1 | 2024-06-20 10:16 | 2024-06-21 15:08 | 28:52 | D/W | Energy meter seal and testing.BCRECL has taken S/D. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Solar Park 2 | 2024-06-12 14:47 | 2024-06-12 16:44 | 1:57 | D/W | Relay test for power station. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Solar Park 2 | 2024-06-20 10:17 | 2024-06-21 15:08 | 28:51 | D/W | Energy meter seal and testing.BCRECL has taken S/D. | 0 | 0 | No interruption
|  |  | Total : | 207:31 |  | Unserved Energy: |  | 1157
Others :Nil
No interruption
|  |  | Total : | 0:00 |  |  |  | 0:00
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1918:39 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June 2024
| Area | Previous Month (May' 2024) |  |  |  | Current Month (June '2024)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 69 | 23 | 105 | 197 | 31 | 22 | 65 | 119
2 | Dhaka (South) Grid Circle. | 94 | 31 | 82 | 207 | 27 | 18 | 42 | 87
3 | Chattogram Grid Circle. | 68 | 27 | 58 | 153 | 12 | 17 | 44 | 73
4 | Cumilla Grid Circle. | 54 | 25 | 56 | 135 | 20 | 13 | 40 | 73
5 | Khulna Grid Circle. | 39 | 20 | 40 | 99 | 20 | 21 | 30 | 71
6 | HVDC Grid Circle | 8 | 23 | 15 | 46 | 1 | 14 | 10 | 25
7 | Bogura Grid Circle. | 31 | 22 | 74 | 127 | 50 | 24 | 62 | 136
8 | Others
9 | Total | 363 | 171 | 430 | 964 | 161 | 129 | 293 | 584
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June 2024
| Area | Previous Month (May' 2024) |  |  |  | Current Month (June '2024)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 940.04 | 368.1 | 3529.57 | 4837.71 | 516.77 | 1347.08 | 2822.78 | 4686.63
2 | Dhaka (South) Grid Circle. | 569.1 | 62 | 373 | 1004.1 | 172.84 | 224.07 | 0 | 396.91
3 | Chattogram Grid Circle. | 245.56 | 50.17 | 1257.4 | 1553.13 | 52.59 | 157.92 | 277.25 | 487.76
4 | Cumilla Grid Circle. | 782.4 | 365.17 | 1034.17 | 2181.74 | 64.2 | 1017.76 | 1168.47 | 2250.43
5 | Khulna Grid Circle. | 48.87 | 169.23 | 153.57 | 371.67 | 782.35 | 590.79 | 1314.73 | 2687.87
6 | HVDC Grid Circle | 44.27 | 71 | 213.5 | 328.77 | 0 | 229.82 | 227.3 | 457.12
7 | Bogura Grid Circle. | 298.26 | 296.68 | 1513.73 | 2108.67 | 572.78 | 428.13 | 2200.25 | 3201.16
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 2928.5 | 1382.35 | 8074.94 | 12385.79 | 2161.53 | 3995.57 | 8010.78 | 14167.88
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June 2024
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 23 | 11 | 34 | 9 | 5 | 20 | 2995.17
2 | Dhaka (South) | 5031.6 | 10 | 0 | 10 | 6 | 3 | 1 | 135.83
3 | Chattogram | 2042 | 7 | 5 | 12 | 3 | 0 | 9 | 479.48
4 | Khulna | 2434 | 22 | 15 | 37 | 8 | 4 | 25 | 2425.77
5 | HVDC | 5954.3 | 3 | 3 | 6 | 0 | 1 | 5 | 457.12
6 | Bogura | 3145.6 | 21 | 12 | 33 | 8 | 4 | 21 | 1600.83
7 | Cumilla | 2981 | 10 | 13 | 23 | 2 | 2 | 19 | 2219.56
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 10313.76
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.96%
4 | Khulna | 99.96%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.96% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June 2024
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 7 | 9 | 16 | 5 | 1 | 10 | 1691.46 |  | 2935.17
2 | Dhaka (South) | 990.29 | - | 2 | - | 2 | - | - | 2 | 261.0667 |  | 1691.46
3 | Chattogram | 917 | - | 2 |  | 2 |  | 2 |  | 8.27
4 | Khulna | 1238.4 | - | 1 | 1 | 2 | - | - | 2 | 262.1
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 15 | 5 | 20 | 11 | 1 | 8 | 1600.33
7 | Cumilla | 1648.16 | - | 4 | - | 4 | 4 | - | - | 30.87
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 3854.0967
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.98%
7 | Cumilla | 99.98%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June 2024
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm | [6 empty] | 5:59 | 6:03
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. |  | 1:10 | 2:18
2024-06-01 | 13 | - | 22 | 42hr42 min | 2 | 8hr21 min | - | - | - | - | - | - | - | 1:08
1:46
2:20
1:45
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption. | [13 empty] | 1:36
2:07
1:30
1:10
0:23
[12 empty] | Executive Engineer |  | 6:32
[12 empty] | Information Management Division |  | 0:29
[12 empty] | LDC, PGCB, Dhaka. |  | 2:15
3:25
0:55
2:09
1:00
1:04
1:32
1:23
1:04

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June 2024
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bhaluka 132/33kV Grid Sub-Station | 5 | 9:12 | 420.5
Kabirpur 132/33kV Grid Sub-Station | 5 | 8:50 | 552
Kishoreganj 132/33kV Grid Sub-Station | 5 | 7:26 | 269.4
Sherpur 132/33kV Grid Sub-Station | 3 | 0:46 | 17.35
Tangail 132/33kV Grid Sub-Station | 4 | 4:50 | 194.05
Tongi 230/132/33kV Grid Sub-Station | 1 | 80:31 | 196.67
Ghatail 132/33kV Grid Sub-Station | 2 | 0:30 | 15
Kabirpur 132/33kV Grid Sub-Station | 3 | 6:12 | 195.55
Kishoreganj 132/33kV Grid Sub-Station | 2 | 0:10 | 3.33
Bhaluka 132/33kV Grid Sub-Station | 1 | 5:48 | 290
Jamalpur 132/33kV Grid Sub-Station | 2 | 2:51 | 93.58
Kabirpur 132/33kV Grid Sub-Station | 1 | 4:40 | 326.6667
Manikganj 132/33kV Grid Sub-Station | 5 | 37:04 | 549.03
Sherpur 132/33kV Grid Sub-Station | 1 | 11:23 | 56.9167
Tangail 132/33kV Grid Sub-Station | 1 | 0:58 | 29
Kaliakoir 400/230/132kV Grid Sub-Station | 2 | 8:46 | 263
Manikganj 132/33kV Grid Sub-Station | 4 | 33:50 | 493.5
Mirzapur 132/33kV GIS Grid Sub-Station | 2 | 4:44 | 47.33
Savar 132/33kV Grid Sub-Station | 5 | 8:59 | 673.75
Hasnabad 132/33kV Grid Substation | 5 | 1:56 | 46.33
Narshingdi 132/33kV Grid Sub-Station | 1 | 1:22 | 54.6667
Sonargaon 132/33kV Grid Sub-Station | 4 | 1:44 | 34.83
Meghnaghat 400/230kV Grid Sub-Station | 2 | 7:53 | 261.07
Baroirhat 132/33kV Grid Sub-Station | 3 | 5:51 | 157.92
Chandraghona 132/33kV Grid Sub-Station | 2 | 0:14 | 6.52
Dohazari 132/33kV Grid Sub-Station | 1 | 0:22 | 27.5
Madunaghat 132/33kV Grid Sub-Station | 1 | 1:43 | 10.3
Hathazari 230/132/33kV Grid Sub-Station | 2 | 1:02 | 8.27
Dohazari 132/33kV Grid Sub-Station | 2 | 2:28 | 132.25
Juldah 132/33kV Grid Sub-Station | 2 | 4:18 | 64.5
Shahmirpur 132/33kV Grid Sub-Station | 1 | 2:18 | 80.5
Chandpur 132/33kV Grid Sub-Station | 1 | 0:49 | 12.25
Chauddagram 132/33kV Grid Sub-Station | 2 | 3:43 | 107.83
Chowmuhani 132/33kV Grid Sub-Station | 2 | 3:30 | 79.17
Cumilla(N) 230/132/33kV Grid Sub-Station | 1 | 2:18 | 69
Cumilla(S) 132/33kV Grid Sub-Station | 2 | 0:50 | 33.33
Daudkandi 132/33kV Grid Sub-Station | 1 | 13:35 | 747.0833
Sylhet (South) 132/33kV GIS Grid Sub-Station | 1 | 1:37 | 2.425
Beanibazar 132/33kV Grid Sub-Station | 1 | 0:11 | 7.3333
Feni 132/33kV Grid Sub-Station | 1 | 0:09 | 4.2
Sylhet (South) 132/33kV GIS Grid Sub-Station | 1 | 0:09 | 6
Sylhet 132/33kV Grid Sub-Station | 2 | 0:20 | 13.33
Chandpur 132/33kV Grid Sub-Station | 2 | 14:33 | 371
Cumilla(N) 230/132/33kV Grid Sub-Station | 2 | 1:48 | 84.5
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 1:27 | 62.35
Daudkandi 132/33kV Grid Sub-Station | 1 | 6:49 | 272.6667
Feni 132/33kV Grid Sub-Station | 3 | 9:36 | 262.97
Ramganj 132/33kV Grid Sub-Station | 2 | 2:10 | 35.92
Shahjibazar 132/33kV Grid Sub-Station | 2 | 2:00 | 79.07
Bagerhat 132/33kV Grid Sub-Station | 3 | 4:37 | 34.9
Benapole 132/33kV Grid Sub-Station | 1 | 1:10 | 42
Bhandaria 132/33kV Grid Sub-Station | 5 | 19:50 | 688.88
Borhanuddin 230/33kV Grid Sub-Station | 2 | 2:55 | 157.08
Gollamari 132/33kV Grid Sub-Station | 2 | 4:22 | 144.1
Gopalganj 132/33kV Grid Sub-Station | 3 | 8:43 | 130.03
Madaripur 132/33kV Grid Sub-Station | 2 | 1:25 | 53.83
Mongla 132/33kV Grid Sub-Station | 2 | 2:45 | 17.71
Rajbari 132/33kV Grid Sub-Station | 2 | 0:28 | 12.6
Bagerhat 132/33kV Grid Sub-Station | 1 | 2:18 | 92
Barishal 230/132kV Grid Sub-Station | 1 | 6:01 | 144.4
Bhandaria 132/33kV Grid Sub-Station | 4 | 15:45 | 563.55
Faridpur 132/33kV Grid Sub-Station | 2 | 5:10 | 212.5
Goalpara 132/33kV Grid Sub-Station | 2 | 7:28 | 37.33
Gollamari 132/33kV Grid Sub-Station | 1 | 0:19 | 4.75
Gopalganj 132/33kV Grid Sub-Station | 2 | 4:59 | 124.75
Madaripur 132/33kV Grid Sub-Station | 1 | 1:23 | 20.75
Noapara 132/33kV Grid Sub-Station | 1 | 1:48 | 30.6
Rajbari 132/33kV Grid Sub-Station | 1 | 2:00 | 6
Bhandaria 132/33kV Grid Sub-Station | 1 | 3:09 | 170.1
Jashore 132/33kV Grid Sub-Station | 1 | 0:55 | 41.25
Kushtia 132/33kV Grid Sub-Station | 2 | 8:08 | 188.57
Jashore 132/33kV Grid Sub-Station | 2 | 3:02 | 152.3
Kushtia 132/33kV Grid Sub-Station | 1 | 3:00 | 75
Barapukuria 230/132/33kV Grid Sub-Station | 1 | 2:09 | 86
Bogura 132/33kV Grid Sub-Station | 1 | 0:41 | 23.9167
Jaldhaka 132/33kV Grid Sub-Station | 5 | 10:07 | 200.4
Kurigram 132/33kV Grid Sub-Station | 1 | 1:00 | 20
Naogaon 132/33kV Grid Sub-Station | 2 | 0:48 | 29.6
Natore 132/33kV Grid Sub-Station | 3 | 1:57 | 64.95
Niamatpur 132/33kV Grid Sub-Station | 3 | 3:10 | 74.35
Palashbari 132/33kV Grid Sub-Station | 2 | 2:50 | 28.33
Purbasadipur 132/33kV Grid Sub-Station | 1 | 0:34 | 17
Thakurgaon 132/33kV Grid Sub-Station | 2 | 12:46 | 13.03
Barapukuria 230/132/33kV Grid Sub-Station | 5 | 10:54 | 246.67
Purbasadipur 132/33kV Grid Sub-Station | 4 | 1:20 | 66.67
Rangpur 132/33kV Grid Sub-Station | 2 | 0:30 | 12.75
Saidpur 132/33kV Grid Sub-Station | 3 | 2:40 | 74.53
Thakurgaon 132/33kV Grid Sub-Station | 2 | 0:41 | 42.72
Bog-Sherpur 132/33kV Grid Sub-Station | 1 | 1:43 | 82.4
Chapai 132/33kV Grid Sub-Station | 1 | 0:17 | 7.0833
Lalmonirhat 132/33kV Grid Sub-Station | 1 | 1:23 | 37.35
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 3:02 | 45.5
Natore 132/33kV Grid Sub-Station | 2 | 6:05 | 273.75
Purbasadipur 132/33kV Grid Sub-Station | 1 | 1:28 | 44
Rajshahi 132/33kV Grid Sub-Station | 1 | 2:30 | 50
Rangpur 132/33kV Grid Sub-Station | 2 | 7:19 | 365.83
Thakurgaon 132/33kV Grid Sub-Station | 2 | 5:45 | 137.33
Naogaon 132/33kV Grid Sub-Station | 2 | 12:59 | 64.92
Rangpur 132/33kV Grid Sub-Station | 1 | 11:43 | 585.8333
Saidpur 132/33kV Grid Sub-Station | 2 | 11:15 | 506.25
Total Unserved energy : | 207 | 563:31 | 14167.8517
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June 2024
Sl. No | name | ss_MW | date_time
1 | AKS | 0 | 2024-06-01 00:00
2 | AKSML | 123 | 2024-06-10 13:00
3 | Aftabnagar | 50 | 2024-06-07 15:00
4 | Agargaon | 128 | 2024-06-13 13:00
5 | Agrabad | 112 | 2024-06-09 13:00
6 | Amnura | 80 | 2024-06-15 22:00
7 | Ashuganj | 99 | 2024-06-11 23:00
8 | BIPTC | N/A | N/A
9 | BSRM | 195 | 2024-06-04 09:00
10 | Bagerhat | 117 | 2024-06-10 22:00
11 | Bakulia | 113 | 2024-06-06 19:30
12 | Banani | 66.4 | 2024-06-06 15:00
13 | Bangabhaban | 24 | 2024-06-02 10:00
14 | Barapukuria | 81 | 2024-06-16 01:00
15 | Barguna | 28 | 2024-06-08 22:00
16 | Barishal | 130 | 2024-06-11 22:00
17 | Barishal-230 | 122 | 2024-06-18 23:00
18 | Baroaulia | 84 | 2024-06-01 10:00
19 | Baroirhat | 77 | 2024-06-03 22:00
20 | Bashundhara | 229 | 2024-06-02 16:00
21 | BashundharaCement | 13 | 2024-06-03 11:00
22 | Beanibazar | 86 | 2024-06-12 21:00
23 | Benapole | 86 | 2024-06-10 19:00
24 | Bhaluka | 208 | 2024-06-09 19:30
25 | Bhandaria | 66 | 2024-06-18 22:00
26 | Bhangura | 45 | 2024-06-17 21:00
27 | Bheramara(GK) | 79 | 2024-06-09 21:00
28 | Bhulta | 267 | 2024-06-11 18:30
29 | Bog-Sherpur | 84 | 2024-06-13 03:00
30 | Bogura | 201 | 2024-06-12 21:00
31 | Borhanuddin | 111 | 2024-06-10 23:00
32 | Brahmanbaria | 195 | 2024-06-02 21:00
33 | Cantonment | 176 | 2024-06-03 15:00
34 | Chandpur | 90 | 2024-06-17 23:00
35 | Chandraghona | 41 | 2024-06-13 13:00
36 | Chapai | 87 | 2024-06-12 22:00
37 | Charsaidpur | 50 | 2024-06-09 11:00
38 | Chauddagram | 81 | 2024-06-02 20:00
39 | Chhatak | 39 | 2024-06-12 22:00
40 | Chowmuhani | 264 | 2024-06-16 22:00
41 | Chuadanga | 124 | 2024-06-03 22:00
42 | Coxsbazar | 139 | 2024-06-04 19:30
43 | Cumilla(N) | 213 | 2024-06-01 21:00
44 | Cumilla(S) | 200 | 2024-06-25 19:00
45 | Daudkandi | 170 | 2024-06-02 20:00
46 | Dhaka | 54 | 2024-06-02 13:00
47 | Dhamrai | 140 | 2024-06-02 19:30
48 | Dhanmondi | 184 | 2024-06-03 13:00
49 | Dohazari | 114 | 2024-06-01 03:00
50 | Faridpur | 192 | 2024-06-11 23:00
51 | Fatullah | 88 | 2024-06-27 16:00
52 | Fenchuganj | 48 | 2024-06-12 17:00
53 | Feni | 139 | 2024-06-01 21:00
54 | GPH | 101 | 2024-06-04 05:00
55 | Ghatail | 70 | 2024-06-10 20:00
56 | Ghorashal | 60 | 2024-06-22 17:00
57 | Goalpara | 40 | 2024-06-05 00:00
58 | Gollamari | 96 | 2024-06-24 00:00
59 | Gopalganj | 130 | 2024-06-11 23:00
60 | Gulshan | 156 | 2024-06-03 15:00
61 | Halishahar | 93.5 | 2024-06-04 10:00
62 | HaripurSBU | 207 | 2024-06-07 00:00
63 | Hasnabad | 108 | 2024-06-01 21:00
64 | Hathazari | 91 | 2024-06-01 20:00
65 | Ishurdi | 94 | 2024-06-05 21:00
66 | Jaldhaka | 90 | 2024-06-05 21:00
67 | Jamalpur | 146 | 2024-06-09 00:00
68 | Jashore | 174 | 2024-06-09 20:00
69 | Jhenaidah | 157 | 2024-06-09 19:30
70 | Joydebpur | 222 | 2024-06-02 18:30
71 | Joypurhat | 73 | 2024-06-06 01:00
72 | Juldah | 32 | 2024-06-04 16:00
73 | KSRM | 45 | 2024-06-04 00:00
74 | Kabirpur | 316 | 2024-06-03 19:00
75 | Kachua | 99 | 2024-06-18 21:00
76 | Kallyanpur | 132 | 2024-06-14 10:00
77 | Kalurghat | 40 | 2024-06-03 10:00
78 | Kamrangirchar | 59.7 | 2024-06-09 13:00
79 | Kaptai | N/A | N/A
80 | Kazla | 121 | 2024-06-01 12:00
81 | Keranigonj | 95 | 2024-06-08 19:30
82 | Khagrachori | 38 | 2024-06-11 20:00
83 | Khulna | 109 | 2024-06-09 13:00
84 | Khulshi | 214 | 2024-06-02 20:00
85 | Kishoreganj | 188 | 2024-06-10 22:00
86 | Kodda | 299 | 2024-06-03 19:30
87 | Kulaura | 60 | 2024-06-01 19:00
88 | Kurigram | 74 | 2024-06-07 20:00
89 | Kushtia | 178 | 2024-06-13 19:30
90 | Lalbag | 106 | 2024-06-09 12:00
91 | Lalmonirhat | 68 | 2024-06-05 20:00
92 | MI_Cement | 18.4 | 2024-06-27 12:00
93 | Madanganj | 41 | 2024-06-30 02:00
94 | Madaripur | 143 | 2024-06-17 23:00
95 | Madartek | 99.35 | 2024-06-06 00:00
96 | Madunaghat | 66 | 2024-06-05 22:00
97 | Magura | 78 | 2024-06-09 19:30
98 | Mahasthangarh | 90 | 2024-06-02 02:00
99 | Manikganj | 155 | 2024-06-08 20:00
100 | Maniknagar | 100 | 2024-06-09 13:00
101 | Matarbari | 52 | 2024-06-06 21:00
102 | Matuail | 80 | 2024-06-04 15:00
103 | Millgate | 142 | 2024-06-02 15:00
104 | Mirpur | 177 | 2024-06-02 16:00
105 | Mirsorai | 41 | 2024-06-08 22:00
106 | Mirzapur | 104 | 2024-06-09 19:00
107 | Mithapukur | 70 | 2024-06-01 21:00
108 | Modern | 0 | 2024-06-01 00:00
109 | Mogbazar | 158.1 | 2024-06-02 15:00
110 | Mongla | 52 | 2024-06-02 12:00
111 | Motijheel | 53 | 2024-06-03 16:00
112 | Munshiganj | 124 | 2024-06-06 00:00
113 | Mymensingh | 299 | 2024-06-11 21:00
114 | Naogaon | 166 | 2024-06-04 00:00
115 | Narail | 71 | 2024-06-13 23:00
116 | Narinda | 75 | 2024-06-13 13:00
117 | Narshingdi | 175 | 2024-06-29 19:30
118 | Natore | 175 | 2024-06-15 22:00
119 | Nawabganj | 68.6 | 2024-06-11 22:00
120 | Netrakona | 139 | 2024-06-21 20:00
121 | New | 61.8 | 2024-06-05 12:00
122 | Niamatpur | 90 | 2024-06-12 22:00
123 | Noapara | 58 | 2024-06-29 19:30
124 | PHP | 11 | 2024-06-14 11:00
125 | Pabna | 145 | 2024-06-08 21:00
126 | Palashbari | 144 | 2024-06-05 20:00
127 | Panchagarh | 64 | 2024-06-22 23:00
128 | Patuakhali | 108 | 2024-06-19 00:00
129 | Payra | 52 | 2024-06-15 23:00
130 | Postogola | 66 | 2024-06-06 00:00
131 | Purbachal | 49 | 2024-06-13 16:00
132 | Purbasadipur | 148 | 2024-06-05 23:00
133 | Rahim | 57 | 2024-06-24 02:00
134 | Rajbari | 92 | 2024-06-09 19:30
135 | Rajendrapur | 128 | 2024-06-13 21:00
136 | Rajshahi | 161 | 2024-06-05 22:00
137 | Rajshahi-230 | 106 | 2024-06-12 00:00
138 | Ramganj | 126 | 2024-06-21 22:00
139 | Rampur | 44 | 2024-06-25 10:00
140 | Rangamati | 21 | 2024-06-11 20:00
141 | Rangpur | 161 | 2024-06-03 21:00
142 | Ruppur | 7.6 | 2024-06-26 15:00
143 | SSM | 47 | 2024-06-02 16:00
144 | Saidpur | 130 | 2024-06-05 19:30
145 | Satkhira | 153 | 2024-06-15 22:00
146 | Satmasjid | 133 | 2024-06-02 16:00
147 | Savar | 232 | 2024-06-11 15:00
148 | SevenRings | 24.18 | 2024-06-09 12:00
149 | ShahCement | 36 | 2024-06-10 10:00
150 | Shahjadpur | 98 | 2024-06-12 22:00
151 | Shahjibazar | 161 | 2024-06-12 23:00
152 | Shahmirpur | 59 | 2024-06-10 00:00
153 | Shariatpur | 106 | 2024-06-17 22:00
154 | Sherpur | 144 | 2024-06-22 21:00
155 | Shikalbaha | 37 | 2024-06-04 18:30
156 | Shikalbaha-230 | N/A | N/A
157 | Shitalakhya | 120 | 2024-06-03 15:00
158 | Sholosohor | 51 | 2024-06-01 15:00
159 | Shyampur | 180 | 2024-06-06 13:00
160 | Siddhirganj | 140 | 2024-06-11 15:00
161 | Sirajganj | 148 | 2024-06-04 20:00
162 | Sonargaon | 123 | 2024-06-06 21:00
163 | Sreemongol | 78 | 2024-06-11 22:00
164 | Sreepur | 102 | 2024-06-29 09:00
165 | Srinagar | 56.41 | 2024-06-17 22:00
166 | Sunamganj | 64 | 2024-06-12 22:00
167 | Sylhet | 50 | 2024-06-18 17:00
168 | Sylhet-132 | 130 | 2024-06-01 19:00
169 | TK | 64 | 2024-06-06 02:00
170 | Tangail | 253 | 2024-06-10 22:00
171 | Thakurgaon | 118 | 2024-06-05 20:00
172 | Tongi | 155 | 2024-06-03 11:00
173 | Ullahpara | 44 | 2024-06-04 21:00
174 | Ullon | 71 | 2024-06-01 19:00
175 | Uttara | 97 | 2024-06-13 15:00
176 | UttaraNew | 61 | 2024-06-12 23:00
177 | Zigatola | 103 | 2024-06-02 16:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: June 2024
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5718.17 | 2024-06-04 | 15:00
Chattogram | 1593 | 2024-06-04 | 21:00
Cumilla | 1560 | 2024-06-02 | 21:00
Mymensingh | 1163 | 2024-06-10 | 22:00
Sylhet | 692 | 2024-06-12 | 21:00
Khulna | 2091.7 | 2024-06-09 | 23:00
Barishal | 565.93 | 2024-06-10 | 23:00
Rajshahi | 1757.6 | 2024-06-12 | 22:00
Rangpur | 1059 | 2024-06-05 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June 2024
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 399 | 2024-06-17 09:00 | 328 | 2024-06-05 22:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 414 | 2024-06-16 20:00 | 327 | 2024-06-18 16:00
4 | Bibiana | 400 | 407 | 2024-06-20 17:00 | 380 | 2024-06-13 16:00
5 | BIPTC | 400 | 409 | 2024-06-14 06:00 | 387 | 2024-06-25 15:00
6 | Bogura | 400 | 415 | 2024-06-20 07:00 | 334 | 2024-06-20 07:00
7 | Gopalganj | 400 | 407 | 2024-06-20 15:00 | 374 | 2024-06-04 15:00
8 | Kaliakoir | 400 | 398 | 2024-06-29 00:00 | 361 | 2024-06-12 02:00
9 | Madunaghat_I | 400 | 425 | 2024-06-03 19:30 | 331 | 2024-06-23 12:00
10 | Meghnaghat | 400 | 395 | 2024-06-17 08:00 | 391 | 2024-06-21 18:30
11 | Payra | 400 | 416 | 2024-06-20 15:00 | 397 | 2024-06-01 09:00
12 | Rahanpur | 400 | 419 | 2024-06-20 07:00 | 365 | 2024-06-28 22:00
13 | Rampal | 400 | 410 | 2024-06-20 15:00 | 379 | 2024-06-06 21:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 250 | 2024-06-11 20:00 | 221 | 2024-06-02 18:00
2 | AKSML | 230 | 239 | 2024-06-29 20:00 | 213 | 2024-06-27 14:00
3 | Aminbazar | 230 | 239 | 2024-06-15 14:00 | 224 | 2024-06-24 09:00
4 | Ashuganj | 230 | 242 | 2024-06-16 17:00 | 124 | 2024-06-08 15:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 235 | 2024-06-19 17:00 | 220 | 2024-06-06 15:00
7 | Barapukuria | 230 | 233 | 2024-06-26 10:00 | 222 | 2024-06-17 11:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 247 | 2024-06-29 10:00 | 229 | 2024-06-08 02:00
10 | Bheramara | 230 | 242 | 2024-06-23 17:00 | 234 | 2024-06-30 06:00
11 | Bhulta | 230 | 240 | 2024-06-17 07:00 | 210 | 2024-06-04 15:00
12 | Bibiana | 230 | 235 | 2024-06-30 22:00 | 221 | 2024-06-02 11:00
13 | BIPTC | 230 | 239 | 2024-06-18 08:00 | 222 | 2024-06-07 22:00
14 | Bogura | 230 | 235 | 2024-06-30 18:00 | 221 | 2024-06-07 09:00
15 | Bogura-400 | 230 | 234 | 2024-06-20 08:00 | 231 | 2024-06-20 07:00
16 | Borhanuddin | 230 | 248 | 2024-06-29 10:00 | 228 | 2024-06-07 23:00
17 | BSRM | 230 | 239 | 2024-06-26 19:30 | 216 | 2024-06-05 11:00
18 | Cumilla(N) | 230 | 236 | 2024-06-24 20:00 | 222 | 2024-06-09 10:00
19 | Faridpur | 230 | N/A | N/A | N/A | N/A
20 | Fenchuganj | 230 | 239 | 2024-06-29 01:00 | 229 | 2024-06-06 02:00
21 | Ghorashal | 230 | 245 | 2024-06-17 07:00 | 220 | 2024-06-01 08:00
22 | Ghorashal-230 | 230 | 240 | 2024-06-17 08:00 | 212 | 2024-06-04 15:00
23 | Gopalganj | 230 | N/A | N/A | N/A | N/A
24 | GPH | 230 | 238 | 2024-06-24 20:00 | 215 | 2024-06-19 19:00
25 | Haripur | 230 | 240 | 2024-06-17 07:00 | 234 | 2024-06-13 18:30
26 | Hasnabad | 230 | 239 | 2024-06-20 16:00 | 211 | 2024-06-04 15:00
27 | Hathazari | 230 | 240 | 2024-06-24 18:30 | 215 | 2024-06-27 15:00
28 | Ishurdi | 230 | 238 | 2024-06-23 18:00 | 216 | 2024-06-13 08:00
29 | Jhenaidah | 230 | 231 | 2024-06-20 16:00 | 209 | 2024-06-07 21:00
30 | Kaliakoir | 230 | 266 | 2024-06-08 22:00 | 215 | 2024-06-01 12:00
31 | Keranigonj | 230 | 239 | 2024-06-17 08:00 | 209 | 2024-06-04 15:00
32 | Khulna(S) | 230 | 236 | 2024-06-20 16:00 | 210 | 2024-06-07 23:00
33 | Madunaghat_I | 230 | 240 | 2024-06-24 18:30 | 218 | 2024-06-17 16:00
34 | Maniknagar | 230 | 240 | 2024-06-17 08:00 | 210 | 2024-06-04 15:00
35 | Meghnaghat | 230 | 246 | 2024-06-17 05:00 | 218 | 2024-06-05 18:00
36 | Meghnaghat-400 | 230 | 241 | 2024-06-16 20:00 | 222 | 2024-06-08 19:00
37 | Mirsorai | 230 | 240 | 2024-06-28 19:30 | 222 | 2024-06-11 18:30
38 | Rajshahi | 230 | 237 | 2024-06-24 17:00 | 219 | 2024-06-10 15:00
39 | Rampal | 230 | 235 | 2024-06-20 15:00 | 213 | 2024-06-07 23:00
40 | Rampur | 230 | N/A | N/A | N/A | N/A
41 | Rampura | 230 | 238 | 2024-06-17 07:00 | 207 | 2024-06-04 15:00
42 | Shikalbaha | 230 | 239 | 2024-06-30 18:30 | 212 | 2024-06-17 21:00
43 | Shyampur | 230 | 239 | 2024-06-17 08:00 | 211 | 2024-06-04 15:00
44 | Siddhirganj | 230 | 241 | 2024-06-17 07:00 | 221 | 2024-06-04 10:00
45 | Sirajgonj | 230 | 241 | 2024-06-19 09:00 | 227 | 2024-06-06 14:00
46 | Sreepur | 230 | 238 | 2024-06-19 09:00 | 228 | 2024-06-22 19:30
47 | Tongi | 230 | 240 | 2024-06-17 07:00 | 210 | 2024-06-01 09:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 138 | 2024-06-24 05:00 | 120 | 2024-06-04 15:00
2 | Agargaon | 132 | 142 | 2024-06-13 18:00 | 136 | 2024-06-19 12:00
3 | Agrabad | 132 | 139 | 2024-06-24 19:30 | 115 | 2024-06-26 04:00
4 | AKS | 132 | 136 | 2024-06-24 19:30 | 122 | 2024-06-06 14:00
5 | Aminbazar | 132 | 143 | 2024-06-13 18:00 | 114 | 2024-06-15 05:00
6 | Amnura | 132 | 141 | 2024-06-24 17:00 | 115 | 2024-06-28 21:00
7 | Ashuganj | 132 | 141 | 2024-06-16 16:00 | 126 | 2024-06-04 18:30
8 | Bagerhat | 132 | 140 | 2024-06-20 15:00 | 114 | 2024-06-19 00:00
9 | Bakulia | 132 | 141 | 2024-06-24 19:00 | 124 | 2024-06-27 12:00
10 | Banani | 132 | 138 | 2024-06-13 18:00 | 120 | 2024-06-04 15:00
11 | Bangabhaban | 132 | 139 | 2024-06-17 04:00 | 119 | 2024-06-04 15:00
12 | Barapukuria | 132 | 142 | 2024-06-18 05:00 | 118 | 2024-06-28 12:00
13 | Barguna | 132 | 137 | 2024-06-29 10:00 | 113 | 2024-06-12 02:00
14 | Barishal | 132 | 140 | 2024-06-23 17:00 | 113 | 2024-06-19 00:00
15 | Barishal-230 | 132 | 142 | 2024-06-29 10:00 | 123 | 2024-06-07 23:00
16 | Baroaulia | 132 | 140 | 2024-06-24 19:30 | 123 | 2024-06-27 15:00
17 | Baroirhat | 132 | 136 | 2024-06-13 19:30 | 128 | 2024-06-20 04:00
18 | Bashundhara | 132 | 150 | 2024-06-27 01:00 | 118 | 2024-06-04 15:00
19 | BashundharaCement | 132 | 132 | 2024-06-27 21:00 | 115 | 2024-06-18 17:00
20 | Beanibazar | 132 | 134 | 2024-06-16 10:00 | 118 | 2024-06-18 00:00
21 | Benapole | 132 | 139 | 2024-06-25 06:00 | 116 | 2024-06-18 23:00
22 | Bhaluka | 132 | 136 | 2024-06-20 10:00 | 118 | 2024-06-01 08:00
23 | Bhandaria | 132 | 137 | 2024-06-30 22:00 | 90 | 2024-06-14 03:00
24 | Bhangura | 132 | 139 | 2024-06-29 14:00 | 128 | 2024-06-06 16:00
25 | Bheramara | 132 | 137 | 2024-06-20 17:00 | 128 | 2024-06-13 21:00
26 | Bheramara(GK) | 132 | 138 | 2024-06-26 01:00 | 113 | 2024-06-11 18:30
27 | Bhulta | 132 | 132 | 2024-06-07 17:00 | 111 | 2024-06-12 18:00
28 | Bog-Sherpur | 132 | 136 | 2024-06-20 07:00 | 121 | 2024-06-28 21:00
29 | Bogura | 132 | 137 | 2024-06-20 07:00 | 121 | 2024-06-28 21:00
30 | Bogura-230 | 132 | 138 | 2024-06-20 07:00 | 112 | 2024-06-02 10:00
31 | Brahmanbaria | 132 | 137 | 2024-06-16 17:00 | 133 | 2024-06-29 06:00
32 | Cantonment | 132 | 142 | 2024-06-13 18:00 | 122 | 2024-06-01 12:00
33 | Chandpur | 132 | 143 | 2024-06-13 19:30 | 113 | 2024-06-05 11:00
34 | Chandraghona | 132 | 139 | 2024-06-24 20:00 | 125 | 2024-06-06 17:00
35 | Chapai | 132 | 138 | 2024-06-30 18:30 | 113 | 2024-06-28 21:00
36 | Charsaidpur | 132 | 141 | 2024-06-13 18:00 | 123 | 2024-06-05 10:00
37 | Chauddagram | 132 | 140 | 2024-06-13 19:30 | 114 | 2024-06-05 11:00
38 | Chhatak | 132 | 134 | 2024-06-16 09:00 | 118 | 2024-06-17 23:00
39 | Chowmuhani | 132 | 138 | 2024-06-13 20:00 | 108 | 2024-06-05 00:00
40 | Chuadanga | 132 | 137 | 2024-06-10 22:00 | 113 | 2024-06-18 23:00
41 | Coxsbazar | 132 | 132 | 2024-06-19 03:00 | 106 | 2024-06-06 13:00
42 | Cumilla(N) | 132 | 140 | 2024-06-28 18:30 | 120 | 2024-06-01 05:00
43 | Cumilla(S) | 132 | 139 | 2024-06-13 19:30 | 119 | 2024-06-05 11:00
44 | Daudkandi | 132 | 140 | 2024-06-13 18:00 | 114 | 2024-06-01 09:00
45 | Dhaka | 132 | 139 | 2024-06-30 05:00 | 120 | 2024-06-04 15:00
46 | Dhamrai | 132 | 143 | 2024-06-17 08:00 | 118 | 2024-06-01 12:00
47 | Dhanmondi | 132 | 140 | 2024-06-16 18:00 | 122 | 2024-06-05 11:00
48 | Dohazari | 132 | 138 | 2024-06-24 20:00 | 117 | 2024-06-06 13:00
49 | Faridpur | 132 | 136 | 2024-06-20 16:00 | 121 | 2024-06-08 23:00
50 | Fatullah | 132 | 140 | 2024-06-13 18:00 | 123 | 2024-06-04 15:00
51 | Fenchuganj | 132 | 136 | 2024-06-18 09:00 | 126 | 2024-06-17 23:00
52 | Feni | 132 | 137 | 2024-06-13 19:30 | 113 | 2024-06-05 11:00
53 | Ghatail | 132 | 132 | 2024-06-01 00:00 | 111 | 2024-06-08 13:00
54 | Ghorashal | 132 | 144 | 2024-06-17 07:00 | 126 | 2024-06-01 15:00
55 | Goalpara | 132 | 141 | 2024-06-20 15:00 | 134 | 2024-06-19 13:00
56 | Gollamari | 132 | 140 | 2024-06-20 15:00 | 118 | 2024-06-21 23:00
57 | Gopalganj | 132 | 138 | 2024-06-20 16:00 | 119 | 2024-06-07 23:00
58 | Gopalganj-400 | 132 | 136 | 2024-06-19 18:00 | 125 | 2024-06-02 10:00
59 | Gulshan | 132 | 138 | 2024-06-13 18:00 | 112 | 2024-06-05 15:00
60 | Halishahar | 132 | 140 | 2024-06-24 19:30 | 123 | 2024-06-05 10:00
61 | Haripur | 132 | 140 | 2024-06-13 18:00 | 123 | 2024-06-04 15:00
62 | HaripurSBU | 132 | 132 | 2024-06-10 19:00 | 123 | 2024-06-04 15:00
63 | Hasnabad | 132 | 140 | 2024-06-13 18:00 | 123 | 2024-06-01 14:00
64 | Hathazari | 132 | 139 | 2024-06-24 18:30 | 127 | 2024-06-05 10:00
65 | Ishurdi | 132 | 139 | 2024-06-24 18:30 | 130 | 2024-06-04 14:00
66 | Jaldhaka | 132 | 137 | 2024-06-18 04:00 | 110 | 2024-06-21 22:00
67 | Jamalpur | 132 | 140 | 2024-06-06 22:00 | 114 | 2024-06-17 22:00
68 | Jashore | 132 | 139 | 2024-06-20 15:00 | 118 | 2024-06-13 21:00
69 | Jhenaidah | 132 | 141 | 2024-06-20 16:00 | 124 | 2024-06-07 23:00
70 | Jhenaidah-230 | 132 | 141 | 2024-06-20 15:00 | 125 | 2024-06-07 23:00
71 | Joydebpur | 132 | 144 | 2024-06-13 17:00 | 121 | 2024-06-04 16:00
72 | Joypurhat | 132 | 135 | 2024-06-20 07:00 | 113 | 2024-06-11 22:00
73 | Juldah | 132 | 142 | 2024-06-24 20:00 | 125 | 2024-06-05 11:00
74 | Kabirpur | 132 | 138 | 2024-06-07 17:00 | 116 | 2024-06-03 09:00
75 | Kachua | 132 | 140 | 2024-06-13 19:00 | 114 | 2024-06-05 16:00
76 | Kaliakoir | 132 | 142 | 2024-06-16 06:00 | 113 | 2024-06-18 04:00
77 | Kallyanpur | 132 | 136 | 2024-06-17 08:00 | 119 | 2024-06-04 15:00
78 | Kalurghat | 132 | 139 | 2024-06-24 20:00 | 124 | 2024-06-17 22:00
79 | Kamrangirchar | 132 | 140 | 2024-06-13 18:00 | 118 | 2024-06-04 15:00
80 | Kaptai | 132 | N/A | N/A | N/A | N/A
81 | Kazla | 132 | 139 | 2024-06-17 04:00 | 119 | 2024-06-04 16:00
82 | Keranigonj | 132 | 141 | 2024-06-13 18:00 | 113 | 2024-06-16 07:00
83 | Khagrachori | 132 | 138 | 2024-06-25 14:00 | 123 | 2024-06-05 11:00
84 | Khulna | 132 | 140 | 2024-06-20 15:00 | 121 | 2024-06-07 21:00
85 | Khulna(S) | 132 | 141 | 2024-06-20 16:00 | 111 | 2024-06-12 05:00
86 | Khulshi | 132 | 138 | 2024-06-24 20:00 | 122 | 2024-06-05 11:00
87 | Kishoreganj | 132 | 136 | 2024-06-19 09:00 | 117 | 2024-06-01 17:00
88 | Kodda | 132 | 143 | 2024-06-13 17:00 | 112 | 2024-06-10 08:00
89 | KSRM | 132 | 140 | 2024-06-24 19:30 | 117 | 2024-06-06 06:00
90 | Kulaura | 132 | 134 | 2024-06-19 10:00 | 125 | 2024-06-12 19:00
91 | Kurigram | 132 | 144 | 2024-06-18 05:00 | 111 | 2024-06-07 19:30
92 | Kushtia | 132 | 139 | 2024-06-29 10:00 | 115 | 2024-06-25 05:00
93 | Lalbag | 132 | 140 | 2024-06-13 18:00 | 121 | 2024-06-01 13:00
94 | Lalmonirhat | 132 | 136 | 2024-06-20 07:00 | 114 | 2024-06-05 21:00
95 | Madanganj | 132 | 140 | 2024-06-13 18:00 | 122 | 2024-06-01 14:00
96 | Madaripur | 132 | 137 | 2024-06-20 16:00 | 113 | 2024-06-19 09:00
97 | Madartek | 132 | 138 | 2024-06-13 18:00 | 113 | 2024-06-29 02:00
98 | Madunaghat | 132 | 139 | 2024-06-24 19:30 | 124 | 2024-06-06 16:00
99 | Magura | 132 | 140 | 2024-06-20 15:00 | 122 | 2024-06-17 01:00
100 | Mahasthangarh | 132 | 136 | 2024-06-20 07:00 | 120 | 2024-06-07 23:00
101 | Manikganj | 132 | 134 | 2024-06-07 18:00 | 112 | 2024-06-30 18:00
102 | Maniknagar | 132 | 139 | 2024-06-16 20:00 | 112 | 2024-06-27 15:00
103 | Matarbari | 132 | 121 | 2024-06-12 21:00 | 106 | 2024-06-06 00:00
104 | Matuail | 132 | 140.6 | 2024-06-13 18:00 | 122.4 | 2024-06-04 15:00
105 | Millgate | 132 | 140 | 2024-06-13 17:00 | 113 | 2024-06-16 01:00
106 | Mirpur | 132 | 141 | 2024-06-13 17:00 | 124 | 2024-06-08 12:00
107 | Mirzapur | 132 | 136 | 2024-06-30 22:00 | 131 | 2024-06-07 20:00
108 | Mithapukur | 132 | 136 | 2024-06-20 07:00 | 118 | 2024-06-05 21:00
109 | MI_Cement | 132 | 141 | 2024-06-13 18:00 | 122 | 2024-06-05 10:00
110 | Modern | 132 | 140 | 2024-06-24 19:00 | 123 | 2024-06-27 13:00
111 | Mogbazar | 132 | 140 | 2024-06-21 04:00 | 120 | 2024-06-04 15:00
112 | Mongla | 132 | 150 | 2024-06-05 19:00 | 111 | 2024-06-19 00:00
113 | Motijheel | 132 | 139 | 2024-06-17 04:00 | 119 | 2024-06-04 15:00
114 | Munshiganj | 132 | 141 | 2024-06-13 18:00 | 122 | 2024-06-05 10:00
115 | Mymensingh | 132 | 137 | 2024-06-09 11:00 | 105 | 2024-06-01 16:00
116 | Naogaon | 132 | 134 | 2024-06-20 07:00 | 116 | 2024-06-11 22:00
117 | Narail | 132 | 140 | 2024-06-20 16:00 | 122 | 2024-06-13 21:00
118 | Narinda | 132 | 0 | 2024-06-01 00:00 | N/A | N/A
119 | Narshingdi | 132 | 136 | 2024-06-13 18:00 | 114 | 2024-06-02 11:00
120 | Natore | 132 | 137 | 2024-06-11 15:00 | 107 | 2024-06-30 18:00
121 | Nawabganj | 132 | 141 | 2024-06-13 18:00 | 123 | 2024-06-01 09:00
122 | Netrakona | 132 | 136 | 2024-06-01 00:00 | 115 | 2024-06-07 17:00
123 | New | 132 | 140 | 2024-06-13 17:00 | 120 | 2024-06-04 15:00
124 | Niamatpur | 132 | 141 | 2024-06-30 18:00 | 120 | 2024-06-28 21:00
125 | Noapara | 132 | 140 | 2024-06-20 15:00 | 120 | 2024-06-13 21:00
126 | Pabna | 132 | 138 | 2024-06-29 15:00 | 126 | 2024-06-04 13:00
127 | Palashbari | 132 | 134 | 2024-06-20 07:00 | 114 | 2024-06-28 22:00
128 | Panchagarh | 132 | 140 | 2024-06-14 06:00 | 106 | 2024-06-28 00:00
129 | Patuakhali | 132 | 137 | 2024-06-29 10:00 | 131 | 2024-06-28 03:00
130 | Payra | 132 | 137 | 2024-06-29 10:00 | 129 | 2024-06-07 22:00
131 | PHP | 132 | 138 | 2024-06-13 20:00 | 114 | 2024-06-01 13:00
132 | Postogola | 132 | 141 | 2024-06-13 18:00 | 123 | 2024-06-01 14:00
133 | Purbachal | 132 | 140 | 2024-06-14 13:00 | 118 | 2024-06-06 12:00
134 | Purbasadipur | 132 | 136 | 2024-06-01 22:00 | 110 | 2024-06-21 22:00
135 | Rahanpur | 132 | 141 | 2024-06-16 05:00 | 120 | 2024-06-28 21:00
136 | Rahim | 132 | 140 | 2024-06-13 18:00 | 105 | 2024-06-06 10:00
137 | Rajbari | 132 | 135 | 2024-06-20 15:00 | 120 | 2024-06-07 23:00
138 | Rajendrapur | 132 | 136 | 2024-06-23 18:30 | 113 | 2024-06-03 10:00
139 | Rajshahi | 132 | 137 | 2024-06-25 09:00 | 124 | 2024-06-17 23:00
140 | Rajshahi-230 | 132 | 137 | 2024-06-24 17:00 | 110 | 2024-06-28 21:00
141 | Ramganj | 132 | 141 | 2024-06-13 19:30 | 109 | 2024-06-06 04:00
142 | Rampur | 132 | 139 | 2024-06-24 18:30 | 113 | 2024-06-07 16:00
143 | Rampura | 132 | 138 | 2024-06-07 17:00 | 133 | 2024-06-15 22:00
144 | Rangamati | 132 | 138 | 2024-06-24 19:30 | 124 | 2024-06-05 11:00
145 | Rangpur | 132 | 146 | 2024-06-18 05:00 | 123 | 2024-06-07 03:00
146 | Ruppur | 132 | 138 | 2024-06-08 06:00 | 128 | 2024-06-04 15:00
147 | Saidpur | 132 | 136 | 2024-06-01 22:00 | 114 | 2024-06-20 19:00
148 | Satkhira | 132 | 140 | 2024-06-20 16:00 | 111 | 2024-06-18 22:00
149 | Satmasjid | 132 | 142 | 2024-06-13 18:00 | 110 | 2024-06-01 05:00
150 | Savar | 132 | 141 | 2024-06-13 17:00 | 122 | 2024-06-08 12:00
151 | SevenRings | 132 | 143 | 2024-06-13 17:00 | 126 | 2024-06-01 13:00
152 | ShahCement | 132 | 141 | 2024-06-13 18:00 | 123 | 2024-06-05 10:00
153 | Shahjadpur | 132 | 141 | 2024-06-26 04:00 | 132 | 2024-06-01 08:00
154 | Shahjibazar | 132 | 135 | 2024-06-19 11:00 | 119 | 2024-06-11 21:00
155 | Shahmirpur | 132 | 141 | 2024-06-24 19:00 | 124 | 2024-06-27 12:00
156 | Shariatpur | 132 | 135 | 2024-06-19 16:00 | 117 | 2024-06-07 23:00
157 | Sherpur | 132 | 139 | 2024-06-14 08:00 | 110 | 2024-06-17 22:00
158 | Shikalbaha | 132 | 130 | 2024-06-25 22:00 | 116 | 2024-06-28 01:00
159 | Shikalbaha-230 | 132 | 142 | 2024-06-24 19:30 | 108 | 2024-06-13 07:00
160 | Shitalakhya | 132 | 141 | 2024-06-13 18:00 | 122 | 2024-06-05 10:00
161 | Sholosohor | 132 | 139 | 2024-06-24 19:30 | 124 | 2024-06-01 04:00
162 | Shyampur | 132 | 138 | 2024-06-16 21:00 | 113 | 2024-06-10 22:00
163 | Shyampur-230 | 132 | 141 | 2024-06-13 18:30 | 120 | 2024-06-06 11:00
164 | Siddhirganj | 132 | 141 | 2024-06-13 18:00 | 123 | 2024-06-04 15:00
165 | Sirajganj | 132 | 136 | 2024-06-19 17:00 | 122 | 2024-06-28 21:00
166 | Sonargaon | 132 | 142 | 2024-06-13 18:00 | 121 | 2024-06-01 14:00
167 | Sreemongol | 132 | 133 | 2024-06-16 18:00 | 121 | 2024-06-06 23:00
168 | Sreepur | 132 | 136 | 2024-06-19 09:00 | 122 | 2024-06-01 09:00
169 | Srinagar | 132 | 141 | 2024-06-13 18:00 | 121 | 2024-06-01 12:00
170 | SSM | 132 | 132 | 2024-06-21 02:00 | 127 | 2024-06-08 14:00
171 | Sunamganj | 132 | 134 | 2024-06-16 09:00 | 112 | 2024-06-18 01:00
172 | Sylhet | 132 | 133 | 2024-06-17 04:00 | 120 | 2024-06-18 00:00
173 | Sylhet-132 | 132 | 133 | 2024-06-17 07:00 | 120 | 2024-06-17 23:00
174 | Tangail | 132 | 132 | 2024-06-19 15:00 | 110 | 2024-06-08 13:00
175 | Thakurgaon | 132 | 141 | 2024-06-03 21:00 | 106 | 2024-06-28 00:00
176 | TK | 132 | 142 | 2024-06-24 19:30 | 112 | 2024-06-06 18:00
177 | Tongi | 132 | 141 | 2024-06-15 04:00 | 122 | 2024-06-04 15:00
178 | Ullahpara | 132 | 139 | 2024-06-24 18:00 | 113 | 2024-06-21 02:00
179 | Ullon | 132 | 139 | 2024-06-24 14:00 | 122 | 2024-06-01 09:00
180 | Uttara | 132 | 142 | 2024-06-13 17:00 | 123 | 2024-06-08 13:00
181 | UttaraNew | 132 | 142 | 2024-06-13 17:00 | 105 | 2024-06-13 03:00
182 | Zigatola | 132 | 141 | 2024-06-13 18:00 | 122 | 2024-06-01 13:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: June 2024
substation | transformer | voltage_level | Date | Hour | MW(LT) | MVAR(LT)
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 02-06-2024 | 21:00 | 445 | 69
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 02-06-2024 | 21:00 | 445 | 69
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 06-06-2024 | 09:00 | -252 | -103
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 06-06-2024 | 09:00 | -252 | -103
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 19-06-2024 | 18:30 | -178 | 25
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 23-06-2024 | 21:00 | -173 | 6
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 06-06-2024 | 19:00 | 386 | 35
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 06-06-2024 | 19:00 | 386 | 35
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 06-06-2024 | 19:00 | 386 | 35
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 10-06-2024 | 11:00 | 227 | 166
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 01-06-2024 | 16:00 | 291 | 17
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 02-06-2024 | 21:00 | -462 | -136
Meghnaghat 400/230kV Grid Sub-Station | ATR - 2 | 400/230 | 09-06-2024 | 02:00 | 547 | 166
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 13-06-2024 | 19:30 | -366.19 | -80.45
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 04-06-2024 | 21:00 | -271.5 | -55.1
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 24-06-2024 | 11:00 | 295 | 15
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 22-06-2024 | 22:00 | -224 | -50
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 22-06-2024 | 22:00 | -224 | -50
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 22-06-2025 | 22:00 | -224 | -50
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 27-06-2024 | 06:00 | 316 | 46
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 27-06-2024 | 06:00 | 316 | 46
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 08-06-2024 | 01:00 | -99 | -42
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 04-06-2024 | 03:00 | -718 | -27
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 11-06-2024 | 23:00 | 182 | 79
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 11-06-2024 | 23:00 | 182 | 79
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | Date | Hour | MW(LT) | MVAR(LT)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 03-06-2024 | 16:00 | 216 | 93
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 03-06-2024 | 16:00 | 216 | 93
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 11-06-2024 | 11:00 | 214 | 214
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 08-06-2024 | 12:00 | 150 | 50
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 08-06-2024 | 12:00 | 155 | 50
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 17-06-2024 | 23:00 | 244 | 135
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 01-06-2024 | 15:00 | 190 | 30
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 20-06-2024 | 20:00 | 172 | 69
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 20-06-2024 | 20:00 | 129 | 50
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 07-06-2024 | 19:00 | 188 | 64
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 07-06-2024 | 19:30 | 184 | 76
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 07-06-2024 | 19:30 | 238 | 70
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 24-06-2024 | 15:00 | 167 | 27
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 24-06-2024 | 15:00 | 167 | 27
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 23-06-2024 | 13:00 | -102 | 62
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 24-06-2024 | 21:00 | 103 | 68
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 16-06-2024 | 00:00 | 160 | 27
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 16-06-2024 | 00:00 | 160 | 27
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 16-06-2024 | 00:00 | 216 | 40
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 16-06-2024 | 00:00 | 216 | 40
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 08-06-2024 | 15:00 | 180 | 62
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 06-06-2024 | 01:00 | 172 | 62
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 08-06-2024 | 15:00 | 195 | 56
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 23-06-2024 | 19:00 | 238 | 92
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 23-06-2024 | 22:00 | 104 | 0
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 23-06-2024 | 22:00 | 104 | 0
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 06-06-2024 | 05:00 | 146 | 74
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 06-06-2024 | 04:00 | 160 | 71
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 06-06-2024 | 05:00 | 149 | 76
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 08-06-2024 | 10:00 | 75 | 44
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 08-06-2024 | 10:00 | 75 | 44
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 08-06-2024 | 10:00 | 75 | 44
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 10-06-2024 | 00:00 | 135 | 23
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 10-06-2024 | 00:00 | 135 | 23
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 10-06-2024 | 00:00 | 135 | 23
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 10-06-2024 | 00:00 | 135 | 23
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 23-06-2024 | 13:00 | 99 | 44
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 23-06-2024 | 13:00 | 99 | 44
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 23-06-2024 | 13:00 | 99 | 44
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 01-06-2024 | 19:30 | -206 | -80
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 01-06-2024 | 19:30 | -206 | -80
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 01-06-2024 | 16:00 | 216 | 54
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 03-06-2024 | 13:00 | 171 | 62
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 03-06-2024 | 13:00 | 171 | 62
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 03-06-2024 | 15:00 | 163 | 56
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 21-06-2024 | 20:00 | -183 | -41
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 21-06-2024 | 20:00 | -183 | -41
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 21-06-2024 | 20:00 | -183 | -41
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 10-06-2024 | 19:30 | 221 | 48
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 14-06-2024 | 15:00 | 229 | 82
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 24-06-2024 | 07:00 | -86 | -11
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 24-06-2024 | 07:00 | -86 | -10
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 09-06-2024 | 09:00 | 12 | 1
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 01-06-2024 | 09:00 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 03-06-2024 | 15:00 | 178 | 39
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 25-06-2024 | 15:00 | 388 | 68
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 | 230/132 | 25-06-2024 | 15:00 | 388 | 68
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 11-06-2024 | 18:30 | 245 | 128
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 11-06-2024 | 18:30 | 245 | 128
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 09-06-2024 | 09:00 | 131 | 24
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 09-06-2024 | 09:00 | 131 | 24
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 30-06-2024 | 15:00 | 181 | 142
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 30-06-2024 | 15:00 | 181 | 142
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 09-06-2024 | 19:00 | 179 | 72
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 09-06-2024 | 19:00 | 179 | 72
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 07-06-2024 | 12:00 | 210 | 35
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 07-06-2024 | 12:00 | 210 | 35
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 07-06-2024 | 12:00 | 210 | 35
Executive Engineer
Information Management Division
|  |  |  | LDC, PGCB, Dhaka. |  |  | 270

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: June 2024 | [5 empty] | (For Evening Peak) | [8 empty] | Month: June 2024 |  |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2024-06-01 | 15336 | 15750 | 395 | 21:00 | 140 | 0 | 0 | 0 | 25 | 210 | 20 | 0 | 0 | - | 2024-06-01 | 13435 | 13700 | 253 | 12:00 | 210 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | -
2024-06-02 | 15199 | 15950 | 717 | 21:00 | 340 | 0 | 5 | 142 | 10 | 105 | 10 | 0 | 105 | - | 2024-06-02 | 13660 | 13660 | 683 | 12:00 | 280 | 40 | 0 | 0 | 75 | 230 | 58 | 0 | 0 | -
2024-06-03 | 14908 | 15100 | 183 | 20:00 | 38 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 60 | - | 2024-06-03 | 13154 | 13400 | 235 | 12:00 | 78 | 0 | 0 | 0 | 112 | 45 | 0 | 0 | 0 | -
2024-06-04 | 14937 | 15080 | 137 | 19:30 | 40 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | - | 2024-06-04 | 13555 | 13650 | 90 | 12:00 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-05 | 15714 | 16250 | 512 | 21:00 | 280 | 0 | 0 | 0 | 92 | 140 | 0 | 0 | 0 | - | 2024-06-05 | 13612 | 14100 | 466 | 12:00 | 336 | 0 | 0 | 0 | 90 | 40 | 0 | 0 | 0 | -
2024-06-06 | 15340 | 15725 | 368 | 19:30 | 83 | 0 | 0 | 0 | 125 | 160 | 0 | 0 | 0 | - | 2024-06-06 | 13503 | 13630 | 121 | 12:00 | 55 | 20 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | -
2024-06-07 | 13936 | 14093 | 150 | 21:00 | 0 | 0 | 0 | 0 | 0 | 125 | 0 | 0 | 25 | - | 2024-06-07 | 12826 | 13450 | 596 | 12:00 | 320 | 0 | 0 | 0 | 45 | 231 | 0 | 0 | 0 | -
2024-06-08 | 15745 | 12681 | 626 | 21:00 | 155 | 66 | 15 | 0 | 133 | 190 | 0 | 0 | 67 | - | 2024-06-08 | 12681 | 12850 | 161 | 12:00 | 141 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | -
2024-06-09 | 15520 | 15900 | 363 | 21:00 | 90 | 0 | 20 | 0 | 0 | 253 | 0 | 0 | 0 | - | 2024-06-09 | 13656 | 13850 | 185 | 12:00 | 65 | 60 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | -
2024-06-10 | 15257 | 15450 | 184 | 21:00 | 50 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 24 | - | 2024-06-10 | 13193 | 13193 | 54 | 12:00 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-11 | 15798 | 16700 | 861 | 21:00 | 185 | 148 | 10 | 0 | 185 | 285 | 0 | 0 | 48 | - | 2024-06-11 | 14167 | 14550 | 366 | 12:00 | 171 | 85 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | -
2024-06-12 | 15708 | 16450 | 709 | 21:00 | 210 | 100 | 10 | 0 | 50 | 239 | 0 | 0 | 100 | - | 2024-06-12 | 13954 | 14500 | 521 | 12:00 | 260 | 30 | 0 | 0 | 0 | 231 | 0 | 0 | 0 | -
2024-06-13 | 13978 | 14100 | 117 | 21:00 | 10 | 0 | 10 | 0 | 0 | 97 | 0 | 0 | 0 | - | 2024-06-13 | 13723 | 14400 | 647 | 12:00 | 380 | 70 | 22 | 0 | 65 | 110 | 0 | 0 | 0 | -
2024-06-14 | 14426 | 14510 | 80 | 21:00 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | - | 2024-06-14 | 11929 | 11929 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-15 | 13723 | 13723 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-15 | 11757 | 11757 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-16 | 12872 | 12872 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-16 | 10337 | 10337 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-17 | 12967 | 12967 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-17 | 9234 | 9234 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-18 | 11633 | 11633 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-18 | 9490 | 9490 | 0 | 13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-19 | 10636 | 10636 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-19 | 8846 | 8846 | 0 | 9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-20 | 10979 | 10979 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-20 | 9352 | 9352 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-21 | 12708 | 12815 | 102 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | - | 2024-06-21 | 10199 | 10199 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-22 | 13436 | 13436 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2024-06-22 | 10825 | 10825 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-23 | 14398 | 14510 | 107 | 21:00 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 47 | - | 2024-06-23 | 12719 | 12719 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2024-06-24 | 13771 | 15200 | 1365 | 21:00 | 180 | 120 | 290 | 180 | 180 | 160 | 90 | 60 | 105 | - | 2024-06-24 | 13225 | 13500 | 263 | 12:00 | 103 | 0 | 0 | 65 | 0 | 10 | 0 | 0 | 85 | -
2024-06-25 | 13792 | 15600 | 1727 | 19:30 | 255 | 110 | 332 | 230 | 215 | 210 | 90 | 70 | 215 | - | 2024-06-25 | 12757 | 14650 | 1808 | 12:00 | 506 | 226 | 256 | 158 | 202 | 238 | 68 | 54 | 100 | -
2024-06-26 | 13874 | 15400 | 1457 | 21:00 | 350 | 120 | 280 | 150 | 160 | 90 | 120 | 70 | 117 | - | 2024-06-26 | 12981 | 14000 | 973 | 12:00 | 200 | 170 | 140 | 123 | 60 | 130 | 70 | 20 | 60 | -
2024-06-27 | 14215 | 14800 | 559 | 21:00 | 130 | 0 | 4 | 125 | 120 | 125 | 0 | 0 | 55 | - | 2024-06-27 | 13362 | 13800 | 418 | 12:00 | 150 | 0 | 0 | 60 | 58 | 115 | 0 | 0 | 35 | -
2024-06-28 | 13496 | 14800 | 214 | 21:00 | 18 | 0 | 0 | 0 | 0 | 130 | 0 | 18 | 48 | - | 2024-06-28 | 11737 | 13800 | 418 | 12:00 | 150 | 0 | 0 | 60 | 58 | 115 | 0 | 0 | 35 | -
2024-06-29 | 13796 | 14000 | 195 | 20:00 | 101 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 28 |  | 2024-06-29 | 11427 | 11427 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024-06-30 | 13493 | 13493 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2024-06-30 | 12422 | 13100 | 433 | 12:00 | 167 | 0 | 157 | 52 | 0 | 47 | 0 | 10 | 0

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: June 2024
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | PDB | 400 |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | [7 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 |  | √
9 | Meghnaghat CCPP(Summit) | IPP | 335 | [18 empty] | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √
10 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Bibiyana South 400 MW CCPP | BPDB | 383
36 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
37 | Shajibazar 100 MW PP | BPDB | 100
38 | Payra 1320 MW Unit-1 | BCPCL | 622
39 | Kushiara 163 MW CCPP (KP) | IPP | 163
40 | Haripur 360MW CCPP(HPL) | IPP | 360
41 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: June 2024
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15798 | 2024-06-11 | 21:00
2 | Maximum Day Peak Genaration | MW | 14167 | 2024-06-11 | 12:00
3 | Maximum Evening Peak Demand | MW | 16700 | 2024-06-30 | 21:00
4 | Minimum Generation | MW | 8396 | 2024-06-20 | 6:00
5 | Average of the daily evening peak Genaration | MW | 14053.0333 | - | -
6 | Average of the daily day peak Genaration | MW | 12257.2667 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1727 | 2024-06-25 | 19:30
8 | Minimum load shed | MW | 0 | 2024-06-15 | 21:00
9 | Total nos. of load shed days | Day | 22 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 370.9333 | - | -
11 | Total Generation | MkWh | 9230.8798 | - | -
12 | Total Generation by BPDB | MkWh | 2340.8823 | % of total Gen. | 25.36%
13 | Total Generation by IPP | MkWh | 2759.3275 | '' | 29.89%
14 | A) Total Generation by Generation Companies | MkWh | 2477.9567 | '' | 26.84%
| B) Total Generation by REB | MkWh | 69.9332 | " | 0.7576%
| C) Total Generation by RENTAL | MkWh | 239.9504 | " | 2.599%
| D) Total Imported from India (BIPTC) | MkWh | 645.6117 | " | 6.994%
| E) Total Imported from Tripura, India (A.C) | MkWh | 697.2182 | " | 7.553%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4103.4492 | % of total Gen. | 44.45%
| B) Oil | MkWh | 1453.05 | '' | 15.74%
| C) Hydro | MkWh | 80.8001 | '' | 0.8753%
| D) Solar | MkWh | 72.0365 | '' | 0.7804%
| E) Coal | MkWh | 2809.9404 | '' | 30.44%
| F) BIPTC (Import from India) | MkWh | 645.6117 | '' | 6.994%
| G) A.C (Import from Tripura, India) | MkWh | 54.841 | '' | 0.5941%
| H) Wind | MkWh | 11.147 | '' | 0.1208%
16 | Maximun of the daily total Generation . | MkWh | 351.8582 | 2024-06-11
17 | Monthly Load factor | % | 76.6243 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 3109.0183 | - | -
| A) Gas | M.Taka | 0 | - | -
| B) Liquid fuel | M.Taka | 0 | - | -
| C) Coal | M.Taka | 0 | - | -
| D) BIPTC (Import from India) | M.Taka | 2634.0955 | - | -
| E) Tripura(Import from India) | M.Taka | 474.9227 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2415.7161 | 2024-06-05
| A) Gas | M.Taka | 464.5033 | 2024-06-15
| B) Liquid fuel | M.Taka | 1442.7107 | 2024-06-18
| C) Coal | M.Taka | 915.9186 | 2024-06-04
| D) BIPTC (Import from India) | M.Taka | 91.3237 | 2024-06-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 0.33681
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 0.3429
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.46 | 30/06/2024 | 06:00
b) | Actual | FT (MSL) | 82.06 | 30/06/2024 | 06:00
22 | Peak Genaration of May 2023 | MW | 14655 | 2023-06-08 | 20:00
23 | Peak Demand of May 2023 | MW | 14655 | 2023-06-08 | 20:00
24 | Maximum peak Generation recorded upto 30/06/2024 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 30/06/2024 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 30/06/2024 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status | [8 empty] | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable |  |  |  |  | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | [10 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable |  | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant