## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-27 | Tuesday
|  | Date (day): | 2024-08-27 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14649.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15756 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-26 | 2024-08-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 405 | 401 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 2 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 17 | 90 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 131 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 9 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 38 | 39 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 13 | 7 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 17 | 17 | 16 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 1 | 240 | 270 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 131 | 130 | 130 |  | 19 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 54 | 54 | 51 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 1 | 82 | 70 | 85 | 19 |  | Lub Oil problem
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 46 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 14 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 19 | 35 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 33 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1635 | 2414 | 2524 | 2710 | 2529 | 921
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 3 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 218 | 217 | 217 | 217
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 217 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 82 | 105 | 105
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 73 | 65 | 75 | 23 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 84 | 80 | 80 |  | 22 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 100 | 85 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 28 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 150 | 50 | 50 | 250 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 17 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 92 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 90 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 70 | 105 | 105
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 17 | 35 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 0 | 0 | 0 | 0 |  | 1224 | under maint.
61 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 24 | 24 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 1156 | 1151 | 1150 | 1150
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1632 | 2361 | 2483 | 2667 | 578 | 1576
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 217 | 215 | 216
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 280 | 280 | 80 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 250 | 240 | 240 | 240 | 120 |  | Gas shortage
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 230 | 230 | 250 | 150 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 34 | 34 | 38 | 38 | 7 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 25 | 5 | 20 | 20 | 35 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 90 | 12 | 140 |  | 10 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 37 | 35 | 37 |  | 15 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 25 | 35 | 40 | 123 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 85 | 200 | 200
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
76 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 52 | 50 | 90 | 90
77 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 43 |  | 9 | Engine problem
79 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 29 | 90 | 65 | 90 |  | 25 | Engine problem
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 35 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2917 | 1246 | 1503 | 1730 | 1876 | 814 | 66
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 9 | 17 | 20 | 20 | 182 |  | Gas shortage
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 98 | 125 | 98 | 125 | 75 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 78 | 58 | 77 | 38 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 6 | 12 |  | 10 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine prblem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 231 | 249 | 250.6 | 269 | 182 | 29
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 38 | 38 | 38 |  | 32 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 163 | 163 | 163
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 28 | 30 | 30 |  | 36 | GT-8 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 10 | 10 | 10 | 76 |  | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 134 | 136 | 135 | 136 |  | 95 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 260 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 350 | 350 | 350 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 349 | 346 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1353 | 1345 | 1390 | 1391 | 197 | 605
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 898 | 894 | 913 | 913
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 98 |  | 17 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 55 |  | 54 | Engine problem
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 293 | 230 | 230 | 230 | 180 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 42 | 70 | 72 | 33 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 36 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 475 | 554 | 586 | 600 | 634 |  | Unit-2 S/D due to Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1702 | 1720 | 1961 | 2008 | 1574 | 85
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 64 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 5 | 9 | 10 | 10
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 136 | 80 | 80 | 80 |  | 114 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1090 | 1160 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 190 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 237 | 270 | 250 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1688 | 1725 | 1885 | 2006 | 115 | 114
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 23 | 30 | 40 |  | 12 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28 |  |  | Engine problem
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 25 | 46
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 196 | 170 | 180 | 40 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 317 | 350 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 25 | 28 |  | 22 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 43 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113
141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 95 | 95 |  | 18 | Engine problem
142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 762 | 760 | 1200 | 1496 |  | 0 | Unit-2 S/D.
143 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 31 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1321 | 1442 | 2089 | 2555 | 483 | 333
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 60 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 99 | 34 | 99 |  | 14 | Engine problem
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 115 | 75 | 115
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 78 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 223 | 274 | 337 | 274 | 40 | 398
| Total |  |  |  |  | 28166 | 27068 | 11031 | 13033 | 14649.6 | 15756 | 6512 | 4127
A. |  | 2024-08-26 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 13033 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 10029 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13225 | MW
3 | Day peak Generation : |  |  | 11031 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12737.19 | MW
4 | Evening peak Generation : |  |  | 13033 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 183 | MW
5 | Total Energy Generation : |  | 278.8691 | MKWHr | By Solar | 2.4339 | MKWHr
| By Gas : | 124.2833 | MKWHr |  | By Oil: | 31.4165 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 92.2134 | MKWHr |  | By Hydro: | 5.2649 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.58608 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6512 | MW | Dhaka | 4688.99 | 4628.99 |  | 60 |  | 18:00 |  | 66.85
|  |  | For Plants S/D or M/C prob = |  |  | 4127 | MW | Chittagong | 1143.5 | 1143.5 |  | 0 |  | 19:00 |  | 151.845
|  |  | Total = |  |  | 10639 | MW | Khulna | 1482.7 | 1482.7 |  | 0 |  | 19:30 |  | 172.855
7 | Total Gas Supplied : |  |  | 886.3 | MMCFD |  |  | Rajshahi | 1298 | 1298 |  | 0 |  | 20:00 |  | 183.36
8 | Fuel Cost : | i) Gas : | Taka | 370447989.424 | ii) Oil : | Taka | 572448684.58 | Comilla | 1037 | 1037 |  | 0 |  | 21:00 |  | 182
|  | iii) Coal : | Taka | 604871865.71 | Total | Taka | 1547768539.714 | Mymensingh | 1166 | 1086 |  | 80 |  | 22:00 |  | 228.245
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 4766.85 | MKWHr. | Sylhet | 601 | 601 |  | 0 |  | 23:00 |  | 215.83
| ii) During Peak Demand : |  |  | 200 | MW (W to E) at | 20:00 | hrs | Barisal | 374 | 374 |  | 0 |  | 24:00 |  | 280.77
| iii) Maximum : |  |  | 200 | MW at | 20:00 | hrs | Rangpur | 946 | 903 |  | 43
10 | Maximum Temperature in Dhaka was |  |  |  | 30°C |  |  | Total | 12737.19 | 12554.19 |  | 183
B. |  | 2024-08-27 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 31.4°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15756 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
4 | Reserve(Generation end) |  |  |  | 1756 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 299.7815 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10428 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.5171 | MKWHr. | ii) HVDC Flow at Peak Time |  | 894 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.1539 | MKWHr. | iii) Maximum HVDC Flow : |  | 899 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.77 |  | (b) Today: | 108.9 |  | (c) Rule Curve: |  | 97.35

## YesterdayGen
2024-08-26 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 260 | 128 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 58 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 0 | 23 | 24 | 13 | 0 | 0 | 139 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 250 | 215 | 0 | 40 | 38 | 26 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 48 | 18 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 167 | 0 | 0 | 97 | 0 | 132 | 0 | 0 | 51 | 10 | 323 | 49 | 17 | 34 | 0 | 52 | 0 | 17 | 17 | 9 | 0 | 320 | 69 | 0 | 90 | 17 | 0 | 35 | 0 | 70 | 17 | 230 | 17 | 0 | 0 | 25 | 1157 | 0 | 0 | 0 | 0 |  | 897 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 28 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 349 | 35 | 0 | 70 | 0 | 77 | 0 | 0 | 95 | 1244 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 527 | 0 | 250 | 760 | 0 | 0 | 0 | 0 |  | 6590 | 5318 | 11908 | 3453 | 897 | 1458 | 0 | 1653 | 4000 | 219 | 0 | 155 | 48 | 0 | 25 | 307.51 | 108.72
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 300 | 129 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 24 | 82 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 16 | 23 | 24 | 13 | 0 | 0 | 140 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 250 | 215 | 0 | 40 | 38 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 18 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 95 | 0 | 0 | 97 | 0 | 132 | 0 | 0 | 51 | 0 | 288 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 0 | 320 | 70 | 0 | 54 | 0 | 0 | 35 | 0 | 67 | 17 | 230 | 0 | 0 | 0 | 27 | 1156 | 0 | 0 | 0 | 0 |  | 897 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 337 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 95 | 1120 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 539 | 0 | 250 | 761 | 0 | 0 | 0 | 0 |  | 6320 | 5070 | 11390 | 3438 | 897 | 1506 | 0 | 1286 | 3888 | 220 | 0 | 82 | 46 | 0 | 27 | 267.4 | 108.73
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 420 | 129 | 0 | 0 | 15 | 300 | 0 | 0 | 0 | 8 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 23 | 24 | 14 | 0 | 0 | 140 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 250 | 215 | 0 | 45 | 38 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 132 | 0 | 0 | 34 | 0 | 302 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 0 | 330 | 31 | 0 | 0 | 0 | 0 | 19 | 0 | 67 | 17 | 230 | 0 | 0 | 0 | 30 | 1155 | 0 | 0 | 0 | 0 |  | 898 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 350 | 0 | 0 | 70 | 0 | 70 | 0 | 0 | 70 | 1010 | 180 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 490 | 0 | 238 | 763 | 0 | 0 | 0 | 0 |  | 6170 | 4875 | 11045 | 3502 | 898 | 1691 | 0 | 892 | 3718 | 220 | 0 | 48 | 46 | 0 | 30 | 253.075 | 108.74
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 420 | 129 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 24 | 14 | 0 | 0 | 140 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 250 | 215 | 0 | 45 | 38 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 19 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 132 | 0 | 0 | 17 | 0 | 287 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 67 | 17 | 230 | 0 | 0 | 0 | 17 | 1156 | 0 | 0 | 0 | 0 |  | 897 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 353 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 50 | 980 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 492 | 0 | 164 | 764 | 0 | 0 | 0 | 0 |  | 6045 | 4813 | 10858 | 3573 | 897 | 1733 | 0 | 724 | 3618 | 220 | 0 | 32 | 44 | 0 | 17 | 250.21 | 108.75
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 420 | 128 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 24 | 14 | 0 | 0 | 138 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 250 | 216 | 0 | 45 | 38 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 19 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 132 | 0 | 0 | 17 | 0 | 287 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 67 | 17 | 230 | 0 | 0 | 0 | 42 | 1156 | 0 | 0 | 0 | 0 |  | 897 | 0 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 327 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 35 | 980 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 463 | 0 | 150 | 763 | 0 | 0 | 0 | 0 |  | 6061 | 4703 | 10764 | 3573 | 897 | 1695 | 0 | 688 | 3571 | 218 | 0 | 32 | 48 | 0 | 42 | 129.88 | 108.76
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 350 | 128 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 23 | 24 | 14 | 0 | 0 | 136 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 275 | 217 | 0 | 45 | 38 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 19 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 118 | 0 | 0 | 17 | 0 | 290 | 49 | 17 | 0 | 0 | 15 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 16 | 17 | 230 | 0 | 0 | 0 | 51 | 1155 | 0 | 0 | 1 | 0 |  | 898 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 317 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 880 | 180 | 0 | 0 | 0 | 1 | 74 | 0 | 0 | 460 | 0 | 150 | 777 | 4 | 0 | 0 | 0 |  | 5829 | 4344 | 10173 | 3432 | 898 | 1512 | 0 | 495 | 3482 | 216 | 0 | 32 | 48 | 7 | 51 | 73.535 | 108.77
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 |  | 0 | 350 | 129 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 14 | 8 | 0 | 136 | 80 | 0 | 0 | 0 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 280 | 275 | 188 | 0 | 45 | 38 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 44 | 18 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 130 | 0 | 0 | 17 | 0 | 290 | 49 | 17 | 0 | 1 | 15 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 13 | 0 | 0 | 0 | 17 | 2 | 16 | 17 | 230 | 0 | 0 | 0 | 47 | 1152 | 0 | 0 | 1 | 0 |  | 898 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 322 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 870 | 180 | 0 | 0 | 0 | 1 | 74 | 0 | 0 | 414 | 4 | 150 | 765 | 22 | 0 | 0 | 1 |  | 5773 | 4256 | 10029 | 3313 | 898 | 1515 | 0 | 507 | 3411 | 216 | 0 | 32 | 44 | 46 | 47 | 58.255 | 108.78
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 |  | 0 | 350 | 130 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 24 | 14 | 8 | 0 | 136 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 315 | 275 | 188 | 0 | 45 | 34 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 40 | 17 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 275 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 132 | 1 | 0 | 17 | 0 | 290 | 49 | 17 | 0 | 2 | 15 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 10 | 0 | 0 | 0 | 17 | 7 | 16 | 17 | 230 | 0 | 0 | 0 | 29 | 1155 | 0 | 0 | 0 | 0 |  | 898 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 323 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 870 | 180 | 0 | 0 | 0 | 10 | 74 | 0 | 0 | 411 | 9 | 150 | 759 | 67 | 0 | 0 | 11 |  | 5756 | 4320 | 10076 | 3335 | 898 | 1496 | 0 | 507 | 3405 | 216 | 0 | 32 | 40 | 118 | 29 | 61.12 | 108.8
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 |  | 0 | 420 | 92 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 23 | 24 | 13 | 17 | 0 | 137 | 80 | 0 | 0 | 0 | 222 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 290 | 285 | 194 | 0 | 45 | 34 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 36 | 17 | 0 | 0 | 1 | 40 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 132 | 3 | 0 | 0 | 0 | 289 | 49 | 34 | 0 | 2 | 0 | 0 | 0 | 0 | 9 | 0 | 320 | 0 | 25 | 0 | 0 | 0 | 17 | 7 | 16 | 32 | 230 | 0 | 0 | 0 | 21 | 1153 | 0 | 0 | 5 | 20 |  | 898 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 353 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 880 | 180 | 0 | 0 | 1 | 7 | 36 | 0 | 0 | 411 | 29 | 150 | 766 | 157 | 0 | 0 | 19 |  | 5828 | 4447 | 10275 | 3316 | 898 | 1576 | 0 | 480 | 3422 | 217 | 0 | 32 | 36 | 257 | 21 | 42.975 | 108.82
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 |  | 0 | 420 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 11 | 23 | 24 | 13 | 17 | 0 | 138 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 310 | 300 | 189 | 0 | 40 | 34 | 31 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 46 | 11 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 132 | 4 | 0 | 0 | 0 | 316 | 49 | 34 | 0 | 3 | 0 | 0 | 0 | 0 | 9 | 0 | 340 | 0 | 26 | 0 | 0 | 0 | 17 | 14 | 16 | 35 | 230 | 0 | 0 | 0 | 25 | 1153 | 0 | 0 | 7 | 33 |  | 898 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 355 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 900 | 220 | 0 | 0 | 1 | 11 | 36 | 0 | 0 | 404 | 13 | 184 | 764 | 113 | 0 | 0 | 22 |  | 5838 | 4592 | 10430 | 3497 | 898 | 1523 | 0 | 492 | 3466 | 218 | 0 | 16 | 46 | 216 | 25 | 38.2 | 108.84
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 11 | 23 | 0 | 13 | 17 | 0 | 138 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 330 | 250 | 194 | 0 | 40 | 34 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 48 | 11 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 0 | 0 | 0 | 98 | 0 | 132 | 3 | 0 | 0 | 0 | 332 | 49 | 34 | 0 | 4 | 0 | 0 | 0 | 0 | 9 | 0 | 359 | 0 | 36 | 0 | 0 | 0 | 17 | 17 | 16 | 35 | 230 | 0 | 0 | 0 | 28 | 1153 | 0 | 0 | 14 | 33 |  | 898 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 360 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 970 | 220 | 0 | 0 | 4 | 23 | 36 | 0 | 0 | 404 | 15 | 200 | 764 | 103 | 0 | 0 | 53 |  | 5942 | 4753 | 10695 | 3569 | 898 | 1555 | 0 | 500 | 3552 | 218 | 0 | 16 | 48 | 278 | 28 | 38 | 108.85
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 2 | 335 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 17 | 9 | 17 | 0 | 11 | 22 | 24 | 13 | 17 | 0 | 138 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 250 | 199 | 0 | 40 | 34 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | 9 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 1 | 0 | 0 | 98 | 0 | 132 | 3 | 0 | 0 | 0 | 349 | 48 | 34 | 0 | 4 | 0 | 0 | 0 | 0 | 9 | 0 | 349 | 1 | 51 | 46 | 0 | 0 | 17 | 14 | 29 | 19 | 230 | 0 | 0 | 0 | 24 | 1156 | 0 | 0 | 35 | 33 |  | 898 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1090 | 220 | 0 | 0 | 4 | 36 | 36 | 0 | 0 | 475 | 13 | 237 | 762 | 78 | 0 | 0 | 31 |  | 6097 | 4934 | 11031 | 3600 | 898 | 1548 | 0 | 589 | 3780 | 218 | 0 | 16 | 52 | 273 | 24 | 56 | 108.86
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 333 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 11 | 22 | 24 | 13 | 17 | 0 | 140 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 280 | 250 | 216 | 0 | 40 | 37 | 12 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 54 | 6 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 163 | 0 | 29 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 40 | 0 | 0 | 98 | 0 | 132 | 7 | 0 | 12 | 0 | 350 | 48 | 34 | 0 | 3 | 0 | 0 | 0 | 0 | 9 | 0 | 336 | 34 | 44 | 90 | 0 | 0 | 17 | 3 | 74 | 34 | 230 | 0 | 0 | 0 | 12 | 1153 | 0 | 0 | 44 | 33 |  | 898 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 313 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 1170 | 220 | 0 | 0 | 1 | 28 | 95 | 0 | 0 | 501 | 27 | 260 | 761 | 173 | 0 | 0 | 15 |  | 6402 | 5194 | 11596 | 3635 | 898 | 1524 | 0 | 948 | 3906 | 220 | 0 | 16 | 54 | 350 | 12 | 52 | 108.86
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 24 | 55 | 55 | 0 | 15 | 22 | 24 | 12 | 17 | 0 | 140 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 290 | 250 | 212 | 0 | 40 | 37 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 50 | 6 | 0 | 0 | 1 | 39 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 45 | 0 | 0 | 97 | 0 | 132 | 4 | 0 | 17 | 0 | 350 | 58 | 34 | 0 | 3 | 0 | 0 | 0 | 0 | 9 | 0 | 333 | 53 | 32 | 90 | 0 | 0 | 17 | 9 | 89 | 35 | 230 | 0 | 0 | 0 | 26 | 1158 | 0 | 0 | 35 | 33 |  | 897 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 343 | 0 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 1110 | 180 | 0 | 0 | 6 | 44 | 115 | 0 | 0 | 464 | 21 | 200 | 768 | 104 | 0 | 0 | 54 |  | 6395 | 4984 | 11379 | 3490 | 897 | 1505 | 0 | 1062 | 3760 | 220 | 0 | 16 | 50 | 320 | 26 | 53 | 108.85
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 15 | 22 | 24 | 12 | 8 | 0 | 140 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 290 | 275 | 211 | 0 | 40 | 37 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 56 | 6 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 163 | 0 | 26 | 10 | 0 | 135 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 45 | 0 | 0 | 97 | 0 | 131 | 8 | 0 | 17 | 0 | 352 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 345 | 53 | 26 | 90 | 0 | 0 | 17 | 19 | 90 | 35 | 230 | 0 | 0 | 0 | 11 | 1152 | 0 | 0 | 20 | 33 |  | 899 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 353 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 1100 | 220 | 0 | 0 | 1 | 25 | 115 | 0 | 0 | 459 | 24 | 200 | 770 | 67 | 0 | 0 | 14 |  | 6429 | 4979 | 11408 | 3605 | 899 | 1569 | 0 | 1047 | 3741 | 220 | 0 | 16 | 56 | 211 | 11 | 87.86 | 108.86
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 15 | 22 | 24 | 12 | 8 | 0 | 140 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 285 | 270 | 212 | 0 | 35 | 37 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 46 | 10 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 45 | 0 | 0 | 96 | 0 | 120 | 4 | 0 | 17 | 0 | 350 | 58 | 17 | 0 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 343 | 53 | 16 | 90 | 0 | 0 | 17 | 10 | 90 | 35 | 230 | 0 | 0 | 0 | 18 | 1151 | 0 | 0 | 11 | 2 |  | 899 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 327 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 1100 | 220 | 0 | 0 | 2 | 23 | 74 | 0 | 0 | 470 | 7 | 200 | 750 | 105 | 0 | 0 | 18 |  | 6337 | 4913 | 11250 | 3598 | 899 | 1526 | 0 | 994 | 3731 | 220 | 0 | 16 | 46 | 200 | 18 | 85.95 | 108.86
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 15 | 22 | 24 | 12 | 8 | 0 | 140 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 285 | 270 | 215 | 0 | 32 | 34 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 46 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 275 | 0 | 2 | 0 | 30 | 0 | 0 | 96 | 0 | 130 | 1 | 0 | 17 | 0 | 350 | 58 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 346 | 38 | 4 | 35 | 0 | 0 | 17 | 6 | 30 | 35 | 230 | 0 | 0 | 0 | 16 | 1153 | 0 | 0 | 4 | 0 |  | 899 | 0 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 331 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1080 | 220 | 0 | 0 | 0 | 21 | 35 | 0 | 0 | 472 | 9 | 200 | 751 | 24 | 0 | 0 | 4 |  | 6137 | 4762 | 10899 | 3592 | 899 | 1518 | 0 | 801 | 3716 | 220 | 0 | 16 | 46 | 75 | 16 | 86.905 | 108.87
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 400 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 15 | 22 | 24 | 11 | 8 | 0 | 140 | 80 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 320 | 305 | 211 | 0 | 23 | 35 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 15 | 42 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 0 | 2 | 0 | 30 | 0 | 0 | 106 | 0 | 131 | 0 | 16 | 17 | 1 | 386 | 58 | 17 | 0 | 0 | 5 | 0 | 0 | 0 | 9 | 0 | 376 | 34 | 0 | 35 | 0 | 0 | 17 | 0 | 19 | 35 | 230 | 0 | 0 | 0 | 16 | 1156 | 0 | 0 | 1 | 0 |  | 894 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 6 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 353 | 17 | 0 | 0 | 0 | 85 | 0 | 1 | 0 | 1060 | 220 | 0 | 0 | 0 | 1 | 35 | 0 | 0 | 420 | 1 | 200 | 764 | 11 | 0 | 0 | 1 |  | 6208 | 4772 | 10980 | 3707 | 894 | 1510 | 0 | 869 | 3660 | 220 | 0 | 46 | 42 | 16 | 16 | 66.85 | 108.88
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.845 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 42 | 131 | 0 | 0 | 0 | 0 | 27 | 55 | 55 | 0 | 16 | 22 | 24 | 11 | 17 | 0 | 136 | 80 | 0 | 0 | 5 | 217 | 0 | 0 | 0 |  | 12 | 44 | 85 | 0 | 0 | 1 | 0 | 22 | 0 | 0 | 0 | 280 | 265 | 201 | 0 | 24 | 32 | 5 | 0 | 51 | 0 | 19 | 14 | 0 | 0 | 0 | 15 | 50 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 137 | 0 | 0 | 0 | 315 | 8 | 2 | 0 | 80 | 0 | 0 | 124 | 0 | 131 | 0 | 100 | 53 | 37 | 350 | 77 | 52 | 34 | 0 | 150 | 1 | 18 | 34 | 9 | 66 | 346 | 70 | 0 | 144 | 22 | 0 | 17 | 0 | 48 | 35 | 230 | 54 | 0 | 0 | 14 | 1151 | 0 | 0 | 0 | 0 |  | 894 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 9 | 16 | 0 | 0 | 0 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 354 | 19 | 0 | 30 | 0 | 99 | 0 | 0 | 70 | 1130 | 220 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 568 | 0 | 270 | 766 | 0 | 0 | 0 | 0 |  | 7344 | 5297 | 12641 | 3581 | 894 | 1599 | 0 | 1914 | 3946 | 216 | 0 | 427 | 50 | 0 | 14 | 151.845 | 108.89
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 74 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 22 | 24 | 11 | 17 | 0 | 136 | 80 | 0 | 0 | 25 | 217 | 0 | 0 | 0 |  | 12 | 72 | 84 | 0 | 0 | 6 | 0 | 26 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 24 | 32 | 5 | 0 | 51 | 0 | 37 | 25 | 0 | 0 | 0 | 18 | 54 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 137 | 0 | 0 | 0 | 275 | 12 | 2 | 0 | 80 | 0 | 0 | 124 | 0 | 131 | 0 | 100 | 120 | 113 | 350 | 77 | 52 | 87 | 0 | 150 | 8 | 48 | 34 | 9 | 100 | 346 | 77 | 0 | 162 | 65 | 0 | 17 | 0 | 90 | 35 | 230 | 36 | 0 | 0 | 20 | 1151 | 0 | 0 | 0 | 0 |  | 893 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 321 | 30 | 0 | 35 | 0 | 99 | 0 | 0 | 70 | 1120 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 547 | 0 | 270 | 758 | 0 | 0 | 0 | 0 |  | 7830 | 5139 | 12969 | 3504 | 893 | 1500 | 0 | 2422 | 3906 | 216 | 0 | 454 | 54 | 0 | 20 | 172.855 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 22 | 24 | 7 | 17 | 0 | 137 | 80 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 12 | 73 | 84 | 0 | 0 | 6 | 0 | 28 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 25 | 34 | 5 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 50 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 136 | 0 | 0 | 0 | 260 | 12 | 2 | 0 | 240 | 0 | 0 | 125 | 0 | 131 | 0 | 100 | 85 | 90 | 350 | 78 | 52 | 82 | 0 | 150 | 17 | 17 | 34 | 9 | 100 | 346 | 82 | 0 | 162 | 70 | 0 | 17 | 0 | 90 | 35 | 230 | 17 | 0 | 0 | 24 | 1151 | 0 | 0 | 0 | 0 |  | 894 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 317 | 42 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 1160 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 554 | 0 | 270 | 760 | 0 | 0 | 0 | 0 |  | 7872 | 5161 | 13033 | 3506 | 894 | 1483 | 0 | 2468 | 3955 | 217 | 0 | 436 | 50 | 0 | 24 | 183.36 | 108.88
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 16 | 23 | 17 | 8 | 17 | 0 | 137 | 80 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 12 | 74 | 51 | 0 | 0 | 6 | 0 | 30 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 25 | 38 | 5 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 52 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 25 | 10 | 0 | 136 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 258 | 0 | 0 | 126 | 0 | 131 | 0 | 100 | 85 | 10 | 356 | 78 | 52 | 87 | 0 | 150 | 17 | 17 | 34 | 9 | 100 | 346 | 85 | 0 | 162 | 72 | 0 | 17 | 0 | 90 | 35 | 250 | 17 | 0 | 0 | 24 | 1157 | 0 | 0 | 0 | 0 |  | 730 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 354 | 51 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 1160 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 559 | 0 | 270 | 771 | 0 | 0 | 0 | 0 |  | 7811 | 5173 | 12984 | 3609 | 730 | 1582 | 0 | 2389 | 3977 | 217 | 0 | 404 | 52 | 0 | 24 | 182 | 108.89
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 17 | 23 | 17 | 12 | 17 | 0 | 137 | 80 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 12 | 32 | 51 | 0 | 0 | 6 | 0 | 36 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 25 | 38 | 5 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 52 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 25 | 10 | 0 | 136 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 258 | 0 | 0 | 126 | 0 | 131 | 0 | 100 | 68 | 10 | 364 | 78 | 52 | 34 | 0 | 80 | 0 | 17 | 34 | 9 | 100 | 360 | 86 | 0 | 162 | 60 | 0 | 17 | 0 | 90 | 35 | 250 | 17 | 0 | 0 | 22 | 1154 | 0 | 0 | 0 | 0 |  | 898 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 354 | 17 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 1140 | 220 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 558 | 0 | 270 | 759 | 0 | 0 | 0 | 0 |  | 7628 | 5183 | 12811 | 3643 | 898 | 1579 | 0 | 2097 | 3941 | 217 | 0 | 362 | 52 | 0 | 22 | 228.245 | 108.89
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 23 | 17 | 12 | 8 | 0 | 138 | 80 | 0 | 0 | 8 | 219 | 0 | 0 | 0 |  | 12 | 8 | 17 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 25 | 38 | 8 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 56 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 25 | 10 | 0 | 136 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 260 | 0 | 0 | 127 | 0 | 132 | 0 | 100 | 68 | 10 | 361 | 78 | 52 | 34 | 0 | 80 | 0 | 17 | 23 | 9 | 100 | 346 | 69 | 0 | 162 | 17 | 0 | 17 | 0 | 90 | 35 | 250 | 17 | 0 | 0 | 21 | 1154 | 0 | 0 | 0 | 0 |  | 898 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 354 | 17 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 1160 | 220 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 618 | 0 | 270 | 790 | 0 | 0 | 0 | 0 |  | 7503 | 5271 | 12774 | 3624 | 898 | 1608 | 0 | 2015 | 4053 | 218 | 0 | 281 | 56 | 0 | 21 | 215.83 | 108.89
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 41 | 131 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 18 | 23 | 17 | 12 | 8 | 0 | 138 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 25 | 38 | 10 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 52 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 195 | 0 | 0 | 121 | 0 | 132 | 0 | 100 | 68 | 10 | 349 | 78 | 35 | 34 | 0 | 80 | 0 | 17 | 34 | 9 | 100 | 346 | 85 | 0 | 108 | 17 | 0 | 17 | 0 | 90 | 35 | 250 | 17 | 0 | 0 | 23 | 1155 | 0 | 0 | 0 | 0 |  | 898 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 353 | 17 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 622 | 0 | 270 | 891 | 0 | 0 | 0 | 0 |  | 7220 | 5386 | 12606 | 3543 | 898 | 1554 | 0 | 1819 | 4243 | 218 | 0 | 256 | 52 | 0 | 23 | 280.77 | 108.9
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9586800 | 0 |  | 0 | 9541500 | 1274618 | 0 | 0 | 762698 | 7427958 | 0 | 0 | 0 | 660240 | 1304160 | 0 | 0 | 0 | 0 | 411480 | 839090 | 835212 | 0 | 352800 | 533520 | 548400 | 290000 | 228960 | 0 | 3328936 | 1936000 | 0 | 0 | 58649 | 5215654 | 0 | 0 | 0 |  | 198480 | 240803 | 285355 | 0 | 0 | 23520 | 0 | 566400 | 0 | 0 | 0 | 7391100 | 6400000 | 5045000 | 0 | 879130 | 864432 | 510720 | 0 | 1176383 | 0 | 178112 | 144110 | 0 | 0 | 0 | 387920 | 1153920 | 321600 | 0 | 0 | 10200 | 922000 | 0 | 0 | 0 | 3575454 | 0 | 662688 | 264907 | 0 | 3237290 | 0 | 0 | 0 | 7132000 | 239568 | 48384 | 0 | 1997236 | 0 | 0 | 2503200 | 0 | 3159792 | 35235 | 562560 | 852480 | 237527 | 8299000 | 1384800 | 702720 | 494291 | 22156 | 895745 | 51783 | 178980 | 240540 | 223440 | 528960 | 8138700 | 906240 | 265810 | 1592640 | 297327 | 0 | 473040 | 120309 | 1440960 | 700560 | 5741600 | 152218 | 0 | 0 | 586080 | 27869090 | 0 | 0 | 215155 | 206000 |  | 21517090 | 0 | 6494976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2745000 | 168399 | 176928 | 0 | 0 | 0 | 105676 | 0 | 236432 | 0 | 0 | 37593 | 0 | 201600 | 0 | 0 | 105012 | 1405090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4714227 | 0 | 8274981 | 293760 | 0 | 530688 | 0 | 1396425 | 0 | 31872 | 588960 | 27541100 | 5205200 | 0 | 0 | 21120 | 267840 | 2100480 | 0 | 0 | 11818180 | 171852 | 5171000 | 18408941 | 1021680 | 0 | 1705 | 249000 |  | 158072325 | 121002807 | 279075132 | 86592759 | 21517090 | 37690562 | 0 | 28674501 | 92213401 | 5264936 | 0 | 2741949 | 1153920 | 2433934 | 586080 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27609984 | 0 |  | 0 | 30341970 | 4359193.56 | 0 | 0 | 13438738.76 | 22655271.9 | 0 | 0 | 0 | 11851308 | 25326787.2 | 0 | 0 | 0 | 0 | 7513624.8 | 13224058.4 | 15276027.48 | 0 | 264600 | 0 | 0 | 0 | 4100673.6 | 0 | 0 | 0 | 0 | 0 | 1110812.06 | 16637936.26 | 0 | 0 | 0 |  | 3491263.2 | 4240540.83 | 5110708.05 | 0 | 0 | 387139.2 | 0 | 0 | 0 | 0 | 0 | 20621169 | 19584000 | 16749400 | 0 | 2839589.9 | 2913135.84 | 2236953.6 | 0 | 4717295.83 | 0 | 3189985.92 | 2602626.6 | 0 | 0 | 0 | 290940 | 7569715.2 | 1000176 | 0 | 0 | 0 | 3595800 | 0 | 0 | 0 | 12228052.68 | 0 | 3677918.4 | 1382814.54 | 0 | 9032039.1 | 0 | 0 | 0 | 22037880 | 179676 | 36771.84 | 0 | 40743614.4 | 0 | 0 | 48086472 | 0 | 55643937.12 | 0 | 10019193.6 | 14790528 | 3938197.66 | 21992350 | 26394288 | 13183027.2 | 8867580.54 | 0 | 14645430.75 | 1006661.52 | 3210901.2 | 4596719.4 | 4336970.4 | 9420777.6 | 21648942 | 15469516.8 | 0 | 29129385.6 | 4989147.06 | 0 | 8453224.8 | 0 | 25966099.2 | 11867486.4 | 17052552 | 2143229.44 | 0 | 0 | 0 | 164427631 | 0 | 0 | 0 | 0 |  | 60463022.9 | 0 | 19160179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8674200 | 798211.26 | 3050238.72 | 0 | 0 | 0 | 1892657.16 | 0 | 3974421.92 | 0 | 0 | 673290.63 | 0 | 3610656 | 0 | 0 | 79494.084 | 15498142.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15698375.91 | 0 | 24162944.52 | 5017420.8 | 0 | 10518236.16 | 0 | 27816786 | 0 | 0 | 11684966.4 | 178466328 | 16188172 | 0 | 0 | 0 | 0 | 36443328 | 0 | 0 | 86272714 | 0 | 38523950 | 121683100.01 | 0 | 0 | 0 | 0 |  | 925450441.44 | 690350836.374 | 1615801277.814 | 251994501.434 | 60463022.9 | 118453487.99 | 0 | 522286407.43 | 604871865.71 | 0 | 0 | 50162277.15 | 7569715.2 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 2 | 335 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 17 | 9 | 17 | 0 | 11 | 22 | 24 | 13 | 17 | 0 | 138 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 280 | 250 | 199 | 0 | 40 | 34 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 52 | 9 | 0 | 0 | 2 | 39 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 1 | 0 | 0 | 98 | 0 | 132 | 3 | 0 | 0 | 0 | 349 | 48 | 34 | 0 | 4 | 0 | 0 | 0 | 0 | 9 | 0 | 349 | 1 | 51 | 46 | 0 | 0 | 17 | 14 | 29 | 19 | 230 | 0 | 0 | 0 | 24 | 1156 | 0 | 0 | 35 | 33 |  | 898 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1090 | 220 | 0 | 0 | 4 | 36 | 36 | 0 | 0 | 475 | 13 | 237 | 762 | 78 | 0 | 0 | 31 |  | 11031 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 16 | 22 | 24 | 7 | 17 | 0 | 137 | 80 | 0 | 0 | 8 | 217 | 0 | 0 | 0 | 0 | 12 | 73 | 84 | 0 | 0 | 6 | 0 | 28 | 0 | 0 | 0 | 280 | 240 | 217 | 0 | 25 | 34 | 5 | 0 | 51 | 0 | 37 | 8 | 0 | 0 | 0 | 18 | 50 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 136 | 0 | 0 | 0 | 260 | 12 | 2 | 0 | 240 | 0 | 0 | 125 | 0 | 131 | 0 | 100 | 85 | 90 | 350 | 78 | 52 | 82 | 0 | 150 | 17 | 17 | 34 | 9 | 100 | 346 | 82 | 0 | 162 | 70 | 0 | 17 | 0 | 90 | 35 | 230 | 17 | 0 | 0 | 24 | 1151 | 0 | 0 | 0 | 0 |  | 894 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 16 | 0 | 0 | 0 | 23 | 0 | 43 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 317 | 42 | 0 | 35 | 0 | 99 | 0 | 0 | 35 | 1160 | 190 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 554 | 0 | 270 | 760 | 0 | 0 | 0 | 0 |  | 13033 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 100 | 80 | 55 | 335 | 0 | 0 | 50 | 90 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 25 | 12 | 17 | 0 | 137 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 75 | 80 | 0 | 0 | 50 | 0 | 20 | 0 | 0 | 0 | 280 | 240 | 216 | 0 | 40 | 38 | 20 | 0 | 51 | 0 | 37 | 43 | 0 | 0 |  | 18 | 90 | 20 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 280 | 0 | 0 | 125 | 0 | 130 | 0 | 100 | 200 | 140 | 350 | 77 | 54 | 105 | 0 | 50 | 54 | 110 | 114 | 9 | 100 | 350 | 85 | 0 | 162 | 105 | 0 | 35 | 0 | 90 | 35 | 250 | 163 | 0 | 0 | 60 | 1150 | 0 | 0 |  |  |  | 913 | 0 | 230 | 0 | 98 | 0 | 0 | 0 | 40 | 55 | 0 | 80 | 10 | 110 | 0 | 0 | 0 | 40 | 20 | 90 | 28 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 72 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 307 | 1496 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 100 | 80 | 55 | 335 | 0 | 0 | 50 | 90 | 16 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 16 | 23 | 25 | 12 | 16 | 0 | 137 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 65 | 80 | 0 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 35 | 8 | 0 | 0 |  | 18 | 90 | 20 | 0 | 0 | 1.6 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 270 | 0 | 0 | 98 | 0 | 130 | 20 | 85 | 200 | 12 | 350 | 58 | 54 | 105 | 5 | 50 | 54 | 92 | 114 | 9 | 90 | 350 | 70 | 50 | 162 | 105 | 0 | 17 | 35 | 65 | 35 | 230 | 35 | 0 | 0 | 42 | 1150 | 0 | 0 | 70 |  |  | 913 | 0 | 230 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 80 | 10 | 64 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 350 | 70 | 0 | 113 | 0 | 34 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 75 | 0 | 0 | 586 | 30 | 250 | 1200 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 17 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 250 | 202 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 15 | 0 | 0 | 98 | 0 | 118 | 5 | 12 | 17 | 0 | 309 | 49 | 0 | 17 | 2 | 15 | 0 | 0 | 0 | 9 | 12 | 320 | 0 | 20 | 0 | 0 | 0 | 17 | 11 | 61 | 17 | 250 | 0 | 0 | 0 | 5 | 1158 | 0 | 0 | 28 | 0 | 0 | 898 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 346 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 890 | 180 | 0 | 0 | 2 | 60 | 52 | 0 | 0 | 495 | 6 | 170 | 1182 | 45 | 0 | 0 | 12 | 0 |  |  |  | 124283321 | 21517090 | 0 | 92213401 | 31416450 | 1153920 | 2433934 | 586080 | 5264936 |  |  | 278869132
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 124.2833 | 21.5171 | 0 | 92.2134 | 31.4165 | 1.1539 | 2.4339 | 0.58608 | 5.2649
| Minimum Generation |  | 10029 | 7:00
| Highest Generation |  | 13033 | 20:00 | [129 empty] | 0 | [74 empty] | 278.8691
| Day Peak Generation |  | 11031 | 12:00
| Evening Peak Generation |  | 13033 | 20:00 | [204 empty] | 202699852
| HVDC Max Flow |  | 899 | 15:00 | [204 empty] | 202.6999
| HVDC EvPeak Flow |  | 894 | 20:00
| Load factor L.F |  | 89.22% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-27
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11031 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 10428
Evening Peak Generation : |  |  | 13033 | MW Hour : | 20:00 | Available Max Generation : |  | 15756
E.P. Demand (at gen end) : |  |  | 13225 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 13033 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1756
Total Gen. (MKWH) : |  |  | 278.8691 | System Load Factor : | 89.22% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 200 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-27
Actual : |  | 108.9 | Ft.(MSL) , | Rule curve : | 97.35 | Ft.( MSL )
Gas Consumed : |  | Total = | 886.3 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 370447989.424
: |  |  | Coal : | 604871865.71 | Oil : | 572448684.58 | Total : | 1547768539.714
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 60 | 1440:00 | 4307.5694 |  |  | 0 | -21.73%
Chittagong Area |  | 0 | 0:00 | 1182.1376 |  |  | 0 | -19.89%
Khulna Area |  | 0 | 0:00 | 1655.4666 |  |  | 0 | -19.5%
Rajshahi Area |  | 0 | 0:00 | 1438.4608 |  |  | 0 | -19.08%
Cumilla Area |  | 0 | 0:00 | 1183.8221 |  |  | 0 | -19.34%
Mymensingh Area |  | 80 | 1920:00 | 880.2349 |  |  | 0 | -18.98%
Sylhet Area |  | 0 | 0:00 | 493.6451 |  |  | 0 | -19.67%
Barisal Area |  | 0 | 0:00 | 411.1693 |  |  | 0 | -18.91%
Rangpur Area |  | 43 | 1032:00 | 804.1802 |  |  | 0 | -18.92%
Total |  | 183 |  | 12356.6859 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
| 08:31 | New Tongi S/S T2(413T) LT is restored.
09:04 | 20:34 | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to work at Hasnabad end
09:04 | 20:35 | Hasnabad 132/33kV S/S Keraniganj-1 (Pre- Lalbag) Scheduled S/D Due to Modification of bus bar protection work.
09:06 | 20:37 | Hasnabad 132/33kV S/S Keraniganj-2 (Pre- Aourahati) Scheduled S/D Due to Modification of 132kv bus bar
protection work.
09:07 | 20:35 | Aggreko-keraniganj 132kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to work at hasnabad end
09:26 | 15:52 | Munshiganj 132/33kV S/S Transformer-1 LT Forced S/D Due to 132kV Power Transformer-01 LT Side Red hot at B phase
09:35 | 10:41 | Purbasadipur 132/33kV S/S T-4 Transformer LT Scheduled S/D Due to PBS Maintenance works |  |  |  |  | 30.0MW load interruption.
09:37 | 10:40 | Purbasadipur 132/33kV S/S T-4 Transformer HT Scheduled S/D Due to PBS Maintenance works
09:38 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- ST
09:44 | 10:42 | Mongla 132/33kV S/S T-1 LT Tripped showing Ins. Over current phase A relays Due to 33 kv Basundhara feeder LA |  |  |  |  | 6.0MW load interruption.
damage.
09:45 |  | Meghnaghat CCPP(Summit) GT-1 Shutdown with remarks:- GT-1 Shutdown as per NLDC demand
09:45 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
09:46 |  | Meghnaghat CCPP(Summit) ST Shutdown with remarks:- ST shutdown given as per NLDC demand
09:47 |  | Meghnaghat CCPP(Summit) GT-1 Ready with remarks:- GT-1 ready
09:48 |  | Meghnaghat CCPP(Summit) ST Ready with remarks:- ST ready
| 11:27 | Jashore 132/33kV S/S T-2 LT is restored.
11:37 | 16:23 | Ashuganj-Sreepur 230 kV Ckt-2 Scheduled S/D from Sirajgonj
230 end Due to Right of way.
12:00 |  | Day Peak Generation:11034 MW
12:04 | 16:24 | Sreepur 230/132/33kV S/S Sreepur-Sirajganj Ckt-2 Scheduled S/D Due to Right of way
12:37 | 17:34 | Jashore 132/33kV S/S T-2 HT Tripped showing 51N,50/51 Trip(87T2) relays Due to CB To CT Loop Disconnect |  |  |  |  | 35.0MW load interruption.
12:37 | 17:55 | Jashore 132/33kV S/S T-2 LT Tripped showing 51N,50/51 Trip P-642,(87T2) relays Due to CT To CB Loop Disconnec
12:54 | 13:39 | Purbasadipur 132/33kV S/S T-4 Transformer LT Scheduled S/D Due to pbs work |  |  |  |  | 12.0MW load interruption.
12:54 | 13:38 | Purbasadipur 132/33kV S/S T-4 Transformer HT Scheduled S/D Due to works of pbs
13:06 | 16:46 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Tripped showing OC relay relays Due to PRV trip
13:08 | 16:46 | Agargaon 230/132kV S/S Auxiliary Tr-1 HT Scheduled S/D Due to 230/132/33kV Tr-1 PRV Trip
13:08 | 16:47 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) LT Scheduled S/D Due to 230/132/33kV Tr-1 PRV Trip
13:08 | 16:46 | Agargaon 230/132kV S/S 230kV Transformer-1 ( 705T1) HT Scheduled S/D Due to 230/132/33kV Tr-1 PRV Trip
13:08 | 16:48 | Agargaon 230/132kV S/S Auxiliary Tr-1 LT Scheduled S/D Due to 230/132/33kV Tr-1 PRV Trip
| 13:29 | Jashore 132/33kV S/S T-1 LT is restored.
14:10 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 17:51 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
| 18:19 | Chowmuhani-Feni 132 kV Ckt-1 is restored.
18:31 | 19:24 | Jashore 132/33kV S/S JH-1(L2) Forced S/D Due to DC fault in CP panel of Jhe ckt-1
18:41 | 19:25 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 Forced S/D Due to DC Fail Jashore 132kV ss
19:02 | 20:31 | Naogaon 132/33kV S/S T-2 HT Forced S/D Due to Emergency maintenance work of patnitola pbs 33 kV |  |  |  |  | 12.0MW load interruption.
feeder source side isolator (R phase)
19:02 | 20:33 | Naogaon 132/33kV S/S T-2 LT Forced S/D Due to Emergency maintenance work of patnitola pbs 33 kV
feeder source side isolator (R phase)
20:00 |  | Evening Peak Generation :13033 MW
20:55 | 22:27 | Magura-Narail 132kV Ckt-2 Forced S/D from Magura 132/33kV end Due to Red hot maintenance and from
Narail 132/33kV end Due to Magura end line-02 red hot.
22:10 |  | Adani Power Jharkhand Ltd. Unit-2 was sync.
23:10 | 01:25 | Naogaon 132/33kV S/S T-1 LT Forced S/D Due to Red hot maintenance of T-1 33KV CB R-phase.
23:11 | 01:24 | Naogaon 132/33kV S/S T-1 HT Forced S/D Due to Red hot maintenance of T-1 33kv CB R-phase.
01:35 | 02:41 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Red hot maintenance of T-3 33KV CT B-Phase
01:36 | 02:40 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Red hot maintenance of T-3 33kv CT B- phase
05:50 |  | Full load interruption is occurring under Kodda 132/33kV grid S/S due to forced shutdown of all 33kV outgoing
feeders due to fire at 33kV outgoing feeder trench.
06:00 |  | Minimum generation 10428 MW
06:59 |  | Ashuganj-Kishoreganj 132kV Ckt-1 Scheduled S/D from Kishoreganj 132/33kV end Due to Bajitpur SS Project work
07:50 |  | Now, partial (about 150 MW) load interruption is occurring under Kodda 132/33kV grid S/S due to forced
shutdown of some 33kV outgoing feeders due to fire at 33kV outgoing feeder trench.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-26
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 401 | 9586800
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9541500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve NENP
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 1274618 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve NENP
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 762698
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve. NENP
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve NENP
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7427958
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 660240 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 411480
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 131 | 1304160 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 839090
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 835212
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 886320 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 548400 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 7 | 290000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 228960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 240 | 1997236 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 3159792 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 702720 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 82 | 906240 | Fuel shortage
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1592640
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 120309
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 700560 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 206000
| Dhaka area Total |  |  |  | 6217 | 2414 | 43982933
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 58649 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 35235
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 23520 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 217 | 5264936
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 217 | 5215654
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 82 | 494291 | Fuel shortage
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 73 | 240803 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 285355 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 562560
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 566400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22156
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 150 | 895745
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 51783 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 178980 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 528960 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 70 | 297327 | Low demand
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 152218 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 0 | 0 | Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 24 | 586080
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 1151 | 27869090
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 2361 | 43329742
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 5045000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7391100
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 240 | 6400000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5741600 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 34 | 864432 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 5 | 510720 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1176383
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 90 | 237527 | Low demand
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 37 | 178112 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 25 | 879130 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 85 | 852480 | Low demand
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 50 | 1153920
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 144110 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 387920 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 240540 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 223440 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1440960 | Engine problem
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 215155
| Cumilla Area Total |  |  |  | 2917 | 1503 | 33082529
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 17 | 321600 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10200
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 125 | 2503200 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1384800 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 265810
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 198480 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 473040 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 249 | 5157130
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 922000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3575454
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 48384 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 662688 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 10 | 264907 | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 136 | 3237290 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 239568 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7132000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8299000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8138700 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1345 | 32519991
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 894 | 21517090
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve NENP
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Low demand
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Low demand
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 230 | 6494976 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 42 | 293760 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 267840
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 554 | 11818180
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1720 | 40391846
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 176928 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 9 | 168399
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 80 | 2745000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1160 | 27541100
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 190 | 5205200
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 270 | 5171000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 1705
| Barisal Area Total |  |  |  | 2236 | 1725 | 41009332
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 23 | 105676 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 37593 | Low demand
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 196 | 4714227 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 317 | 8274981 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 201600 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 105012 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 43 | 236432 | Low demand
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 530688 | Low demand
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 588960 | Low demand
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 21120
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 760 | 18408941
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 249000
| Rajshahi Area Total |  |  |  | 3449 | 1442 | 33474230
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 60 | 1405090
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1396425 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 31872
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2100480
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 171852
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1021680
| Rangpur Area Total |  |  |  | 950 | 274 | 6127399
| Total |  |  |  | 27068 | 13033 | 279075132
| Eastern Grid Total |  |  |  | 16579 | 7872 | 158072325
| Western Grid Total |  |  |  | 10489 | 5161 | 121002807
| National Grid Total |  |  |  | 27068 | 13033 | 279075132
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-08-2024 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8310.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4162 | MW
i) Dhaka area |  |  | 4784.48 |  | MW | i) Khulna area |  |  |  | 1569.4 | MW
ii) Chattogram area |  |  | 1066 |  | MW | ii) Barishal area |  |  |  | 336 | MW
iii) Cumilla area |  |  | 819 |  | MW | iii) Rajshahi area |  |  |  | 1384.6 | MW
iv) Mymensingh area |  |  | 1055 |  | MW | iv) Rangpur area |  |  |  | 872 | MW
v) Sylhet area |  |  | 586 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12472.48 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 102 | 07:00 | 133 | Rahim | 43 | 12:00
2 | AKSML | 101 | 10:00 | 68 | Jashore | 106 | 19:00 | 134 | Rajbari | 72 | 19:30
3 | Aftabnagar | 30 | 19:00 | 69 | Jhenaidah | 103 | 00:00 | 135 | Rajendrapur | 96 | 21:00
4 | Agargaon | 91 | 19:00 | 70 | Joydebpur | 192 | 19:00 | 136 | Rajshahi | 120 | 00:00
5 | Agrabad | 90 | 19:30 | 71 | Joypurhat | 65 | 00:00 | 137 | Rajshahi-230 | 65 | 00:00
6 | Amnura | 68 | 00:00 | 72 | Juldah | 15 | 00:00 | 138 | Ramganj | 96 | 18:30
7 | Ashuganj | 75 | 00:00 | 73 | KSRM | 36 | 16:00 | 139 | Rampur | 25 | 19:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 302 | 12:00 | 140 | Rangamati | 17 | 19:30
9 | BSRM | 139 | 19:30 | 75 | Kachua | 66 | 22:00 | 141 | Rangpur | 152 | 19:00
10 | Bagerhat | 75 | 19:00 | 76 | Kallyanpur | 105 | 20:00 | 142 | Ruppur | 5.6 | 09:00
11 | Bakulia | 85 | 19:00 | 77 | Kalurghat | 34 | 15:00 | 143 | SSM | 0 | 00:00
12 | Banani | 49 | 15:00 | 78 | Kamrangirchar | 51.62 | 12:00 | 144 | Saidpur | 110 | 19:00
13 | Bangabhaban | 4 | 00:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 109 | 19:00
14 | Barapukuria | 51 | 22:00 | 80 | Kazla | 96 | 13:00 | 146 | Satmasjid | 96 | 13:00
15 | Barguna | 18 | 21:00 | 81 | Keranigonj | 70 | 19:30 | 147 | Savar | 205 | 15:00
16 | Barishal | 93 | 13:00 | 82 | Khagrachori | 32 | 19:30 | 148 | SevenRings | 4.36 | 19:30
17 | Barishal-230 | 78 | 19:30 | 83 | Khulna | 68 | 13:00 | 149 | ShahCement | 20 | 23:00
18 | Baroaulia | 55 | 10:00 | 84 | Khulshi | 125 | 19:00 | 150 | Shahjadpur | 74 | 20:00
19 | Baroirhat | 31 | 20:00 | 85 | Kishoreganj | 156 | 21:00 | 151 | Shahjibazar | 124 | 23:00
20 | Bashundhara | 146 | 13:00 | 86 | Kodda | 286 | 21:00 | 152 | Shahmirpur | 45 | 04:00
21 | BashundharaCement | 7 | 00:00 | 87 | Kulaura | 50 | 20:00 | 153 | Shariatpur | 75 | 22:00
22 | Beanibazar | 78 | 20:00 | 88 | Kurigram | 63 | 19:30 | 154 | Sherpur | 146 | 19:30
23 | Benapole | 66 | 19:30 | 89 | Kushtia | 132 | 00:00 | 155 | Shikalbaha | 22 | 19:00
24 | Bhaluka | 130 | 00:00 | 90 | Lalbag | 77 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 45 | 22:00 | 91 | Lalmonirhat | 66 | 19:30 | 157 | Shitalakhya | 73.5 | 13:00
26 | Bhangura | 32 | 00:00 | 92 | MI_Cement | 12.2 | 23:00 | 158 | Sholosohor | 40 | 19:00
27 | Bheramara(GK) | 59 | 00:00 | 93 | Madanganj | 28 | 00:00 | 159 | Shyampur | 138 | 00:00
28 | Bhulta | 236 | 09:00 | 94 | Madaripur | 90 | 22:00 | 160 | Siddhirganj | 106 | 15:00
29 | Bog-Sherpur | 60 | 01:00 | 95 | Madartek | 79.07 | 20:00 | 161 | Sirajganj | 106 | 20:00
30 | Bogura | 157 | 20:00 | 96 | Madunaghat | 45 | 21:00 | 162 | Sonargaon | 68 | 21:00
31 | Borhanuddin | 68 | 21:00 | 97 | Magura | 57 | 19:30 | 163 | Sreemongol | 68 | 00:00
32 | Brahmanbaria | 162 | 21:00 | 98 | Mahasthangarh | 74 | 00:00 | 164 | Sreepur | 108 | 19:00
33 | Cantonment | 96 | 13:00 | 99 | Manikganj | 109 | 22:00 | 165 | Srinagar | 41.7 | 22:00
34 | Chandpur | 62 | 19:30 | 100 | Maniknagar | 49 | 13:00 | 166 | Sunamganj | 58 | 20:00
35 | Chandraghona | 32 | 19:00 | 101 | Matarbari | 38 | 19:30 | 167 | Sylhet | 46 | 23:00
36 | Chapai | 61 | 00:00 | 102 | Matuail | 58 | 10:00 | 168 | Sylhet-132 | 122 | 19:30
37 | Charsaidpur | 36 | 01:00 | 103 | Millgate | 115 | 16:00 | 169 | TK | 28.5 | 18:30
38 | Chauddagram | 54 | 19:00 | 104 | Mirpur | 135 | 15:00 | 170 | Tangail | 168 | 20:00
39 | Chhatak | 34 | 00:00 | 105 | Mirsorai | 5 | 19:00 | 171 | Thakurgaon | 108 | 19:30
40 | Chowmuhani | 129 | 22:00 | 106 | Mirzapur | 34 | 19:00 | 172 | Tongi | 136 | 11:00
41 | Chuadanga | 108 | 00:00 | 107 | Mithapukur | 60 | 19:00 | 173 | Ullahpara | 23 | 19:00
42 | Coxsbazar | 102 | 18:30 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 50 | 13:00
43 | Cumilla(N) | 150 | 22:00 | 109 | Mogbazar | 97.4 | 13:00 | 175 | Uttara | 60 | 19:00
44 | Cumilla(S) | 119 | 19:30 | 110 | Mongla | 27 | 00:00 | 176 | UttaraNew | 48 | 19:00
45 | Daudkandi | 139 | 19:00 | 111 | Motijheel | 30 | 13:00 | 177 | Zigatola | 88 | 19:00
46 | Dhaka | 34 | 13:00 | 112 | Munshiganj | 93 | 00:00
47 | Dhamrai | 130 | 19:00 | 113 | Mymensingh | 239 | 19:00
48 | Dhanmondi | 104 | 13:00 | 114 | Naogaon | 122 | 00:00
49 | Dohazari | 88 | 19:00 | 115 | Narail | 52 | 19:00
50 | Faridpur | 149 | 19:30 | 116 | Narinda | 60 | 13:00
51 | Fatullah | 83 | 12:00 | 117 | Narshingdi | 172 | 19:00
52 | Fenchuganj | 36 | 18:30 | 118 | Natore | 137 | 00:00
53 | Feni | 40 | 22:00 | 119 | Nawabganj | 42 | 21:00
54 | GPH | 5 | 00:00 | 120 | Netrakona | 117 | 18:30
55 | Ghatail | 56 | 18:30 | 121 | New | 37.2 | 00:00
56 | Ghorashal | 57 | 18:00 | 122 | Niamatpur | 68 | 00:00
57 | Goalpara | 36 | 13:00 | 123 | Noapara | 49 | 19:30

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 388 | 05:00 | 376 | 12:00 | Kaliakoir | 377 | 03:00 | 363 | 12:00
| Ashuganj | 409 | 6:00 | 393 | 12:00 | Madunaghat | 395 | 07:00 | 386 | 12:00
| Bhulta | 398 | 06:00 | 381 | 12:00 | Meghnaghat | 384 | 05:00 | 371 | 13:00
| Bibiana | 396 | 06:00 | 386 | 14:00 | Payra | 413 | 06:00 | 404 | 19:00
| BIPTC | 407 | 21:00 | 400 | 00:00 | Rahanpur | 399 | 10:00 | 383 | 22:00
| Bogura | 389 | 10:00 | 369 | 22:00 | Rampal | 406 | 06:00 | 389 | 19:00
| Gopalganj | 403 | 06:00 | 388 | 18:30
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 13:00 | 221 | 11:00 | Haripur | 233 | 02:00 | 223 | 12:00
| AKSML | 237 | 20:00 | 225 | 12:00 | Hasnabad | 232 | 00:00 | 223 | 10:00
| Aminbazar | 232 | 02:00 | 221 | 11:00 | Hathazari | 239 | 19:30 | 228 | 13:00
| Ashuganj | 236 | 08:00 | 227 | 12:00 | Ishurdi | 237 | 06:00 | 225 | 23:00
| Ashuganj-400 | 236 | 6:00 | 225 | 13:00 | Jhenaidah | 238 | 10:00 | 217 | 23:00
| Baghabari | 234 | 06:00 | 224 | 21:00 | Kaliakoir | 234 | 00:00 | 222 | 12:00
| Barapukuria | 211 | 13:00 | 200 | 23:00 | Keranigonj | 231 | 06:00 | 220 | 11:00
| Barapukuria-230 | 211 | 13:00 | 200 | 23:00 | Khulna(S) | 235 | 06:00 | 218 | 23:00
| Barishal | 240 | 06:00 | 232 | 23:00 | Madunaghat | 237 | 19:30 | 228 | 11:00
| Bheramara | 234 | 06:00 | 222 | 22:00 | Maniknagar | 234 | 03:00 | 223 | 12:00
| Bhulta | 234 | 00:00 | 224 | 12:00 | Meghnaghat | 241 | 03:00 | 232 | 10:00
| Bibiana | 227 | 06:00 | 220 | 12:00 | Meghnaghat-400 | 235 | 00:00 | 223 | 04:00
| BIPTC | 237 | 06:00 | 224 | 19:30 | Mirsorai | 231 | 19:00 | 224 | 12:00
| Bogura | 223 | 02:00 | 211 | 21:00 | Rajshahi | 235 | 08:00 | 221 | 22:00
| Bogura-400 | 223 | 09:00 | 211 | 22:00 | Rampal | 234 | 06:00 | 219 | 23:00
| Borhanuddin | 244 | 07:00 | 238 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 233 | 19:00 | 225 | 11:00 | Rampura | 234 | 01:00 | 222 | 12:00
| Cumilla(N) | 230 | 06:00 | 223 | 12:00 | Shikalbaha | 237 | 19:30 | 225 | 15:00
| Faridpur | 239 | 06:00 | 229 | 22:00 | Shyampur | 232 | 01:00 | 222 | 12:00
| Fenchuganj | 229 | 06:00 | 223 | 18:30 | Siddhirganj | 234 | 00:00 | 225 | 11:00
| Ghorashal | 235 | 00:00 | 230 | 14:00 | Sirajgonj | 236 | 06:00 | 227 | 12:00
| Ghorashal-230 | 232 | 06:00 | 222 | 12:00 | Sreepur | 230 | 03:00 | 221 | 16:00
| Gopalganj | 239 | 06:00 | 230 | 18:30 | Tongi | 235 | 03:00 | 218 | 11:00
| GPH | 235 | 19:00 | 226 | 18:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 137 | 07:00 | 129 | 12:00 | Kushtia | 139 | 06:00 | 129 | 23:00
| Agargaon | 135 | 02:00 | 127 | 14:00 | Lalbag | 135 | 06:00 | 128 | 11:00
| Agrabad | 137 | 19:00 | 129 | 15:00 | Lalmonirhat | 123 | 14:00 | 113 | 19:30
| AKS | 135 | 18:30 | 127 | 15:00 | Madanganj | 133 | 00:00 | 127 | 13:00
| Aminbazar | 140 | 00:00 | 129 | 15:00 | Madaripur | 135 | 06:00 | 129 | 23:00
| Amnura | 136 | 08:00 | 124 | 21:00 | Madartek | 136 | 02:00 | 128 | 12:00
| Ashuganj | 139 | 06:00 | 135 | 12:00 | Madunaghat | 138 | 20:00 | 130 | 13:00
| Bagerhat | 135 | 01:00 | 122 | 18:30 | Magura | 140 | 06:00 | 125 | 22:00
| Bakulia | 138 | 19:00 | 130 | 13:00 | Mahasthangarh | 129 | 06:00 | 121 | 22:00
| Banani | 138 | 06:00 | 128 | 13:00 | Manikganj | 129 | 00:00 | 118 | 15:00
| Bangabhaban | 133 | 04:00 | 125 | 12:00 | Maniknagar | 133 | 06:00 | 126 | 12:00
| Barapukuria | 130 | 13:00 | 122 | 19:30 | Matarbari | 128 | 19:00 | 120 | 18:00
| Barguna | 137 | 06:00 | 131 | 22:00 | Matuail | 133 | 00:00 | 127 | 11:00
| Barishal | 137 | 07:00 | 129 | 23:00 | Millgate | 135 | 01:00 | 124 | 12:00
| Barishal-230 | 136 | 06:00 | 130 | 22:00 | Mirpur | 138 | 01:00 | 130 | 11:00
| Baroaulia | 138 | 19:30 | 130 | 15:00 | Mirzapur | 127 | 00:00 | 119 | 18:30
| Baroirhat | 131 | 04:00 | 123 | 18:00 | Mithapukur | 127 | 14:00 | 119 | 21:00
| Bashundhara | 136 | 01:00 | 124 | 12:00 | MI_Cement | 135 | 01:00 | 127 | 11:00
| BashundharaCement | 133 | 20:00 | 127 | 13:00 | Modern | 137 | 19:30 | 129 | 12:00
| Beanibazar | 125 | 07:00 | 117 | 18:30 | Mogbazar | 138 | 06:00 | 125 | 20:00
| Benapole | 138 | 06:00 | 121 | 19:00 | Mongla | 135 | 07:00 | 123 | 19:00
| Bhaluka | 131 | 10:00 | 118 | 22:00 | Motijheel | 133 | 04:00 | 123 | 08:00
| Bhandaria | 135 | 04:00 | 124 | 23:00 | Munshiganj | 134 | 01:00 | 127 | 11:00
| Bhangura | 136 | 06:00 | 127 | 23:00 | Mymensingh | 128 | 12:00 | 113 | 22:00
| Bheramara | 137 | 06:00 | 130 | 23:00 | Naogaon | 128 | 08:00 | 117 | 22:00
| Bheramara(GK) | 138 | 06:00 | 131 | 22:00 | Narail | 141 | 06:00 | 123 | 22:00
| Bhulta | 124 | 00:00 | 116 | 11:00 | Narinda | 133 | 06:00 | 126 | 12:00
| Bog-Sherpur | 129 | 11:00 | 118 | 22:00 | Narshingdi | 122 | 00:00 | 117 | 11:00
| Bogura | 133 | 09:00 | 122 | 22:00 | Natore | 134 | 08:00 | 125 | 22:00
| Bogura-230 | 133 | 02:00 | 123 | 21:00 | Nawabganj | 135 | 02:00 | 127 | 12:00
| Brahmanbaria | 131 | 07:00 | 123 | 21:00 | Netrakona | 127 | 09:00 | 114 | 18:30
| Cantonment | 135 | 06:00 | 127 | 14:00 | New | 135 | 00:00 | 126 | 11:00
| Chandpur | 134 | 19:30 | 121 | 18:00 | Niamatpur | 135 | 10:00 | 128 | 22:00
| Chandraghona | 138 | 19:00 | 132 | 15:00 | Noapara | 139 | 05:00 | 124 | 19:00
| Chapai | 133 | 15:00 | 126 | 21:00 | Pabna | 137 | 06:00 | 128 | 23:00
| Charsaidpur | 134 | 01:00 | 127 | 11:00 | Palashbari | 125 | 00:00 | 117 | 22:00
| Chauddagram | 131 | 07:00 | 124 | 18:00 | Panchagarh | 132 | 14:00 | 116 | 19:30
| Chhatak | 123 | 07:00 | 117 | 18:30 | Patuakhali | 137 | 04:00 | 133 | 12:00
| Chowmuhani | 128 | 19:30 | 118 | 18:00 | Payra | 139 | 06:00 | 134 | 19:00
| Chuadanga | 140 | 06:00 | 119 | 23:00 | PHP | 130 | 08:00 | 123 | 18:00
| Coxsbazar | 126 | 08:00 | 121 | 18:00 | Postogola | 136 | 01:00 | 129 | 11:00
| Cumilla(N) | 133 | 01:00 | 129 | 11:00 | Purbachal | 136 | 00:00 | 124 | 12:00
| Cumilla(S) | 133 | 08:00 | 120 | 12:00 | Purbasadipur | 126 | 13:00 | 115 | 12:00
| Daudkandi | 130 | 03:00 | 124 | 12:00 | Rahanpur | 136 | 09:00 | 130 | 21:00
| Dhaka | 137 | 06:00 | 129 | 12:00 | Rahim | 133 | 01:00 | 127 | 12:00
| Dhamrai | 132 | 00:00 | 125 | 11:00 | Rajbari | 134 | 06:00 | 126 | 23:00
| Dhanmondi | 137 | 06:00 | 129 | 12:00 | Rajendrapur | 130 | 00:00 | 118 | 15:00
| Dohazari | 136 | 19:30 | 126 | 15:00 | Rajshahi | 134 | 05:00 | 127 | 22:00
| Faridpur | 134 | 06:00 | 128 | 19:30 | Rajshahi-230 | 136 | 06:00 | 120 | 22:00
| Fatullah | 135 | 02:00 | 128 | 11:00 | Ramganj | 130 | 19:30 | 120 | 18:00
| Fenchuganj | 132 | 08:00 | 127 | 19:00 | Rampur | 137 | 19:00 | 128 | 14:00
| Feni | 130 | 19:00 | 122 | 17:00 | Rampura | 136 | 01:00 | 128 | 12:00
| Ghatail | 126 | 08:00 | 115 | 18:30 | Rangamati | 137 | 19:00 | 131 | 11:00
| Ghorashal | 138 | 04:00 | 132 | 12:00 | Rangpur | 125 | 14:00 | 115 | 19:00
| Goalpara | 141 | 06:00 | 127 | 23:00 | Ruppur | 137 | 05:00 | 131 | 22:00
| Gollamari | 139 | 06:00 | 128 | 19:00 | Saidpur | 126 | 13:00 | 118 | 12:00
| Gopalganj | 135 | 05:00 | 127 | 19:00 | Satkhira | 137 | 06:00 | 122 | 19:00
| Gopalganj-400 | 135 | 06:00 | 129 | 18:30 | Satmasjid | 135 | 06:00 | 126 | 14:00
| Gulshan | 136 | 06:00 | 129 | 11:00 | Savar | 139 | 01:00 | 127 | 11:00
| Halishahar | 138 | 19:30 | 128 | 15:00 | SevenRings | 138 | 06:00 | 132 | 12:00
| Haripur | 133 | 00:00 | 127 | 11:00 | ShahCement | 134 | 01:00 | 127 | 11:00
| HaripurSBU | 130 | 09:00 | 123 | 03:00 | Shahjadpur | 136 | 10:00 | 132 | 00:00
| Hasnabad | 136 | 00:00 | 130 | 11:00 | Shahjibazar | 128 | 07:00 | 121 | 21:00
| Hathazari | 139 | 19:00 | 132 | 16:00 | Shahmirpur | 138 | 18:30 | 129 | 15:00
| Ishurdi | 138 | 06:00 | 131 | 23:00 | Shariatpur | 134 | 06:00 | 126 | 23:00
| Jaldhaka | 124 | 14:00 | 112 | 19:00 | Sherpur | 130 | 11:00 | 117 | 21:00
| Jamalpur | 131 | 08:00 | 120 | 03:00 | Shikalbaha | 127 | 19:30 | 118 | 15:00
| Jashore | 138 | 05:00 | 121 | 19:00 | Shikalbaha-230 | 140 | 19:30 | 129 | 13:00
| Jhenaidah | 142 | 06:00 | 127 | 23:00 | Shitalakhya | 135 | 01:00 | 127 | 11:00
| Jhenaidah-230 | 143 | 06:00 | 127 | 23:00 | Sholosohor | 137 | 19:00 | 130 | 11:00
| Joydebpur | 135 | 00:00 | 124 | 15:00 | Shyampur | 134 | 05:00 | 130 | 14:00
| Joypurhat | 128 | 09:00 | 115 | 22:00 | Shyampur-230 | 134 | 00:00 | 128 | 11:00
| Juldah | 139 | 19:30 | 130 | 11:00 | Siddhirganj | 134 | 01:00 | 127 | 11:00
| Kabirpur | 134 | 00:00 | 121 | 12:00 | Sirajganj | 132 | 06:00 | 113 | 22:00
| Kachua | 134 | 19:30 | 124 | 17:00 | Sonargaon | 132 | 00:00 | 125 | 11:00
| Kaliakoir | 135 | 00:00 | 124 | 12:00 | Sreemongol | 128 | 07:00 | 122 | 21:00
| Kallyanpur | 132 | 03:00 | 127 | 14:00 | Sreepur | 130 | 05:00 | 123 | 16:00
| Kalurghat | 139 | 19:00 | 130 | 11:00 | Srinagar | 134 | 00:00 | 128 | 11:00
| Kamrangirchar | 136 | 01:00 | 125 | 12:00 | SSM | 141 | 21:00 | 135 | 15:00
| Kaptai | 135 | 16:00 | 129 | 8:00 | Sunamganj | 122 | 08:00 | 115 | 19:00
| Kazla | 132 | 01:00 | 125 | 13:00 | Sylhet | 125 | 07:00 | 121 | 00:00
| Keranigonj | 135 | 01:00 | 128 | 12:00 | Sylhet-132 | 126 | 08:00 | 122 | 18:30
| Khagrachori | 136 | 19:00 | 130 | 11:00 | Tangail | 125 | 09:00 | 114 | 18:30
| Khulna | 138 | 08:00 | 126 | 19:00 | Thakurgaon | 130 | 14:00 | 114 | 12:00
| Khulna(S) | 140 | 06:00 | 128 | 19:00 | TK | 137 | 19:00 | 130 | 14:00
| Khulshi | 136 | 19:30 | 127 | 15:00 | Tongi | 136 | 01:00 | 128 | 11:00
| Kishoreganj | 130 | 06:00 | 120 | 15:00 | Ullahpara | 137 | 07:00 | 133 | 00:00
| Kodda | 131 | 00:00 | 119 | 15:00 | Ullon | 136 | 04:00 | 129 | 11:00
| KSRM | 137 | 19:00 | 130 | 11:00 | Uttara | 138 | 00:00 | 130 | 11:00
| Kulaura | 130 | 07:00 | 126 | 12:00 | UttaraNew | 138 | 01:00 | 130 | 11:00
| Kurigram | 125 | 01:00 | 115 | 19:00 | Zigatola | 136 | 06:00 | 128 | 12:00

## L-Curve
Date | 2024-08-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 456 | 7220 | 5386 | 12606 |  |  |  | QF-LDC-11
0:30 | 396 | 6905 | 5352 | 12257 | Date: | 2024-08-26
1:00 | 336 | 6590 | 5318 | 11908
1:30 | 377 | 6455 | 5194 | 11649
2:00 | 418 | 6320 | 5070 | 11390
2:30 | 417 | 6245 | 4972.5 | 11217.5 | [5 empty] | Gen. at Eve. Peak | 13033 | 13033 MW (20:00 )
3:00 | 416 | 6170 | 4875 | 11045 | [6 empty] | 20:00
3:30 | 402 | 6107.5 | 4844 | 10951.5 | [5 empty] | Gen. at Day Peak | 11031 | 11031 MW (12:00 )
4:00 | 388 | 6045 | 4813 | 10858 | [6 empty] | 12:00
4:30 | 384 | 6053 | 4758 | 10811 | [5 empty] | Highest Generation | 13033
5:00 | 380 | 6061 | 4703 | 10764 | [6 empty] | 20:00
5:30 | 420 | 5945 | 4523.5 | 10468.5
6:00 | 460 | 5829 | 4344 | 10173
6:30 | 454 | 5801 | 4300 | 10101
7:00 | 448 | 5773 | 4256 | 10029
7:30 | 581 | 5764.5 | 4288 | 10052.5
8:00 | 714 | 5756 | 4320 | 10076
8:30 | 742 | 5792 | 4383.5 | 10175.5
9:00 | 770 | 5828 | 4447 | 10275
9:30 | 777 | 5833 | 4519.5 | 10352.5
10:00 | 784 | 5838 | 4592 | 10430
10:30 | 843 | 5890 | 4672.5 | 10562.5
11:00 | 902 | 5942 | 4753 | 10695
11:30 | 885 | 6019.5 | 4843.5 | 10863
12:00 | 868 | 6097 | 4934 | 11031
12:30 | 794 | 6249.5 | 5064 | 11313.5
13:00 | 720 | 6402 | 5194 | 11596
13:30 | 644 | 6398.5 | 5089 | 11487.5
14:00 | 568 | 6395 | 4984 | 11379
14:30 | 635 | 6412 | 4981.5 | 11393.5
15:00 | 702 | 6429 | 4979 | 11408
15:30 | 669 | 6383 | 4946 | 11329
16:00 | 636 | 6337 | 4913 | 11250
16:30 | 660 | 6237 | 4837.5 | 11074.5
17:00 | 684 | 6137 | 4762 | 10899
17:30 | 666 | 6172.5 | 4767 | 10939.5
18:00 | 648 | 6208 | 4772 | 10980
18:30 | 472 | 6776 | 5034.5 | 11810.5
19:00 | 296 | 7344 | 5297 | 12641
19:30 | 268 | 7830 | 5139 | 12969
20:00 | 200 | 7872 | 5161 | 13033 |  |  |  | Executive Engineer
20:30 | 278 | 7841.5 | 5167 | 13008.5 |  |  |  | Network Operation Division
21:00 | 356 | 7811 | 5173 | 12984
21:30 | 352 | 7719.5 | 5178 | 12897.5
22:00 | 348 | 7628 | 5183 | 12811 |  |  |  |  | Page 6 of 7
22:30 | 384 | 7565.5 | 5227 | 12792.5
23:00 | 420 | 7503 | 5271 | 12774
23:30 | 438 | 7361.5 | 5328.5 | 12690
24:00 | 456 | 7220 | 5386 | 12606
13033 MW (20:00 )
11031 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-26 |  | Energy |  | 279075132
[15 empty] | 2024-08-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3543 | 898 | 1554 | 0 | 1819 | 4243 | 218 | 0 | 256 | 52 | 0 | 23 | 280.77
0:30 | 3498 | 897.5 | 1506 | 0 | 1736 | 4121.5 | 218.5 | 0 | 205.5 | 50 | 0 | 24 | 294.14 |  |  | Date: | 44068
1:00 | 3453 | 897 | 1458 | 0 | 1653 | 4000 | 219 | 0 | 155 | 48 | 0 | 25 | 307.51
1:30 | 3445.5 | 897 | 1482 | 0 | 1469.5 | 3944 | 219.5 | 0 | 118.5 | 47 | 0 | 26 | 287.455 | [9 empty] | Total Energy | 279.0751 | 279.0751 | Total Energy Gen 279.075 MKWHr Energy Not Served 3.256 MKWHr Energy Requirement 282.332 MKWHr
2:00 | 3438 | 897 | 1506 | 0 | 1286 | 3888 | 220 | 0 | 82 | 46 | 0 | 27 | 267.4 | [9 empty] | Energy not Served | 3.2565 | 3.2565
2:30 | 3470 | 897.5 | 1598.5 | 0 | 1089 | 3803 | 220 | 0 | 65 | 46 | 0 | 28.5 | 260.2375 | [9 empty] | Energy Requirement | 282.3316 | 282.3316
3:00 | 3502 | 898 | 1691 | 0 | 892 | 3718 | 220 | 0 | 48 | 46 | 0 | 30 | 253.075
3:30 | 3537.5 | 897.5 | 1712 | 0 | 808 | 3668 | 220 | 0 | 40 | 45 | 0 | 23.5 | 251.6425 | [8 empty] | Shortage
4:00 | 3573 | 897 | 1733 | 0 | 724 | 3618 | 220 | 0 | 32 | 44 | 0 | 17 | 250.21
4:30 | 3573 | 897 | 1714 | 0 | 706 | 3594.5 | 219 | 0 | 32 | 46 | 0 | 29.5 | 190.045
5:00 | 3573 | 897 | 1695 | 0 | 688 | 3571 | 218 | 0 | 32 | 48 | 0 | 42 | 129.88
5:30 | 3502.5 | 897.5 | 1603.5 | 0 | 591.5 | 3526.5 | 217 | 0 | 32 | 48 | 3.5 | 46.5 | 101.7075
6:00 | 3432 | 898 | 1512 | 0 | 495 | 3482 | 216 | 0 | 32 | 48 | 7 | 51 | 73.535
6:30 | 3372.5 | 898 | 1513.5 | 0 | 501 | 3446.5 | 216 | 0 | 32 | 46 | 26.5 | 49 | 65.895 | [7 empty] | Coal
7:00 | 3313 | 898 | 1515 | 0 | 507 | 3411 | 216 | 0 | 32 | 44 | 46 | 47 | 58.255
7:30 | 3324 | 898 | 1505.5 | 0 | 507 | 3408 | 216 | 0 | 32 | 42 | 82 | 38 | 59.6875 | [6 empty] | Oil
8:00 | 3335 | 898 | 1496 | 0 | 507 | 3405 | 216 | 0 | 32 | 40 | 118 | 29 | 61.12
8:30 | 3325.5 | 898 | 1536 | 0 | 493.5 | 3413.5 | 216.5 | 0 | 32 | 38 | 187.5 | 25 | 52.0475
9:00 | 3316 | 898 | 1576 | 0 | 480 | 3422 | 217 | 0 | 32 | 36 | 257 | 21 | 42.975
9:30 | 3406.5 | 898 | 1549.5 | 0 | 486 | 3444 | 217.5 | 0 | 24 | 41 | 236.5 | 23 | 40.5875
10:00 | 3497 | 898 | 1523 | 0 | 492 | 3466 | 218 | 0 | 16 | 46 | 216 | 25 | 38.2
10:30 | 3533 | 898 | 1539 | 0 | 496 | 3509 | 218 | 0 | 16 | 47 | 247 | 26.5 | 38.1
11:00 | 3569 | 898 | 1555 | 0 | 500 | 3552 | 218 | 0 | 16 | 48 | 278 | 28 | 38
11:30 | 3584.5 | 898 | 1551.5 | 0 | 544.5 | 3666 | 218 | 0 | 16 | 50 | 275.5 | 26 | 47
12:00 | 3600 | 898 | 1548 | 0 | 589 | 3780 | 218 | 0 | 16 | 52 | 273 | 24 | 56
12:30 | 3617.5 | 898 | 1536 | 0 | 768.5 | 3843 | 219 | 0 | 16 | 53 | 311.5 | 18 | 54.5
13:00 | 3635 | 898 | 1524 | 0 | 948 | 3906 | 220 | 0 | 16 | 54 | 350 | 12 | 53
13:30 | 3635 | 898 | 1524 | 0 | 948 | 3906 | 220 | 0 | 16 | 54 | 350 | 12 | 53
14:00 | 3635 | 898 | 1524 | 0 | 948 | 3906 | 220 | 0 | 16 | 54 | 350 | 12 | 53
14:30 | 3620 | 898.5 | 1546.5 | 0 | 997.5 | 3823.5 | 220 | 0 | 16 | 55 | 280.5 | 11.5 | 70.43
15:00 | 3605 | 899 | 1569 | 0 | 1047 | 3741 | 220 | 0 | 16 | 56 | 211 | 11 | 87.86
15:30 | 3601.5 | 899 | 1547.5 | 0 | 1020.5 | 3736 | 220 | 0 | 16 | 51 | 205.5 | 14.5 | 86.905
16:00 | 3598 | 899 | 1526 | 0 | 994 | 3731 | 220 | 0 | 16 | 46 | 200 | 18 | 85.95
16:30 | 3595 | 899 | 1522 | 0 | 897.5 | 3723.5 | 220 | 0 | 16 | 46 | 137.5 | 17 | 86.4275
17:00 | 3592 | 899 | 1518 | 0 | 801 | 3716 | 220 | 0 | 16 | 46 | 75 | 16 | 86.905
17:30 | 3649.5 | 896.5 | 1514 | 0 | 835 | 3688 | 220 | 0 | 31 | 44 | 45.5 | 16 | 76.8775
18:00 | 3707 | 894 | 1510 | 0 | 869 | 3660 | 220 | 0 | 46 | 42 | 16 | 16 | 66.85
18:30 | 3644 | 894 | 1554.5 | 0 | 1391.5 | 3803 | 218 | 0 | 236.5 | 46 | 8 | 15 | 109.3475
19:00 | 3581 | 894 | 1599 | 0 | 1914 | 3946 | 216 | 0 | 427 | 50 | 0 | 14 | 151.845
19:30 | 3504 | 893 | 1500 | 0 | 2422 | 3906 | 216 | 0 | 454 | 54 | 0 | 20 | 167.6025
20:00 | 3506 | 894 | 1483 | 0 | 2468 | 3955 | 217 | 0 | 436 | 50 | 0 | 24 | 183.36
20:30 | 3557.5 | 812 | 1532.5 | 0 | 2428.5 | 3966 | 217 | 0 | 420 | 51 | 0 | 24 | 182.68
21:00 | 3609 | 730 | 1582 | 0 | 2389 | 3977 | 217 | 0 | 404 | 52 | 0 | 24 | 182
21:30 | 3626 | 814 | 1580.5 | 0 | 2243 | 3959 | 217 | 0 | 383 | 52 | 0 | 23 | 205.1225
22:00 | 3643 | 898 | 1579 | 0 | 2097 | 3941 | 217 | 0 | 362 | 52 | 0 | 22 | 228.245
22:30 | 3633.5 | 898 | 1593.5 | 0 | 2056 | 3997 | 217.5 | 0 | 321.5 | 54 | 0 | 21.5 | 222.0375
23:00 | 3624 | 898 | 1608 | 0 | 2015 | 4053 | 218 | 0 | 281 | 56 | 0 | 21 | 215.83
23:30 | 3583.5 | 898 | 1581 | 0 | 1917 | 4148 | 218 | 0 | 268.5 | 54 | 0 | 22 | 248.3 |  |  | Max Temp. in Dhaka |  | 30°C
24:00 | 3543 | 898 | 1554 | 0 | 1819 | 4243 | 218 | 0 | 256 | 52 | 0 | 23 | 280.77
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 279.075 MKWHr Energy Not Served 3.256 MKWHr Energy Requirement 282.332 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 139 | 140 | 140 | 140 | 138 | 136 | 136 | 136 | 137 | 138 | 138 | 138 | 140 | 140 | 140 | 140 | 140 | 140 |  | 136 | 136 | 137 | 137 | 137 | 138 | 138 | 3328936
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1936000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [19 empty] | 5 | 25 | 8 | 8 | 8 | 8 |  | 58649
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 1 | 3 | 4 | 3 | 3 | 7 | 4 | 8 | 4 | 1 | 0 | [8 empty] | 35235
6 | Sikalbaha 225MW CCPP (Gas) | 223 | 222 | 222 | 223 | 222 | 222 | 223 | 222 | 222 | 221 | 220 | 220 | 221 | 219 | 218 | 217 | 219 | 218 |  | 217 | 217 | 217 | 217 | 217 | 219 | 221 | 5215654
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 85 | 84 | 84 | 51 | 51 | 17 |  | 285355
12 | Hathazari 100 MW peaking PP | [19 empty] | 44 | 72 | 73 | 74 | 32 | 8 |  | 240803
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | 17 | 17 | 17 | 0 | [13 empty] | 34 | 87 | 82 | 87 | 34 | 34 | 34 | 494291
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [19 empty] | 19 | 37 | 37 | 37 | 37 | 37 | 37 | 178112
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 300 | 335 | 335 | 280 | 280 | 280 | 280 | 280 | 335 | 335 | 333 | 280 | 280 | 280 | 280 | 280 |  | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 7427958
18 | Kodda 300 MW PP Unit-2 (Summit) | 167 | 95 | 0 | [8 empty] | 1 | 40 | 45 | 45 | 45 | 30 | 30 |  | 80 | 80 | 240 | 258 | 258 | 260 | 195 | 1997236
19 | Ashuganj 195 MW PP (APSCL-United)
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | [26 empty] | 0
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 34 | 34 | 34 | 34 | 34 | 37 | 37 | 37 | 37 | 34 | 35 |  | 32 | 32 | 34 | 38 | 38 | 38 | 38 | 864432
33 | Ashuganj 225 MW CCPP | 215 | 215 | 215 | 215 | 216 | 217 | 188 | 188 | 194 | 189 | 194 | 199 | 216 | 212 | 211 | 212 | 215 | 211 |  | 201 | 216 | 217 | 214 | 214 | 214 | 214 | 5045000
34 | Ashuganj 450 MW CCPP(South) | 250 | 250 | 250 | 250 | 250 | 275 | 275 | 275 | 285 | 300 | 250 | 250 | 250 | 250 | 275 | 270 | 270 | 305 |  | 265 | 240 | 240 | 240 | 240 | 240 | 240 | 6400000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 315 | 290 | 310 | 330 | 280 | 280 | 290 | 290 | 285 | 285 | 320 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7391100
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 250 | 250 | 250 | 250 | 5741600
35 | Ashuganj 55 MW PP (Precision) | 26 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 31 | 25 | 25 | 12 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 8 | 10 | 510720
36 | Chandpur 150 MW CCPP | 40 | 40 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 40 | 40 | 40 | 40 | 40 | 40 | 35 | 32 | 23 |  | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 879130
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 408 | 408 | 409 | 409 | 408 | 407 | 358 | 351 | 355 | 356 | 356 | 405 | 408 | 368 | 392 | 410 | 412 | 407 |  | 402 | 402 | 401 | 401 | 410 | 406 | 405 | 9586800
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 260 | 300 | 420 | 420 | 420 | 350 | 350 | 350 | 420 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 400 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9541500
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 18 | 18 | 18 | 19 | 19 | 19 | 18 | 17 | 17 | 11 | 11 | 9 | 6 | 6 | 6 | 10 | 11 | 11 |  | 11 | 11 | 17 | 17 | 17 | 17 | 17 | 321600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 13 | 10 | 25 | 26 | 36 | 51 | 44 | 32 | 26 | 16 | 4 | 0 | [8 empty] | 265810
44 | Fenchugonj CCPP Phase-1 | 39 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 922000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 28 | 28 | 28 | 28 | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 29 | 28 | 26 | 28 | 30 | 30 |  | 28 | 28 | 28 | 25 | 25 | 25 | 20 | 662688
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 264907
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 134 | 135 | 135 | 135 | 135 | 135 | 135 |  | 137 | 137 | 136 | 136 | 136 | 136 | 137 | 3237290
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 48384
55 | Fenchugonj 51 MW PP (Barakatullah) | [26 empty] | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 8 | 12 | 12 | 12 | 12 | 12 | 12 | 239568
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 300 | 300 | 290 | 270 | 270 | 275 | 295 | 300 | 310 | 310 | 290 | 290 | 305 | 290 | 275 | 290 |  | 315 | 275 | 260 | 290 | 280 | 305 | 290 | 7132000
| Bibiyana South 400 MW | 320 | 320 | 330 | 320 | 320 | 320 | 320 | 320 | 320 | 340 | 359 | 349 | 336 | 333 | 345 | 343 | 346 | 376 |  | 346 | 346 | 346 | 346 | 360 | 346 | 346 | 8138700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 0 | [7 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 835212
59 | Tangail Palli Power Gen 22 MW | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 198480
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 48 | 46 | 46 | 44 | 48 | 48 | 44 | 40 | 36 | 46 | 48 | 52 | 54 | 50 | 56 | 46 | 46 | 42 |  | 50 | 54 | 50 | 52 | 52 | 56 | 52 | 1153920
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 38 | 12 | 10 | 10 | 5 | 7 | 10 | 7 | 6 | 5 | 8 | 12 |  | 22 | 26 | 28 | 30 | 36 | 37 | 40 | 566400
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 12 | 12 | 12 | 12 | 15 | 15 | 15 | 15 | 15 |  | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 387920
69 | Summit Ashulia | 0 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 3 | 11 | 11 | 11 | 11 | 15 | 15 | 15 | 15 | 15 |  | 16 | 17 | 16 | 16 | 17 | 18 | 18 | 352800
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 533520
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 17 | 17 | 17 | 17 | 548400
72 | Rupganj 33 MW PP(Summit) | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 12 | 11 |  | 11 | 11 | 7 | 8 | 12 | 12 | 12 | 290000
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 17 | 0 | [17 empty] | 34 | 34 | 34 | 34 | 34 | 23 | 34 | 240540
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 223440
| Manikgonj 162MW PP(MPGL) | 90 | 54 | 0 | [8 empty] | 46 | 90 | 90 | 90 | 90 | 35 | 35 |  | 144 | 162 | 162 | 162 | 162 | 162 | 108 | 1592640
77 | Siddhirganj 100 PP(Dutch Bangla) | [26 empty] | 0
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 228960
79 | Kodda 150 MW PP | 82 | 82 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 1304160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 0 | [11 empty] | 8 | 8 | 8 | 8 | 8 |  | 14 | 25 | 8 | 8 | 8 | 8 | 8 | 144110
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 702720
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 2 | 2 | 3 | 4 | 4 | 3 | 3 |  | 1 | 0 | [9 empty] | 22156
| Jodiac Power | [19 empty] | 1 | 8 | 17 | 17 |  |  |  | 51783
| Karnaphuli Power Ltd. | 17 | 0 | [17 empty] | 18 | 48 | 17 | 17 | 17 | 17 | 17 | 178980
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 128 | 129 | 129 | 129 | 128 | 128 | 129 | 130 | 92 | [17 empty] | 1274618
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 69 | 70 | 31 | 0 | [7 empty] | 1 | 34 | 53 | 53 | 53 | 38 | 34 |  | 70 | 77 | 82 | 85 | 86 | 69 | 85 | 906240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1176383
94 | Gagnagar 102 MW PP (Digital Power) | 58 | 24 | 8 | 0 | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 42 | 74 | 90 | 90 | 90 | 90 | 41 | 660240
95 | Patenga 50MW PP (Baraka) | [19 empty] | 1 | 6 | 6 | 6 | 6 |  |  | 23520
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 15 | 0 | [7 empty] | 2 | 30 | 55 | 55 | 55 | 30 | 30 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 762698
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 17 | 0 | [7 empty] | 9 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 839090
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 120 | 3575454
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 0 | 2 | 2 | 2 | 1 | 2 | 0 | 0 | 0 | [8 empty] | 10200
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 0 | [7 empty] | 9 | 17 | 17 | 17 | 24 | 35 | 35 | 35 | 17 |  | 27 | 54 | 54 | 17 | 17 | 17 |  | 411480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 97 | 97 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 97 | 97 | 96 | 96 | 106 |  | 124 | 124 | 125 | 126 | 126 | 127 | 121 | 2503200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 132 | 132 | 132 | 132 | 118 | 130 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 131 | 120 | 130 | 131 |  | 131 | 131 | 131 | 131 | 131 | 132 | 132 | 3159792
115 | Juldah 100 MW PP Unit-3 (Acorn) | [17 empty] | 16 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 562560
116 | Chandpur 200 MW (Desh energy) | 51 | 51 | 34 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 12 | 17 | 17 | 17 | 17 | 17 |  | 53 | 120 | 85 | 85 | 68 | 68 | 68 | 852480
117 | Ashuganj 150 MW PP (Midland) | 10 | 0 | [15 empty] | 1 |  | 37 | 113 | 90 | 10 | 10 | 10 | 10 | 237527
118 | Bibiyana-III 400 MW CCPP | 323 | 288 | 302 | 287 | 287 | 290 | 290 | 290 | 289 | 316 | 332 | 349 | 350 | 350 | 352 | 350 | 350 | 386 |  | 350 | 350 | 350 | 356 | 364 | 361 | 349 | 8299000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 58 | 58 | 58 | 58 | 58 |  | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 1384800
| Anwara 300 MW PP (United) | 52 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | [9 empty] | 5 |  | 150 | 150 | 150 | 150 | 80 | 80 | 80 | 895745
| Juldah unit-2 (Acorn) | [19 empty] | 66 | 100 | 100 | 100 | 100 | 100 | 100 | 528960
| Anlima Energy Ltd. | 17 | 0 | [17 empty] | 22 | 65 | 70 | 72 | 60 | 17 | 17 | 297327
| Bhairob 54.5 MW | 35 | 35 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 473040
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 7 | 7 | 14 | 17 | 14 | 3 | 9 | 19 | 10 | 6 | 0 | [8 empty] | 120309
| Chandpur 115(Doreen) | 70 | 67 | 67 | 67 | 67 | 16 | 16 | 16 | 16 | 16 | 16 | 29 | 74 | 89 | 90 | 90 | 30 | 19 |  | 48 | 90 | 90 | 90 | 90 | 90 | 90 | 1440960
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 35 | 35 | 19 | 34 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 700560
| Mirsharai 150 MW (Oil) | 17 | 0 | [17 empty] | 54 | 36 | 17 | 17 | 17 | 17 | 17 | 152218
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 25 | 27 | 30 | 17 | 42 | 51 | 47 | 29 | 21 | 25 | 28 | 24 | 12 | 26 | 11 | 18 | 16 | 16 |  | 14 | 20 | 24 | 24 | 22 | 21 | 23 | 586080
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 1 |  | 5 | 7 | 14 | 35 | 44 | 35 | 20 | 11 | 4 | 1 | [8 empty] | 215155
| Matarbari 2*600 MW (CPGCL) | 1157 | 1156 | 1155 | 1156 | 1156 | 1155 | 1152 | 1155 | 1153 | 1153 | 1153 | 1156 | 1153 | 1158 | 1152 | 1151 | 1153 | 1156 |  | 1151 | 1151 | 1151 | 1157 | 1154 | 1154 | 1155 | 27869090
| Meghnaghat (Reliance) 718MW CCPP | [8 empty] | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 2 | [10 empty] | 206000
120 | Eastern Zone Total | 6590 | 6320 | 6170 | 6045 | 6061 | 5829 | 5773 | 5756 | 5828 | 5838 | 5942 | 6097 | 6402 | 6395 | 6429 | 6337 | 6137 | 6208 | 0 | 7344 | 7830 | 7872 | 7811 | 7628 | 7503 | 7220 | 158072325
121
122
123 | Khulna 60MW
124 | manik
Khulna 115 PP MW (KPCL-2)
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 0
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 | [15 empty] | 17 |  | 19 | 30 | 42 | 51 | 17 | 17 | 17 | 293760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 1 | 10 | 7 | 11 | 23 | 36 | 28 | 44 | 25 | 23 | 21 | 1 | [8 empty] | 267840
131 | Rampal 1320 MW (BIFPCL) | 527 | 539 | 490 | 492 | 463 | 460 | 414 | 411 | 411 | 404 | 404 | 475 | 501 | 464 | 459 | 470 | 472 | 420 |  | 568 | 547 | 554 | 559 | 558 | 618 | 622 | 11818180
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 |  | 220 | 190 | 190 | 220 | 220 | 220 | 220 | 5205200
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 16 | 0 | [16 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 176928
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 250 | 238 | 164 | 150 | 150 | 150 | 150 | 150 | 184 | 200 | 237 | 260 | 200 | 200 | 200 | 200 | 200 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 5171000
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 1705
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 136 | 136 | 80 | 80 | 83 | 83 | 136 | 136 | 136 | 136 | 80 | 136 | 136 | 136 | 136 |  | 110 | 80 | 80 | 134 | 134 | 134 | 80 | 2745000
140 | Bhola 33 MW PP (Venture) | 9 | 9 | 8 | 7 | 6 | 6 | 5 | 5 | 5 | 6 | 4 | 5 | 5 | 6 | 6 | 5 | 5 | 6 |  | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 168399
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 897 | 897 | 898 | 897 | 897 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 898 | 897 | 899 | 899 | 899 | 894 |  | 894 | 893 | 894 | 730 | 898 | 898 | 898 | 21517090
147 | Bheramara 410 MW CCPP | 267 | 272 | 275 | 278 | 279 | 230 | 230 | 230 | 230 | 285 | 295 | 293 | 293 | 288 | 290 | 280 | 277 | 275 |  | 275 | 230 | 230 | 258 | 258 | 257 | 261 | 6494976
148 | Payra 1320 MW | 1244 | 1120 | 1010 | 980 | 980 | 880 | 870 | 870 | 880 | 900 | 970 | 1090 | 1170 | 1110 | 1100 | 1100 | 1080 | 1060 |  | 1130 | 1120 | 1160 | 1160 | 1140 | 1160 | 1244 | 27541100
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 62 | 62 | 59 | 60 | 60 | 60 | 62 | 61 | 61 | 60 | 61 | 60 | 60 | 60 | 60 | 60 |  | 61 | 60 | 60 | 60 | 60 | 61 | 61 | 1405090
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 18 |  | 23 | 23 | 23 | 23 | 23 | 0 |  | 105676
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 1 | 1 | 4 | 4 | 1 | 6 | 1 | 2 | 0 | 0 | [8 empty] | 21120
| Sirajganj 68 MW Solar Park | [6 empty] | 1 | 11 | 19 | 22 | 53 | 31 | 15 | 54 | 14 | 18 | 4 | 1 | [8 empty] | 249000
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 192 | 191 | 191 | 191 | 180 | 140 | 140 | 140 | 145 | 167 | 172 | 198 | 201 | 201 | 200 | 200 | 200 |  | 197 | 197 | 196 | 198 | 196 | 196 | 180 | 4714227
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 349 | 337 | 350 | 353 | 327 | 317 | 322 | 323 | 353 | 355 | 360 | 350 | 313 | 343 | 353 | 327 | 331 | 353 |  | 354 | 321 | 317 | 354 | 354 | 354 | 353 | 8274981
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 |  |  | 2 | 2 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 105012
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 28 | 0 | [24 empty] | 37593
168 | Santahar 50 MW Peaking PP | 28 | 0 | [15 empty] | 12 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 201600
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 236432
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 50 | 35 | 0 | [13 empty] | 30 | 35 | 35 | 35 |  |  |  | 530688
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 70 | 50 | 35 | 0 | [13 empty] | 70 | 70 | 35 | 35 |  |  |  | 588960
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 77 | 70 | 70 | 49 | 42 | 42 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 85 |  | 99 | 99 | 99 | 99 | 99 | 99 | 92 | 1396425
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 2 | 4 | 2 | 3 | 7 | 5 | 3 | 2 | 1 | [8 empty] | 31872
178 | Energypac Power Venture Thakurgaon Ltd. | 115 | 115 | 115 | 115 | 115 | 74 | 74 | 74 | 36 | 36 | 36 | 36 | 95 | 115 | 115 | 74 | 35 | 35 |  | 110 | 115 | 115 | 115 | 95 | 95 | 95 | 2100480
| Intraco Solar 30 MW | [5 empty] | 0 | 4 | 9 | 29 | 13 | 15 | 13 | 27 | 21 | 24 | 7 | 9 | 1 | [8 empty] | 171852
| Adani Power Jharkhanda Ltd | 760 | 761 | 763 | 764 | 763 | 777 | 765 | 759 | 766 | 764 | 764 | 762 | 761 | 768 | 770 | 750 | 751 | 764 |  | 766 | 758 | 760 | 771 | 759 | 790 | 891 | 18408941
178 | Teesta Solar Limited |  |  |  |  | 0 | 4 | 22 | 67 | 157 | 113 | 103 | 78 | 173 | 104 | 67 | 105 | 24 | 11 | [8 empty] | 1021680