## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-28 | Wednesday
|  | Date (day): | 2024-08-28 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14957.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16406 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-27 | 2024-08-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 408 | 421 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 18 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 90 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 2 | 54 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 131 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 29 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 23 | 41 | 39 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 24 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 11 | 11 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 16 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 258 | 270 | 280 |  | 20 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 132 | 131 | 130 | 130 |  | 19 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 54 | 54 | 51 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 27 | 86 | 70 | 85 | 19 |  | Lub Oil problem
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 87 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 1705 | 2446 | 2524 | 2710 | 2529 | 921
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 8 | 8 | 8 | 17 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 7 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 217 | 217 | 217
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 216 | 215 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 105 | 105
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 72 | 65 | 75 | 23 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 84 | 80 | 84 |  | 18 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 88 | 85 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 100 | 50 | 100 | 200 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 22 | 92 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 100 | 90 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 105 | 105
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 0 | 108 | 35 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 0 | 0 | 612 | 612 |  | 612 | Under maint.
61 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 14 | 10 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 1151 | 1151 | 1150 | 1150
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 1683 | 2258 | 3095 | 3333 | 528 | 960
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 205 | 210 | 210
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 280 | 280 | 280 | 80 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 260 | 270 | 270 | 90 |  | Gas shortage
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 250 | 230 | 230 | 250 | 150 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 36 | 38 | 38 | 7 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 5 | 20 | 20 | 35 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 110 | 12 | 140 |  | 10 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 36 | 35 | 37 |  | 15 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 31 | 30 | 35 | 40 | 123 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 18 | 200 | 200 | 200
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
76 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 34 | 56 | 90 | 90
77 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 7 | 42 | 8 | 43 |  | 9 | Engine problem
79 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 73 | 65 | 90 |  | 25 | Engine problem
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 57 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2917 | 1402 | 1693 | 1755 | 1900 | 784 | 66
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 6 | 10 | 20 | 20 | 182 |  | Gas shortage
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 95 | 124 | 98 | 125 | 75 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 77 | 58 | 77 | 38 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 6 | 12 |  | 10 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 35 |  | 19 | Engine prblem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 202 | 240 | 250.6 | 269 | 182 | 29
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 38 | 38 | 38 |  | 32 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 120 | 163 | 163
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 26 | 28 | 30 | 30 |  | 36 | GT-8 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 10 | 10 | 10 | 76 |  | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 137 | 134 | 135 | 136 |  | 95 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 260 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 349 | 350 | 350 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 368 | 346 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1398 | 1299 | 1390 | 1391 | 197 | 605
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 898 | 897 | 913 | 913
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 98 |  | 17 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 3 | 30 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 0 | 55 |  | 54 | Engine problem
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 245 | 250 | 250 | 160 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 70 | 72 | 33 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 11 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 505 | 600 | 586 | 600 | 634 |  | Unit-2 S/D due to Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1684 | 1832 | 1981 | 2028 | 1554 | 85
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 64 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 10 | 10 | 10
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 100 | 100 | 100 |  | 94 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1090 | 1244 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 17 | 35 | 115 |  | Fuel shortage
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 261 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1657 | 2015 | 1962 | 2026 | 115 | 94
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 38 | 30 | 40 |  | 12 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 19 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28 |  |  | Engine problem
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 25 | 46
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 171 | 196 | 196 | 24 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 354 | 309 | 350 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 25 | 28 |  | 22 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 110 | 113 | 113
141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 95 | 95 | 95 |  | 18 | Engine problem
142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1279 | 883 | 748 | 1400
143 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 49 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1882 | 1790 | 1663 | 2475 | 467 | 333
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 61 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 99 | 34 | 99 |  | 14 | Engine problem
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 55 | 94 | 75 | 115
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 97 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 275 | 254 | 337 | 274 | 40 | 398
| Total |  |  |  |  | 28166 | 27068 | 11888 | 13827 | 14957.6 | 16406 | 6396 | 3491
A. |  | 2024-08-27 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 13827 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 10428 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14220 | MW
3 | Day peak Generation : |  |  | 11888 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13667.62 | MW
4 | Evening peak Generation : |  |  | 13827 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 375 | MW
5 | Total Energy Generation : |  | 292.9766 | MKWHr | By Solar | 2.8739 | MKWHr
| By Gas : | 123.0357 | MKWHr |  | By Oil: | 35.0353 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 103.63 | MKWHr |  | By Hydro: | 5.1697 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.2496 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6396 | MW | Dhaka | 5008.72 | 4897.72 |  | 111 |  | 18:00 |  | 177
|  |  | For Plants S/D or M/C prob = |  |  | 3491 | MW | Chittagong | 1191.1 | 1191.1 |  | 0 |  | 19:00 |  | 330
|  |  | Total = |  |  | 9887 | MW | Khulna | 1599 | 1599 |  | 0 |  | 19:30 |  | 375.315
7 | Total Gas Supplied : |  |  | 884.5 | MMCFD |  |  | Rajshahi | 1408.6 | 1408.6 |  | 0 |  | 20:00 |  | 326.61
8 | Fuel Cost : | i) Gas : | Taka | 365747159.194 | ii) Oil : | Taka | 640014537.54 | Comilla | 1160 | 1148 |  | 12 |  | 21:00 |  | 390.595
|  | iii) Coal : | Taka | 681972425.34 | Total | Taka | 1687734122.074 | Mymensingh | 1226 | 1106 |  | 120 |  | 22:00 |  | 403.965
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7657.65 | MKWHr. | Sylhet | 616 | 609 |  | 7 |  | 23:00 |  | 403.01
| ii) During Peak Demand : |  |  | 394 | MW (W to E) at | 19:30 | hrs | Barisal | 421.2 | 421.2 |  | 0 |  | 24:00 |  | 380.09
| iii) Maximum : |  |  | 394 | MW at | 19:30 | hrs | Rangpur | 1037 | 912 |  | 125
10 | Maximum Temperature in Dhaka was |  |  |  | 33.0°C |  |  | Total | 13667.62 | 13292.62 |  | 375
B. |  | 2024-08-28 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.0°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16406 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13000 | MW
4 | Reserve(Generation end) |  |  |  | 1806 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 309.3723 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11361 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7642 | MKWHr. | ii) HVDC Flow at Peak Time |  | 897 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.2182 | MKWHr. | iii) Maximum HVDC Flow : |  | 898 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.9 |  | (b) Today: | 108.7 |  | (c) Rule Curve: |  | 97.68
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-08-27 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 23 | 17 | 12 | 0 | 0 | 138 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 25 | 38 | 17 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 50 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 95 | 0 | 0 | 93 | 0 | 132 | 0 | 49 | 68 | 0 | 361 | 57 | 17 | 34 | 0 | 80 | 0 | 17 | 34 | 9 | 50 | 350 | 52 | 0 | 17 | 17 | 0 | 17 | 0 | 90 | 17 | 250 | 0 | 0 | 0 | 16 | 1154 | 0 | 0 | 0 | 0 |  | 897 | 0 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 347 | 17 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 1244 | 220 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 623 | 0 | 270 | 971 | 0 | 0 | 0 | 0 |  | 6499 | 5318 | 11817 | 3540 | 897 | 1555 | 0 | 1158 | 4323 | 218 | 0 | 60 | 50 | 0 | 16 | 394.415 | 108.9
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 23 | 17 | 12 | 0 | 0 | 138 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 30 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 45 | 0 | 0 | 102 | 0 | 119 | 0 | 12 | 51 | 0 | 350 | 49 | 17 | 17 | 0 | 50 | 0 | 0 | 34 | 9 | 12 | 346 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 67 | 17 | 250 | 0 | 0 | 0 | 16 | 1154 | 0 | 0 | 0 | 0 |  | 898 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 326 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1180 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624 | 0 | 250 | 1135 | 0 | 0 | 0 | 0 |  | 6165 | 5298 | 11463 | 3553 | 898 | 1526 | 0 | 782 | 4404 | 218 | 0 | 16 | 50 | 0 | 16 | 388.685 | 108.9
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 23 | 17 | 12 | 0 | 0 | 138 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 30 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 15 | 0 | 0 | 102 | 0 | 132 | 0 | 12 | 51 | 0 | 348 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 12 | 350 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 67 | 17 | 250 | 0 | 0 | 0 | 13 | 1157 | 0 | 0 | 0 | 0 |  | 898 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 345 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1120 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 545 | 0 | 250 | 1133 | 0 | 0 | 0 | 0 |  | 6082 | 5191 | 11273 | 3569 | 898 | 1560 | 0 | 682 | 4267 | 218 | 0 | 16 | 50 | 0 | 13 | 360.035 | 108.9
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 23 | 17 | 12 | 0 | 0 | 139 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 48 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 15 | 0 | 0 | 102 | 0 | 132 | 0 | 12 | 17 | 0 | 350 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 12 | 370 | 17 | 0 | 17 | 0 | 0 | 17 | 0 | 67 | 17 | 250 | 0 | 0 | 0 | 11 | 1155 | 0 | 0 | 0 | 0 |  | 898 | 0 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 345 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 1000 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 250 | 1169 | 0 | 0 | 0 | 0 |  | 6066 | 5096 | 11162 | 3604 | 898 | 1555 | 0 | 627 | 4184 | 219 | 0 | 16 | 48 | 0 | 11 | 322.79 | 108.9
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 380 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 23 | 17 | 12 | 0 | 0 | 139 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 280 | 240 | 214 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 15 | 0 | 0 | 102 | 0 | 132 | 0 | 12 | 17 | 0 | 376 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 12 | 362 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 67 | 17 | 250 | 0 | 0 | 0 | 15 | 1157 | 0 | 0 | 0 | 0 |  | 898 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 347 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 990 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 250 | 1171 | 0 | 0 | 0 | 0 |  | 5898 | 5054 | 10952 | 3567 | 898 | 1451 | 0 | 553 | 4183 | 219 | 0 | 16 | 50 | 0 | 15 | 284.59 | 108.9
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 23 | 17 | 12 | 0 | 0 | 138 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 280 | 240 | 215 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 15 | 0 | 0 | 105 | 0 | 101 | 0 | 12 | 17 | 0 | 301 | 49 | 17 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 12 | 315 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 39 | 17 | 250 | 0 | 0 | 0 | 15 | 1153 | 0 | 0 | 5 | 0 |  | 898 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 334 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 920 | 180 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 488 | 0 | 200 | 1157 | 3 | 0 | 0 | 0 |  | 5622 | 4806 | 10428 | 3381 | 898 | 1372 | 0 | 490 | 3978 | 218 | 0 | 16 | 50 | 10 | 15 | 259.76 | 108.9
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 |  | 0 | 320 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 23 | 17 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 280 | 340 | 198 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 50 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 15 | 0 | 0 | 96 | 0 | 112 | 2 | 12 | 17 | 0 | 335 | 49 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 9 | 12 | 330 | 0 | 7 | 0 | 0 | 0 | 17 | 2 | 41 | 17 | 250 | 0 | 0 | 0 | 21 | 1156 | 0 | 0 | 11 | 0 |  | 897 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 347 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 860 | 180 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 491 | 3 | 170 | 1162 | 13 | 0 | 0 | 3 |  | 5698 | 4753 | 10451 | 3462 | 897 | 1385 | 0 | 469 | 3898 | 217 | 0 | 0 | 50 | 52 | 21 | 218.695 | 108.9
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 0 |  | 0 | 360 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 17 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 250 | 202 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 46 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 15 | 0 | 0 | 98 | 0 | 118 | 5 | 12 | 17 | 0 | 309 | 49 | 0 | 17 | 2 | 15 | 0 | 0 | 0 | 9 | 12 | 320 | 0 | 20 | 0 | 0 | 0 | 17 | 11 | 61 | 17 | 250 | 0 | 0 | 0 | 5 | 1158 | 0 | 0 | 28 | 0 |  | 898 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 346 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 890 | 180 | 0 | 0 | 2 | 60 | 52 | 0 | 0 | 495 | 6 | 170 | 1182 | 45 | 0 | 0 | 12 |  | 5677 | 4961 | 10638 | 3359 | 898 | 1400 | 0 | 550 | 3955 | 217 | 0 | 16 | 46 | 192 | 5 | 154.71 | 108.91
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 217 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 280 | 250 | 205 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 44 | 11 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 305 | 12 | 2 | 0 | 15 | 0 | 0 | 97 | 0 | 133 | 0 | 12 | 17 | 0 | 323 | 49 | 1 | 17 | 3 | 15 | 0 | 0 | 0 | 9 | 12 | 345 | 0 | 26 | 0 | 0 | 0 | 17 | 6 | 67 | 29 | 250 | 0 | 0 | 0 | 7 | 1152 | 0 | 0 | 40 | 0 |  | 898 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 398 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 940 | 220 | 0 | 0 | 1 | 50 | 55 | 0 | 0 | 495 | 15 | 170 | 1168 | 73 | 0 | 0 | 16 |  | 5980 | 5139 | 11119 | 3505 | 898 | 1625 | 0 | 586 | 3987 | 217 | 0 | 16 | 44 | 234 | 7 | 58.255 | 108.92
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 250 | 212 | 0 | 30 | 35 | 7 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 58 | 7 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 15 | 0 | 0 | 97 | 0 | 132 | 0 | 12 | 17 | 0 | 355 | 49 | 34 | 17 | 3 | 15 | 0 | 0 | 0 | 9 | 12 | 352 | 0 | 35 | 0 | 0 | 0 | 17 | 23 | 67 | 35 | 250 | 0 | 0 | 0 | 8 | 1152 | 0 | 0 | 20 | 0 |  | 898 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 414 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 940 | 220 | 0 | 0 | 2 | 48 | 55 | 0 | 0 | 460 | 17 | 170 | 1155 | 49 | 0 | 0 | 34 |  | 6057 | 5143 | 11200 | 3588 | 898 | 1618 | 0 | 624 | 3938 | 217 | 0 | 16 | 58 | 235 | 8 | 48 | 108.92
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 3 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 16 | 0 | 17 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 300 | 265 | 212 | 0 | 30 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 48 | 6 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 163 | 0 | 26 | 10 | 0 | 137 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 15 | 0 | 0 | 97 | 0 | 132 | 5 | 12 | 17 | 0 | 364 | 49 | 34 | 17 | 2 | 15 | 0 | 0 | 0 | 9 | 12 | 352 | 1 | 19 | 0 | 0 | 0 | 17 | 8 | 70 | 35 | 250 | 0 | 0 | 0 | 6 | 1151 | 0 | 0 | 29 | 0 |  | 898 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 414 | 0 | 0 | 0 | 0 | 34 | 0 | 3 | 0 | 1020 | 220 | 0 | 0 | 1 | 17 | 55 | 0 | 0 | 486 | 30 | 208 | 1250 | 91 | 0 | 0 | 17 |  | 6092 | 5419 | 11511 | 3655 | 898 | 1631 | 0 | 640 | 4176 | 217 | 0 | 16 | 48 | 224 | 6 | 70.67 | 108.91
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 18 | 280 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 2 | 29 | 55 | 0 | 16 | 7 | 17 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 300 | 210 | 0 | 31 | 33 | 5 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 15 | 34 | 6 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 120 | 0 | 26 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 45 | 0 | 0 | 95 | 0 | 132 | 7 | 12 | 18 | 0 | 385 | 49 | 34 | 17 | 5 | 30 | 0 | 0 | 0 | 9 | 12 | 368 | 27 | 26 | 87 | 0 | 0 | 17 | 20 | 72 | 35 | 250 | 0 | 0 | 0 | 14 | 1151 | 0 | 0 | 57 | 0 |  | 898 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 354 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 1090 | 220 | 0 | 0 | 3 | 11 | 55 | 0 | 0 | 505 | 24 | 261 | 1279 | 97 | 0 | 0 | 49 |  | 6390 | 5498 | 11888 | 3625 | 898 | 1518 | 0 | 913 | 4346 | 217 | 0 | 16 | 34 | 307 | 14 | 78.31 | 108.91
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 32 | 55 | 55 | 0 | 16 | 7 | 22 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 280 | 275 | 212 | 0 | 31 | 32 | 5 | 0 | 51 | 0 | 0 | 20 | 0 | 0 | 0 | 15 | 42 | 6 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 136 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 188 | 0 | 0 | 95 | 0 | 116 | 1 | 12 | 34 | 6 | 325 | 48 | 34 | 17 | 5 | 30 | 0 | 0 | 17 | 9 | 12 | 315 | 48 | 50 | 108 | 0 | 0 | 17 | 24 | 68 | 35 | 250 | 0 | 0 | 0 | 19 | 1152 | 0 | 0 | 77 | 0 |  | 897 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 325 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 1100 | 220 | 0 | 0 | 3 | 26 | 55 | 0 | 0 | 560 | 34 | 270 | 1357 | 70 | 0 | 0 | 41 |  | 6595 | 5602 | 12197 | 3451 | 897 | 1479 | 0 | 1239 | 4499 | 217 | 0 | 16 | 42 | 338 | 19 | 117 | 108.9
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 16 | 7 | 22 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 285 | 275 | 205 | 0 | 31 | 35 | 5 | 0 | 51 | 0 | 0 | 32 | 0 | 0 | 0 | 18 | 38 | 5 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 120 | 0 | 25 | 10 | 0 | 136 | 0 | 0 | 0 | 280 | 10 | 2 | 0 | 225 | 0 | 0 | 95 | 0 | 115 | 19 | 12 | 34 | 33 | 305 | 58 | 34 | 17 | 3 | 30 | 0 | 0 | 17 | 9 | 12 | 315 | 50 | 31 | 108 | 0 | 0 | 17 | 23 | 84 | 35 | 250 | 0 | 0 | 0 | 4 | 1156 | 0 | 0 | 47 | 0 |  | 898 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 7 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 2 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 352 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1090 | 180 | 0 | 0 | 2 | 49 | 55 | 0 | 0 | 510 | 35 | 270 | 1375 | 156 | 0 | 0 | 32 |  | 6606 | 5657 | 12263 | 3408 | 898 | 1460 | 0 | 1344 | 4460 | 217 | 0 | 34 | 38 | 400 | 4 | 131 | 108.91
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 19 | 22 | 22 | 11 | 0 | 0 | 48 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 295 | 185 | 0 | 30 | 35 | 5 | 0 | 51 | 0 | 37 | 33 | 0 | 0 | 0 | 18 | 60 | 6 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 163 | 0 | 25 | 10 | 0 | 134 | 0 | 0 | 0 | 310 | 11 | 2 | 0 | 229 | 0 | 0 | 94 | 0 | 113 | 8 | 12 | 34 | 36 | 330 | 58 | 34 | 17 | 1 | 30 | 0 | 0 | 17 | 9 | 12 | 340 | 51 | 42 | 140 | 0 | 0 | 17 | 26 | 72 | 35 | 230 | 0 | 0 | 0 | 15 | 1152 | 0 | 0 | 57 | 0 |  | 898 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 2 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 353 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 1130 | 180 | 0 | 0 | 2 | 17 | 55 | 0 | 0 | 516 | 35 | 307 | 1281 | 146 | 0 | 0 | 27 |  | 6805 | 5614 | 12419 | 3534 | 898 | 1530 | 0 | 1370 | 4445 | 128 | 0 | 74 | 60 | 365 | 15 | 221 | 108.89
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 19 | 22 | 22 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 280 | 260 | 189 | 0 | 30 | 35 | 5 | 0 | 51 | 0 | 37 | 33 | 0 | 0 | 0 | 18 | 58 | 8 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 163 | 0 | 25 | 10 | 0 | 134 | 0 | 0 | 0 | 305 | 11 | 2 | 0 | 241 | 0 | 0 | 95 | 0 | 113 | 6 | 12 | 64 | 35 | 300 | 57 | 34 | 17 | 1 | 30 | 0 | 0 | 17 | 9 | 12 | 316 | 84 | 30 | 162 | 5 | 0 | 17 | 4 | 74 | 35 | 230 | 0 | 0 | 0 | 5 | 1153 | 0 | 0 | 32 | 0 |  | 897 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 16 | 0 | 0 | 0 | 34 | 14 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 348 | 0 | 0 | 15 | 0 | 34 | 0 | 2 | 35 | 1180 | 180 | 0 | 0 | 2 | 5 | 55 | 0 | 0 | 520 | 22 | 307 | 1008 | 103 | 0 | 0 | 29 |  | 6861 | 5437 | 12298 | 3441 | 897 | 1520 | 0 | 1572 | 4229 | 217 | 0 | 122 | 58 | 237 | 5 | 202 | 108.88
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 19 | 22 | 22 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 285 | 260 | 201 | 0 | 31 | 36 | 5 | 0 | 51 | 0 | 36 | 33 | 0 | 0 | 0 | 18 | 54 | 10 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 300 | 11 | 2 | 0 | 243 | 0 | 0 | 95 | 0 | 126 | 3 | 12 | 68 | 33 | 349 | 57 | 34 | 17 | 0 | 30 | 0 | 9 | 17 | 9 | 12 | 316 | 85 | 2 | 162 | 17 | 0 | 17 | 2 | 73 | 35 | 230 | 0 | 0 | 0 | 4 | 1150 | 0 | 0 | 5 | 0 |  | 898 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 100 | 6 | 16 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 0 | 21 | 0 | 13 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 392 | 0 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 1180 | 220 | 0 | 0 | 1 | 3 | 55 | 0 | 0 | 517 | 9 | 307 | 756 | 46 | 0 | 0 | 13 |  | 6912 | 5227 | 12139 | 3515 | 898 | 1607 | 0 | 1635 | 3971 | 217 | 0 | 152 | 54 | 86 | 4 | 202 | 108.87
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 320 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 19 | 22 | 22 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 1 | 215 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 305 | 260 | 208 | 0 | 30 | 36 | 5 | 0 | 51 | 0 | 36 | 33 | 0 | 0 | 0 | 18 | 50 | 9 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 134 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 251 | 0 | 0 | 95 | 0 | 131 | 0 | 12 | 68 | 30 | 387 | 57 | 34 | 17 | 0 | 30 | 0 | 17 | 17 | 9 | 12 | 336 | 85 | 1 | 162 | 17 | 0 | 17 | 1 | 73 | 0 | 230 | 17 | 0 | 0 | 0 | 1153 | 0 | 0 | 1 | 0 |  | 898 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 1 | 27 | 0 | 100 | 6 | 16 | 0 | 0 | 0 | 38 | 21 | 0 | 0 | 0 | 25 | 0 | 28 | 0 | 0 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 349 | 9 | 0 | 35 | 0 | 95 | 0 | 1 | 35 | 1000 | 180 | 0 | 2 | 0 | 1 | 94 | 0 | 0 | 514 | 1 | 250 | 753 | 2 | 0 | 0 | 0 |  | 6671 | 4944 | 11615 | 3427 | 898 | 1345 | 0 | 1730 | 3731 | 217 | 0 | 209 | 50 | 8 | 0 | 177 | 108.87
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.845 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 74 | 132 | 0 | 0 | 0 | 0 | 39 | 55 | 55 | 0 | 19 | 22 | 22 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 6 | 215 | 0 | 0 | 0 |  | 12 | 72 | 85 | 0 | 0 | 3 | 0 | 23 | 0 | 0 | 0 | 280 | 260 | 200 | 0 | 30 | 36 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 60 | 10 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 320 | 12 | 2 | 0 | 257 | 0 | 0 | 124 | 0 | 131 | 0 | 88 | 91 | 83 | 349 | 77 | 52 | 34 | 0 | 120 | 14 | 22 | 52 | 9 | 88 | 346 | 86 | 0 | 162 | 32 | 0 | 17 | 0 | 73 | 29 | 230 | 90 | 0 | 0 | 4 | 1151 | 0 | 0 | 0 | 0 |  | 898 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 2 | 39 | 0 | 100 | 10 | 64 | 0 | 0 | 0 | 38 | 21 | 83 | 0 | 0 | 42 | 0 | 28 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 393 | 26 | 0 | 50 | 0 | 99 | 0 | 0 | 95 | 1100 | 220 | 0 | 37 | 0 | 0 | 94 | 0 | 0 | 614 | 0 | 307 | 868 | 0 | 0 | 0 | 0 |  | 7862 | 5692 | 13554 | 3515 | 898 | 1645 | 0 | 2447 | 4100 | 217 | 0 | 668 | 60 | 0 | 4 | 330 | 108.84
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 72 | 84 | 0 | 0 | 6 | 0 | 26 | 0 | 0 | 0 | 280 | 260 | 205 | 0 | 30 | 36 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 56 | 10 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 260 | 12 | 2 | 0 | 258 | 0 | 0 | 124 | 0 | 131 | 0 | 88 | 200 | 110 | 349 | 77 | 52 | 34 | 0 | 100 | 0 | 22 | 52 | 9 | 100 | 346 | 86 | 0 | 162 | 17 | 0 | 17 | 0 | 73 | 35 | 230 | 108 | 0 | 0 | 10 | 1151 | 0 | 0 | 0 | 0 |  | 897 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 3 | 52 | 0 | 100 | 10 | 80 | 0 | 0 | 0 | 38 | 19 | 90 | 0 | 0 | 42 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 309 | 35 | 0 | 110 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 600 | 0 | 307 | 883 | 0 | 0 | 0 | 0 |  | 7936 | 5891 | 13827 | 3546 | 897 | 1461 | 0 | 2691 | 4246 | 217 | 0 | 703 | 56 | 0 | 10 | 375.315 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 72 | 84 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 285 | 260 | 211 | 0 | 30 | 37 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 60 | 11 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 270 | 12 | 2 | 0 | 264 | 0 | 0 | 125 | 0 | 131 | 0 | 100 | 183 | 6 | 350 | 78 | 52 | 17 | 0 | 50 | 0 | 17 | 52 | 9 | 100 | 346 | 85 | 0 | 162 | 17 | 0 | 17 | 0 | 73 | 35 | 230 | 17 | 0 | 0 | 7 | 1152 | 0 | 0 | 0 | 0 |  | 898 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 110 | 0 | 0 | 0 | 38 | 19 | 90 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 338 | 35 | 0 | 110 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 581 | 0 | 307 | 909 | 0 | 0 | 0 | 0 |  | 7645 | 5913 | 13558 | 3558 | 898 | 1497 | 0 | 2504 | 4255 | 217 | 0 | 562 | 60 | 0 | 7 | 326.61 | 108.85
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 132 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 136 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 72 | 84 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 285 | 260 | 207 | 0 | 30 | 35 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 60 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 26 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 278 | 0 | 0 | 125 | 0 | 131 | 0 | 100 | 172 | 6 | 350 | 78 | 52 | 17 | 0 | 50 | 0 | 17 | 52 | 9 | 100 | 346 | 85 | 0 | 108 | 17 | 0 | 17 | 0 | 72 | 35 | 230 | 17 | 0 | 0 | 3 | 1153 | 0 | 0 | 0 | 0 |  | 898 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 110 | 0 | 0 | 0 | 38 | 18 | 90 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 393 | 35 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 180 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 586 | 0 | 307 | 1037 | 0 | 0 | 0 | 0 |  | 7663 | 6028 | 13691 | 3554 | 898 | 1593 | 0 | 2418 | 4388 | 216 | 0 | 561 | 60 | 0 | 3 | 390.595 | 108.84
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 50 | 131 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 136 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 32 | 34 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 280 | 260 | 210 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 62 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 26 | 10 | 0 | 135 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 195 | 0 | 0 | 125 | 0 | 131 | 0 | 100 | 163 | 6 | 350 | 78 | 52 | 17 | 0 | 50 | 0 | 17 | 52 | 9 | 100 | 346 | 85 | 0 | 35 | 17 | 0 | 17 | 0 | 72 | 35 | 230 | 17 | 0 | 0 | 10 | 1151 | 0 | 0 | 0 | 0 |  | 898 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 64 | 0 | 0 | 0 | 38 | 18 | 90 | 0 | 0 | 35 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 35 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 180 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 593 | 0 | 307 | 1177 | 0 | 0 | 0 | 0 |  | 7218 | 6139 | 13357 | 3477 | 898 | 1597 | 0 | 2142 | 4532 | 216 | 0 | 423 | 62 | 0 | 10 | 403.965 | 108.82
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 42 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 325 | 260 | 206 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 62 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 26 | 10 | 0 | 136 | 0 | 0 | 0 | 285 | 12 | 2 | 0 | 195 | 0 | 0 | 125 | 0 | 131 | 0 | 100 | 136 | 0 | 391 | 78 | 52 | 17 | 0 | 50 | 0 | 17 | 52 | 9 | 100 | 375 | 85 | 0 | 35 | 17 | 0 | 17 | 0 | 73 | 35 | 230 | 0 | 0 | 0 | 12 | 1155 | 0 | 0 | 0 | 25 |  | 898 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 64 | 0 | 0 | 0 | 38 | 18 | 90 | 0 | 0 | 35 | 0 | 28 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 50 | 0 | 50 | 0 | 92 | 0 | 0 | 50 | 1244 | 180 | 0 | 17 | 0 | 0 | 94 | 0 | 0 | 593 | 0 | 307 | 1308 | 0 | 0 | 0 | 0 |  | 7181 | 6172 | 13353 | 3590 | 898 | 1605 | 0 | 2002 | 4669 | 217 | 0 | 273 | 62 | 0 | 12 | 403.01 | 108.8
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 41 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 22 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 280 | 260 | 206 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 42 | 0 | 0 | 0 | 18 | 60 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 195 | 0 | 0 | 125 | 0 | 131 | 0 | 88 | 136 | 0 | 349 | 78 | 35 | 17 | 0 | 50 | 0 | 17 | 52 | 9 | 90 | 346 | 85 | 0 | 35 | 17 | 0 | 17 | 0 | 71 | 35 | 230 | 0 | 0 | 96 | 7 | 1154 | 0 | 0 | 0 | 38 |  | 898 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 64 | 0 | 0 | 0 | 38 | 14 | 90 | 0 | 0 | 35 | 0 | 28 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 396 | 65 | 0 | 50 | 0 | 84 | 0 | 0 | 50 | 1244 | 180 | 0 | 17 | 0 | 0 | 95 | 0 | 0 | 598 | 0 | 250 | 1407 | 0 | 0 | 0 | 0 |  | 7147 | 6205 | 13352 | 3470 | 898 | 1614 | 0 | 1968 | 4811 | 217 | 0 | 269 | 60 | 0 | 7 | 380.09 | 108.78
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9493200 | 0 |  | 0 | 9929000 | 0 | 0 | 0 | 715790 | 7410394 | 0 | 0 | 0 | 759600 | 966720 | 0 | 0 | 0 | 0 | 385200 | 802161 | 754704 | 0 | 447600 | 415440 | 506200 | 255200 | 960 | 0 | 3249655 | 1920000 | 0 | 0 | 48132 | 5156686 | 0 | 0 | 0 |  | 192960 | 236671 | 291983 | 0 | 0 | 8160 | 0 | 528000 | 0 | 0 | 0 | 7365200 | 6348000 | 5031000 | 0 | 752990 | 866304 | 266880 | 0 | 1176493 | 0 | 246816 | 450960 | 0 | 0 | 0 | 415500 | 1218240 | 270720 | 0 | 0 | 11100 | 911000 | 0 | 0 | 0 | 3439964 | 0 | 638112 | 261120 | 0 | 3281410 | 0 | 0 | 0 | 7259000 | 273168 | 55384 | 0 | 3259309 | 0 | 0 | 2481600 | 0 | 3028032 | 60750 | 827520 | 1581600 | 384727 | 8717000 | 1386000 | 731040 | 490945 | 22797 | 918327 | 21980 | 189020 | 443460 | 232680 | 884160 | 8189400 | 1094400 | 289780 | 1584000 | 199473 | 0 | 434880 | 164071 | 1686720 | 703800 | 5977000 | 175636 | 0 | 10909 | 249600 | 27869090 | 0 | 0 | 384309 | 16000 |  | 21764160 | 0 | 6445440 | 0 | 0 | 0 | 0 | 0 | 2400 | 78592 | 0 | 2213000 | 190407 | 533472 | 0 | 0 | 0 | 320275 | 144932 | 501120 | 0 | 0 | 252136 | 0 | 227570 | 0 | 0 | 106992 | 1405090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4546082 | 0 | 8738327 | 283200 | 0 | 680640 | 0 | 1390454 | 0 | 34812 | 583200 | 28273200 | 5158080 | 0 | 159600 | 27780 | 333360 | 1277568 | 0 | 0 | 13127270 | 207459 | 6153000 | 26791431 | 1023000 | 0 | 3469 | 311250 |  | 159703792 | 133288768 | 292992560 | 86088422 | 21764160 | 36947271 | 0 | 31590434 | 103629990 | 5169655 | 0 | 3444851 | 1218240 | 2873937 | 249600 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27340416 | 0 |  | 0 | 31574220 | 0 | 0 | 0 | 12612219.8 | 22601701.7 | 0 | 0 | 0 | 13634820 | 18773702.4 | 0 | 0 | 0 | 0 | 7033752 | 12642057.36 | 13803536.16 | 0 | 335700 | 0 | 0 | 0 | 17193.6 | 0 | 0 | 0 | 0 | 0 | 911620.08 | 16449828.34 | 0 | 0 | 0 |  | 3394166.4 | 4167776.31 | 5229415.53 | 0 | 0 | 134313.6 | 0 | 0 | 0 | 0 | 0 | 20548908 | 19424880 | 16702920 | 0 | 2432157.7 | 2919444.48 | 1168934.4 | 0 | 4717736.93 | 0 | 4420474.56 | 8144337.6 | 0 | 0 | 0 | 311625 | 7991654.4 | 841939.2 | 0 | 0 | 0 | 3552900 | 0 | 0 | 0 | 11764676.88 | 0 | 3541521.6 | 1363046.4 | 0 | 9155133.9 | 0 | 0 | 0 | 22430310 | 204876 | 42091.84 | 0 | 66489903.6 | 0 | 0 | 47671536 | 0 | 53323643.52 | 0 | 14738131.2 | 27440760 | 6378773.66 | 23100050 | 26417160 | 13714310.4 | 8807553.3 | 0 | 15014646.45 | 427291.2 | 3391018.8 | 8474520.6 | 4516318.8 | 15746889.6 | 21783804 | 18681408 | 0 | 28971360 | 3347156.94 | 0 | 7771305.6 | 0 | 30394694.4 | 11922372 | 17751690 | 2472954.88 | 0 | 76035.73 | 0 | 164427631 | 0 | 0 | 0 | 0 |  | 61157289.6 | 0 | 19014048 | 0 | 0 | 0 | 0 | 0 | 45144 | 1478315.52 | 0 | 6993080 | 902529.18 | 9197057.28 | 0 | 0 | 0 | 5736125.25 | 2659502.2 | 8423827.2 | 0 | 0 | 4515755.76 | 0 | 4075778.7 | 0 | 0 | 80992.944 | 15498142.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15138453.06 | 0 | 25515914.84 | 4837056 | 0 | 13490284.8 | 0 | 27697843.68 | 0 | 0 | 11570688 | 183210336 | 16041628.8 | 0 | 3088260 | 0 | 0 | 22165804.8 | 0 | 0 | 95829071 | 0 | 45839850 | 177091358.91 | 0 | 0 | 0 | 0 |  | 975588927.85 | 781294138.224 | 1756883066.074 | 250268161.764 | 61157289.6 | 115478997.43 | 0 | 578015765.23 | 681972425.34 | 0 | 0 | 61998772.31 | 7991654.4 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 |  | 0 | 450 | 0 | 0 | 0 | 18 | 280 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 2 | 29 | 55 | 0 | 16 | 7 | 17 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 310 | 300 | 210 | 0 | 31 | 33 | 5 | 0 | 51 | 0 | 0 | 7 | 0 | 0 | 0 | 15 | 34 | 6 | 0 | 0 | 3 | 38 | 0 | 0 | 0 | 120 | 0 | 26 | 10 | 0 | 137 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 45 | 0 | 0 | 95 | 0 | 132 | 7 | 12 | 18 | 0 | 385 | 49 | 34 | 17 | 5 | 30 | 0 | 0 | 0 | 9 | 12 | 368 | 27 | 26 | 87 | 0 | 0 | 17 | 20 | 72 | 35 | 250 | 0 | 0 | 0 | 14 | 1151 | 0 | 0 | 57 | 0 |  | 898 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 354 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 1090 | 220 | 0 | 0 | 3 | 11 | 55 | 0 | 0 | 505 | 24 | 261 | 1279 | 97 | 0 | 0 | 49 |  | 11888 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 131 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 | 0 | 12 | 72 | 84 | 0 | 0 | 6 | 0 | 26 | 0 | 0 | 0 | 280 | 260 | 205 | 0 | 30 | 36 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 56 | 10 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 260 | 12 | 2 | 0 | 258 | 0 | 0 | 124 | 0 | 131 | 0 | 88 | 200 | 110 | 349 | 77 | 52 | 34 | 0 | 100 | 0 | 22 | 52 | 9 | 100 | 346 | 86 | 0 | 162 | 17 | 0 | 17 | 0 | 73 | 35 | 230 | 108 | 0 | 0 | 10 | 1151 | 0 | 0 | 0 | 0 |  | 897 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 3 | 52 | 0 | 100 | 10 | 80 | 0 | 0 | 0 | 38 | 19 | 90 | 0 | 0 | 42 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 309 | 35 | 0 | 110 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 54 | 0 | 0 | 94 | 0 | 0 | 600 | 0 | 307 | 883 | 0 | 0 | 0 | 0 |  | 13827 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 100 | 80 | 55 | 335 | 0 | 0 | 50 | 90 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 25 | 12 | 17 | 0 | 137 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 75 | 84 | 0 | 0 | 50 | 0 | 20 | 0 | 0 | 0 | 280 | 270 | 210 | 0 | 40 | 38 | 20 | 0 | 51 | 0 | 37 | 43 | 0 | 0 |  | 18 | 90 | 20 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 280 | 0 | 0 | 125 | 0 | 130 | 0 | 100 | 200 | 140 | 350 | 77 | 54 | 105 | 0 | 100 | 54 | 110 | 114 | 9 | 100 | 350 | 85 | 0 | 162 | 105 | 0 | 35 | 0 | 90 | 35 | 250 | 163 | 0 | 612 | 60 | 1150 | 0 | 0 |  |  |  | 913 | 0 | 250 | 0 | 98 | 0 | 0 | 0 | 40 | 55 | 0 | 100 | 10 | 110 | 0 | 0 | 0 | 40 | 20 | 90 | 28 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 72 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 307 | 1400 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 100 | 80 | 55 | 335 | 0 | 0 | 50 | 90 | 16 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 16 | 23 | 25 | 12 | 16 | 0 | 137 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 65 | 80 | 0 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 280 | 270 | 210 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 35 | 8 | 0 | 0 |  | 18 | 90 | 20 | 0 | 0 | 1.6 | 38 | 0 | 0 | 0 | 163 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 270 | 0 | 0 | 98 | 0 | 130 | 20 | 85 | 200 | 12 | 350 | 58 | 54 | 105 | 5 | 50 | 54 | 92 | 114 | 9 | 90 | 350 | 70 | 50 | 162 | 105 | 0 | 17 | 35 | 65 | 35 | 230 | 35 | 0 | 612 | 42 | 1150 | 0 | 0 | 70 |  |  | 913 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 100 | 10 | 64 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 350 | 70 | 0 | 113 | 0 | 34 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 75 | 0 | 0 | 586 | 30 | 307 | 748 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 23 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 270 | 196 | 0 | 25 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 16 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 131 | 9 | 5 | 17 | 0 | 350 | 49 | 17 | 0 | 0 | 5 | 0 | 0 | 17 | 9 | 12 | 340 | 0 | 27 | 38 | 0 | 0 | 0 | 13 | 17 | 17 | 230 | 0 | 0 | 612 | 1 | 1152 | 0 | 0 | 10 | 0 | 0 | 896 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 395 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 1140 | 220 | 0 | 0 | 2 | 22 | 0 | 0 | 0 | 500 | 15 | 307 | 762 | 95 | 0 | 0 | 2 | 0 |  |  |  | 123035693 | 21764160 | 0 | 103629990 | 35035285 | 1218240 | 2873937 | 249600 | 5169655 |  |  | 292976560
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 123.0357 | 21.7642 | 0 | 103.63 | 35.0353 | 1.2182 | 2.8739 | 0.2496 | 5.1697
| Minimum Generation |  | 10428 | 6:00
| Highest Generation |  | 13827 | 19:30 | [129 empty] | 0 | [74 empty] | 292.9766
| Day Peak Generation |  | 11888 | 12:00
| Evening Peak Generation |  | 13827 | 19:30 | [204 empty] | 202699852
| HVDC Max Flow |  | 898 | 2:00 | [204 empty] | 202.6999
| HVDC EvPeak Flow |  | 897 | 19:30
| Load factor L.F |  | 88.29% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-28
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11888 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 11361
Evening Peak Generation : |  |  | 13827 | MW Hour : | 19:30 | Available Max Generation : |  | 16406
E.P. Demand (at gen end) : |  |  | 14220 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 14600
Maximum Generation : |  |  | 13827 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1806
Total Gen. (MKWH) : |  |  | 292.9766 | System Load Factor : | 88.29% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 394 | MW at | 19:30 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-28
Actual : |  | 108.7 | Ft.(MSL) , | Rule curve : | 97.68 | Ft.( MSL )
Gas Consumed : |  | Total = | 884.5 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 365747159.194
: |  |  | Coal : | 681972425.34 | Oil : | 640014537.54 | Total : | 1687734122.074
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 111 | 2664:00 | 4307.5694 |  |  | 0 | -21.73%
Chittagong Area |  | 0 | 0:00 | 1182.1376 |  |  | 0 | -19.89%
Khulna Area |  | 0 | 0:00 | 1655.4666 |  |  | 0 | -19.5%
Rajshahi Area |  | 0 | 0:00 | 1438.4608 |  |  | 0 | -19.08%
Cumilla Area |  | 12 | 288:00 | 1183.8221 |  |  | 0 | -19.34%
Mymensingh Area |  | 120 | 2880:00 | 880.2349 |  |  | 0 | -18.98%
Sylhet Area |  | 7 | 168:00 | 493.6451 |  |  | 0 | -19.67%
Barisal Area |  | 0 | 0:00 | 411.1693 |  |  | 0 | -18.91%
Rangpur Area |  | 125 | 3000:00 | 804.1802 |  |  | 0 | -18.92%
Total |  | 375 |  | 12356.6859 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
09:01 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D Due to Transformer upgradation
09:02 |  | Natore 132/33kV S/S TR-4 (435 T) HT Scheduled S/D Due to Transformer upgradation
09:13 | 17:31 | Hasnabad 132/33kV S/S Keraniganj-1 (Pre- Lalbag) Scheduled S/D Due to Modification of 132kv bus bar protection work.
09:17 | 17:37 | Keranigonj 230/132/33kV S/S Hasnabad Scheduled S/D Due to Bus work at Hasnabad Grid S/S
09:17 | 11:13 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T LT Forced S/D Due to 33 kv Nesco Red hot Maintenance Work |  |  |  |  | 45.0MW load interrup.
09:17 | 11:13 | Barapukuria 230/132/33kV S/S 132/33 KV T-4, 444T HT Forced S/D Due to 33 kv Nesco Red hot Maintenance wo |  |  |  |  | 45.0MW load interrup.
09:25 | 18:38 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due to Modification of 132kv bus bar protection work.
09:25 | 18:38 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due to Modification of 132kv bus bar protection work.
09:54 | 17:24 | Haripur 230/132kV S/S Bus-1 Scheduled S/D Due to Redhot maintanance 230 Kv Bhulta Ckt-2 Bus-1 DS.
10:28 | 19:36 | BIPTC S/S Baharampur-1 Forced S/D Due to Shutdown is taken from Baharampur end
10:58 | 13:35 | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D Due to Relay Change
12:00 |  | Day Peak Gen. 11888 MW
12:07 |  | Bogura 230 KV Bay -1 S/D at Bogura (W).
12:08 | 15:33 | Gopalganj 400/132kV S/S ATR-05 LT Project Work S/D
12:08 |  | Bogura 230 KV Bay -2 S/D at Bogura (W).
12:09 | 15:32 | Gopalganj 400/132kV S/S ATR-05 HT Project Work S/D
12:11 |  | Naogaon 230 KV Bay -1 S/D at Bogura (W).
12:13 |  | Naogaon 230 KV Bay -2 S/D at Bogura (W).
| 13:02 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
| 13:02 | Ashuganj-Kishoreganj 132kV Ckt-1 is restored.
13:25 | 14:03 | Munshiganj 132/33kV S/S Transformer-1 LT Forced S/D Due to Red Hot(Temperature Rise)
14:44 | 15:19 | Chandraghona-Kaptai 132 kV Ckt-2 Tripped from Chandraghona 132/33kV end showing REL670 relays.
16:35 |  | Patuakhali 132/33kV S/S 405T (T-1) HT Forced S/D Due to 132 kV LA bad sound
16:35 |  | Patuakhali 132/33kV S/S 405T (T-1) LT Forced S/D Due to For T-1 transformer 132 kV LA bad Sounds
19:30 |  | Evening peak Generation = 13,827 MW
21:16 | 22:39 | Patuakhali 132/33kV S/S 425T (T-3) LT Forced S/D Due to Red hot at 33 kV bust section DS that's why shutdown by PBS
21:16 | 22:38 | Patuakhali 132/33kV S/S 425T (T-3) HT Forced S/D Due to Red hot at 33 kV bust section DS that's why shutdown by PBS
| 22:39 | Patuakhali 132/33kV S/S 425T (T-3) LT is restored.
23:51 |  | SS Power Synchronized
05:54 |  | Rajbari 132/33kV S/S 132 kV Bus-I Project Work S/D Due to Gantry Tower Piling.
05:59 | 07:20 | Shyampur 132/33kV S/S GT-3 HT Forced S/D Due to Red hot Repair at HT CT terminal Blue phase
06:00 |  | Minimum Generation :11361MW
06:38 | 07:27 | Bagerhat 132/33kV S/S Transformer-1 (403T) LT Scheduled S/D |  |  |  |  | 19.0MW load interrup.
06:38 | 07:24 | Bagerhat 132/33kV S/S Transformer-1 (403T) HT Scheduled S/D Due to Shutdown for Red hot maintenance work of 33kV Rampal |  |  |  |  | 19.0MW load interrup.
Feeder Bus DS.
07:20 |  | APJL Godda U#2 was withdrawn at 07:20 hrs BST of 28.08.24 for turbine balancing work.
07:20 |  | Adani Power Jharkhand Ltd. Unit-2 was forced shutdown.
| 07:29 | Sirajganj-Ullahpara 132KV Ckt-2 is restored.
07:29 |  | Baghabari-Ullahpara 132 kV Ckt-1 Scheduled S/D from Ullahpara 132/33kV end Due to Baghabari Power Station Work.
07:40 |  | Baghabari 230/132kV S/S T-1 LT Scheduled S/D Due to S/D Taken by BPDB
07:41 |  | Baghabari 230/132kV S/S T-2 Bank LT Scheduled S/D Due to Taken by BPDB
07:49 |  | Baghabari 230/132kV S/S T-1 HT Scheduled S/D Due to S/D taken by BPDB
07:56 |  | Baghabari 230/132kV S/S T-2 Bank HT Scheduled S/D Due to S/D Taken by BPDB
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-27
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 421 | 9493200
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9929000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve NENP
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve NENP
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 715790
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve. NENP
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve NENP
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7410394
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 759600 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 385200
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 131 | 966720 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 802161
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 754704
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 863040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 506200 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 255200 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 960 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 258 | 3259309 | Engine problem
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 3028032 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 731040 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 86 | 1094400 | Engine problem
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1584000
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 164071
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 703800 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 16000
| Dhaka area Total |  |  |  | 6217 | 2446 | 43422821
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 48132 | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 60750
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 8160 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 217 | 5169655
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 215 | 5156686
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 34 | 490945 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 72 | 236671 | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 291983 | Fuel shortage
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 827520 | Engine problem
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 528000
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22797
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 918327 | Fuel shortage
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 21980 | Reserve
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 22 | 189020 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 884160 | Fuel shortage
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 199473 | Low demand
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 108 | 175636 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 0 | 10909 | Under maint.
| Cox's Bazar Wind |  | IPP | 66 | 60 | 10 | 249600
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 1151 | 27869090
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 2258 | 43359494
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 205 | 5031000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7365200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6348000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 230 | 5977000 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 36 | 866304 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 5 | 266880 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1176493
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 110 | 384727 | Low demand
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 246816 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 752990 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 1581600
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 56 | 1218240
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 42 | 450960 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 415500 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 443460 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 232680 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 1686720 | Engine problem
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 384309
| Cumilla Area Total |  |  |  | 2917 | 1693 | 34828879
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 10 | 270720 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11100
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 124 | 2481600 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1386000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 289780
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 192960 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 434880 | Engine problem
| Mymensingh Area Total |  |  |  | 646 | 240 | 5067040
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 911000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 120 | 3439964
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 55384 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 28 | 638112 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 10 | 261120 | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 134 | 3281410 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 273168 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7259000 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 8717000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 346 | 8189400 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1299 | 33025558
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 897 | 21764160
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve NENP
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 3 | 2400 | Low demand
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 78592 | Fuel shortage
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 245 | 6445440 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 283200 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 333360
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 600 | 13127270 | Unit-1 under maint
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1832 | 42034422
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 533472 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 10 | 190407
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 100 | 2213000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 28273200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5158080
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 159600 | Low demand
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6153000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 3469
| Barisal Area Total |  |  |  | 2236 | 2015 | 42684228
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 38 | 320275 | Engine problem
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 19 | 144932 | Engine problem
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 252136 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 171 | 4546082 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 309 | 8738327 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 227570 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 106992 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 501120 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 110 | 680640
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 583200 | Engine problem
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 27780
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 883 | 26791431
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 311250
| Rajshahi Area Total |  |  |  | 3449 | 1790 | 43231735
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1405090
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1390454 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34812
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 94 | 1277568 | Engine problem
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 207459
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1023000
| Rangpur Area Total |  |  |  | 950 | 254 | 5338383
| Total |  |  |  | 27068 | 13827 | 292992560
| Eastern Grid Total |  |  |  | 16579 | 7936 | 159703792
| Western Grid Total |  |  |  | 10489 | 5891 | 133288768
| National Grid Total |  |  |  | 27068 | 13827 | 292992560
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 2024-08-27 | [6 empty] | QF-LDC-09 (Page-3)
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8310.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4162 | MW
i) Dhaka area |  |  | 4784.48 |  | MW | i) Khulna area |  |  |  | 1569.4 | MW
ii) Chattogram area |  |  | 1066 |  | MW | ii) Barishal area |  |  |  | 336 | MW
iii) Cumilla area |  |  | 819 |  | MW | iii) Rajshahi area |  |  |  | 1384.6 | MW
iv) Mymensingh area |  |  | 1055 |  | MW | iv) Rangpur area |  |  |  | 872 | MW
v) Sylhet area |  |  | 586 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12472.48 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 108 | 19:00 | 133 | Rahim | 41 | 17:00
2 | AKSML | 102 | 02:00 | 68 | Jashore | 116 | 19:00 | 134 | Rajbari | 80 | 19:00
3 | Aftabnagar | 34 | 19:00 | 69 | Jhenaidah | 113 | 19:30 | 135 | Rajendrapur | 116 | 21:00
4 | Agargaon | 107 | 14:00 | 70 | Joydebpur | 207 | 19:00 | 136 | Rajshahi | 120 | 21:00
5 | Agrabad | 88 | 12:00 | 71 | Joypurhat | 70 | 00:00 | 137 | Rajshahi-230 | 59 | 21:00
6 | Amnura | 60 | 21:00 | 72 | Juldah | 15 | 16:00 | 138 | Ramganj | 112 | 21:00
7 | Ashuganj | 79 | 23:00 | 73 | KSRM | 30 | 13:00 | 139 | Rampur | 35 | 23:00
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 321 | 19:00 | 140 | Rangamati | 19 | 19:00
9 | BSRM | 139 | 23:00 | 75 | Kachua | 74 | 19:00 | 141 | Rangpur | 134 | 13:00
10 | Bagerhat | 77 | 19:00 | 76 | Kallyanpur | 111 | 19:00 | 142 | Ruppur | 6.8 | 10:00
11 | Bakulia | 89 | 19:30 | 77 | Kalurghat | 36 | 15:00 | 143 | SSM | 0 | 00:00
12 | Banani | 64 | 10:00 | 78 | Kamrangirchar | 53.2 | 13:00 | 144 | Saidpur | 118 | 19:00
13 | Bangabhaban | 21 | 12:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 110 | 19:00
14 | Barapukuria | 52 | 12:00 | 80 | Kazla | 111 | 13:00 | 146 | Satmasjid | 78 | 14:00
15 | Barguna | 20 | 22:00 | 81 | Keranigonj | 75 | 19:00 | 147 | Savar | 211 | 15:00
16 | Barishal | 103 | 19:00 | 82 | Khagrachori | 32 | 19:00 | 148 | SevenRings | 5.97 | 20:00
17 | Barishal-230 | 88 | 20:00 | 83 | Khulna | 61 | 19:00 | 149 | ShahCement | 19 | 00:00
18 | Baroaulia | 59 | 12:00 | 84 | Khulshi | 135 | 18:30 | 150 | Shahjadpur | 86 | 19:30
19 | Baroirhat | 39 | 19:00 | 85 | Kishoreganj | 164 | 19:30 | 151 | Shahjibazar | 123 | 20:00
20 | Bashundhara | 160 | 13:00 | 86 | Kodda | 244 | 05:00 | 152 | Shahmirpur | 53 | 00:00
21 | BashundharaCement | 1 | 11:00 | 87 | Kulaura | 54 | 19:00 | 153 | Shariatpur | 83 | 22:00
22 | Beanibazar | 80 | 19:00 | 88 | Kurigram | 66 | 18:30 | 154 | Sherpur | 124 | 18:30
23 | Benapole | 60 | 00:00 | 89 | Kushtia | 133 | 19:00 | 155 | Shikalbaha | 28 | 19:00
24 | Bhaluka | 130 | 17:00 | 90 | Lalbag | 77 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 49 | 21:00 | 91 | Lalmonirhat | 61 | 21:00 | 157 | Shitalakhya | 81.6 | 13:00
26 | Bhangura | 36 | 21:00 | 92 | MI_Cement | 12 | 12:00 | 158 | Sholosohor | 40 | 14:00
27 | Bheramara(GK) | 58 | 20:00 | 93 | Madanganj | 32 | 13:00 | 159 | Shyampur | 148 | 15:00
28 | Bhulta | 236 | 19:00 | 94 | Madaripur | 100 | 22:00 | 160 | Siddhirganj | 124 | 11:00
29 | Bog-Sherpur | 66 | 19:00 | 95 | Madartek | 76.7 | 00:00 | 161 | Sirajganj | 116 | 19:30
30 | Bogura | 163 | 20:00 | 96 | Madunaghat | 51 | 18:30 | 162 | Sonargaon | 86 | 12:00
31 | Borhanuddin | 79 | 22:00 | 97 | Magura | 62 | 19:00 | 163 | Sreemongol | 73 | 21:00
32 | Brahmanbaria | 155 | 18:30 | 98 | Mahasthangarh | 74 | 19:00 | 164 | Sreepur | 115 | 19:30
33 | Cantonment | 108 | 13:00 | 99 | Manikganj | 126 | 22:00 | 165 | Srinagar | 45 | 22:00
34 | Chandpur | 68 | 19:00 | 100 | Maniknagar | 64 | 15:00 | 166 | Sunamganj | 59 | 00:00
35 | Chandraghona | 33 | 19:00 | 101 | Matarbari | 43 | 21:00 | 167 | Sylhet | 46 | 18:30
36 | Chapai | 60 | 00:00 | 102 | Matuail | 58 | 10:00 | 168 | Sylhet-132 | 125 | 18:30
37 | Charsaidpur | 27 | 23:00 | 103 | Millgate | 115 | 14:00 | 169 | TK | 30 | 21:00
38 | Chauddagram | 59 | 19:30 | 104 | Mirpur | 133.5 | 13:00 | 170 | Tangail | 174 | 22:00
39 | Chhatak | 38 | 20:00 | 105 | Mirsorai | 6 | 10:00 | 171 | Thakurgaon | 112 | 19:00
40 | Chowmuhani | 163 | 21:00 | 106 | Mirzapur | 52 | 19:30 | 172 | Tongi | 144 | 18:30
41 | Chuadanga | 108 | 19:00 | 107 | Mithapukur | 68 | 19:00 | 173 | Ullahpara | 27 | 19:00
42 | Coxsbazar | 118 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 52 | 21:00
43 | Cumilla(N) | 160 | 22:00 | 109 | Mogbazar | 118.4 | 15:00 | 175 | Uttara | 67 | 17:00
44 | Cumilla(S) | 131 | 19:00 | 110 | Mongla | 30 | 15:00 | 176 | UttaraNew | 52 | 19:00
45 | Daudkandi | 154 | 22:00 | 111 | Motijheel | 37 | 13:00 | 177 | Zigatola | 93 | 13:00
46 | Dhaka | 52 | 13:00 | 112 | Munshiganj | 103 | 21:00
47 | Dhamrai | 130 | 19:00 | 113 | Mymensingh | 232 | 00:00
48 | Dhanmondi | 117 | 13:00 | 114 | Naogaon | 123 | 21:00
49 | Dohazari | 90 | 19:30 | 115 | Narail | 54 | 19:00
50 | Faridpur | 160 | 19:00 | 116 | Narinda | 72.5 | 13:00
51 | Fatullah | 85 | 13:00 | 117 | Narshingdi | 158 | 06:00
52 | Fenchuganj | 35 | 00:00 | 118 | Natore | 145 | 21:00
53 | Feni | 68 | 23:00 | 119 | Nawabganj | 46.2 | 21:00
54 | GPH | 9 | 11:00 | 120 | Netrakona | 111 | 19:30
55 | Ghatail | 52 | 13:00 | 121 | New | 39 | 10:00
56 | Ghorashal | 60 | 19:30 | 122 | Niamatpur | 72 | 22:00
57 | Goalpara | 36 | 13:00 | 123 | Noapara | 52 | 19:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 384 | 06:00 | 368 | 11:00 | Kaliakoir | 368 | 18:30 | 359 | 15:00
| Ashuganj | 405 | 6:00 | 386 | 11:00 | Madunaghat | 394 | 19:00 | 380 | 16:00
| Bhulta | 393 | 06:00 | 373 | 11:00 | Meghnaghat | 378 | 06:00 | 364 | 15:00
| Bibiana | 393 | 06:00 | 385 | 11:00 | Payra | 409 | 06:00 | 401 | 20:00
| BIPTC | 408 | 05:00 | 392 | 19:30 | Rahanpur | 404 | 18:30 | 384 | 13:00
| Bogura | 392 | 18:30 | 366 | 23:00 | Rampal | 399 | 06:00 | 385 | 23:00
| Gopalganj | 396 | 06:00 | 383 | 15:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 06:00 | 215 | 11:00 | Haripur | 228 | 00:00 | 219 | 12:00
| AKSML | 235 | 19:00 | 222 | 13:00 | Hasnabad | 228 | 03:00 | 216 | 11:00
| Aminbazar | 228 | 02:00 | 218 | 11:00 | Hathazari | 235 | 19:00 | 224 | 11:00
| Ashuganj | 232 | 07:00 | 224 | 11:00 | Ishurdi | 232 | 18:00 | 224 | 12:00
| Ashuganj-400 | 232 | 7:00 | 224 | 11:00 | Jhenaidah | 226 | 18:00 | 216 | 22:00
| Baghabari | 231 | 17:00 | 221 | 12:00 | Kaliakoir | 230 | 19:30 | 222 | 15:00
| Barapukuria | 211 | 18:30 | 194 | 05:00 | Keranigonj | 227 | 06:00 | 215 | 11:00
| Barapukuria-230 | 211 | 18:30 | 194 | 5:00 | Khulna(S) | 228 | 06:00 | 218 | 22:00
| Barishal | 236 | 06:00 | 230 | 22:00 | Madunaghat | 234 | 19:30 | 225 | 13:00
| Bheramara | 230 | 18:00 | 223 | 00:00 | Maniknagar | 228 | 00:00 | 217 | 11:00
| Bhulta | 230 | 06:00 | 219 | 11:00 | Meghnaghat | 236 | 17:00 | 230 | 22:00
| Bibiana | 224 | 06:00 | 218 | 11:00 | Meghnaghat-400 | 232 | 06:00 | 222 | 11:00
| BIPTC | 233 | 18:00 | 222 | 13:00 | Mirsorai | 230 | 00:00 | 26 | 04:00
| Bogura | 224 | 18:00 | 211 | 14:00 | Rajshahi | 231 | 18:00 | 221 | 12:00
| Bogura-400 | 224 | 18:00 | 211 | 23:00 | Rampal | 227 | 06:00 | 218 | 23:00
| Borhanuddin | 241 | 06:00 | 237 | 11:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 232 | 19:00 | 221 | 12:00 | Rampura | 230 | 06:00 | 217 | 11:00
| Cumilla(N) | 226 | 00:00 | 217 | 11:00 | Shikalbaha | 234 | 19:30 | 223 | 12:00
| Faridpur | 234 | 06:00 | 225 | 23:00 | Shyampur | 228 | 06:00 | 217 | 11:00
| Fenchuganj | 226 | 08:00 | 220 | 15:00 | Siddhirganj | 230 | 01:00 | 220 | 11:00
| Ghorashal | 235 | 01:00 | 230 | 07:00 | Sirajgonj | 234 | 18:00 | 227 | 14:00
| Ghorashal-230 | 228 | 05:00 | 217 | 11:00 | Sreepur | 226 | 18:00 | 219 | 11:00
| Gopalganj | 234 | 06:00 | 227 | 11:00 | Tongi | 228 | 19:30 | 216 | 11:00
| GPH | 232 | 21:00 | 23 | 21:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 134 | 06:00 | 124 | 12:00 | Kushtia | 133 | 03:00 | 127 | 22:00
| Agargaon | 133 | 06:00 | 125 | 11:00 | Lalbag | 132 | 06:00 | 124 | 11:00
| Agrabad | 135 | 19:00 | 126 | 15:00 | Lalmonirhat | 126 | 18:30 | 110 | 23:00
| AKS | 132 | 00:00 | 126 | 12:00 | Madanganj | 133 | 04:00 | 122 | 11:00
| Aminbazar | 138 | 02:00 | 124 | 11:00 | Madaripur | 131 | 05:00 | 127 | 14:00
| Amnura | 136 | 18:30 | 122 | 23:00 | Madartek | 134 | 06:00 | 124 | 15:00
| Ashuganj | 136 | 06:00 | 133 | 11:00 | Madunaghat | 135 | 00:00 | 128 | 11:00
| Bagerhat | 131 | 18:00 | 122 | 15:00 | Magura | 132 | 18:00 | 125 | 19:30
| Bakulia | 135 | 19:30 | 127 | 15:00 | Mahasthangarh | 131 | 18:00 | 120 | 00:00
| Banani | 134 | 06:00 | 123 | 14:00 | Manikganj | 129 | 00:00 | 118 | 15:00
| Bangabhaban | 130 | 05:00 | 121 | 12:00 | Maniknagar | 130 | 03:00 | 121 | 12:00
| Barapukuria | 130 | 18:30 | 118 | 04:00 | Matarbari | 125 | 07:00 | 117 | 18:30
| Barguna | 135 | 18:00 | 131 | 00:00 | Matuail | 130.6 | 00:00 | 123 | 11:00
| Barishal | 133 | 06:00 | 129 | 11:00 | Millgate | 132 | 00:00 | 123 | 11:00
| Barishal-230 | 134 | 18:00 | 129 | 12:00 | Mirpur | 136 | 00:00 | 126 | 11:00
| Baroaulia | 135 | 00:00 | 128 | 14:00 | Mirzapur | 127 | 00:00 | 118 | 23:00
| Baroirhat | 127 | 00:00 | 120 | 15:00 | Mithapukur | 128 | 18:00 | 116 | 04:00
| Bashundhara | 133 | 00:00 | 123 | 11:00 | MI_Cement | 131 | 00:00 | 123 | 11:00
| BashundharaCement | 133 | 04:00 | 122 | 11:00 | Modern | 134 | 00:00 | 127 | 11:00
| Beanibazar | 121 | 07:00 | 114 | 23:00 | Mogbazar | 136 | 03:00 | 123 | 17:00
| Benapole | 129 | 06:00 | 120 | 22:00 | Mongla | 130 | 05:00 | 122 | 23:00
| Bhaluka | 124 | 05:00 | 117 | 23:00 | Motijheel | 130 | 05:00 | 121 | 12:00
| Bhandaria | 129 | 09:00 | 125 | 00:00 | Munshiganj | 131 | 00:00 | 122 | 11:00
| Bhangura | 135 | 17:00 | 126 | 15:00 | Mymensingh | 128 | 00:00 | 113 | 23:00
| Bheramara | 134 | 06:00 | 129 | 23:00 | Naogaon | 130 | 18:00 | 117 | 23:00
| Bheramara(GK) | 134 | 06:00 | 130 | 22:00 | Narail | 132 | 09:00 | 125 | 00:00
| Bhulta | 122 | 03:00 | 114 | 11:00 | Narinda | 127 | 2:00 | 121 | 12:00
| Bog-Sherpur | 130 | 18:00 | 120 | 00:00 | Narshingdi | 123 | 03:00 | 113 | 11:00
| Bogura | 133 | 18:30 | 124 | 01:00 | Natore | 133 | 18:00 | 125 | 23:00
| Bogura-230 | 134 | 18:00 | 124 | 00:00 | Nawabganj | 133 | 06:00 | 124 | 11:00
| Brahmanbaria | 127 | 05:00 | 121 | 23:00 | Netrakona | 128 | 19:00 | 118 | 08:00
| Cantonment | 133 | 00:00 | 124 | 11:00 | New | 133 | 00:00 | 123 | 15:00
| Chandpur | 131 | 20:00 | 123 | 15:00 | Niamatpur | 135 | 18:00 | 126 | 23:00
| Chandraghona | 136 | 19:00 | 130 | 11:00 | Noapara | 132 | 18:00 | 124 | 22:00
| Chapai | 133 | 18:00 | 124 | 23:00 | Pabna | 134 | 18:00 | 127 | 13:00
| Charsaidpur | 131 | 00:00 | 124 | 11:00 | Palashbari | 126 | 18:00 | 113 | 23:00
| Chauddagram | 127 | 00:00 | 121 | 15:00 | Panchagarh | 133 | 18:00 | 108 | 05:00
| Chhatak | 122 | 06:00 | 116 | 18:30 | Patuakhali | 135 | 18:00 | 130 | 00:00
| Chowmuhani | 124 | 10:00 | 114 | 23:00 | Payra | 136 | 06:00 | 133 | 15:00
| Chuadanga | 129 | 09:00 | 116 | 22:00 | PHP | 126 | 00:00 | 120 | 15:00
| Coxsbazar | 126 | 07:00 | 118 | 12:00 | Postogola | 134 | 00:00 | 126 | 11:00
| Cumilla(N) | 130 | 00:00 | 125 | 15:00 | Purbachal | 134 | 00:00 | 122 | 12:00
| Cumilla(S) | 132 | 06:00 | 124 | 15:00 | Purbasadipur | 126 | 18:00 | 107 | 05:00
| Daudkandi | 127 | 18:00 | 120 | 11:00 | Rahanpur | 137 | 18:30 | 130 | 03:00
| Dhaka | 134 | 05:00 | 124 | 11:00 | Rahim | 130 | 00:00 | 124 | 12:00
| Dhamrai | 131 | 00:00 | 123 | 11:00 | Rajbari | 131 | 06:00 | 126 | 20:00
| Dhanmondi | 135 | 03:00 | 124 | 15:00 | Rajendrapur | 127 | 00:00 | 118 | 15:00
| Dohazari | 131 | 20:00 | 123 | 15:00 | Rajshahi | 133 | 18:00 | 127 | 00:00
| Faridpur | 132 | 06:00 | 127 | 12:00 | Rajshahi-230 | 133 | 18:00 | 119 | 23:00
| Fatullah | 132 | 00:00 | 124 | 11:00 | Ramganj | 126 | 10:00 | 117 | 23:00
| Fenchuganj | 129 | 06:00 | 126 | 15:00 | Rampur | 134 | 18:30 | 126 | 14:00
| Feni | 125 | 00:00 | 121 | 15:00 | Rampura | 134 | 06:00 | 124 | 14:00
| Ghatail | 126 | 00:00 | 116 | 05:00 | Rangamati | 134 | 00:00 | 128 | 15:00
| Ghorashal | 137 | 01:00 | 130 | 15:00 | Rangpur | 126 | 18:00 | 114 | 02:00
| Goalpara | 134 | 06:00 | 126 | 23:00 | Ruppur | 135 | 18:00 | 130 | 13:00
| Gollamari | 134 | 06:00 | 127 | 22:00 | Saidpur | 129 | 18:00 | 110 | 05:00
| Gopalganj | 131 | 06:00 | 125 | 23:00 | Satkhira | 131 | 06:00 | 121 | 22:00
| Gopalganj-400 | 132 | 06:00 | 127 | 23:00 | Satmasjid | 133 | 06:00 | 124 | 11:00
| Gulshan | 134 | 06:00 | 123 | 15:00 | Savar | 137 | 00:00 | 123 | 11:00
| Halishahar | 135 | 19:00 | 127 | 11:00 | SevenRings | 136 | 07:00 | 129 | 11:00
| Haripur | 130 | 00:00 | 124 | 12:00 | ShahCement | 131 | 00:00 | 124 | 11:00
| HaripurSBU | 130 | 00:00 | 124 | 12:00 | Shahjadpur | 133 | 03:00 | 132 | 00:00
| Hasnabad | 133 | 00:00 | 127 | 11:00 | Shahjibazar | 126 | 07:00 | 120 | 23:00
| Hathazari | 137 | 19:00 | 130 | 12:00 | Shahmirpur | 135 | 00:00 | 128 | 10:00
| Ishurdi | 135 | 06:00 | 131 | 11:00 | Shariatpur | 131 | 07:00 | 124 | 23:00
| Jaldhaka | 125 | 18:00 | 109 | 05:00 | Sherpur | 131 | 00:00 | 116 | 05:00
| Jamalpur | 132 | 19:00 | 120 | 03:00 | Shikalbaha | 124 | 00:00 | 116 | 14:00
| Jashore | 130 | 07:00 | 122 | 19:00 | Shikalbaha-230 | 136 | 19:30 | 128 | 12:00
| Jhenaidah | 133 | 05:00 | 126 | 22:00 | Shitalakhya | 131.2 | 06:00 | 123 | 11:00
| Jhenaidah-230 | 134 | 06:00 | 127 | 00:00 | Sholosohor | 134 | 19:00 | 127 | 15:00
| Joydebpur | 131 | 00:00 | 123 | 14:00 | Shyampur | 131 | 21:00 | 124 | 11:00
| Joypurhat | 128 | 18:00 | 114 | 23:00 | Shyampur-230 | 131 | 00:00 | 124 | 11:00
| Juldah | 136 | 19:00 | 127 | 15:00 | Siddhirganj | 131 | 00:00 | 125 | 10:00
| Kabirpur | 129 | 05:00 | 118 | 15:00 | Sirajganj | 125 | 18:00 | 115 | 23:00
| Kachua | 129 | 19:00 | 120 | 08:00 | Sonargaon | 131 | 00:00 | 121 | 11:00
| Kaliakoir | 132 | 18:00 | 123 | 15:00 | Sreemongol | 125 | 06:00 | 120 | 23:00
| Kallyanpur | 130 | 01:00 | 124 | 11:00 | Sreepur | 126 | 04:00 | 121 | 15:00
| Kalurghat | 135 | 19:00 | 128 | 11:00 | Srinagar | 132 | 00:00 | 126 | 11:00
| Kamrangirchar | 132 | 00:00 | 123 | 11:00 | SSM | 138 | 00:00 | 131 | 14:00
| Kaptai | 137 | 9:00 | 133 | 13:00 | Sunamganj | 120 | 06:00 | 114 | 00:00
| Kazla | 130 | 06:00 | 121 | 12:00 | Sylhet | 124 | 06:00 | 118 | 23:00
| Keranigonj | 133 | 06:00 | 125 | 11:00 | Sylhet-132 | 124 | 01:00 | 120 | 23:00
| Khagrachori | 133 | 00:00 | 127 | 15:00 | Tangail | 127 | 00:00 | 115 | 23:00
| Khulna | 133 | 08:00 | 126 | 19:00 | Thakurgaon | 131 | 18:00 | 104 | 05:00
| Khulna(S) | 134 | 06:00 | 127 | 22:00 | TK | 135 | 19:00 | 128 | 11:00
| Khulshi | 134 | 19:30 | 126 | 11:00 | Tongi | 133 | 00:00 | 126 | 15:00
| Kishoreganj | 128 | 18:00 | 120 | 11:00 | Ullahpara | 136 | 17:00 | 130 | 12:00
| Kodda | 132 | 06:00 | 118 | 14:00 | Ullon | 136 | 04:00 | 123 | 14:00
| KSRM | 135 | 04:00 | 128 | 12:00 | Uttara | 136 | 00:00 | 125 | 11:00
| Kulaura | 128 | 07:00 | 124 | 15:00 | UttaraNew | 136 | 00:00 | 126 | 11:00
| Kurigram | 126 | 18:00 | 112 | 01:00 | Zigatola | 132 | 00:00 | 125 | 12:00

## L-Curve
Date | 2024-08-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1076 | 7147 | 6205 | 13352 |  |  |  | QF-LDC-11
0:30 | 788 | 6823 | 5761.5 | 12584.5 | Date: | 2024-08-27
1:00 | 500 | 6499 | 5318 | 11817
1:30 | 592 | 6332 | 5308 | 11640
2:00 | 684 | 6165 | 5298 | 11463
2:30 | 667 | 6123.5 | 5244.5 | 11368 | [5 empty] | Gen. at Eve. Peak | 13827 | 13827 MW (19:30 )
3:00 | 650 | 6082 | 5191 | 11273 | [6 empty] | 19:30
3:30 | 722 | 6074 | 5143.5 | 11217.5 | [5 empty] | Gen. at Day Peak | 11888 | 11888 MW (12:00 )
4:00 | 794 | 6066 | 5096 | 11162 | [6 empty] | 12:00
4:30 | 814 | 5982 | 5075 | 11057 | [5 empty] | Highest Generation | 13827
5:00 | 834 | 5898 | 5054 | 10952 | [6 empty] | 19:30
5:30 | 850 | 5760 | 4930 | 10690
6:00 | 866 | 5622 | 4806 | 10428
6:30 | 798 | 5660 | 4779.5 | 10439.5
7:00 | 730 | 5698 | 4753 | 10451
7:30 | 871 | 5687.5 | 4857 | 10544.5
8:00 | 1012 | 5677 | 4961 | 10638
8:30 | 1077 | 5828.5 | 5050 | 10878.5
9:00 | 1142 | 5980 | 5139 | 11119
9:30 | 1179 | 6018.5 | 5141 | 11159.5
10:00 | 1216 | 6057 | 5143 | 11200
10:30 | 1252 | 6074.5 | 5281 | 11355.5
11:00 | 1288 | 6092 | 5419 | 11511
11:30 | 1220 | 6241 | 5458.5 | 11699.5
12:00 | 1152 | 6390 | 5498 | 11888
12:30 | 1108 | 6492.5 | 5550 | 12042.5
13:00 | 1064 | 6595 | 5602 | 12197
13:30 | 1178 | 6600.5 | 5629.5 | 12230
14:00 | 1292 | 6606 | 5657 | 12263
14:30 | 1213 | 6705.5 | 5635.5 | 12341
15:00 | 1134 | 6805 | 5614 | 12419
15:30 | 1062 | 6833 | 5525.5 | 12358.5
16:00 | 990 | 6861 | 5437 | 12298
16:30 | 1107 | 6886.5 | 5332 | 12218.5
17:00 | 1224 | 6912 | 5227 | 12139
17:30 | 985 | 6791.5 | 5085.5 | 11877
18:00 | 746 | 6671 | 4944 | 11615
18:30 | 605 | 7266.5 | 5318 | 12584.5
19:00 | 464 | 7862 | 5692 | 13554
19:30 | 394 | 7936 | 5891 | 13827
20:00 | 452 | 7645 | 5913 | 13558 |  |  |  | Executive Engineer
20:30 | 534 | 7654 | 5970.5 | 13624.5 |  |  |  | Network Operation Division
21:00 | 616 | 7663 | 6028 | 13691
21:30 | 727 | 7440.5 | 6083.5 | 13524
22:00 | 838 | 7218 | 6139 | 13357 |  |  |  |  | Page 6 of 7
22:30 | 892 | 7199.5 | 6155.5 | 13355
23:00 | 946 | 7181 | 6172 | 13353
23:30 | 1011 | 7164 | 6188.5 | 13352.5
24:00 | 1076 | 7147 | 6205 | 13352
13827 MW (19:30 )
11888 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-27 |  | Energy |  | 292992560
[15 empty] | 2024-08-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3470 | 898 | 1614 | 0 | 1968 | 4811 | 217 | 0 | 269 | 60 | 0 | 7 | 380.09
0:30 | 3505 | 897.5 | 1584.5 | 0 | 1563 | 4567 | 217.5 | 0 | 164.5 | 55 | 0 | 11.5 | 387.2525 |  |  | Date: | 44069
1:00 | 3540 | 897 | 1555 | 0 | 1158 | 4323 | 218 | 0 | 60 | 50 | 0 | 16 | 394.415
1:30 | 3546.5 | 897.5 | 1540.5 | 0 | 970 | 4363.5 | 218 | 0 | 38 | 50 | 0 | 16 | 391.55 | [9 empty] | Total Energy | 292.9926 | 292.9926 | Total Energy Gen 292.993 MKWHr Energy Not Served 5.882 MKWHr Energy Requirement 298.875 MKWHr
2:00 | 3553 | 898 | 1526 | 0 | 782 | 4404 | 218 | 0 | 16 | 50 | 0 | 16 | 388.685 | [9 empty] | Energy not Served | 5.8821 | 5.8821
2:30 | 3561 | 898 | 1543 | 0 | 732 | 4335.5 | 218 | 0 | 16 | 50 | 0 | 14.5 | 374.36 | [9 empty] | Energy Requirement | 298.8747 | 298.8747
3:00 | 3569 | 898 | 1560 | 0 | 682 | 4267 | 218 | 0 | 16 | 50 | 0 | 13 | 360.035
3:30 | 3586.5 | 898 | 1557.5 | 0 | 654.5 | 4225.5 | 218.5 | 0 | 16 | 49 | 0 | 12 | 341.4125 | [8 empty] | Shortage
4:00 | 3604 | 898 | 1555 | 0 | 627 | 4184 | 219 | 0 | 16 | 48 | 0 | 11 | 322.79
4:30 | 3585.5 | 898 | 1503 | 0 | 590 | 4183.5 | 219 | 0 | 16 | 49 | 0 | 13 | 303.69
5:00 | 3567 | 898 | 1451 | 0 | 553 | 4183 | 219 | 0 | 16 | 50 | 0 | 15 | 284.59
5:30 | 3474 | 898 | 1411.5 | 0 | 521.5 | 4080.5 | 218.5 | 0 | 16 | 50 | 5 | 15 | 272.175
6:00 | 3381 | 898 | 1372 | 0 | 490 | 3978 | 218 | 0 | 16 | 50 | 10 | 15 | 259.76
6:30 | 3421.5 | 897.5 | 1378.5 | 0 | 479.5 | 3938 | 217.5 | 0 | 8 | 50 | 31 | 18 | 239.2275 | [7 empty] | Coal
7:00 | 3462 | 897 | 1385 | 0 | 469 | 3898 | 217 | 0 | 0 | 50 | 52 | 21 | 218.695
7:30 | 3410.5 | 897.5 | 1392.5 | 0 | 509.5 | 3926.5 | 217 | 0 | 8 | 48 | 122 | 13 | 186.7025 | [6 empty] | Oil
8:00 | 3359 | 898 | 1400 | 0 | 550 | 3955 | 217 | 0 | 16 | 46 | 192 | 5 | 154.71
8:30 | 3432 | 898 | 1512.5 | 0 | 568 | 3971 | 217 | 0 | 16 | 45 | 213 | 6 | 106.4825
9:00 | 3505 | 898 | 1625 | 0 | 586 | 3987 | 217 | 0 | 16 | 44 | 234 | 7 | 58.255
9:30 | 3546.5 | 898 | 1621.5 | 0 | 605 | 3962.5 | 217 | 0 | 16 | 51 | 234.5 | 7.5 | 53.1275
10:00 | 3588 | 898 | 1618 | 0 | 624 | 3938 | 217 | 0 | 16 | 58 | 235 | 8 | 48
10:30 | 3621.5 | 898 | 1624.5 | 0 | 632 | 4057 | 217 | 0 | 16 | 53 | 229.5 | 7 | 59.335
11:00 | 3655 | 898 | 1631 | 0 | 640 | 4176 | 217 | 0 | 16 | 48 | 224 | 6 | 70.67
11:30 | 3640 | 898 | 1574.5 | 0 | 776.5 | 4261 | 217 | 0 | 16 | 41 | 265.5 | 10 | 74.49
12:00 | 3625 | 898 | 1518 | 0 | 913 | 4346 | 217 | 0 | 16 | 34 | 307 | 14 | 78.31
12:30 | 3538 | 897.5 | 1498.5 | 0 | 1076 | 4422.5 | 217 | 0 | 16 | 38 | 322.5 | 16.5 | 104.655
13:00 | 3451 | 897 | 1479 | 0 | 1239 | 4499 | 217 | 0 | 16 | 42 | 338 | 19 | 131
13:30 | 3451 | 897 | 1479 | 0 | 1239 | 4499 | 217 | 0 | 16 | 42 | 338 | 19 | 131
14:00 | 3451 | 897 | 1479 | 0 | 1239 | 4499 | 217 | 0 | 16 | 42 | 338 | 19 | 131
14:30 | 3492.5 | 897.5 | 1504.5 | 0 | 1304.5 | 4472 | 172.5 | 0 | 45 | 51 | 351.5 | 17 | 176
15:00 | 3534 | 898 | 1530 | 0 | 1370 | 4445 | 128 | 0 | 74 | 60 | 365 | 15 | 221
15:30 | 3487.5 | 897.5 | 1525 | 0 | 1471 | 4337 | 172.5 | 0 | 98 | 59 | 301 | 10 | 211.5
16:00 | 3441 | 897 | 1520 | 0 | 1572 | 4229 | 217 | 0 | 122 | 58 | 237 | 5 | 202
16:30 | 3478 | 897.5 | 1563.5 | 0 | 1603.5 | 4100 | 217 | 0 | 137 | 56 | 161.5 | 4.5 | 202
17:00 | 3515 | 898 | 1607 | 0 | 1635 | 3971 | 217 | 0 | 152 | 54 | 86 | 4 | 202
17:30 | 3471 | 898 | 1476 | 0 | 1682.5 | 3851 | 217 | 0 | 180.5 | 52 | 47 | 2 | 189.5
18:00 | 3427 | 898 | 1345 | 0 | 1730 | 3731 | 217 | 0 | 209 | 50 | 8 | 0 | 177
18:30 | 3471 | 898 | 1495 | 0 | 2088.5 | 3915.5 | 217 | 0 | 438.5 | 55 | 4 | 2 | 253.5
19:00 | 3515 | 898 | 1645 | 0 | 2447 | 4100 | 217 | 0 | 668 | 60 | 0 | 4 | 330
19:30 | 3546 | 897 | 1461 | 0 | 2691 | 4246 | 217 | 0 | 703 | 56 | 0 | 10 | 328.305
20:00 | 3558 | 898 | 1497 | 0 | 2504 | 4255 | 217 | 0 | 562 | 60 | 0 | 7 | 326.61
20:30 | 3556 | 898 | 1545 | 0 | 2461 | 4321.5 | 216.5 | 0 | 561.5 | 60 | 0 | 5 | 358.6025
21:00 | 3554 | 898 | 1593 | 0 | 2418 | 4388 | 216 | 0 | 561 | 60 | 0 | 3 | 390.595
21:30 | 3515.5 | 898 | 1595 | 0 | 2280 | 4460 | 216 | 0 | 492 | 61 | 0 | 6.5 | 397.28
22:00 | 3477 | 898 | 1597 | 0 | 2142 | 4532 | 216 | 0 | 423 | 62 | 0 | 10 | 403.965
22:30 | 3533.5 | 898 | 1601 | 0 | 2072 | 4600.5 | 216.5 | 0 | 348 | 62 | 0 | 11 | 403.4875
23:00 | 3590 | 898 | 1605 | 0 | 2002 | 4669 | 217 | 0 | 273 | 62 | 0 | 12 | 403.01
23:30 | 3530 | 898 | 1609.5 | 0 | 1985 | 4740 | 217 | 0 | 271 | 61 | 0 | 9.5 | 391.55 |  |  | Max Temp. in Dhaka |  | 33.0°C
24:00 | 3470 | 898 | 1614 | 0 | 1968 | 4811 | 217 | 0 | 269 | 60 | 0 | 7 | 380.09
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 292.993 MKWHr Energy Not Served 5.882 MKWHr Energy Requirement 298.875 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 138 | 138 | 138 | 139 | 139 | 138 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 48 | 137 | 137 | 137 |  | 137 | 137 | 137 | 136 | 136 | 137 | 137 | 3249655
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1920000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 48132
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 5 |  |  | 5 | 7 | 1 | 19 | 8 | 6 | 3 | 0 | [8 empty] | 60750
6 | Sikalbaha 225MW CCPP (Gas) | 221 | 220 | 220 | 220 | 220 | 221 | 221 | 221 | 217 | 216 | 216 | 216 | 216 | 216 | 216 | 215 | 216 | 215 |  | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 5156686
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 85 | 84 | 84 | 84 | 34 | 0 | 0 | 291983
12 | Hathazari 100 MW peaking PP | [19 empty] | 72 | 72 | 72 | 72 | 32 | 0 |  | 236671
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 490945
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [14 empty] | 37 | 37 | 36 | 36 |  | 36 | 36 | 36 | 36 |  |  | 0 | 246816
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 335 | 280 | 260 | 260 | 260 | 335 | 335 | 335 | 280 | 280 | 280 | 330 | 330 | 332 | 280 |  | 335 | 335 | 335 | 335 | 280 | 280 | 280 | 7410394
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 45 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 45 | 188 | 225 | 229 | 241 | 243 | 251 |  | 257 | 258 | 264 | 278 | 195 | 195 | 195 | 3259309
19 | Ashuganj 195 MW PP (APSCL-United) | [25 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | [25 empty] | 96 | 10909
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 35 | 33 | 32 | 35 | 35 | 35 | 36 | 36 |  | 36 | 36 | 37 | 35 | 38 | 38 | 38 | 866304
33 | Ashuganj 225 MW CCPP | 214 | 215 | 215 | 215 | 214 | 215 | 198 | 202 | 205 | 212 | 212 | 210 | 212 | 205 | 185 | 189 | 201 | 208 |  | 200 | 205 | 211 | 207 | 210 | 206 | 206 | 5031000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 340 | 250 | 250 | 250 | 265 | 300 | 275 | 275 | 295 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6348000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 300 | 310 | 280 | 285 | 310 | 280 | 285 | 305 |  | 280 | 280 | 285 | 285 | 280 | 325 | 280 | 7365200
| Ashuganj 420 MW CCPP(East) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 230 | 230 | 230 | 230 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 5977000
35 | Ashuganj 55 MW PP (Precision) | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 266880
36 | Chandpur 150 MW CCPP | 25 | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 31 | 31 | 31 | 30 | 30 | 31 | 30 |  | 30 | 30 | 30 | 30 | 35 | 35 | 35 | 752990
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 405 | 405 | 405 | 405 | 382 | 331 | 353 | 401 | 410 | 408 | 408 | 409 | 388 | 381 | 403 | 403 | 320 |  | 411 | 421 | 414 | 409 | 380 | 380 | 380 | 9493200
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 380 | 320 | 320 | 360 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 320 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9929000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 18 | 17 | 17 | 18 | 18 | 18 | 18 | 11 | 11 | 7 | 6 | 6 | 6 | 5 | 6 | 8 | 10 | 9 |  | 10 | 10 | 11 | 16 | 16 | 17 | 17 | 270720
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 7 | 20 | 26 | 35 | 19 | 26 | 50 | 31 | 42 | 30 | 2 | 1 | [8 empty] | 289780
44 | Fenchugonj CCPP Phase-1 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 38 | 38 | 39 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 911000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 25 | 25 | 25 | 25 | 28 | 30 |  | 30 | 28 | 28 | 26 | 26 | 26 | 20 | 638112
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 261120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 136 | 136 | 134 | 134 | 134 | 134 |  | 135 | 134 | 134 | 135 | 135 | 136 | 137 | 3281410
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 55384
55 | Fenchugonj 51 MW PP (Barakatullah) | [25 empty] | 0 | 0
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 11 | 11 | 11 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 273168
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 295 | 290 | 295 | 290 | 300 | 300 | 305 | 295 | 310 | 300 | 285 | 280 | 310 | 305 | 300 | 290 |  | 320 | 260 | 270 | 300 | 280 | 285 | 310 | 7259000
| Bibiyana South 400 MW | 350 | 346 | 350 | 370 | 362 | 315 | 330 | 320 | 345 | 352 | 352 | 368 | 315 | 315 | 340 | 316 | 316 | 336 |  | 346 | 346 | 346 | 346 | 346 | 375 | 346 | 8189400
58 | Nababganj 55 MW PP (Southern power ) | 17 | [9 empty] | 10 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 754704
59 | Tangail Palli Power Gen 22 MW | 2 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 192960
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 50 | 50 | 50 | 48 | 50 | 50 | 50 | 46 | 44 | 58 | 48 | 34 | 42 | 38 | 60 | 58 | 54 | 50 |  | 60 | 56 | 60 | 60 | 62 | 62 | 60 | 1218240
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 41 | 41 | 31 | 8 | 3 | 2 | 2 | 2 | 6 | 5 | 2 | 2 | 10 | 14 |  | 23 | 26 | 23 | 31 | 34 | 37 | 39 | 528000
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 15 | 15 | 15 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 415500
69 | Summit Ashulia | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 19 | 18 | 18 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 447600
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  |  |  | 7 | 7 | 7 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 415440
71 | Maona 33 MW PP(Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 506200
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 255200
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 34 | 34 | [10 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 443460
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 232680
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | [7 empty] | 87 | 108 | 108 | 140 | 162 | 162 | 162 |  | 162 | 162 | 162 | 108 | 35 | 35 | 35 | 1584000
77 | Siddhirganj 100 PP(Dutch Bangla) | [25 empty] | 0 | 0
78 | Gazipur 52 MW PP | [25 empty] | 0 | 960
79 | Kodda 150 MW PP | 32 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 132 | 131 | 132 | 132 | 131 | 64 | 64 | 966720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | [10 empty] | 7 | 20 | 32 | 33 | 33 | 33 | 33 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 450960
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 1 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 731040
| Kaptai 7 MW Solar PP | [7 empty] | 2 | 3 | 3 | 2 | 5 | 5 | 3 | 1 | 1 | 0 | [9 empty] | 22797
| Jodiac Power | [19 empty] | 14 | [5 empty] | 0 | 21980
| Karnaphuli Power Ltd. | 17 | [15 empty] | 9 | 17 |  | 22 | 22 | 17 | 17 | 17 | 17 | 17 | 189020
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 52 | 34 | 17 | 17 | [6 empty] | 1 | 27 | 48 | 50 | 51 | 84 | 85 | 85 |  | 86 | 86 | 85 | 85 | 85 | 85 | 85 | 1094400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1176493
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | [6 empty] | 3 | 16 | 32 | 32 | 32 | 64 | 64 | 64 |  | 74 | 90 | 90 | 90 | 50 | 42 | 41 | 759600
95 | Patenga 50MW PP (Baraka) | [19 empty] | 3 | 6 |  |  |  |  | 0 | 8160
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | [7 empty] | 18 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 715790
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | [7 empty] | 29 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 802161
101 | Kushiara 163 MW CCPP (KP) | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 163 | 120 |  | 163 | 120 | 120 | 163 | 163 | 163 | 163 | 3439964
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 1 | 1 | 0 | 1 | 0 | 0 | [8 empty] | 11100
103 | Kamalaghat 54 MW PP(Banco Energy) | [11 empty] | 2 | 32 | 35 | 35 | 35 | 35 | 35 |  | 39 | 54 | 17 | 17 | 17 | 17 | 17 | 385200
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 93 | 102 | 102 | 102 | 102 | 105 | 96 | 98 | 97 | 97 | 97 | 95 | 95 | 95 | 94 | 95 | 95 | 95 |  | 124 | 124 | 125 | 125 | 125 | 125 | 125 | 2481600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 119 | 132 | 132 | 132 | 101 | 112 | 118 | 133 | 132 | 132 | 132 | 116 | 115 | 113 | 113 | 126 | 131 |  | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 3028032
115 | Juldah 100 MW PP Unit-3 (Acorn) | 49 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 88 | 88 | 100 | 100 | 100 | 100 | 88 | 827520
116 | Chandpur 200 MW (Desh energy) | 68 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 34 | 34 | 34 | 64 | 68 | 68 |  | 91 | 200 | 183 | 172 | 163 | 136 | 136 | 1581600
117 | Ashuganj 150 MW PP (Midland) | [12 empty] | 6 | 33 | 36 | 35 | 33 | 30 |  | 83 | 110 | 6 | 6 | 6 | 0 | 0 | 384727
118 | Bibiyana-III 400 MW CCPP | 361 | 350 | 348 | 350 | 376 | 301 | 335 | 309 | 323 | 355 | 364 | 385 | 325 | 305 | 330 | 300 | 349 | 387 |  | 349 | 349 | 350 | 350 | 350 | 391 | 349 | 8717000
| Jamalpur 115 MW PP (United) | 57 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 58 | 58 | 57 | 57 | 57 |  | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 1386000
| Anwara 300 MW PP (United) | 80 | 50 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 120 | 100 | 50 | 50 | 50 | 50 | 50 | 918327
| Juldah unit-2 (Acorn) | 50 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 88 | 100 | 100 | 100 | 100 | 100 | 90 | 884160
| Anlima Energy Ltd. | 17 | [14 empty] | 5 | 17 | 17 |  | 32 | 17 | 17 | 17 | 17 | 17 | 17 | 199473
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434880
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 11 | 6 | 23 | 8 | 20 | 24 | 23 | 26 | 4 | 2 | 1 | [8 empty] | 164071
| Chandpur 115(Doreen) | 90 | 67 | 67 | 67 | 67 | 39 | 41 | 61 | 67 | 67 | 70 | 72 | 68 | 84 | 72 | 74 | 73 | 73 |  | 73 | 73 | 73 | 72 | 72 | 73 | 71 | 1686720
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 29 | 35 | 35 | 35 | 35 | 35 | 35 | 703800
| Mirsharai 150 MW (Oil) | [17 empty] | 17 |  | 90 | 108 | 17 | 17 | 17 | 0 | 0 | 175636
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 16 | 16 | 13 | 11 | 15 | 15 | 21 | 5 | 7 | 8 | 6 | 14 | 19 | 4 | 15 | 5 | 4 | 0 |  | 4 | 10 | 7 | 3 | 10 | 12 | 7 | 249600
| Sonagazi 75 MW Solar Plant | [5 empty] | 5 | 11 | 28 | 40 | 20 | 29 | 57 | 77 | 47 | 57 | 32 | 5 | 1 | [8 empty] | 384309
| Matarbari 2*600 MW (CPGCL) | 1154 | 1154 | 1157 | 1155 | 1157 | 1153 | 1156 | 1158 | 1152 | 1152 | 1151 | 1151 | 1152 | 1156 | 1152 | 1153 | 1150 | 1153 |  | 1151 | 1151 | 1152 | 1153 | 1151 | 1155 | 1154 | 27869090
| Meghnaghat (Reliance) 718MW CCPP | [24 empty] | 25 | 38 | 16000
120 | Eastern Zone Total | 6499 | 6165 | 6082 | 6066 | 5898 | 5622 | 5698 | 5677 | 5980 | 6057 | 6092 | 6390 | 6595 | 6606 | 6805 | 6861 | 6912 | 6671 | 0 | 7862 | 7936 | 7645 | 7663 | 7218 | 7181 | 7147 | 159703792
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [25 empty] | 0 | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 1 |  | 2 | 3 | [5 empty] | 2400
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [16 empty] | 9 |  | 26 | 35 | 35 | 35 | 35 | 50 | 65 | 283200
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 11 | 60 | 50 | 48 | 17 | 11 | 26 | 49 | 17 | 5 | 3 | 1 | [8 empty] | 333360
131 | Rampal 1320 MW (BIFPCL) | 623 | 624 | 545 | 550 | 555 | 488 | 491 | 495 | 495 | 460 | 486 | 505 | 560 | 510 | 516 | 520 | 517 | 514 |  | 614 | 600 | 581 | 586 | 593 | 593 | 598 | 13127270
132 | United Payra Power Ltd. | [17 empty] | 2 |  | 37 | 54 | 54 | 17 | 17 | 17 | 17 | 159600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 220 | 180 |  | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 5158080
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | [14 empty] | 16 | 16 | 16 |  | 64 | 80 | 110 | 110 | 64 | 64 | 64 | 533472
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 270 | 250 | 250 | 250 | 250 | 200 | 170 | 170 | 170 | 170 | 208 | 261 | 270 | 270 | 307 | 307 | 307 | 250 |  | 307 | 307 | 307 | 307 | 307 | 307 | 250 | 6153000
136 | Barisal 1 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 3469
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 100 | 134 | 80 | 80 | 80 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2213000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 9 | 9 | 7 | 6 | 6 | 5 | 5 | 6 | 6 | 6 | 7 | 7 | 6 | 6 | 6 | 6 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 190407
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 8 | 27 |  | 39 | 52 | [5 empty] | 78592
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 897 | 898 | 898 | 898 | 898 | 898 | 897 | 898 | 898 | 898 | 898 | 898 | 897 | 898 | 898 | 897 | 898 | 898 |  | 898 | 897 | 898 | 898 | 898 | 898 | 898 | 21764160
147 | Bheramara 410 MW CCPP | 266 | 267 | 274 | 281 | 282 | 282 | 282 | 287 | 287 | 282 | 275 | 270 | 261 | 258 | 248 | 248 | 249 | 250 |  | 245 | 245 | 245 | 244 | 245 | 245 | 245 | 6445440
148 | Payra 1320 MW | 1244 | 1180 | 1120 | 1000 | 990 | 920 | 860 | 890 | 940 | 940 | 1020 | 1090 | 1100 | 1090 | 1130 | 1180 | 1180 | 1000 |  | 1100 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 28273200
149
150 | Barapukuria TPP Unit-1 | 61 | 61 | 62 | 60 | 60 | 60 | 59 | 60 | 62 | 61 | 61 | 60 | 60 | 59 | 59 | 61 | 61 | 61 |  | 60 | 61 | 62 | 61 | 60 | 62 | 62 | 1405090
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 34 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 320275
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 1 | 2 | 1 | 3 | 3 | 2 | 2 | 2 | 1 | 0 | [8 empty] | 27780
| Sirajganj 68 MW Solar Park | [5 empty] | 0 | 3 | 12 | 16 | 34 | 17 | 49 | 41 | 32 | 27 | 29 | 13 | 0 | [8 empty] | 311250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 150 | 173 | 180 | 180 | 180 | 150 | 150 | 150 | 153 | 192 | 197 | 195 | 193 | 193 | 193 | 193 | 190 | 150 |  | 157 | 171 | 176 | 180 | 180 | 180 | 180 | 4546082
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 347 | 326 | 345 | 345 | 347 | 334 | 347 | 346 | 398 | 414 | 414 | 354 | 325 | 352 | 353 | 348 | 392 | 349 |  | 393 | 309 | 338 | 393 | 414 | 414 | 396 | 8738327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 4 | 4 | 14 | 20 | 21 |  | 21 | 19 | 19 | 18 | 18 | 18 | 14 | 144932
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 106992
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [13 empty] | 14 | 17 | 21 | 21 | 25 |  | 42 | 42 | 46 | 46 | 35 | 35 | 35 | 252136
168 | Santahar 50 MW Peaking PP | 28 | [15 empty] | 13 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 227570
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 83 | 90 | 90 | 90 | 90 | 90 | 90 | 501120
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [15 empty] | 15 | 35 | 35 |  | 50 | 110 | 110 | 113 | 113 | 50 | 50 | 680640
172 | Confidence Power Bogura Unit-1 113 MW | [15 empty] | 35 | 35 | 35 |  | 95 | 95 | 95 | 95 | 95 | 50 | 50 | 583200
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 78 | 70 | 70 | 49 | 49 | 42 | 34 | 35 | 35 | 35 | 34 | 34 | 35 | 34 | 34 | 34 | 34 | 95 |  | 99 | 99 | 99 | 99 | 99 | 92 | 84 | 1390454
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 3 | 3 | 3 | 5 | 6 | 2 | 4 | 2 | 2 | 1 | [8 empty] | 34812
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | [6 empty] | 52 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 95 | 1277568
| Intraco Solar 30 MW | [5 empty] | 0 | 3 | 6 | 15 | 17 | 30 | 24 | 34 | 35 | 35 | 22 | 9 | 1 | [8 empty] | 207459
| Adani Power Jharkhanda Ltd | 971 | 1135 | 1133 | 1169 | 1171 | 1157 | 1162 | 1182 | 1168 | 1155 | 1250 | 1279 | 1357 | 1375 | 1281 | 1008 | 756 | 753 |  | 868 | 883 | 909 | 1037 | 1177 | 1308 | 1407 | 26791431
178 | Teesta Solar Limited | [5 empty] | 3 | 13 | 45 | 73 | 49 | 91 | 97 | 70 | 156 | 146 | 103 | 46 | 2 | [8 empty] | 1023000