## Forecast
[5 empty] | Power Grid Bangladesh PLC. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of National Grid on | [6 empty] | 2024-08-29 | Thursday
|  | Date (day): | 2024-08-29 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15690.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16447 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2024-08-28 | 2024-08-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 400 | 403 | 411 | 400 | 400
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 0 | 80 | 80 |  | 22 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 13 | 13 | 62 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 0 | 58 | 58 | 42 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 335 | 335 | 335
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 90 | 25 | 90 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 17 | 17 | 54
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 130 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 41 | 39 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 25 | 25 |  | 8 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 10 | 11 | 12 | 12 |  | 21 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 16 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 206 | 195 | 270 | 280 |  | 20
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 117 | 130 | 130 | 130 |  | 19 | Engine problem
33 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 54 | 54 | 51 |  | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 80 | 85 | 70 | 85 | 19 |  | Lub Oil problem
35 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
36 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 18 | 0 | 35 | 0
37 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 26 | 35 | 35 | 35 |  | 20 | Engine problem.
38 | Meghnaghat Unique power |  | Gas | IPP | 586 | 584 | 584 | 0 | 0 | 0 | 0 | 584 |  | Gas shortage
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 583 | 583 | 0 | 0 | 0 | 0 | 583 |  | Gas shortage
| Meghnaghat (Reliance) 718MW CCPP |  | Gas | IPP | 718 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 6930 | 6217 | 2263 | 2268 | 2532 | 2718 | 2521 | 921
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
40 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 0 | 8 | 8 | 17 |  | Fuel shortage
41 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 217 | 215 | 215 | 215
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 220 | 220
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 105 | 105
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 66 | 24 | 65 | 75 | 23 |  | Fuel shortage
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 77 | 34 | 80 | 84 |  | 18 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 50 | 85 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 31 | 10 | 20
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 15 | 280 | 280 | 20 |  | Fuel shortage
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 92 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 50 | 90 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 105 | 105
59 | Mirsharai 150 MW |  | HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 36 | 17 | 35 | 163
60 | SS Power I |  | Coal | SS Power | 2*612 | 1224 | 1224 | 420 | 500 | 612 | 612 |  | 612
61 | Cox's Bazar Wind |  | Wind | IPP | 66 | 60 | 60 | 0 | 0 | 42 | 60 |  |  | On test.
62 | Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 575 | 575 | 957 | 1150 | 1150 | 1150
| Mirsharai 150 MW (Gas) |  | Gas | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Chattogram area Total |  |  |  |  | 4442 | 4382 | 2211 | 2323 | 3323 | 3511 | 348 | 960
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
63 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 213 | 210 | 210
64 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 285 | 280 | 310 | 50 |  | Gas shortage
65 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 270 | 270 | 270 | 90 |  | Gas shortage
66 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 240 | 230 | 250 | 150 |  | Gas shortage
67 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 38 | 20 | 38 | 38 | 7 |  | Gas shortage
68 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 55 | 5 | 5 | 20 | 20 | 35 |  | Gas shortage
69 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
70 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
71 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 6 | 24 | 140 |  | 10 | Engine problem
72 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 36 | 36 | 35 | 37 |  | 15 | Engine problem
73 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 25 | 30 | 35 | 40 | 123 |  | Gas shortage
74 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 115 | 136 | 200 | 200
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | Contract Expired
76 | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 60 | 60 | 90 | 90
77 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
78 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 25 | 16 | 43 |  | 9 | Engine problem
79 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 18 | 18 | 18 |  | 7 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 70 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 63 | 80 | 65 | 90 |  | 25 | Engine problem
| Sonagazi 75 MW Solar Plant |  | Solar | EGCB | 75 | 75 | 75 | 36 | 0 | 70 | 0
| Cumilla Area Total |  |  |  |  | 2958 | 2917 | 1582 | 1554 | 1775 | 1930 | 754 | 66
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 8 | 17 | 20 | 20 | 182 |  | Gas shortage
84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 124 | 98 | 125 | 75 |  | Fuel shortage
87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 77 | 58 | 77 | 38 |  | Fuel shortage
88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 0 | 6 | 12 |  | 10 | Engine prblem
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 0 | 17 | 35 |  | 19 | Engine prblem
| Mymensingh Area Total |  |  |  |  | 749 | 646 | 225 | 218 | 250.6 | 269 | 182 | 29
90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 38 | 38 | 38 | 38 |  | 32 | Machine problem.
91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 20 | 20 |  | 70 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Gas shortage
95 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 2 | 2 | 2 |  | 9 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 0 | 0 | 0 |  | 66 | GT-8 Under maint.
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 10 | 10 | 10 | 76 |  | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0
100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 135 | 135 | 136 |  | 95 | ST Under maint.
101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Gas shortage
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 120 | 290 | 300 | 300 |  |  | FGMO
104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 350 | 350 | 350 |  |  | FGMO
105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 340 | 350 | 350 |  |  | FGMO
| Sylhet Area Total |  |  |  |  | 2462 | 2417 | 1231 | 1360 | 1380 | 1381 | 197 | 615
107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 896 | 706 | 913 | 913
108 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 32 | 98 |  | 17 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 30 | 40 |  | 14 | Engine problem
110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 0 | 55 |  | 54 | Engine problem
112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 265 | 250 | 250 | 250 | 160 |  | Gas shortage
113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 71 | 70 | 72 | 33 |  | Fuel shortage
115 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 52 | 0 | 100 | 0
117 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 336 |  | Fuel shortage
118 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 617*2 | 1234 | 1234 | 510 | 623 | 586 | 600 | 634
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3858 | 3854 | 1723 | 1700 | 1981 | 2028 | 1554 | 85
119 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 64 | 110
120 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 10 | 6 | 9 | 10 | 10
121 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 80 | 134 | 135 | 135 |  | 59 | ST Under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1060 | 1220 | 1244 | 1244
123 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 180 | 220 | 220 | 220
124 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 17 | 35 | 115 |  | Fuel shortage
125 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 307 | 307 | 307
| Barisal 1 MW Solar Plant |  | Solar | BPDB | 1 | 1 | 1 | 0 | 0 | 0 | 0
| Barisal Area Total |  |  |  |  | 2266 | 2236 | 1576 | 1906 | 1997 | 2061 | 115 | 59
126 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
127 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 30 | 40 |  | 12 | Engine problem
128 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
129 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 28 |  |  | Engine problem
130 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
131 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 25 | 46
132 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
133 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
134 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 181 | 154 | 196 | 196 | 24 |  | Gas shortage
135 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 314 | 350 | 414
136 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 6 | 28 | 25 | 28 |  | 22 | Engine problem
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 5 | 5 |  | 6 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 88 | 50 | 90 |  | 14 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 64 | 113 | 113 | 113
141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 95 | 95 |  | 18 | Engine problem
142 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
** | Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 766 | 1511 | 1200 | 1200
143 | Sirajganj 68 MW Solar Park |  | Solar | IPP | 68 | 68 | 68 | 65 | 0 | 20 | 0
| Rajshahi Area Total |  |  |  |  | 3471 | 3449 | 1601 | 2353 | 2115 | 2275 | 467 | 333
144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 60 | 61 | 60 | 60 |  | 25 | Machine problem
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 99 | 34 | 99 |  | 14 | Engine problem
149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
150 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 75 | 115 | 75 | 115
151 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 30 | 0
152 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 175 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 387 | 275 | 337 | 274 | 40 | 398
| Total |  |  |  |  | 28166 | 27068 | 12799 | 13957 | 15690.6 | 16447 | 6178 | 3466
A. |  | 2024-08-28 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 13957 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11361 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14470 | MW
3 | Day peak Generation : |  |  | 12799 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13848.5 | MW
4 | Evening peak Generation : |  |  | 13957 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 490 | MW
5 | Total Energy Generation : |  | 306.8166 | MKWHr | By Solar | 3.459 | MKWHr
| By Gas : | 122.3897 | MKWHr |  | By Oil: | 41.1932 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 112.3985 | MKWHr |  | By Hydro: | 5.2203 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.08352 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6178 | MW | Dhaka | 4910 | 4780 |  | 130 |  | 18:00 |  | 285.545
|  |  | For Plants S/D or M/C prob = |  |  | 3466 | MW | Chittagong | 1216.1 | 1216.1 |  | 0 |  | 19:00 |  | 459.355
|  |  | Total = |  |  | 9644 | MW | Khulna | 1684 | 1684 |  | 0 |  | 19:30 |  | 482.275
7 | Total Gas Supplied : |  |  | 882.49 | MMCFD |  |  | Rajshahi | 1562.2 | 1562.2 |  | 0 |  | 20:00 |  | 488.96
8 | Fuel Cost : | i) Gas : | Taka | 362700197.806 | ii) Oil : | Taka | 754162937.08 | Comilla | 1164 | 1144 |  | 20 |  | 21:00 |  | 489.915
|  | iii) Coal : | Taka | 746341507.89 | Total | Taka | 1863204642.776 | Mymensingh | 1239 | 1049 |  | 190 |  | 22:00 |  | 500.42
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 7131.3 | MKWHr. | Sylhet | 629 | 609 |  | 20 |  | 23:00 |  | 500.42
| ii) During Peak Demand : |  |  | 694 | MW (W to E) at | 21:00 | hrs | Barisal | 433.2 | 433.2 |  | 0 |  | 24:00 |  | 501.375
| iii) Maximum : |  |  | 592 | MW at | 20:00 | hrs | Rangpur | 1011 | 881 |  | 130
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6°C |  |  | Total | 13848.5 | 13358.5 |  | 490
B. |  | 2024-08-29 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 31.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 16447 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 13800 | MW
4 | Reserve(Generation end) |  |  |  | 1447 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 329.984 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 11578 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.7187 | MKWHr. | ii) HVDC Flow at Peak Time |  | 706 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.3536 | MKWHr. | iii) Maximum HVDC Flow : |  | 899 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 108.7 |  | (b) Today: | 108.62 |  | (c) Rule Curve: |  | 98.01
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2024-08-28 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | Sonagazi 75 MW Solar Plant | Meghnaghat (Reliance) 718MW CCPP | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | Barisal 1 MW Solar Plant | Sirajganj 68 MW Solar Park | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 41 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 19 | 22 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 260 | 216 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 58 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 195 | 0 | 0 | 98 | 0 | 131 | 0 | 88 | 136 | 0 | 350 | 49 | 17 | 17 | 0 | 50 | 0 | 17 | 52 | 9 | 90 | 346 | 85 | 0 | 35 | 17 | 0 | 17 | 0 | 55 | 17 | 230 | 0 | 0 | 273 | 4 | 1152 | 0 | 0 | 0 | 39 |  | 899 | 0 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 312 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1120 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 555 | 0 | 250 | 1515 | 0 | 0 | 0 | 0 |  | 7151 | 5655 | 12806 | 3477 | 899 | 1498 | 0 | 1623 | 4927 | 217 | 0 | 64 | 58 | 0 | 4 | 400.145 | 108.76
2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 41 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 285 | 260 | 213 | 0 | 37 | 38 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 56 | 17 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 120 | 0 | 12 | 68 | 0 | 350 | 49 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 9 | 12 | 340 | 45 | 0 | 17 | 0 | 0 | 17 | 0 | 48 | 17 | 230 | 0 | 0 | 360 | 3 | 1155 | 0 | 0 | 0 | 45 |  | 899 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 331 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1100 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 550 | 0 | 250 | 1532 | 0 | 0 | 0 | 0 |  | 6559 | 5591 | 12150 | 3481 | 899 | 1475 | 0 | 949 | 5009 | 217 | 0 | 16 | 56 | 0 | 3 | 382 | 108.74
3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 41 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 285 | 260 | 216 | 0 | 37 | 38 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 56 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 275 | 12 | 2 | 0 | 30 | 0 | 0 | 97 | 0 | 129 | 0 | 0 | 68 | 0 | 350 | 49 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 9 | 0 | 340 | 34 | 0 | 17 | 0 | 0 | 17 | 0 | 48 | 17 | 230 | 0 | 0 | 436 | 3 | 1150 | 0 | 0 | 0 | 47 |  | 898 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 313 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 1080 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 539 | 0 | 250 | 1531 | 0 | 0 | 0 | 0 |  | 6574 | 5545 | 12119 | 3493 | 898 | 1453 | 0 | 888 | 5048 | 217 | 0 | 16 | 56 | 0 | 3 | 363.855 | 108.73
4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 24 | 11 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 285 | 260 | 214 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 54 | 19 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 131 | 0 | 0 | 17 | 0 | 350 | 49 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 9 | 0 | 340 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 51 | 17 | 230 | 0 | 0 | 516 | 3 | 1008 | 0 | 0 | 0 | 45 |  | 898 | 0 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 333 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 1040 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 486 | 0 | 250 | 1526 | 0 | 0 | 0 | 0 |  | 6331 | 5461 | 11792 | 3501 | 898 | 1536 | 0 | 636 | 4886 | 217 | 0 | 16 | 54 | 0 | 3 | 365.765 | 108.72
5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 285 | 260 | 215 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 0 | 18 | 60 | 19 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 131 | 0 | 0 | 17 | 0 | 350 | 49 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 9 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 17 | 230 | 0 | 0 | 585 | 2 | 1009 | 0 | 0 | 0 | 45 |  | 898 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 324 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 1030 | 180 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 487 | 0 | 250 | 1390 | 0 | 0 | 0 | 0 |  | 6352 | 5298 | 11650 | 3508 | 898 | 1521 | 0 | 570 | 4813 | 217 | 0 | 16 | 60 | 0 | 2 | 358.125 | 108.71
6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 305 | 260 | 213 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 56 | 19 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 20 | 10 | 0 | 137 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 131 | 0 | 0 | 17 | 0 | 376 | 49 | 17 | 0 | 0 | 0 | 0 | 0 | 34 | 9 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 17 | 250 | 0 | 0 | 612 | 1 | 865 | 0 | 0 | 1 | 45 |  | 898 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 349 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1030 | 180 | 0 | 0 | 0 | 1 | 75 | 0 | 0 | 406 | 0 | 250 | 1252 | 4 | 0 | 0 | 1 |  | 6251 | 5110 | 11361 | 3600 | 898 | 1546 | 0 | 497 | 4477 | 217 | 0 | 16 | 56 | 8 | 1 | 371.495 | 108.7
7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 305 | 345 | 190 | 0 | 35 | 38 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 18 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 139 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 131 | 7 | 0 | 17 | 0 | 362 | 49 | 17 | 0 | 0 | 0 | 0 | 0 | 17 | 9 | 0 | 360 | 0 | 12 | 0 | 0 | 0 | 0 | 5 | 17 | 17 | 250 | 0 | 0 | 612 | 0 | 855 | 0 | 0 | 5 | 20 |  | 898 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 348 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 1070 | 220 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 409 | 6 | 298 | 1062 | 42 | 0 | 0 | 11 |  | 6293 | 5073 | 11366 | 3692 | 898 | 1596 | 0 | 408 | 4368 | 217 | 0 | 16 | 52 | 99 | 0 | 318.97 | 108.69
8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 18 | 23 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 280 | 270 | 196 | 0 | 25 | 35 | 5 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 16 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 137 | 0 | 0 | 0 | 295 | 12 | 2 | 0 | 0 | 0 | 0 | 97 | 0 | 131 | 9 | 5 | 17 | 0 | 350 | 49 | 17 | 0 | 0 | 5 | 0 | 0 | 17 | 9 | 12 | 340 | 0 | 27 | 38 | 0 | 0 | 0 | 13 | 17 | 17 | 230 | 0 | 0 | 612 | 1 | 1152 | 0 | 0 | 10 | 0 |  | 896 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 395 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 1140 | 220 | 0 | 0 | 2 | 22 | 0 | 0 | 0 | 500 | 15 | 307 | 762 | 95 | 0 | 0 | 2 |  | 6564 | 5056 | 11620 | 3584 | 896 | 1604 | 0 | 513 | 4535 | 217 | 0 | 16 | 54 | 200 | 1 | 382 | 108.68
9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 38 | 335 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 3 | 35 | 55 | 0 | 18 | 22 | 24 | 12 | 0 | 0 | 137 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 204 | 0 | 25 | 38 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 46 | 11 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 137 | 0 | 0 | 0 | 230 | 12 | 2 | 0 | 19 | 0 | 0 | 97 | 0 | 131 | 8 | 50 | 36 | 18 | 350 | 49 | 52 | 17 | 1 | 15 | 0 | 0 | 34 | 9 | 50 | 340 | 20 | 38 | 108 | 0 | 0 | 15 | 16 | 30 | 17 | 230 | 17 | 0 | 501 | 0 | 1103 | 0 | 0 | 18 | 0 |  | 896 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 327 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 1090 | 180 | 0 | 0 | 3 | 55 | 0 | 0 | 0 | 502 | 24 | 250 | 754 | 140 | 0 | 0 | 32 |  | 6858 | 4953 | 11811 | 3622 | 896 | 1379 | 0 | 1018 | 4261 | 217 | 0 | 33 | 46 | 339 | 0 | 419.245 | 108.67
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 82 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 17 | 22 | 24 | 12 | 0 | 0 | 136 | 80 | 0 | 0 | 0 | 221 | 0 | 0 | 0 |  | 6 | 36 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 206 | 0 | 24 | 35 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 56 | 11 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 115 | 12 | 2 | 0 | 110 | 0 | 0 | 97 | 0 | 129 | 20 | 50 | 68 | 50 | 350 | 49 | 52 | 17 | 3 | 15 | 0 | 0 | 52 | 9 | 50 | 340 | 52 | 22 | 108 | 0 | 0 | 17 | 13 | 71 | 17 | 230 | 36 | 0 | 450 | 0 | 1006 | 0 | 0 | 23 | 0 |  | 895 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 320 | 0 | 0 | 2 | 0 | 34 | 0 | 7 | 30 | 1090 | 180 | 0 | 0 | 2 | 51 | 0 | 0 | 0 | 510 | 20 | 250 | 760 | 132 | 0 | 0 | 41 |  | 6948 | 4988 | 11936 | 3599 | 895 | 1257 | 0 | 1345 | 4128 | 216 | 0 | 104 | 56 | 336 | 0 | 443 | 108.66
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 42 | 35 | 55 | 0 | 17 | 22 | 24 | 10 | 0 | 0 | 137 | 80 | 0 | 0 | 3 | 217 | 0 | 0 | 0 |  | 6 | 64 | 34 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 285 | 270 | 202 | 0 | 25 | 38 | 5 | 0 | 43 | 0 | 29 | 16 | 0 | 0 | 0 | 18 | 56 | 8 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 120 | 0 | 30 | 10 | 0 | 135 | 0 | 0 | 0 | 120 | 12 | 2 | 0 | 156 | 0 | 0 | 96 | 0 | 116 | 14 | 62 | 76 | 52 | 350 | 49 | 52 | 17 | 4 | 15 | 0 | 0 | 52 | 9 | 84 | 380 | 67 | 43 | 162 | 0 | 0 | 17 | 36 | 68 | 17 | 230 | 36 | 0 | 420 | 0 | 956 | 0 | 0 | 35 | 0 |  | 896 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 337 | 0 | 0 | 35 | 0 | 34 | 0 | 7 | 70 | 1040 | 180 | 0 | 0 | 4 | 48 | 54 | 0 | 0 | 510 | 32 | 250 | 766 | 138 | 0 | 0 | 40 |  | 7236 | 5049 | 12285 | 3580 | 896 | 1273 | 0 | 1662 | 4003 | 217 | 0 | 195 | 56 | 403 | 0 | 301 | 108.66
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 22 | 24 | 10 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 66 | 77 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 295 | 275 | 190 | 0 | 25 | 38 | 5 | 0 | 51 | 0 | 36 | 16 | 0 | 0 | 0 | 18 | 60 | 8 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 120 | 12 | 2 | 0 | 206 | 0 | 0 | 96 | 0 | 117 | 20 | 62 | 115 | 50 | 363 | 49 | 52 | 17 | 5 | 15 | 0 | 0 | 70 | 9 | 90 | 360 | 80 | 47 | 162 | 0 | 0 | 17 | 18 | 63 | 26 | 230 | 36 | 0 | 420 | 0 | 957 | 0 | 0 | 36 | 0 |  | 896 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 414 | 0 | 0 | 64 | 0 | 34 | 0 | 6 | 95 | 1060 | 180 | 0 | 0 | 5 | 52 | 75 | 0 | 0 | 510 | 37 | 250 | 766 | 175 | 0 | 0 | 65 |  | 7512 | 5287 | 12799 | 3577 | 896 | 1402 | 0 | 1903 | 4023 | 217 | 0 | 253 | 60 | 468 | 0 | 211 | 108.66
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 22 | 24 | 5 | 0 | 0 | 138 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 65 | 82 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 285 | 270 | 206 | 0 | 25 | 20 | 5 | 0 | 51 | 0 | 36 | 16 | 0 | 0 | 0 | 18 | 60 | 8 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 170 | 12 | 2 | 0 | 210 | 0 | 0 | 95 | 0 | 119 | 20 | 75 | 120 | 52 | 315 | 48 | 52 | 17 | 5 | 15 | 0 | 0 | 106 | 9 | 90 | 346 | 86 | 39 | 162 | 0 | 0 | 17 | 31 | 55 | 28 | 230 | 36 | 0 | 408 | 0 | 859 | 0 | 0 | 53 | 0 |  | 896 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 350 | 0 | 0 | 112 | 0 | 34 | 0 | 5 | 95 | 1080 | 180 | 0 | 0 | 1 | 81 | 75 | 0 | 0 | 550 | 33 | 270 | 767 | 172 | 0 | 0 | 37 |  | 7460 | 5396 | 12856 | 3528 | 896 | 1391 | 0 | 2011 | 3994 | 218 | 0 | 279 | 60 | 479 | 0 | 195 | 108.65
14:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 22 | 24 | 5 | 0 | 0 | 136 | 80 | 0 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 64 | 82 | 0 | 0 | 11 | 0 | 6 | 0 | 0 | 0 | 285 | 270 | 212 | 0 | 25 | 20 | 5 | 0 | 51 | 0 | 28 | 16 | 0 | 0 | 0 | 18 | 58 | 8 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 295 | 12 | 5 | 0 | 210 | 0 | 0 | 96 | 0 | 114 | 17 | 75 | 100 | 52 | 325 | 57 | 52 | 17 | 4 | 15 | 0 | 0 | 106 | 9 | 90 | 326 | 86 | 24 | 162 | 0 | 0 | 17 | 35 | 56 | 18 | 230 | 36 | 0 | 415 | 5 | 850 | 0 | 0 | 31 | 0 |  | 895 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 112 | 0 | 34 | 0 | 7 | 95 | 1040 | 220 | 0 | 0 | 5 | 59 | 75 | 0 | 0 | 550 | 17 | 240 | 879 | 193 | 0 | 0 | 56 |  | 7451 | 5461 | 12912 | 3470 | 895 | 1514 | 0 | 1998 | 4036 | 216 | 0 | 270 | 58 | 450 | 5 | 275.04 | 108.66
15:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 24 | 5 | 0 | 0 | 136 | 80 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 6 | 55 | 82 | 0 | 0 | 6 | 0 | 4 | 0 | 0 | 0 | 305 | 285 | 210 | 0 | 25 | 10 | 5 | 0 | 43 | 0 | 30 | 16 | 0 | 0 | 0 | 18 | 62 | 8 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 310 | 12 | 5 | 0 | 208 | 0 | 0 | 97 | 0 | 113 | 14 | 36 | 100 | 53 | 328 | 57 | 35 | 17 | 2 | 15 | 0 | 0 | 106 | 9 | 50 | 326 | 86 | 28 | 162 | 0 | 0 | 17 | 12 | 44 | 35 | 230 | 17 | 0 | 420 | 8 | 852 | 0 | 0 | 58 | 0 |  | 895 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 113 | 0 | 34 | 0 | 6 | 95 | 1040 | 220 | 0 | 0 | 2 | 41 | 75 | 0 | 0 | 555 | 17 | 240 | 1094 | 140 | 0 | 0 | 29 |  | 7399 | 5612 | 13011 | 3522 | 895 | 1519 | 0 | 1902 | 4262 | 216 | 0 | 275 | 62 | 350 | 8 | 275.995 | 108.64
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 90 | 40 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 24 | 5 | 0 | 0 | 136 | 80 | 0 | 0 | 8 | 214 | 0 | 0 | 0 |  | 6 | 55 | 82 | 0 | 0 | 6 | 0 | 4 | 0 | 0 | 0 | 290 | 270 | 210 | 0 | 25 | 10 | 5 | 0 | 43 | 0 | 36 | 16 | 0 | 0 | 0 | 18 | 54 | 8 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 5 | 0 | 208 | 0 | 0 | 96 | 0 | 113 | 9 | 36 | 100 | 52 | 299 | 57 | 17 | 17 | 2 | 15 | 0 | 0 | 70 | 9 | 50 | 320 | 86 | 22 | 162 | 0 | 0 | 17 | 6 | 54 | 35 | 230 | 17 | 0 | 420 | 20 | 850 | 0 | 0 | 15 | 0 |  | 896 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 7 | 0 | 0 | 0 | 0 | 38 | 4 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 350 | 0 | 0 | 50 | 0 | 34 | 0 | 4 | 95 | 1040 | 220 | 0 | 0 | 1 | 37 | 75 | 0 | 0 | 555 | 8 | 240 | 1183 | 48 | 0 | 0 | 23 |  | 7236 | 5534 | 12770 | 3459 | 896 | 1509 | 0 | 1793 | 4348 | 216 | 0 | 300 | 54 | 175 | 20 | 315.15 | 108.64
17:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 |  | 0 | 320 | 0 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 136 | 80 | 0 | 0 | 10 | 213 | 0 | 0 | 0 |  | 6 | 55 | 82 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 285 | 270 | 214 | 0 | 25 | 10 | 5 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 18 | 52 | 11 | 0 | 0 | 0 | 38 | 10 | 0 | 0 | 120 | 0 | 28 | 10 | 0 | 134 | 0 | 0 | 0 | 285 | 12 | 5 | 0 | 228 | 0 | 0 | 95 | 0 | 113 | 4 | 36 | 100 | 52 | 302 | 57 | 17 | 17 | 1 | 15 | 0 | 0 | 70 | 9 | 50 | 320 | 86 | 10 | 162 | 0 | 0 | 0 | 3 | 48 | 35 | 280 | 17 | 0 | 420 | 19 | 850 | 0 | 0 | 12 | 0 |  | 896 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 37 | 4 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 300 | 0 | 0 | 50 | 0 | 52 | 0 | 2 | 95 | 920 | 180 | 0 | 0 | 0 | 8 | 90 | 0 | 0 | 485 | 6 | 200 | 1342 | 19 | 0 | 0 | 7 |  | 7099 | 5273 | 12372 | 3422 | 896 | 1282 | 0 | 1827 | 4277 | 216 | 0 | 309 | 52 | 72 | 19 | 332.34 | 108.63
18:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 |  | 0 | 320 | 0 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 90 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 135 | 80 | 0 | 0 | 16 | 220 | 0 | 0 | 0 |  | 6 | 70 | 82 | 0 | 0 | 6 | 0 | 10 | 0 | 0 | 0 | 290 | 270 | 214 | 0 | 23 | 20 | 5 | 0 | 51 | 0 | 36 | 33 | 0 | 0 | 0 | 18 | 52 | 11 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 230 | 0 | 0 | 96 | 0 | 117 | 0 | 36 | 100 | 57 | 300 | 67 | 17 | 17 | 0 | 15 | 0 | 1 | 70 | 9 | 50 | 320 | 82 | 2 | 162 | 2 | 0 | 0 | 1 | 49 | 35 | 260 | 17 | 0 | 420 | 13 | 850 | 0 | 0 | 2 | 0 |  | 895 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 80 | 6 | 16 | 0 | 0 | 0 | 37 | 15 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 250 | 0 | 0 | 50 | 0 | 82 | 0 | 1 | 95 | 760 | 180 | 0 | 4 | 0 | 2 | 94 | 0 | 0 | 445 | 1 | 160 | 1410 | 7 | 0 | 0 | 1 |  | 6988 | 5083 | 12071 | 3286 | 895 | 1232 | 0 | 1923 | 4104 | 215 | 0 | 334 | 52 | 17 | 13 | 285.545 | 108.63
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 392 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 90 | 130 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 135 | 80 | 0 | 0 | 18 | 219 | 0 | 0 | 0 |  | 4 | 70 | 82 | 0 | 0 | 6 | 0 | 10 | 0 | 0 | 0 | 300 | 270 | 215 | 0 | 23 | 20 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 18 | 58 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 134 | 0 | 0 | 0 | 290 | 12 | 5 | 0 | 228 | 0 | 0 | 123 | 0 | 124 | 0 | 74 | 130 | 92 | 349 | 77 | 52 | 17 | 0 | 15 | 0 | 17 | 85 | 9 | 88 | 340 | 85 | 0 | 162 | 17 | 0 | 0 | 0 | 49 | 35 | 260 | 71 | 0 | 480 | 5 | 1100 | 0 | 0 | 0 | 0 |  | 896 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 134 | 10 | 32 | 0 | 0 | 0 | 37 | 22 | 86 | 0 | 0 | 19 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 340 | 35 | 0 | 80 | 0 | 98 | 0 | 0 | 95 | 850 | 180 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 563 | 0 | 212 | 1431 | 0 | 0 | 0 | 0 |  | 8082 | 5767 | 13849 | 3539 | 896 | 1509 | 0 | 2330 | 4696 | 215 | 0 | 601 | 58 | 0 | 5 | 459.355 | 108.63
19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 |  | 0 | 380 | 0 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 90 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 135 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 0 | 24 | 34 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 300 | 270 | 214 | 0 | 23 | 20 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 12 | 58 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 134 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 235 | 0 | 0 | 124 | 0 | 130 | 0 | 74 | 170 | 50 | 349 | 77 | 52 | 17 | 0 | 15 | 0 | 17 | 90 | 9 | 89 | 340 | 85 | 0 | 162 | 17 | 0 | 0 | 0 | 72 | 35 | 240 | 71 | 0 | 500 | 2 | 1150 | 0 | 0 | 0 | 0 |  | 895 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 80 | 10 | 48 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 36 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 336 | 68 | 0 | 113 | 0 | 98 | 0 | 0 | 95 | 960 | 180 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 608 | 0 | 230 | 1488 | 0 | 0 | 0 | 0 |  | 7846 | 5999 | 13845 | 3416 | 895 | 1390 | 0 | 2396 | 4996 | 215 | 0 | 477 | 58 | 0 | 2 | 482.275 | 0
20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 24 | 34 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 300 | 270 | 215 | 0 | 25 | 20 | 5 | 0 | 51 | 0 | 36 | 42 | 0 | 0 | 0 | 12 | 56 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 134 | 0 | 0 | 0 | 280 | 12 | 5 | 0 | 242 | 0 | 0 | 124 | 0 | 129 | 0 | 50 | 170 | 50 | 349 | 77 | 52 | 17 | 0 | 15 | 0 | 0 | 88 | 9 | 50 | 340 | 85 | 0 | 162 | 0 | 0 | 0 | 0 | 62 | 35 | 240 | 35 | 0 | 505 | 3 | 1150 | 0 | 0 | 0 | 0 |  | 706 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 80 | 10 | 32 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 46 | 0 | 28 | 0 | 0 | 8 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 336 | 71 | 0 | 113 | 0 | 98 | 0 | 0 | 95 | 1030 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 621 | 0 | 250 | 1516 | 0 | 0 | 0 | 0 |  | 7868 | 5990 | 13858 | 3487 | 706 | 1508 | 0 | 2272 | 5132 | 215 | 0 | 479 | 56 | 0 | 3 | 488.96 | 108.63
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 25 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 24 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 285 | 270 | 213 | 0 | 30 | 20 | 5 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 18 | 60 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 195 | 0 | 0 | 124 | 0 | 130 | 0 | 50 | 136 | 6 | 350 | 77 | 52 | 17 | 0 | 15 | 0 | 0 | 70 | 9 | 50 | 340 | 85 | 0 | 162 | 0 | 0 | 0 | 0 | 80 | 35 | 240 | 17 | 0 | 500 | 0 | 1150 | 0 | 0 | 0 | 0 |  | 706 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 42 | 0 | 28 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 314 | 71 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1220 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 623 | 0 | 307 | 1511 | 0 | 0 | 0 | 0 |  | 7723 | 6234 | 13957 | 3578 | 706 | 1543 | 0 | 2034 | 5372 | 215 | 0 | 449 | 60 | 0 | 0 | 489.915 | 108.63
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 409 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 332 | 0 | 0 | 0 | 25 | 130 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 310 | 290 | 211 | 0 | 30 | 20 | 5 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 58 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 195 | 0 | 0 | 124 | 0 | 131 | 0 | 12 | 136 | 6 | 365 | 77 | 52 | 17 | 0 | 15 | 0 | 0 | 70 | 9 | 50 | 358 | 83 | 0 | 72 | 0 | 0 | 0 | 0 | 72 | 35 | 240 | 17 | 0 | 500 | 0 | 1085 | 0 | 0 | 0 | 0 |  | 706 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 347 | 71 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 625 | 0 | 307 | 1514 | 0 | 0 | 0 | 0 |  | 7497 | 6279 | 13776 | 3679 | 706 | 1587 | 0 | 1855 | 5335 | 214 | 0 | 342 | 58 | 0 | 0 | 500.42 | 108.62
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 404 | 0 |  | 0 | 450 | 0 | 0 | 0 | 30 | 334 | 0 | 0 | 0 | 25 | 98 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 295 | 260 | 213 | 0 | 33 | 20 | 5 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 60 | 19 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 310 | 12 | 2 | 0 | 200 | 0 | 0 | 124 | 0 | 117 | 0 | 12 | 136 | 6 | 347 | 77 | 52 | 17 | 0 | 15 | 0 | 0 | 70 | 9 | 50 | 358 | 68 | 0 | 72 | 0 | 0 | 0 | 0 | 72 | 35 | 230 | 17 | 0 | 500 | 0 | 1084 | 0 | 0 | 0 | 4 |  | 706 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 10 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 414 | 71 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 624 | 0 | 307 | 1506 | 0 | 0 | 0 | 0 |  | 7376 | 6350 | 13726 | 3624 | 706 | 1671 | 0 | 1831 | 5325 | 214 | 0 | 291 | 60 | 0 | 0 | 500.42 | 108.62
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 0 | 0 | 45 | 335 | 0 | 0 | 0 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 0 | 18 | 23 | 24 | 12 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 285 | 260 | 213 | 0 | 33 | 20 | 5 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 0 | 18 | 58 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 265 | 0 | 0 | 124 | 0 | 113 | 0 | 12 | 136 | 6 | 347 | 77 | 35 | 0 | 0 | 0 | 0 | 0 | 70 | 9 | 12 | 340 | 63 | 0 | 126 | 0 | 0 | 15 | 0 | 72 | 35 | 230 | 17 | 0 | 500 | 0 | 1085 | 0 | 0 | 0 | 18 |  | 706 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 10 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 395 | 71 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 618 | 0 | 307 | 1516 | 0 | 0 | 0 | 0 |  | 7353 | 6272 | 13625 | 3593 | 706 | 1642 | 0 | 1866 | 5330 | 214 | 0 | 198 | 58 | 0 | 0 | 501.375 | 108.62
KWH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9468000 | 0 |  | 0 | 10301000 | 0 | 0 | 0 | 936307 | 7480649 | 0 | 0 | 0 | 1238976 | 1187520 | 0 | 0 | 0 | 0 | 619560 | 949374 | 1037966 | 0 | 445200 | 535320 | 602800 | 239800 | 0 | 0 | 3280319 | 1940000 | 0 | 0 | 107451 | 5130869 | 0 | 0 | 0 |  | 79680 | 612192 | 777181 | 0 | 0 | 61920 | 0 | 508800 | 0 | 0 | 0 | 7436300 | 6666000 | 5063000 | 0 | 681860 | 666072 | 127200 | 0 | 1120030 | 0 | 354496 | 434227 | 0 | 0 | 0 | 361550 | 1353600 | 312000 | 0 | 0 | 12000 | 896000 | 121200 | 0 | 0 | 3481364 | 0 | 449088 | 263040 | 0 | 3260850 | 0 | 0 | 0 | 6454500 | 276288 | 69552 | 0 | 3515236 | 0 | 0 | 2476800 | 0 | 2980800 | 140265 | 926400 | 2246400 | 712581 | 8618000 | 1380000 | 830880 | 303599 | 26641 | 338727 | 0 | 56040 | 1515060 | 223440 | 1139520 | 8237100 | 1365120 | 323780 | 2268000 | 53945 | 0 | 244440 | 197292 | 1283520 | 635040 | 5919700 | 398109 | 0 | 11110908 | 83520 | 24261818 | 0 | 0 | 326391 | 222600 |  | 20718720 | 0 | 6130080 | 0 | 0 | 0 | 0 | 0 | 1920 | 160000 | 0 | 2699000 | 194624 | 234720 | 0 | 0 | 0 | 170474 | 48755 | 506720 | 0 | 0 | 78783 | 0 | 302230 | 0 | 0 | 145908 | 1405091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4540027 | 0 | 8380364 | 492480 | 0 | 1383744 | 0 | 1382457 | 0 | 51425 | 1339104 | 27724800 | 5106600 | 0 | 46800 | 32760 | 462240 | 1754496 | 0 | 0 | 12836360 | 215337 | 6131000 | 28928520 | 1330000 | 0 | 2592 | 338250 |  | 171762773 | 135276381 | 307039154 | 86452213 | 20718720 | 35937522 | 0 | 36594810 | 112398497 | 5220319 | 0 | 4598380 | 1353600 | 3458973 | 83520 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27267840 | 0 |  | 0 | 32757180 | 0 | 0 | 0 | 16497729.34 | 22815979.45 | 0 | 0 | 0 | 22239619.2 | 23061638.4 | 0 | 0 | 0 | 0 | 11313165.6 | 14962134.24 | 18984398.14 | 0 | 333900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2035121.94 | 16367472.11 | 0 | 0 | 0 |  | 1401571.2 | 10780701.12 | 13919311.71 | 0 | 0 | 1019203.2 | 0 | 0 | 0 | 0 | 0 | 20747277 | 20397960 | 16809160 | 0 | 2202407.8 | 2244662.64 | 557136 | 0 | 4491320.3 | 0 | 6349023.36 | 7842139.62 | 0 | 0 | 0 | 271162.5 | 8879616 | 970320 | 0 | 0 | 0 | 3494400 | 452076 | 0 | 0 | 11906264.88 | 0 | 2492438.4 | 1373068.8 | 0 | 9097771.5 | 0 | 0 | 0 | 19944405 | 207216 | 52859.52 | 0 | 71710814.4 | 0 | 0 | 47579328 | 0 | 52491888 | 0 | 16499184 | 38975040 | 11814592.98 | 22837700 | 26302800 | 15587308.8 | 5446566.06 | 0 | 5538186.45 | 0 | 1005357.6 | 28952796.6 | 4336970.4 | 20294851.2 | 21910686 | 23302598.4 | 0 | 41481720 | 905197.1 | 0 | 4368142.8 | 0 | 23129030.4 | 10757577.6 | 17581509 | 5605374.72 | 0 | 77443028.76 | 0 | 143144726.2 | 0 | 0 | 0 | 0 |  | 58219603.2 | 0 | 18083736 | 0 | 0 | 0 | 0 | 0 | 36115.2 | 3009600 | 0 | 8528840 | 922517.76 | 4046572.8 | 0 | 0 | 0 | 3053189.34 | 894654.25 | 8517963.2 | 0 | 0 | 1411003.53 | 0 | 5412939.3 | 0 | 0 | 110452.356 | 15498153.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15118289.91 | 0 | 24470662.88 | 8411558.4 | 0 | 27425806.08 | 0 | 27538543.44 | 0 | 0 | 26567823.36 | 179656704 | 15881526 | 0 | 905580 | 0 | 0 | 30440505.6 | 0 | 0 | 93705428 | 0 | 45675950 | 191217517.2 | 0 | 0 | 0 | 0 |  | 1115542626.44 | 814761235.536 | 1930303861.976 | 250396116.186 | 58219603.2 | 112304081.62 | 0 | 672111422.95 | 746341507.89 | 0 | 0 | 82051514.13 | 8879616 | 0 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 403 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 17 | 22 | 24 | 10 | 0 | 0 | 137 | 80 | 0 | 0 | 8 | 218 | 0 | 0 | 0 |  | 6 | 66 | 77 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 295 | 275 | 190 | 0 | 25 | 38 | 5 | 0 | 51 | 0 | 36 | 16 | 0 | 0 | 0 | 18 | 60 | 8 | 0 | 0 | 2 | 38 | 0 | 0 | 0 | 163 | 0 | 28 | 10 | 0 | 135 | 0 | 0 | 0 | 120 | 12 | 2 | 0 | 206 | 0 | 0 | 96 | 0 | 117 | 20 | 62 | 115 | 50 | 363 | 49 | 52 | 17 | 5 | 15 | 0 | 0 | 70 | 9 | 90 | 360 | 80 | 47 | 162 | 0 | 0 | 17 | 18 | 63 | 26 | 230 | 36 | 0 | 420 | 0 | 957 | 0 | 0 | 36 | 0 |  | 896 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 414 | 0 | 0 | 64 | 0 | 34 | 0 | 6 | 95 | 1060 | 180 | 0 | 0 | 5 | 52 | 75 | 0 | 0 | 510 | 37 | 250 | 766 | 175 | 0 | 0 | 65 |  | 12799 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 |  | 0 | 450 | 0 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 25 | 130 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 18 | 23 | 24 | 11 | 0 | 0 | 135 | 80 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 24 | 34 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 285 | 270 | 213 | 0 | 30 | 20 | 5 | 0 | 51 | 0 | 36 | 25 | 0 | 0 | 0 | 18 | 60 | 17 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 290 | 12 | 2 | 0 | 195 | 0 | 0 | 124 | 0 | 130 | 0 | 50 | 136 | 6 | 350 | 77 | 52 | 17 | 0 | 15 | 0 | 0 | 70 | 9 | 50 | 340 | 85 | 0 | 162 | 0 | 0 | 0 | 0 | 80 | 35 | 240 | 17 | 0 | 500 | 0 | 1150 | 0 | 0 | 0 | 0 |  | 706 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 134 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 42 | 0 | 28 | 0 | 0 | 8 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 314 | 71 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1220 | 220 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 623 | 0 | 307 | 1511 | 0 | 0 | 0 | 0 |  | 13957 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  | 0 | 450 | 0 | 100 | 80 | 55 | 335 | 0 | 0 | 58 | 90 | 132 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 18 | 23 | 25 | 12 | 17 | 0 | 135 | 80 | 0 | 0 | 8 | 220 | 0 | 0 | 0 |  | 12 | 75 | 84 | 0 | 0 | 50 | 0 | 20 | 0 | 0 | 0 | 310 | 270 | 210 | 0 | 40 | 38 | 20 | 0 | 51 | 0 | 37 | 43 | 0 | 0 |  | 18 | 90 | 20 | 0 | 0 | 0 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 136 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 280 | 0 | 0 | 125 | 0 | 130 | 0 | 100 | 200 | 140 | 350 | 77 | 54 | 105 | 0 | 280 | 54 | 110 | 114 | 9 | 100 | 350 | 85 | 0 | 162 | 105 | 0 | 35 | 0 | 90 | 35 | 250 | 163 | 0 | 612 | 60 | 1150 | 0 | 0 |  |  |  | 913 | 0 | 250 | 0 | 98 | 0 | 0 | 0 | 40 | 55 | 0 | 135 | 10 | 110 | 0 | 0 | 0 | 40 | 20 | 90 | 28 | 0 | 46 | 0 | 28 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 414 | 72 | 0 | 113 | 0 | 99 | 0 | 0 | 95 | 1244 | 220 | 0 | 35 | 0 | 0 | 115 | 0 | 0 | 600 | 0 | 307 | 1200 | 0 | 0 |  |  |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 450 | 0 | 100 | 80 | 55 | 335 | 0 | 0 | 58 | 90 | 16 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 16 | 23 | 25 | 12 | 16 | 0 | 135 | 80 | 0 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 65 | 80 | 0 | 0 | 50 | 0 | 10 | 0 | 0 | 0 | 280 | 270 | 210 | 0 | 35 | 38 | 20 | 0 | 51 | 0 | 35 | 16 | 0 | 0 |  | 18 | 90 | 20 | 0 | 0 | 1.6 | 38 | 20 | 0 | 0 | 163 | 0 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 300 | 12 | 2 | 0 | 270 | 0 | 0 | 98 | 0 | 130 | 20 | 85 | 200 | 24 | 350 | 58 | 54 | 105 | 5 | 280 | 54 | 92 | 114 | 9 | 90 | 350 | 70 | 50 | 162 | 105 | 0 | 17 | 35 | 65 | 35 | 230 | 35 | 0 | 612 | 42 | 1150 | 0 | 0 | 70 |  |  | 913 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 135 | 10 | 64 | 0 | 0 | 0 | 30 | 0 | 50 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 5 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 350 | 70 | 0 | 113 | 0 | 34 | 0 | 8 | 95 | 1244 | 220 |  | 17 | 6 | 100 | 75 | 0 | 0 | 586 | 30 | 307 | 1200 | 130 | 0 |  | 20 |  |  |  |  | gas | hvdc | hsd | coal | hfo | tripura | solar | wind | hydro
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 38 | 250 | 0 | 0 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 16 | 35 | 55 | 0 | 17 | 23 | 24 | 12 | 0 | 0 | 134 | 80 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 310 | 240 | 210 | 0 | 25 | 38 | 5 | 0 | 51 | 0 | 0 | 16 | 0 | 0 | 0 | 18 | 74 | 11 | 0 | 0 | 1 | 38 | 20 | 0 | 0 | 120 | 0 | 0 | 10 | 0 | 137 | 0 | 0 | 0 | 280 | 12 | 2 | 0 | 22 | 0 | 0 | 97 | 0 | 113 | 0 | 0 | 136 | 13 | 348 | 48 | 17 | 0 | 0 | 0 | 0 | 0 | 52 | 9 | 0 | 340 | 24 | 12 | 144 | 0 | 0 | 0 | 14 | 57 | 17 | 230 | 0 | 0 | 430 | 0 | 938 | 0 | 0 | 16 | 0 | 0 | 895 | 0 | 257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 353 | 0 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 1244 | 220 | 0 | 0 | 1 | 37 | 75 | 0 | 0 | 510 | 13 | 307 | 755 | 93 | 0 | 0 | 30 | 0 |  |  |  | 122389735 | 20718720 | 0 | 112398497 | 41193190 | 1353600 | 3458973 | 83520 | 5220319 |  |  | 306816554
[8 empty] | 299430 |  |  |  | 25503 | 299634 |  | 299624 | 299625 | 299739 |  | 299743 |  | 299750 | 299565 | [26 empty] | 399366 | 399587 | [7 empty] | 299667 | 299280 | 299277 |  |  |  | 299773 |  |  |  |  | 399261 | [5 empty] | 299772 |  |  |  | 299338 | [6 empty] | 299755 | [9 empty] | 299472 |  |  | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 | 299566 | 399747 |  | 399277 |  | 399575 | 399337 | 399467 | 399589 | 299230 | 299765 |  | 299674 |  |  |  |  | 399245 |  | 299282 | 399274 |  | 399226 |  | 399630 | 299864 | [6 empty] | 599249 |  | 59039 |  |  |  |  | 599468 |  |  |  | 599230 | [19 empty] | 499698 |  | 499699 |  |  |  | 499700 |  | 499696 | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 |  |  | 599864 | [5 empty] | 599726 |  | 599228 | [9 empty] | 122.3897 | 20.7187 | 0 | 112.3985 | 41.1932 | 1.3536 | 3.459 | 0.08352 | 5.2203
| Minimum Generation |  | 11361 | 6:00
| Highest Generation |  | 13957 | 21:00 | [129 empty] | 0 | [74 empty] | 306.8166
| Day Peak Generation |  | 12799 | 12:00
| Evening Peak Generation |  | 13957 | 21:00 | [204 empty] | 202699852
| HVDC Max Flow |  | 899 | 1:00 | [204 empty] | 202.6999
| HVDC EvPeak Flow |  | 706 | 21:00
| Load factor L.F |  | 91.66% | [168 empty] | 1275.5

## P1
POWER GRID BANGLADESH PLC.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2024-08-29
Till now the maximum generation is : - |  |  |  | 16477 | 21:00 | Hrs on | 2024-04-30
The Summary of Yesterday's |  |  | 2024-08-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12799 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 11578
Evening Peak Generation : |  |  | 13957 | MW Hour : | 21:00 | Available Max Generation : |  | 16447
E.P. Demand (at gen end) : |  |  | 14470 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15000
Maximum Generation : |  |  | 13957 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1447
Total Gen. (MKWH) : |  |  | 306.8166 | System Load Factor : | 91.66% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 592 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2024-08-29
Actual : |  | 108.62 | Ft.(MSL) , | Rule curve : | 98.01 | Ft.( MSL )
Gas Consumed : |  | Total = | 882.49 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 362700197.806
: |  |  | Coal : | 746341507.89 | Oil : | 754162937.08 | Total : | 1863204642.776
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 130 | 3120:00 | 4307.5694 |  |  | 0 | -21.73%
Chittagong Area |  | 0 | 0:00 | 1182.1376 |  |  | 0 | -19.89%
Khulna Area |  | 0 | 0:00 | 1655.4666 |  |  | 0 | -19.5%
Rajshahi Area |  | 0 | 0:00 | 1438.4608 |  |  | 0 | -19.08%
Cumilla Area |  | 20 | 480:00 | 1183.8221 |  |  | 0 | -19.34%
Mymensingh Area |  | 190 | 4560:00 | 880.2349 |  |  | 0 | -18.98%
Sylhet Area |  | 20 | 480:00 | 493.6451 |  |  | 0 | -19.67%
Barisal Area |  | 0 | 0:00 | 411.1693 |  |  | 0 | -18.91%
Rangpur Area |  | 130 | 3120:00 | 804.1802 |  |  | 0 | -18.92%
Total |  | 490 |  | 12356.6859 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,4,5,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restoration |  |  | Description of Event |  |  |  | Description of Event
Time | Time
08:25 | 10:03 | Kushtia 132/33kV S/S T-3 LT Project Work S/D Due to 33 kv incoming -03 High Temperature maintenance work |  |  |  |  | 35.0MW load interrup.
08:35 | 15:14 | Baghabari-Bangura 132 kV Ckt-1 Forced S/D from Bhangura end Due to Baghabari power station Bus maintenance work |  |  |  |  | 15.0MW load interrup.
09:02 | 14:21 | Ramganj 132/33kV S/S Ramgonj-Desh Energy Ckt-02 Scheduled S/D Due to D/S red hot point maintenance
09:22 |  | Hasnabad-Keraniganj 230kV Ckt-1 Scheduled S/D from Keranigonj 230/132/33kV end Due to work at Hasnabad end
09:42 | 10:11 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Distance Relay (P442) relays Due to
Heavy Rain & Thundering and from Sonargaon 132/33kV end showing General Trip, y-ph pick up, Non-dir E/R trip relays
09:45 |  | Hasnabad 230/132kV S/S AUTO TR-3 LT Project Work S/D Due to 132kV bus bar protection work
11:10 | 12:09 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Clamp temperature high
12:56 | 13:29 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Tripped showing earth fault stage 2 relays.
12:56 | 13:28 | Ishurdi 230/132kV S/S 230/132 kV T-02 LT Tripped showing earth fault stage 2 relays.
12:56 | 13:33 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Tripped showing earth fault stage 2 relays.
12:56 | 16:50 | Ishurdi-Pabna 132kV ckt Tripped from Ishurdi 132/33kV end showing earth fault, s phase, zone 2 and zone 3 relays.
13:00 |  | Adani Power Jharkhand Ltd. Unit-2 was sync.
13:01 | 17:28 | BIPTC S/S 20DF24 Tripped showing Tripped by Impedence 21R relays Due to Tripped by Impedence 21R
| 13:11 | Sirajganj-Ullahpara 132KV Ckt-1 is restored.
| 13:28 | Pabna- Shahjadpur 132kV Ckt-1 is restored.
13:53 | 15:26 | Feni 132/33kV S/S T-2(415T) LT Scheduled S/D Due to Due to flooded Condition
| 13:58 | Patuakhali 132/33kV S/S 405T (T-1) HT is restored.
| 15:07 | Baghabari 230/132kV S/S T-2 Bank HT is restored.
| 15:21 | Baghabari 230/132kV S/S T-1 HT is restored.
| 15:24 | Baghabari-Ullahpara 132 kV Ckt-1 is restored.
15:42 | 17:28 | BIPTC S/S 20DF24 Scheduled S/D Due to Impedance 21R trip
| 17:41 | Rajbari 132/33kV S/S 132 kV Bus-I is restored.
21:45 |  | Fenchuganj 132/33KV T2-B transformer was switched on
04:51 |  | Fenchuganj 230/132/33kV S/S TR-02 HT Tripped showing REC 650 relays. |  |  |  |  | 19.0MW load interrup.
05:52 |  | Rajbari 132/33kV S/S 132 kV Bus-I Project Work S/D Due to T-3 gantry tower piling
07:20 |  | Jhenaidah 132/33kV S/S Transformer T-2 LT Scheduled S/D Due to 33 kv isolator hook up with BUS conductor.
07:55 |  | Bogura 132/33kV S/S Transformer-3 LT Forced S/D Due to Red-Hot |  |  |  |  | 17.0MW load interrup.
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  | Network Operation Division

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2024-08-28
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400 | 411 | 9468000
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10301000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve NENP
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 0 | 0 | Reserve NENP
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 936307
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Reserve NENP
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 0 | 0 | Reserve NENP
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7480649
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 25 | 1238976 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 619560 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 1187520 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 949374
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1037966
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 980520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 602800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 11 | 239800 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | 33 kV feeder fault.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 3515236 | Low demand
| Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
32 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 130 | 2980800 | Engine problem
33 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 830880 | Fuel shortage
34 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 85 | 1365120 | Engine problem
35 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2268000
36 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 197292
37 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 635040 | Fuel shortage
38 | Meghnaghat Unique power |  | IPP | 586 | 584 | 0 | 0 | Under S/D
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 583 | 0 | 0 | On test.
| Meghnaghat (Reliance) 718MW CCPP |  | IPP | 718 | 0 | 0 | 222600
| Dhaka area Total |  |  |  | 6217 | 2268 | 47057440
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 107451 | Reserve
41 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 140265
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 61920 | Reserve
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 215 | 5220319
44 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 220 | 5130869
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | PDB | 6*17.5 | 105 | 17 | 303599 | Mengaghat bus section limitation
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 24 | 612192 | Mengaghat bus section limitation
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 777181 | Mengaghat bus section limitation
49 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 0 | 0 | Contract Expired
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 50 | 926400 | Mengaghat bus section limitation
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 0 | 0 | 0 | Contract Expired
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 508800
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26641
54 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 338727 | Mengaghat bus section limitation
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Mengaghat bus section limitation
56 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 56040 | Mengaghat bus section limitation
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 1139520 | 33 kV feeder fault.
58 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 53945 | Mengaghat bus section limitation
59 | Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 398109 | Low demand
60 | SS Power I |  | SS Power | 2*612 | 1224 | 500 | 11110908 | Mengaghat bus section limitation
| Cox's Bazar Wind |  | IPP | 66 | 60 | 0 | 83520
61 | Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 575 | 1150 | 24261818
| Mirsharai 150 MW (Gas) |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 4382 | 2323 | 51258224
| Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 5063000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7436300
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6666000 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 240 | 5919700 | Gas shortage
66 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 666072 | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 55 | 5 | 127200 | Gas shortage
68 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1120030
70 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 712581 | Low demand
71 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 36 | 354496 | Engine problem
72 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 681860 | Machine problem.
73 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2246400 | Low demand
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 60 | 1353600
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 0 | 0 | 0 | Contract Expired
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 434227 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 18 | 361550 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 1515060 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 223440 | Fuel shortage
81 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 80 | 1283520 | Fuel shortage
| Sonagazi 75 MW Solar Plant |  | EGCB | 75 | 75 | 0 | 326391
| Cumilla Area Total |  |  |  | 2917 | 1554 | 36491427
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 17 | 312000 | Gas shortage
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12000
85 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 124 | 2476800 | Fuel shortage
86 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 77 | 1380000 | Fuel shortage
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 323780
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 79680 | Fuel shortage
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 244440 | Fuel shortage
| Mymensingh Area Total |  |  |  | 646 | 218 | 4828700
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 38 | 896000 | Machine problem.
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 121200 | Machine problem.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3481364
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 0 | 0 | Gas shortage
94 | Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
95 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 69552 | Engine problem
96 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 449088 | Gas shortage
97 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 10 | 263040 | Gas shortage
98 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0
99 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 135 | 3260850 | ST Under maint.
100 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
101 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 12 | 276288 | Engine problem
102 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6454500 | FGMO
103 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8618000 | FGMO
104 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 0 | 0 | 0 | Contract Expired
105 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8237100 | FGMO
| Sylhet Area Total |  |  |  | 2417 | 1360 | 32126982
106 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 706 | 20718720
107 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 0 | Reserve NENP
108 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 1920 | Reserve
109 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
110 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 50 | 160000 | Engine problem
111 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 6130080 | Gas shortage
112 | Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
113 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 71 | 492480 | Fuel shortage
114 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
115 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 462240
116 | Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0 | On test.
117 | Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 617*2 | 1234 | 623 | 12836360 | Unit-1 under maint
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3854 | 1700 | 40801800
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 234720 | Low demand
119 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 10 | 9 | 194624
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 2699000 | Machine problem.
| Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1220 | 27724800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5106600
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 46800 | Reserve
124 | Barisal 307 MW |  | IPP | 307*1 | 307 | 307 | 6131000
| Barisal 1 MW Solar Plant |  | BPDB | 1 | 1 | 0 | 2592
| Barisal Area Total |  |  |  | 2236 | 1906 | 42140136
125 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
126 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 170474 | Reserve
127 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 48755 | Reserve
128 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve NENP
129 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 0 | 0 | 0 | Contract Expired
130 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 78783 | Engine problem
131 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
132 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
133 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 154 | 4540027 | Gas shortage
134 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 314 | 8380364 | FGMO
135 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 302230 | Engine problem
| Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
136 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 145908 | Engine problem
137 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
138 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 506720 | Engine problem
| Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 0 | 0 | 0 | Contract Expired
139 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1383744
140 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1339104 | Engine problem
141 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32760
** | Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1511 | 28928520
| Sirajganj 68 MW Solar Park |  | IPP | 68 | 68 | 0 | 338250
| Rajshahi Area Total |  |  |  | 3449 | 2353 | 46195639
142 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 61 | 1405091
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
143 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
144 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
146 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1382457 | Engine problem
147 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51425
148 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 1754496
149 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 215337
150 | Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1330000
| Rangpur Area Total |  |  |  | 950 | 275 | 6138806
| Total |  |  |  | 27068 | 13957 | 307039154
| Eastern Grid Total |  |  |  | 16579 | 7723 | 171762773
| Western Grid Total |  |  |  | 10489 | 6234 | 135276381
| National Grid Total |  |  |  | 27068 | 13957 | 307039154
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-08-2024
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8793.39 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4560.4 | MW
i) Dhaka area |  |  | 4775.29 |  | MW | i) Khulna area |  |  |  | 1684 | MW
ii) Chattogram area |  |  | 1216.1 |  | MW | ii) Barishal area |  |  |  | 433.2 | MW
iii) Cumilla area |  |  | 1144 |  | MW | iii) Rajshahi area |  |  |  | 1562.2 | MW
iv) Mymensingh area |  |  | 1049 |  | MW | iv) Rangpur area |  |  |  | 881 | MW
v) Sylhet area |  |  | 609 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13353.79 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Jamalpur | 112 | 19:00 | 133 | Rahim | 44 | 10:00
2 | AKSML | 99 | 00:00 | 68 | Jashore | 113 | 13:00 | 134 | Rajbari | 82 | 19:30
3 | Aftabnagar | 34 | 19:00 | 69 | Jhenaidah | 127 | 19:00 | 135 | Rajendrapur | 116 | 19:00
4 | Agargaon | 113 | 13:00 | 70 | Joydebpur | 202 | 19:30 | 136 | Rajshahi | 145 | 21:00
5 | Agrabad | 88 | 17:00 | 71 | Joypurhat | 72 | 22:00 | 137 | Rajshahi-230 | 67 | 22:00
6 | Amnura | 67 | 22:00 | 72 | Juldah | 19 | 18:30 | 138 | Ramganj | 112 | 15:00
7 | Ashuganj | 90 | 03:00 | 73 | KSRM | 31 | 12:00 | 139 | Rampur | 36 | 18:30
8 | BIPTC | N/A | N/A | 74 | Kabirpur | 296 | 20:00 | 140 | Rangamati | 19 | 18:30
9 | BSRM | 137 | 17:00 | 75 | Kachua | 72 | 19:30 | 141 | Rangpur | 146 | 13:00
10 | Bagerhat | 86 | 20:00 | 76 | Kallyanpur | 111 | 23:00 | 142 | Ruppur | 7 | 10:00
11 | Bakulia | 92 | 19:30 | 77 | Kalurghat | 40 | 13:00 | 143 | SSM | 0 | 00:00
12 | Banani | 58.4 | 13:00 | 78 | Kamrangirchar | 55.2 | 13:00 | 144 | Saidpur | 120 | 19:00
13 | Bangabhaban | 21 | 10:00 | 79 | Kaptai | N/A | N/A | 145 | Satkhira | 123 | 22:00
14 | Barapukuria | 53 | 12:00 | 80 | Kazla | 110 | 13:00 | 146 | Satmasjid | 97 | 13:00
15 | Barguna | 20 | 22:00 | 81 | Keranigonj | 72 | 19:30 | 147 | Savar | 215 | 15:00
16 | Barishal | 101 | 13:00 | 82 | Khagrachori | 34 | 19:00 | 148 | SevenRings | 13.92 | 17:00
17 | Barishal-230 | 88 | 20:00 | 83 | Khulna | 69 | 19:30 | 149 | ShahCement | 31 | 18:00
18 | Baroaulia | 62 | 09:00 | 84 | Khulshi | 164 | 14:00 | 150 | Shahjadpur | 83 | 18:30
19 | Baroirhat | 44 | 19:00 | 85 | Kishoreganj | 144 | 01:00 | 151 | Shahjibazar | 113 | 18:30
20 | Bashundhara | 153 | 13:00 | 86 | Kodda | 193 | 18:30 | 152 | Shahmirpur | 49 | 01:00
21 | BashundharaCement | 7 | 13:00 | 87 | Kulaura | 56 | 18:30 | 153 | Shariatpur | 80 | 00:00
22 | Beanibazar | 82 | 20:00 | 88 | Kurigram | 62 | 14:00 | 154 | Sherpur | 122 | 00:00
23 | Benapole | 76 | 21:00 | 89 | Kushtia | 134 | 23:00 | 155 | Shikalbaha | 21 | 19:30
24 | Bhaluka | 132 | 14:00 | 90 | Lalbag | 81 | 13:00 | 156 | Shikalbaha-230 | N/A | N/A
25 | Bhandaria | 50 | 22:00 | 91 | Lalmonirhat | 52 | 00:00 | 157 | Shitalakhya | 79.9 | 12:00
26 | Bhangura | 41 | 19:00 | 92 | MI_Cement | 16.5 | 13:00 | 158 | Sholosohor | 43 | 18:30
27 | Bheramara(GK) | 64 | 19:30 | 93 | Madanganj | 32 | 23:00 | 159 | Shyampur | 144 | 12:00
28 | Bhulta | 239 | 22:00 | 94 | Madaripur | 102 | 22:00 | 160 | Siddhirganj | 133 | 11:00
29 | Bog-Sherpur | 68 | 19:00 | 95 | Madartek | 75.16 | 23:00 | 161 | Sirajganj | 122 | 21:00
30 | Bogura | 175 | 20:00 | 96 | Madunaghat | 54 | 19:00 | 162 | Sonargaon | 94 | 12:00
31 | Borhanuddin | 79 | 00:00 | 97 | Magura | 67 | 19:00 | 163 | Sreemongol | 71 | 19:00
32 | Brahmanbaria | 159 | 00:00 | 98 | Mahasthangarh | 80 | 00:00 | 164 | Sreepur | 115 | 19:00
33 | Cantonment | 109 | 13:00 | 99 | Manikganj | 116 | 00:00 | 165 | Srinagar | 43.87 | 22:00
34 | Chandpur | 68 | 23:00 | 100 | Maniknagar | 61 | 13:00 | 166 | Sunamganj | 60 | 19:00
35 | Chandraghona | 35 | 19:00 | 101 | Matarbari | 45 | 19:00 | 167 | Sylhet | 48 | 19:00
36 | Chapai | 63 | 19:00 | 102 | Matuail | 60 | 10:00 | 168 | Sylhet-132 | 127 | 19:00
37 | Charsaidpur | 29 | 15:00 | 103 | Millgate | 120 | 15:00 | 169 | TK | 30.6 | 19:00
38 | Chauddagram | 56 | 16:00 | 104 | Mirpur | 135 | 12:00 | 170 | Tangail | 176 | 19:30
39 | Chhatak | 38 | 22:00 | 105 | Mirsorai | 5 | 00:00 | 171 | Thakurgaon | 104 | 00:00
40 | Chowmuhani | 152 | 18:30 | 106 | Mirzapur | 46 | 00:00 | 172 | Tongi | 146 | 19:30
41 | Chuadanga | 117 | 19:00 | 107 | Mithapukur | 62 | 20:00 | 173 | Ullahpara | 28 | 19:00
42 | Coxsbazar | 109 | 19:00 | 108 | Modern | 0 | 00:00 | 174 | Ullon | 54 | 19:00
43 | Cumilla(N) | 166 | 20:00 | 109 | Mogbazar | 124.4 | 16:00 | 175 | Uttara | 65 | 15:00
44 | Cumilla(S) | 131 | 19:30 | 110 | Mongla | 29 | 16:00 | 176 | UttaraNew | 54 | 13:00
45 | Daudkandi | 145 | 19:00 | 111 | Motijheel | 37 | 13:00 | 177 | Zigatola | 93 | 11:00
46 | Dhaka | 50 | 12:00 | 112 | Munshiganj | 109 | 00:00
47 | Dhamrai | 130 | 19:00 | 113 | Mymensingh | 231 | 01:00
48 | Dhanmondi | 138 | 13:00 | 114 | Naogaon | 132 | 21:00
49 | Dohazari | 90 | 19:00 | 115 | Narail | 58 | 19:00
50 | Faridpur | 160 | 19:00 | 116 | Narinda | 72 | 13:00
51 | Fatullah | 91 | 11:00 | 117 | Narshingdi | 164 | 00:00
52 | Fenchuganj | 40 | 23:00 | 118 | Natore | 154 | 22:00
53 | Feni | 79 | 22:00 | 119 | Nawabganj | 46.6 | 22:00
54 | GPH | 10 | 00:00 | 120 | Netrakona | 101 | 21:00
55 | Ghatail | 48 | 00:00 | 121 | New | 37.4 | 12:00
56 | Ghorashal | 60 | 19:30 | 122 | Niamatpur | 75 | 22:00
57 | Goalpara | 34 | 13:00 | 123 | Noapara | 56 | 19:00

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2024-08-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
| Aminbazar | 385 | 18:00 | 373 | 22:00 | Kaliakoir | 370 | 17:00 | 357 | 04:00
| Ashuganj | 402 | 18:07 | 390 | 3:18 | Madunaghat | 396 | 18:00 | 384 | 04:00
| Bhulta | 390 | 00:00 | 380 | 02:00 | Meghnaghat | 376 | 18:00 | 368 | 00:00
| Bibiana | 394 | 18:00 | 385 | 05:00 | Payra | 410 | 17:00 | 401 | 23:00
| BIPTC | 402 | 04:00 | 394 | 13:00 | Rahanpur | 403 | 14:00 | 376 | 01:00
| Bogura | 390 | 11:00 | 353 | 02:00 | Rampal | 400 | 18:00 | 385 | 23:00
| Gopalganj | 398 | 15:00 | 383 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 228 | 18:00 | 220 | 08:00 | Haripur | 228 | 18:00 | 221 | 00:00
| AKSML | 233 | 19:00 | 223 | 04:00 | Hasnabad | 228 | 15:00 | 222 | 00:00
| Aminbazar | 227 | 17:00 | 221 | 00:00 | Hathazari | 235 | 11:00 | 20 | 00:00
| Ashuganj | 231 | 13:00 | 224 | 00:00 | Ishurdi | 234 | 11:00 | 223 | 13:00
| Ashuganj-400 | 231 | 13:00 | 224 | 00:00 | Jhenaidah | 227 | 09:00 | 217 | 01:00
| Baghabari | 233 | 10:00 | 221 | 01:00 | Kaliakoir | 229 | 19:00 | 221 | 03:00
| Barapukuria | 210 | 11:00 | 192 | 02:00 | Keranigonj | 227 | 18:00 | 220 | 04:00
| Barapukuria-230 | 210 | 11:00 | 192 | 02:00 | Khulna(S) | 228 | 18:00 | 218 | 02:00
| Barishal | 236 | 18:00 | 229 | 22:00 | Madunaghat | 234 | 18:00 | 227 | 04:00
| Bheramara | 233 | 13:00 | 223 | 01:00 | Maniknagar | 227 | 18:00 | 222 | 12:00
| Bhulta | 229 | 00:00 | 222 | 15:00 | Meghnaghat | 232 | 15:00 | 230 | 00:00
| Bibiana | 225 | 13:00 | 218 | 00:00 | Meghnaghat-400 | 232 | 18:00 | 225 | 00:00
| BIPTC | 237 | 13:00 | 222 | 01:00 | Mirsorai | 232 | 14:00 | 222 | 00:00
| Bogura | 223 | 12:00 | 209 | 04:00 | Rajshahi | 233 | 13:00 | 220 | 01:00
| Bogura-400 | 224 | 14:00 | 205 | 02:00 | Rampal | 229 | 18:00 | 219 | 02:00
| Borhanuddin | 241 | 18:00 | 236 | 22:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 232 | 18:00 | 222 | 03:00 | Rampura | 226 | 18:00 | 221 | 12:00
| Cumilla(N) | 229 | 18:00 | 220 | 00:00 | Shikalbaha | 234 | 18:00 | 224 | 03:00
| Faridpur | 235 | 18:00 | 225 | 22:00 | Shyampur | 229 | 18:00 | 221 | 08:00
| Fenchuganj | 226 | 14:00 | 221 | 02:00 | Siddhirganj | 230 | 18:00 | 222 | 17:00
| Ghorashal | 230 | 00:00 | 230 | 00:00 | Sirajgonj | 236 | 13:00 | 226 | 01:00
| Ghorashal-230 | 227 | 18:00 | 220 | 04:00 | Sreepur | 227 | 11:00 | 220 | 00:00
| Gopalganj | 235 | 18:00 | 227 | 21:00 | Tongi | 227 | 13:00 | 220 | 01:00
| GPH | 233 | 18:00 | 223 | 02:00
| 132 KV | KV |  | KV |  | 132 KV | KV |  | KV
| Aftabnagar | 131 | 01:00 | 126 | 12:00 | Kushtia | 134 | 09:00 | 128 | 00:00
| Agargaon | 132 | 18:00 | 127 | 15:00 | Lalbag | 132 | 18:00 | 128 | 00:00
| Agrabad | 134 | 18:30 | 129 | 02:00 | Lalmonirhat | 125 | 18:00 | 108 | 01:00
| AKS | 132 | 18:00 | 126 | 01:00 | Madanganj | 131 | 18:00 | 125 | 07:00
| Aminbazar | 137 | 17:00 | 132 | 02:00 | Madaripur | 131 | 05:00 | 127 | 22:00
| Amnura | 136 | 18:30 | 119 | 20:00 | Madartek | 131 | 03:00 | 126 | 12:00
| Ashuganj | 135 | 09:00 | 133 | 00:00 | Madunaghat | 135 | 13:00 | 130 | 08:00
| Bagerhat | 131 | 18:00 | 123 | 01:00 | Magura | 135 | 18:00 | 126 | 02:00
| Bakulia | 134 | 11:00 | 129 | 04:00 | Mahasthangarh | 130 | 11:00 | 117 | 01:00
| Banani | 131 | 06:00 | 125 | 15:00 | Manikganj | 127 | 19:00 | 118 | 00:00
| Bangabhaban | 127 | 01:00 | 123 | 15:00 | Maniknagar | 127 | 03:00 | 123 | 13:00
| Barapukuria | 130 | 11:00 | 119 | 01:00 | Matarbari | 126 | 18:00 | 116 | 21:00
| Barguna | 136 | 18:00 | 129 | 22:00 | Matuail | 130 | 18:00 | 126 | 03:00
| Barishal | 133 | 18:00 | 129 | 22:00 | Millgate | 129 | 13:00 | 125 | 09:00
| Barishal-230 | 133 | 18:00 | 128 | 21:00 | Mirpur | 136 | 18:00 | 131 | 03:00
| Baroaulia | 135 | 18:00 | 130 | 07:00 | Mirzapur | 126 | 19:00 | 116 | 05:00
| Baroirhat | 130 | 17:00 | 120 | 01:00 | Mithapukur | 127 | 11:00 | 115 | 01:00
| Bashundhara | 131 | 01:00 | 124 | 19:30 | MI_Cement | 132 | 18:00 | 126 | 08:00
| BashundharaCement | 131 | 18:00 | 125 | 07:00 | Modern | 133 | 11:00 | 128 | 04:00
| Beanibazar | 121 | 12:00 | 113 | 23:00 | Mogbazar | 135 | 01:00 | 126 | 15:00
| Benapole | 131 | 18:00 | 122 | 00:00 | Mongla | 132 | 18:00 | 123 | 01:00
| Bhaluka | 124 | 11:00 | 118 | 00:00 | Motijheel | 127 | 01:00 | 123 | 15:00
| Bhandaria | 130 | 18:00 | 120 | 22:00 | Munshiganj | 131 | 18:00 | 126 | 04:00
| Bhangura | 134 | 18:00 | 127 | 01:00 | Mymensingh | 130 | 16:00 | 11 | 19:30
| Bheramara | 135 | 18:00 | 130 | 00:00 | Naogaon | 130 | 18:00 | 113 | 01:00
| Bheramara(GK) | 135 | 13:00 | 130 | 00:00 | Narail | 135 | 09:00 | 124 | 19:00
| Bhulta | 121 | 18:00 | 115 | 05:00 | Narinda | 127 | 03:00 | 123 | 13:00
| Bog-Sherpur | 132 | 18:00 | 116 | 01:00 | Narshingdi | 123 | 18:00 | 115 | 23:00
| Bogura | 134 | 18:00 | 122 | 04:00 | Natore | 133 | 18:00 | 124 | 01:00
| Bogura-230 | 135 | 17:00 | 123 | 04:00 | Nawabganj | 132 | 18:00 | 127 | 00:00
| Brahmanbaria | 128 | 18:00 | 121 | 00:00 | Netrakona | 130 | 16:00 | 116 | 04:00
| Cantonment | 131 | 18:00 | 127 | 15:00 | New | 131 | 13:00 | 126 | 09:00
| Chandpur | 132 | 18:00 | 117 | 04:00 | Niamatpur | 134 | 11:00 | 124 | 01:00
| Chandraghona | 135 | 11:00 | 130 | 03:00 | Noapara | 133 | 18:00 | 125 | 19:00
| Chapai | 131 | 14:00 | 120 | 21:00 | Pabna | 133 | 18:00 | 119 | 15:00
| Charsaidpur | 132 | 18:00 | 126 | 04:00 | Palashbari | 125 | 11:00 | 113 | 01:00
| Chauddagram | 130 | 18:00 | 121 | 02:00 | Panchagarh | 132 | 21:00 | 116 | 05:00
| Chhatak | 121 | 10:00 | 114 | 20:00 | Patuakhali | 135 | 18:00 | 130 | 22:00
| Chowmuhani | 127 | 18:00 | 115 | 00:00 | Payra | 137 | 18:00 | 133 | 02:00
| Chuadanga | 129 | 18:00 | 116 | 19:00 | PHP | 129 | 18:00 | 119 | 04:00
| Coxsbazar | 126 | 12:00 | 116 | 22:00 | Postogola | 133 | 18:00 | 128 | 23:00
| Cumilla(N) | 133 | 18:00 | 126 | 00:00 | Purbachal | 131 | 02:00 | 124 | 09:00
| Cumilla(S) | 133 | 18:00 | 124 | 00:00 | Purbasadipur | 126 | 18:00 | 111 | 03:00
| Daudkandi | 138 | 23:00 | 121 | 00:00 | Rahanpur | 136 | 14:00 | 127 | 01:00
| Dhaka | 131 | 01:00 | 126 | 15:00 | Rahim | 129 | 18:00 | 126 | 08:00
| Dhamrai | 130 | 18:00 | 125 | 04:00 | Rajbari | 131 | 18:00 | 126 | 00:00
| Dhanmondi | 132 | 03:00 | 126 | 15:00 | Rajendrapur | 128 | 19:30 | 119 | 04:00
| Dohazari | 132 | 18:00 | 124 | 23:00 | Rajshahi | 133 | 18:00 | 128 | 00:00
| Faridpur | 131 | 18:00 | 126 | 23:00 | Rajshahi-230 | 133 | 10:00 | 115 | 21:00
| Fatullah | 132 | 18:00 | 128 | 00:00 | Ramganj | 128 | 19:00 | 114 | 04:00
| Fenchuganj | 130 | 18:00 | 126 | 00:00 | Rampur | 134 | 14:00 | 128 | 03:00
| Feni | 129 | 19:30 | 121 | 00:00 | Rampura | 131 | 01:00 | 126 | 12:00
| Ghatail | 126 | 16:00 | 118 | 00:00 | Rangamati | 134 | 11:00 | 130 | 03:00
| Ghorashal | 133 | 03:00 | 131 | 00:00 | Rangpur | 124 | 08:00 | 114 | 00:00
| Goalpara | 134 | 18:00 | 126 | 02:00 | Ruppur | 136 | 18:00 | 131 | 00:00
| Gollamari | 134 | 18:00 | 128 | 00:00 | Saidpur | 124 | 06:00 | 113 | 01:00
| Gopalganj | 132 | 18:00 | 126 | 00:00 | Satkhira | 131 | 18:00 | 122 | 19:00
| Gopalganj-400 | 133 | 18:00 | 127 | 02:00 | Satmasjid | 131 | 18:00 | 127 | 15:00
| Gulshan | 131 | 06:00 | 126 | 12:00 | Savar | 136 | 18:00 | 130 | 03:00
| Halishahar | 134 | 13:00 | 129 | 07:00 | SevenRings | 135 | 13:00 | 131 | 00:00
| Haripur | 130 | 18:00 | 126 | 02:00 | ShahCement | 132 | 18:00 | 126 | 04:00
| HaripurSBU | 129 | 18:00 | 126 | 08:00 | Shahjadpur | 137 | 10:00 | 120 | 13:00
| Hasnabad | 133 | 18:00 | 129 | 10:00 | Shahjibazar | 125 | 09:00 | 120 | 00:00
| Hathazari | 136 | 11:00 | 133 | 00:00 | Shahmirpur | 135 | 13:00 | 128 | 22:00
| Ishurdi | 137 | 18:00 | 130 | 01:00 | Shariatpur | 132 | 18:00 | 125 | 01:00
| Jaldhaka | 124 | 18:00 | 110 | 01:00 | Sherpur | 131 | 19:00 | 118 | 02:00
| Jamalpur | 135 | 17:00 | 122 | 03:00 | Shikalbaha | 123 | 13:00 | 118 | 22:00
| Jashore | 131 | 18:00 | 123 | 00:00 | Shikalbaha-230 | 136 | 19:00 | 129 | 02:00
| Jhenaidah | 135 | 18:00 | 126 | 19:00 | Shitalakhya | 132 | 18:00 | 126 | 08:00
| Jhenaidah-230 | 135 | 10:00 | 127 | 00:00 | Sholosohor | 134 | 18:00 | 129 | 02:00
| Joydebpur | 130 | 13:00 | 123 | 16:00 | Shyampur | 133 | 18:30 | 127 | 07:00
| Joypurhat | 128 | 18:00 | 114 | 02:00 | Shyampur-230 | 132 | 18:00 | 127 | 04:00
| Juldah | 135 | 00:00 | 128 | 01:00 | Siddhirganj | 130 | 18:00 | 126 | 08:00
| Kabirpur | 129 | 19:00 | 121 | 03:00 | Sirajganj | 132 | 18:00 | 113 | 02:00
| Kachua | 132 | 19:30 | 119 | 03:00 | Sonargaon | 130 | 18:00 | 123 | 07:00
| Kaliakoir | 132 | 18:30 | 122 | 05:00 | Sreemongol | 125 | 09:00 | 120 | 00:00
| Kallyanpur | 129 | 05:00 | 125 | 00:00 | Sreepur | 128 | 11:00 | 122 | 22:00
| Kalurghat | 135 | 18:00 | 129 | 04:00 | Srinagar | 132 | 18:00 | 128 | 00:00
| Kamrangirchar | 133 | 18:00 | 125 | 00:00 | SSM | 139 | 18:00 | 132 | 07:00
| Kaptai | 138 | 18:00 | 135 | 1:00 | Sunamganj | 119 | 06:00 | 112 | 20:00
| Kazla | 128 | 07:00 | 123 | 13:00 | Sylhet | 123 | 09:00 | 119 | 00:00
| Keranigonj | 133 | 18:00 | 128 | 08:00 | Sylhet-132 | 123 | 08:00 | 120 | 00:00
| Khagrachori | 133 | 13:00 | 128 | 03:00 | Tangail | 126 | 17:00 | 114 | 05:00
| Khulna | 133 | 10:00 | 127 | 00:00 | Thakurgaon | 129 | 21:00 | 114 | 02:00
| Khulna(S) | 135 | 18:00 | 128 | 02:00 | TK | 134 | 11:00 | 130 | 05:00
| Khulshi | 133 | 18:00 | 128 | 04:00 | Tongi | 133 | 00:00 | 127 | 18:30
| Kishoreganj | 127 | 10:00 | 121 | 00:00 | Ullahpara | 134 | 05:00 | 116 | 08:00
| Kodda | 130 | 13:00 | 121 | 11:00 | Ullon | 131 | 01:00 | 126 | 12:00
| KSRM | 136 | 13:00 | 130 | 01:00 | Uttara | 134 | 17:00 | 130 | 15:00
| Kulaura | 127 | 05:00 | 124 | 00:00 | UttaraNew | 135 | 18:00 | 131 | 04:00
| Kurigram | 126 | 19:00 | 114 | 04:00 | Zigatola | 133 | 18:00 | 127 | 00:00

## L-Curve
Date | 2024-08-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 830 | 7353 | 6272 | 13625 |  |  |  | QF-LDC-11
0:30 | 850 | 7252 | 5963.5 | 13215.5 | Date: | 2024-08-28
1:00 | 870 | 7151 | 5655 | 12806
1:30 | 924 | 6855 | 5623 | 12478
2:00 | 978 | 6559 | 5591 | 12150
2:30 | 978 | 6566.5 | 5568 | 12134.5 | [5 empty] | Gen. at Eve. Peak | 13957 | 13957 MW (21:00 )
3:00 | 978 | 6574 | 5545 | 12119 | [6 empty] | 21:00
3:30 | 999 | 6452.5 | 5503 | 11955.5 | [5 empty] | Gen. at Day Peak | 12799 | 12799 MW (12:00 )
4:00 | 1020 | 6331 | 5461 | 11792 | [6 empty] | 12:00
4:30 | 985 | 6341.5 | 5379.5 | 11721 | [5 empty] | Highest Generation | 13957
5:00 | 950 | 6352 | 5298 | 11650 | [6 empty] | 21:00
5:30 | 917 | 6301.5 | 5204 | 11505.5
6:00 | 884 | 6251 | 5110 | 11361
6:30 | 825 | 6272 | 5091.5 | 11363.5
7:00 | 766 | 6293 | 5073 | 11366
7:30 | 735 | 6428.5 | 5064.5 | 11493
8:00 | 704 | 6564 | 5056 | 11620
8:30 | 727 | 6711 | 5004.5 | 11715.5
9:00 | 750 | 6858 | 4953 | 11811
9:30 | 796 | 6903 | 4970.5 | 11873.5
10:00 | 842 | 6948 | 4988 | 11936
10:30 | 821 | 7092 | 5018.5 | 12110.5
11:00 | 800 | 7236 | 5049 | 12285
11:30 | 825 | 7374 | 5168 | 12542
12:00 | 850 | 7512 | 5287 | 12799
12:30 | 840 | 7486 | 5341.5 | 12827.5
13:00 | 830 | 7460 | 5396 | 12856
13:30 | 852 | 7455.5 | 5428.5 | 12884
14:00 | 874 | 7451 | 5461 | 12912
14:30 | 950 | 7425 | 5536.5 | 12961.5
15:00 | 1026 | 7399 | 5612 | 13011
15:30 | 1005 | 7317.5 | 5573 | 12890.5
16:00 | 984 | 7236 | 5534 | 12770
16:30 | 996 | 7167.5 | 5403.5 | 12571
17:00 | 1008 | 7099 | 5273 | 12372
17:30 | 1057 | 7043.5 | 5178 | 12221.5
18:00 | 1106 | 6988 | 5083 | 12071
18:30 | 934 | 7535 | 5425 | 12960
19:00 | 762 | 8082 | 5767 | 13849
19:30 | 668 | 7846 | 5999 | 13845
20:00 | 592 | 7868 | 5990 | 13858 |  |  |  | Executive Engineer
20:30 | 643 | 7795.5 | 6112 | 13907.5 |  |  |  | Network Operation Division
21:00 | 694 | 7723 | 6234 | 13957
21:30 | 687 | 7610 | 6256.5 | 13866.5
22:00 | 680 | 7497 | 6279 | 13776 |  |  |  |  | Page 6 of 7
22:30 | 752 | 7436.5 | 6314.5 | 13751
23:00 | 824 | 7376 | 6350 | 13726
23:30 | 827 | 7364.5 | 6311 | 13675.5
24:00 | 830 | 7353 | 6272 | 13625
13957 MW (21:00 )
12799 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2024-08-28 |  | Energy |  | 307039154
[15 empty] | 2024-08-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3593 | 706 | 1642 | 0 | 1866 | 5330 | 214 | 0 | 198 | 58 | 0 | 0 | 501.375
0:30 | 3535 | 802.5 | 1570 | 0 | 1744.5 | 5128.5 | 215.5 | 0 | 131 | 58 | 0 | 2 | 450.76 |  |  | Date: | 44070
1:00 | 3477 | 899 | 1498 | 0 | 1623 | 4927 | 217 | 0 | 64 | 58 | 0 | 4 | 400.145
1:30 | 3479 | 899 | 1486.5 | 0 | 1286 | 4968 | 217 | 0 | 40 | 57 | 0 | 3.5 | 391.0725 | [9 empty] | Total Energy | 307.0392 | 307.0392 | Total Energy Gen 307.039 MKWHr Energy Not Served 8.896 MKWHr Energy Requirement 315.935 MKWHr
2:00 | 3481 | 899 | 1475 | 0 | 949 | 5009 | 217 | 0 | 16 | 56 | 0 | 3 | 382 | [9 empty] | Energy not Served | 8.8962 | 8.8962
2:30 | 3487 | 898.5 | 1464 | 0 | 918.5 | 5028.5 | 217 | 0 | 16 | 56 | 0 | 3 | 372.9275 | [9 empty] | Energy Requirement | 315.9353 | 315.9353
3:00 | 3493 | 898 | 1453 | 0 | 888 | 5048 | 217 | 0 | 16 | 56 | 0 | 3 | 363.855
3:30 | 3497 | 898 | 1494.5 | 0 | 762 | 4967 | 217 | 0 | 16 | 55 | 0 | 3 | 364.81 | [8 empty] | Shortage
4:00 | 3501 | 898 | 1536 | 0 | 636 | 4886 | 217 | 0 | 16 | 54 | 0 | 3 | 365.765
4:30 | 3504.5 | 898 | 1528.5 | 0 | 603 | 4849.5 | 217 | 0 | 16 | 57 | 0 | 2.5 | 361.945
5:00 | 3508 | 898 | 1521 | 0 | 570 | 4813 | 217 | 0 | 16 | 60 | 0 | 2 | 358.125
5:30 | 3554 | 898 | 1533.5 | 0 | 533.5 | 4645 | 217 | 0 | 16 | 58 | 4 | 1.5 | 364.81
6:00 | 3600 | 898 | 1546 | 0 | 497 | 4477 | 217 | 0 | 16 | 56 | 8 | 1 | 371.495
6:30 | 3646 | 898 | 1571 | 0 | 452.5 | 4422.5 | 217 | 0 | 16 | 54 | 53.5 | 0.5 | 345.2325 | [7 empty] | Coal
7:00 | 3692 | 898 | 1596 | 0 | 408 | 4368 | 217 | 0 | 16 | 52 | 99 | 0 | 318.97
7:30 | 3638 | 897 | 1600 | 0 | 460.5 | 4451.5 | 217 | 0 | 16 | 53 | 149.5 | 0.5 | 350.485 | [6 empty] | Oil
8:00 | 3584 | 896 | 1604 | 0 | 513 | 4535 | 217 | 0 | 16 | 54 | 200 | 1 | 382
8:30 | 3603 | 896 | 1491.5 | 0 | 765.5 | 4398 | 217 | 0 | 24.5 | 50 | 269.5 | 0.5 | 400.6225
9:00 | 3622 | 896 | 1379 | 0 | 1018 | 4261 | 217 | 0 | 33 | 46 | 339 | 0 | 419.245
9:30 | 3610.5 | 895.5 | 1318 | 0 | 1181.5 | 4194.5 | 216.5 | 0 | 68.5 | 51 | 337.5 | 0 | 431.1225
10:00 | 3599 | 895 | 1257 | 0 | 1345 | 4128 | 216 | 0 | 104 | 56 | 336 | 0 | 443
10:30 | 3589.5 | 895.5 | 1265 | 0 | 1503.5 | 4065.5 | 216.5 | 0 | 149.5 | 56 | 369.5 | 0 | 372
11:00 | 3580 | 896 | 1273 | 0 | 1662 | 4003 | 217 | 0 | 195 | 56 | 403 | 0 | 301
11:30 | 3578.5 | 896 | 1337.5 | 0 | 1782.5 | 4013 | 217 | 0 | 224 | 58 | 435.5 | 0 | 256
12:00 | 3577 | 896 | 1402 | 0 | 1903 | 4023 | 217 | 0 | 253 | 60 | 468 | 0 | 211
12:30 | 3552.5 | 896 | 1396.5 | 0 | 1957 | 4008.5 | 217.5 | 0 | 266 | 60 | 473.5 | 0 | 243.02
13:00 | 3528 | 896 | 1391 | 0 | 2011 | 3994 | 218 | 0 | 279 | 60 | 479 | 0 | 275.04
13:30 | 3528 | 896 | 1391 | 0 | 2011 | 3994 | 218 | 0 | 279 | 60 | 479 | 0 | 275.04
14:00 | 3528 | 896 | 1391 | 0 | 2011 | 3994 | 218 | 0 | 279 | 60 | 479 | 0 | 275.04
14:30 | 3525 | 895.5 | 1455 | 0 | 1956.5 | 4128 | 217 | 0 | 277 | 61 | 414.5 | 4 | 275.5175
15:00 | 3522 | 895 | 1519 | 0 | 1902 | 4262 | 216 | 0 | 275 | 62 | 350 | 8 | 275.995
15:30 | 3490.5 | 895.5 | 1514 | 0 | 1847.5 | 4305 | 216 | 0 | 287.5 | 58 | 262.5 | 14 | 295.5725
16:00 | 3459 | 896 | 1509 | 0 | 1793 | 4348 | 216 | 0 | 300 | 54 | 175 | 20 | 315.15
16:30 | 3440.5 | 896 | 1395.5 | 0 | 1810 | 4312.5 | 216 | 0 | 304.5 | 53 | 123.5 | 19.5 | 323.745
17:00 | 3422 | 896 | 1282 | 0 | 1827 | 4277 | 216 | 0 | 309 | 52 | 72 | 19 | 332.34
17:30 | 3354 | 895.5 | 1257 | 0 | 1875 | 4190.5 | 215.5 | 0 | 321.5 | 52 | 44.5 | 16 | 308.9425
18:00 | 3286 | 895 | 1232 | 0 | 1923 | 4104 | 215 | 0 | 334 | 52 | 17 | 13 | 285.545
18:30 | 3412.5 | 895.5 | 1370.5 | 0 | 2126.5 | 4400 | 215 | 0 | 467.5 | 55 | 8.5 | 9 | 372.45
19:00 | 3539 | 896 | 1509 | 0 | 2330 | 4696 | 215 | 0 | 601 | 58 | 0 | 5 | 459.355
19:30 | 3416 | 895 | 1390 | 0 | 2396 | 4996 | 215 | 0 | 477 | 58 | 0 | 2 | 474.1575
20:00 | 3487 | 706 | 1508 | 0 | 2272 | 5132 | 215 | 0 | 479 | 56 | 0 | 3 | 488.96
20:30 | 3532.5 | 706 | 1525.5 | 0 | 2153 | 5252 | 215 | 0 | 464 | 58 | 0 | 1.5 | 489.4375
21:00 | 3578 | 706 | 1543 | 0 | 2034 | 5372 | 215 | 0 | 449 | 60 | 0 | 0 | 489.915
21:30 | 3628.5 | 706 | 1565 | 0 | 1944.5 | 5353.5 | 214.5 | 0 | 395.5 | 59 | 0 | 0 | 495.1675
22:00 | 3679 | 706 | 1587 | 0 | 1855 | 5335 | 214 | 0 | 342 | 58 | 0 | 0 | 500.42
22:30 | 3651.5 | 706 | 1629 | 0 | 1843 | 5330 | 214 | 0 | 316.5 | 59 | 0 | 0 | 500.42
23:00 | 3624 | 706 | 1671 | 0 | 1831 | 5325 | 214 | 0 | 291 | 60 | 0 | 0 | 500.42
23:30 | 3608.5 | 706 | 1656.5 | 0 | 1848.5 | 5327.5 | 214 | 0 | 244.5 | 59 | 0 | 0 | 500.8975 |  |  | Max Temp. in Dhaka |  | 31.6°C
24:00 | 3593 | 706 | 1642 | 0 | 1866 | 5330 | 214 | 0 | 198 | 58 | 0 | 0 | 501.375
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 307.039 MKWHr Energy Not Served 8.896 MKWHr Energy Requirement 315.935 MKWHr
Shortage
Note on W13: Author:

## Generation
2024-08-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 136 | 137 | 137 | 138 | 136 | 136 | 136 | 136 | 135 |  | 135 | 135 | 135 | 135 | 134 | 134 | 134 | 3280319
2 | Karnaphuli Hydro PP Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1940000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 0 | [8 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 10 | 16 |  | 18 | 8 | [5 empty] | 107451
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 7 | 9 | 8 | 20 | 14 | 20 | 20 | 17 | 14 | 9 | 4 | 0 | [8 empty] | 140265
6 | Sikalbaha 225MW CCPP (Gas) | 215 | 215 | 219 | 220 | 221 | 220 | 219 | 220 | 221 | 221 | 217 | 218 | 218 | 216 | 214 | 214 | 213 | 220 |  | 219 | 220 | 220 | 220 | 220 | 220 | 220 | 5130869
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [10 empty] | 34 | 77 | 82 | 82 | 82 | 82 | 82 | 82 |  | 82 | 34 | 34 | 34 | 34 | 16 |  | 777181
12 | Hathazari 100 MW peaking PP | [9 empty] | 36 | 64 | 66 | 65 | 64 | 55 | 55 | 55 | 70 |  | 70 | 24 | 24 | 24 |  |  |  | 612192
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 0 | [6 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 303599
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [10 empty] | 29 | 36 | 36 | 28 | 30 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 |  |  |  | 354496
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 331 | 333 | 280 | 250 |  | 290 | 270 | 335 | 335 | 332 | 334 | 335 | 7480649
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 30 | 30 | 0 |  |  |  |  | 19 | 110 | 156 | 206 | 210 | 210 | 208 | 208 | 228 | 230 |  | 228 | 235 | 242 | 195 | 195 | 200 | 265 | 3515236
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 273 | 360 | 436 | 516 | 585 | 612 | 612 | 612 | 501 | 450 | 420 | 420 | 408 | 415 | 420 | 420 | 420 | 420 |  | 480 | 500 | 505 | 500 | 500 | 500 | 500 | 11110908
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 35 | 38 | 35 | 38 | 38 | 20 | 20 | 10 | 10 | 10 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 666072
33 | Ashuganj 225 MW CCPP | 216 | 213 | 216 | 214 | 215 | 213 | 190 | 196 | 204 | 206 | 202 | 190 | 206 | 212 | 210 | 210 | 214 | 214 |  | 215 | 214 | 215 | 213 | 211 | 213 | 213 | 5063000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 345 | 270 | 270 | 270 | 270 | 275 | 270 | 270 | 285 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 290 | 260 | 260 | 6666000
| Ashuganj 450 MW CCPP(North) | 280 | 285 | 285 | 285 | 285 | 305 | 305 | 280 | 285 | 285 | 285 | 295 | 285 | 285 | 305 | 290 | 285 | 290 |  | 300 | 300 | 300 | 285 | 310 | 295 | 285 | 7436300
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 250 | 250 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 280 | 260 |  | 260 | 240 | 240 | 240 | 240 | 230 | 230 | 5919700
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 127200
36 | Chandpur 150 MW CCPP | 35 | 37 | 37 | 35 | 35 | 35 | 35 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 23 |  | 23 | 23 | 25 | 30 | 30 | 33 | 33 | 681860
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 400 | 403 | 404 | 391 | 403 | 405 | 376 | 406 | 406 | 407 | 320 |  | 392 | 360 | 379 | 411 | 409 | 404 | 400 | 9468000
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 320 | 320 |  | 450 | 380 | 450 | 450 | 450 | 450 | 450 | 10301000
41 | Haripur 360 MW CCPP(HPL)
42 | RPCL 210MW CCPP | 17 | 17 | 18 | 19 | 19 | 19 | 18 | 16 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 17 | 17 | 17 | 17 | 17 | 19 | 17 | 312000
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 12 | 27 | 38 | 22 | 43 | 47 | 39 | 24 | 28 | 22 | 10 | 2 | [8 empty] | 323780
44 | Fenchugonj CCPP Phase-1 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 896000
45 | Fenchugonj CCPP Phase-2 | [16 empty] | 10 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 121200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 28 | 28 | 28 | 28 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | [9 empty] | 449088
48 | Shahjibazar 86 MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 263040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 137 | 137 | 137 | 137 | 137 | 137 | 139 | 137 | 137 | 135 | 135 | 135 | 135 | 135 | 134 | 135 | 134 | 135 |  | 134 | 134 | 134 | 135 | 135 | 135 | 136 | 3260850
51 | Sylhet 20 MW GTPP
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh)
54 | Hobiganj 11 MW PP Cofidence-E | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 69552
55 | Fenchugonj 51 MW PP (Barakatullah)
56 | Shahjahanulla 25 MW PP | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 276288
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 275 | 295 | 290 | 290 | 310 | 295 | 230 | 115 | 120 | 120 | 170 | 295 | 310 | 300 | 285 | 280 |  | 290 | 280 | 280 | 290 | 300 | 310 | 300 | 6454500
| Bibiyana South 400 MW | 346 | 340 | 340 | 340 | 340 | 360 | 360 | 340 | 340 | 340 | 380 | 360 | 346 | 326 | 326 | 320 | 320 | 320 |  | 340 | 340 | 340 | 340 | 358 | 358 | 340 | 8237100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 0 |  |  |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1037966
59 | Tangail Palli Power Gen 22 MW | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 4 | 0 | 0 | 0 | 0 | 0 | 2 | 79680
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen)
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 58 | 56 | 56 | 54 | 60 | 56 | 52 | 54 | 46 | 56 | 56 | 60 | 60 | 58 | 62 | 54 | 52 | 52 |  | 58 | 58 | 56 | 60 | 58 | 60 | 58 | 1353600
64 | Malancha, Ctg. EPZ (United) | 37 | 39 | 39 | 39 | 39 | 39 | 32 | 8 | 2 | 2 | 2 | 3 | 6 | 6 | 4 | 4 | 5 | 10 |  | 10 | 18 | 26 | 31 | 31 | 38 | 38 | 508800
65 | Feni 22 MW PP (Doreen)
66 | Feni 11 MW PP (Doreen)
67 | Jangalia 33 MW PP (Summit)
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 12 | 12 | 18 | 18 | 18 | 18 | 361550
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 445200
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 535320
71 | Maona 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 602800
72 | Rupganj 33 MW PP(Summit) | 12 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 5 | 5 | 5 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 239800
73 | Ghorashal 108 MW PP (Regent)
| Feni Lanka Power | 52 | 52 | 52 | 52 | 52 | 34 | 17 | 17 | 34 | 52 | 52 | 70 | 106 | 106 | 106 | 70 | 70 | 70 |  | 85 | 90 | 88 | 70 | 70 | 70 | 70 | 1515060
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 223440
| Manikgonj 162MW PP(MPGL) | 35 | 17 | 17 | 0 |  |  |  | 38 | 108 | 108 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 72 | 72 | 126 | 2268000
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150 MW PP | 64 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 48 | 48 |  | 130 | 130 | 130 | 130 | 130 | 98 | 64 | 1187520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | 16 | 16 | 8 | 0 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 33 |  | 42 | 42 | 42 | 25 | 25 | 25 | 25 | 434227
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 52 | 35 | 830880
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 3 | 4 | 5 | 5 | 4 | 2 | 2 | 1 | [9 empty] | 26641
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 17 | 0 | [15 empty] | 1 |  | 17 | 17 | [5 empty] | 56040
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 85 | 45 | 34 | 17 | 0 |  |  |  | 20 | 52 | 67 | 80 | 86 | 86 | 86 | 86 | 86 | 82 |  | 85 | 85 | 85 | 85 | 83 | 68 | 63 | 1365120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn)
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 43 | 43 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1120030
94 | Gagnagar 102 MW PP (Digital Power) | 41 | 41 | 41 | 0 |  |  |  | 8 | 64 | 82 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 25 | 25 | 25 | 25 | 1238976
95 | Patenga 50MW PP (Baraka) | [13 empty] | 11 | 6 | 6 |  | 6 |  | 6 | [6 empty] | 61920
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 15 | 0 |  |  |  | 38 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 | 30 | 45 | 936307
100 | Manikganj 55 MW PP (Northern) | 55 | 35 | 0 |  |  |  |  | 17 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 949374
101 | Kushiara 163 MW CCPP (KP) | 163 | 120 | 120 | 163 | 163 | 163 | 163 | 163 | 120 | 120 | 120 | 163 | 163 | 120 | 120 | 120 | 120 | 120 |  | 163 | 120 | 120 | 163 | 163 | 163 | 163 | 3481364
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 12000
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 0 |  |  |  |  | 3 | 17 | 42 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 17 | 17 | 17 |  |  |  | 619560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 98 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 96 | 95 | 96 | 97 | 96 | 95 | 96 |  | 123 | 124 | 124 | 124 | 124 | 124 | 124 | 2476800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 131 | 120 | 129 | 131 | 131 | 131 | 131 | 131 | 131 | 129 | 116 | 117 | 119 | 114 | 113 | 113 | 113 | 117 |  | 124 | 130 | 129 | 130 | 131 | 117 | 113 | 2980800
115 | Juldah 100 MW PP Unit-3 (Acorn) | 88 | 12 | 0 |  |  |  |  | 5 | 50 | 50 | 62 | 62 | 75 | 75 | 36 | 36 | 36 | 36 |  | 74 | 74 | 50 | 50 | 12 | 12 | 12 | 926400
116 | Chandpur 200 MW (Desh energy) | 136 | 68 | 68 | 17 | 17 | 17 | 17 | 17 | 36 | 68 | 76 | 115 | 120 | 100 | 100 | 100 | 100 | 100 |  | 130 | 170 | 170 | 136 | 136 | 136 | 136 | 2246400
117 | Ashuganj 150 MW PP (Midland) | [8 empty] | 18 | 50 | 52 | 50 | 52 | 52 | 53 | 52 | 52 | 57 |  | 92 | 50 | 50 | 6 | 6 | 6 | 6 | 712581
118 | Bibiyana-III 400 MW CCPP | 350 | 350 | 350 | 350 | 350 | 376 | 362 | 350 | 350 | 350 | 350 | 363 | 315 | 325 | 328 | 299 | 302 | 300 |  | 349 | 349 | 349 | 350 | 365 | 347 | 347 | 8618000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 57 | 57 | 57 | 57 | 67 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1380000
| Anwara 300 MW PP (United) | 50 | 0 | [5 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 |  | 338727
| Juldah unit-2 (Acorn) | 90 | 12 | 0 |  |  |  |  | 12 | 50 | 50 | 84 | 90 | 90 | 90 | 50 | 50 | 50 | 50 |  | 88 | 89 | 50 | 50 | 50 | 50 | 12 | 1139520
| Anlima Energy Ltd. | 17 | 0 | [15 empty] | 2 |  | 17 | 17 | [5 empty] | 53945
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 0 |  |  |  | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [9 empty] | 15 | 244440
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 13 | 16 | 13 | 36 | 18 | 31 | 35 | 12 | 6 | 3 | 1 | [8 empty] | 197292
| Chandpur 115(Doreen) | 55 | 48 | 48 | 51 | 56 | 17 | 17 | 17 | 30 | 71 | 68 | 63 | 55 | 56 | 44 | 54 | 48 | 49 |  | 49 | 72 | 62 | 80 | 72 | 72 | 72 | 1283520
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 28 | 18 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 635040
| Mirsharai 150 MW (Oil) | [8 empty] | 17 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 |  | 71 | 71 | 35 | 17 | 17 | 17 | 17 | 398109
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 4 | 3 | 3 | 3 | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 8 | 20 | 19 | 13 |  | 5 | 2 | 3 | 0 | 0 | 0 | 0 | 83520
| Sonagazi 75 MW Solar Plant | [5 empty] | 1 | 5 | 10 | 18 | 23 | 35 | 36 | 53 | 31 | 58 | 15 | 12 | 2 | [8 empty] | 326391
| Matarbari 2*600 MW (CPGCL) | 1152 | 1155 | 1150 | 1008 | 1009 | 865 | 855 | 1152 | 1103 | 1006 | 956 | 957 | 859 | 850 | 852 | 850 | 850 | 850 |  | 1100 | 1150 | 1150 | 1150 | 1085 | 1084 | 1085 | 24261818
| Meghnaghat (Reliance) 718MW CCPP | 39 | 45 | 47 | 45 | 45 | 45 | 20 | [17 empty] | 4 | 18 | 222600
120 | Eastern Zone Total | 7151 | 6559 | 6574 | 6331 | 6352 | 6251 | 6293 | 6564 | 6858 | 6948 | 7236 | 7512 | 7460 | 7451 | 7399 | 7236 | 7099 | 6988 | 0 | 8082 | 7846 | 7868 | 7723 | 7497 | 7376 | 7353 | 171762773
121
122
123 | Khulna 60MW
124 | manik
| Khulna 115 PP MW (KPCL-2) | [26 empty] | 0
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 2 | 1 | [8 empty] | 1920
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 0 | [17 empty] | 35 | 68 | 71 | 71 | 71 | 71 | 71 | 492480
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 1 | 10 | 22 | 55 | 51 | 48 | 52 | 81 | 59 | 41 | 37 | 8 | 2 | [8 empty] | 462240
131 | Rampal 1320 MW (BIFPCL) | 555 | 550 | 539 | 486 | 487 | 406 | 409 | 500 | 502 | 510 | 510 | 510 | 550 | 550 | 555 | 555 | 485 | 445 |  | 563 | 608 | 621 | 623 | 625 | 624 | 618 | 12836360
132 | United Payra Power Ltd. | [17 empty] | 4 |  | 17 | 17 | 17 |  |  |  |  | 46800
133 | Bhola Nutan Biddut BD LTD (GAS) | 180 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 180 | 180 | 180 | 180 | 180 | 220 | 220 | 220 | 180 | 180 |  | 180 | 180 | 220 | 220 | 220 | 220 | 220 | 5106600
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 0 | [15 empty] | 16 |  | 32 | 48 | 32 | 16 | 16 | 16 | 16 | 234720
Barisal GT PP Unit-1& 2
| Barisal 307 MW | 250 | 250 | 250 | 250 | 250 | 250 | 298 | 307 | 250 | 250 | 250 | 250 | 270 | 240 | 240 | 240 | 200 | 160 |  | 212 | 230 | 250 | 307 | 307 | 307 | 307 | 6131000
136 | Barisal 1 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2592
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 134 | 134 | 134 | 134 | 80 | 80 | 134 | 134 | 134 | 134 | 80 | 80 |  | 134 | 80 | 80 | 134 | 134 | 134 | 134 | 2699000
140 | Bhola 33 MW PP (Venture) | 10 | 9 | 10 | 10 | 9 | 9 | 7 | 7 | 4 | 4 | 6 | 6 | 6 | 7 | 7 | 7 | 6 | 6 |  | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 194624
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [19 empty] | 20 | 30 | 58 | 50 | 45 | 43 |  | 160000
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 899 | 899 | 898 | 898 | 898 | 898 | 898 | 896 | 896 | 895 | 896 | 896 | 896 | 895 | 895 | 896 | 896 | 895 |  | 896 | 895 | 706 | 706 | 706 | 706 | 706 | 20718720
147 | Bheramara 410 MW CCPP | 241 | 248 | 252 | 256 | 257 | 264 | 264 | 263 | 265 | 265 | 265 | 265 | 247 | 238 | 240 | 239 | 239 | 239 |  | 238 | 238 | 242 | 250 | 250 | 259 | 259 | 6130080
148 | Payra 1320 MW | 1120 | 1100 | 1080 | 1040 | 1030 | 1030 | 1070 | 1140 | 1090 | 1090 | 1040 | 1060 | 1080 | 1040 | 1040 | 1040 | 920 | 760 |  | 850 | 960 | 1030 | 1220 | 1244 | 1244 | 1244 | 27724800
149
150 | Barapukuria TPP Unit-1 | 62 | 62 | 62 | 60 | 62 | 62 | 62 | 62 | 61 | 62 | 61 | 60 | 60 | 62 | 61 | 60 | 60 | 59 |  | 60 | 60 | 60 | 61 | 60 | 60 | 60 | 1405091
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 31 | 38 | 37 | 37 |  | 37 | [6 empty] | 170474
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 2 | 4 | 5 | 1 | 5 | 2 | 1 | 0 | 0 | [8 empty] | 32760
| Sirajganj 68 MW Solar Park | [5 empty] | 1 | 11 | 2 | 32 | 41 | 40 | 65 | 37 | 56 | 29 | 23 | 7 | 1 | [8 empty] | 338250
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 180 | 180 | 186 | 189 | 190 | 192 | 196 | 195 | 194 | 191 | 181 | 178 | 160 | 160 | 160 | 160 | 160 |  | 164 | 173 | 150 | 154 | 184 | 187 | 187 | 4540027
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 312 | 331 | 313 | 333 | 324 | 349 | 348 | 395 | 327 | 320 | 337 | 414 | 350 | 350 | 350 | 350 | 300 | 250 |  | 340 | 336 | 336 | 314 | 347 | 414 | 395 | 8380364
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 4 | 4 | 15 |  | 22 | [6 empty] | 48755
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 8 | 8 | 8 | 10 | 10 | 145908
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 19 | 36 | 46 | 42 |  |  |  | 78783
168 | Santahar 50 MW Peaking PP | [11 empty] | 6 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 302230
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 86 | 88 | 88 | 88 | 88 | 89 | 89 | 506720
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [9 empty] | 2 | 35 | 64 | 112 | 112 | 113 | 50 | 50 | 50 |  | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 1383744
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 30 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1339104
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 70 | 56 | 42 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 52 | 82 |  | 98 | 98 | 98 | 99 | 99 | 99 | 99 | 1382457
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 4 | 2 | 7 | 7 | 6 | 5 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 51425
178 | Energypac Power Venture Thakurgaon Ltd. | 75 | 75 | 75 | 75 | 75 | 75 |  |  |  |  | 54 | 75 | 75 | 75 | 75 | 75 | 90 | 94 |  | 115 | 115 | 115 | 115 | 115 | 115 | 95 | 1754496
| Intraco Solar 30 MW | [5 empty] | 0 | 6 | 15 | 24 | 20 | 32 | 37 | 33 | 17 | 17 | 8 | 6 | 1 | [8 empty] | 215337
| Adani Power Jharkhanda Ltd | 1515 | 1532 | 1531 | 1526 | 1390 | 1252 | 1062 | 762 | 754 | 760 | 766 | 766 | 767 | 879 | 1094 | 1183 | 1342 | 1410 |  | 1431 | 1488 | 1516 | 1511 | 1514 | 1506 | 1516 | 28928520
178 | Teesta Solar Limited |  |  |  |  | 0 | 4 | 42 | 95 | 140 | 132 | 138 | 175 | 172 | 193 | 140 | 48 | 19 | 7 | [8 empty] | 1330000