## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2019-03-10 | Sunday
|  | Date (day): | 2019-03-10 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11677 | MW |  |  | (b) At Evening Peak Hour : |  | 12957 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-03-09 | 2019-03-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | Unit #1 Under maint.
| Ghorasal GT: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under Maint.
| Ghorasal GT: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  |  | On test.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 320 | 330 | 360 | 360
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 40 | 0 | 40 | 38 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 42 | 55 | 55
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 40 | 40
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 354 | 360 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under Maint.
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 0 |  | 305 | Under Maint.
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 110 | 110 | 110 | 110
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 80 | 120 | 100 | 120 | 90 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 115 | 115 | 115 |  | 102 | Machine problem
0 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
21 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 102 | 102
22 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 48 | 48 | 48
23 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 54 | 54
24 | Kodda 149MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
25 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
26 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 45 | 50 | 50 |  | 58 | Engine problem
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 57 | 58 | 58 |  | 22 | Engine problem
29 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
30 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 29 | 29 | 29
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 51 | 51
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
33 | Summit Gazipur -2 |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 200 | 300
34 | APR Energy , Keranigonj |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 200 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 | 149 | 149 | 0 | 36 | 149 | 149
| Dhaka area Total |  |  |  |  | 6034 | 5798 | 1717 | 2272 | 3887 | 4247 | 233 | 1067
38 | Chattogram ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 140 | 140 | 140 | 140 | 40 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
40 | Teknaf Solartech 20MW |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
41 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 40 | 50 | 50
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 70 | 72 | 72 |  | 158 | Low water lavel
43 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under S/D
44 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 201 | 201 | 225 | 225
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
46 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 24 | 33 | 51 | 51
47 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 75
48 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 14 | 0 | 68
49 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 20 | 70 | 70 |  | 30 | Engine problem
50 | Juldah 100 MW Unit-3 |  | HFO | IPP | 0 | 100 | 100 | 0 | 101 | 100 | 100
51 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 11 | 26
52 | Chattogram ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 106 | 106
| Chattogram area Total |  |  |  |  | 1761 | 1681 | 468 | 689 | 889 | 1027 | 220 | 378
53 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 70 | 70 | 70 | 70 | 65 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
54 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 224 | 199 | 221 | 221 |  |  | FGMO
55 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 360 | 360 | 360
56 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 280 | 360 | 360
57 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 40 | 40 | 40 |  | 5 | Engine problem
58 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
59 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas Shortage
60 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas Shortage
61 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 5 | 45 | 45 |  | 6 | Engine problem
62 | Midland 150MW |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 15 | 150 | 150
63 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
64 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
65 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST under maint.
66 | Chandpur Desh 200MW |  | HFO | IPP | 0 | 200 | 200 | 52 | 125 | 200 | 200
67 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
68 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 96 | 124 | 101 | 125
69 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
70 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
71 | Summit Cumilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 22 | 22 | 22
72 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1234 | 1504 | 1985 | 2159 | 533 | 74
73 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 206 | 207 | 210 | 210
74 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
75 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 28 | 88 | 88 | 88 |  | 7 | Enjgine problem
76 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 2 | 0
77 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 7 | 40 | 100 | 200
78 | United Jamalpur PPL |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 0 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 265.4 | 357 | 537 | 635 | 0 | 7
79 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
80 | Fenchugonj CCPP-2 |  | Gas | PDB | !F71 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint
81 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
82 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 136 | 132 | 220 | 220
83 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
84 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 5 | 50 | 44 | 44
85 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
86 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 69 | 66 | 66
87 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 85 | 86 | 86
88 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 5 | 48 | 50 | 50
89 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 115 | 86 | 115 | 115
90 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 20 | 20
91 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 7 | 46 | 46 | 46 |  | 4 | Engine problem
92 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 25 | 25 | 25
93 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 320 | 341 | 341
| Bibiyana-3 285MW |  | Gas | PDB | 285 MW | 0 | 0 | 40 | 0 | 0 | 0 |  |  | On test
94 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 984 | 1177 | 1308 | 1308 | 0 | 94
95 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 46
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 714 | 859 | 721 | 870
| Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
96 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 16 | 115 | 115
97 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 44
98 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 |  |  | Reserve
99 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 50 | 0 | 80
100 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 420 | 410 | 410
101 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 24 | 40 | 40 | 40
0 | Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
102 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 100 | 100
103 | Labon Chora 105 MW |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| Khulna Area Total |  |  |  |  | 2223 | 2209 | 1078 | 1534 | 1491 | 1810 | 0 | 0
104 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 100 | 100 |  | 10 | Engine problem
105 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
106 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 19 | 26 | 26 |  | 7 | Engine problem
107 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 174 | 187 | 187 | 187
108 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 198 | 318 | 408 | 438 | 0 | 17
109 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 65 | 65
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage.
110 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 16 | 0 | 50
111 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 45
112 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 50 | 50 | 50
113 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 50 | 50
114 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
115 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 162 | 182 | 200 | 200 |  |  | FGMO
116 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 148 | 180 | 196 | 196 |  |  | FGMO
117 | Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 186 | 220 | 220
118 | Sirajgonj Unit-4 414 MW(Gas) |  | Gas | SNWPGCL | 1*282 | 282 | 282 | 0 | 0 | 0 | 0 | 282 |  | Under S/D
119 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 30
120 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
121 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 17 | 16 | 17 | 17
122 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
123 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
124 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 51 | 100 | 100
125 | Paramount Baghabari |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Reserve
| Confidence CPBL-2 |  | HFO | IPP | 113 MW | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Rajshahi Area Total |  |  |  |  | 1835 | 1825 | 696 | 906 | 1023 | 1148 | 382 | 0
126 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
127 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 149 | 149 | 149 | 125 |  | Coal shortage
128 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
129 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 149 | 184 | 149 | 185 | 125 | 170
| Total |  |  |  |  | 18079 | 17536 | 6789.4 | 8941 | 11677 | 12957 | 1493 | 1807
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6372.5137 | 8392 | 10960.0027 | 12161.4074
A. |  | 2019-03-09 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 8941 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 5087 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8941 | MW
3 | Day peak Generation : |  |  | 6789.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8392 | MW
4 | Evening peak Generation : |  |  | 8941 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 164.9193 | MKWHr | By Solar | 0.03336 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 131.49 | MKWHr |  | By Oil: | 9.0729 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6435 | MKWHr |  | By Hydro: | 1.6458 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1493 | MW | Dhaka | 2998 | 2998 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1807 | MW | Chittagong | 895 | 895 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3300 | MW | Khulna | 1016 | 1016 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1130.32 | MMCFD |  |  | Rajshahi | 944 | 944 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 93596571.858 | ii) Oil : | Taka | 71402764.95 | Comilla | 717 | 717 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14063910 | Total | Taka | 179063246.808 | Mymensingh | 669 | 669 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 1.0665 | MKWHr. | Sylhet | 332 | 332 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -250 | MW (E to W) at | 19:30 | hrs | Barisal | 201 | 201 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -280 | MW at | 19:00 | hrs | Rangpur | 620 | 620 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 30.2° C |  |  | Total | 8392 | 8392 |  | 0
B. |  | 2019-03-10 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 27.3° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12957 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7600 | MW
4 | Reserve(Generation end) |  |  |  | 3657 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 171.5412 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5614 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.7433 | MKWHr. | ii) HVDC Flow at Peak Time |  | 859 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2906 | MKWHr. | iii) Maximum HVDC Flow : |  | 860 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 90.9 |  | (b) Today: | 90.71 |  | (c) Rule Curve: |  | 91.56
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-03-09
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal GT: Unit-3 | Ghorasal GT: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chattogram ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chattogram ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Cumilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur -2 | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | Teknaf Solartech 20MW | Juldah 100 MW Unit-3 | Chandpur Desh 200MW | Midland 150MW | Bibiyana-3 285MW | United Jamalpur PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | Sirajgonj Unit-4 414 MW(Gas) | Labon Chora 105 MW | Paramount Baghabari | Confidence CPBL-2 | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 0 | 0 | 190 | 270 | 13 | 0 | 349 | 0 | 0 | 20 | 380 | 0 | 0 | 0 | 0 | 115 | 110 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 25 | 29 | 0 | 0 | 41 | 30 | 140 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 28 | 70 | 80 | 0 | 300 | 300 | 184 | 8 | 100 | 20 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 0 | 0 | 19 | 82 | 214 | 0 | 0 | 0 | 58 | 0 | 5 | 5 | 100 | 133 | 40 | 5 | 5 | 84 | 0 | 5 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 146 | 0 | 11 | 0 | 154 | 0 | 0 | 0 | 0 | 0 |  | 4331 | 1679 | 6010 | 4256 | 517 | 901 | 34 | 149 | 71 | 0 | 82 | 0 | 0 | 90.95
2:00 | 35 | 0 | 0 | 170 | 250 | 13 | 0 | 340 | 0 | 0 | 20 | 330 | 0 | 0 | 0 | 0 | 115 | 110 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 25 | 29 | 0 | 0 | 40 | 30 | 140 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 10 | 70 | 80 | 0 | 260 | 250 | 183 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 78 | 216 | 0 | 0 | 0 | 57 | 0 | 5 | 5 | 100 | 133 | 40 | 5 | 5 | 98 | 0 | 5 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 518 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 14 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 159 | 0 | 148 | 0 | 11 | 0 | 135 | 0 | 0 | 0 | 0 | 0 |  | 4071 | 1592 | 5663 | 3997 | 518 | 817 | 34 | 149 | 70 | 0 | 78 | 0 | 0 | 90.94
3:00 | 35 | 0 | 0 | 170 | 250 | 13 | 0 | 340 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 0 | 115 | 110 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 31 | 25 | 29 | 0 | 0 | 40 | 30 | 140 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 70 | 80 | 0 | 250 | 240 | 152 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 76 | 151 | 0 | 0 | 0 | 58 | 0 | 5 | 5 | 100 | 133 | 40 | 5 | 5 | 84 | 0 | 5 | 0 | 285 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 145 | 0 | 130 | 0 | 10 | 0 | 135 | 0 | 0 | 0 | 0 | 0 |  | 3896 | 1554 | 5450 | 3819 | 517 | 785 | 34 | 149 | 70 | 0 | 76 | 0 | 0 | 90.93
4:00 | 35 | 0 | 0 | 170 | 250 | 0 | 0 | 300 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 31 | 25 | 29 | 0 | 0 | 39 | 30 | 100 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 70 | 80 | 0 | 230 | 230 | 152 | 8 | 50 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 72 | 147 | 0 | 0 | 0 | 23 | 0 | 5 | 5 | 100 | 133 | 40 | 5 | 5 | 89 | 0 | 5 | 0 | 265 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 13 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 5 | 0 | 0 | 149 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 |  | 3548 | 1539 | 5087 | 3526 | 517 | 737 | 17 | 149 | 69 | 0 | 72 | 0 | 0 | 90.92
5:00 | 35 | 0 | 0 | 170 | 250 | 0 | 0 | 325 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 29 | 0 | 0 | 38 | 30 | 100 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 70 | 80 | 0 | 230 | 230 | 183 | 8 | 50 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 74 | 151 | 0 | 0 | 0 | 23 | 0 | 5 | 5 | 100 | 133 | 40 | 5 | 5 | 100 | 0 | 5 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 517 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 13 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 135 | 0 | 130 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 |  | 3619 | 1556 | 5175 | 3591 | 517 | 759 | 17 | 149 | 68 | 0 | 74 | 0 | 0 | 90.91
6:00 | 35 | 0 | 0 | 170 | 250 | 0 | 0 | 377 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 115 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 29 | 0 | 0 | 39 | 30 | 100 | 0 | 0 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | 70 | 80 | 0 | 270 | 260 | 183 | 8 | 50 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 78 | 152 | 0 | 0 | 0 | 23 | 0 | 5 | 5 | 100 | 133 | 40 | 89 | 5 | 95 | 0 | 5 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 518 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 13 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 165 | 0 | 146 | 0 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | 0 |  | 3897 | 1603 | 5500 | 3786 | 518 | 883 | 17 | 149 | 69 | 0 | 78 | 0 | 0 | 90.9
7:00 | 35 | 0 | 0 | 170 | 280 | 0 | 0 | 379 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 25 | 29 | 0 | 0 | 40 | 30 | 140 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 28 | 70 | 80 | 0 | 270 | 260 | 166 | 8 | 90 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 19 | 74 | 218 | 0 | 0 | 0.2 | 23 | 0 | 5 | 5 | 130 | 133 | 71 | 89 | 5 | 104 | 0 | 7 | 0 | 325 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 2.42 | 0 | 0 | 0 | 0 | 0 |  | 640 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 12 | 0 | 0 | 0 | 70 | 0 | 0 | 51 | 40 | 0 | 0 | 45 | 0 | 22 | 5 | 8 | 0 | 0 | 149 | 0 | 0 | 173 | 0 | 163 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 |  | 4197.62 | 1986 | 6183.62 | 4094 | 640 | 1001 | 102 | 149 | 70 | 51 | 74 | 2.62 | 0 | 90.89
8:00 | 35 | 0 | 0 | 170 | 280 | 0 | 0 | 358 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 25 | 29 | 0 | 0 | 40 | 30 | 140 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 7 | 70 | 80 | 0 | 270 | 260 | 180 | 8 | 100 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 82 | 212 | 30 | 0 | 0.8 | 23 | 0 | 5 | 5 | 130 | 133 | 53 | 89 | 5 | 114 | 0 | 6 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.8 | 0 | 0 | 0 | 0 | 0 |  | 713 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 190 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 51 | 40 | 8 | 0 | 52 | 22 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 165 | 0 | 156 | 0 | 9 | 0 | 163 | 0 | 0 | 0 | 0 | 0 |  | 4276.6 | 2162 | 6438.6 | 4180 | 713 | 991 | 171 | 149 | 70 | 73 | 82 | 9.6 | 0 | 91.04
9:00 | 35 | 0 | 0 | 170 | 280 | 0 | 0 | 363 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 30 | 25 | 29 | 8 | 0 | 42 | 30 | 140 | 0 | 0 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 21 | 2 | 70 | 80 | 0 | 270 | 260 | 183 | 8 | 100 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 90 | 209 | 28 | 0 | 1.5 | 60 | 0 | 5 | 5 | 163 | 133 | 52 | 86 | 5 | 118 | 0 | 6 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 714 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 189 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 51 | 40 | 24 | 0 | 52 | 30 | 22 | 14 | 8 | 0 | 0 | 149 | 0 | 0 | 167 | 0 | 158 | 0 | 11 | 0 | 161 | 0 | 0 | 0 | 0 | 0 |  | 4337.5 | 2230 | 6567.5 | 4259 | 714 | 1008 | 193 | 149 | 72 | 81 | 90 | 1.5 | 0 | 91.03
10:00 | 35 | 0 | 0 | 190 | 280 | 0 | 0 | 363 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 115 | 110 | 37 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 22 | 25 | 12 | 25 | 0 | 42 | 30 | 140 | 0 | 0 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 80 | 0 | 270 | 260 | 180 | 8 | 0 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 90 | 208 | 28 | 0 | 2 | 60 | 0 | 5 | 5 | 163 | 134 | 66 | 89 | 5 | 118 | 0 | 6 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 714 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 187 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 51 | 40 | 24 | 0 | 52 | 31 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 168 | 0 | 161 | 0 | 11 | 0 | 164 | 0 | 0 | 0 | 0 | 13 |  | 4295 | 2251 | 6546 | 4179 | 714 | 1028 | 230 | 149 | 72 | 82 | 90 | 2 | 0 | 91.03
11:00 | 35 | 0 | 0 | 190 | 320 | 0 | 0 | 390 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 10 | 115 | 110 | 80 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 22 | 25 | 12 | 25 | 0 | 42 | 30 | 140 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 80 | 0 | 270 | 260 | 188 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 8 | 0 | 21 | 94 | 204 | 28 | 22 | 2.3 | 60 | 0 | 5 | 5 | 163 | 135 | 40 | 89 | 5 | 105 | 0 | 6 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 |  | 714 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 186 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 176 | 0 | 150 | 0 | 11 | 0 | 162 | 0 | 0 | 0 | 0 | 14 |  | 4650.3 | 2135 | 6785.3 | 4386 | 714 | 1098 | 270 | 149 | 72 | 0 | 94 | 2.3 | 0 | 91.02
12:00 | 35 | 0 | 0 | 190 | 320 | 0 | 0 | 354 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 15 | 0 | 110 | 80 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 22 | 25 | 12 | 25 | 0 | 42 | 30 | 140 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 80 | 0 | 270 | 260 | 224 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 96 | 206 | 28 | 22 | 2.4 | 60 | 0 | 5 | 5 | 163 | 136 | 51 | 89 | 5 | 115 | 0 | 7 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 52 | 0 | 40 | 0 |  | 714 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 174 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 162 | 0 | 148 | 0 | 11 | 0 | 187 | 0 | 0 | 0 | 0 | 0 |  | 4668.4 | 2121 | 6789.4 | 4335 | 714 | 1082 | 339 | 149 | 72 | 0 | 96 | 2.4 | 0 | 91.02
13:00 | 35 | 0 | 0 | 190 | 350 | 0 | 0 | 374 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 15 | 0 | 110 | 73 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 25 | 22 | 25 | 12 | 25 | 0 | 42 | 30 | 140 | 0 | 0 | 204 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 19 | 9 | 70 | 80 | 0 | 270 | 260 | 190 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 100 | 201 | 28 | 20 | 2.3 | 60 | 0 | 5 | 5 | 163 | 134 | 51 | 89 | 5 | 115 | 0 | 7 | 0 | 310 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 52 | 0 | 40 | 0 |  | 714 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 185 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 17 | 0 | 0 | 0 | 149 | 0 | 0 | 201 | 0 | 190 | 0 | 11 | 0 | 201 | 0 | 0 | 0 | 0 | 0 |  | 4672.3 | 2216 | 6888.3 | 4436 | 714 | 1096 | 319 | 149 | 72 | 0 | 100 | 2.3 | 0 | 91.01
14:00 | 35 | 0 | 0 | 190 | 300 | 0 | 0 | 362 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 15 | 0 | 110 | 80 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 18 | 25 | 12 | 25 | 0 | 42 | 30 | 135 | 0 | 0 | 215 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 19 | 7 | 70 | 80 | 0 | 270 | 260 | 205 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 104 | 190 | 28 | 20 | 2 | 60 | 0 | 5 | 5 | 130 | 135 | 50 | 87 | 5 | 122 | 0 | 7 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 53 | 0 | 40 | 0 |  | 713 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 184 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 191 | 0 | 188 | 0 | 11 | 0 | 194 | 0 | 0 | 0 | 0 | 0 |  | 4460 | 2146 | 6606 | 4319 | 713 | 962 | 285 | 149 | 72 | 0 | 104 | 2 | 0 | 91.01
15:00 | 35 | 0 | 0 | 190 | 380 | 0 | 0 | 388 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 0 | 110 | 120 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 18 | 25 | 12 | 25 | 0 | 42 | 30 | 135 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 80 | 0 | 300 | 310 | 205 | 8 | 100 | 37 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 104 | 191 | 28 | 20 | 1.6 | 58 | 0 | 5 | 5 | 163 | 134 | 50 | 40 | 5 | 111 | 0 | 6 | 0 | 320 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 53 | 0 | 40 | 0 |  | 713 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 184 | 12 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 203 | 0 | 199 | 0 | 11 | 0 | 206 | 0 | 0 | 0 | 0 | 0 |  | 4819.6 | 2137 | 6956.6 | 4634 | 713 | 1080 | 202 | 149 | 72 | 1 | 104 | 1.6 | 0 | 91
16:00 | 35 | 0 | 0 | 190 | 380 | 0 | 0 | 355 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 77 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 24 | 25 | 12 | 25 | 0 | 42 | 30 | 135 | 0 | 0 | 202 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 80 | 0 | 300 | 280 | 185 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 19 | 11 | 0 | 21 | 104 | 193 | 28 | 22 | 1 | 56 | 0 | 5 | 5 | 130 | 132 | 40 | 10 | 5 | 106 | 0 | 6 | 0 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 53 | 0 | 30 | 0 |  | 713 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 184 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 0 | 22 | 16 | 8 | 0 | 0 | 149 | 0 | 0 | 186 | 0 | 182 | 0 | 11 | 0 | 184 | 0 | 0 | 0 | 0 | 0 |  | 4708 | 2059 | 6767 | 4503 | 713 | 986 | 231 | 149 | 72 | 8 | 104 | 1 | 0 | 91
17:00 | 35 | 0 | 0 | 190 | 340 | 0 | 0 | 360 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 77 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 22 | 25 | 12 | 25 | 0 | 42 | 30 | 135 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 10 | 0 | 0 | 19 | 10 | 70 | 80 | 0 | 300 | 280 | 185 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 100 | 203 | 28 | 22 | 0.3 | 58 | 0 | 5 | 5 | 100 | 135 | 40 | 10 | 5 | 90 | 0 | 7 | 0 | 275 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10 | 60 | 0 | 34 | 0 |  | 713 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8 | 159 | 10 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 24 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 189 | 0 | 155 | 0 | 12 | 0 | 159 | 0 | 0 | 0 | 0 | 0 |  | 4655.3 | 1992 | 6647.3 | 4397 | 713 | 951 | 250 | 149 | 72 | 15 | 100 | 0.3 | 0 | 90.99
18:00 | 35 | 0 | 0 | 190 | 330 | 0 | 0 | 363 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 15 | 115 | 110 | 120 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 28 | 0 | 25 | 22 | 25 | 29 | 51 | 0 | 40 | 30 | 135 | 0 | 6 | 214 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 10 | 10 | 6 | 19 | 6 | 70 | 80 | 0 | 270 | 280 | 206 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 114 | 203 | 28 | 22 | 0 | 60 | 0 | 5 | 5 | 100 | 135 | 40 | 10 | 5 | 97 | 0 | 7 | 0 | 270 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 70 | 90 | 0 | 0 | 0 |  | 713 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 23 | 30 | 8 | 185 | 13 | 13 | 0 | 0 | 60 | 0 | 0 | 0 | 12 | 0 | 0 | 25 | 14 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 0 | 191 | 0 | 156 | 0 | 12 | 0 | 162 | 0 | 0 | 17 | 0 | 0 |  | 4749 | 2166 | 6915 | 4463 | 713 | 835 | 487 | 149 | 70 | 84 | 114 | 0 | 0 | 90.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 0 | 0 | 195 | 330 | 108 | 35 | 374 | 0 | 0 | 0 | 450 | 0 | 0 | 10 | 31 | 115 | 110 | 120 | 0 | 0 | 40 | 0 | 0 | 24 | 0 | 39 | 35 | 55 | 55 | 0 | 25 | 26 | 25 | 22 | 51 | 0 | 40 | 30 | 140 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 33 | 0 | 17 | 40 | 30 | 47 | 19 | 19 | 70 | 80 | 0 | 360 | 280 | 185 | 8 | 100 | 40 | 5 | 5 | 15 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 124 | 207 | 88 | 22 | 0 | 60 | 0 | 53 | 36 | 163 | 135 | 63 | 85 | 48 | 85 | 19 | 47 | 10 | 290 | 25 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 25 | 0 | 101 | 108 | 30 | 0 | 0 |  | 860 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 44 | 80 | 41 | 165 | 19 | 16 | 0 | 0 | 65 | 16 | 0 | 51 | 50 | 32 | 0 | 52 | 30 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 18 | 195 | 0 | 176 | 0 | 97 | 0 | 183 | 0 | 0 | 105 | 0 | 0 |  | 6058 | 2876 | 8934 | 4712 | 860 | 1531 | 1215 | 149 | 70 | 273 | 124 | 0 | 0 | 90.98
19:30 | 35 | 0 | 0 | 190 | 330 | 42 | 40 | 360 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 120 | 0 | 0 | 7 | 0 | 0 | 45 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 32 | 25 | 29 | 51 | 0 | 40 | 30 | 140 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 33 | 0 | 14 | 20 | 0 | 40 | 19 | 26 | 70 | 80 | 0 | 360 | 280 | 199 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 124 | 207 | 88 | 22 | 0 | 60 | 0 | 53 | 50 | 163 | 132 | 69 | 85 | 48 | 86 | 19 | 46 | 10 | 320 | 25 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 0 | 101 | 125 | 15 | 0 | 0 |  | 859 | 0 | 420 | 0 | 16 | 0 | 0 | 0 | 44 | 50 | 40 | 187 | 19 | 16 | 0 | 0 | 60 | 16 | 0 | 51 | 50 | 50 | 0 | 52 | 30 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 18 | 182 | 0 | 180 | 0 | 96 | 0 | 186 | 0 | 0 | 105 | 0 | 0 |  | 5999 | 2942 | 8941 | 4827 | 859 | 1509 | 1163 | 149 | 70 | 240 | 124 | 0 | 0 | 0
20:00 | 35 | 0 | 0 | 190 | 330 | 42 | 40 | 350 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 120 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 32 | 25 | 29 | 51 | 0 | 40 | 30 | 140 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 10 | 0 | 28 | 19 | 26 | 70 | 80 | 0 | 360 | 280 | 199 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 118 | 206 | 88 | 22 | 0 | 60 | 0 | 53 | 50 | 163 | 134 | 68 | 85 | 48 | 86 | 19 | 46 | 10 | 275 | 25 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 0 | 101 | 120 | 0 | 0 | 0 |  | 859 | 0 | 424 | 0 | 16 | 0 | 0 | 0 | 18 | 40 | 40 | 186 | 19 | 16 | 0 | 0 | 60 | 17 | 0 | 51 | 50 | 50 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 18 | 187 | 0 | 184 | 0 | 96 | 0 | 190 | 0 | 0 | 105 | 0 | 0 |  | 5884 | 2894 | 8778 | 4833 | 859 | 1465 | 1123 | 149 | 70 | 161 | 118 | 0 | 0 | 90.98
21:00 | 35 | 0 | 0 | 190 | 380 | 0 | 40 | 380 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 114 | 110 | 195 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 35 | 0 | 55 | 0 | 25 | 32 | 25 | 29 | 51 | 0 | 40 | 30 | 140 | 0 | 8 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 20 | 30 | 70 | 80 | 0 | 360 | 315 | 197 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 120 | 205 | 88 | 22 | 0 | 58 | 0 | 53 | 50 | 163 | 133 | 68 | 85 | 48 | 93 | 19 | 46 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 101 | 80 | 0 | 0 | 0 |  | 859 | 0 | 420 | 0 | 16 | 0 | 0 | 0 | 18 | 40 | 40 | 189 | 19 | 16 | 0 | 0 | 60 | 0 | 0 | 34 | 50 | 24 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 18 | 200 | 0 | 197 | 0 | 95 | 0 | 203 | 0 | 0 | 105 | 0 | 0 |  | 5729 | 2871 | 8600 | 4971 | 859 | 1461 | 843 | 149 | 70 | 127 | 120 | 0 | 0 | 90.97
22:00 | 35 | 0 | 0 | 190 | 270 | 0 | 40 | 353 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 175 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 35 | 0 | 55 | 0 | 25 | 32 | 25 | 29 | 26 | 0 | 40 | 30 | 140 | 0 | 8 | 201 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 19 | 30 | 70 | 80 | 0 | 360 | 320 | 185 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 112 | 205 | 88 | 20 | 0 | 60 | 0 | 53 | 50 | 163 | 112 | 45 | 85 | 48 | 103 | 19 | 46 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 100 | 34 | 0 | 0 | 0 |  | 859 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 40 | 168 | 18 | 16 | 0 | 0 | 60 | 0 | 0 | 6 | 50 | 0 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 188 | 0 | 184 | 0 | 96 | 0 | 190 | 0 | 0 | 53 | 0 | 0 |  | 5406 | 2501 | 7907 | 4594 | 859 | 1421 | 674 | 149 | 70 | 28 | 112 | 0 | 0 | 90.97
23:00 | 35 | 0 | 0 | 190 | 270 | 0 | 40 | 350 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 0 | 25 | 32 | 25 | 29 | 0 | 0 | 41 | 30 | 140 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 19 | 35 | 70 | 80 | 0 | 360 | 315 | 185 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 22 | 102 | 198 | 88 | 20 | 0 | 58 | 0 | 53 | 50 | 163 | 111 | 56 | 85 | 48 | 106 | 0 | 46 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 |  | 761 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 17 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 182 | 0 | 178 | 0 | 96 | 0 | 184 | 0 | 0 | 17 | 0 | 0 |  | 5256 | 2231 | 7487 | 4533 | 761 | 1435 | 436 | 149 | 71 | 0 | 102 | 0 | 0 | 90.96
24:00 | 35 | 0 | 0 | 190 | 270 | 0 | 0 | 349 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 15 | 115 | 110 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25 | 32 | 25 | 29 | 0 | 0 | 41 | 30 | 140 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 10 | 0 | 0 | 19 | 35 | 70 | 80 | 0 | 325 | 315 | 185 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 90 | 198 | 50 | 20 | 0 | 58 | 0 | 53 | 50 | 130 | 113 | 46 | 85 | 48 | 103 | 0 | 44 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 761 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 16 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 181 | 0 | 178 | 0 | 66 | 0 | 183 | 0 | 0 | 0 | 0 | 0 |  | 4878 | 2034 | 6912 | 4394 | 761 | 1289 | 158 | 149 | 71 | 0 | 90 | 0 | 0 | 90.96
KWH | 836000 | 0 | 0 | 4473000 | 7148818 | 246727 | 337120 | 8741890 | 0 | 0 | 97500 | 8807625 | 0 | 0 | 13824 | 238105 | 2353110 | 2586150 | 2065000 | 0 | 0 | 124128 | 0 | 0 | 60480 | 0 | 97632 | 331560 | 105406 | 456100 | 210132 | 600000 | 605880 | 577900 | 591500 | 473340 | 0 | 917760 | 728000 | 3200000 | 0 | 77788 | 4839573 | 0 | 0 | 0 | 0 | 442080 | 0 | 22553 | 306120 | 37440 | 82080 | 393744 | 386400 | 1690506 | 1939420 | 0 | 7336000 | 6753000 | 4496000 | 217454 | 2069180 | 473976 | 128160 | 120000 | 173150 | 0 | 5320 | 0 | 392652 | 173520 | 66280 | 523420 | 2290560 | 4611800 | 817920 | 282708 | 16350 | 1262000 | 0 | 387600 | 376000 | 3510720 | 2849000 | 1149048 | 1419840 | 441360 | 2502380 | 75000 | 389720 | 20880 | 7610500 | 66240 | 172032 | 0 | 0 | 0 | 0 | 374400 | 0 | 66240 | 17010 | 504960 | 868320 | 68580 | 476800 | 0 |  | 16743272 | 0 | 7568064 | 0 | 85280 | 0 | 0 | 0 | 100320 | 228608 | 393000 | 4400873 | 318500 | 82560 | 0 | 0 | 1415000 | 32682 | 0 | 311191 | 592440 | 182482 | 0 | 771840 | 123411 | 400800 | 289224 | 179244 | 0 | 0 | 3643500 | 65000 | 67000 | 4498718 | 0 | 4143755 | 0 | 697519 | 0 | 4323854 | 0 | 0 | 434880 | 0 | 27840 |  | 112798471 | 52120857 | 164919328 | 105210667 | 16743272 | 26279299 | 8116825 | 3643500 | 1645760 | 956085 | 2290560 | 33360 | 0
Fuel Cost | 718960 | 0 | 0 | 3846780 | 4575243.52 | 199848.87 | 316892.8 | 5332552.9 | 0 | 0 | 133575 | 5901108.75 | 0 | 0 | 92344.32 | 1454821.55 | 1529521.5 | 2482704 | 2292150 | 0 | 0 | 818003.52 | 0 | 0 | 362275.2 | 0 | 651205.44 | 2364022.8 | 658787.5 | 2859747 | 157599 | 450000 | 0 | 0 | 0 | 4477796.4 | 0 | 0 | 0 | 3520000 | 0 | 736652.36 | 3194118.18 | 0 | 0 | 0 | 0 | 3885883.2 | 0 | 219440.69 | 1894882.8 | 241862.4 | 536803.2 | 334682.4 | 0 | 1538360.46 | 1764872.2 | 0 | 4548320 | 4659570 | 3147200 | 150043.26 | 1986412.8 | 317563.92 | 110217.6 | 110400 | 141983 | 0 | 57668.8 | 0 | 302342.04 | 130140 | 51035.6 | 392565 | 15667430.4 | 3458850 | 7516684.8 | 217685.16 | 0 | 1312480 | 0 | 372096 | 338400 | 2738361.6 | 1994300 | 1309914.72 | 1519228.8 | 485496 | 2852713.2 | 96000 | 362439.6 | 19418.4 | 4870720 | 49680 | 130744.32 | 0 | 0 | 0 | 0 | 2676960 | 0 | 0 | 0 | 0 | 8110108.8 | 640537.2 | 414816 | 0 |  | 85390687.2 | 0 | 5070602.88 | 0 | 706971.2 | 0 | 0 | 0 | 1129603.2 | 2693002.24 | 3096840 | 3036602.37 | 315315 | 610944 | 0 | 0 | 1485750 | 374208.9 | 0 | 2788271.36 | 5124606 | 1624089.8 | 0 | 7656652.8 | 1452547.47 | 440880 | 271870.56 | 135687.708 | 0 | 0 | 14063910 | 2094950 | 1793590 | 3059128.24 | 0 | 2900628.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 132804024.98 | 147317339.428 | 280121364.408 | 74931851.618 | 85390687.2 | 18664720.24 | 58799482.29 | 14063910 | 0 | 12603282.66 | 15667430.4 | 0 | 0
Yesterday Day Peak | 35 | 0 | 0 | 190 | 320 | 0 | 0 | 354 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 15 | 0 | 110 | 80 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 22 | 25 | 22 | 25 | 12 | 25 | 0 | 42 | 30 | 140 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 10 | 0 | 0 | 19 | 2 | 70 | 80 | 0 | 270 | 260 | 224 | 8 | 100 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 96 | 206 | 28 | 22 | 2.4 | 60 | 0 | 5 | 5 | 163 | 136 | 51 | 89 | 5 | 115 | 0 | 7 | 0 | 300 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 52 | 0 | 40 | 0 |  | 714 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 174 | 13 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 0 | 0 | 52 | 0 | 22 | 17 | 8 | 0 | 0 | 149 | 0 | 0 | 162 | 0 | 148 | 0 | 11 | 0 | 187 | 0 | 0 | 0 | 0 | 0 |  | 6789.4 | DayPeak
Yesterday Evening Peak | 35 | 0 | 0 | 190 | 330 | 42 | 40 | 360 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 15 | 115 | 110 | 120 | 0 | 0 | 7 | 0 | 0 | 45 | 0 | 48 | 35 | 55 | 55 | 22 | 25 | 32 | 25 | 29 | 51 | 0 | 40 | 30 | 140 | 0 | 25 | 201 | 0 | 0 | 0 | 0 | 33 | 0 | 14 | 20 | 0 | 40 | 19 | 26 | 70 | 80 | 0 | 360 | 280 | 199 | 8 | 100 | 40 | 5 | 5 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 124 | 207 | 88 | 22 | 0 | 60 | 0 | 53 | 50 | 163 | 132 | 69 | 85 | 48 | 86 | 19 | 46 | 10 | 320 | 25 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 36 | 0 | 101 | 125 | 15 | 0 | 0 |  | 859 | 0 | 420 | 0 | 16 | 0 | 0 | 0 | 44 | 50 | 40 | 187 | 19 | 16 | 0 | 0 | 60 | 16 | 0 | 51 | 50 | 50 | 0 | 52 | 30 | 22 | 16 | 11 | 0 | 0 | 149 | 17 | 18 | 182 | 0 | 180 | 0 | 96 | 0 | 186 | 0 | 0 | 105 | 0 | 0 |  | 8941 | EvPeak
Forecast for Evening | 35 | 0 | 0 | 190 | 360 | 55 | 40 | 412 | 0 | 110 | 40 | 450 | 0 | 100 | 100 | 55 | 115 | 110 | 120 | 100 | 100 | 102 | 149 | 100 | 50 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 29 | 51 | 0 | 42 | 30 | 140 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 51 | 75 | 68 | 70 | 106 | 50 | 19 | 26 | 70 | 80 | 0 | 360 | 360 | 221 | 8 | 100 | 40 | 5 | 5 | 45 | 0 | 50 | 52 | 22 | 11 | 33 | 22 | 125 | 210 | 88 | 22 | 0 | 60 | 0 | 51 | 44 | 163 | 220 | 66 | 86 | 50 | 115 | 20 | 46 | 10 | 341 | 25 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 |  | 870 | 46 | 410 | 0 | 115 | 0 | 0 | 0 | 44 | 80 | 40 | 187 | 26 | 100 | 30 | 0 | 65 | 50 | 45 | 100 | 50 | 50 | 40 | 52 | 30 | 22 | 17 | 11 | 0 | 0 | 149 | 17 | 19 | 200 | 0 | 196 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 0
Forecast for Day | 35 | 0 | 0 | 190 | 360 | 55 | 0 | 412 | 0 | 110 | 40 | 450 | 0 | 100 | 100 | 55 | 115 | 110 | 100 | 100 | 100 | 102 | 149 | 100 | 50 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 29 | 51 | 0 | 42 | 30 | 140 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 70 | 106 | 50 | 19 | 11 | 70 | 80 | 0 | 360 | 360 | 221 | 8 | 100 | 40 | 5 | 5 | 45 | 0 | 0 | 52 | 22 | 11 | 33 | 22 | 101 | 210 | 88 | 22 | 2 | 60 | 0 | 51 | 44 | 163 | 220 | 66 | 86 | 50 | 115 | 20 | 46 | 10 | 341 | 25 | 11 | 100 | 200 | 200 | 50 | 100 | 50 | 149 | 20 | 100 | 200 | 150 | 0 | 115 |  | 721 | 0 | 410 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 187 | 26 | 100 | 0 | 0 | 65 | 0 | 0 | 100 | 50 | 50 | 40 | 52 | 0 | 22 | 17 | 11 | 0 | 0 | 149 |  | 0 | 200 | 0 | 196 | 0 | 95 | 100 | 220 | 0 | 0 | 105 | 0
Generation at 08:00(Today) | 35 | 0 | 0 | 190 | 380 | 55 | 0 | 383 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 4 | 115 | 110 | 100 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 32 | 25 | 29 | 8 | 0 | 41 | 30 | 140 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 10 | 0 | 0 | 19 | 11 | 70 | 80 | 0 | 360 | 360 | 199 | 8 | 80 | 34 | 5 | 5 | 27 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 84 | 160 | 14 | 22 | 0.7 | 60 | 0 | 51 | 50 | 130 | 115 | 69 | 83 | 48 | 96 | 20 | 42 | 10 | 341 | 25 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0 | 468 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 186 | 11 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 12 | 0 | 0 | 45 | 0 | 22 | 17 | 11 | 0 | 0 | 149 | 0 | 0 | 199 | 0 | 196 | 0 | 45 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5087 | 4:00
| Highest Generation |  | 8941 | 19:30
| Day Peak Generation |  | 6789.4 | 12:00
| Evening Peak Generation |  | 8941 | 19:30
| HVDC Max Flow |  | 860 | 19:00
| HVDC EvPeak Flow |  | 859 | 19:30
| Load factor L.F |  | 76.86%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-03-10
Till now the maximum generation is : - |  |  | 11623 MW | 19:30 | Hrs on | 2018-09-19
The Summary of Yesterday's |  | 2019-03-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6789.4 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5614 | MW
Evening Peak Generation : |  | 8941 | MW Hour : | 19:30 | Available Max Generation : |  | 12957 | MW
E.P. Demand (at gen end) : |  | 8941 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 9300 | MW
Maximum Generation : |  | 8941 | MW Hour : | 19:30 | Reserve(Generation end) |  | 3657 | MW
Total Gen. (MKWH) : |  | 164.9193 | System Load Factor : | 76.86% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -280 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-03-10
Actual : | 90.71 | Ft.(MSL) , | Rule curve : | 91.56 | Ft.( MSL )
Gas Consumed : | Total = | 1130.32 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 93596571.858
|  | Coal : | 14063910 | Oil : | 71402764.95 | Total : | 179063246.808
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3260.8084 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1103.8736 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 988.1465 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 892.5585 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 806.766 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 651.019 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 370.4285 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 167.7896 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 502.0675 |  |  | 0 | 0%
Total | 0 |  | 8743.4577 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Fenchuganj CCPP-2
2) Khulna ST 110 MW
3) Ghorasal Unit-3,4
4) Bhagabari 100 MW
5) Sikalbaha 150MW Peaking
6) Haripur 360 MW
7) Ashuganj #5
8) Summit Meghnaghat 305 MW
9) Haripur GT-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Bibiyana 230 kV bus-2 was under shut down from 09:09 to 17:12 for D/W.
b) Bibiyana 400/230 kV ICT-2 transformer was under shut down from 09:09 to 17:12 for D/W.
c) Mongla-Bagherhat 132 kV Ckt was under shut down from 09:03 to 17:53 for C/M. |  |  |  | About 30 MW power interruption occurred under Mongla S/S
area 09:03 to 17:53.
d) Ishurdi 33 kV full bus was under shut down from 08:00 to 18:35 for C/M. |  |  |  | About 25 MW power interruption occurred under Ishurdi S/S
area from 08:00 to 18:35.
e) Madaripur 132/33 kV T2 transformer was under shut down from 08:47 to 14:12 for C/M.
f) Norsingdi 132/33 kV T1 transformer was under shut down from 10:54 to 17:49 for D/W.
g) Hasnabad 132/33 kV T2 transformer was under shut down from 09:48 to 12:19 for red hot maintenance.
h) Kishoreganj 132/33 kV T2 transformer was under shut down from 08:46 to 10:54 for C/M.
i) Meghnaghat-Shyampur 230 kV Ckt-2 was under shut down from 09:02 to 15:14 for C/M.
j) Ullon-Haripur 132 kV Ckt-2 tripped at 08:12 from both ends showing Dist Z1 Y,B-phase at Ullon end & Dist Z3,
Z4 Y, B-phase, Master trip M,B at Haripur end and was switched on at 13:30.
k) Dhanmondi 132/33 kV T1 (New) transformer was switched on at 12:55.
l) Chandpur CCPP GT tripped at 09:34 due to 132 kV CB not healthy and was synchronized at 10:56.
m) Bibiyana Unit-3 GT was synchronized at 11:03 for test purpose and was shut down at 17:34.
n) Siddhirganj 335 MW CCPP GT was tripped at 11:59 due to tripping of gas booster and was synchronized at 15:06.
o) Madaripur 132/33 kV T1 transformer was under shut down from 14:17 to 15:09 for oil leakage maintenance.
p) Gopalganj-Modhumoti PP 132 kV Ckt was switched on at 18:10.
q) Hasnabad 132/33 kV T2 transformer was under shut down from 17:26 to 22:24 due to smoke was coming
out from 33 kV Y-phase CT.
r) Shahjibazar 330 MW GT-2 was shut down at 21:08 due to Differential pressure high.
s) Shyampur(N)-Shyampur(Old) 132 kV Ckt-2 was switched on at 01:47(10/03/2019).
t) Shyampur(Old) 132/33 kV T4 transformer was switched on at 02:02(10/03/2019).
u) Shyampur(Old)-Shyampur(N) 132 kV Ckt-2 tripped at 02:23 (10/03/2019) from Shyampur(Old) end showing
SOTF and was switched on at 02:37.
v) HVDC Bheramara block-1 is under shut down from 06:18 to 09:39(10/03/2019) for red hot maintenance at DS.
w) Hasnabad 132/33 kV T2 & T5 transformers tripped at 04:58(10/03/2019) due to 33 kV B-phase CB pole burst |  |  |  | About 80 MW power interruption occurred under Hasnabad S/S
at T5 transformer and T2 transformer is switched on at 05:35. |  |  |  | area from 04:58 to 05:35(10/03/2019).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-03-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 35 | 836000 | #2 Under maint.
| Ghorasal GT: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal GT: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | On test
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 190 | 4473000
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 7148818
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 40 | 337120 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 42 | 246727 | Ghorasal Transformer O/L.
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 97500 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8741890 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 0 | 0 | Under maint.
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8807625
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Machine problem
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 0 | 13824 | Reserve
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 238105 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 210132
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 110 | 2586150
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 120 | 2065000 | FGMO
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Reserve
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 115 | 2353110 | Machine problem
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 124128 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 97632
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 35 | 331560 | Low demand
25 | Kodda 149MW |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 105406
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 456100
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 45 | 60480 | Low demand
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1205880 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 577900 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 29 | 591500 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 473340
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
34 | Summit Gazipur -2 |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve
35 | APR Energy , Keranigonj |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
36 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
37 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
38 | Summit Gazipur-1 150MW |  | IPP | 149 | 149 | 36 | 66240 | Low demand
| Dhaka area Total |  |  |  | 5798 | 2272 | 42245167
39 | Chattogram ST-1 (Raozan) |  | PDB | 1*210 | 180 | 140 | 3200000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 77788
| Teknaf Solartech 20MW |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 17010
41 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 40 | 82080
42 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1645760 | Low water lavel
43 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 201 | 4839573 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
46 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 33 | 442080 | Low demand
47 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
48 | Dohazari Peaking |  | PDB | 6*17 | 102 | 14 | 22553 | Low demand
49 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 306120 | Low demand
| Juldah 100 MW Unit-3 |  | IPP | 0 | 100 | 101 | 504960
50 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 393744
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 386400
51 | Chattogram ECPV 108 MW |  | IPP | 16*7 | 108 | 0 | 37440 | Reserve
| Chattogram area Total |  |  |  | 1681 | 689 | 11955508
52 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 1690506 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1939420 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
53 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 199 | 4496000 | FGMO
54 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 360 | 7336000
55 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6753000 | Transformer O/L
56 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 473976 | Engine problem
57 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 5 | 128160 | Gas shortage
58 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
59 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
60 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 5 | 173150 | Low demand
| Midland 150MW |  | IPP | 23*7.015 | 150 | 15 | 68580 | Low demand
61 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
62 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 5320 | Reserve
63 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2069180
| Chandpur Desh 200MW |  | IPP | 0 | 200 | 125 | 868320 | Low demand
64 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 392652
65 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 173520
** | Tripura |  | Imported power | 0 | 160 | 124 | 2290560
66 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 66280
67 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
68 | Summit Cumilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 523420
69 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1504 | 29785498
70 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 207 | 4611800
71 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 282708
72 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 88 | 817920 | Engine problem
73 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 16350
74 | United Mymensingh PPL |  | IPP | 200 | 200 | 40 | 374400 | Low demand
| United Jamalpur PPL |  | IPP | 115 MW | 115 | 0 | 0 | Reserve
| Mymensingh Area Total |  |  |  | 637 | 357 | 6103178
75 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1262000
76 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
77 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3510720
78 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 132 | 2849000 | Dif. pressure high
79 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 387600
80 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 376000
81 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 172032
82 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 69 | 1149048 | FGMO
83 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 85 | 1419840
84 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 441360
85 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 86 | 2502380 | FGMO
86 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 75000
87 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 389720 | Engine problem
88 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 25 | 66240
89 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 320 | 7610500 | FGMO
| Bibiyana-3 285MW |  | PDB | 285 MW | 0 | 0 | 476800 | On test
90 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 20880
| Sylhet Area Total |  |  |  | 1549 | 1177 | 22709120
91 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 859 | 16743272
92 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
93 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 16 | 85280 | Low demand
94 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 44 | 100320 | Low demand
95 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
96 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 50 | 228608 | Low demand
97 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 420 | 7568064
98 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 393000
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
99 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
| Labon Chora 105 MW |  | IPP | 6*18.445 | 105 | 105 | 434880
| Khulna Area Total |  |  |  | 2209 | 1534 | 25553424
100 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 16 | 82560 | Low demand
101 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
102 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 19 | 318500 | Engine problem
103 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 187 | 4400873
104 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 96 | 697519
| Barisal Area Total |  |  |  | 462 | 318 | 5499452
105 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 60 | 1415000
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
106 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 16 | 32682 | Low demand
107 | Bera Peaking |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
108 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 592440
109 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 182482
110 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
111 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 182 | 4498718 | FGMO
112 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 180 | 4143755 | FGMO
113 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4323854 | FGMO
| Sirajgonj Unit-4 414 MW(Gas) |  | SNWPGCL | 1*282 | 282 | 0 | 0 | On test
114 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 30 | 123411 | Low demand
115 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 400800
116 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 16 | 289224
117 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 179244
118 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 771840
119 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 51 | 311191 | Low demand
| Paramount Baghabari |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
| Confidence CPBL-2 |  | IPP | 113 MW | 0 | 0 | 27840 | On test
| Rajshahi Area Total |  |  |  | 1825 | 906 | 17292481
120 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
121 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 149 | 3643500
122 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 65000
123 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 67000
| Rangpur Area Total |  |  |  | 484 | 184 | 3775500
| Total |  |  |  | 17536 | 8941 | 164919328
| Eastern Grid Total |  |  |  | 12556 | 5999 | 112798471
| Western Grid Total |  |  |  | 4980 | 2942 | 52120857
| National Grid Total |  |  |  | 17536 | 8941 | 164919328
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-03-09 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5611 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2781 | MW
i) Dhaka area |  |  | 2998 | MW | i) Khulna area |  |  | 1016 | MW
ii) Chittagong area |  |  | 895 | MW | ii) Rajshahi area |  |  | 944 | MW
iii) Comilla area |  |  | 717 | MW | iii) Barisal area |  |  | 201 | MW
iv) Mymensingh area |  |  | 669 | MW | iv) Rangpur area |  |  | 620 | MW
v) Sylhet area |  |  | 332 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8392 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 94 | 1100 | Netrokona | 81 | 1830 | Central s/s | 66 | 1900
Munsiganj | 86 | 1900 | Jamalpur | 96 | 1900 | Noapara | 74 | 1900
Sonargaon | 54 | 1900 | Sherpur | 80 | 1900 | Jessore | 120 | 1900
Shyampur | 138 | 200 | Srimongal | 26 | 1930 | Jhenida | 78 | 1900
Bhulta | 155 | 1930 | Shahjibazar | 81 | 1900 | Bottail | 86 | 1830
Madanganj | 50 | 1930 | Fenchuganj | 26 | 1830 | G.K Project | 37 | 1900
Shitalakhya | 99 | 1100 | Kulawara | 28 | 1900 | Faridpur | 120 | 1900
Rahim steel | 9 | 1300 | Sylhet | 97 | 1900 | Madaripur | 107 | 2100
Matuail | 72 | 1000 | Chatak | 23 | 1930 | Gopalganj | 64 | 1900
Ghorasal | 59 | 1900 | Sunamganj | 24 | 1930 | Bagerhat | 62 | 1900
Narsingdi | 100 | 1930 | Biani Bazar | 30 | 1930 | Mongla | 28 | 100
Haripur (SBU) | 88 | 1900 | Comilla (S) | 124 | 1830 | Satkhira | 70 | 1930
Ullon | 60 | 1830 | Comilla(N) | 73 | 1900 | Gallamari | 34 | 1200
Hasnabad | 143 | 1830 | Chandpur | 74 | 2000 | Magura | 40 | 2000
Magbazar | 87 | 1300 | Feni | 98 | 1830 | Chuadanga | 59 | 1900
Maniknagar | 76 | 1200 | Chowmuhani | 132 | 1900 | Barisal | 84 | 1900
Bangabhaban | 14 | 1100 | Ashuganj | 41 | 1930 | Patuakhali | 61 | 1900
Narinda | 72 | 1200 | Daudkandi | 88 | 2100 | Bhandaria | 38 | 1830
Dhanmondi | 63 | 1800 | B.Baria | 88 | 1900 | Ishurdi | 41 | 1900
Lalbag | 60 | 1830 | Ramganj | 24 | 1900 | Ruppur Paromanobik | 1 | 100
Madartek | 36 | 1900 | Madunaghat | 45 | 1830 | Natore | 87 | 1930
Mirpur | 78 | 1830 | Hathazari | 68 | 1800 | Bogra | 183 | 1930
Kalyanpur | 72 | 1300 | Khulshi | 160 | 1830 | Noagaon | 107 | 1900
Gulshan | 80 | 1300 | Halishahar | 96 | 1500 | Rajshahi | 112 | 2000
Uttara | 35 | 1830 | Baraulia | 111 | 1400 | C.Nawabganj | 56 | 1930
Uttara(New) | 11 | 1000 | Sikalbaha | 28 | 1830 | Amnura | 34 | 1900
Kamrangirchar | 72 | 1830 | Dohazari | 66 | 2000 | Pabna | 81 | 1900
Savar | 106 | 1200 | Cox'sbazar | 74 | 1900 | Shahjadpur | 70 | 1930
Bhasantec | 108 | 1930 | Chandraghona | 19 | 1830 | Serajganj | 63 | 1200
Agargaon | 37 | 1900 | Kaptai | 4 | 1900 | Niyamatpur | 72 | 1900
Satmosjid | 66 | 1900 | A. Khaer Stl. | 0 | 0 | Joypurhat | 44 | 1900
Tongi | 114 | 1800 | Bakulia | 79 | 1900 | Mohastangor | 5 | 700
Kabirpur | 165 | 1500 | Julda | 20 | 1500 | Rangpur | 105 | 1830
Basundhara | 90 | 1830 | TK chemical | 3.2 | 1200 | Lalmonirhat | 85 | 1900
Manikganj | 62 | 1900 | Modern Steel | 16 | 1200 | Saidpur | 98 | 1900
Joydevpur | 187 | 1900 | Shahmirpur | 24 | 1830 | Purbasadipur | 90 | 1900
New Tongi | 85 | 1200 | Khagrachhari | 16 | 1830 | Thakurgaon | 64 | 1900
Kodda | 195 | 1900 | Matarbari | 20 | 1900 | Palashbari | 92 | 1900
Dhamrai | 42 | 1830 | Baroiar Hat | 16 | 2000 | Barapukuria | 49 | 1930
Valuka | 55 | 2000 | Rangamati | 8 | 1800 | Panchagar | 40 | 1830
Tangail | 152 | 1830 | Abul Khair 230 | 125 | 400 | Joldhaka | 17 | 800
Mymensing | 168 | 1900 | BSRM | 136 | 1000
Kishorganj | 74 | 1900 | Goalpara | 20 | 1800
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-03-09
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 409 | 2:00 | 396 | 17:00 | Kaliakoir | 398 | 2:00 | 384 | 12:00
Bheramara | 404 | 3:00 | 385 | 18:30 | Bhulta | 408 | 2:00 | 395 | 12:00
Ashuganj(N) | 410 | 1:00 | 399 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 240 | 1:00 | 235 | 10:00 | Hathazari | 222 | 5:00 | 214 | 10:00
Ishurdi | 238 | 2:00 | 230 | 19:00 | Megnaghat | 237 | 5:00 | 228 | 14:00
Ashuganj | 244 | 1:00 | 238 | 13:00 | Fenchuganj | 241 | 24:00 | 236 | 8:00
Serajganj | 229 | 1:00 | 222 | 20:00 | Siddhirganj | 237 | 4:00 | 228 | 12:00
Baghabari | 232 | 3:00 | 228 | 8:00 | Maniknagar | 234 | 1:00 | 226 | 15:00
Barapukuria | 228 | 15:00 | 222 | 9:00 | Old Airport | 235 | 2:00 | 224 | 15:00
Bogra | 228 | 3:00 | 215 | 19:00 | Barisal | 235 | 23:00 | 226 | 7:00
Khulna South | 241 | 5:00 | 226 | 7:00 | AKSML | 226 | 7:00 | 214 | 15:00
Rampura | 232 | 4:00 | 228 | 12:00 | BSRM | 225 | 2:00 | 216 | 14:00
Haripur | 233 | 5:00 | 228 | 12:00 | Bibiyana | 241 | 2:00 | 235 | 17:00
Hasnabad | 235 | 1:00 | 226 | 11:00 | Bhulta | 236 | 1:00 | 227 | 14:00
Aminbazar | 235 | 1:00 | 225 | 12:00 | Ashuganj (S) | 242 | 2:00 | 236 | 13:00
Tongi | 231 | 1:00 | 224 | 11:00 | Kaliakoir | 237 | 2:00 | 227 | 12:00
Comilla (N) | 240 | 2:00 | 235 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 200 | 131 | 1200 | Madanhat | 133 | 100 | 129 | 1000
Munsiganj | 135 | 100 | 130 | 1200 | Hathazari | 133 | 500 | 129 | 1000
Megnaghat | 136 | 400 | 131 | 700 | Khulshi | 130 | 700 | 125 | 1000
Shyampur | 139 | 100 | 130 | 1500 | Halishahar | 132 | 1900 | 125 | 1500
Bhulta | 132 | 100 | 124 | 1200 | Baraulia | 131 | 700 | 126 | 1500
Madanganj | 138 | 1900 | 130 | 1200 | Sikalbaha | 132 | 1900 | 126 | 1500
Shitalakhya | 141 | 400 | 132 | 1500 | Dohazari | 131 | 300 | 127 | 1500
Rahim steal | 136 | 100 | 132 | 1200 | Cox'sbazar | 126 | 100 | 120 | 2000
Matuail | 137 | 300 | 131 | 1200 | Chandraghona | 132 | 100 | 128 | 1600
Ghorasal | 145 | 100 | 140 | 900 | Kaptai | 134 | 500 | 129 | 1500
Narsinghdi | 136 | 600 | 130 | 1800 | A. Khaer Stl. | 130 | 100 | 126 | 1500
Haripur (SBU) | 134 | 100 | 132 | 1000 | Bakulia | 129 | 700 | 124 | 1500
Ullon | 136 | 100 | 131 | 1000 | Julda | 130 | 100 | 126 | 1600
Hasnabad | 138 | 100 | 133 | 1300 | TK Chemical | 135 | 100 | 129 | 1600
Magbazar | 137 | 200 | 130 | 1300 | Modern Steel | 131 | 200 | 126 | 1000
Maniknagar | 135 | 100 | 130 | 1500 | Shahmirpur | 132 | 1900 | 127 | 1500
Bangabhaban | 140 | 400 | 131 | 1300 | Khagrachhari | 132 | 1830 | 128 | 1200
Narinda | 137 | 200 | 130 | 1400 | Matarbari | 129 | 400 | 122 | 1930
Dhanmondi | 136 | 100 | 131 | 1000 | Baroiar Hat | 133 | 100 | 130 | 2100
Lalbag | 140 | 400 | 131 | 1300 | Rangamati | 132 | 600 | 128 | 1000
Madartek | 137 | 200 | 130 | 1400 | Goalpara | 137 | 200 | 127 | 700
Mirpur | 136 | 100 | 127 | 1200 | Central s/s | 138 | 400 | 128 | 800
Kalyanpur | 136 | 100 | 131 | 900 | Noapara | 135 | 100 | 126 | 1930
Gulshan | 136 | 100 | 130 | 1200 | Jessore | 132 | 200 | 124 | 800
Uttara | 136 | 100 | 128 | 1300 | Jhenida | 134 | 500 | 118 | 1900
Uttara New | 134 | 300 | 127 | 1200 | Bottail | 139 | 200 | 132 | 1900
Kamrangirchar | 140 | 600 | 131 | 1300 | G.K.Project | 142 | 300 | 139 | 1830
Savar | 133 | 300 | 126 | 1200 | Faridpur | 135 | 400 | 128 | 2000
Bhasantec | 136 | 500 | 128 | 1200 | Madaripur | 134 | 1000 | 130 | 700
Agargaon | 136 | 200 | 129 | 1500 | Gopalganj | 137 | 1700 | 128 | 700
Satmosjid | 136 | 200 | 129 | 1300 | Bagerhat | 136 | 500 | 130 | 1930
Tongi | 138 | 100 | 132 | 1800 | Mongla | 132 | 900 | 126 | 700
Kabirpur | 135 | 400 | 130 | 1800 | Satkhira | 136 | 200 | 126 | 700
Basundhara | 131 | 100 | 126 | 1800 | Gallamari | 138 | 200 | 129 | 700
Manikganj | 140 | 100 | 135 | 1830 | Magura | 135 | 200 | 120 | 700
Joydevpur | 140 | 600 | 134 | 1500 | Chuadanga | 131 | 100 | 114 | 1900
New Tongi | 136 | 100 | 130 | 1500 | Barisal | 137 | 200 | 135 | 1200
Kodda | 139 | 2000 | 133 | 1200 | Patuakhali | 135 | 100 | 130 | 1830
Dhamrai | 135 | 2400 | 130 | 1800 | Bhandaria | 135 | 300 | 130 | 1830
Valuka | 130 | 300 | 118 | 800 | Ishurdi | 141 | 300 | 136 | 1830
Tangail | 134 | 400 | 127 | 800 | Ruppur Paromanobik | 141 | 100 | 136 | 1900
Mymensing | 134 | 2300 | 124 | 800 | Natore | 137 | 1000 | 133 | 1500
Kishorganj | 135 | 300 | 126 | 1830 | Bogra | 138 | 200 | 128 | 1900
Netrokona | 135 | 500 | 124 | 1830 | Noagaon | 134 | 300 | 124 | 1900
Jamalpur | 132 | 2200 | 120 | 1800 | Rajshahi | 133 | 900 | 129 | 400
Sherpur | 132 | 2300 | 117 | 800 | C.Nawabganj | 130 | 700 | 124 | 1500
Srimongal | 140 | 900 | 136 | 1830 | Amnura | 134 | 800 | 124 | 1500
Shahjibazar | 141 | 700 | 135 | 1600 | Pabna | 136 | 300 | 130 | 800
Fenchuganj | 137 | 600 | 135 | 1500 | Shahjadpur | 142 | 100 | 137 | 2000
Khulawara | 138 | 500 | 135 | 1300 | Serajganj | 137 | 100 | 130 | 1900
Sylhet | 137 | 600 | 134 | 1500 | Niyamatpur | 132 | 300 | 118 | 1900
Chatak | 137 | 200 | 134 | 1400 | Joypurhat | 135 | 200 | 122 | 1900
Sunamganj | 136 | 200 | 133 | 1500 | Mohastangor | 135 | 100 | 127 | 1830
Biani Bazar | 137 | 200 | 134 | 1600 | Rangpur | 132 | 400 | 116 | 900
Comilla(s) | 129 | 200 | 125 | 800 | Lalmonirhat | 127 | 200 | 110 | 1200
Comilla(n) | 140 | 1800 | 136 | 1100 | Saidpur | 133 | 300 | 116 | 1300
Chandpur | 138 | 1600 | 135 | 2300 | Purbasadipur | 130 | 100 | 116 | 900
Feni | 134 | 700 | 127 | 1000 | Thakurgaon | 128 | 300 | 106 | 1900
Chowmuhani | 132 | 800 | 130 | 1800 | Palashbari | 133 | 200 | 120 | 800
Ashuganj | 140 | 200 | 136 | 1500 | Barapukuria | 133 | 200 | 122 | 900
Daudkandi | 136 | 800 | 133 | 1000 | Panchagar | 127 | 400 | 102 | 1900
B.Baria | 137 | 300 | 133 | 1800 | Joldhaka | 132 | 300 | 114 | 1900

## L-Curve
Date | 2019-03-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 210 | 4878 | 2034 | 6912 |  |  |  | QF-LDC-12
0:30 | 110 | 4604.5 | 1856.5 | 6461 | Date: | 2019-03-09
1:00 | 10 | 4331 | 1679 | 6010
1:30 | 10 | 4201 | 1635.5 | 5836.5
2:00 | 10 | 4071 | 1592 | 5663
2:30 | 10 | 3983.5 | 1573 | 5556.5 | [5 empty] | Gen. at Eve. Peak | 8941 | 8941 MW (19:30 )
3:00 | 10 | 3896 | 1554 | 5450 | [6 empty] | 19:30
3:30 | 10 | 3722 | 1546.5 | 5268.5 | [5 empty] | Gen. at Day Peak | 6789.4 | 6789.4 MW (12:00 )
4:00 | 10 | 3548 | 1539 | 5087 | [6 empty] | 12:00
4:30 | 10 | 3583.5 | 1547.5 | 5131 | [5 empty] | Highest Generation | 8941
5:00 | 10 | 3619 | 1556 | 5175 | [6 empty] | 19:30
5:30 | 75 | 3758 | 1579.5 | 5337.5
6:00 | 140 | 3897 | 1603 | 5500
6:30 | 150 | 4047.31 | 1794.5 | 5841.81
7:00 | 160 | 4197.62 | 1986 | 6183.62
7:30 | 100 | 4237.11 | 2074 | 6311.11
8:00 | 40 | 4276.6 | 2162 | 6438.6
8:30 | 35 | 4307.05 | 2196 | 6503.05
9:00 | 30 | 4337.5 | 2230 | 6567.5
9:30 | 75 | 4316.25 | 2240.5 | 6556.75
10:00 | 120 | 4295 | 2251 | 6546
10:30 | 140 | 4472.65 | 2193 | 6665.65
11:00 | 160 | 4650.3 | 2135 | 6785.3
11:30 | 120 | 4659.35 | 2128 | 6787.35
12:00 | 80 | 4668.4 | 2121 | 6789.4
12:30 | 80 | 4670.35 | 2168.5 | 6838.85
13:00 | 80 | 4672.3 | 2216 | 6888.3
13:30 | 65 | 4566.15 | 2181 | 6747.15
14:00 | 50 | 4460 | 2146 | 6606
14:30 | 110 | 4639.8 | 2141.5 | 6781.3
15:00 | 170 | 4819.6 | 2137 | 6956.6
15:30 | 150 | 4763.8 | 2098 | 6861.8
16:00 | 130 | 4708 | 2059 | 6767
16:30 | 140 | 4681.65 | 2025.5 | 6707.15
17:00 | 150 | 4655.3 | 1992 | 6647.3
17:30 | 135 | 4702.15 | 2079 | 6781.15
18:00 | 120 | 4749 | 2166 | 6915
18:30 | 200 | 5403.5 | 2521 | 7924.5
19:00 | 280 | 6058 | 2876 | 8934
19:30 | 250 | 5999 | 2942 | 8941
20:00 | 280 | 5884 | 2894 | 8778 |  |  |  | Executive Engineer
20:30 | 250 | 5806.5 | 2882.5 | 8689 |  |  |  | Network Operation Division
21:00 | 220 | 5729 | 2871 | 8600
21:30 | 225 | 5567.5 | 2686 | 8253.5
22:00 | 230 | 5406 | 2501 | 7907 |  |  |  |  | Page 6 of 7
22:30 | 215 | 5331 | 2366 | 7697
23:00 | 200 | 5256 | 2231 | 7487
23:30 | 205 | 5067 | 2132.5 | 7199.5
24:00 | 210 | 4878 | 2034 | 6912
8941 MW (19:30 )
6789.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-03-09 |  | Energy | 164919328
[10 empty] | 2019-03-09 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4394 | 761 | 1289 | 158 | 149 | 71 | 0 | 0 | 90
0:30 | 4325 | 639 | 1095 | 96 | 149 | 71 | 0 | 0 | 86 | Date: | 2019-03-09
1:00 | 4256 | 517 | 901 | 34 | 149 | 71 | 0 | 0 | 82
1:30 | 4126.5 | 517.5 | 859 | 34 | 149 | 70.5 | 0 | 0 | 80 | [7 empty] | Total Energy | 164.9193 | Total Energy Gen 164.919 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 164.919 MKWHr
2:00 | 3997 | 518 | 817 | 34 | 149 | 70 | 0 | 0 | 78 | [7 empty] | Energy not Served | 0
2:30 | 3908 | 517.5 | 801 | 34 | 149 | 70 | 0 | 0 | 77 | [7 empty] | Energy Requirement | 164.9193
3:00 | 3819 | 517 | 785 | 34 | 149 | 70 | 0 | 0 | 76
3:30 | 3672.5 | 517 | 761 | 25.5 | 149 | 69.5 | 0 | 0 | 74 | [6 empty] | Shortage
4:00 | 3526 | 517 | 737 | 17 | 149 | 69 | 0 | 0 | 72
4:30 | 3558.5 | 517 | 748 | 17 | 149 | 68.5 | 0 | 0 | 73
5:00 | 3591 | 517 | 759 | 17 | 149 | 68 | 0 | 0 | 74
5:30 | 3688.5 | 517.5 | 821 | 17 | 149 | 68.5 | 0 | 0 | 76
6:00 | 3786 | 518 | 883 | 17 | 149 | 69 | 0 | 0 | 78
6:30 | 3940 | 579 | 942 | 59.5 | 149 | 69.5 | 25.5 | 0 | 76 |  |  |  |  | Coal
7:00 | 4094 | 640 | 1001 | 102 | 149 | 70 | 51 | 0 | 74
7:30 | 4137 | 676.5 | 996 | 136.5 | 149 | 70 | 62 | 0 | 78 |  |  |  | Oil |  |  |  | ,
8:00 | 4180 | 713 | 991 | 171 | 149 | 70 | 73 | 0 | 82
8:30 | 4219.5 | 713.5 | 999.5 | 182 | 149 | 71 | 77 | 0 | 86
9:00 | 4259 | 714 | 1008 | 193 | 149 | 72 | 81 | 0 | 90
9:30 | 4219 | 714 | 1018 | 211.5 | 149 | 72 | 81.5 | 0 | 90
10:00 | 4179 | 714 | 1028 | 230 | 149 | 72 | 82 | 0 | 90
10:30 | 4282.5 | 714 | 1063 | 250 | 149 | 72 | 41 | 0 | 92
11:00 | 4386 | 714 | 1098 | 270 | 149 | 72 | 0 | 0 | 94
11:30 | 4360.5 | 714 | 1090 | 304.5 | 149 | 72 | 0 | 0 | 95
12:00 | 4335 | 714 | 1082 | 339 | 149 | 72 | 0 | 0 | 96
12:30 | 4385.5 | 714 | 1089 | 329 | 149 | 72 | 0 | 0 | 98
13:00 | 4436 | 714 | 1096 | 319 | 149 | 72 | 0 | 0 | 100
13:30 | 4436 | 714 | 1096 | 319 | 149 | 72 | 0 | 0 | 100
14:00 | 4436 | 714 | 1096 | 319 | 149 | 72 | 0 | 0 | 100
14:30 | 4535 | 713.5 | 1088 | 260.5 | 149 | 72 | 0.5 | 0 | 102
15:00 | 4634 | 713 | 1080 | 202 | 149 | 72 | 1 | 0 | 104
15:30 | 4568.5 | 713 | 1033 | 216.5 | 149 | 72 | 4.5 | 0 | 104
16:00 | 4503 | 713 | 986 | 231 | 149 | 72 | 8 | 0 | 104
16:30 | 4450 | 713 | 968.5 | 240.5 | 149 | 72 | 11.5 | 0 | 102
17:00 | 4397 | 713 | 951 | 250 | 149 | 72 | 15 | 0 | 100
17:30 | 4430 | 713 | 893 | 368.5 | 149 | 71 | 49.5 | 0 | 107
18:00 | 4463 | 713 | 835 | 487 | 149 | 70 | 84 | 0 | 114
18:30 | 4587.5 | 786.5 | 1183 | 851 | 149 | 70 | 178.5 | 0 | 119
19:00 | 4712 | 860 | 1531 | 1215 | 149 | 70 | 273 | 0 | 124
19:30 | 4827 | 859 | 1509 | 1163 | 149 | 70 | 240 | 0 | 124
20:00 | 4833 | 859 | 1465 | 1123 | 149 | 70 | 161 | 0 | 118
20:30 | 4902 | 859 | 1463 | 983 | 149 | 70 | 144 | 0 | 119
21:00 | 4971 | 859 | 1461 | 843 | 149 | 70 | 127 | 0 | 120
21:30 | 4782.5 | 859 | 1441 | 758.5 | 149 | 70 | 77.5 | 0 | 116
22:00 | 4594 | 859 | 1421 | 674 | 149 | 70 | 28 | 0 | 112
22:30 | 4563.5 | 810 | 1428 | 555 | 149 | 70.5 | 14 | 0 | 107
23:00 | 4533 | 761 | 1435 | 436 | 149 | 71 | 0 | 0 | 102
23:30 | 4463.5 | 761 | 1362 | 297 | 149 | 71 | 0 | 0 | 96 | Max Temp. in Dhaka |  | 30.2° C
24:00 | 4394 | 761 | 1289 | 158 | 149 | 71 | 0 | 0 | 90
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 164.919 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 164.919 MKWHr
Note on W13: Author:

## Generation
2019-03-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 41 | 40 | 40 | 39 | 38 | 39 | 40 | 40 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 |  | 40 | 40 | 40 | 40 | 40 | 41 | 41 | 917760
2 | Kaptai Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 728000
3 | Chattogram ST-1 (Raozan) | 140 | 140 | 140 | 100 | 100 | 100 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 135 | 135 | 135 | 135 | 135 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3200000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [16 empty] | 0 | 6 |  | 25 | 25 | 25 | 8 | 8 | 0 |  | 77788
| Teknaf Solartech 20MW | [5 empty] | 0 | 2.42 | 8.8 | 0 | [17 empty] | 17010
6 | Sikalbaha 225MW (Gas) | 200 | 200 | 200 | 186 | 187 | 213 | 201 | 217 | 207 | 203 | 201 | 201 | 204 | 215 | 210 | 202 | 201 | 214 |  | 201 | 201 | 201 | 201 | 201 | 200 | 200 | 4839573
7 | Sikalbaha 225MW (Oil)
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil)
| Dohazari Peaking | [19 empty] | 17 | 14 | 0 |  |  |  |  | 22553
12 | Hathazari peaking
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [19 empty] | 0 | [6 empty] | 5320
15 | Siddhirgonj ST 210MW | 110 | 110 | 110 | 110 | 110 | 115 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2586150
16 | Siddhirgonj GT Unit-1& 2 | 80 | 70 | 80 | 0 | [5 empty] | 37 | 80 | 80 | 73 | 80 | 120 | 77 | 77 | 120 |  | 120 | 120 | 120 | 195 | 175 | 195 | 145 | 2065000
17 | Siddhirganj CCPP-335 MW | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 0 | 0 |  | 0 | 115 | 115 | 115 |  | 115 | 115 | 115 | 114 | 115 | 115 | 115 | 2353110
18 | Summit Gazipur -2
19 | Ashuganj 195MW Modular | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal ST: Unit-1,2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836000
21 | Ghorasal GT: Unit-3
22 | Ghorasal GT: Unit-4
23 | Ghorasal ST: Unit-5 | 190 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 195 | 190 | 190 | 190 | 190 | 190 | 190 | 4473000
24
25 | Ghorasal ST: Unit-7 | 270 | 250 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 280 | 320 | 320 | 350 | 300 | 380 | 380 | 340 | 330 |  | 330 | 330 | 330 | 380 | 270 | 270 | 270 | 7148818
26
28 | Ashuganj ST: Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1690506
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1939420
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 37 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 473976
33 | Ashuganj CCPP 225 MW | 184 | 183 | 152 | 152 | 183 | 183 | 166 | 180 | 183 | 180 | 188 | 224 | 190 | 205 | 205 | 185 | 185 | 206 |  | 185 | 199 | 199 | 197 | 185 | 185 | 185 | 4496000
34 | Ashuganj CCPP(South) | 300 | 250 | 240 | 230 | 230 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 310 | 280 | 280 | 280 |  | 280 | 280 | 280 | 315 | 320 | 315 | 315 | 6753000
| Ashuganj CCPP(North) | 300 | 260 | 250 | 230 | 230 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 300 | 300 | 270 |  | 360 | 360 | 360 | 360 | 360 | 360 | 325 | 7336000
35 | Ashuganj (Precision) 55MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 128160
36 | Chandpur CCPP | 100 | 100 | 100 | 50 | 50 | 50 | 90 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2069180
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 0 | [21 empty] | 97500
39 | Haripur 412 MW CCPP | 349 | 340 | 340 | 300 | 325 | 377 | 379 | 358 | 363 | 363 | 390 | 354 | 374 | 362 | 388 | 355 | 360 | 363 |  | 374 | 360 | 350 | 380 | 353 | 350 | 349 | 8741890
40 | Meghnaghat CCPP 450MW | 380 | 330 | 300 | 300 | 320 | 320 | 350 | 350 | 350 | 350 | 420 | 420 | 420 | 330 | 450 | 450 | 450 | 340 |  | 450 | 450 | 450 | 450 | 450 | 450 | 420 | 8807625
41 | Haripur Power CCPP 360MW
42 | Mymensingh RPCL 210MW | 214 | 216 | 151 | 147 | 151 | 152 | 218 | 212 | 209 | 208 | 204 | 206 | 201 | 190 | 191 | 193 | 203 | 203 |  | 207 | 207 | 206 | 205 | 205 | 198 | 198 | 4611800
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 58 | 57 | 58 | 23 | 23 | 23 | 23 | 23 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 56 | 58 | 60 |  | 60 | 60 | 60 | 58 | 60 | 58 | 58 | 1262000
45 | Fenchugonj CCPP-2
46 | Shajibazar 330 MW | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 134 | 135 | 136 | 134 | 135 | 134 | 132 | 135 | 135 |  | 135 | 132 | 134 | 133 | 112 | 111 | 113 | 2849000
47 | Shahjibazar GT: Unit- 8, 9 | 40 | 40 | 40 | 40 | 40 | 40 | 71 | 53 | 52 | 66 | 40 | 51 | 51 | 50 | 50 | 40 | 40 | 40 |  | 63 | 69 | 68 | 68 | 45 | 56 | 46 | 1149048
48 | Shahjibazar 86MW | 5 | 5 | 5 | 5 | 5 | 89 | 89 | 89 | 86 | 89 | 89 | 89 | 89 | 87 | 40 | 10 | 10 | 10 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1419840
49 | Shahjibazar (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 441360
50 | Sylhet GT 150 MW | 84 | 98 | 84 | 89 | 100 | 95 | 104 | 114 | 118 | 118 | 105 | 115 | 115 | 122 | 111 | 106 | 90 | 97 |  | 85 | 86 | 86 | 93 | 103 | 106 | 103 | 2502380
51 | Sylhet GT 20 MW | [19 empty] | 19 | 19 | 19 | 19 | 19 | 0 |  | 75000
52 | Sylhet (EPL) 50MW | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 6 | 6 | 7 | 7 |  | 47 | 46 | 46 | 46 | 46 | 46 | 44 | 389720
53 | Sylhet (Desh) 10MW | [19 empty] | 10 | 10 | 10 |  |  |  |  | 20880
54 | Hobiganj 11MW | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 0 |  |  |  | 172032
55 | Fenchugonj (Barakatullah) 51MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 387600
56 | Shahjahanulla 25 MW | [16 empty] | 0 | 0 |  | 25 | 25 | 25 | 0 |  |  |  | 66240
57 | Summit Bibiana- 2 | 300 | 285 | 285 | 265 | 270 | 310 | 325 | 320 | 310 | 320 | 320 | 300 | 310 | 300 | 320 | 290 | 275 | 270 |  | 290 | 320 | 275 | 320 | 280 | 290 | 280 | 7610500
58 | Southern 55MW | [9 empty] | 0 | 17 | 55 | 35 | 0 | 0 |  | 0 | 28 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 456100
59 | Sikalbaha (Energis) | 0 | [8 empty] | 0 | 12 | 24 | 24 | 24 | 24 | 24 | 27 | 33 |  | 33 | 33 | 33 | 41 | 41 | 41 | 41 | 442080
60 | Barabkunda (Regent) | 21 | 21 | 0 |  |  |  | 0 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 20 | 19 | 19 | 19 | 393744
61 | Narshingdi (Doreen) | [7 empty] | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 |  | 0 | 22 | 22 | 0 |  |  |  | 210132
62 | Tangail (Doreen) 22MW | [10 empty] | 22 | 22 | 20 | 20 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 282708
63 | Tripura | 82 | 78 | 76 | 72 | 74 | 78 | 74 | 82 | 90 | 90 | 94 | 96 | 100 | 104 | 104 | 104 | 100 | 114 |  | 124 | 124 | 118 | 120 | 112 | 102 | 90 | 2290560
64 | Malancha, Ctg. EPZ (United) | 28 | 10 | 10 | 10 | 10 | 10 | 28 | 7 | 2 | 2 | 2 | 2 | 9 | 7 | 2 | 2 | 10 | 6 |  | 19 | 26 | 26 | 30 | 30 | 35 | 35 | 386400
65 | Feni (Doreen) 22MW | 22 | 0 |  |  |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 392652
66 | Feni, Mohipal (Doreen) | 0 | [6 empty] | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 173520
67 | Jangalia (Summit) 33MW | [16 empty] | 0 | 0 |  | 33 | 33 | 33 | 0 |  |  |  | 66280
68 | Summit Cumilla 25MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 523420
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 24 | 24 | 24 | 24 | 30 | 22 | 22 | 22 | 22 | 18 | 18 | 24 | 22 | 22 |  | 26 | 32 | 32 | 32 | 32 | 32 | 32 | 605880
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577900
72 | Summit Rupganj | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 29 |  | 22 | 29 | 29 | 29 | 29 | 29 | 29 | 591500
73 | Ghorashal (Regent) | 13 | 13 | 13 | 0 | [13 empty] | 0 |  | 108 | 42 | 42 | 0 |  |  |  | 246727
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | [8 empty] | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 51 |  | 51 | 51 | 51 | 51 | 26 | 0 |  | 473340
79 | Kodda 149MW
80 | Jamalpur 95MW | [7 empty] | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 88 | 88 | 88 | 88 | 88 | 88 | 50 | 817920
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | [19 empty] | 10 | 0 | [5 empty] | 13824
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj (Powerpac) 100MW
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL)
88 | Ghorashal 78MW (MAX) | [19 empty] | 35 | 40 | 40 | 40 | 40 | 40 | 0 | 337120
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 20 | 10 | 10 | 10 | 10 | 10 | 306120
92 | Fenchuganj (EPL) 44MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 376000
93 | Ashuganj (Midland) 51MW | 5 | 5 | 5 | 0 | [5 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 15 | 5 | 5 | 5 | 5 | 5 | 5 | 173150
94 | Gagnagar (Orion) | [9 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 40 | 7 | 0 |  |  |  |  | 124128
95 | Patenga 50MW | [16 empty] | 0 | 6 |  | 47 | 40 | 28 | 0 |  |  |  | 82080
96 | Chattogram ECPV 108 MW | [17 empty] | 10 |  | 30 | 0 | 0 |  |  |  |  | 37440
97 | Katpotti 51 MW | [19 empty] | 39 | 48 | 48 | 0 |  |  |  | 97632
98 | Bosila 108MW | [19 empty] | 24 | 45 | 54 | 16 | 11 | 0 |  | 60480
99 | Madanganj-55 MW | [10 empty] | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 31 | 15 | 15 | 15 | 15 | 15 | 15 | 238105
100 | Northern 55 MW | [17 empty] | 18 |  | 55 | 55 | 55 | 0 |  |  |  | 105406
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 130 | 163 | 130 | 100 | 100 |  | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 3510720
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.2 | 0.8 | 1.5 | 2 | 2.3 | 2.4 | 2.3 | 2 | 1.6 | 1 | 0.3 | 0 |  | 0 | [6 empty] | 16350
103 | Banco Energy 54MW | 17 | 17 | 17 | 0 | [10 empty] | 0 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 331560
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 36 | 40 | 40 | 40 | 40 | 7 | 7 | 374400
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | [17 empty] | 0 |  | 25 | 36 | 36 | 0 |  |  |  | 66240
115 | Juldah 100 MW Unit-3 | [16 empty] | 10 | 70 |  | 101 | 101 | 101 | 101 | 100 | 60 | 0 | 504960
116 | Chandpur Desh 200MW | [9 empty] | 0 | 24 | 52 | 52 | 53 | 53 | 53 | 60 | 90 |  | 108 | 125 | 120 | 80 | 34 | 0 |  | 868320
117 | Midland 150MW | [17 empty] | 0 |  | 30 | 15 | 0 | 0 |  |  |  | 68580
118 | Bibiyana-3 285MW | [10 empty] | 0 | 40 | 40 | 40 | 40 | 30 | 34 | 0 |  | 0 | [6 empty] | 476800
United Jamalpur PPL
120 | Eastern Zone Total | 4331 | 4071 | 3896 | 3548 | 3619 | 3897 | 4197.62 | 4276.6 | 4337.5 | 4295 | 4650.3 | 4668.4 | 4672.3 | 4460 | 4819.6 | 4708 | 4655.3 | 4749 |  | 6058 | 5999 | 5884 | 5729 | 5406 | 5256 | 4878 | 112798471
121
122 | o
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3)
125 | Khulna (KPCL-2) | [17 empty] | 16 |  | 16 | 16 | 16 | 16 | 0 |  |  | 85280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur Peaking | [17 empty] | 23 |  | 44 | 44 | 18 | 18 | 0 |  |  | 100320
Khulna CCPP 225MW
129 | Labon Chora 105 MW | [17 empty] | 17 |  | 105 | 105 | 105 | 105 | 53 | 17 | 0 | 434880
130
131
132
133
| Summit Barisal 110 MW | [17 empty] | 13 |  | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 82560
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 11 | 11 | 10 | 0 |  |  |  | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 |  | 97 | 96 | 96 | 95 | 96 | 96 | 66 | 697519
| Bhola CCPP 194MW | 174 | 167 | 164 | 164 | 164 | 164 | 153 | 190 | 189 | 187 | 186 | 174 | 185 | 184 | 184 | 184 | 159 | 185 |  | 165 | 187 | 186 | 189 | 168 | 179 | 158 | 4400873
140 | Bhola (Venture) 33MW | 15 | 14 | 13 | 13 | 13 | 13 | 12 | 11 | 11 | 11 | 11 | 13 | 10 | 13 | 12 | 11 | 10 | 13 |  | 19 | 19 | 19 | 19 | 18 | 17 | 16 | 318500
141 | Bangla Trak Noapara
142 | Noapara (KZA) 40MW | [7 empty] | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 8 | 8 |  | 41 | 40 | 40 | 40 | 40 | 40 | 0 | 393000
143 | Gopalganj Peaking | [14 empty] | 1 | 8 | 15 | 30 |  | 80 | 50 | 40 | 40 | 22 | 0 |  | 228608
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 517 | 518 | 517 | 517 | 517 | 518 | 640 | 713 | 714 | 714 | 714 | 714 | 714 | 713 | 713 | 713 | 713 | 713 |  | 860 | 859 | 859 | 859 | 859 | 761 | 761 | 16743272
147 | Bheramara 360 MW | 260 | 220 | 220 | 240 | 260 | 260 | 300 | 300 | 340 | 340 | 340 | 340 | 340 | 280 | 320 | 280 | 280 | 300 |  | 350 | 420 | 424 | 420 | 300 | 250 | 250 | 7568064
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3643500
153 | Baghabari GT 71MW | 60 | 60 | 60 | 45 | 45 | 45 | 70 | 65 | 65 | 65 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 65 | 60 | 60 | 60 | 60 | 60 | 45 | 1415000
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | [19 empty] | 16 | 16 | 17 | 0 |  |  |  | 32682
157 | Sirajgonj Unit-1 225MW (Gas) | 182 | 159 | 145 | 135 | 135 | 165 | 173 | 165 | 167 | 168 | 176 | 162 | 201 | 191 | 203 | 186 | 189 | 191 |  | 195 | 182 | 187 | 200 | 188 | 182 | 181 | 4498718
158 | Sirajgonj Unit-1 225MW (Oil)
| Sirajgonj Unit-2 225MW (Gas) | 146 | 148 | 130 | 130 | 130 | 146 | 163 | 156 | 158 | 161 | 150 | 148 | 190 | 188 | 199 | 182 | 155 | 156 |  | 176 | 180 | 184 | 197 | 184 | 178 | 178 | 4143755
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas) | 154 | 135 | 135 | 135 | 135 | 135 | 155 | 163 | 161 | 164 | 162 | 187 | 201 | 194 | 206 | 184 | 159 | 162 |  | 183 | 186 | 190 | 203 | 190 | 184 | 183 | 4323854
Sirajgonj Unit-3 225 MW(Oil)
160 | Sirajgonj Unit-4 414 MW(Gas)
161 | Bera Peaking
162 | Bogra (GBB) | 3 | 3 | 3 | 3 | 3 | 3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 400800
163 | Bogra (EPL) | 3 | 3 | 3 | 3 | 0 | 0 | 5 | 14 | 14 | 16 | 16 | 17 | 17 | 17 | 16 | 16 | 17 | 17 |  | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 289224
164 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 179244
165 | Amnura 50MW | [5 empty] | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 12 | 12 | 12 |  | 50 | 50 | 50 | 50 | 50 | 0 |  | 592440
166 | Katakhali (Northern) | [6 empty] | 0 | 8 | 24 | 24 | 0 | 0 | [5 empty] | 0 |  | 32 | 50 | 50 | 24 | 0 |  |  | 182482
167 | Katakhali Peaking
168 | Santahar Peaking | [7 empty] | 22 | 30 | 31 | 0 | 0 | [5 empty] | 14 |  | 30 | 30 | 0 | 0 |  |  |  | 123411
169 | Rajlanka 52 MW | [5 empty] | 0 | 45 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 24 | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 0 | 771840
170 | Chapainawabganj-100 MW | [5 empty] | 0 | 51 | 51 | 51 | 51 | 0 | 0 | [7 empty] | 51 | 51 | 51 | 34 | 6 | 0 |  | 311191
171 | Paramount Baghabari
172 | Confidence CPBL-2 | [9 empty] | 13 | 14 | 0 | [14 empty] | 27840
173 | Rangpur GT | [17 empty] | 17 |  | 17 | 17 | 17 | 17 | 0 |  |  | 65000
175 | Saidpur GT | [17 empty] | 0 |  | 18 | 18 | 18 | 18 | 0 |  |  | 67000
176
177
178
178 | Western Zone Total | 1679 | 1592 | 1554 | 1539 | 1556 | 1603 | 1986 | 2162 | 2230 | 2251 | 2135 | 2121 | 2216 | 2146 | 2137 | 2059 | 1992 | 2166 |  | 2876 | 2942 | 2894 | 2871 | 2501 | 2231 | 2034 | 52120857